## Lines & Transformers
Sbase = 1 MVA
| Line Data | [8 empty] | Transformers Data
| From bus- To bus | Line length(m) | R(mΩ) | X(mΩ) | Line-charging(μF) | Current-limits(A) | System voltage | Operating voltage (kV) | Voltage bases (Vb) |  | Connected to Bus | Transfor-mer Id | X(%) | Rating(kVA)
| 07:3/4-07:8.1 | 275 | 34.4 | 23.3 | 0.11 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:3/4 | T04.6 | 5.8 | 1000
| 07:3/4-07:1 | 250 | 14.4 | 6.4 | 0.0245 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:06 | T06.1 | 5.8 | 800
| 07:6-07:8.1.2 | 110 | 13.8 | 9.3 | 0.044 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | O13 | T13.1 | 4.82 | 800
| 013-07:1 | 100 | 20.6 | 9.3 | 0.035 | 300 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:29E | T5 | 5 | 1250
| 07:8.1-07:8 | 25 | 1.6 | 1.1 | 0.005 | 770 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:29E | T3 | 5 | 1250
| 07:8.1-07:8.1.1 | 15 | 1.9 | 1.3 | 0.006 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:29E | T1 | 4.9 | 1250
| 07:8.1-07:8.1.2 | 20 | 2.5 | 1.7 | 0.008 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:8.1.1.1 | T08.1 | 6.31 | 800
| 07:8.1-07:8.1.3 | 25 | 3.1 | 2.1 | 0.01 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:8.1.1.1 | T08.3 | 5 | 800
| 07:8-07:29E | 420 | 52.5 | 35.6 | 0.168 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:01 | T01.1 | 5.7 | 800
| 07:8.1.1-07:8.1.1.1 | 25 | 3.1 | 2.1 | 0.01 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:01 | T01.2 | 6.3 | 1000
| 07:8.1.2-07:11B | 330 | 41.3 | 28 | 0.132 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:19 | T19.1 | 4.27 | 400
| 07:8.1.2-07:28 | 80 | 10 | 6.8 | 0.032 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:23 | T23.1 | 4.8 | 800
| 07:8.1.3-07:19 | 225 | 28.1 | 19.1 | 0.09 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:27 | T27.2 | 4.9 | 800
| 07:8.1.3-07:35 | 400 | 50 | 33.9 | 0.16 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:41 | T40.1 | 5.8 | 800
| 07:19-07:23 | 300 | 37.5 | 25.4 | 0.12 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:11B | T11.2 | 4.5 | 1250
| 07:23-07:27 | 165 | 20.6 | 14 | 0.066 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:28 | T28.1 | 6.3 | 800
* | 07:41-07:35(SF) | 400 | 51.3 | 34.8 | 0.164 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 7:28 | T28.3 | 6.3 | 800
* | 07:35(HS)-07:12 | 25 | 4 | 1.2 | 0.004 | 205 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:35(SF) | T35.1 | 5.2 | 800
* | 07:35(HS)-07:35(SF) | 10 | 1.3 | 0.9 | 0.004 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4 |  | 07:35(SF) | T35.2 | 4.9 | 600
[11 empty] | 7:12 | T12.1 | 5.2 | 1250
[11 empty] | 7:12 | T12.2 | 5.2 | 1250
*07:35(SF) | Ställverk/Förråd
*07:35(HS) | Hyresgästens ställverk

## Buses
bus_name | Building_name | bus_number | baseKV | in_service | geodata | type | zone | VM | VA | VNLB | VNUB | VELB | VEUB
07:8 | Kraftcentral_RUM1120 | 0 | 10.5 | TRUE | 57.68936959071839, 11.977282946239676
07:8.1 | Kraftcentral_RUM4026 | 1 | 10.5 | TRUE | 57.68936959071839, 11.977282946239676
07:8.1.1 | Kraftcentral_RUM4023 | 2 | 10.5 | TRUE | 57.68936959071839, 11.977282946239676
07:8.1.2 | Kraftcentral_RUM4023 | 3 | 10.5 | TRUE | 57.68936959071839, 11.977282946239676
07:8.1.3 | Kraftcentral_RUM4023 | 4 | 10.5 | TRUE | 57.68936959071839, 11.977282946239676
07:8.1.1.1 | Kraftcentral_RUM1019 | 5 | 10.5 | TRUE | 57.68936959071839, 11.977282946239676
07:19 | Administration_RUM1031 | 6 | 10.5 | TRUE | 57.68889361071283, 11.974691932327556
07:23 | VoVI_RUM0120 | 7 | 10.5 | TRUE | 57.68744845124028, 11.977240048987328
07:28 | Maskin_RUM0303 | 8 | 10.5 | TRUE | 57.688837813397555, 11.978367919935518
07:28D5 | MaskinDel5_RUM0211 | 9 | 10.5 | TRUE | 57.68822951457298, 11.97794032573145
07:27 | VoVII_RUM0053 | 10 | 10.5 | TRUE | 57.686393009670695, 11.977594748559932
07:41 | MatematisktCentrum_RUMxx | 11 | 10.5 | TRUE | 57.68554403007448, 11.981385351028386
07:11B | ElektroData_RUMxx | 12 | 10.5 | TRUE | 57.687699324095576, 11.978917041907883
07:35 | Elektro | 13 | 10.5 | TRUE | 57.687188415166176, 11.980019287689991
07:12 | Elkraft | 14 | 10.5 | TRUE | 57.687188415166176, 11.980019287689991
07:29E | MikroElektronik_RUMxx | 15 | 10.5 | TRUE | 57.691520957780114, 11.973935169200454
013 | Keram_RUM014 | 16 | 10.5 | TRUE | 57.69046503857689, 11.974687356606786
07:1 | Fysik_RUM3118 | 17 | 10.5 | TRUE | 57.69025910014651, 11.975843018484557
07:6 | MV_RUM1110 | 18 | 10.5 | TRUE | 57.68990604836349, 11.977579105751436
07:3/4 | 07:3/4_RUM0001 | 19 | 10.5 | TRUE | 57.69070671680911, 11.975991685873511
07:4.1 | Kemi_RUM2105 | 20 | 10.5 | TRUE | 57.69098089922031, 11.977227125676464
07:4.2 | Kemi_RUM0008 | 21 | 10.5 | TRUE | 57.69124139067213, 11.978222962788031
07:8_T08.4_LV | Kraftcentral_RUM4026 | 22 | 0.4 | TRUE | 57.68936959071839, 11.977282946239676
07:28D5_T28.5_LV | MaskinDel5_RUM0211 | 23 | 0.4 | TRUE | 57.68822951457298, 11.97794032573145
07:8.1.1.1_T08.3_LV | Kraftcentral_RUM1019 | 24 | 0.4 | TRUE | 57.68936959071839, 11.977282946239676
07:8.1.1.1_T08.1_LV | Kraftcentral_RUM1019 | 25 | 0.4 | TRUE | 57.68936959071839, 11.977282946239676
07:8.1.3_T08.5_LV | Kraftcentral_RUM4023 | 26 | 0.4 | TRUE | 57.68936959071839, 11.977282946239676
07:19_T19.1_LV | Administration_RUM1031 | 27 | 0.4 | TRUE | 57.68889361071283, 11.974691932327556
07:19_T19.2_LV | Administration_RUM1031 | 28 | 0.4 | FALSE | 57.68889361071283, 11.974691932327556
07:23_T23.2_LV | VoVI_RUM0120 | 29 | 0.4 | TRUE | 57.68744845124028, 11.977240048987328
07:23_T23.1_LV | VoVI_RUM0120 | 30 | 0.4 | TRUE | 57.68744845124028, 11.977240048987328
07:27_T27.1_LV | VoVII_RUM0053 | 31 | 0.4 | FALSE | 57.686393009670695, 11.977594748559932
07:27_T27.2_LV | VoVII_RUM0053 | 32 | 0.4 | TRUE | 57.686393009670695, 11.977594748559932
07:41_T40.1_LV | MatematisktCentrum_RUMxx | 33 | 0.4 | TRUE | 57.68554403007448, 11.981385351028386
07:41_T40.2_LV | MatematisktCentrum_RUMxx | 34 | 0.4 | FALSE | 57.68554403007448, 11.981385351028386
07:11B_T11.1_LV | ElektroData_RUMxx | 35 | 0.4 | FALSE | 57.687699324095576, 11.978917041907883
07:11B_T11.2_LV | ElektroData_RUMxx | 36 | 0.4 | TRUE | 57.687699324095576, 11.978917041907883
07:28_T28.1_LV | Maskin_RUM0303 | 37 | 0.4 | TRUE | 57.688837813397555, 11.978367919935518
07:28_T28.2_LV | Maskin_RUM0303 | 38 | 0.4 | FALSE | 57.688837813397555, 11.978367919935518
07:28_T28.3_LV | Maskin_RUM0303 | 39 | 0.4 | TRUE | 57.688837813397555, 11.978367919935518
07:35_T35.1_LV | Elektro | 40 | 0.4 | TRUE | 57.687188415166176, 11.980019287689991
07:35_T35.2_LV | Elektro | 41 | 0.23 | TRUE | 57.687188415166176, 11.980019287689991
07:12_T12.1_LV | Elkraft | 42 | 0.4 | TRUE | 57.687188415166176, 11.980019287689991
07:12_T12.2_LV | Elkraft | 43 | 0.4 | TRUE | 57.687188415166176, 11.980019287689991
07:29E_T1_LV | MikroElektronik_RUMA104 | 44 | 0.4 | TRUE | 57.691520957780114, 11.973935169200454
07:29E_T2_LV | MikroElektronik_RUMA104 | 45 | 0.4 | FALSE | 57.691520957780114, 11.973935169200454
07:29E_T3_LV | MikroElektronik_RUMA104 | 46 | 0.4 | TRUE | 57.691520957780114, 11.973935169200454
07:29E_T4_LV | MikroElektronik_RUMA104 | 47 | 0.4 | FALSE | 57.691520957780114, 11.973935169200454
07:29E_T5_LV | MikroElektronik_RUMA109 | 48 | 0.4 | TRUE | 57.691520957780114, 11.973935169200454
07:29E_T6_LV | MikroElektronik_RUMA109 | 49 | 0.4 | FALSE | 57.691520957780114, 11.973935169200454
07:29E_T7_LV | MikroElektronik_RUMA109 | 50 | 0.4 | FALSE | 57.691520957780114, 11.973935169200454
013_T13.1_LV | Keram_RUM014 | 51 | 0.4 | TRUE | 57.69046503857689, 11.974687356606786
07:1_T01.1_LV | Fysik_RUM3118 | 52 | 0.4 | TRUE | 57.69025910014651, 11.975843018484557
07:1_T01.2_LV | Fysik_RUM3118 | 53 | 0.4 | TRUE | 57.69025910014651, 11.975843018484557
07:1_T01.3_LV | Fysik_RUM3118 | 54 | 0.23 | TRUE | 57.69025910014651, 11.975843018484557
07:6_T06.1_LV | MV_RUM1110 | 55 | 0.4 | TRUE | 57.68990604836349, 11.977579105751436
07:6_T06.2_LV | MV_RUM1110 | 56 | 0.4 | FALSE | 57.68990604836349, 11.977579105751436
07:3/4_T04.6_LV | 07:3/4_RUM11002 | 57 | 0.4 | TRUE | 57.69070671680911, 11.975991685873511
07:4.1_T04.1_LV | Kemi_RUM2105 | 58 | 0.4 | TRUE | 57.69098089922031, 11.977227125676464
07:4.1_T04.2_LV | Kemi_RUM2105 | 59 | 0.4 | TRUE | 57.69098089922031, 11.977227125676464
07:4.1_T04.3_LV | Kemi_RUM2105 | 60 | 0.4 | TRUE | 57.69098089922031, 11.977227125676464
07:4.2_T04.4_LV | Kemi_RUM0008 | 61 | 0.4 | FALSE | 57.69124139067213, 11.978222962788031
07:4.2_T04.5_LV | Kemi_RUM0008 | 62 | 0.4 | TRUE | 57.69124139067213, 11.978222962788031
ExtGrid | Artificial_bus_extGrid | 63 | 10.5 | TRUE | 57.68936959071839, 11.977282946239676
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: "Box\Common project folder\Chalmers Campus Test Bed\Original Maps and Material from AH\MV el diagram with PV.pdf"
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Have given a number just in order for now. Can be changed. The aim is that other sheets would be updated automatically if we change something here.
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: "Box\Common project folder\Chalmers Campus Test Bed\Original Maps and Material from AH\MV stations with buildings.pdf"
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: n=node b=busbar m=muff
Note on F14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Location for the station at 07:24
Note on F16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MArked at the same location as 07:35
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: gen bus
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This trafo is connected to 7:8.1.1.1 or 07:8.1.3 in different versions of the single line diagram. The 2014 version is the base for what is written here

## Lines
name_names | from_busname | to_busname | from_busnumber | to_busnumber | length_km | cable_type | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | r (ohm) | x (ohm) | c (nF) | B(1/ohm) | max_I_kA | ShortTermRating | ContinousRating | in_service | angLB | angUB | probability | y_pu | capacity_kW
07:8-07:8.1_a |  | 07:8.1 | 0 | 1 | 0.025 | Al 240 | 0.125 | 0.084821 | 420 | 0.003125 | 0.0021205 | 10.5 | 6.594e-08 | 0.34 |  |  | TRUE |  |  |  | 471.5841 | 5874.2503 |  | The "old" list of lines (from sheet "Lines and Transformers")
07:8-07:8.1_b | 07:8 | 07:8.1 | 0 | 1 | 0.025 | Al 240 | 0.125 | 0.084821 | 420 | 0.00375 | 0.0021205 | 10.5 | 6.594e-08 | 0.34 |  |  | TRUE |  |  |  | 471.5841 | 5874.2503 |  | corresponding row in the new table (excel's row) | From bus- To bus | cable_type | Line length(m) | r_per_km | R(mΩ) | X_per_km | X(mΩ) |  | Line-charging(μF) | Current-limits(A) | System voltage | Operating voltage (kV) | Voltage bases (Vb)
07:8-07:29E_a | 07:8 | 07:29E | 0 | 15 | 0.42 | Al 240 | 0.125 | 0.084821 | 420 | 0.0525 | 0.035625 | 176.4 | 1.1078e-06 | 0.34 |  |  | TRUE |  |  |  | 28.0705 | 5874.2503 |  | 9 | 07:3/4-07:8.1 | Al 240 | 275 | 125.0909 | 34.4 | 84.7273 | 23.3 | 0.4 | 0.11 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8-07:29E_b | 07:8 | 07:29E | 0 | 15 | 0.42 | Al 240 | 0.125 | 0.084821 | 420 | 0.0525 | 0.035625 | 176.4 | 1.1078e-06 | 0.34 |  |  | FALSE |  |  |  | 28.0705 | 5874.2503 |  | 25 | 07:3/4-07:1 | Al 150 | 250 | 57.6 | 14.4 | 25.6 | 6.4 | 0.098 | 0.0245 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1-07:8.1.1 | 07:8.1 | 07:8.1.1 | 1 | 2 | 0.015 | Al 240 | 0.125 | 0.084821 | 420 | 0.001875 | 0.0012723 | 6.3 | 3.9564e-08 | 0.34 |  |  | TRUE |  |  |  | 785.9735 | 5874.2503 |  | 13 | 07:6-07:8.1.2 | Al 240 | 110 | 125.4545 | 13.8 | 84.5455 | 9.3 | 0.4 | 0.044 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1-07:8.1.2 | 07:8.1 | 07:8.1.2 | 1 | 3 | 0.02 | Al 240 | 0.125 | 0.084821 | 420 | 0.0025 | 0.0016964 | 8.4 | 5.2752e-08 | 0.34 |  |  | TRUE |  |  |  | 589.4801 | 5874.2503 |  | 26 | 013-07:1 | Al 95 | 100 | 206 | 20.6 | 93 | 9.3 | 0.35 | 0.035 | 300 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1-07:8.1.3 | 07:8.1 | 07:8.1.3 | 1 | 4 | 0.025 | Al 240 | 0.125 | 0.084821 | 420 | 0.003125 | 0.0021205 | 10.5 | 6.594e-08 | 0.34 |  |  | TRUE |  |  |  | 471.5841 | 5874.2503 |  | 2&3 | 07:8.1-07:8 | Al 240 | 25 | 64 | 1.6 | 44 | 1.1 | 0.2 | 0.005 | 770 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1-07:3/4 | 07:8.1 | 07:3/4 | 1 | 19 | 0.275 | Al 240 | 0.125 | 0.084821 | 420 | 0.034375 | 0.023326 | 115.5 | 7.2534e-07 | 0.34 |  |  | TRUE |  |  |  | 42.8713 | 5874.2503 |  | 6 | 07:8.1-07:8.1.1 | Al 240 | 15 | 126.6667 | 1.9 | 86.6667 | 1.3 | 0.4 | 0.006 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1.1-07:8.1.1.1 | 07:8.1.1 | 07:8.1.1.1 | 2 | 5 | 0.025 | Al 240 | 0.125 | 0.084821 | 420 | 0.003125 | 0.0021205 | 10.5 | 6.594e-08 | 0.34 |  |  | TRUE |  |  |  | 471.5841 | 5874.2503 |  | 7 | 07:8.1-07:8.1.2 | Al 240 | 20 | 125 | 2.5 | 85 | 1.7 | 0.4 | 0.008 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1.2-07:28 | 07:8.1.2 | 07:28 | 3 | 8 | 0.08 | Al 240 | 0.125 | 0.084821 | 420 | 0.01 | 0.0067856 | 33.6 | 2.1101e-07 | 0.34 |  |  | TRUE |  |  |  | 147.37 | 5874.2503 |  | 8 | 07:8.1-07:8.1.3 | Al 240 | 25 | 124 | 3.1 | 84 | 2.1 | 0.4 | 0.01 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1.2-07:11B | 07:8.1.2 | 07:11B | 3 | 12 | 0.33 | Al 240 | 0.125 | 0.084821 | 420 | 0.04125 | 0.027991 | 138.6 | 8.7041e-07 | 0.34 |  |  | TRUE |  |  |  | 35.7261 | 5874.2503 |  | 4&5 | 07:8-07:29E | Al 240 | 420 | 125 | 52.5 | 84.7619 | 35.6 | 0.4 | 0.168 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1.2-07:6 | 07:8.1.2 | 07:6 | 3 | 18 | 0.11 | Al 240 | 0.125 | 0.084821 | 420 | 0.01375 | 0.0093303 | 46.2 | 2.9014e-07 | 0.34 |  |  | TRUE |  |  |  | 107.1782 | 5874.2503 |  | 10 | 07:8.1.1-07:8.1.1.1 | Al 240 | 25 | 124 | 3.1 | 84 | 2.1 | 0.4 | 0.01 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1.3-07:19 | 07:8.1.3 | 07:19 | 4 | 6 | 0.225 | Al 240 | 0.125 | 0.084821 | 420 | 0.028125 | 0.019085 | 94.5 | 5.9346e-07 | 0.34 |  |  | TRUE |  |  |  | 52.3982 | 5874.2503 |  | 12 | 07:8.1.2-07:11B | Al 240 | 330 | 125.1515 | 41.3 | 84.8485 | 28 | 0.4 | 0.132 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:8.1.3-07:35 | 07:8.1.3 | 07:35 | 4 | 13 | 0.4 | Al 240 | 0.125 | 0.084821 | 420 | 0.05 | 0.033928 | 168 | 1.055e-06 | 0.34 |  |  | TRUE |  |  |  | 29.474 | 5874.2503 |  | 11 | 07:8.1.2-07:28 | Al 240 | 80 | 125 | 10 | 85 | 6.8 | 0.4 | 0.032 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:19-07:23 | 07:19 | 07:23 | 6 | 7 | 0.3 | Al 240 | 0.125 | 0.084821 | 420 | 0.0375 | 0.025446 | 126 | 7.9128e-07 | 0.34 |  |  | TRUE |  |  |  | 39.2987 | 5874.2503 |  | 14 | 07:8.1.3-07:19 | Al 240 | 225 | 124.8889 | 28.1 | 84.8889 | 19.1 | 0.4 | 0.09 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:23-07:27 | 07:23 | 07:27 | 7 | 10 | 0.165 | Al 240 | 0.125 | 0.084821 | 420 | 0.020625 | 0.013995 | 69.3 | 4.352e-07 | 0.34 |  |  | TRUE |  |  |  | 71.4521 | 5874.2503 |  | 15 | 07:8.1.3-07:35 | Al 240 | 400 | 125 | 50 | 84.75 | 33.9 | 0.4 | 0.16 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:27-07:41 | 07:27 | 07:41 | 10 | 11 | 0.29 | Al 240 | 0.125 | 0.084821 | 420 | 0.03625 | 0.024598 | 121.8 | 7.649e-07 | 0.34 |  |  | FALSE |  |  |  | 40.6538 | 5874.2503 |  | 16 | 07:19-07:23 | Al 240 | 300 | 125 | 37.5 | 84.6667 | 25.4 | 0.4 | 0.12 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:41-07:35 | 07:41 | 07:35 | 11 | 13 | 0.35 | Al 240 | 0.125 | 0.084821 | 420 | 0.04375 | 0.029687 | 147 | 9.2316e-07 | 0.34 |  |  | TRUE |  |  |  | 33.6846 | 5874.2503 |  | 17 | 07:23-07:27 | Al 240 | 165 | 124.8485 | 20.6 | 84.8485 | 14 | 0.4 | 0.066 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:4.1-07:3/4 | 07:4.1 | 07:3/4 | 20 | 19 | 0.07 | Al 240 | 0.125 | 0.084821 | 420 | 0.00875 | 0.0059374 | 29.4 | 1.8463e-07 | 0.34 |  |  | TRUE |  |  |  | 168.4229 | 5874.2503 |  | 19 | 07:41-07:35(SF) |  | 400 | 128.25 | 51.3 | 87 | 34.8 | 0.41 | 0.164 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:4.1-07:4.2 | 07:4.1 | 07:4.2 | 20 | 21 | 0.075 | Al 240 | 0.125 | 0.084821 | 420 | 0.009375 | 0.0063615 | 31.5 | 1.9782e-07 | 0.34 |  |  | TRUE |  |  |  | 157.1947 | 5874.2503 |  |  | 07:35(HS)-07:12 |  | 25 | 160 | 4 | 48 | 1.2 | 0.16 | 0.004 | 205 | 12 kV | 10.5/0.4 | 10.5/0.4
07:4.2-07:3/4 | 07:4.2 | 07:3/4 | 21 | 19 | 0.14 | Al 240 | 0.125 | 0.084821 | 420 | 0.0175 | 0.011875 | 58.8 | 3.6926e-07 | 0.34 |  |  | FALSE |  |  |  | 84.2114 | 5874.2503 |  |  | 07:35(HS)-07:35(SF) |  | 10 | 130 | 1.3 | 90 | 0.9 | 0.4 | 0.004 | 385 | 12 kV | 10.5/0.4 | 10.5/0.4
07:3/4-07:6 | 07:3/4 | 07:6 | 19 | 18 | 0.25 | Al 240 | 0.125 | 0.084821 | 420 | 0.03125 | 0.021205 | 105 | 6.594e-07 | 0.34 |  |  | FALSE |  |  |  | 47.1584 | 5874.2503
07:3/4-013 | 07:3/4 | 013 | 19 | 16 | 0.13 | Al 240 | 0.125 | 0.084821 | 420 | 0.01625 | 0.011027 | 54.6 | 3.4289e-07 | 0.34 |  |  | FALSE |  |  |  | 90.6893 | 5874.2503 | To do:
07:3/4-07:1 | 07:3/4 | 07:1 | 19 | 17 | 0.07 | Al 150 | 0.206 | 0.91104 | 350 | 0.01442 | 0.063772 | 24.5 | 1.5386e-07 | 0.26 |  |  | TRUE |  |  |  | 15.6808 | 4492.0738 | Link the bus names and numbers to the "Buses" sheet (similar to what is implemented in "Transformers" sheet)
013-07:1 | 013 | 07:1 | 16 | 17 | 0.1 | Al 95 | 0.32 | 0.097387 | 300 | 0.032 | 0.0097387 | 30 | 1.884e-07 | 0.205 |  |  | TRUE |  |  |  | 102.6836 | 3541.8274 | Find a reference for cable properties
07:3/4-07:29E | 07:3/4 | 07:29E | 19 | 15 | 0.2 | Al 240 | 0.125 | 0.084821 | 420 | 0.025 | 0.016964 | 84 | 5.2752e-07 | 0.34 |  |  | FALSE |  |  |  | 58.948 | 5874.2503
07:28-07:35 | 07:28 | 07:35 | 8 | 13 | 0.35 | Al 240 | 0.125 | 0.084821 | 420 | 0.04375 | 0.029687 | 147 | 9.2316e-07 | 0.34 |  |  | FALSE |  |  |  | 33.6846 | 5874.2503
07:8.1.3-07:28D5 | 07:8.1.3 | 07:28D5 | 4 | 9 | 0.23 | Al 95 | 0.32 | 0.097387 | 300 | 0.0736 | 0.022399 | 69 | 4.3332e-07 | 0.205 |  |  | TRUE |  |  |  | 44.6451 | 3541.8274
07:35-07:11B | 07:35 | 07:11B | 13 | 12 | 0.1 | Al 240 | 0.125 | 0.084821 | 420 | 0.0125 | 0.0084821 | 42 | 2.6376e-07 | 0.34 |  |  | FALSE |  |  |  | 117.896 | 5874.2503
07:35-07:12 | 07:35 | 07:12 | 13 | 14 | 0.01 | Al 150 | 0.206 | 0.91104 | 350 | 0.00206 | 0.0091104 | 3.5 | 1.5386e-07 | 0.26 |  |  | TRUE |  |  |  | 109.7653 | 4492.0738
07:8-ExtGrid | ExtGrid | 07:8 | 63 | 0 | 0.05 | Al 240 | 0.125 | 0.084821 | 420 | 0.00375 | 0.004241 | 21 | 6.594e-08 | 0.34 |  |  | TRUE |  |  |  | 235.7921 | 5874.2503
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: What is the old line list? Where did this column come from? Why do we need it? Can we delete it? Reply: I have built this column based on the list of the buses in "Buses" sheet. The lines are coming from the AH one line diagram map ( both "HSP schema för Chalmers grid _ SLD.pdf" and "MV el diagram with PV.pdf" which are updated 2011 and 2014). I have tried to choose an intuitive name for the lines and include ALL the lines that were in the AH diagram. Reply: The old list is the list we had in sheet "Lines and Transformers"
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to names in sheet "Buses"
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to numbers in sheet "Buses"
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to numbers in sheet "Buses"
Note on E1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to numbers in sheet "Buses".
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: "Box\Common project folder\Chalmers Campus Test Bed\Original Maps and Material from AH\HSP schema för Chalmers grid _ SLD.pdf"
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: "Box\Common project folder\Chalmers Campus Test Bed\Original Maps and Material from AH\HSP schema för Chalmers grid _ SLD.pdf"
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2*pi*f*L
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old line list Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Reply: Yes but not the list we had before (in "Lines and Transformers" sheet).
Note on AD5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the type is Al240 at 07:3/4, Al150 in the middle, and Al185 at 07:1
Note on AE5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The length shoul be 70m according to AH one line digaram
Note on AD7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the type is Al185 at 07:1, Al95 in the middle, and Al150 at 013
Note on AE7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: source for the length
Note on A18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old line list Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Reply: Yes included in the diagram but not in the old list we had. The old list --> the list in "Lines and Transformers" sheet.
Note on F19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was missing in the map. Apprximately added a length
Note on A20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old line list
Note on AE20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: source?
Note on A21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: If we are to include this line in the power flow calculation, notice that in AH's electrical diagram of October 2008, there is no bus named 07:4.2. There is a bus named 07:4 and its connection to bu 07:.4.1 is not through just one line (there is a bus in between, not named in the diagram) Reply: The bus is actually on the diagram at the upper-left corner. The map I am talking about is this one: "Box\Common project folder\Chalmers Campus Test Bed\Original Maps and Material from AH\HSP schema för Chalmers grid _ SLD.pdf"
Note on A22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: If we consider that bus 26 is bus 07:4, this line is included in the electrical diagram (updated in October 2008) provided by AH. Reply: Yes included in the diagram but not in the old list we had. The old list --> the list in "Lines and Transformers" sheet.
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Reply: Yes included in the diagram but not in the old list we had. The old list --> the list in "Lines and Transformers" sheet.
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Reply: Yes included in the diagram but not in the old list we had. The old list --> the list in "Lines and Transformers" sheet.
Note on F25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the lenght do not match with the old list of lines
Note on G25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the type is Al240 at 07:3/4, Al150 in the middle, and Al185 at 07:1 Reply: The thinest cable is chosen
Note on F26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was missing in the map. Apprximately added a length
Note on G26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the type is Al185 at 07:1, Al95 in the middle, and Al150 at 013 Reply: The thinest cable is chosen
Note on A27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Reply: Yes included in the diagram but not in the old list we had. The old list --> the list in "Lines and Transformers" sheet.
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Reply: Yes included in the diagram but not in the old list we had. The old list --> the list in "Lines and Transformers" sheet.
Note on A29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Where did you see the name 07:28D5? Any reference? In FED and m2M-GRID projects, transformer T28.5 (connected at "bus" 07:28D5) was not considered as it only supplies a small area of that building. Reply: 07:28D5 is the HV bus right at T28.5. The name is a mix of the building and the fact that it is in del 5 of 07:28. Reply: Are you sure the load is small? I have in my notes that HP VKA1 is connected to T28.5...
Note on A30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not in the old list for lines Reply: The electrical diagram provided by AH (updated in Oct. 2008) contains this line. Reply: Yes included in the diagram but not in the old list we had. The old list --> the list in "Lines and Transformers" sheet.
Note on F30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was missing in the map. Apprximately added a length
Note on A32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Imaginary line connecting campus to external grid

## Transformers
name | from_busname | to_busname | from_busnumber | to_busnumber | stat | type | r | x | b | ShortTermRating_kVA | ContinousRating_kVA | angLB | angUB | PhaseShift | TapRatio | TapLB | TapUB | contingency | probability | in_service | Meter ID, etc
T04.1 | 07:4.1 | 07:4.1_T04.1_LV | 20 | 58 |  |  |  | 4 |  |  | 800 | [8 empty] | TRUE
T04.2 | 07:4.1 | 07:4.1_T04.2_LV | 20 | 59 |  |  |  | 4 |  |  | 800 | [8 empty] | TRUE |  | The "old" list of trafos (from sheet "Lines and Transformers")
T04.3 | 07:4.1 | 07:4.1_T04.3_LV | 20 | 60 |  |  |  | 4 |  |  | 800 | [8 empty] | TRUE |  | corresponding row in the new table (excel's row) | Connected to Bus | Transfor-mer Id | X(%) | Rating(kVA)
T04.4 | 07:4.2 | 07:4.2_T04.4_LV | 21 | 61 |  |  |  | 4 |  |  | 800 | [8 empty] | FALSE |  | 7 | 07:3/4 | T04.6 | 5.8 | 1000
T04.5 | 07:4.2 | 07:4.2_T04.5_LV | 21 | 62 |  |  |  | 4 |  |  | 800 | [8 empty] | TRUE |  | 8 | 7:06 | T06.1 | 5.8 | 800
T04.6 | 07:3/4 | 07:3/4_T04.6_LV | 19 | 57 |  |  |  | 5.8 |  |  | 1000 | [8 empty] | TRUE |  | 13 | O13 | T13.1 | 4.82 | 800
T06.1 | 07:6 | 07:6_T06.1_LV | 18 | 55 |  |  |  | 5.8 |  |  | 800 | [8 empty] | TRUE |  | 18 | 07:29E | T5 | 5 | 1250
T06.2 | 07:6 | 07:6_T06.2_LV | 18 | 56 |  |  |  | 4 |  |  | 800 | [8 empty] | FALSE |  | 16 | 07:29E | T3 | 5 | 1250
T01.1 | 07:1 | 07:1_T01.1_LV | 17 | 52 |  |  |  | 5.7 |  |  | 800 | [8 empty] | TRUE |  | 14 | 07:29E | T1 | 4.9 | 1250
T01.2 | 07:1 | 07:1_T01.2_LV | 17 | 53 |  |  |  | 6.3 |  |  | 1000 | [8 empty] | TRUE |  | 21 | 07:8.1.1.1 | T08.1 | 6.31 | 800
T01.3 | 07:1 | 07:1_T01.3_LV | 17 | 54 |  |  |  | 4 |  |  | 80 | [8 empty] | TRUE |  | 22 | 07:8.1.1.1 | T08.3 | 5 | 800
T13.1 | 013 | 013_T13.1_LV | 16 | 51 |  |  |  | 4.82 |  |  | 800 | [8 empty] | TRUE |  | 10 | 7:01 | T01.1 | 5.7 | 800
T1 | 07:29E | 07:29E_T1_LV | 15 | 44 |  |  |  | 4.9 |  |  | 1250 | [8 empty] | TRUE |  | 11 | 7:01 | T01.2 | 6.3 | 1000
T2 | 07:29E | 07:29E_T2_LV | 15 | 45 |  |  |  | 4 |  |  | 1250 | [8 empty] | FALSE |  | 25 | 7:19 | T19.1 | 4.27 | 400
T3 | 07:29E | 07:29E_T3_LV | 15 | 46 |  |  |  | 5 |  |  | 1250 | [8 empty] | TRUE |  | 37 | 7:23 | T23.1 | 4.8 | 800
T4 | 07:29E | 07:29E_T4_LV | 15 | 47 |  |  |  | 4 |  |  | 1250 | [8 empty] | FALSE |  | 40 | 7:27 | T27.2 | 4.9 | 800
T5 | 07:29E | 07:29E_T5_LV | 15 | 48 |  |  |  | 5 |  |  | 1250 | [8 empty] | TRUE |  | 41 | 7:41 | T40.1 | 5.8 | 800
T6 | 07:29E | 07:29E_T6_LV | 15 | 49 |  |  |  | 4 |  |  | 1250 | [8 empty] | FALSE |  | 36 | 07:11B | T11.2 | 4.5 | 1250
T7 | 07:29E | 07:29E_T7_LV | 15 | 50 |  |  |  | 4 |  |  | 1250 | [8 empty] | FALSE |  | 28 | 7:28 | T28.1 | 6.3 | 800
T08.1 | 07:8.1.1.1 | 07:8.1.1.1_T08.1_LV | 5 | 25 |  |  |  | 6.31 |  |  | 800 | [8 empty] | TRUE |  | 30 | 7:28 | T28.3 | 6.3 | 800
T08.3 | 07:8.1.1.1 | 07:8.1.1.1_T08.3_LV | 5 | 24 |  |  |  | 5 |  |  | 800 | [8 empty] | TRUE |  | 33 | 07:35(SF) | T35.1 | 5.2 | 800
T08.4 | 07:8 | 07:8_T08.4_LV | 0 | 22 |  |  |  | 4 |  |  | 800 | [8 empty] | TRUE |  | 34 | 07:35(SF) | T35.2 | 4.9 | 600
T08.5 | 07:8.1.3 | 07:8.1.3_T08.5_LV | 4 | 26 |  |  |  | 4 |  |  | 1250 | [8 empty] | TRUE |  | 31 | 7:12 | T12.1 | 5.2 | 1250
T19.1 | 07:19 | 07:19_T19.1_LV | 6 | 27 |  |  |  | 4.27 |  |  | 400 | [8 empty] | TRUE |  | 32 | 7:12 | T12.2 | 5.2 | 1250
T19.2 | 07:19 | 07:19_T19.2_LV | 6 | 28 |  |  |  | 4 |  |  | 400 | [8 empty] | FALSE
T28.5 | 07:28D5 | 07:28D5_T28.5_LV | 9 | 23 |  |  |  | 4 |  |  | 1600 | [8 empty] | TRUE
T28.1 | 07:28 | 07:28_T28.1_LV | 8 | 37 |  |  |  | 6.3 |  |  | 800 | [8 empty] | TRUE |  |  | Check which ones were not in the "old" list
T28.2 | 07:28 | 07:28_T28.2_LV | 8 | 38 |  |  |  | 4 |  |  | 800 | [8 empty] | FALSE |  |  | Add the meters' Ids
T28.3 | 07:28 | 07:28_T28.3_LV | 8 | 39 |  |  |  | 6.3 |  |  | 800 | [8 empty] | TRUE |  |  | Add the historical data Ids, etc
T12.1 | 07:12 | 07:12_T12.1_LV | 14 | 42 |  |  |  | 5.2 |  |  | 1250 | [8 empty] | TRUE
T12.2 | 07:12 | 07:12_T12.2_LV | 14 | 43 |  |  |  | 5.2 |  |  | 1250 | [8 empty] | TRUE
T35.1 | 07:35 | 07:35_T35.1_LV | 13 | 40 |  |  |  | 5.2 |  |  | 800 | [8 empty] | TRUE
T35.2 | 07:35 | 07:35_T35.2_LV | 13 | 41 |  |  |  | 4.9 |  |  | 600 | [8 empty] | TRUE
T11.1 | 07:11B | 07:11B_T11.1_LV | 12 | 35 |  |  |  | 4 |  |  | 1250 | [8 empty] | FALSE
T11.2 | 07:11B | 07:11B_T11.2_LV | 12 | 36 |  |  |  | 4.5 |  |  | 1250 | [8 empty] | TRUE
T23.1 | 07:23 | 07:23_T23.1_LV | 7 | 30 |  |  |  | 4.8 |  |  | 800 | [8 empty] | TRUE
T23.2 | 07:23 | 07:23_T23.2_LV | 7 | 29 |  |  |  | 4 |  |  | 800 | [8 empty] | TRUE
T27.1 | 07:27 | 07:27_T27.1_LV | 10 | 31 |  |  |  | 4 |  |  | 800 | [8 empty] | FALSE
T27.2 | 07:27 | 07:27_T27.2_LV | 10 | 32 |  |  |  | 4.9 |  |  | 800 | [8 empty] | TRUE
T40.1 | 07:41 | 07:41_T40.1_LV | 11 | 33 |  |  |  | 5.8 |  |  | 800 | [8 empty] | TRUE
T40.2 | 07:41 | 07:41_T40.2_LV | 11 | 34 |  |  |  | 4 |  |  | 800 | [8 empty] | FALSE
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 9 trafos that are in_service were missing in the "old" list
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: linked to "Buses" sheet. Change the names there if you wish
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: linked to "Buses" sheet. Change the names there if you wish
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: linked to "Buses" sheet. Change the names there if you wish
Note on E1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: linked to "Buses" sheet. Change the names there if you wish
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list
Note on I2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4 values in red are taken from the standard type from Panda Power library because the value was missing in our data
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list
Note on A12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Trafo is in "Chalmers OLD network diagram with numbered buses.pdf" but not in "MV el diagram with PV.pdf"! Reply: was not in the "old" list
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list
Note on L23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was missing. Just replaced with 800...
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list
Note on A27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list
Note on A38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: was not in the "old" list

## Demand
name | busname | busnumber | in_service | Filename_historic_data | ID_realtime_API | Division factor | Load_basecase | d_f
D_T04.1 | 07:4.1_T04.1_LV | 58 | TRUE | Kemi | O3060132_EL_SUM_CONS_PV | 5 | 897.1 | 5
D_T04.2 | 07:4.1_T04.2_LV | 59 | TRUE | Kemi | O3060132_EL_SUM_CONS_PV | 5 | 897.1 | 5
D_T04.3 | 07:4.1_T04.3_LV | 60 | TRUE | Kemi | O3060132_EL_SUM_CONS_PV | 5 | 897.1 | 5
D_T04.4 | 07:4.2_T04.4_LV | 61 | FALSE
D_T04.5 | 07:4.2_T04.5_LV | 62 | TRUE | Kemi | O3060132_EL_SUM_CONS_PV | 5 | 897.1 | 5
D_T04.6 | 07:3/4_T04.6_LV | 57 | TRUE | \Chalmers test site\Historical data\Mätdata\Mätdata\Kemi | O3060132_EL_SUM_CONS_PV | 5 | 897.1 | 5
D_T06.1_Nyamatte | 07:6_T06.1_LV | 55 | TRUE | 14506 | O0007006_EL_SUM_CONS_PV | 1 | 74.7 | 1
D_T06.1_Bibliotek | 07:6_T06.1_LV | 56 | TRUE | 9613 | O0007017_EL_SUM_CONS_PV | 1 | 53.2 | 1
D_T06.2 | 07:6_T06.2_LV | 56 | FALSE
D_T01.1 | 07:1_T01.1_LV | 52 | TRUE | 14505 | O0007001_EL_SUM_CONS_PV | 2 | 107.1 | 3
D_T01.2 | 07:1_T01.2_LV | 53 | TRUE | 14505 | O0007001_EL_SUM_CONS_PV | 2 | 107.1 | 3
D_T01.3 | 07:1_T01.3_LV | 54 | TRUE |  |  |  | 107.1 | 3
D_T13.1 | 013_T13.1_LV | 51 | TRUE | 14503 | O0011001_EL_SUM_CONS_PV | 1 | 22.2 | 1
D_T1 | 07:29E_T1_LV | 44 | TRUE | none | O3060133_EL_SUM_CONS_PV | 3 | 912 | 3
D_T2 | 07:29E_T2_LV | 45 | FALSE
D_T3 | 07:29E_T3_LV | 46 | TRUE | none | O3060133_EL_SUM_CONS_PV | 3 | 912 | 3
D_T4 | 07:29E_T4_LV | 47 | FALSE
D_T5 | 07:29E_T5_LV | 48 | TRUE | none | O3060133_EL_SUM_CONS_PV | 3 | 912 | 3
D_T6 | 07:29E_T6_LV | 49 | FALSE
D_T7 | 07:29E_T7_LV | 50 | FALSE
D_T08.1_KC | 07:8.1.1.1_T08.1_LV | 25 | TRUE | 9513 | O0007008_EL_SUM_CONS_PV | 2 | 736.6 | 4
D_T08.3_KC | 07:8.1.1.1_T08.3_LV | 24 | TRUE | 9513 | O0007008_EL_SUM_CONS_PV | 2 | 736.6 | 4
D_T08.1_Kontor | 07:8.1.1.1_T08.1_LV | 25 | TRUE | 9821 | O0007888_EL_001_PV2 | 2
D_T08.3_Kontor | 07:8.1.1.1_T08.3_LV | 24 | TRUE | 9821 | O0007888_EL_001_PV2 | 2
D_T08.4 | 07:8_T08.4_LV | 22 | TRUE |  |  |  | 736.6 | 4
D_T08.5 | 07:8.1.3_T08.5_LV | 26 | TRUE |  |  |  | 736.6 | 4
D_T19.1 | 07:19_T19.1_LV | 27 | TRUE | 9653 | O0007019_EL_SUM_CONS_PV | 1 | 22.7 | 2
D_T19.2 | 07:19_T19.2_LV | 28 | FALSE |  |  |  | 22.7 | 2
D_T28.5 | 07:28D5_T28.5_LV | 23 | TRUE |  |  |  | 349.7 | 3
D_T28.1_Maskin | 07:28_T28.1_LV | 37 | TRUE | 9686 | O0007028_EL_SUM_CONS_PV | 2 | 349.7 | 3
D_T28.1_HB | 07:28_T28.1_LV | 37 | TRUE | 9657 | O0007022_EL_SUM_CONS_PV | 2
D_T28.1_HA | 07:28_T28.1_LV | 37 | TRUE | 9656 | O0007025_EL_SUM_CONS_PV | 2
D_T28.2 | 07:28_T28.2_LV | 38 | FALSE
D_T28.3_Maskin | 07:28_T28.3_LV | 39 | TRUE | 9686 | O0007028_EL_SUM_CONS_PV | 2 | 349.7 | 3
D_T28.3_HB | 07:28_T28.3_LV | 39 | TRUE | 9657 | O0007022_EL_SUM_CONS_PV | 2
D_T28.3_HA | 07:28_T28.3_LV | 39 | TRUE | 9656 | O0007025_EL_SUM_CONS_PV | 2
D_T12.1_ELKTek | 07:12_T12.1_LV | 42 | TRUE | 9651 | O0007012_EL_SUM_CONS_PV | 2 | 73.8 | 2
D_T12.1_HC | 07:12_T12.1_LV | 42 | TRUE | 9655 | O0007021_EL_SUM_CONS_PV | 2
D_T12.1_GibHerr | 07:12_T12.1_LV | 42 | TRUE | 9515 | O0007014_EL_SUM_CONS_PV | 2
D_T12.2_ELKTek | 07:12_T12.2_LV | 43 | TRUE | 9651 | O0007012_EL_SUM_CONS_PV | 2 | 73.8 | 2
D_T12.2_HC | 07:12_T12.2_LV | 43 | TRUE | 9655 | O0007021_EL_SUM_CONS_PV | 2
D_T12.2_GibHerr | 07:12_T12.2_LV | 43 | TRUE | 9515 | O0007014_EL_SUM_CONS_PV | 2
D_T35.1 | 07:35_T35.1_LV | 40 | TRUE |  |  |  | 0 | 1
D_T35.2 | 07:35_T35.2_LV | 41 | TRUE |  |  |  | 0 | 1
D_T11.1 | 07:11B_T11.1_LV | 35 | FALSE |  |  |  | 0 | 1
D_T11.2_Idelara | 07:11B_T11.2_LV | 36 | TRUE | 9652 | O0007018_EL_SUM_CONS_PV | 1 | 23.7 | 1
D_T11.2_Edit | 07:11B_T11.2_LV | 36 | TRUE | 14497 | O0007024_EL_SUM_CONS_PV | 1
D_T23.1 | 07:23_T23.1_LV | 30 | TRUE | 9614 | O0007023_EL_SUM_CONS_PV | 1 | 25.8 | 1
D_T23.2 | 07:23_T23.2_LV | 29 | TRUE | 9658 | O0007026_EL_SUM_CONS_PV | 1 | 78.3 | 1
D_T27.1 | 07:27_T27.1_LV | 31 | FALSE |  |  |  | 0 | 1
D_T27.2_SB3 | 07:27_T27.2_LV | 32 | TRUE | 9659 | O0007027_EL_SUM_CONS_PV | 1 | 178.9 | 1
D_T27.2_Phus | 07:27_T27.2_LV | 32 | TRUE | 15755 | O0007043_EL_SUM_CONS_PV | 1 | 37.7 | 1
D_T27.2_AWL | 07:27_T27.2_LV | 32 | TRUE | 16991 | O0007044_EL_SUM_CONS_PV | 1 | 78.4 | 1
D_T40.1 | 07:41_T40.1_LV | 33 | TRUE | 9687 | O0007040_EL_SUM_CONS_PV | 1 | 89.2 | 1
D_T40.2 | 07:41_T40.2_LV | 34 | FALSE |  |  |  | 0 | 1
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: some meters measure the aggregated demand for a few transformers together. As a preliminary workaround, we can divide the load equaly between the transformers with this division factor. Reply: the source for what meters measure is sheet "Loads, DERs, IEDs, per bus"

## PV(staticGen)
name | busname | busnumber | in_service | orientation | Inverter_capacity (kW) | Filename_historic_data | ID_realtime_API | Division factor
PV_T04.1 | 07:4.1_T04.1_LV | 58 | TRUE
PV_T04.2 | 07:4.1_T04.2_LV | 59 | TRUE
PV_T04.3 | 07:4.1_T04.3_LV | 60 | TRUE
PV_T04.4 | 07:4.2_T04.4_LV | 61 | FALSE
PV_T04.5 | 07:4.2_T04.5_LV | 62 | TRUE
PV_T04.6 | 07:3/4_T04.6_LV | 57 | TRUE
PV_T06.1 | 07:6_T06.1_LV | 55 | TRUE |  |  | 16872 | O0007017_EL_SUM_PROD_PV | 1
PV_T06.2 | 07:6_T06.2_LV | 56 | FALSE
PV_T01.1 | 07:1_T01.1_LV | 52 | TRUE
PV_T01.2 | 07:1_T01.2_LV | 53 | TRUE
PV_T01.3 | 07:1_T01.3_LV | 54 | TRUE
PV_T13.1 | 013_T13.1_LV | 51 | TRUE
PV_T1 | 07:29E_T1_LV | 44 | TRUE
PV_T2 | 07:29E_T2_LV | 45 | FALSE
PV_T3 | 07:29E_T3_LV | 46 | TRUE
PV_T4 | 07:29E_T4_LV | 47 | FALSE
PV_T5 | 07:29E_T5_LV | 48 | TRUE
PV_T6 | 07:29E_T6_LV | 49 | FALSE
PV_T7 | 07:29E_T7_LV | 50 | FALSE
PV_T08.1 | 07:8.1.1.1_T08.1_LV | 25 | TRUE |  |  | 16943 | O0007008_EL_SUM_PROD_PV | 2
PV_T08.3 | 07:8.1.1.1_T08.3_LV | 24 | TRUE |  |  | 16943 | O0007008_EL_SUM_PROD_PV | 2
PV_T08.4 | 07:8_T08.4_LV | 22 | TRUE
PV_T08.5 | 07:8.1.3_T08.5_LV | 26 | TRUE
PV_T19.1 | 07:19_T19.1_LV | 27 | TRUE
PV_T19.2 | 07:19_T19.2_LV | 28 | FALSE
PV_T28.5 | 07:28D5_T28.5_LV | 23 | TRUE
PV_T28.1_Maskin | 07:28_T28.1_LV | 37 | TRUE |  |  | O7_28 external file+E22D22:K23N23F22:K23C22:K23 | O0007028_EL_SUM_PROD_PV | 2
PV_T28.2 | 07:28_T28.2_LV | 38 | FALSE
PV_T28.3_Maskin | 07:28_T28.3_LV | 39 | TRUE |  |  | O7_28 external file+E22D22:K23N23F22:K23C22:K23 | O0007028_EL_SUM_PROD_PV | 2
PV_T12.1 | 07:12_T12.1_LV | 42 | TRUE
PV_T12.2 | 07:12_T12.2_LV | 43 | TRUE
PV_T35.1 | 07:35_T35.1_LV | 40 | TRUE
PV_T35.2 | 07:35_T35.2_LV | 41 | TRUE
PV_T11.1 | 07:11B_T11.1_LV | 35 | FALSE
PV_T11.2_Edit | 07:11B_T11.2_LV | 36 | TRUE |  |  | O7_24 external file | O0007024_EL_SUM_PROD_PV | 1
PV_T23.1 | 07:23_T23.1_LV | 30 | TRUE |  |  | 16821 | O0007023_EL_SUM_PROD_PV | 1
PV_T23.2 | 07:23_T23.2_LV | 29 | TRUE |  |  | 16710 | O0007026_EL_SUM_PROD_PV | 1
PV_T27.1 | 07:27_T27.1_LV | 31 | FALSE
PV_T27.2_SB3 | 07:27_T27.2_LV | 32 | TRUE |  |  | 16871 (norra) | O0007027_EL_SUM_PROD_PV | 1
PV_T27.2_Phus | 07:27_T27.2_LV | 32 | TRUE
PV_T27.2_AWL | 07:27_T27.2_LV | 32 | TRUE |  |  | 16884 | O0007044_EL_SUM_PROD_PV | 1
PV_T40.1 | 07:41_T40.1_LV | 33 | TRUE
PV_T40.2 | 07:41_T40.2_LV | 34 | FALSE
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: some meters measure the aggregated value for a few transformers together. As a preliminary workaround, we can divide the number equaly between the transformers with this division factor. Reply: the source for what meters measure is sheet "Loads, DERs, IEDs, per bus"

## DERs location
bus_name | Building_name | bus_number | in_service | DER_names | tag
07:8_T08.4_LV | Kraftcentral_RUM4026 | 22 | TRUE | CHP
07:28D5_T28.5_LV | MaskinDel5_RUM0211 | 23 | TRUE
07:8.1.1.1_T08.3_LV | Kraftcentral_RUM1019 | 24 | TRUE | PV,VKA2,VKA4
07:8.1.1.1_T08.1_LV | Kraftcentral_RUM1019 | 25 | TRUE
07:8.1.3_T08.5_LV | Kraftcentral_RUM4023 | 26 | TRUE
07:19_T19.1_LV | Administration_RUM1031 | 27 | TRUE
07:19_T19.2_LV | Administration_RUM1031 | 28 | FALSE
07:23_T23.2_LV | VoVI_RUM0120 | 29 | TRUE | PV
07:23_T23.1_LV | VoVI_RUM0120 | 30 | TRUE | PV
07:27_T27.1_LV | VoVII_RUM0053 | 31 | FALSE
07:27_T27.2_LV | VoVII_RUM0053 | 32 | TRUE | PV,BES_SB
07:41_T40.1_LV | MatematisktCentrum_RUMxx | 33 | TRUE
07:41_T40.2_LV | MatematisktCentrum_RUMxx | 34 | FALSE
07:11B_T11.1_LV | ElektroData_RUMxx | 35 | FALSE
07:11B_T11.2_LV | ElektroData_RUMxx | 36 | TRUE | PV
07:28_T28.1_LV | Maskin_RUM0303 | 37 | TRUE | PV,BES_M,VKA1
07:28_T28.2_LV | Maskin_RUM0303 | 38 | FALSE
07:28_T28.3_LV | Maskin_RUM0303 | 39 | TRUE | Ref_HP?
07:35_T35.1_LV | Elektro | 40 | TRUE
07:35_T35.2_LV | Elektro | 41 | TRUE
07:12_T12.1_LV | Elkraft | 42 | TRUE
07:12_T12.2_LV | Elkraft | 43 | TRUE
07:29E_T1_LV | MikroElektronik_RUMA104 | 44 | TRUE
07:29E_T2_LV | MikroElektronik_RUMA104 | 45 | FALSE
07:29E_T3_LV | MikroElektronik_RUMA104 | 46 | TRUE
07:29E_T4_LV | MikroElektronik_RUMA104 | 47 | FALSE
07:29E_T5_LV | MikroElektronik_RUMA109 | 48 | TRUE
07:29E_T6_LV | MikroElektronik_RUMA109 | 49 | FALSE
07:29E_T7_LV | MikroElektronik_RUMA109 | 50 | FALSE
013_T13.1_LV | Keram_RUM014 | 51 | TRUE | PV
07:1_T01.1_LV | Fysik_RUM3118 | 52 | TRUE
07:1_T01.2_LV | Fysik_RUM3118 | 53 | TRUE
07:1_T01.3_LV | Fysik_RUM3118 | 54 | TRUE
07:6_T06.1_LV | MV_RUM1110 | 55 | TRUE | PV
07:6_T06.2_LV | MV_RUM1110 | 56 | FALSE
07:3/4_T04.6_LV | 07:3/4_RUM11002 | 57 | TRUE
07:4.1_T04.1_LV | Kemi_RUM2105 | 58 | TRUE | CF_PV?
07:4.1_T04.2_LV | Kemi_RUM2105 | 59 | TRUE | CF_PV?
07:4.1_T04.3_LV | Kemi_RUM2105 | 60 | TRUE | CF_PV?
07:4.2_T04.4_LV | Kemi_RUM0008 | 61 | FALSE
07:4.2_T04.5_LV | Kemi_RUM0008 | 62 | TRUE
Note on E1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: \Box\Common project folder\Chalmers Campus Test Bed\Original Maps and Material from AH\Location of HPs and maskin batteries_2022-04.pdf Reply: If more than 1 tech, separate ONLY with a comma
Note on E19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is the refrigeration HP here?
Note on E38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Chalmers Fastigheter's PV. not data. Location is also unclear
Note on E39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Chalmers Fastigheter's PV. not data. Location is also unclear
Note on E40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Chalmers Fastigheter's PV. not data. Location is also unclear

## 2016_2017 buildings demand
| O7:4 | O7:43 | O7:17 | O7:06 | O7:08 | O7:0888 | O7:41 | O7:14 | O7:22 | O7:25 | O7:12 | O7:21 | O7:28 | O7:01 | O7:35 | O13 | O11 | O7:35 | O7:19 | O7:23 | O7:23 | O7:27 | O7:24
Datum(Starting from 01-01-2016) | Kemi | Phus | Bibliotek | NyaMatte | Kraftcentral | Lokalkontor | GamlaMatte | Gibraltar_herrgard | HA | HB | Elkraftteknik | HC | Maskinteknik | Fysik_Origo | Edit | Keramforskning | Fysik_Soliden | Idelara | Karhuset | VOV1 | Arkitektur | VOV2 | Edit
1 | 712.6488 | 1.7397 | 41.9136 | 107.126 | 32.8205 | 7.8213 | 61.3575 | 5.939 | 6.3131 | 36.3116 | 62.2532 | 6.6617 | 154.4778 | 100.2284 | 227.6256 | 8.557 | 71.6359 | 11.534 | 109 | 13.2868 | 60.1194 | 228.1276 | 0
2 | 720.4993 | 1.698 | 41.8274 | 106.5612 | 34.2681 | 6.4461 | 53.5223 | 5.8956 | 6.0527 | 34.0515 | 63.2053 | 6.6367 | 157.1945 | 100.2949 | 217.3339 | 8.5313 | 71.2092 | 11.4707 | 114 | 13.597 | 60.088 | 221.195 | 0
3 | 711.383 | 1.6226 | 41.8741 | 106.079 | 34.2966 | 6.419 | 47.3833 | 6.0862 | 5.7992 | 37.0277 | 63.013 | 7.0255 | 157.9507 | 94.2315 | 204.243 | 8.5065 | 71.2579 | 11.8171 | 133 | 12.9544 | 60.0817 | 217.6975 | 0
4 | 710.039 | 1.7168 | 41.8475 | 104.5542 | 34.8338 | 5.9086 | 50.4639 | 6.0356 | 5.7457 | 45.6408 | 63.0249 | 6.7845 | 157.0178 | 92.1795 | 195.6698 | 8.5679 | 71.2233 | 11.7235 | 104 | 11.7189 | 59.8762 | 220.1355 | 0
5 | 712.7814 | 2.0403 | 42.6403 | 103.6079 | 34.3301 | 6.3872 | 59.7392 | 5.8618 | 5.5739 | 49.8355 | 63.3202 | 6.6331 | 156.1585 | 101.8643 | 196.852 | 8.5468 | 72.0023 | 11.5135 | 100 | 11.1049 | 58.4285 | 234.2751 | 0
6 | 710.0172 | 3.0178 | 42.9651 | 103.812 | 34.781 | 5.9588 | 52.7958 | 5.749 | 5.6887 | 61.6652 | 63.5363 | 7.1584 | 154.7528 | 106.164 | 197.0587 | 8.5416 | 76.7992 | 11.4579 | 119 | 11.3842 | 57.563 | 248.0843 | 0
7 | 721.6987 | 3.3892 | 42.936 | 101.5726 | 35.0135 | 5.738 | 50.8464 | 5.7148 | 6.7651 | 81.2342 | 71.1504 | 7.2625 | 156.5533 | 109.1409 | 205.2765 | 8.6264 | 74.1512 | 11.4594 | 117 | 10.0726 | 59.083 | 248.6071 | 0
8 | 731.7262 | 3.2356 | 42.9999 | 100.0445 | 30.4602 | 10.0636 | 65.0438 | 5.7669 | 7.977 | 77.7108 | 88.6078 | 6.3613 | 161.3566 | 127.2076 | 239.6864 | 8.7746 | 72.0245 | 11.6554 | 117 | 10.036 | 60.7138 | 254.5604 | 0
9 | 730.9846 | 3.3128 | 42.707 | 99.4883 | 29.0674 | 11.3868 | 75.4767 | 6.1061 | 8.7157 | 73.843 | 95.643 | 4.3677 | 167.2378 | 132.1639 | 258.1986 | 8.6532 | 71.31 | 12.302 | 109 | 10.1911 | 62.3989 | 246.5001 | 0
10 | 740.3958 | 3.2317 | 41.9544 | 97.7859 | 29.0072 | 11.4439 | 67.1195 | 5.7029 | 9.9263 | 60.2272 | 93.0294 | 3.7192 | 169.9022 | 137.2844 | 259.2495 | 8.4426 | 70.0782 | 12.2869 | 99 | 9.5721 | 62.4666 | 225.7878 | 0.0068503
11 | 739.9469 | 3.0541 | 41.6507 | 97.3912 | 27.4628 | 12.9111 | 61.8321 | 5.3022 | 10.4364 | 47.5662 | 92.4509 | 3.7379 | 168.3891 | 136.7693 | 257.0956 | 8.3894 | 69.6765 | 12.1928 | 103 | 9.6531 | 61.7824 | 213.9393 | 0.012859
12 | 738.4104 | 2.039 | 41.6223 | 97.0595 | 27.8466 | 12.5465 | 65.9036 | 5.3672 | 9.8626 | 52.8447 | 93.0921 | 3.9343 | 169.6522 | 136.0262 | 253.0948 | 8.322 | 69.7255 | 12.1892 | 106 | 10.2072 | 58.7055 | 217.1511 | 0.015062
13 | 738.4627 | 2.0984 | 41.5755 | 97.688 | 28.9807 | 11.4691 | 74.8755 | 5.4328 | 8.0815 | 63.0142 | 92.3902 | 4.0531 | 171.074 | 132.3929 | 272.7528 | 8.3208 | 70.5351 | 12.1932 | 108 | 9.6102 | 57.9654 | 214.7703 | 0.024031
14 | 733.2607 | 3.1027 | 42.0642 | 97.1779 | 28.9643 | 11.4847 | 68.8324 | 5.4535 | 10.3422 | 72.0015 | 102.5424 | 4.4689 | 171.6892 | 134.4925 | 290.6613 | 8.3142 | 70.855 | 12.2155 | 106 | 11.1967 | 56.4803 | 215.4288 | 0.012521
15 | 750.0373 | 4.0197 | 42.6132 | 96.9434 | 29.7737 | 10.7158 | 63.4238 | 5.7306 | 9.7626 | 69.2621 | 110.8827 | 6.655 | 173.0094 | 139.2798 | 262.2373 | 8.2509 | 72.9778 | 12.6163 | 105 | 10.2668 | 57.477 | 213.7683 | 0.0047849
16 | 776.1903 | 3.8564 | 42.7928 | 98.638 | 29.3121 | 11.1543 | 68.646 | 5.7726 | 10.1064 | 70.4766 | 110.0611 | 7.2506 | 171.4652 | 153.4014 | 274.9659 | 8.4423 | 78.2961 | 13.467 | 104 | 12.0955 | 58.7716 | 225.7534 | 0
17 | 788.4953 | 4.5433 | 43.1027 | 100.7886 | 32.8823 | 7.7626 | 75.8589 | 5.7746 | 7.1534 | 72.2386 | 106.1512 | 7.7251 | 178.4799 | 159.735 | 277.6434 | 8.538 | 81.2528 | 14.1482 | 108 | 11.9382 | 60.7874 | 226.7203 | 0
18 | 796.2378 | 8.6879 | 43.1267 | 100.9547 | 34.8588 | 5.8849 | 67.4229 | 5.7868 | 9.0077 | 62.8133 | 109.8714 | 7.3016 | 181.5696 | 144.6933 | 241.2328 | 8.5714 | 80.155 | 14.1514 | 107 | 11.3911 | 62.3403 | 212.3249 | 0
19 | 781.6498 | 9.2602 | 42.2697 | 99.9673 | 35.0946 | 5.6609 | 59.7376 | 5.8098 | 7.0852 | 60.6453 | 89.1152 | 7.4866 | 179.2964 | 118.0285 | 211.7988 | 8.4636 | 75.6804 | 13.926 | 102 | 12.4746 | 64.1512 | 203.913 | 0
20 | 769.8475 | 5.0836 | 41.953 | 98.9467 | 34.9922 | 5.7582 | 61.1533 | 5.8223 | 5.6652 | 44.1168 | 69.9309 | 7.4514 | 174.8384 | 107.8365 | 208.2183 | 8.5502 | 72.2471 | 13.5169 | 111 | 10.1849 | 66.1917 | 203.4411 | 0
21 | 757.3031 | 3.2158 | 41.9416 | 98.6979 | 34.3366 | 6.381 | 58.3864 | 5.8727 | 5.8437 | 35.3181 | 67.2592 | 7.9746 | 165.7886 | 106.9972 | 206.4845 | 8.5344 | 71.3914 | 13.1038 | 124 | 8.954 | 63.1817 | 202.8845 | 0
22 | 737.2093 | 3.1534 | 41.6136 | 99.9726 | 34.8193 | 5.9224 | 50.2527 | 6.1264 | 5.7465 | 34.438 | 69.6438 | 9.4433 | 160.1483 | 99.1718 | 202.2026 | 8.5895 | 71.0679 | 12.4122 | 109 | 8.796 | 58.7833 | 202.4199 | 0
23 | 721.9243 | 2.8253 | 42.2849 | 101.1399 | 35.0099 | 5.7414 | 48.1989 | 6.1505 | 5.7488 | 33.7996 | 67.46 | 7.9993 | 154.7682 | 95.6048 | 211.2987 | 8.6361 | 71.5416 | 12.1416 | 110 | 9.8478 | 58.111 | 205.2672 | 0
24 | 713.4135 | 1.8435 | 43.0003 | 101.5396 | 34.2955 | 6.42 | 58.4794 | 6.0333 | 5.7155 | 33.6141 | 63.7411 | 7.2885 | 152.84 | 88.9438 | 231.091 | 8.4939 | 73.0741 | 11.7875 | 93 | 9.4444 | 56.8023 | 209.7321 | 0
25 | 712.4713 | 1.6695 | 43.5195 | 101.4314 | 34.8226 | 5.9193 | 54.7858 | 6.1449 | 5.733 | 34.4759 | 62.5007 | 8.0653 | 155.3811 | 84.6707 | 221.0973 | 8.4608 | 50.6626 | 11.5583 | 95 | 9.7958 | 59.3483 | 217.1612 | 0
26 | 714.0396 | 1.8524 | 43.9349 | 102.1945 | 34.2916 | 6.4237 | 48.5278 | 6.2831 | 5.9363 | 35.2219 | 62.5109 | 7.3627 | 158.5234 | 83.8417 | 201.5109 | 8.5703 | 51.5806 | 11.5434 | 95 | 9.1827 | 59.3384 | 218.6538 | 0
27 | 716.4627 | 1.6411 | 43.359 | 105.8317 | 34.8015 | 5.9393 | 47.5971 | 6.3736 | 5.7377 | 35.5274 | 62.6862 | 6.9296 | 158.49 | 83.4532 | 200.5495 | 8.5456 | 51.4874 | 11.5604 | 114 | 8.8897 | 57.6785 | 220.1445 | 0
28 | 710.4054 | 1.6105 | 42.3007 | 109.0737 | 34.3137 | 6.4028 | 56.5445 | 6.6503 | 5.7733 | 37.1238 | 63.1659 | 6.8281 | 157.5636 | 83.2741 | 226.0454 | 8.5363 | 51.1384 | 11.5656 | 88 | 8.8245 | 57.4189 | 218.0116 | 0
29 | 703.994 | 1.8357 | 41.7134 | 109.4392 | 34.8236 | 5.9183 | 55.274 | 6.7126 | 5.6508 | 45.62 | 63.5181 | 6.754 | 156.5929 | 83.2432 | 218.9034 | 8.4598 | 52.5644 | 11.5553 | 90 | 8.7093 | 57.1738 | 217.8223 | 0
30 | 706.3476 | 2.9766 | 51.1026 | 110.3457 | 34.9916 | 5.7587 | 49.8353 | 6.8069 | 5.5968 | 59.362 | 63.6683 | 6.7261 | 156.991 | 83.2017 | 202.4047 | 8.4564 | 55.0719 | 11.564 | 87 | 8.6321 | 58.189 | 216.5189 | 0
31 | 711.8789 | 3.4789 | 54.7181 | 112.0086 | 34.364 | 6.3549 | 47.8682 | 6.8548 | 6.2765 | 75.6392 | 64.1217 | 6.6508 | 161.0217 | 83.4934 | 224.4731 | 8.4255 | 52.6508 | 11.5387 | 90 | 8.984 | 59.4196 | 219.8238 | 0
32 | 717.7697 | 3.259 | 69.1753 | 113.2658 | 34.7834 | 5.9566 | 54.6726 | 6.8225 | 8.2475 | 75.7306 | 69.4928 | 7.9085 | 163.2843 | 88.529 | 234.3848 | 8.5108 | 50.8551 | 11.8062 | 93 | 12.706 | 61.8366 | 224.6184 | 0
33 | 727.5992 | 3.1413 | 75.0461 | 113.9075 | 34.2605 | 6.4533 | 52.8071 | 6.6949 | 6.2783 | 65.7316 | 94.9195 | 10.7848 | 165.1537 | 92.0831 | 235.3178 | 8.2582 | 50.5462 | 12.5506 | 95 | 14.3853 | 63.5258 | 227.8613 | 0
34 | 741.8252 | 3.283 | 84.0299 | 110.9364 | 34.0923 | 6.6131 | 47.8554 | 6.6247 | 8.2113 | 59.5289 | 112.5801 | 6.0796 | 167.6107 | 98.8157 | 229.7761 | 8.0032 | 51.8763 | 13.4099 | 99 | 11.1113 | 92.1061 | 218.815 | 0.012317
35 | 759.5697 | 3.638 | 86.0794 | 111.1543 | 34.8268 | 5.9153 | 47.1217 | 6.6071 | 9.175 | 68.629 | 123.0683 | 3.9216 | 185.5546 | 112.706 | 222.4167 | 7.8022 | 53.183 | 14.5937 | 106 | 8.9719 | 103.6585 | 216.1831 | 0.021419
36 | 772.6593 | 3.8245 | 86.0847 | 117.1199 | 34.0609 | 6.643 | 50.3592 | 6.4061 | 6.4681 | 79.6198 | 130.6331 | 3.9989 | 196.51 | 120.227 | 233.3559 | 7.9415 | 52.927 | 16.0497 | 108 | 9.6249 | 105.6988 | 220.9941 | 0.021192
37 | 773.3549 | 4.013 | 86.8533 | 113.503 | 34.212 | 6.4993 | 54.9807 | 6.5415 | 10.2994 | 81.1417 | 125.0941 | 4.6493 | 194.8795 | 123.0691 | 266.4762 | 7.9301 | 52.1817 | 16.7924 | 113 | 9.6937 | 106.0574 | 218.3459 | 0.021479
38 | 781.4395 | 3.9795 | 85.3114 | 111.7266 | 34.1003 | 6.6055 | 50.0372 | 6.5933 | 13.4644 | 74.6578 | 99.0091 | 4.8398 | 194.9105 | 125.6868 | 270.8746 | 7.9273 | 51.3472 | 17.139 | 111 | 11.8951 | 105.508 | 217.9926 | 0.01752
39 | 792.4427 | 4.6186 | 75.6512 | 112.4274 | 33.2254 | 7.4367 | 47.6885 | 6.6338 | 13.1338 | 67.9962 | 86.4647 | 7.9668 | 195.0554 | 137.5129 | 286.9291 | 7.8886 | 51.5669 | 17.1865 | 116 | 12.2683 | 104.5359 | 219.305 | 0.0054057
40 | 786.253 | 4.3878 | 66.7176 | 111.2072 | 33.8607 | 6.8331 | 48.1639 | 7.0492 | 12.6038 | 56.3871 | 88.5882 | 18.4439 | 188.5484 | 133.1239 | 295.2476 | 8.0617 | 52.9123 | 17.2952 | 114 | 14.0289 | 102.1662 | 224.6616 | 0
41 | 790.364 | 4.1108 | 51.555 | 114.2233 | 34.0251 | 6.6769 | 54.3516 | 7.8386 | 13.6752 | 44.7899 | 89.6251 | 19.9011 | 188.1795 | 134.7841 | 312.5394 | 8.3176 | 52.4456 | 17.6873 | 117 | 13.8021 | 85.3977 | 232.0206 | 0
42 | 780.0088 | 3.7691 | 46.9302 | 114.4477 | 34.8557 | 5.8879 | 50.3714 | 7.8942 | 13.5538 | 42.2539 | 85.0211 | 18.8865 | 188.9864 | 130.7995 | 299.9159 | 8.4726 | 51.3962 | 17.099 | 116 | 14.3167 | 77.9933 | 239.3176 | 0
43 | 765.2663 | 3.4916 | 46.7275 | 111.8274 | 34.2898 | 6.4255 | 48.2847 | 7.93 | 13.5235 | 43.1465 | 83.5016 | 14.5687 | 182.75 | 132.4581 | 289.3412 | 8.4556 | 51.0857 | 16.2407 | 121 | 12.7859 | 77.9818 | 243.3267 | 0
44 | 759.7813 | 3.8287 | 46.8141 | 110.7025 | 34.8139 | 5.9276 | 48.7017 | 7.9721 | 12.8762 | 41.3055 | 83.8485 | 8.4993 | 178.001 | 124.9735 | 279.5873 | 8.4746 | 52.3691 | 15.3631 | 116 | 12.4211 | 74.7484 | 245.7461 | 0
45 | 754.1563 | 3.9815 | 46.7413 | 109.7239 | 34.284 | 6.4309 | 53.4807 | 7.8615 | 11.6368 | 40.7912 | 75.0455 | 6.5949 | 171.3774 | 113.3943 | 245.3361 | 8.4339 | 51.9484 | 14.3316 | 116 | 14.9036 | 68.5224 | 241.6047 | 0
46 | 736.8852 | 3.4444 | 46.7853 | 109.4675 | 34.0693 | 6.635 | 51.9486 | 7.4652 | 7.5978 | 40.8937 | 66.8191 | 6.7888 | 162.9156 | 105.2709 | 238.0445 | 8.4878 | 51.0961 | 13.1294 | 115 | 14.2216 | 66.8281 | 238.3418 | 0
47 | 725.9395 | 2.8344 | 46.1875 | 108.885 | 34.8302 | 5.9121 | 49.3016 | 7.5716 | 5.978 | 39.9073 | 63.8456 | 6.6853 | 158.9916 | 103.9637 | 241.9053 | 8.5254 | 50.8382 | 12.1076 | 110 | 12.92 | 64.0239 | 238.4564 | 0
48 | 717.2306 | 2.052 | 45.595 | 109.077 | 34.2484 | 6.4648 | 48.6885 | 7.4541 | 6.0175 | 38.3706 | 62.6202 | 6.5092 | 156.9613 | 104.7735 | 241.5637 | 8.4232 | 50.4125 | 11.7702 | 99 | 11.0427 | 61.0062 | 237.1065 | 0
49 | 732.9264 | 2.208 | 45.4774 | 108.5486 | 34.8432 | 5.8997 | 50.3025 | 7.3247 | 5.8737 | 38.0759 | 62.0186 | 6.431 | 156.8043 | 92.8849 | 223.5624 | 8.457 | 50.1768 | 11.5507 | 94 | 11.4908 | 61.3628 | 257.4992 | 0
50 | 729.6577 | 2.1904 | 45.4784 | 108.4479 | 33.5271 | 7.1501 | 53.8389 | 7.3616 | 5.585 | 37.5485 | 61.9982 | 6.4112 | 158.2202 | 86.3179 | 227.0817 | 8.3921 | 50.1938 | 11.4601 | 95 | 11.3011 | 62.9438 | 255.693 | 0
51 | 737.8148 | 1.7162 | 45.4325 | 108.3314 | 32.3299 | 8.2874 | 50.2118 | 7.6657 | 5.9587 | 36.864 | 62.5584 | 6.4462 | 159.4729 | 86.1818 | 246.4391 | 8.4636 | 50.2045 | 11.4679 | 109 | 13.99 | 61.8545 | 241.1855 | 0
52 | 731.2128 | 1.5751 | 45.4448 | 107.7857 | 33.5788 | 7.1009 | 47.773 | 8.2192 | 5.71 | 37.0155 | 63.3359 | 6.4202 | 158.5607 | 86.1153 | 251.5693 | 8.4431 | 50.2967 | 11.4831 | 89 | 13.1755 | 60.3964 | 235.2553 | 0
53 | 719.8016 | 1.9777 | 45.3558 | 108.4019 | 33.2651 | 7.3989 | 47.7034 | 9.1663 | 5.5257 | 36.6084 | 63.5788 | 6.3766 | 156.3433 | 86.0002 | 238.3384 | 8.4597 | 51.9022 | 11.4793 | 91 | 12.8735 | 60.1135 | 227.1103 | 0
54 | 718.7209 | 3.1498 | 45.699 | 108.3029 | 33.8088 | 6.8824 | 55.6252 | 8.3455 | 5.6132 | 45.0196 | 63.8408 | 6.4107 | 153.8612 | 86.0479 | 235.016 | 8.3931 | 54.5055 | 11.4869 | 90 | 11.0837 | 60.9112 | 224.1774 | 0
55 | 727.8894 | 3.2706 | 48.5394 | 109.0148 | 34.8259 | 5.9162 | 56.343 | 7.6473 | 5.7073 | 60.0825 | 64.4905 | 6.4301 | 153.8786 | 86.1599 | 215.7788 | 8.4597 | 52.1424 | 11.4983 | 95 | 10.5646 | 60.5925 | 228.0456 | 0
56 | 746.9001 | 3.2157 | 62.9643 | 112.4704 | 33.4942 | 7.1813 | 52.4403 | 7.5991 | 8.5327 | 62.7883 | 65.5419 | 5.976 | 159.9634 | 86.9327 | 224.9846 | 8.457 | 50.2911 | 11.8095 | 90 | 10.9582 | 61.9981 | 230.6863 | 0
57 | 742.9937 | 3.3667 | 73.1877 | 113.9696 | 33.0499 | 7.6034 | 51.9207 | 7.7821 | 10.224 | 56.9386 | 65.5102 | 4.4845 | 166.9968 | 92.4378 | 238.2332 | 8.2507 | 49.4481 | 12.7272 | 95 | 11.3096 | 62.5226 | 225.524 | 0
58 | 759.6905 | 3.0177 | 75.6953 | 113.1667 | 33.8279 | 6.8643 | 58.173 | 8.5633 | 6.6334 | 57.9475 | 64.602 | 4.3149 | 176.55 | 98.9883 | 250.5622 | 8.2292 | 49.3153 | 13.3967 | 105 | 12.0193 | 67.0642 | 224.5128 | 0.021741
59 | 792.3634 | 1.9948 | 73.7755 | 111.0726 | 34.7888 | 5.9514 | 58.8842 | 8.5308 | 5.1267 | 72.6239 | 77.4174 | 7.1418 | 195.5695 | 108.9568 | 257.5491 | 8.4112 | 49.5181 | 14.8169 | 116 | 9.7534 | 70.3515 | 226.6021 | 0.028733
60 | 800.8843 | 1.7063 | 72.5862 | 109.7785 | 34.2559 | 6.4577 | 51.2161 | 8.0691 | 7.4979 | 78.5829 | 85.7649 | 10.3888 | 205.9287 | 121.1606 | 272.2942 | 8.1097 | 50.63 | 15.9113 | 121 | 10.2704 | 72.7042 | 234.7653 | 0.053075
61 | 792.6353 | 1.6209 | 72.8145 | 111.273 | 34.064 | 6.6399 | 48.5417 | 7.4619 | 9.6932 | 70.1504 | 87.6235 | 9.7414 | 209.2257 | 127.8176 | 281.4018 | 7.9994 | 51.0982 | 16.3536 | 127 | 10.8396 | 74.4737 | 243.1461 | 0.072449
62 | 790.7823 | 1.5499 | 72.1793 | 111.5422 | 34.1289 | 6.5784 | 51.3794 | 7.2512 | 7.2387 | 66.5545 | 87.0202 | 15.9865 | 206.5427 | 128.7729 | 319.9608 | 8.112 | 52.309 | 16.344 | 133 | 12.6956 | 71.8443 | 263.9748 | 0.048395
63 | 787.3655 | 2.652 | 72.0707 | 111.4051 | 34.0061 | 6.6949 | 56.5201 | 7.2248 | 6.8053 | 72.9905 | 86.5487 | 21.1347 | 205.271 | 128.2156 | 344.9061 | 8.0266 | 51.744 | 16.666 | 118 | 12.5104 | 71.9582 | 258.9215 | 0.0083703
64 | 795.5465 | 3.6999 | 66.3141 | 113.4286 | 34.0572 | 6.6465 | 52.0207 | 7.3987 | 9.9595 | 72.929 | 87.4696 | 24.3054 | 204.0794 | 124.2566 | 339.7045 | 8.0948 | 51.4996 | 17.1087 | 109 | 10.366 | 73.1881 | 263.9334 | 0
65 | 792.3062 | 4.3173 | 50.9994 | 118.6904 | 34.0948 | 6.6107 | 49.6844 | 7.7525 | 12.5663 | 67.5417 | 89.9259 | 21.5754 | 204.7751 | 132.0597 | 359.8567 | 8.3445 | 52.598 | 17.9643 | 130 | 13.2885 | 73.0313 | 267.6073 | 0
66 | 796.2448 | 4.0001 | 46.2935 | 117.2534 | 34.7616 | 5.9773 | 48.9273 | 8.2337 | 10.1687 | 64.3676 | 92.3942 | 11.1131 | 201.0525 | 127.9447 | 348.664 | 8.6016 | 52.6747 | 17.2584 | 131 | 13.6338 | 72.4885 | 260.7812 | 0
67 | 792.1938 | 3.6517 | 46.9476 | 113.3957 | 34.3309 | 6.3864 | 54.6878 | 8.8704 | 8.7105 | 58.3298 | 91.5164 | 7.4897 | 196.3164 | 122.4496 | 351.089 | 8.8782 | 52.5399 | 16.453 | 111 | 14.5187 | 71.3571 | 256.9739 | 0
68 | 782.9892 | 3.4856 | 47.2303 | 110.3769 | 34.0435 | 6.6595 | 51.4387 | 8.7948 | 10.3917 | 47.1385 | 87.4194 | 7.7375 | 191.591 | 122.1269 | 319.0239 | 8.7515 | 51.9001 | 15.7649 | 97 | 12.6063 | 69.15 | 253.358 | 0
69 | 760.144 | 3.6142 | 47.1086 | 110.6118 | 34.7904 | 5.9499 | 48.6078 | 7.9174 | 10.4622 | 42.9008 | 75.7192 | 7.1408 | 187.7801 | 116.5297 | 277.1384 | 8.4964 | 51.7144 | 14.9072 | 97 | 10.3639 | 67.7898 | 260.2832 | 0
70 | 736.5123 | 3.5865 | 47.205 | 109.4899 | 33.6016 | 7.0792 | 49.584 | 7.7675 | 6.9922 | 42.9569 | 66.7734 | 6.8241 | 178.4127 | 109.9505 | 264.4987 | 8.5722 | 51.7824 | 13.9233 | 94 | 9.959 | 66.6979 | 256.5035 | 0
71 | 727.7408 | 3.057 | 47.1801 | 109.2642 | 33.8178 | 6.8739 | 55.358 | 7.9564 | 5.8562 | 40.4738 | 63.769 | 6.7232 | 173.4898 | 102.7895 | 257.4421 | 8.498 | 51.1665 | 13.2756 | 94 | 10.9424 | 63.5561 | 250.8951 | 0
72 | 721.5934 | 2.1181 | 46.6203 | 108.4429 | 34.7703 | 5.969 | 54.445 | 8.4856 | 5.824 | 39.6112 | 62.7231 | 6.6212 | 172.2027 | 97.4557 | 243.3344 | 8.4902 | 50.6061 | 12.9516 | 91 | 12.9119 | 62.0675 | 248.7601 | 0
73 | 714.39 | 1.6088 | 45.8857 | 107.7066 | 48.5659 | 6.4461 | 54.9035 | 9.7447 | 5.4388 | 39.0151 | 63.3422 | 6.6257 | 172.9348 | 88.8111 | 240.0436 | 8.4877 | 50.4483 | 13.0737 | 89 | 12.956 | 63.691 | 251.7083 | 0
74 | 710.6355 | 1.7386 | 45.8329 | 107.2299 | 49.1262 | 5.9139 | 54.7758 | 8.8112 | 5.2283 | 37.9138 | 62.9673 | 6.6343 | 169.0835 | 87.2207 | 246.8653 | 8.4222 | 50.3912 | 12.8047 | 90 | 12.5449 | 65.6022 | 254.3906 | 0
75 | 708.4219 | 1.869 | 45.8221 | 106.3877 | 48.6142 | 6.4002 | 59.5711 | 8.1441 | 5.4007 | 37.9057 | 62.3987 | 6.973 | 166.2403 | 91.9739 | 236.9817 | 8.49 | 50.517 | 12.874 | 102 | 11.3374 | 66.5481 | 258.7393 | 0
76 | 710.5001 | 1.4297 | 45.8839 | 105.685 | 48.3721 | 6.6302 | 58.996 | 8.2777 | 5.4298 | 40.5002 | 62.8775 | 7.0736 | 164.4742 | 100.8095 | 234.0178 | 8.4603 | 51.1085 | 12.0703 | 85 | 10.9841 | 68.9587 | 252.0621 | 0
77 | 705.9218 | 2.0465 | 46.0826 | 108.5202 | 48.3767 | 6.6259 | 57.1587 | 10.2962 | 5.2595 | 50.9378 | 63.0703 | 7.0095 | 162.5523 | 110.8293 | 230.216 | 8.5306 | 52.2314 | 11.697 | 85 | 9.852 | 67.7305 | 267.2105 | 0
78 | 717.9987 | 3.0562 | 47.3483 | 107.3082 | 49.0848 | 5.9532 | 58.0213 | 9.4123 | 5.3003 | 65.0598 | 63.9414 | 10.3015 | 168.8469 | 112.6905 | 237.6258 | 8.4331 | 54.6932 | 11.7211 | 84 | 10.7653 | 65.9311 | 281.4145 | 0
79 | 743.3415 | 3.9577 | 57.4142 | 112.0967 | 47.052 | 7.8844 | 76.3379 | 8.264 | 7.619 | 93.9956 | 96.0725 | 20.4332 | 197.2869 | 156.4758 | 263.6267 | 11.3541 | 53.575 | 12.4245 | 110 | 15.4173 | 68.9421 | 313.0607 | 0
80 | 793.3148 | 5.0722 | 80.1621 | 121.1297 | 41.7922 | 12.8812 | 101.3166 | 9.2687 | 17.0913 | 120.0118 | 121.7618 | 33.3423 | 253.0751 | 201.6562 | 329.2298 | 20.9976 | 58.3797 | 12.9796 | 135 | 21.5814 | 105.7971 | 383.9374 | 0
81 | 821.1317 | 6.0442 | 100.0989 | 126.9223 | 38.7878 | 15.7354 | 107.4479 | 12.1841 | 21.3543 | 123.9215 | 134.8599 | 36.5065 | 296.0842 | 235.8981 | 405.5901 | 26.4612 | 66.2599 | 13.2141 | 174 | 21.1422 | 127.9305 | 433.6471 | 0
82 | 854.268 | 4.8268 | 104.0733 | 119.9725 | 39.1777 | 15.3649 | 100.4702 | 12.996 | 21.4635 | 117.8715 | 141.8484 | 37.0083 | 316.001 | 255.6268 | 477.517 | 28.2965 | 72.7176 | 16.1188 | 165 | 17.8599 | 142.2222 | 468.7467 | 0.11481
83 | 892.9742 | 3.7334 | 104.0674 | 148.9653 | 37.7777 | 16.6949 | 101.1551 | 12.0265 | 21.628 | 126.8889 | 149.8958 | 41.8252 | 324.3788 | 261.4868 | 503.0188 | 30.5471 | 77.0814 | 16.5344 | 172 | 16.8572 | 145.9122 | 472.508 | 0.14291
84 | 920.3348 | 3.5878 | 106.0315 | 145.8635 | 38.7908 | 15.7324 | 104.6319 | 12.0593 | 21.5222 | 122.2775 | 154.2709 | 43.6464 | 339.3852 | 271.1678 | 497.6256 | 31.5875 | 76.457 | 16.5269 | 217 | 16.498 | 144.826 | 476.2352 | 0.17918
85 | 929.3047 | 3.2353 | 107.1503 | 138.2743 | 38.5486 | 15.9626 | 99.4005 | 11.9673 | 19.5838 | 121.9013 | 156.4991 | 43.3838 | 337.3334 | 274.1407 | 479.9771 | 30.6673 | 76.9277 | 17.051 | 192 | 17.0275 | 140.0243 | 475.7094 | 0.17832
86 | 919.597 | 3.047 | 108.3199 | 142.8427 | 39.1374 | 15.4032 | 97.7241 | 12.5993 | 15.969 | 124.4258 | 158.6151 | 43.4357 | 333.7776 | 285.3656 | 489.8773 | 30.0454 | 79.7554 | 17.3403 | 191 | 17.8864 | 138.9771 | 480.8554 | 0.17745
87 | 925.3229 | 3.8148 | 108.7241 | 140.2275 | 38.6688 | 15.8484 | 99.74 | 13.7289 | 13.2318 | 113.6376 | 161.8031 | 42.8748 | 332.6531 | 292.8414 | 525.6787 | 30.2011 | 82.5077 | 17.0763 | 175 | 17.4263 | 141.6635 | 473.5125 | 0.10029
88 | 937.8436 | 5.2889 | 106.4523 | 137.5962 | 36.1302 | 18.2601 | 101.7759 | 13.4774 | 11.6827 | 110.1106 | 159.0321 | 43.801 | 332.2014 | 283.3669 | 527.0542 | 29.8287 | 82.4472 | 17.783 | 157 | 14.6891 | 141.6425 | 451.1512 | 0
89 | 929.554 | 5.7461 | 102.2223 | 133.0166 | 40.5726 | 14.0397 | 90.8909 | 12.6893 | 11.7285 | 109.9786 | 157.8881 | 42.9147 | 311.3648 | 271.9097 | 505.1576 | 25.1616 | 77.848 | 19.0025 | 156 | 13.4266 | 132.8807 | 395.5493 | 0
90 | 880.1491 | 4.9443 | 91.2761 | 124.398 | 46.995 | 7.9385 | 75.9265 | 10.9372 | 15.1795 | 98.8663 | 153.6633 | 39.7234 | 284.4771 | 227.0296 | 431.7354 | 14.4652 | 70.6449 | 18.9766 | 149 | 12.364 | 95.5014 | 315.8284 | 0
91 | 849.5635 | 4.3582 | 69.1225 | 115.4396 | 48.3601 | 6.6417 | 67.192 | 8.9205 | 16.1432 | 81.7988 | 129.0752 | 30.9241 | 246.2874 | 180.0782 | 328.5792 | 9.6807 | 63.5885 | 18.1263 | 141 | 10.7951 | 78.9951 | 287.4341 | 0
92 | 830.9865 | 4.2948 | 61.7644 | 110.9708 | 48.3294 | 6.6708 | 59.4687 | 8.1118 | 15.0927 | 55.2171 | 104.9035 | 13.7742 | 226.878 | 166.6944 | 265.2325 | 9.1668 | 59.3129 | 16.9958 | 123 | 9.604 | 75.0699 | 253.4943 | 0
93 | 806.2369 | 4.0107 | 52.1396 | 107.8488 | 49.1464 | 5.8946 | 53.0317 | 8.0803 | 13.1462 | 46.0971 | 96.859 | 8.0946 | 206.7924 | 147.952 | 269.3315 | 9.1809 | 54.5196 | 16.3958 | 136 | 9.2095 | 72.1123 | 247.2536 | 0
94 | 785.3419 | 5.3619 | 48.1615 | 107.0743 | 48.5365 | 6.4741 | 49.9985 | 8.347 | 8.8292 | 44.7963 | 91.6376 | 8.3273 | 190.1079 | 130.0346 | 281.7634 | 9.261 | 51.8628 | 15.7348 | 124 | 8.4279 | 69.0148 | 248.2764 | 0
95 | 772.1794 | 3.8563 | 47.8355 | 105.3174 | 48.3844 | 6.6186 | 49.0872 | 8.9567 | 6.94 | 39.672 | 77.2685 | 8.2618 | 183.6831 | 114.2777 | 260.3245 | 9.1396 | 51.2664 | 15.0831 | 116 | 8.1427 | 67.1182 | 248.7021 | 0
96 | 750.9117 | 2.0098 | 47.4269 | 103.7327 | 49.1337 | 5.9067 | 49.3468 | 9.4599 | 6.3113 | 38.27 | 70.0052 | 8.0753 | 178.2216 | 105.2689 | 222.2207 | 9.0464 | 51.3187 | 14.171 | 103 | 8.3111 | 66.0318 | 246.4205 | 0
97 | 747.636 | 1.6807 | 47.5651 | 102.6543 | 55.6967 | 6.4624 | 52.3281 | 9.0331 | 6.0583 | 38.3298 | 69.3603 | 8.0784 | 186.088 | 101.6233 | 246.0554 | 9.1335 | 50.8585 | 13.9346 | 97 | 8.7574 | 64.6498 | 250.9625 | 0
98 | 746.7223 | 1.6128 | 47.6067 | 102.3348 | 55.5239 | 6.6266 | 49.7587 | 8.5171 | 6.0013 | 38.4462 | 71.8648 | 8.1276 | 188.0093 | 96.9088 | 261.5694 | 9.1385 | 50.7069 | 13.841 | 98 | 8.4038 | 65.2117 | 243.1511 | 0
99 | 747.1772 | 1.6416 | 48.5739 | 102.7096 | 56.2734 | 5.9146 | 48.1138 | 8.275 | 6.033 | 38.3272 | 75.0104 | 8.2601 | 184.3716 | 93.2985 | 265.61 | 9.1353 | 50.9056 | 13.5658 | 116 | 8.0675 | 64.3805 | 239.3138 | 0
100 | 741.651 | 1.7344 | 48.8834 | 102.7915 | 55.681 | 6.4773 | 50.388 | 8.6985 | 6.1526 | 40.1762 | 76.3418 | 8.2285 | 181.3412 | 91.6457 | 245.5679 | 9.0829 | 51.2185 | 12.6814 | 93 | 7.9763 | 64.0749 | 243.5466 | 0
101 | 729.7148 | 2.2131 | 48.7597 | 102.5856 | 55.5098 | 6.64 | 54.2492 | 9.7685 | 5.9145 | 45.0883 | 74.7368 | 8.2782 | 178.1431 | 101.4787 | 221.1925 | 9.1459 | 52.7677 | 12.1343 | 92 | 7.9551 | 63.5897 | 264.4201 | 0
102 | 730.0519 | 3.2007 | 35.9178 | 103.542 | 55.4978 | 6.6514 | 55.0744 | 9.4325 | 6.076 | 54.3043 | 70.7172 | 9.5805 | 185.3619 | 110.3508 | 227.4685 | 9.092 | 54.9231 | 12.6515 | 93 | 8.6196 | 64.5511 | 285.5632 | 0
103 | 750.7908 | 4.6043 | 30.9649 | 109.6937 | 53.2275 | 8.8082 | 68.4733 | 8.5918 | 9.2903 | 82.5218 | 83.3118 | 19.2358 | 203.586 | 153.4449 | 266.5729 | 12.1072 | 52.8508 | 12.9345 | 121 | 12.3068 | 71.1719 | 317.4647 | 0
104 | 803.5857 | 5.3286 | 30.9649 | 117.4648 | 48.6761 | 13.132 | 97.0114 | 9.7607 | 14.7698 | 103.9163 | 115.1419 | 36.2985 | 254.8037 | 205.7117 | 338.3548 | 20.875 | 55.6144 | 12.6688 | 130 | 17.2477 | 110.4109 | 386.7205 | 0
105 | 858.4762 | 6.6436 | 80.9153 | 122.3256 | 45.1157 | 16.5144 | 104.1591 | 13.6388 | 16.5503 | 103.0777 | 131.4643 | 38.4011 | 298.7454 | 245.9293 | 412.64 | 25.6351 | 61.5721 | 14.8019 | 143 | 23.2246 | 133.8809 | 445.9907 | 0
106 | 902.0383 | 5.9446 | 105.4072 | 126.8807 | 46.1195 | 15.5608 | 105.4006 | 15.7439 | 17.0343 | 93.0655 | 143.6683 | 35.9263 | 320.9827 | 270.9265 | 473.0797 | 27.7465 | 68.5674 | 15.5697 | 150 | 23.1157 | 139.1069 | 465.0907 | 0.029674
107 | 948.0228 | 5.3716 | 106.5109 | 129.44 | 47.2106 | 14.5243 | 118.2264 | 14.0188 | 16.6653 | 102.6887 | 149.2616 | 37.881 | 337.224 | 302.8652 | 515.2201 | 28.7695 | 72.9853 | 16.8116 | 154 | 17.3657 | 143.6646 | 475.1982 | 0.062601
108 | 970.5629 | 4.8962 | 107.3324 | 131.1004 | 46.6161 | 15.089 | 122.1379 | 13.3008 | 16.1761 | 103.3829 | 149.918 | 42.3425 | 338.9641 | 314.4534 | 536.1293 | 28.6533 | 73.6695 | 17.374 | 156 | 13.0109 | 155.658 | 484.116 | 0.11227
109 | 970.0008 | 4.097 | 106.947 | 132.3423 | 44.3368 | 17.2544 | 109.837 | 13.6917 | 17.2251 | 93.5748 | 151.8894 | 40.4608 | 338.0521 | 304.0171 | 523.1507 | 28.7964 | 72.4074 | 17.7969 | 163 | 11.7735 | 153.11 | 477.4945 | 0.19554
110 | 977.9806 | 3.1508 | 109.0037 | 135.8834 | 45.8412 | 15.8252 | 119.2131 | 13.2508 | 18.7453 | 91.0753 | 152.1537 | 36.7933 | 337.8547 | 303.1766 | 499.1472 | 28.7993 | 74.0277 | 17.8809 | 156 | 12.3795 | 152.805 | 505.453 | 0.18355
111 | 977.9581 | 2.9157 | 105.2698 | 133.6665 | 47.3407 | 14.4006 | 123.8179 | 11.0327 | 20.3697 | 92.0552 | 149.9649 | 35.75 | 335.0947 | 311.9415 | 516.058 | 28.4488 | 75.7381 | 18.2354 | 150 | 12.6809 | 155.3716 | 498.2135 | 0.11451
112 | 961.506 | 4.8264 | 102.4306 | 133.2455 | 47.4413 | 14.3051 | 106.2549 | 9.1278 | 20.453 | 92.428 | 149.0455 | 38.1213 | 326.2729 | 298.3479 | 518.3256 | 27.6469 | 73.4355 | 18.4349 | 145 | 11.8106 | 159.8741 | 479.2256 | 0
113 | 907.8865 | 4.8985 | 101.5196 | 131.7826 | 50.5636 | 11.3389 | 88.4569 | 9.0109 | 19.6765 | 94.1925 | 152.5113 | 37.4392 | 317.0122 | 287.5908 | 490.9138 | 23.4621 | 70.3194 | 18.5725 | 142 | 11.9158 | 148.0634 | 400.3568 | 0
114 | 848.6138 | 4.4794 | 93.1443 | 126.5872 | 51.4713 | 10.4766 | 74.6276 | 9.6518 | 19.903 | 85.0051 | 148.7121 | 35.6636 | 292.6277 | 237.4649 | 425.4562 | 13.2851 | 67.1504 | 17.7345 | 146 | 10.974 | 107.6442 | 329.2515 | 0
115 | 817.7369 | 4.1862 | 69.3427 | 117.7092 | 54.5561 | 7.546 | 65.0148 | 10.1997 | 17.6533 | 60.6738 | 123.8353 | 30.241 | 256.1017 | 187.9933 | 388.6558 | 9.0812 | 64.5937 | 16.8008 | 138 | 9.5556 | 84.2987 | 303.2455 | 0
116 | 808.1199 | 3.8978 | 61.3304 | 112.1803 | 56.2241 | 5.9614 | 55.6907 | 9.1573 | 15.7631 | 44.7614 | 88.274 | 24.6611 | 227.1933 | 167.3846 | 353.7578 | 9.0556 | 61.3402 | 16.027 | 125 | 9.9154 | 76.1871 | 270.4481 | 0
117 | 802.1975 | 4.0494 | 51.9261 | 110.8815 | 55.7806 | 6.3827 | 52.8729 | 8.8199 | 13.9949 | 41.8096 | 71.9794 | 19.7787 | 205.8769 | 153.0136 | 314.0597 | 9.2321 | 55.9242 | 15.0286 | 121 | 8.1268 | 71.2266 | 256.9646 | 0
118 | 798.7772 | 3.8516 | 48.7599 | 108.3421 | 55.512 | 6.6379 | 53.3946 | 10.0091 | 10.0343 | 41.0828 | 70.4276 | 13.6443 | 191.9518 | 139.0137 | 273.6247 | 9.1965 | 53.224 | 13.7526 | 123 | 7.1621 | 67.1468 | 254.6944 | 0
119 | 786.8687 | 3.32 | 48.7694 | 105.8629 | 55.5247 | 6.6258 | 52.7595 | 10.8807 | 7.7885 | 40.9497 | 67.1023 | 11.6836 | 182.479 | 130.0223 | 255.5542 | 9.2539 | 53.6893 | 13.3778 | 121 | 7.0459 | 66.2764 | 260.7167 | 0
120 | 764.7614 | 2.1305 | 48.6345 | 105.746 | 55.4421 | 6.7043 | 55.4948 | 9.7069 | 7.1368 | 41.3391 | 64.3389 | 11.874 | 177.72 | 125.598 | 252.6772 | 9.2417 | 52.7301 | 13.1671 | 109 | 7.0048 | 65.7397 | 260.9911 | 0
121 | 749.013 | 1.7434 | 48.4038 | 105.0112 | 55.5858 | 6.5678 | 54.2059 | 10.8378 | 7.066 | 40.6938 | 63.697 | 11.6568 | 177.0577 | 121.1086 | 247.161 | 9.1497 | 49.5595 | 12.9723 | 101 | 6.8863 | 62.5618 | 254.4065 | 0
122 | 743.0689 | 2.0267 | 48.3484 | 104.9001 | 55.4179 | 6.7273 | 52.3249 | 10.3716 | 7.2014 | 41.2735 | 63.5217 | 11.5301 | 178.4551 | 117.0459 | 243.2415 | 9.2057 | 48.2834 | 12.9 | 98 | 6.8167 | 61.9844 | 265.3018 | 0
123 | 747.0911 | 2.0217 | 48.5124 | 105.6579 | 53.9578 | 8.1144 | 51.8107 | 10.0166 | 7.0118 | 44.8192 | 63.9977 | 11.5524 | 177.3804 | 115.2437 | 243.1507 | 9.1875 | 48.2626 | 13.0781 | 111 | 6.8452 | 60.8262 | 266.9042 | 0
124 | 738.7879 | 1.6985 | 48.5906 | 106.7432 | 55.8265 | 6.3391 | 51.6915 | 11.2818 | 7.2151 | 52.8254 | 64.5969 | 11.5534 | 177.6346 | 114.0012 | 245.216 | 9.1431 | 48.078 | 13.1217 | 94 | 6.8408 | 60.1567 | 258.1351 | 0
125 | 736.4362 | 2.2214 | 48.8294 | 106.9754 | 55.7783 | 6.385 | 52.3251 | 10.1834 | 7.1365 | 56.3003 | 64.4516 | 11.5464 | 174.4432 | 112.3152 | 242.0615 | 9.1341 | 49.7962 | 12.9912 | 92 | 6.976 | 60.1172 | 271.6122 | 0
126 | 744.835 | 3.2375 | 49.0084 | 108.1627 | 55.406 | 6.7387 | 54.3444 | 11.3802 | 6.1546 | 67.8625 | 64.6076 | 11.5734 | 172.2713 | 111.2656 | 244.7159 | 9.1689 | 52.4238 | 12.6296 | 91 | 7.1512 | 60.6165 | 284.0963 | 0
127 | 739.1257 | 3.7253 | 50.1752 | 107.4045 | 54.8035 | 7.311 | 61.7078 | 10.3643 | 7.3956 | 89.0665 | 72.5733 | 11.5061 | 174.9921 | 115.761 | 249.9597 | 9.1638 | 50.2185 | 12.4937 | 99 | 6.9254 | 60.8739 | 287.3386 | 0
128 | 747.7998 | 3.6958 | 62.5191 | 106.8627 | 51.5135 | 10.4365 | 68.8468 | 11.6407 | 10.4445 | 95.5137 | 90.7212 | 11.6127 | 189.036 | 148.6897 | 293.5037 | 9.1454 | 49.607 | 12.6597 | 103 | 7.3683 | 64.479 | 287.3716 | 0
129 | 757.7317 | 3.8417 | 74.043 | 108.5485 | 50.4847 | 11.4139 | 72.4902 | 10.2037 | 14.2652 | 91.8213 | 96.9074 | 12.4966 | 213.1744 | 195.4771 | 349.1396 | 8.8423 | 51.4596 | 13.51 | 112 | 9.0608 | 71.4507 | 277.0242 | 0
130 | 776.1537 | 2.8305 | 80.5693 | 111.3427 | 50.4059 | 11.4887 | 71.3977 | 11.1042 | 16.6155 | 93.2794 | 99.5828 | 14.9601 | 231.1765 | 220.9615 | 406.6224 | 8.5838 | 54.7431 | 15.1904 | 108 | 8.843 | 78.9939 | 270.7156 | 0.1202
131 | 812.9036 | 1.6021 | 81.5896 | 112.0632 | 50.4601 | 11.4373 | 68.8899 | 9.8869 | 16.412 | 94.4088 | 109.4058 | 24.7117 | 235.6194 | 234.2081 | 436.5074 | 8.5897 | 57.0588 | 17.6298 | 113 | 9.2259 | 82.8727 | 273.5182 | 0.14698
132 | 825.9413 | 1.519 | 81.4349 | 111.0412 | 51.2662 | 10.6714 | 68.2769 | 8.6779 | 16.8352 | 98.0119 | 114.2697 | 25.6792 | 240.3131 | 243.9147 | 452.9676 | 9.1788 | 58.5974 | 18.3289 | 118 | 9.0955 | 84.4551 | 273.7673 | 0.17664
133 | 822.0935 | 1.7794 | 83.1778 | 110.0372 | 50.7821 | 11.1313 | 71.6503 | 10.1176 | 17.712 | 101.3455 | 114.9799 | 25.293 | 243.0143 | 251.4576 | 462.094 | 10.4321 | 60.7039 | 18.5157 | 120 | 9.1713 | 86.2825 | 278.3065 | 0.18951
134 | 819.1788 | 1.7106 | 83.2177 | 110.8536 | 50.4437 | 11.4528 | 74.0958 | 9.8946 | 18.0077 | 100.7256 | 116.0769 | 29.0993 | 241.9485 | 253.8427 | 446.0562 | 11.2306 | 59.3383 | 18.9642 | 116 | 9.9306 | 83.827 | 283.3245 | 0.1744
135 | 823.232 | 1.9487 | 83.0081 | 115.4417 | 51.3046 | 10.635 | 73.8107 | 8.6579 | 18.5131 | 104.4729 | 119.5467 | 32.0238 | 243.5181 | 245.4324 | 434.2606 | 11.871 | 56.3077 | 19.3728 | 119 | 10.5533 | 84.2921 | 294.1607 | 0.11182
136 | 828.0751 | 3.8738 | 77.6138 | 117.0934 | 50.0133 | 11.8617 | 71.1131 | 8.6623 | 19.4851 | 100.8541 | 121.8725 | 34.0928 | 251.1338 | 239.6301 | 446.7604 | 11.3438 | 54.5139 | 19.4474 | 119 | 9.944 | 85.2009 | 303.7947 | 0
137 | 827.9904 | 4.1864 | 59.3366 | 112.9112 | 52.4982 | 9.5011 | 74.8114 | 10.9586 | 17.9008 | 102.0435 | 125.0943 | 32.9468 | 250.2857 | 243.6536 | 446.1872 | 10.661 | 55.621 | 19.399 | 120 | 8.5033 | 88.9617 | 306.1904 | 0
138 | 818.4451 | 3.7551 | 52.6162 | 112.9543 | 54.2886 | 7.8001 | 72.6866 | 10.5843 | 16.9852 | 82.0901 | 121.4595 | 33.8298 | 238.8477 | 219.2711 | 390.2332 | 9.6225 | 57.454 | 18.8727 | 116 | 8.9183 | 87.2105 | 281.6561 | 0
139 | 806.9152 | 4.167 | 52.6293 | 109.2739 | 55.2931 | 6.8459 | 65.1973 | 12.2942 | 15.587 | 74.631 | 105.7422 | 28.7907 | 224.1158 | 175.2462 | 346.3036 | 9.1661 | 56.7684 | 17.9539 | 109 | 8.8029 | 80.9688 | 270.9753 | 0
140 | 800.0381 | 3.8322 | 52.7523 | 106.3209 | 55.4684 | 6.6793 | 55.1714 | 11.0953 | 14.501 | 61.2222 | 91.6233 | 15.8379 | 209.6873 | 151.8261 | 310.5341 | 9.143 | 54.9797 | 16.957 | 112 | 8.0593 | 78.462 | 260.1326 | 0
141 | 777.421 | 4.0478 | 52.7189 | 105.0365 | 54.7166 | 7.3936 | 51.9884 | 12.365 | 12.5457 | 54.0791 | 78.0747 | 9.3217 | 197.5051 | 136.1926 | 284.6593 | 9.1851 | 51.1271 | 16.0712 | 106 | 7.6762 | 71.839 | 263.5636 | 0
142 | 761.2129 | 4.0153 | 52.989 | 106.1169 | 54.5311 | 7.5697 | 52.6166 | 11.358 | 8.6852 | 53.9598 | 72.3228 | 8.154 | 186.2454 | 119.2756 | 270.1949 | 9.291 | 48.9415 | 15.4041 | 104 | 8.6044 | 69.1543 | 275.3451 | 0
143 | 750.469 | 3.2806 | 53.1125 | 104.7264 | 55.2444 | 6.8921 | 52.2705 | 11.9817 | 7.3225 | 51.2845 | 71.0754 | 7.9939 | 179.4151 | 112.0364 | 267.3204 | 9.2026 | 48.8278 | 14.7108 | 105 | 7.4963 | 68.0887 | 274.2727 | 0
144 | 733.2875 | 2.2301 | 53.9879 | 105.028 | 55.4963 | 6.6528 | 52.6434 | 10.5314 | 7.2585 | 45.9895 | 67.5073 | 8.0355 | 178.6415 | 104.9505 | 265.0911 | 9.263 | 49.5975 | 14.1895 | 94 | 7.0942 | 66.1566 | 272.7943 | 0
145 | 729.6477 | 1.6859 | 53.4888 | 105.992 | 55.5026 | 6.6469 | 54.0079 | 11.498 | 7.5725 | 46.6441 | 66.5921 | 8.0258 | 178.7895 | 101.8927 | 269.4992 | 9.1581 | 51.3191 | 13.7172 | 96 | 7.2858 | 64.0491 | 270.7935 | 0
146 | 729.0232 | 1.6964 | 53.304 | 106.6694 | 55.5027 | 6.6467 | 55.6092 | 9.1629 | 7.9437 | 45.7497 | 65.5028 | 8.0607 | 181.7024 | 98.6967 | 267.5651 | 9.2561 | 50.34 | 13.5228 | 94 | 7.4857 | 63.2736 | 266.3217 | 0
147 | 729.8819 | 1.5112 | 53.2298 | 106.496 | 55.5417 | 6.6097 | 53.7733 | 8.7115 | 7.579 | 45.3848 | 65.0691 | 8.0873 | 180.1553 | 96.7037 | 257.1434 | 9.2518 | 50.1564 | 13.3119 | 108 | 7.2209 | 61.3974 | 265.4379 | 0
148 | 722.6102 | 1.4202 | 53.1153 | 106.1466 | 54.7223 | 7.3882 | 52.6321 | 15.7128 | 7.437 | 47.8678 | 65.6804 | 8.0314 | 175.4616 | 97.9411 | 252.634 | 9.2751 | 50.641 | 12.3744 | 93 | 7.0766 | 60.2694 | 270.3348 | 0
149 | 727.6806 | 1.9413 | 53.7905 | 106.1084 | 55.2217 | 6.9137 | 52.9675 | 9.1135 | 7.2935 | 58.0029 | 65.8125 | 8.0394 | 174.9585 | 107.8728 | 250.0796 | 9.2144 | 52.1293 | 12.0331 | 91 | 7.1081 | 60.1826 | 289.0169 | 0
150 | 744.6473 | 3.3329 | 54.0747 | 106.5712 | 55.5159 | 6.6342 | 54.637 | 9.4379 | 7.3733 | 73.315 | 65.7985 | 12.7245 | 177.524 | 115.8738 | 249.3884 | 9.1297 | 54.1784 | 11.9925 | 90 | 8.0673 | 61.0837 | 312.7661 | 0
151 | 761.0748 | 4.4797 | 63.9763 | 114.5842 | 53.9998 | 8.0745 | 68.6251 | 15.116 | 9.924 | 98.1542 | 81.9695 | 22.0207 | 204.8345 | 166.2426 | 264.2964 | 12.0968 | 56.3665 | 11.9277 | 119 | 12.9896 | 69.0227 | 341.972 | 0
152 | 809.3956 | 5.1225 | 86.2816 | 119.9446 | 46.1708 | 15.512 | 96.9048 | 18.1097 | 18.9518 | 127.1962 | 116.6472 | 38.3117 | 249.8345 | 218.9229 | 325.578 | 22.3089 | 60.4477 | 12.8172 | 202 | 23.1188 | 117.7618 | 426.3858 | 0
153 | 896.4706 | 6.9954 | 102.6683 | 122.7118 | 44.3081 | 17.2816 | 109.0125 | 13.7446 | 23.1453 | 131.0684 | 135.6429 | 45.2178 | 295.25 | 268.5236 | 415.3041 | 28.5557 | 65.4313 | 15.7166 | 207 | 21.3247 | 147.5875 | 499.1367 | 0
154 | 954.1313 | 7.6852 | 106.7763 | 128.8981 | 45.2922 | 16.3467 | 110.5607 | 15.7026 | 22.8137 | 128.5356 | 146.1636 | 43.2929 | 329.3197 | 314.1118 | 508.7603 | 29.1255 | 71.7617 | 17.3811 | 304 | 18.5962 | 166.01 | 518.543 | 0.023332
155 | 983.3734 | 7.2443 | 108.5106 | 133.3155 | 45.5757 | 16.0774 | 112.7272 | 17.7971 | 22.714 | 125.2818 | 147.6807 | 42.2267 | 339.3942 | 330.4313 | 543.1871 | 30.0507 | 80.4009 | 17.9673 | 283 | 15.381 | 177.6001 | 514.5069 | 0.049509
156 | 1011.309 | 7.2426 | 112.6751 | 140.7921 | 45.3394 | 16.3019 | 112.204 | 17.9024 | 22.9293 | 124.2403 | 150.0528 | 43.0967 | 348.8547 | 347.1246 | 543.1646 | 33.1198 | 87.7673 | 18.2981 | 259 | 15.1764 | 182.5025 | 513.2335 | 0.044806
157 | 1010.6984 | 7.1621 | 114.2129 | 140.3743 | 44.7294 | 16.8814 | 109.7249 | 17.8405 | 21.6131 | 122.8303 | 156.6847 | 42.8972 | 348.3857 | 354.9803 | 548.7384 | 33.9334 | 86.8717 | 18.6343 | 276 | 14.8623 | 175.898 | 518.4226 | 0.057312
158 | 1020.736 | 6.7686 | 113.7982 | 140.089 | 41.6435 | 19.813 | 112.3481 | 15.1081 | 21.9234 | 121.5351 | 161.7928 | 44.4493 | 347.8671 | 349.0558 | 561.9574 | 34.6403 | 88.2741 | 18.973 | 252 | 13.8344 | 174.7332 | 504.6273 | 0.027919
159 | 1025.8402 | 6.2977 | 110.286 | 138.8206 | 41.2367 | 20.1994 | 114.8669 | 14.3849 | 22.9007 | 116.8109 | 161.1016 | 44.1091 | 354.8057 | 347.1628 | 537.3401 | 35.4501 | 90.3563 | 19.2305 | 239 | 12.3262 | 176.4451 | 495.067 | 0.0073075
160 | 1004.1871 | 6.6127 | 107.5975 | 145.3121 | 43.6331 | 17.9229 | 113.029 | 14.8668 | 23.2038 | 119.9412 | 157.3747 | 45.1874 | 350.9455 | 339.9093 | 530.9577 | 34.8442 | 89.4301 | 19.3472 | 219 | 11.6399 | 177.1191 | 483.1721 | 0
161 | 978.6549 | 5.9347 | 104.8105 | 143.733 | 45.2492 | 16.3876 | 102.1112 | 14.4317 | 21.5627 | 118.9255 | 158.3373 | 45.107 | 332.9014 | 328.4181 | 532.0289 | 28.7991 | 83.3457 | 19.2258 | 192 | 11.6776 | 166.7286 | 441.7126 | 0
162 | 934.6836 | 5.2769 | 100.9695 | 131.0888 | 49.976 | 11.8971 | 86.3696 | 11.7812 | 20.6475 | 112.0333 | 150.3346 | 43.8433 | 301.6295 | 273.5544 | 453.7054 | 15.7599 | 76.1952 | 18.4999 | 174 | 10.8709 | 125.934 | 363.3686 | 0
163 | 890.7687 | 5.0608 | 98.1668 | 119.4769 | 54.5337 | 7.5673 | 74.7537 | 9.7666 | 17.7228 | 102.0534 | 123.7572 | 39.912 | 260.9573 | 203.5831 | 375.3579 | 9.5372 | 70.4418 | 17.7364 | 181 | 10.9333 | 104.9782 | 322.0628 | 0
164 | 846.9088 | 4.4118 | 89.84 | 115.3047 | 55.4555 | 6.6916 | 68.4681 | 8.6005 | 15.796 | 98.4682 | 99.756 | 23.4724 | 232.6603 | 165.3026 | 329.4066 | 9.1404 | 65.2374 | 17.0984 | 154 | 10.7982 | 96.7576 | 286.4464 | 0
165 | 811.8911 | 4.2686 | 54.377 | 115.4893 | 54.7738 | 7.3392 | 62.2151 | 8.3158 | 14.223 | 98.4448 | 92.796 | 15.9684 | 213.4068 | 146.305 | 289.8682 | 9.1161 | 60.2737 | 15.5898 | 150 | 9.3744 | 86.953 | 269.2665 | 0
166 | 790.6195 | 3.7692 | 35.7616 | 112.9924 | 54.4698 | 7.628 | 57.2652 | 8.2398 | 8.7102 | 93.0328 | 88.2595 | 14.7034 | 190.4354 | 134.1429 | 246.6005 | 9.0703 | 57.3208 | 14.4749 | 133 | 7.6139 | 79.1887 | 265.4989 | 0
167 | 759.3134 | 3.165 | 33.9605 | 110.2597 | 55.2883 | 6.8504 | 55.9421 | 8.2604 | 6.3853 | 86.8324 | 74.5504 | 13.5823 | 175.6069 | 122.7765 | 238.8763 | 9.1205 | 57.0289 | 14.0267 | 115 | 6.9261 | 74.6647 | 265.9512 | 0
168 | 746.5095 | 2.2352 | 33.9825 | 108.4552 | 56.2249 | 5.9606 | 60.3337 | 8.9185 | 7.0615 | 77.801 | 65.6414 | 13.2489 | 170.8099 | 111.5868 | 246.3287 | 9.102 | 56.9457 | 13.6628 | 111 | 6.6445 | 70.3923 | 267.0762 | 0
169 | 742.0754 | 2.1034 | 33.629 | 109.0819 | 55.7681 | 6.3946 | 60.3334 | 9.0774 | 6.802 | 62.1001 | 64.604 | 13.0374 | 172.7366 | 104.4649 | 258.3037 | 9.0897 | 56.5929 | 13.4484 | 106 | 6.2049 | 66.1495 | 260.9943 | 0
170 | 743.9938 | 1.767 | 33.5049 | 110.2323 | 55.5069 | 6.6428 | 57.1789 | 8.9762 | 5.5453 | 56.6704 | 63.8246 | 12.9205 | 174.7724 | 99.7996 | 265.7046 | 8.9631 | 56.4902 | 13.0605 | 103 | 6.0128 | 64.7247 | 257.4182 | 0
171 | 728.3371 | 1.7459 | 33.5049 | 109.8225 | 55.436 | 6.7101 | 55.9472 | 8.6377 | 5.407 | 56.8345 | 63.3913 | 12.9325 | 173.3188 | 97.0659 | 263.6253 | 9.0891 | 56.6897 | 12.2922 | 119 | 6.0447 | 63.7052 | 257.6132 | 0
172 | 720.6727 | 2.3323 | 33.6677 | 112.6492 | 54.7979 | 7.3163 | 58.7459 | 8.4072 | 5.3867 | 58.8963 | 64.0646 | 12.9559 | 172.9387 | 97.3408 | 250.4153 | 9.1947 | 57.1082 | 12.1143 | 101 | 6.07 | 63.309 | 254.1582 | 0
173 | 736.8791 | 2.8776 | 33.5453 | 112.6615 | 54.4661 | 7.6315 | 60.0252 | 8.0407 | 5.229 | 64.8544 | 64.2421 | 12.938 | 172.041 | 107.3439 | 245.1958 | 9.0889 | 58.2871 | 11.6066 | 101 | 6.0572 | 63.2591 | 274.8635 | 0
174 | 739.7586 | 3.2042 | 35.1891 | 113.9232 | 53.816 | 8.2491 | 58.8016 | 7.9588 | 5.442 | 78.4027 | 64.2144 | 14.8283 | 178.1407 | 114.2248 | 248.1951 | 9.0581 | 59.9382 | 11.3423 | 102 | 6.3576 | 64.4914 | 298.8925 | 0
175 | 771.6066 | 4.3427 | 19.2871 | 120.1544 | 53.4305 | 8.6153 | 67.626 | 7.9792 | 11.542 | 101.503 | 78.7183 | 22.374 | 214.2985 | 149.8795 | 272.3862 | 12.051 | 59.732 | 12.9454 | 134 | 8.3713 | 70.2289 | 333.4229 | 0
176 | 829.9251 | 6.7483 | 65.7097 | 123.8588 | 48.2952 | 13.4939 | 89.918 | 10.0643 | 15.188 | 109.4841 | 110.8541 | 34.1494 | 264.1349 | 209.661 | 350.1207 | 22.457 | 64.7081 | 13.8201 | 194 | 9.9091 | 116.1306 | 406.4068 | 0
177 | 872.1878 | 8.825 | 97.7475 | 133.3448 | 46.4888 | 15.21 | 106.1059 | 13.342 | 17.225 | 101.8972 | 138.9929 | 39.2164 | 309.734 | 266.6036 | 459.0124 | 31.3502 | 71.1615 | 15.0274 | 218 | 10.4754 | 147.284 | 467.4361 | 0
178 | 919.3749 | 8.1218 | 108.279 | 137.2094 | 46.5901 | 15.1137 | 105.5481 | 14.9305 | 17.914 | 108.3631 | 142.017 | 40.2326 | 342.4271 | 312.093 | 520.0967 | 34.3453 | 78.2011 | 16.7813 | 251 | 11.3446 | 166.8906 | 506.6924 | 0.011542
179 | 973.8927 | 5.3214 | 110.7736 | 141.6768 | 45.6451 | 16.0115 | 104.4462 | 14.8341 | 18.312 | 117.7047 | 136.5065 | 44.8314 | 355.4776 | 343.6596 | 548.6657 | 34.0627 | 84.343 | 17.9979 | 277 | 11.3889 | 178.0001 | 521.047 | 0.01779
180 | 999.4097 | 3.5337 | 111.2397 | 144.5117 | 44.1723 | 17.4106 | 106.3658 | 14.3987 | 19.583 | 119.9066 | 139.183 | 45.9181 | 370.6946 | 361.2608 | 570.6242 | 35.1792 | 83.9165 | 18.2779 | 273 | 9.6693 | 182.3355 | 511.2571 | 0.023065
181 | 1000.4402 | 3.4854 | 115.5587 | 141.4391 | 44.255 | 17.3321 | 111.3376 | 14.2467 | 19.7767 | 115.1844 | 144.4137 | 43.1135 | 369.7914 | 345.0485 | 573.0205 | 36.6821 | 82.007 | 18.6257 | 308 | 8.8792 | 178.9466 | 499.8557 | 0.023629
182 | 1008.9822 | 3.7531 | 118.7984 | 145.6382 | 44.3099 | 17.2799 | 108.7344 | 12.9595 | 20.3282 | 116.6721 | 151.5402 | 43.5065 | 363.7028 | 356.4346 | 559.327 | 36.4223 | 84.1721 | 19.2655 | 273 | 8.2703 | 185.6032 | 498.9351 | 0.0076098
183 | 1011.2757 | 8.462 | 119.4155 | 147.469 | 45.3281 | 16.3126 | 104.6828 | 11.6829 | 21.264 | 115.2645 | 150.5916 | 44.4094 | 364.3713 | 346.4623 | 568.5693 | 34.823 | 85.2057 | 20.0488 | 296 | 8.4214 | 185.0727 | 495.5851 | 0.0085251
184 | 1006.3854 | 12.2544 | 113.0638 | 145.8755 | 45.6287 | 16.0271 | 104.9021 | 11.3662 | 18.6971 | 111.0074 | 148.2245 | 45.6258 | 350.6831 | 324.8808 | 555.5803 | 34.9652 | 82.5255 | 20.259 | 256 | 8.2016 | 185.039 | 463.3523 | 0
185 | 982.7888 | 7.5363 | 108.0833 | 149.7377 | 52.0783 | 9.8999 | 105.7895 | 10.9598 | 17.2998 | 112.7907 | 149.8506 | 43.8972 | 331.5172 | 295.5074 | 502.4769 | 24.1453 | 79.5153 | 20.0421 | 252 | 7.9217 | 174.8133 | 414.7139 | 0
186 | 939.6495 | 4.4998 | 104.0751 | 137.1212 | 55.2673 | 6.8704 | 89.2068 | 9.1937 | 17.7301 | 102.6697 | 141.9923 | 41.0636 | 297.1108 | 241.304 | 427.5434 | 13.0142 | 74.4203 | 19.3139 | 232 | 6.9088 | 127.2634 | 360.192 | 0
187 | 888.7564 | 5.0814 | 96.7115 | 122.5614 | 55.4746 | 6.6734 | 80.1036 | 7.9714 | 16.844 | 92.4694 | 116.7344 | 36.0584 | 266.0006 | 182.4357 | 358.3285 | 9.4968 | 66.8645 | 18.6895 | 195 | 6.6205 | 104.5005 | 329.9526 | 0
188 | 836.4965 | 4.9595 | 94.1109 | 115.0825 | 56.2284 | 5.9573 | 73.4186 | 7.6625 | 14.816 | 83.0274 | 89.8719 | 26.854 | 246.3874 | 154.2231 | 309.2321 | 8.9299 | 59.9098 | 17.8853 | 167 | 6.3672 | 94.0294 | 310.529 | 0
189 | 796.9922 | 4.0521 | 72.9568 | 112.7819 | 55.7859 | 6.3777 | 72.3659 | 7.8631 | 9.131 | 78.5175 | 73.614 | 15.1573 | 214.6784 | 136.1803 | 284.4516 | 8.8676 | 56.8106 | 16.9636 | 169 | 6.2513 | 81.6799 | 302.3013 | 0
190 | 774.6635 | 3.8052 | 63.5509 | 111.2476 | 55.4873 | 6.6614 | 63.6218 | 7.7683 | 6.14 | 75.1439 | 66.9462 | 9.4403 | 195.3481 | 134.106 | 263.4078 | 8.7953 | 56.1125 | 15.7189 | 157 | 5.8612 | 75.2254 | 296.1946 | 0
191 | 758.0447 | 3.2578 | 63.4575 | 109.0557 | 56.1727 | 6.0102 | 59.0397 | 7.6734 | 5.542 | 68.9694 | 64.3804 | 8.501 | 182.5517 | 128.0765 | 233.1485 | 8.8724 | 55.235 | 15.0591 | 150 | 5.5317 | 72.1851 | 294.6555 | 0
192 | 730.4669 | 2.316 | 63.2206 | 108.6806 | 55.7879 | 6.3758 | 60.4333 | 7.8644 | 5.895 | 64.3637 | 62.2418 | 8.5236 | 174.8065 | 115.293 | 241.5203 | 8.8526 | 54.1871 | 14.4983 | 141 | 5.2449 | 70.3303 | 296.0155 | 0
193 | 727.85 | 2.0244 | 63.2188 | 109.8109 | 56.2692 | 5.9186 | 64.7258 | 7.8905 | 5.614 | 61.7832 | 61.1635 | 8.5342 | 174.2798 | 108.9297 | 255.3284 | 8.8915 | 53.8668 | 13.6395 | 129 | 4.7641 | 66.893 | 294.2237 | 0
194 | 717.1465 | 2.1447 | 63.1411 | 110.3673 | 55.0321 | 7.0938 | 61.5836 | 7.8185 | 5.578 | 61.2951 | 61.0827 | 8.5521 | 175.8915 | 103.9772 | 250.882 | 8.9007 | 54.0207 | 13.2193 | 120 | 4.6724 | 66.0373 | 295.2418 | 0
195 | 718.4158 | 2.5821 | 62.7875 | 109.4162 | 54.4642 | 7.6333 | 59.1163 | 7.7925 | 5.594 | 60.8506 | 61.6458 | 8.5815 | 174.8329 | 98.2925 | 219.6648 | 8.7909 | 54.0972 | 12.7409 | 129 | 4.7344 | 63.3261 | 299.8891 | 0
196 | 721.8573 | 2.6678 | 62.9841 | 108.9007 | 55.2482 | 6.8885 | 59.604 | 7.8299 | 5.822 | 61.1274 | 62.5296 | 8.5823 | 173.0522 | 91.8183 | 219.368 | 8.8723 | 53.9906 | 11.9241 | 109 | 4.7254 | 62.3212 | 297.9355 | 0
197 | 722.1158 | 2.7296 | 62.8415 | 108.7752 | 54.8277 | 7.288 | 65.204 | 8.0967 | 5.917 | 65.5687 | 62.882 | 8.5216 | 170.9903 | 90.1463 | 224.2221 | 8.947 | 55.3498 | 11.644 | 106 | 4.7098 | 61.8839 | 295.5929 | 0
198 | 729.4402 | 3.4679 | 62.7409 | 108.8132 | 54.4525 | 7.6444 | 62.7997 | 7.9756 | 7.3386 | 78.991 | 63.9828 | 8.4879 | 168.296 | 90.3633 | 226.8798 | 8.9232 | 57.454 | 11.627 | 105 | 4.6693 | 62.8433 | 286.1708 | 0
199 | 733.6449 | 3.499 | 64.3064 | 110.4101 | 54.4878 | 7.6109 | 61.6735 | 7.8397 | 8.9891 | 99.0592 | 66.0401 | 8.493 | 170.2193 | 92.6993 | 228.7477 | 8.8628 | 55.2565 | 11.6224 | 110 | 5.014 | 63.747 | 290.0364 | 0
200 | 746.1069 | 4.3392 | 76.3022 | 110.7035 | 54.484 | 7.6145 | 68.4169 | 7.8382 | 14.9722 | 112.3629 | 70.3518 | 14.4078 | 186.2452 | 100.9445 | 230.7144 | 8.8143 | 53.7353 | 11.9463 | 115 | 6.8051 | 64.6517 | 307.7411 | 0
201 | 759.4456 | 4.1748 | 88.6632 | 109.9877 | 54.5007 | 7.5986 | 85.1661 | 7.9735 | 20.882 | 110.994 | 90.473 | 23.9468 | 209.8306 | 112.1717 | 241.1231 | 8.5693 | 53.307 | 13.8604 | 143 | 6.2377 | 68.3403 | 299.4282 | 0
202 | 778.6703 | 2.9619 | 92.681 | 110.4941 | 53.0381 | 8.9881 | 79.9528 | 8.1829 | 22.3013 | 99.256 | 115.1679 | 25.7467 | 227.1111 | 121.3476 | 259.5297 | 8.4605 | 54.1925 | 15.0811 | 143 | 5.3003 | 103.8053 | 301.0333 | 0.0099575
203 | 811.7046 | 2.3277 | 97.3596 | 112.783 | 53.9568 | 8.1153 | 71.1867 | 8.0878 | 22.316 | 97.1904 | 126.5019 | 28.5015 | 237.5422 | 129.5358 | 274.8979 | 8.3603 | 55.1527 | 15.9781 | 171 | 4.8762 | 120.9402 | 301.101 | 0.018333
204 | 849.3446 | 1.8065 | 97.2233 | 112.5971 | 55.2519 | 6.885 | 79.0224 | 8.3683 | 20.2687 | 96.4877 | 128.2427 | 30.1879 | 242.2071 | 152.6143 | 278.6457 | 8.4142 | 56.4212 | 17.1926 | 184 | 4.7583 | 119.3918 | 303.2051 | 0.017463
205 | 849.2058 | 1.7101 | 97.4554 | 112.0176 | 55.5596 | 6.5927 | 87.4176 | 9.3911 | 16.6996 | 95.7973 | 122.187 | 27.6912 | 245.2803 | 169.7067 | 271.1877 | 8.2625 | 56.4893 | 17.613 | 179 | 5.483 | 118.3293 | 303.473 | 0.024822
206 | 846.0303 | 2.2213 | 96.9785 | 113.2756 | 55.4466 | 6.7001 | 84.1597 | 9.8887 | 14.9104 | 98.4706 | 98.7585 | 29.1143 | 250.6704 | 182.9829 | 282.7826 | 8.2559 | 56.3041 | 17.9122 | 167 | 5.4463 | 126.0563 | 294.1005 | 0.019047
207 | 859.4939 | 2.5072 | 96.5677 | 113.0846 | 56.2333 | 5.9527 | 84.6319 | 9.3016 | 14.7161 | 88.8639 | 85.6667 | 30.1797 | 249.6469 | 168.9202 | 294.2165 | 8.3553 | 54.7518 | 18.3159 | 194 | 5.5484 | 131.1259 | 289.3007 | 0.0058398
208 | 862.6392 | 3.418 | 92.7915 | 113.7362 | 55.7438 | 6.4177 | 96.1366 | 8.2439 | 13.836 | 72.7251 | 85.3241 | 24.0357 | 243.787 | 167.9512 | 315.3602 | 8.3601 | 56.5946 | 18.6212 | 207 | 5.8256 | 132.1443 | 298.4188 | 0
209 | 860.9114 | 3.6211 | 67.6486 | 115.2461 | 55.4837 | 6.6648 | 96.6312 | 8.0598 | 12.999 | 72.8853 | 86.81 | 21.484 | 238.0137 | 164.8141 | 319.5845 | 8.7072 | 59.2338 | 18.5582 | 166 | 6.0684 | 108.192 | 313.7346 | 0
210 | 849.3385 | 3.927 | 54.6585 | 115.5037 | 56.294 | 5.895 | 79.5377 | 8.0135 | 13.685 | 77.834 | 84.2077 | 21.5995 | 229.3865 | 158.8922 | 315.0533 | 8.7878 | 59.1474 | 17.4022 | 179 | 6.9165 | 97.4901 | 319.2139 | 0
211 | 808.6386 | 3.7331 | 53.8353 | 114.2856 | 55.7296 | 6.4312 | 70.6916 | 8.1303 | 10.616 | 57.4982 | 74.6395 | 18.358 | 215.1934 | 146.5609 | 299.7652 | 8.8173 | 56.5682 | 16.9141 | 169 | 6.8369 | 94.8144 | 318.7754 | 0
212 | 792.07 | 3.6967 | 53.3563 | 112.4044 | 56.2432 | 5.9433 | 68.4194 | 7.9126 | 10.071 | 43.3041 | 69.4631 | 18.0572 | 203.4965 | 135.3525 | 290.832 | 8.8257 | 54.7809 | 16.5538 | 162 | 6.3281 | 93.1324 | 313.581 | 0
213 | 785.9989 | 3.8492 | 52.7879 | 110.6589 | 55.7161 | 6.444 | 70.5694 | 7.6033 | 7.796 | 41.5613 | 69.5353 | 24.0154 | 200.1891 | 128.5312 | 276.5606 | 8.9036 | 54.4672 | 15.5993 | 158 | 6.2414 | 89.2396 | 313.9785 | 0
214 | 778.5162 | 3.7652 | 52.6791 | 109.7684 | 56.2683 | 5.9194 | 70.3403 | 7.7666 | 6.0435 | 40.7631 | 68.5709 | 23.3356 | 187.0154 | 118.6106 | 253.5511 | 8.8549 | 54.3702 | 14.4965 | 160 | 6.3481 | 88.0496 | 311.0522 | 0
215 | 774.8386 | 3.1161 | 52.5767 | 112.4066 | 55.76 | 6.4023 | 68.0994 | 7.4977 | 7.1545 | 39.3401 | 65.4884 | 16.2651 | 179.0446 | 110.6564 | 233.9981 | 8.8296 | 54.454 | 13.737 | 147 | 6.2314 | 84.7972 | 305.0695 | 0
216 | 754.4008 | 1.9407 | 52.6953 | 112.0116 | 55.4992 | 6.65 | 67.2723 | 7.3432 | 7.9719 | 38.9208 | 62.6691 | 10.883 | 173.3552 | 105.6173 | 233.0287 | 8.8468 | 53.9631 | 13.1363 | 130 | 5.7101 | 78.9525 | 300.5813 | 0
217 | 768.0441 | 1.5157 | 52.179 | 111.3264 | 56.2791 | 5.9091 | 75.7226 | 7.3257 | 10.647 | 39.107 | 61.8435 | 8.8154 | 172.8823 | 99.5008 | 234.0224 | 8.9454 | 53.4598 | 12.0224 | 123 | 5.0673 | 75.6123 | 305.7925 | 0
218 | 767.6882 | 1.6629 | 51.5485 | 110.9652 | 55.0257 | 7.0999 | 74.7788 | 7.4058 | 11.823 | 38.9759 | 61.9064 | 8.414 | 175.5259 | 98.6621 | 231.7352 | 8.9071 | 53.4579 | 11.4637 | 117 | 5.4949 | 74.2717 | 300.6375 | 0
219 | 767.6846 | 1.8946 | 50.4485 | 112.4867 | 52.9606 | 9.0617 | 69.6127 | 7.2591 | 9.82 | 38.5852 | 62.1891 | 8.3576 | 175.402 | 94.6614 | 233.4011 | 8.893 | 53.4115 | 11.3684 | 128 | 7.3331 | 68.7478 | 304.6921 | 0
220 | 768.5973 | 1.9723 | 50.0538 | 112.3169 | 52.503 | 9.4965 | 68.2187 | 7.0993 | 7.5253 | 39.5619 | 63.0879 | 8.355 | 174.7342 | 92.2115 | 238.4113 | 8.8486 | 53.3665 | 11.3563 | 107 | 6.6714 | 62.5797 | 300.4566 | 0
221 | 740.6547 | 2.711 | 48.9392 | 111.3753 | 53.2626 | 8.7749 | 76.4684 | 7.0494 | 8.6663 | 39.8384 | 63.364 | 8.3435 | 174.0487 | 91.9003 | 237.202 | 8.8376 | 55.1621 | 11.3507 | 107 | 6.8665 | 60.6444 | 292.1924 | 0
222 | 738.7523 | 3.2679 | 48.4704 | 111.4173 | 54.2176 | 7.8675 | 75.8552 | 6.9484 | 8.1704 | 48.7402 | 63.5838 | 8.3487 | 172.4283 | 91.9232 | 225.435 | 8.9552 | 57.6933 | 11.3769 | 108 | 5.366 | 60.6239 | 293.3533 | 0
223 | 756.405 | 3.4131 | 58.9223 | 111.5563 | 54.4864 | 7.6123 | 69.5577 | 7.1024 | 7.589 | 63.6535 | 63.9448 | 8.3344 | 175.4546 | 93.4462 | 224.0972 | 8.9685 | 55.1727 | 11.3575 | 114 | 4.7798 | 60.4081 | 291.422 | 0
224 | 769.1447 | 3.553 | 76.2773 | 112.2465 | 53.7595 | 8.3028 | 69.22 | 7.0534 | 11.227 | 66.5929 | 65.1765 | 9.6768 | 185.0514 | 102.4058 | 228.1149 | 8.948 | 54.4695 | 11.9999 | 111 | 5.0782 | 60.6798 | 285.3174 | 0
225 | 790.9596 | 3.3076 | 87.2298 | 113.0993 | 55.0317 | 7.0942 | 79.1786 | 6.7451 | 13.035 | 65.7551 | 65.8405 | 15.4439 | 198.3007 | 121.7421 | 230.8989 | 8.6811 | 53.8852 | 13.704 | 142 | 4.4617 | 65.008 | 278.6643 | 0
226 | 787.6748 | 1.9754 | 89.8243 | 114.5387 | 56.2391 | 5.9471 | 81.1809 | 6.4104 | 13.707 | 68.6599 | 67.0454 | 21.097 | 212.991 | 133.2594 | 246.2873 | 8.5464 | 52.6977 | 14.7376 | 169 | 4.0001 | 72.4542 | 274.0509 | 0.0097349
227 | 823.9869 | 1.5238 | 89.6931 | 115.6742 | 55.7133 | 6.4467 | 83.2816 | 6.1293 | 14.986 | 79.3384 | 77.2994 | 19.4331 | 226.4185 | 143.7396 | 262.6835 | 8.4236 | 54.8812 | 15.835 | 182 | 3.8631 | 80.6362 | 274.6974 | 0.02687
228 | 851.0513 | 1.8004 | 89.6423 | 116.4757 | 55.502 | 6.6474 | 87.2012 | 6.0497 | 16.2995 | 84.5815 | 84.8812 | 13.7201 | 239.5491 | 158.0176 | 277.3062 | 8.4173 | 56.8037 | 17.5929 | 178 | 3.75 | 86.9792 | 279.3135 | 0.022461
229 | 845.8238 | 1.8277 | 90.7102 | 114.0957 | 55.5735 | 6.5795 | 93.7326 | 6.3715 | 17.149 | 74.6211 | 100.4621 | 14.1428 | 246.8446 | 163.3466 | 294.1078 | 8.444 | 57.8687 | 18.078 | 184 | 3.7484 | 90.5846 | 283.6204 | 0.03253
230 | 834.8353 | 2.9491 | 92.156 | 113.8242 | 56.2204 | 5.965 | 92.4255 | 6.2435 | 17.5503 | 63.3538 | 111.183 | 16.5505 | 249.7555 | 165.2929 | 294.8468 | 8.4823 | 57.1519 | 18.1907 | 183 | 3.7834 | 95.1367 | 291.4247 | 0.015594
231 | 832.5914 | 3.6762 | 92.0296 | 116.0649 | 55.6963 | 6.4628 | 86.471 | 6.0901 | 17.2812 | 60.0134 | 98.459 | 17.5399 | 245.2121 | 168.8668 | 292.3648 | 8.4344 | 55.2135 | 19.2159 | 181 | 3.8349 | 98.4227 | 283.193 | 0.0045611
232 | 835.2011 | 4.4919 | 88.2972 | 119.633 | 56.2304 | 5.9554 | 79.2568 | 6.2161 | 16.57 | 60.3093 | 90.6928 | 18.7776 | 237.8844 | 162.9069 | 303.9449 | 8.4951 | 54.814 | 19.882 | 184 | 3.9286 | 97.0513 | 284.1365 | 0
233 | 847.1764 | 4.0442 | 65.9365 | 126.9765 | 55.7665 | 6.3961 | 90.7735 | 6.4129 | 16.274 | 66.2536 | 92.7903 | 17.3775 | 234.8153 | 167.5227 | 315.6558 | 8.834 | 56.001 | 20.2581 | 192 | 4.4598 | 96.516 | 289.7796 | 0
234 | 832.0144 | 3.8531 | 56.3841 | 123.8158 | 55.5451 | 6.6065 | 88.8894 | 6.5169 | 16.586 | 67.9498 | 91.4842 | 15.5225 | 227.6814 | 155.8326 | 325.2514 | 8.9755 | 57.232 | 19.7821 | 165 | 4.6497 | 93.4352 | 295.0309 | 0
235 | 818.7958 | 4.0235 | 55.9112 | 118.0392 | 56.1869 | 5.9968 | 75.1958 | 6.6981 | 16.695 | 59.7274 | 91.0969 | 14.2996 | 218.5766 | 145.7841 | 318.6282 | 8.9908 | 56.9704 | 18.9399 | 141 | 4.6653 | 92.6453 | 300.5418 | 0
236 | 813.446 | 4.3178 | 53.3371 | 116.0147 | 56.5782 | 5.625 | 72.9819 | 6.7778 | 14.468 | 48.7559 | 87.3162 | 13.8995 | 211.4643 | 136.1406 | 295.4707 | 9.0409 | 57.0528 | 17.1419 | 131 | 4.6695 | 90.4652 | 300.2156 | 0
237 | 778.2984 | 3.9417 | 49.6635 | 115.7959 | 55.7113 | 6.4486 | 75.6222 | 6.6769 | 11.532 | 45.7715 | 74.6933 | 10.122 | 205.0417 | 128.9497 | 253.5947 | 8.937 | 56.1599 | 15.9417 | 131 | 4.6731 | 87.4915 | 293.5252 | 0
238 | 752.2405 | 3.6498 | 48.6212 | 113.9063 | 56.2845 | 5.904 | 69.8955 | 6.7337 | 7.3076 | 46.1477 | 69.3491 | 8.0477 | 201.6847 | 119.6808 | 247.0435 | 8.9025 | 55.2025 | 14.7056 | 127 | 4.7154 | 78.8223 | 294.4137 | 0
239 | 741.9872 | 3.0963 | 48.3955 | 112.649 | 55.749 | 6.4128 | 66.7406 | 6.7547 | 5.5942 | 46.1914 | 67.8491 | 7.8172 | 192.4862 | 108.8955 | 251.0966 | 8.969 | 55.2228 | 13.8437 | 124 | 4.7443 | 73.4503 | 298.133 | 0
240 | 715.9294 | 2.0692 | 48.1127 | 111.9441 | 56.1982 | 5.986 | 72.0973 | 6.6878 | 5.4152 | 44.9121 | 64.1006 | 7.6804 | 181.7246 | 104.2802 | 247.5975 | 8.8782 | 54.6614 | 13.7216 | 107 | 5.1596 | 72.6495 | 295.7152 | 0
241 | 712.1303 | 1.8532 | 48.2178 | 111.572 | 55.7561 | 6.4061 | 73.8681 | 6.6543 | 5.4739 | 44.2602 | 62.1518 | 7.8157 | 177.1726 | 99.6994 | 249.6095 | 8.852 | 53.9618 | 13.2965 | 105 | 5.1123 | 72.3699 | 288.1074 | 0
242 | 717.0218 | 1.5233 | 48.0269 | 112.3424 | 56.2507 | 5.9361 | 68.5284 | 6.9156 | 5.328 | 43.2345 | 61.8203 | 7.6832 | 177.5094 | 97.1342 | 249.4711 | 8.8831 | 53.5168 | 12.6529 | 98 | 4.6715 | 69.8063 | 291.6889 | 0
243 | 718.4766 | 1.5253 | 47.6876 | 113.3449 | 55.7372 | 6.4239 | 66.2301 | 6.8919 | 5.607 | 42.0378 | 62.0785 | 7.9487 | 174.6327 | 97.4495 | 245.4142 | 8.9493 | 53.4913 | 12.0725 | 118 | 4.57 | 68.7157 | 292.8719 | 0
244 | 712.147 | 1.8572 | 48.1075 | 110.7621 | 54.8188 | 7.2965 | 72.1526 | 6.76 | 5.8385 | 44.8194 | 62.7012 | 8.1408 | 174.0717 | 105.4717 | 238.3802 | 8.8583 | 53.1923 | 11.4376 | 101 | 4.4526 | 71.2235 | 294.9438 | 0
245 | 712.0412 | 2.6248 | 48.8019 | 111.3129 | 55.1878 | 6.9459 | 74.4019 | 6.7867 | 5.9317 | 54.6243 | 62.968 | 8.0294 | 173.0264 | 115.7032 | 230.7301 | 8.7788 | 54.8614 | 11.2219 | 98 | 4.4667 | 69.5377 | 309.9295 | 0
246 | 727.0861 | 3.6575 | 48.9773 | 113.913 | 54.7351 | 7.376 | 68.8382 | 6.7805 | 7.1288 | 69.3732 | 63.2111 | 9.5087 | 178.3875 | 121.5662 | 236.0832 | 8.9169 | 57.479 | 11.2349 | 103 | 4.7135 | 75.9539 | 325.0941 | 0
247 | 758.0665 | 5.1429 | 58.6105 | 119.8517 | 53.7053 | 8.3543 | 73.7065 | 6.7957 | 10.696 | 98.7334 | 85.8926 | 19.5519 | 228.8218 | 184.3968 | 306.6303 | 12.2886 | 55.6776 | 12.4838 | 186 | 6.214 | 113.4064 | 369.3029 | 0
248 | 827.829 | 6.5283 | 88.5947 | 130.6873 | 49.8481 | 12.0186 | 104.9513 | 8.5161 | 16.644 | 116.0232 | 113.2205 | 36.054 | 282.5515 | 241.2299 | 392.8485 | 26.1766 | 59.8163 | 14.3874 | 291 | 8.5966 | 152.7777 | 435.3671 | 0
249 | 921.5803 | 7.4478 | 110.2303 | 143.2056 | 46.3954 | 15.2986 | 123.9955 | 10.5741 | 21.2942 | 117.0337 | 130.3848 | 43.084 | 338.5064 | 289.7895 | 459.2923 | 36.7471 | 70.3312 | 17.4317 | 330 | 9.6278 | 180.4905 | 487.2579 | 0
250 | 1003.2196 | 10.1649 | 117.884 | 145.8041 | 44.625 | 16.9806 | 125.0648 | 10.9252 | 22.1497 | 112.3528 | 142.1887 | 42.1882 | 383.3645 | 326.6015 | 522.5353 | 42.9333 | 79.5457 | 18.6101 | 376 | 8.7595 | 211.6267 | 508.1449 | 0.009354
251 | 1047.4711 | 12.2801 | 120.2185 | 149.0812 | 44.4508 | 17.1461 | 126.9237 | 10.8665 | 19.9891 | 116.817 | 148.7714 | 42.4267 | 407.5251 | 354.6097 | 562.0333 | 45.5518 | 88.5078 | 19.3896 | 371 | 9.0409 | 225.0611 | 513.4005 | 0.018211
252 | 1098.7512 | 11.9149 | 124.2678 | 148.4635 | 45.3722 | 16.2707 | 139.366 | 11.7548 | 18.126 | 114.6509 | 151.6724 | 42.4964 | 418.8089 | 364.0643 | 597.931 | 44.3182 | 92.6598 | 19.7885 | 337 | 11.2304 | 222.4165 | 515.4194 | 0.022665
253 | 1102.3068 | 7.9381 | 120.8326 | 147.7766 | 45.3438 | 16.2977 | 136.2428 | 11.6316 | 18.421 | 108.2836 | 150.8656 | 42.3308 | 421.0331 | 377.2222 | 614.2741 | 45.9106 | 91.2927 | 19.6535 | 339 | 11.4947 | 223.6807 | 503.8457 | 0.022367
254 | 1124.6947 | 5.9463 | 118.7041 | 149.0488 | 45.5215 | 16.1289 | 129.5506 | 10.861 | 20.956 | 120.4573 | 151.9331 | 42.9371 | 423.7395 | 389.189 | 593.8441 | 47.9487 | 89.4698 | 19.3567 | 301 | 11.4821 | 225.4785 | 507.7328 | 0.021797
255 | 1098.5227 | 6.9038 | 116.737 | 151.2548 | 45.5536 | 16.0984 | 132.9816 | 10.4817 | 21.994 | 110.6261 | 157.5615 | 43.5588 | 432.9782 | 381.7451 | 576.4611 | 46.1409 | 88.3615 | 19.6175 | 286 | 11.2888 | 223.6837 | 521.2578 | 0.006191
256 | 1079.6626 | 7.6182 | 114.7905 | 152.6711 | 45.5742 | 16.0788 | 133.4985 | 10.8508 | 21.9906 | 104.4763 | 154.6783 | 45.9625 | 414.4021 | 358.8017 | 560.1588 | 43.4633 | 87.8837 | 19.7315 | 275 | 10.3838 | 220.0842 | 508.8257 | 0
257 | 1046.3732 | 7.3833 | 110.2223 | 149.1635 | 51.4267 | 10.5189 | 125.4592 | 10.2868 | 21.767 | 104.8671 | 151.3807 | 44.4648 | 385.7324 | 335.1909 | 516.0264 | 35.6952 | 86.1685 | 19.7327 | 251 | 9.7956 | 206.5944 | 460.9906 | 0
258 | 986.5633 | 6.144 | 104.0443 | 138.3005 | 55.6657 | 6.4919 | 117.1163 | 8.3141 | 20.0604 | 98.7716 | 146.7065 | 41.9975 | 335.3071 | 273.6785 | 433.1889 | 19.6732 | 80.9346 | 18.7126 | 229 | 7.7827 | 185.927 | 391.525 | 0
259 | 940.9283 | 5.0399 | 100.6951 | 125.949 | 56.5089 | 5.6909 | 108.6551 | 6.9091 | 15.9943 | 81.9017 | 122.8042 | 33.341 | 277.2351 | 215.937 | 379.6629 | 12.8821 | 75.5803 | 17.7631 | 221 | 7.0623 | 172.1078 | 341.7604 | 0
260 | 900.8755 | 4.1779 | 89.9752 | 117.7454 | 55.7957 | 6.3684 | 79.7125 | 6.2439 | 13.6472 | 56.166 | 98.8554 | 22.9236 | 237.9678 | 183.9773 | 342.2559 | 12.238 | 69.4471 | 17.0585 | 192 | 7.1831 | 145.5948 | 299.1238 | 0
261 | 862.6271 | 4.3155 | 70.7054 | 113.8458 | 54.7274 | 7.3833 | 65.2792 | 6.1014 | 10.0685 | 45.8219 | 92.5463 | 20.0685 | 217.331 | 154.0159 | 296.3723 | 10.9493 | 61.8071 | 16.179 | 173 | 6.657 | 130.8439 | 273.7113 | 0
262 | 835.2148 | 4.0792 | 63.6593 | 109.4703 | 55.9743 | 6.1987 | 70.8412 | 6.1861 | 7.362 | 43.9064 | 89.5551 | 17.0399 | 196.1649 | 130.0189 | 260.8017 | 10.3305 | 56.4763 | 15.4131 | 160 | 6.0718 | 125.9029 | 274.748 | 0
263 | 813.6166 | 3.4235 | 63.2336 | 106.0334 | 56.4287 | 5.767 | 74.7309 | 6.2235 | 6.3131 | 39.2545 | 77.0058 | 10.0671 | 186.518 | 120.4789 | 253.6503 | 10.3001 | 54.7893 | 14.6234 | 144 | 5.8927 | 117.8959 | 268.5963 | 0
264 | 794.1914 | 2.5595 | 63.195 | 104.9931 | 56.4521 | 5.7448 | 67.0826 | 6.2127 | 6.2624 | 36.0404 | 70.0878 | 7.5358 | 182.9625 | 112.531 | 268.3158 | 10.1993 | 54.5919 | 13.7246 | 126 | 5.8609 | 91.0073 | 265.0619 | 0
265 | 796.1099 | 1.9011 | 61.8786 | 105.7091 | 54.9823 | 7.1411 | 63.5231 | 6.3831 | 6.3013 | 35.7095 | 69.02 | 7.7285 | 183.3791 | 105.9586 | 275.8456 | 10.2538 | 54.4667 | 12.7953 | 111 | 6.2698 | 77.0272 | 265.3101 | 0
266 | 794.4007 | 2.1174 | 57.7062 | 107.1793 | 55.221 | 6.9144 | 71.3508 | 6.2876 | 6.2613 | 35.3743 | 69.3634 | 7.6078 | 186.8165 | 104.2074 | 260.3133 | 10.1769 | 54.4187 | 12.3997 | 104 | 6.032 | 73.9888 | 262.8574 | 0
267 | 782.0789 | 1.814 | 56.5827 | 106.8542 | 55.5814 | 6.572 | 73.1175 | 6.1781 | 6.4363 | 35.8515 | 71.6808 | 7.5362 | 187.7007 | 103.2402 | 249.3571 | 10.1038 | 54.4649 | 12.315 | 125 | 5.8904 | 70.0691 | 261.8791 | 0
268 | 785.0176 | 1.9214 | 56.5403 | 106.5347 | 56.2546 | 5.9325 | 66.5222 | 6.2552 | 6.467 | 38.7239 | 73.5596 | 7.6289 | 187.643 | 107.0593 | 250.667 | 10.1607 | 54.6676 | 11.9887 | 104 | 5.9493 | 67.2938 | 262.1656 | 0
269 | 782.8998 | 2.034 | 56.5608 | 105.5297 | 55.735 | 6.4261 | 63.6674 | 6.3343 | 6.4858 | 49.9815 | 72.3862 | 7.6185 | 187.0914 | 116.2796 | 247.6833 | 10.2308 | 56.4511 | 11.6964 | 102 | 5.9466 | 67.1165 | 282.3865 | 0
270 | 788.0059 | 3.4306 | 57.4557 | 105.6778 | 55.4633 | 6.6842 | 72.6952 | 6.505 | 6.2707 | 65.8862 | 68.794 | 9.2775 | 193.8506 | 125.4417 | 243.0141 | 10.1651 | 59.0162 | 11.5897 | 105 | 6.0975 | 71.8983 | 308.5003 | 0
271 | 816.4504 | 5.0402 | 62.4623 | 113.4874 | 53.9402 | 8.1311 | 84.5635 | 6.3626 | 7.8498 | 92.8855 | 83.5683 | 17.2808 | 217.9609 | 182.4956 | 264.8131 | 13.6716 | 57.8274 | 11.9791 | 184 | 8.2724 | 107.1738 | 349.0614 | 0
272 | 877.317 | 6.4753 | 80.8946 | 122.4084 | 48.9167 | 12.9035 | 103.2818 | 8.0225 | 15.8057 | 111.5602 | 114.6288 | 34.1365 | 273.955 | 234.2761 | 381.1224 | 29.422 | 61.5438 | 13.0338 | 291 | 10.9624 | 154.0908 | 420.1418 | 0
273 | 990.5732 | 7.6803 | 101.4447 | 137.5739 | 45.9859 | 15.6877 | 119.2249 | 9.3391 | 19.765 | 111.5087 | 137.2474 | 39.9559 | 343.1952 | 286.8193 | 486.9316 | 38.5934 | 70.7668 | 18.0653 | 335 | 10.8608 | 194.5163 | 468.5122 | 0
274 | 1086.7634 | 7.9902 | 108.0606 | 144.7304 | 46.1645 | 15.518 | 137.6424 | 10.3784 | 20.3763 | 107.8307 | 150.6727 | 42.9038 | 389.0205 | 330.5307 | 550.6748 | 42.7245 | 81.5856 | 19.0363 | 353 | 11.0377 | 221.2197 | 515.3199 | 0.0068245
275 | 1153.4211 | 8.0958 | 107.5906 | 148.7958 | 45.0998 | 16.5295 | 134.6256 | 10.6128 | 20.794 | 110.0569 | 156.361 | 45.0941 | 399.7735 | 377.9448 | 572.1552 | 45.2964 | 88.6236 | 19.3299 | 360 | 7.7471 | 229.2147 | 535.9464 | 0.013353
276 | 1175.2027 | 7.6788 | 108.0193 | 149.9416 | 45.8533 | 15.8137 | 130.1059 | 10.7135 | 21.5195 | 116.1778 | 164.0687 | 44.2159 | 401.246 | 385.3601 | 584.0188 | 44.365 | 92.4458 | 22.005 | 356 | 8.4123 | 223.5847 | 541.4789 | 0.014886
277 | 1167.3722 | 7.5861 | 105.9441 | 149.7217 | 44.275 | 17.313 | 142.4118 | 10.9882 | 21.2512 | 109.7883 | 165.2882 | 42.9527 | 401.5463 | 379.5388 | 594.4774 | 43.5007 | 91.9363 | 20.8665 | 369 | 8.4744 | 218.7148 | 541.7488 | 0.01541
278 | 1160.8751 | 5.6011 | 107.5889 | 150.1497 | 42.0407 | 19.4356 | 135.2092 | 11.0936 | 23.4132 | 108.4879 | 173.3003 | 42.8714 | 404.2525 | 365.47 | 603.382 | 46.1625 | 92.3526 | 20.2948 | 317 | 6.6121 | 219.1495 | 550.431 | 0.022219
279 | 1146.3342 | 9.461 | 109.6311 | 151.3182 | 45.3993 | 16.245 | 126.3693 | 11.3799 | 25.1785 | 105.4801 | 171.7558 | 43.687 | 398.6016 | 369.7983 | 597.9392 | 48.0862 | 90.9812 | 20.3839 | 317 | 5.4113 | 223.1455 | 535.2112 | 0.0053941
280 | 1142.5257 | 12.6995 | 110.0763 | 148.3764 | 46.4034 | 15.2911 | 131.5927 | 11.0384 | 25.3523 | 107.9501 | 168.0516 | 46.0715 | 411.6847 | 357.3941 | 594.8985 | 45.6836 | 88.0486 | 20.0365 | 272 | 4.7163 | 225.8638 | 520.3855 | 0
281 | 1103.585 | 11.0834 | 106.7352 | 147.0853 | 52.5944 | 9.4096 | 124.6798 | 10.5827 | 25.4806 | 109.8283 | 166.7191 | 45.099 | 385.245 | 337.6586 | 571.6134 | 36.3425 | 85.165 | 19.9052 | 242 | 3.1753 | 212.7639 | 486.9651 | 0
282 | 1034.2062 | 8.0851 | 102.0674 | 131.7797 | 55.2909 | 6.848 | 105.2649 | 8.0858 | 23.5854 | 98.6233 | 159.2874 | 41.2786 | 342.2616 | 274.5976 | 493.0751 | 19.6369 | 78.947 | 19.1722 | 208 | 0.83763 | 182.1228 | 399.2435 | 0
283 | 976.6257 | 5.5342 | 100.0183 | 117.8372 | 55.5573 | 6.5949 | 93.2525 | 6.4971 | 17.724 | 76.6085 | 133.2578 | 31.1449 | 303.9126 | 217.8162 | 436.5718 | 12.4642 | 71.0385 | 17.3537 | 205 | -0.26069 | 168.2124 | 355.8975 | 0
284 | 930.4294 | 4.629 | 90.8643 | 112.2082 | 54.7051 | 7.4045 | 75.1721 | 6.1541 | 14.443 | 53.1547 | 106.9632 | 14.9155 | 265.1373 | 187.3246 | 398.2171 | 11.3999 | 64.8038 | 16.1381 | 187 | -0.39371 | 152.6961 | 320.2163 | 0
285 | 886.0944 | 3.8394 | 71.0789 | 112.1183 | 54.4516 | 7.6453 | 61.4662 | 6.3217 | 12.3733 | 48.1773 | 98.4256 | 8.8977 | 228.8121 | 175.1756 | 355.2592 | 10.19 | 58.96 | 15.3639 | 174 | -0.43523 | 143.6528 | 294.8859 | 0
286 | 849.1277 | 3.4969 | 64.1338 | 113.4482 | 54.5273 | 7.5734 | 58.5024 | 6.5001 | 8.6683 | 48.0211 | 91.5386 | 8.2875 | 201.8188 | 152.961 | 320.0908 | 9.8331 | 56.7649 | 15.0967 | 158 | -0.43281 | 138.1413 | 293.2582 | 0
287 | 815.0081 | 3.0242 | 63.701 | 110.88 | 56.046 | 6.1306 | 67.4933 | 6.6401 | 6.633 | 40.6219 | 76.8183 | 7.7003 | 196.9965 | 140.4351 | 298.9761 | 9.6519 | 55.906 | 14.9757 | 136 | -0.39757 | 133.4838 | 288.5524 | 0
288 | 784.0847 | 2.3611 | 60.4101 | 110.354 | 55.7862 | 6.3774 | 61.907 | 7.0294 | 6.353 | 37.173 | 70.4117 | 7.4402 | 193.2714 | 134.3592 | 267.4239 | 9.692 | 55.6127 | 14.3619 | 117 | -0.19149 | 97.8011 | 287.3098 | 0
289 | 779.0998 | 1.729 | 57.6286 | 111.3503 | 56.2216 | 5.9638 | 56.7305 | 7.1005 | 6.3772 | 37.4719 | 70.2227 | 7.3914 | 185.8612 | 127.2252 | 248.2565 | 9.6311 | 55.2645 | 13.4556 | 112 | -0.28423 | 87.7142 | 301.9489 | 0
290 | 766.2913 | 1.3321 | 56.9915 | 112.7368 | 55.7055 | 6.4541 | 58.098 | 7.1575 | 6.3585 | 37.9936 | 69.3283 | 7.3949 | 182.5328 | 121.0054 | 239.6386 | 9.6627 | 55.2549 | 12.8834 | 110 | -0.39994 | 83.4442 | 304.9755 | 0
291 | 757.8401 | 1.3104 | 56.8457 | 111.4834 | 56.2477 | 5.939 | 65.1081 | 7.2491 | 6.3213 | 38.0542 | 69.2403 | 7.3609 | 181.3257 | 117.597 | 233.638 | 9.5809 | 55.1608 | 12.6586 | 127 | -0.40074 | 78.9209 | 297.3215 | 0
292 | 756.5077 | 1.7608 | 56.9336 | 109.0391 | 55.722 | 6.4384 | 60.3126 | 7.2909 | 6.1461 | 39.6597 | 69.8406 | 7.3395 | 190.1743 | 117.4755 | 231.9076 | 9.539 | 55.1055 | 12.6003 | 107 | -0.38695 | 76.8846 | 292.4168 | 0
293 | 754.2539 | 2.0886 | 57.7933 | 107.672 | 55.5092 | 6.6406 | 56.6144 | 7.4794 | 6.2525 | 50.3719 | 70.1793 | 7.3501 | 195.5863 | 116.8637 | 235.6335 | 9.4966 | 56.8233 | 12.4688 | 104 | -0.38079 | 77.1017 | 309.8208 | 0
294 | 770.4992 | 3.4336 | 58.1073 | 108.4583 | 55.4854 | 6.6632 | 58.6372 | 7.5462 | 7.8235 | 65.7211 | 71.359 | 9.9304 | 210.2296 | 122.5145 | 244.0623 | 9.5952 | 58.9148 | 12.273 | 108 | -0.012546 | 79.7348 | 342.9716 | 0
295 | 807.9933 | 4.428 | 64.0279 | 115.046 | 53.1937 | 8.8403 | 77.7754 | 7.5707 | 13.3077 | 94.9357 | 86.8622 | 18.7383 | 237.5291 | 182.3981 | 289.6407 | 12.606 | 57.3795 | 12.589 | 186 | 0.9831 | 119.4081 | 382.5269 | 0
296 | 858.8677 | 5.9836 | 86.6821 | 119.7603 | 48.013 | 13.762 | 104.6719 | 8.5378 | 20.3785 | 116.1645 | 121.6788 | 36.9658 | 276.8205 | 243.0375 | 387.1134 | 25.6669 | 63.0032 | 13.369 | 265 | 2.8282 | 163.0745 | 452.5211 | 0
297 | 947.6709 | 6.6187 | 105.9096 | 129.913 | 45.651 | 16.0059 | 119.3641 | 11.0726 | 24.3512 | 115.6008 | 143.8114 | 45.1704 | 314.4488 | 295.8427 | 467.5818 | 36.5731 | 73.9087 | 15.5282 | 258 | 3.3099 | 194.1603 | 506.574 | 0
298 | 1021.4383 | 5.6684 | 116.2626 | 135.9593 | 45.3646 | 16.278 | 122.3964 | 11.8629 | 24.5183 | 109.6242 | 147.2037 | 45.3992 | 367.1379 | 354.7897 | 518.8128 | 42.1503 | 81.8068 | 17.2326 | 331 | 3.3702 | 214.811 | 533.3067 | 0.016718
299 | 1085.8482 | 4.151 | 123.5065 | 140.4337 | 46.4069 | 15.2878 | 127.5663 | 12.0881 | 23.9934 | 107 | 144.2204 | 45.2654 | 400.8594 | 390.3124 | 541.1211 | 44.4064 | 87.5238 | 20.7873 | 333 | 3.7445 | 235.9262 | 537.7375 | 0.038404
300 | 1095.2988 | 3.6202 | 115.1178 | 140.4941 | 45.7124 | 15.9475 | 130.3218 | 12.1012 | 23.5294 | 107.7025 | 158.8064 | 43.4225 | 410.7934 | 402.5734 | 550.703 | 43.1113 | 89.7201 | 19.7734 | 330 | 3.6074 | 234.8489 | 538.5996 | 0.051045
301 | 1088.197 | 3.7269 | 116.1713 | 137.3714 | 45.4713 | 16.1766 | 124.659 | 12.2314 | 22.2935 | 106.4318 | 162.7743 | 43.742 | 406.7843 | 399.3484 | 562.6041 | 45.3167 | 89.1156 | 18.6305 | 345 | 3.3924 | 224.9525 | 532.3421 | 0.044551
302 | 1107.8664 | 5.6282 | 115.8561 | 138.1597 | 43.8978 | 17.6714 | 123.4395 | 12.702 | 23.2288 | 114.829 | 163.518 | 45.5824 | 470.4863 | 397.156 | 557.2243 | 45.9821 | 89.5614 | 18.8773 | 303 | 3.5751 | 225.062 | 560.7515 | 0.031124
303 | 1126.3732 | 11.8126 | 109.2209 | 141.4016 | 45.8963 | 15.7728 | 130.5001 | 13.0108 | 24.1212 | 113.2476 | 167.7544 | 45.2111 | 504.0604 | 400.9423 | 555.2141 | 44.4763 | 86.5432 | 19.0874 | 294 | 3.8062 | 224.7396 | 541.6873 | 0.019477
304 | 1124.5849 | 15.2204 | 108.6706 | 140.3635 | 43.4337 | 18.1123 | 115.7032 | 11.8958 | 23.572 | 109.8267 | 169.1098 | 46.1434 | 515.805 | 369.842 | 548.6763 | 40.0866 | 83.7609 | 19.4218 | 253 | 3.4179 | 222.8316 | 518.2488 | 0
305 | 1090.0022 | 11.7036 | 107.6283 | 138.6895 | 48.6865 | 13.1221 | 99.7821 | 10.623 | 22.9703 | 111.8524 | 166.8058 | 44.7964 | 504.265 | 333.219 | 523.6366 | 34.2594 | 81.8655 | 19.266 | 238 | 2.3045 | 209.6359 | 494.2171 | 0
306 | 1022.4954 | 8.3748 | 101.0252 | 129.2354 | 53.5907 | 8.4631 | 88.5246 | 9.2855 | 20.9838 | 105.7917 | 159.7233 | 43.351 | 449.3128 | 262.6404 | 452.7408 | 21.5467 | 77.5377 | 18.244 | 233 | 1.0204 | 183.1175 | 423.0459 | 0
307 | 966.7078 | 5.5972 | 92.8503 | 119.884 | 55.2402 | 6.8962 | 73.088 | 8.0577 | 16.5018 | 85.062 | 133.9561 | 35.0432 | 398.4986 | 194.7103 | 406.2003 | 13.3937 | 72.1796 | 16.9393 | 231 | 0.56504 | 162.8004 | 384.9761 | 0
308 | 926.4893 | 3.9225 | 75.8038 | 114.812 | 56.2343 | 5.9518 | 59.5572 | 7.7445 | 14.7763 | 58.7493 | 108.2923 | 23.6298 | 371.2534 | 163.8905 | 368.4271 | 10.9791 | 67.22 | 15.6464 | 203 | 0.37095 | 141.8256 | 335.5598 | 0
309 | 881.3779 | 3.8082 | 70.1155 | 110.4969 | 55.7612 | 6.4011 | 55.0318 | 8.1562 | 13.5763 | 52.8219 | 100.4761 | 12.5675 | 347.2396 | 146.8248 | 323.1637 | 10.3616 | 60.9663 | 14.8904 | 167 | 0.33941 | 125.2955 | 307.2442 | 0
310 | 847.6856 | 3.9877 | 60.9234 | 107.6137 | 55.5499 | 6.6019 | 57.042 | 7.8697 | 9.4492 | 52.1157 | 98.6954 | 8.7711 | 332.8256 | 130.8562 | 292.9291 | 10.1552 | 57.4686 | 14.6803 | 151 | 0.13823 | 119.1898 | 304.9747 | 0
311 | 826.1026 | 3.1155 | 57.0205 | 104.4306 | 56.2529 | 5.934 | 53.6915 | 7.6002 | 6.7645 | 49.5946 | 82.8236 | 8.308 | 323.4188 | 121.2386 | 287.3467 | 10.1649 | 56.7356 | 14.3181 | 139 | 0.034379 | 115.776 | 301.1378 | 0
312 | 809.8875 | 2.1529 | 56.7594 | 103.3688 | 55.6958 | 6.4633 | 51.439 | 7.2265 | 6.0148 | 46.0541 | 73.0222 | 7.8892 | 317.134 | 117.2873 | 270.9546 | 10.0592 | 56.7889 | 13.3679 | 129 | 0.23288 | 88.173 | 301.9869 | 0
313 | 802.3286 | 1.701 | 56.6137 | 104.3615 | 55.4964 | 6.6528 | 51.3057 | 6.9089 | 5.9028 | 44.3562 | 71.4514 | 7.7393 | 308.1739 | 114.379 | 253.0969 | 10.1092 | 56.6804 | 12.9823 | 120 | -0.22267 | 75.138 | 297.042 | 0
314 | 792.7694 | 1.4112 | 56.7668 | 105.191 | 56.2777 | 5.9105 | 56.4422 | 6.9155 | 6.2297 | 44.1131 | 71.973 | 7.5382 | 298.7637 | 108.4987 | 245.09 | 10.2043 | 56.4059 | 12.8471 | 132 | 0.34204 | 72.7589 | 295.3665 | 0
315 | 785.2643 | 1.4636 | 56.6868 | 105.5815 | 55.754 | 6.4081 | 55.2191 | 6.9047 | 5.9658 | 42.2502 | 73.2871 | 7.4539 | 292.0635 | 103.0562 | 235.2927 | 10.1479 | 55.9125 | 12.7623 | 137 | 0.16391 | 72.9703 | 296.0985 | 0
316 | 786.832 | 1.379 | 56.3524 | 106.8845 | 55.4547 | 6.6924 | 53.7474 | 7.5482 | 5.9462 | 43.6981 | 72.8196 | 7.4279 | 287.3659 | 105.1035 | 230.7893 | 10.2246 | 55.5116 | 12.7242 | 113 | -0.054013 | 71.4015 | 298.0983 | 0
317 | 786.0092 | 1.8984 | 56.1082 | 108.4743 | 55.5274 | 6.6233 | 52.4267 | 7.9419 | 6.1362 | 54.8967 | 72.1996 | 7.4534 | 285.7264 | 113.8504 | 235.9904 | 10.0361 | 57.1872 | 12.436 | 103 | -0.060542 | 70.7162 | 311.4796 | 0
318 | 784.9004 | 3.1541 | 56.8518 | 108.0333 | 54.6617 | 7.4457 | 54.6411 | 8.5994 | 7.4094 | 69.6593 | 72.2425 | 8.8462 | 292.8732 | 125.6457 | 244.5813 | 10.045 | 59.4822 | 11.8269 | 107 | -0.057262 | 72.4034 | 345.5047 | 0
319 | 823.9502 | 4.7368 | 75.6493 | 114.5736 | 53.7317 | 8.3292 | 67.2431 | 8.9448 | 10.1687 | 97.0122 | 91.1394 | 20.1593 | 338.9767 | 182.042 | 280.1984 | 12.823 | 58.1812 | 11.6144 | 160 | 1.0808 | 97.7333 | 390.5719 | 0
320 | 874.338 | 6.0549 | 82.4428 | 121.9616 | 48.2209 | 13.5645 | 96.1258 | 9.5222 | 17.3903 | 121.1681 | 124.7299 | 38.0886 | 391.5416 | 233.7516 | 373.748 | 27.5983 | 62.8187 | 12.3372 | 287 | 3.0622 | 126.1591 | 458.6146 | 0
321 | 945.6656 | 6.5265 | 103.7202 | 128.9506 | 45.0313 | 16.5946 | 113.5726 | 10.9436 | 23.3876 | 123.5266 | 140.3952 | 45.2977 | 471.3152 | 273.8215 | 455.2493 | 38.4779 | 70.5868 | 14.9411 | 293 | 4.2214 | 181.0249 | 505.4278 | 0
322 | 1020.48 | 5.0213 | 115.6671 | 136.3373 | 45.1838 | 16.4497 | 115.4414 | 11.4375 | 24.9071 | 111.6628 | 151.2864 | 43.3035 | 529.592 | 312.0993 | 502.5176 | 44.8894 | 78.5137 | 15.9944 | 351 | 4.932 | 215.0142 | 520.9249 | 0.072031
323 | 1073.0378 | 4.1876 | 116.8173 | 139.4219 | 43.3125 | 18.2275 | 120.1827 | 12.2315 | 24.7265 | 120.6204 | 162.8728 | 43.2906 | 558.2394 | 338.2251 | 500.8123 | 47.2019 | 84.7804 | 17.0677 | 348 | 5.5944 | 230.9555 | 530.318 | 0.12045
324 | 1093.4013 | 4.3308 | 116.0008 | 138.0608 | 41.6339 | 19.8221 | 120.5296 | 13.081 | 24.349 | 131.9883 | 174.7773 | 43.9554 | 559.6746 | 345.4306 | 503.3332 | 45.3263 | 86.9452 | 20.1349 | 350 | 4.6656 | 228.5084 | 519.5094 | 0.15253
325 | 1095.5464 | 4.7812 | 118.902 | 139.0358 | 44.5177 | 17.0825 | 119.2541 | 13.9222 | 22.7465 | 123.0786 | 175.5013 | 42.4137 | 542.2926 | 344.6138 | 517.7094 | 44.1184 | 85.4774 | 19.228 | 367 | 3.4014 | 218.0209 | 507.672 | 0.17148
326 | 1106.2808 | 6.3787 | 119.3327 | 148.1301 | 46.2724 | 15.4155 | 120.5319 | 13.7468 | 22.6617 | 120.8944 | 174.3585 | 43.0023 | 542.3366 | 341.2711 | 534.6672 | 45.2798 | 86.2724 | 18.48 | 313 | 3.764 | 221.4728 | 510.4971 | 0.15805
327 | 1119.2267 | 7.4671 | 118.9168 | 149.6351 | 45.8635 | 15.8039 | 125.5164 | 11.6981 | 22.4658 | 117.8337 | 178.0774 | 44.0756 | 538.8818 | 336.2166 | 542.2585 | 44.9579 | 86.7861 | 18.9233 | 294 | 4.0089 | 224.0253 | 514.0957 | 0.074042
328 | 1105.6488 | 9.3954 | 117.7224 | 143.6506 | 45.4936 | 16.1554 | 123.26 | 11.8819 | 22.4892 | 113.902 | 180.7249 | 45.6016 | 525.6529 | 331.2528 | 534.88 | 41.6016 | 90.6711 | 19.2282 | 282 | 3.7412 | 217.097 | 511.6517 | 0
329 | 1066.5828 | 8.4134 | 112.1535 | 141.9018 | 46.9096 | 14.8102 | 116.7821 | 12.0129 | 22.732 | 111.6442 | 180.207 | 44.5615 | 522.1776 | 318.3826 | 524.2365 | 33.1682 | 91.0858 | 19.5924 | 273 | 2.3716 | 205.9953 | 476.7632 | 0
330 | 1016.2949 | 6.9794 | 104.1342 | 136.7094 | 53.6147 | 8.4403 | 111.7173 | 9.9799 | 21.9113 | 108.8146 | 172.2285 | 43.5105 | 490.611 | 261.1923 | 458.062 | 19.0734 | 85.498 | 19.6491 | 243 | 0.99269 | 178.3449 | 404.6468 | 0
331 | 966.2909 | 5.8145 | 101.9326 | 127.5981 | 54.7378 | 7.3734 | 98.6354 | 9.7106 | 16.959 | 102.0807 | 144.9181 | 35.2918 | 409.037 | 205.7968 | 379.4855 | 12.2766 | 77.4249 | 18.6942 | 230 | 0.60517 | 163.0638 | 362.0943 | 0
332 | 927.1081 | 4.508 | 92.3073 | 120.1994 | 55.2451 | 6.8915 | 72.0307 | 8.8416 | 14.8064 | 98.6794 | 117.5257 | 20.8617 | 363.886 | 174.9478 | 315.4372 | 10.8688 | 70.9674 | 17.5852 | 194 | 0.61694 | 140.5009 | 322.7652 | 0
333 | 894.2768 | 4.2924 | 70.2556 | 113.2413 | 55.5052 | 6.6443 | 57.9279 | 7.8902 | 12.6844 | 98.5724 | 108.0185 | 15.7251 | 353.9414 | 153.7243 | 273.3501 | 10.5983 | 65.0328 | 15.9532 | 177 | 0.50731 | 127.0646 | 309.0553 | 0
334 | 866.0442 | 4.2191 | 63.2973 | 109.1268 | 54.7584 | 7.3539 | 55.6835 | 9.1022 | 8.6635 | 94.9539 | 103.8034 | 13.8758 | 321.0333 | 132.1841 | 247.4614 | 10.4701 | 61.17 | 15.2083 | 165 | 0.54391 | 124.1601 | 303.3598 | 0
335 | 835.7034 | 3.5441 | 63.1948 | 106.299 | 55.3 | 6.8393 | 58.0952 | 9.9103 | 7.1163 | 88.9041 | 89.0687 | 12.7294 | 226.351 | 121.4038 | 235.6486 | 10.4991 | 60.3029 | 14.1518 | 141 | 0.59216 | 118.5291 | 304.1778 | 0
336 | 816.1982 | 2.752 | 63.1044 | 107.7431 | 55.4447 | 6.7019 | 57.1267 | 8.6248 | 6.5255 | 80.1569 | 81.2007 | 9.0114 | 185.5937 | 112.4814 | 232.5384 | 10.537 | 60.2167 | 13.6652 | 129 | 0.32999 | 90.5959 | 310.4125 | 0
337 | 804.5267 | 2.1939 | 63.3114 | 107.0364 | 54.7332 | 7.3778 | 55.8007 | 9.3026 | 6.3157 | 60.6877 | 80.3889 | 7.6309 | 184.6527 | 104.9516 | 238.2215 | 10.4762 | 60.3772 | 13.5921 | 113 | 0.20365 | 79.602 | 303.0856 | 0
338 | 803.995 | 1.9532 | 63.4715 | 106.201 | 54.5274 | 7.5733 | 56.3439 | 9.875 | 6.181 | 55.6275 | 80.132 | 7.5897 | 185.2556 | 102.7046 | 242.5255 | 10.4729 | 60.3197 | 12.8437 | 111 | 0.26455 | 80.7773 | 302.2081 | 0
339 | 797.4205 | 2.1519 | 59.9781 | 106.3713 | 53.7515 | 8.3104 | 55.9999 | 9.0783 | 6.3092 | 55.9915 | 80.4921 | 7.6124 | 186.7194 | 103.5782 | 237.1691 | 10.4882 | 60.3737 | 12.5951 | 126 | 0.017702 | 79.1432 | 302.7035 | 0
340 | 797.0828 | 1.8782 | 57.2547 | 107.07 | 55.0036 | 7.1209 | 55.899 | 10.2879 | 6.0217 | 57.1187 | 81.6407 | 7.6801 | 185.34 | 104.8069 | 232.5965 | 10.7042 | 60.7339 | 12.4167 | 107 | 0.023609 | 77.46 | 306.3203 | 0
341 | 805.1435 | 2.3327 | 56.2513 | 106.9396 | 55.5046 | 6.645 | 55.429 | 9.5352 | 5.9015 | 60.1997 | 81.6617 | 7.6791 | 182.3904 | 114.8458 | 226.493 | 10.6607 | 62.2106 | 12.554 | 105 | -0.071166 | 77.6107 | 326.0219 | 0
342 | 811.4841 | 3.2945 | 58.3706 | 106.6957 | 54.781 | 7.3324 | 59.003 | 10.4728 | 7.6157 | 72.2943 | 81.5123 | 10.9624 | 189.9884 | 126.3256 | 238.1092 | 10.4282 | 64.7061 | 12.4549 | 107 | -0.04608 | 79.6621 | 354.1341 | 0
343 | 849.5263 | 4.9279 | 69.7747 | 113.618 | 53.6792 | 8.3791 | 70.2441 | 8.6181 | 11.4147 | 105.1715 | 101.5124 | 23.0122 | 212.6918 | 175.3763 | 264.1061 | 13.6875 | 63.4521 | 12.0994 | 177 | 0.93851 | 113.6674 | 390.0611 | 0
344 | 913.9491 | 6.0117 | 92.5042 | 120.1478 | 48.209 | 13.5757 | 99.4029 | 7.5441 | 18.713 | 119.183 | 137.8227 | 40.3291 | 280.5219 | 219.4195 | 337.7665 | 26.129 | 67.9837 | 12.3991 | 250 | 1.5181 | 148.1808 | 445.9894 | 0
345 | 1001.1026 | 8.9072 | 107.7871 | 128.1784 | 44.1321 | 17.4488 | 119.0215 | 14.8222 | 23.4965 | 119.8416 | 160.3087 | 47.2644 | 357.9256 | 270.743 | 434.9877 | 36.6598 | 77.1692 | 14.1766 | 309 | 1.4657 | 178.3811 | 499.6656 | 0
346 | 1069.0022 | 8.0487 | 116.6974 | 140.0293 | 43.4975 | 18.0517 | 121.5598 | 19.7143 | 24.1605 | 125.7859 | 170.8688 | 46.1952 | 392.9333 | 298.403 | 495.1044 | 43.2736 | 85.7018 | 14.5354 | 350 | 1.3961 | 202.0199 | 537.8934 | 0.12227
347 | 1101.7447 | 7.2776 | 122.3462 | 143.784 | 42.7656 | 18.747 | 121.7378 | 21.1687 | 23.7203 | 122.9693 | 175.1802 | 44.9295 | 400.7468 | 316.8071 | 508.1616 | 45.1409 | 90.4171 | 14.7079 | 345 | 1.5322 | 219.6648 | 556.1045 | 0.15517
348 | 1122.1393 | 9.1671 | 118.6508 | 143.4202 | 46.2424 | 15.444 | 124.878 | 17.2768 | 22.8447 | 116.2643 | 184.9905 | 46.1101 | 401.4794 | 328.6656 | 498.0315 | 43.5142 | 91.1468 | 15.5314 | 361 | 1.9442 | 225.4166 | 549.7454 | 0.19766
349 | 1108.0817 | 12.4799 | 122.2538 | 137.9848 | 44.2822 | 17.3062 | 120.3316 | 15.2735 | 21.1955 | 114.2596 | 180.7395 | 45.7575 | 394.3229 | 318.0393 | 496.8425 | 45.0165 | 91.3356 | 15.988 | 385 | 3.5951 | 227.5759 | 549.7619 | 0.20831
350 | 1140.8031 | 12.2033 | 122.3645 | 135.0559 | 45.1845 | 16.4491 | 114.1681 | 15.0269 | 21.1258 | 124.8375 | 178.7227 | 44.6763 | 398.4692 | 316.3604 | 501.8525 | 47.8902 | 89.9816 | 15.7595 | 330 | 3.5867 | 220.2998 | 553.2111 | 0.17477
351 | 1134.1502 | 7.4178 | 121.6313 | 139.9362 | 45.4768 | 16.1714 | 114.5622 | 14.5228 | 21.3315 | 128.6867 | 185.5752 | 44.3883 | 399.9362 | 321.4469 | 492.0883 | 47.9324 | 88.4701 | 15.6879 | 310 | 2.9123 | 215.5115 | 550.7459 | 0.088822
352 | 1105.6642 | 6.0321 | 121.6313 | 142.7289 | 45.4054 | 16.2392 | 110.7431 | 13.1862 | 21.125 | 128.3692 | 183.692 | 46.5049 | 399.2294 | 295.6201 | 479.5734 | 44.4191 | 88.8111 | 15.6796 | 273 | 2.1261 | 207.423 | 533.8355 | 0.013465
353 | 1048.1438 | 6.1813 | 111.997 | 143.9121 | 51.8 | 10.1644 | 100.1736 | 13.5805 | 21.4055 | 128.4236 | 179.019 | 46.3847 | 392.2174 | 267.3421 | 463.0931 | 28.5389 | 89.218 | 15.9901 | 261 | 1.3356 | 198.0491 | 465.5699 | 0
354 | 981.0431 | 6.1481 | 101.6288 | 132.621 | 55.0357 | 7.0904 | 83.5109 | 12.0868 | 20.9265 | 120.2685 | 169.7035 | 43.2328 | 334.0375 | 212.8719 | 395.2584 | 16.0901 | 82.4516 | 15.4461 | 224 | 0.89616 | 183.6894 | 382.4318 | 0
355 | 919.9883 | 5.3193 | 71.5815 | 119.5426 | 55.4659 | 6.6817 | 74.6588 | 9.7906 | 17.4335 | 98.6877 | 142.053 | 31.05 | 270.537 | 157.9156 | 337.3929 | 13.4213 | 72.0836 | 14.9278 | 214 | 0.64677 | 166.5744 | 321.118 | 0
356 | 877.9252 | 4.7024 | 54.1166 | 112.6777 | 54.7798 | 7.3335 | 59.0692 | 10.337 | 15.3115 | 74.1966 | 108.0876 | 15.1427 | 237.0505 | 134.7911 | 299.0977 | 13.6378 | 63.1391 | 15.2097 | 185 | 0.48184 | 147.5968 | 284.7447 | 0
357 | 851.4803 | 4.1378 | 49.1153 | 109.0434 | 54.4925 | 7.6064 | 52.9188 | 10.8118 | 12.6723 | 67.3861 | 87.8061 | 9.2345 | 219.464 | 128.0111 | 281.3018 | 12.8139 | 59.8995 | 14.9648 | 165 | 0.43487 | 135.0426 | 272.6633 | 0
358 | 830.2513 | 3.6968 | 47.7884 | 107.663 | 55.2762 | 6.8619 | 52.4637 | 10.1262 | 8.2412 | 66.535 | 82.585 | 8.2655 | 206.0139 | 122.566 | 267.9665 | 12.0039 | 58.3298 | 15.7999 | 154 | 0.49424 | 128.3153 | 272.1701 | 0
359 | 806.8643 | 3.3426 | 47.7616 | 107.0026 | 54.7054 | 7.4042 | 51.7331 | 11.4876 | 6.5251 | 62.0005 | 81.2041 | 7.687 | 183.971 | 113.974 | 248.8156 | 11.7193 | 58.1769 | 15.5013 | 141 | 0.44585 | 123.4085 | 269.3226 | 0
360 | 799.4804 | 2.3662 | 48.0085 | 106.395 | 55.2503 | 6.8865 | 52.3698 | 10.4682 | 6.0408 | 60.057 | 80.3322 | 7.5316 | 166.138 | 113.2568 | 222.1353 | 11.7189 | 58.3192 | 14.2146 | 126 | 0.51798 | 97.0618 | 269.1973 | 0
361 | 799.2686 | 2.0578 | 47.9381 | 105.2183 | 55.5402 | 6.6112 | 52.685 | 11.6939 | 6.2329 | 60.0426 | 80.5831 | 7.7251 | 163.1337 | 108.9686 | 224.0194 | 11.7196 | 57.7969 | 13.8571 | 127 | 0.52163 | 87.4215 | 271.4942 | 0
362 | 790.8882 | 1.8605 | 47.5607 | 105.1551 | 55.517 | 6.6332 | 53.0521 | 10.4279 | 6.274 | 60.6952 | 80.574 | 7.6393 | 159.8848 | 104.7695 | 232.7641 | 11.6421 | 57.6297 | 13.8849 | 124 | 0.49596 | 85.0245 | 270.1239 | 0
363 | 797.598 | 1.6785 | 47.4502 | 105.3386 | 55.4858 | 6.6628 | 53.1489 | 9.1671 | 6.2758 | 60.4386 | 81.035 | 7.5987 | 158.2554 | 101.3746 | 232.9415 | 11.655 | 57.2839 | 13.5724 | 151 | 0.49858 | 82.2888 | 274.4097 | 0
364 | 798.2171 | 1.7194 | 47.4912 | 106.0971 | 55.4768 | 6.6714 | 54.8929 | 10.0423 | 6.1753 | 60.6969 | 81.6677 | 7.5779 | 158.2384 | 100.113 | 231.5756 | 11.7338 | 57.129 | 12.9766 | 130 | 0.48348 | 79.2691 | 271.9159 | 0
365 | 801.7904 | 2.0567 | 47.2155 | 106.4829 | 55.5529 | 6.599 | 53.9683 | 10.8417 | 6.1228 | 65.3736 | 81.6715 | 7.5245 | 156.7059 | 96.9537 | 228.3413 | 11.6758 | 58.7187 | 12.8197 | 122 | 0.51989 | 78.2814 | 263.3335 | 0
366 | 800.9932 | 2.8327 | 48.0303 | 105.4099 | 55.4434 | 6.7031 | 52.8752 | 9.7879 | 6.0412 | 77.8857 | 82.0975 | 7.546 | 153.5866 | 94.8735 | 219.4124 | 11.6814 | 61.5597 | 12.814 | 115 | 0.59346 | 78.2588 | 259.6154 | 0
367 | 807.1287 | 3.3641 | 65.11 | 104.7123 | 55.502 | 6.6474 | 57.8646 | 9.4113 | 7.1638 | 97.824 | 82.5169 | 7.5763 | 153.643 | 94.4641 | 218.5737 | 11.5218 | 58.7676 | 12.7809 | 114 | 0.80029 | 78.1337 | 260.6657 | 0
368 | 811.1287 | 3.6046 | 73.5497 | 105.8383 | 54.7375 | 7.3737 | 68.8791 | 11.0237 | 16.1913 | 119.9797 | 90.6734 | 12.8421 | 185.2482 | 95.4457 | 218.9653 | 11.6553 | 56.898 | 13.074 | 118 | 1.165 | 77.6673 | 263.1897 | 0
369 | 812.9433 | 3.6394 | 82.363 | 104.2294 | 53.745 | 8.3165 | 68.6095 | 9.6425 | 22.3033 | 119.8568 | 124.4836 | 21.4577 | 209.6455 | 96.3233 | 215.1086 | 11.2618 | 56.0309 | 13.6433 | 123 | 0.9336 | 79.036 | 256.1485 | 0
370 | 839.728 | 2.093 | 88.5529 | 104.3729 | 53.53 | 8.5208 | 63.6227 | 8.6286 | 23.1793 | 113.3262 | 143.4515 | 21.8883 | 217.2152 | 98.4794 | 212.3543 | 11.1665 | 55.7589 | 13.8747 | 130 | 0.70823 | 108.1911 | 248.2132 | 0.010414
371 | 865.9131 | 2.3017 | 87.3094 | 104.9373 | 54.2599 | 7.8274 | 69.1495 | 8.4352 | 23.3078 | 113.605 | 146.7318 | 21.6125 | 225.8941 | 100.3256 | 211.0285 | 11.0627 | 56.2304 | 13.9516 | 161 | 0.61765 | 122.2527 | 252.3642 | 0.026774
372 | 883.5267 | 2.4002 | 87.234 | 105.6359 | 54.5135 | 7.5865 | 66.2212 | 8.261 | 22.9313 | 116.7077 | 147.0138 | 21.9565 | 236.323 | 104.3926 | 224.5612 | 11.0571 | 56.3152 | 14.0512 | 176 | 0.61069 | 125.4762 | 250.9455 | 0.046014
373 | 876.9389 | 1.8157 | 87.592 | 104.6167 | 54.4979 | 7.6014 | 70.2716 | 9.4147 | 22.2985 | 116.3725 | 139.5155 | 21.4597 | 241.4861 | 113.1817 | 228.1263 | 11.0441 | 56.099 | 14.1683 | 184 | 0.37817 | 128.454 | 249.3045 | 0.026874
374 | 870.6779 | 1.6646 | 79.7551 | 104.5674 | 53.7594 | 8.3029 | 75.0584 | 9.6296 | 22.5787 | 110.0626 | 115.5077 | 20.9886 | 246.1132 | 118.6407 | 206.2632 | 11.1619 | 55.7404 | 13.9278 | 186 | 0.47868 | 129.2591 | 254.3046 | 0.013397
375 | 874.3669 | 2.3249 | 65.0159 | 103.6047 | 54.9386 | 7.1826 | 65.2506 | 9.3429 | 22.4877 | 101.9134 | 101.9775 | 19.8982 | 235.8636 | 122.8306 | 206.2073 | 11.0862 | 56.3537 | 13.4684 | 178 | 0.5108 | 128.4783 | 260.4389 | 0.010602
376 | 859.858 | 3.7688 | 59.9092 | 104.595 | 55.491 | 6.6578 | 67.3295 | 8.8701 | 22.7527 | 82.8781 | 97.8613 | 22.9956 | 229.6717 | 118.5867 | 227.796 | 11.052 | 56.1945 | 13.5781 | 201 | 0.46829 | 124.8583 | 262.7826 | 0.00082765
377 | 863.131 | 4.5558 | 59.6953 | 106.4885 | 55.559 | 6.5933 | 64.4257 | 8.9223 | 23.244 | 66.8071 | 100.4926 | 22.0253 | 224.4 | 117.0543 | 250.021 | 11.363 | 56.9248 | 14.1074 | 189 | 0.49719 | 100.5059 | 275.8394 | 0
378 | 858.4105 | 4.3188 | 59.6276 | 106.6091 | 54.6908 | 7.418 | 60.351 | 9.3605 | 22.9428 | 62.2749 | 101.6843 | 21.3298 | 218.5422 | 116.7037 | 243.0453 | 11.644 | 58.0656 | 14.7413 | 191 | 0.50095 | 93.5191 | 282.1164 | 0
379 | 838.4963 | 4.2586 | 59.6774 | 106.7988 | 54.5367 | 7.5644 | 57.9167 | 11.5194 | 17.0868 | 51.8542 | 92.4319 | 12.8283 | 199.5409 | 115.1011 | 244.6614 | 11.5874 | 58.0345 | 14.9502 | 187 | 0.49719 | 94.9219 | 289.9283 | 0
380 | 821.0425 | 4.3041 | 59.8098 | 105.8503 | 54.4729 | 7.625 | 53.333 | 10.3701 | 13.8582 | 44.1746 | 85.0141 | 8.3332 | 187.6633 | 111.8505 | 244.0552 | 11.5837 | 57.6467 | 14.6283 | 183 | 0.45497 | 93.2466 | 279.5002 | 0
381 | 810.293 | 4.104 | 59.7093 | 105.3461 | 54.5482 | 7.5535 | 51.8109 | 9.3705 | 12.094 | 43.9391 | 83.9568 | 7.6183 | 183.984 | 107.4322 | 242.6776 | 11.6874 | 57.1394 | 13.9709 | 175 | 0.36013 | 89.3525 | 267.0944 | 0
382 | 809.824 | 4.1897 | 59.8595 | 105.4697 | 54.4732 | 7.6247 | 51.8188 | 11.5753 | 8.0742 | 50.1632 | 83.4185 | 7.5218 | 176.3684 | 102.5747 | 240.0951 | 11.552 | 56.9858 | 13.2135 | 176 | 0.33397 | 86.6617 | 273.8103 | 0
383 | 801.7118 | 3.6424 | 60.1731 | 106.1835 | 54.4146 | 7.6805 | 52.4358 | 10.8812 | 6.5352 | 52.2718 | 81.3411 | 7.5427 | 181.7959 | 101.1899 | 236.1336 | 11.5928 | 57.073 | 12.9865 | 163 | 0.30829 | 83.8917 | 278.4569 | 0
384 | 782.5249 | 2.2687 | 59.7298 | 105.9907 | 53.047 | 8.9797 | 55.5599 | 10.0268 | 9.6878 | 47.2361 | 80.1175 | 7.5226 | 185.5674 | 101.0423 | 240.7556 | 11.6111 | 57.2319 | 12.9537 | 139 | 0.40504 | 83.5755 | 287.5501 | 0
385 | 800.7803 | 1.9789 | 59.8574 | 104.0195 | 54.061 | 8.0164 | 53.4091 | 11.8062 | 10.3078 | 44.9152 | 81.2586 | 7.4604 | 169.2508 | 98.2301 | 246.7101 | 11.7247 | 57.1579 | 12.6491 | 135 | 0.4095 | 82.8155 | 274.7154 | 0
386 | 819.2712 | 2.1074 | 61.7264 | 104.2032 | 53.729 | 8.3318 | 51.9523 | 11.0592 | 8.4375 | 44.9967 | 80.4915 | 7.9692 | 162.1465 | 101.7097 | 241.5965 | 11.6326 | 57.1806 | 13.0963 | 137 | 1.0588 | 81.1952 | 266.4234 | 0
387 | 805.2807 | 2.7468 | 62.6372 | 103.4566 | 43.5482 | 18.0035 | 52.3905 | 11.8948 | 6.596 | 44.2375 | 80.2615 | 7.684 | 160.5824 | 98.8469 | 226.8003 | 11.6049 | 57.2571 | 13.0451 | 155 | 2.8385 | 78.8197 | 266.352 | 0
388 | 792.1609 | 2.5098 | 62.4713 | 104.6094 | 42.6518 | 18.8551 | 52.5791 | 12.7379 | 6.0698 | 42.4995 | 81.1553 | 7.4672 | 167.7281 | 96.2671 | 227.6554 | 11.6567 | 57.1749 | 12.9221 | 132 | 2.0237 | 80.3692 | 264.0676 | 0
389 | 782.2322 | 2.2423 | 61.1343 | 103.6919 | 48.1498 | 13.632 | 51.9839 | 11.4618 | 5.9282 | 42.0779 | 81.4879 | 7.476 | 168.8347 | 96.5287 | 221.2516 | 11.6796 | 58.7651 | 12.7538 | 132 | 1.6709 | 80.8703 | 258.0453 | 0
390 | 778.3082 | 2.9516 | 60.3433 | 103.1782 | 54.1725 | 7.9104 | 51.7887 | 12.5078 | 5.8585 | 50.7719 | 81.6117 | 7.4594 | 165.5482 | 96.5536 | 217.6186 | 11.4909 | 61.1679 | 12.4452 | 117 | 0.53595 | 80.4661 | 257.5821 | 0
391 | 791.1229 | 3.5978 | 60.2473 | 104.1416 | 55.4735 | 6.6745 | 51.9296 | 8.3375 | 5.7855 | 68.6279 | 82.1896 | 7.4743 | 168.7175 | 96.459 | 216.7504 | 11.6006 | 58.6313 | 12.2984 | 116 | 0.30073 | 79.3776 | 257.5682 | 0
392 | 795.7639 | 3.5905 | 60.1498 | 105.1074 | 54.7184 | 7.3918 | 51.9337 | 9.4592 | 6.5053 | 74.591 | 83.7938 | 7.486 | 171.0574 | 96.4584 | 219.3443 | 10.92 | 57.0489 | 12.5901 | 114 | 0.65554 | 79.7497 | 262.3753 | 0
393 | 791.1413 | 3.1993 | 60.2011 | 103.3532 | 53.7608 | 8.3016 | 52.0764 | 14.3796 | 10.8635 | 70.9663 | 82.3733 | 6.8761 | 165.2024 | 95.8466 | 217.3054 | 10.2339 | 56.555 | 13.2621 | 122 | 0.45795 | 81.168 | 255.8589 | 0
394 | 812.1624 | 2.4979 | 60.5865 | 102.7802 | 53.4717 | 8.5762 | 51.7746 | 15.4619 | 12.2407 | 71.5453 | 80.4055 | 5.4292 | 170.7839 | 98.265 | 208.2755 | 10.0982 | 56.9245 | 13.4085 | 133 | 0.19473 | 83.7705 | 250.9323 | 0.10737
395 | 831.3365 | 2.1145 | 60.2384 | 103.4037 | 54.986 | 7.1376 | 52.3404 | 15.1808 | 12.1357 | 81.8559 | 79.7716 | 5.007 | 183.6181 | 102.5424 | 199.3464 | 10.567 | 57.6163 | 13.5026 | 151 | 0.17015 | 83.5739 | 253.2321 | 0.14712
396 | 856.0858 | 1.8515 | 60.7928 | 103.8631 | 54.7682 | 7.3445 | 53.212 | 15.0751 | 11.7072 | 89.6033 | 88.5105 | 7.8364 | 189.1572 | 102.0993 | 198.8005 | 11.0298 | 58.8431 | 13.9715 | 168 | 0.17613 | 86.3381 | 254.344 | 0.18939
397 | 854.725 | 2.5119 | 60.5123 | 103.5443 | 55.2015 | 6.9329 | 55.0396 | 15.2326 | 12.1685 | 85.068 | 95.4704 | 11.2019 | 193.5844 | 106.4142 | 208.508 | 10.969 | 58.854 | 14.4427 | 180 | 0.1931 | 89.3299 | 251.1993 | 0.21755
398 | 848.548 | 2.9176 | 59.9738 | 105.3117 | 54.7559 | 7.3562 | 55.3443 | 15.5358 | 11.8443 | 78.3905 | 95.8781 | 9.8295 | 197.3009 | 107.4018 | 218.458 | 11.1851 | 58.2312 | 14.5798 | 177 | 0.2526 | 93.5171 | 251.862 | 0.20187
399 | 843.7315 | 2.471 | 59.6763 | 107.3318 | 55.3026 | 6.8368 | 62.3278 | 15.4031 | 10.5424 | 71.6017 | 95.0541 | 16.5735 | 202.829 | 110.0586 | 208.01 | 11.1207 | 58.4125 | 14.6575 | 179 | 0.23739 | 92.7844 | 255.1434 | 0.15643
400 | 843.3641 | 3.8171 | 59.6172 | 104.6664 | 54.7949 | 7.3191 | 67.6363 | 15.1516 | 10.7192 | 68.7822 | 104.1791 | 20.2476 | 200.338 | 110.5628 | 209.6966 | 11.0725 | 59.3983 | 14.5393 | 177 | 0.19019 | 93.4798 | 261.233 | 0.035714
401 | 829.1751 | 4.4121 | 59.8031 | 105.0923 | 54.4186 | 7.6767 | 75.3212 | 15.4202 | 12.8162 | 74.5705 | 121.1772 | 13.7592 | 198.5522 | 116.8665 | 243.5899 | 11.3533 | 60.5746 | 14.292 | 170 | 0.19678 | 96.659 | 288.0943 | 0
402 | 827.8193 | 4.9509 | 60.04 | 105.9397 | 53.9544 | 8.1176 | 74.2878 | 15.7761 | 12.2658 | 77.3427 | 112.947 | 9.1277 | 192.1037 | 121.8475 | 275.7182 | 11.6096 | 60.51 | 14.3271 | 179 | 0.2599 | 95.678 | 298.6547 | 0
403 | 822.6147 | 4.3958 | 60.5857 | 108.4053 | 55.052 | 7.0749 | 66.264 | 15.8863 | 12.0396 | 68.9904 | 104.3021 | 7.8437 | 190.8904 | 119.0945 | 257.8352 | 11.7407 | 60.5953 | 14.249 | 148 | 0.28492 | 96.14 | 298.9966 | 0
404 | 808.5758 | 3.8176 | 60.5548 | 109.0576 | 55.4953 | 6.6538 | 57.8201 | 16.2168 | 11.755 | 50.4837 | 104.0252 | 8.112 | 190.0497 | 112.4855 | 232.4179 | 11.8065 | 59.303 | 13.946 | 126 | 0.32379 | 95.8065 | 296.1776 | 0
405 | 796.1196 | 3.7617 | 60.7598 | 106.9743 | 55.451 | 6.6959 | 55.1094 | 16.1098 | 11.3088 | 43.7878 | 94.6622 | 7.9745 | 190.6391 | 103.3765 | 219.8108 | 11.7549 | 58.5891 | 13.5638 | 117 | 0.32748 | 91.3358 | 289.077 | 0
406 | 780.3871 | 3.6899 | 60.9209 | 107.1167 | 55.4901 | 6.6587 | 55.0234 | 15.8876 | 7.399 | 43.2319 | 85.7429 | 7.6364 | 184.5905 | 102.2022 | 210.7575 | 11.7014 | 58.7799 | 12.7277 | 120 | 0.28224 | 89.1528 | 287.0345 | 0
407 | 764.5115 | 3.3472 | 60.4899 | 106.9148 | 55.5104 | 6.6394 | 54.8954 | 15.9376 | 5.938 | 42.531 | 81.4061 | 7.5855 | 179.9765 | 102.4454 | 199.1849 | 11.6244 | 58.9571 | 12.1986 | 116 | 0.31912 | 83.4283 | 285.7906 | 0
408 | 749.5117 | 2.3656 | 60.0322 | 105.5579 | 56.2196 | 5.9657 | 54.4277 | 15.8779 | 6.129 | 42.1402 | 79.201 | 7.5567 | 167.3983 | 100.0802 | 201.5985 | 11.6986 | 58.4477 | 12.0605 | 111 | 0.33983 | 78.1924 | 278.7088 | 0
409 | 742.1397 | 6.3523 | 60.3573 | 104.8949 | 55.7729 | 6.39 | 54.4314 | 16.031 | 5.977 | 41.9429 | 80.2228 | 7.5391 | 159.7883 | 99.7701 | 208.9626 | 11.7145 | 58.3867 | 12.1538 | 107 | 0.28199 | 79.4148 | 266.9936 | 0
410 | 744.2911 | 5.1658 | 60.4563 | 104.3213 | 55.4797 | 6.6686 | 55.489 | 15.9372 | 5.778 | 41.9225 | 79.3309 | 7.5219 | 160.4576 | 96.7244 | 211.5699 | 11.5825 | 58.3448 | 12.1373 | 106 | 0.25816 | 80.3955 | 261.9643 | 0
411 | 737.8749 | 2.1027 | 60.0756 | 104.0955 | 55.4626 | 6.6848 | 59.091 | 15.7285 | 5.751 | 41.2175 | 78.6395 | 7.8822 | 160.4585 | 98.6099 | 207.6781 | 11.643 | 57.8094 | 11.992 | 123 | 0.23957 | 80.1577 | 264.4099 | 0
412 | 748.0185 | 1.3439 | 59.9212 | 103.9567 | 56.3116 | 5.8783 | 63.0815 | 15.6248 | 5.8041 | 44.6956 | 79.1753 | 7.925 | 160.4506 | 107.9373 | 207.2049 | 11.6154 | 56.9904 | 11.9414 | 103 | 0.22548 | 82.8662 | 265.1306 | 0
413 | 748.5814 | 1.808 | 60.1489 | 105.476 | 55.7819 | 6.3815 | 61.568 | 15.598 | 5.8327 | 55.1006 | 79.4344 | 7.9191 | 162.7493 | 117.2318 | 209.4068 | 11.6262 | 58.4156 | 11.9303 | 103 | 0.21385 | 81.8867 | 285.9291 | 0
414 | 765.1084 | 3.1837 | 60.0873 | 104.7067 | 56.227 | 5.9586 | 59.7096 | 15.5713 | 6.1682 | 70.4269 | 80.7113 | 9.4479 | 166.6057 | 121.2728 | 215.5254 | 11.5622 | 60.6921 | 11.9863 | 107 | 0.20796 | 86.4814 | 303.9818 | 0
415 | 808.4259 | 5.1808 | 64.1565 | 112.1457 | 53.5155 | 8.5346 | 71.133 | 16.1416 | 9.621 | 101.3261 | 109.8216 | 19.4573 | 206.8426 | 168.1187 | 256.1983 | 14.6624 | 59.6848 | 12.7677 | 164 | 0.94109 | 116.4165 | 348.1816 | 0
416 | 885.0321 | 5.9994 | 91.2784 | 121.9274 | 45.8423 | 15.8242 | 101.1201 | 17.2654 | 19.0654 | 121.0163 | 139.9961 | 36.3328 | 270.5886 | 217.1404 | 324.6675 | 27.3041 | 64.6479 | 13.2585 | 276 | 2.0286 | 143.5061 | 415.3459 | 0
417 | 971.4534 | 5.9893 | 111.1895 | 130.2748 | 44.1567 | 17.4255 | 110.9578 | 19.7369 | 27.981 | 120.8643 | 154.9563 | 46.0334 | 321.181 | 267.9825 | 422.6964 | 36.4558 | 76.5524 | 13.5732 | 316 | 2.0495 | 168.6416 | 473.5282 | 0
418 | 1081.7536 | 4.1283 | 122.4631 | 139.0929 | 44.6142 | 16.9908 | 111.7788 | 21.5323 | 29.7838 | 117.7062 | 163.6808 | 45.4157 | 364.5869 | 322.6403 | 502.0198 | 41.7503 | 87.2352 | 15.4482 | 310 | 3.1094 | 179.1518 | 522.7845 | 0.020526
419 | 1134.7334 | 3.3646 | 124.0944 | 144.4644 | 42.3062 | 19.1834 | 121.8099 | 21.4128 | 29.6815 | 114.1795 | 161.8604 | 44.2651 | 382.4825 | 355.6753 | 535.8308 | 43.4756 | 107.553 | 14.5387 | 347 | 3.2427 | 184.9366 | 555.6829 | 0.044654
420 | 1142.8366 | 3.459 | 126.1081 | 145.3261 | 42.9653 | 18.5573 | 118.04 | 21.3048 | 26.746 | 124.8796 | 166.0123 | 43.379 | 398.5432 | 369.0452 | 557.1012 | 43.3153 | 112.9403 | 14.2758 | 311 | 2.734 | 190.4961 | 555.3169 | 0.11444
421 | 1137.0528 | 3.7587 | 123.0202 | 142.7371 | 44.8648 | 16.7528 | 113.3088 | 17.3232 | 22.9442 | 122.8016 | 173.5444 | 43.3908 | 407.5277 | 367.404 | 552.2044 | 42.9583 | 107.883 | 15.0249 | 373 | 2.4 | 196.2596 | 563.0425 | 0.081956
422 | 1136.3934 | 3.457 | 122.3836 | 144.6234 | 43.3813 | 18.1621 | 119.6757 | 14.7824 | 30.8472 | 119.1747 | 179.0285 | 45.167 | 410.1127 | 369.1822 | 560.0293 | 44.0461 | 106.7612 | 14.9882 | 283 | 2.1931 | 209.3407 | 574.6373 | 0.073567
423 | 1146.1593 | 3.5134 | 124.1421 | 145.9066 | 43.1247 | 18.4058 | 114.7403 | 14.5858 | 33.184 | 113.9568 | 179.1139 | 43.8265 | 406.4834 | 375.1104 | 563.8267 | 44.8244 | 107.023 | 14.9139 | 293 | 0.80537 | 220.6899 | 581.0217 | 0.073578
424 | 1140.2043 | 4.8337 | 116.5122 | 145.2221 | 44.9251 | 16.6955 | 110.6822 | 14.1796 | 25.1338 | 112.2133 | 180.3629 | 43.8859 | 379.0283 | 348.6432 | 545.7394 | 44.2223 | 112.1657 | 16.1596 | 283 | 0.40711 | 215.4709 | 553.8678 | 0.0065096
425 | 1109.557 | 5.6874 | 113.123 | 144.529 | 47.7879 | 13.9758 | 105.5117 | 13.6703 | 19.2344 | 108.4473 | 181.5936 | 39.585 | 355.4543 | 319.1925 | 498.6819 | 35.8269 | 114.1193 | 16.9419 | 242 | -0.60294 | 201.3175 | 496.6638 | 0
426 | 1054.1488 | 5.9382 | 101.8751 | 139.6389 | 54.5073 | 7.5924 | 94.3023 | 12.1531 | 16.4438 | 99.7013 | 174.5615 | 37.1972 | 336.0767 | 249.2886 | 412.7732 | 22.373 | 102.0961 | 16.2724 | 244 | -1.0773 | 173.8473 | 417.8276 | 0
427 | 996.4175 | 5.1243 | 94.6616 | 125.8089 | 55.6873 | 6.4714 | 77.3748 | 9.8644 | 15.517 | 86.5238 | 146.6083 | 32.9437 | 295.1975 | 184.9673 | 350.7792 | 14.4568 | 78.8444 | 14.8055 | 219 | -1.2142 | 153.4353 | 365.1734 | 0
428 | 943.3314 | 4.3843 | 80.6093 | 116.6484 | 56.276 | 5.9121 | 70.5489 | 8.8195 | 15.099 | 57.8225 | 120.5259 | 18.9444 | 254.3336 | 156.9597 | 329.0412 | 11.8634 | 65.4736 | 13.9706 | 193 | -1.2525 | 133.1719 | 321.4463 | 0
429 | 914.4976 | 4.4144 | 75.0558 | 110.097 | 55.8116 | 6.3533 | 66.0312 | 8.4771 | 12.863 | 46.7433 | 111.4119 | 13.7373 | 226.9629 | 138.9032 | 296.8853 | 10.7121 | 58.8212 | 13.3773 | 168 | -1.3246 | 124.4378 | 297.2117 | 0
430 | 892.5243 | 4.2012 | 68.1241 | 108.3221 | 56.2192 | 5.9661 | 59.2459 | 8.1753 | 8.5178 | 47.7986 | 107.6093 | 13.1912 | 188.8934 | 131.7224 | 260.1863 | 10.3895 | 56.1166 | 12.5755 | 155 | -1.3638 | 120.9175 | 295.5513 | 0
431 | 860.0871 | 3.2886 | 64.9966 | 109.0771 | 55.7551 | 6.407 | 57.4685 | 7.8674 | 6.6787 | 46.2782 | 92.5815 | 12.8836 | 167.8804 | 121.0124 | 225.7307 | 10.319 | 55.4563 | 12.2931 | 144 | -1.3928 | 114.3306 | 289.8131 | 0
432 | 821.0251 | 2.0141 | 64.9119 | 110.0798 | 54.7147 | 7.3954 | 66.5377 | 7.5765 | 6.4673 | 43.1924 | 83.3148 | 12.8666 | 166.0101 | 113.116 | 223.7303 | 10.3159 | 55.8775 | 12.1786 | 130 | -1.3956 | 88.2199 | 283.3141 | 0
433 | 804.5567 | 1.4044 | 65.356 | 110.7955 | 55.2763 | 6.8618 | 64.4765 | 7.526 | 6.2857 | 41.6801 | 80.6996 | 12.6681 | 164.2626 | 107.8763 | 234.0409 | 10.3618 | 55.4592 | 12.0373 | 125 | -1.3854 | 76.4149 | 276.5577 | 0
434 | 812.7811 | 1.291 | 65.4226 | 111.3021 | 56.2429 | 5.9435 | 59.3313 | 7.7574 | 6.3604 | 42.09 | 82.6565 | 12.5814 | 164.6767 | 107.1112 | 233.4087 | 10.41 | 55.2915 | 11.7265 | 112 | -1.3841 | 75.5182 | 272.6157 | 0
435 | 819.2764 | 1.3013 | 65.2873 | 111.5758 | 55.7468 | 6.4148 | 58.4201 | 7.9649 | 6.1832 | 42.439 | 86.3337 | 12.5672 | 163.4697 | 104.4969 | 235.6365 | 10.4328 | 55.5106 | 11.54 | 129 | -1.3718 | 75.4702 | 273.5728 | 0
436 | 819.7933 | 1.3611 | 65.4646 | 112.439 | 54.0363 | 8.0398 | 64.7687 | 8.215 | 6.0864 | 45.7837 | 88.0472 | 12.5433 | 158.8475 | 104.2439 | 242.7441 | 10.3719 | 55.6829 | 11.4936 | 112 | -1.3504 | 75.0449 | 275.4699 | 0
437 | 821.6095 | 1.6503 | 65.536 | 112.9326 | 54.9986 | 7.1257 | 65.4406 | 8.362 | 6.3838 | 55.5593 | 86.932 | 12.51 | 157.4769 | 113.8445 | 239.7971 | 10.3525 | 57.1297 | 11.4838 | 107 | -1.3716 | 74.4473 | 294.4072 | 0
438 | 829.6869 | 2.9972 | 65.5608 | 113.225 | 55.485 | 6.6635 | 60.6903 | 8.514 | 7.9618 | 72.4244 | 84.237 | 13.4122 | 163.787 | 121.4781 | 245.6157 | 10.2616 | 59.4215 | 11.4652 | 107 | -1.3754 | 76.4193 | 321.0023 | 0
439 | 849.9827 | 4.2322 | 66.2829 | 115.9634 | 53.9679 | 8.1048 | 65.5576 | 8.4741 | 8.9454 | 96.2092 | 97.2739 | 21.4621 | 186.5088 | 141.388 | 254.2923 | 13.3504 | 58.0113 | 11.4779 | 142 | -1.1991 | 105.072 | 354.5978 | 0
440 | 901.4749 | 5.3032 | 73.4207 | 122.0794 | 48.9802 | 12.8432 | 90.3516 | 8.6811 | 13.3745 | 107.4272 | 130.3434 | 35.733 | 241.441 | 208.8068 | 313.3731 | 24.6885 | 59.7028 | 11.8312 | 268 | -0.29107 | 142.8706 | 406.8971 | 0
441 | 958.1802 | 5.1451 | 93.8491 | 124.5849 | 44.582 | 17.0215 | 108.858 | 8.9406 | 17.639 | 109.3851 | 143.6753 | 42.5909 | 295.8417 | 255.0753 | 406.123 | 32.5755 | 66.3838 | 12.9646 | 265 | -0.036388 | 172.3213 | 444.0521 | 0
442 | 1015.6316 | 4.2254 | 101.433 | 131.6875 | 44.1864 | 17.3973 | 109.6962 | 10.0459 | 21.039 | 115.95 | 156.0372 | 43.3164 | 339.3503 | 283.0283 | 471.946 | 36.7227 | 76.1409 | 14.1351 | 325 | 0.15164 | 189.0044 | 479.8444 | 0.012679
443 | 1069.6118 | 3.4669 | 110.9038 | 140.7332 | 44.4741 | 17.1239 | 111.0421 | 11.7779 | 23.513 | 120.6608 | 170.8353 | 42.6505 | 367.952 | 303.2 | 506.8246 | 39.8683 | 93.2579 | 14.6342 | 303 | 0.64959 | 201.0292 | 522.0128 | 0.017922
444 | 1097.0151 | 3.0295 | 117.5968 | 144.0552 | 44.4629 | 17.1345 | 119.3382 | 11.805 | 22.663 | 145.6819 | 183.4004 | 40.524 | 380.7245 | 313.8484 | 521.5222 | 40.7143 | 100.4551 | 15.2047 | 292 | 0.6497 | 213.3794 | 562.1055 | 0.023103
445 | 1111.4629 | 3.3251 | 121.4286 | 141.3693 | 46.0018 | 15.6727 | 116.5423 | 11.2486 | 19.118 | 132.5229 | 182.9306 | 36.7543 | 380.1242 | 311.4483 | 527.5014 | 42.2117 | 88.8513 | 16.7309 | 325 | 0.53537 | 219.7354 | 565.7193 | 0.020672
446 | 1115.1169 | 3.1875 | 122.0327 | 142.329 | 44.3502 | 17.2416 | 107.8659 | 11.5368 | 22.602 | 121.1217 | 179.5436 | 40.9454 | 381.8835 | 326.3276 | 543.3635 | 44.2592 | 86.7537 | 17.6273 | 294 | 0.56256 | 216.8598 | 568.3016 | 0.043801
447 | 1124.1807 | 3.1625 | 119.9442 | 145.3522 | 45.1309 | 16.5 | 105.0674 | 12.6049 | 22.67 | 117.0068 | 179.3608 | 43.1474 | 387.3486 | 344.0158 | 547.6883 | 44.9151 | 91.5681 | 16.5879 | 327 | 1.0066 | 221.6808 | 567.0132 | 0.010492
448 | 1113.7959 | 4.1681 | 120.5478 | 141.8609 | 46.1778 | 15.5054 | 111.7319 | 12.7599 | 21.2008 | 112.2224 | 176.2644 | 41.6323 | 386.6677 | 326.9217 | 546.1181 | 42.5577 | 90.4646 | 16.1477 | 288 | 0.98178 | 226.9683 | 555.3298 | 0.0016646
449 | 1093.107 | 5.117 | 113.7903 | 141.7359 | 51.538 | 10.4132 | 102.9798 | 12.0792 | 17.7689 | 110.9624 | 175.9096 | 39.3315 | 365.9277 | 300.7582 | 514.8937 | 34.3435 | 88.925 | 16.3499 | 240 | 0.2406 | 220.3557 | 506.7776 | 0
450 | 1030.6736 | 5.8586 | 103.9039 | 132.8191 | 55.0726 | 7.0553 | 87.2167 | 10.578 | 17.0338 | 104.4223 | 172.6459 | 34.0994 | 328.8434 | 242.4603 | 432.523 | 20.5533 | 83.1357 | 15.8899 | 229 | -0.39798 | 187.75 | 428.9986 | 0
451 | 967.542 | 5.4232 | 97.1095 | 125.3943 | 55.4342 | 6.7118 | 75.9119 | 8.8804 | 16.1526 | 87.7118 | 148.3965 | 27.104 | 277.1625 | 184.7462 | 382.188 | 12.9744 | 72.6869 | 15.3586 | 219 | -0.5252 | 168.5335 | 375.5267 | 0
452 | 938.3975 | 5.335 | 89.8489 | 122.0944 | 55.4872 | 6.6615 | 69.2268 | 8.3552 | 14.7852 | 58.0883 | 119.8481 | 14.8231 | 248.3049 | 157.1241 | 347.5963 | 10.5592 | 65.2013 | 15.0225 | 194 | -0.50547 | 152.5357 | 324.2522 | 0
453 | 902.0579 | 4.781 | 77.4276 | 116.8429 | 55.4631 | 6.6844 | 62.432 | 8.3383 | 12.1874 | 49.8889 | 111.7394 | 9.3524 | 233.5786 | 139.5677 | 317.4152 | 10.0445 | 60.2729 | 14.7653 | 173 | -0.46046 | 139.6232 | 305.632 | 0
454 | 872.8383 | 4.185 | 60.8447 | 112.3759 | 56.2656 | 5.9219 | 59.1035 | 8.6014 | 9.1431 | 48.8796 | 108.5926 | 8.5798 | 217.2356 | 124.6995 | 281.4128 | 10.0485 | 57.0999 | 14.049 | 156 | -0.5164 | 131.4346 | 299.7757 | 0
455 | 832.944 | 3.3898 | 56.1006 | 110.2785 | 55.7193 | 6.4409 | 58.913 | 9.3911 | 7.6375 | 45.1161 | 92.4977 | 8.2123 | 185.3512 | 115.133 | 261.4311 | 10.0287 | 56.1675 | 13.5189 | 133 | -0.52624 | 124.4229 | 299.0895 | 0
456 | 812.7467 | 2.3173 | 56.5725 | 110.4836 | 55.5048 | 6.6448 | 61.6613 | 9.79 | 6.6878 | 43.3416 | 84.6288 | 7.8807 | 168.1449 | 115.7733 | 252.9516 | 10.0138 | 56.1634 | 13.1936 | 119 | -0.45538 | 97.8894 | 305.4988 | 0
457 | 806.6596 | 1.5197 | 56.695 | 110.0607 | 54.7228 | 7.3877 | 62.6812 | 9.5933 | 6.2723 | 42.067 | 84.2794 | 7.825 | 167.6101 | 117.7762 | 248.6479 | 9.9868 | 56.4053 | 12.9602 | 116 | -0.45785 | 91.0657 | 310.8889 | 0
458 | 793.5843 | 1.3701 | 56.6783 | 108.2215 | 53.7529 | 8.3091 | 60.3567 | 8.9957 | 6.2172 | 41.7702 | 84.0804 | 7.7925 | 175.2271 | 113.126 | 246.0895 | 9.9328 | 56.3401 | 12.3531 | 115 | -0.56678 | 89.0303 | 304.4572 | 0
459 | 784.3872 | 1.4557 | 56.7344 | 108.0389 | 54.2834 | 7.8051 | 59.621 | 8.6496 | 6.3132 | 42.3014 | 84.6683 | 7.7853 | 172.6918 | 112.2802 | 243.2649 | 10.0214 | 56.2122 | 11.8973 | 140 | -0.55698 | 87.8905 | 299.0599 | 0
460 | 782.9244 | 1.4302 | 56.1784 | 105.5227 | 54.5177 | 7.5825 | 59.4282 | 8.6799 | 6.0347 | 44.9644 | 85.638 | 7.8181 | 172.6938 | 111.8055 | 241.6938 | 10.0213 | 56.374 | 11.8407 | 110 | -0.53077 | 84.241 | 300.1431 | 0
461 | 783.0722 | 1.9146 | 56.1544 | 104.5666 | 53.6263 | 8.4294 | 61.7301 | 9.6714 | 5.9162 | 54.667 | 85.7254 | 7.8106 | 175.4562 | 111.3102 | 237.1576 | 10.0368 | 57.9643 | 11.8524 | 106 | -0.54818 | 82.5903 | 314.837 | 0
462 | 805.0698 | 3.2506 | 57.7686 | 105.6474 | 52.7494 | 9.2624 | 62.5486 | 10.7234 | 6.7213 | 68.3486 | 86.0617 | 9.2144 | 182.2789 | 115.9166 | 250.0353 | 9.96 | 60.3147 | 11.8698 | 109 | -0.51111 | 85.8261 | 346.5584 | 0
463 | 829.7269 | 4.945 | 71.2143 | 114.6551 | 52.5262 | 9.4744 | 71.2538 | 9.3117 | 13.6114 | 95.973 | 104.0512 | 19.6588 | 228.7596 | 176.5814 | 281.7833 | 13.5848 | 58.5824 | 11.8182 | 186 | 0.070581 | 120.0171 | 381.4219 | 0
464 | 900.3803 | 6.1733 | 91.3539 | 122.1106 | 47.8081 | 13.9566 | 96.6192 | 9.4216 | 19.7675 | 113.0163 | 137.4005 | 34.9567 | 278.6007 | 249.9591 | 364.4179 | 28.5357 | 62.9614 | 12.4421 | 243 | 0.94985 | 175.6953 | 449.3438 | 0
465 | 991.6756 | 6.0978 | 97.1819 | 130.1934 | 43.5278 | 18.0229 | 114.7781 | 12.2336 | 23.062 | 107.5618 | 167.9409 | 40.0656 | 337.9338 | 304.9099 | 448.3907 | 37.5542 | 74.2685 | 15.4447 | 318 | 1.0678 | 211.0931 | 501.8769 | 0
466 | 1102.0076 | 4.6751 | 97.1819 | 138.2576 | 44.7987 | 16.8156 | 122.7529 | 14.9244 | 26.003 | 116.4392 | 181.2444 | 38.6459 | 390.7035 | 328.8712 | 537.7514 | 42.0375 | 85.5344 | 16.1467 | 330 | 1.105 | 227.4722 | 539.0401 | 0.0093978
467 | 1150.7912 | 3.8925 | 97.1819 | 144.0125 | 44.809 | 16.8058 | 124.3318 | 15.4102 | 29.8155 | 126.2681 | 183.5262 | 40.4189 | 414.6029 | 339.7773 | 565.757 | 44.8338 | 94.7328 | 15.8521 | 379 | 0.83706 | 232.4596 | 556.6549 | 0.016114
468 | 1182.5451 | 3.7912 | 97.1819 | 147.4438 | 45.3614 | 16.281 | 125.2148 | 14.8607 | 27.8697 | 124.5928 | 181.4647 | 40.4837 | 420.6728 | 355.8499 | 599.104 | 43.4088 | 95.3282 | 16.2058 | 340 | 0.72942 | 241.8749 | 565.9413 | 0.081829
469 | 1164.1193 | 4.1493 | 97.1819 | 146.4262 | 46.0979 | 15.5814 | 124.5274 | 14.936 | 22.3866 | 122.691 | 179.6324 | 41.6382 | 414.6415 | 353.3673 | 601.8388 | 44.0806 | 88.4723 | 16.2016 | 346 | 2.1448 | 242.7858 | 569.6998 | 0.16928
470 | 1190.3725 | 4.0504 | 97.1819 | 143.1552 | 44.9634 | 16.6591 | 121.0302 | 15.3381 | 27.3122 | 128.8811 | 186.9835 | 41.934 | 410.6579 | 366.1195 | 589.7858 | 45.2632 | 89.8129 | 16.0212 | 316 | 3.6303 | 241.1808 | 557.591 | 0.18623
471 | 1198.7732 | 4.0606 | 97.1819 | 145.9958 | 42.2306 | 19.2552 | 115.3492 | 14.7802 | 29.6866 | 126.5987 | 192.376 | 41.6201 | 421.3432 | 365.4526 | 588.3942 | 44.6496 | 93.4336 | 16.065 | 312 | 3.1992 | 240.4814 | 549.1289 | 0.13779
472 | 1189.0399 | 4.8071 | 97.1819 | 148.9856 | 42.3751 | 19.118 | 112.3977 | 12.8498 | 21.8301 | 120.0351 | 193.3525 | 38.8894 | 415.3838 | 347.2354 | 580.4868 | 41.3987 | 93.195 | 17.559 | 273 | 2.2505 | 239.297 | 545.1962 | 0.027974
473 | 1144.6747 | 6.187 | 97.1819 | 147.776 | 49.9839 | 11.8896 | 109.3571 | 12.2207 | 18.5554 | 117.7557 | 193.474 | 35.6485 | 388.1374 | 334.7134 | 546.2397 | 34.2959 | 93.0576 | 17.6071 | 249 | 1.372 | 221.3193 | 515.2278 | 0
474 | 1080.6492 | 6.0214 | 97.1819 | 140.8236 | 54.8833 | 7.2351 | 93.8206 | 11.8179 | 18.7118 | 111.3876 | 183.9404 | 31.7639 | 330.1403 | 271.535 | 459.7187 | 21.4765 | 86.0015 | 16.4442 | 214 | 0.89285 | 191.6929 | 432.7521 | 0
475 | 1018.8118 | 5.8577 | 97.1819 | 129.5243 | 53.9457 | 8.1259 | 80.4914 | 11.7937 | 19.1613 | 97.3333 | 152.2637 | 25.8756 | 288.9985 | 222.3162 | 404.7629 | 14.6984 | 77.2826 | 15.4434 | 200 | 0.93085 | 175.6985 | 388.5674 | 0
476 | 962.3454 | 5.2313 | 97.1819 | 120.9681 | 54.2352 | 7.8509 | 67.4446 | 10.7115 | 16.2813 | 72.6052 | 122.6516 | 13.1411 | 259.2059 | 195.5499 | 349.4822 | 11.8759 | 68.7197 | 15.3435 | 187 | 0.9601 | 156.3982 | 343.2366 | 0
477 | 913.7695 | 4.6191 | 97.1819 | 115.4926 | 55.2946 | 6.8445 | 62.3352 | 11.2989 | 13.1132 | 66.0111 | 114.4601 | 8.1904 | 234.0555 | 160.4237 | 298.7421 | 10.1285 | 60.628 | 15.4575 | 180 | 0.93727 | 145.3242 | 321.8061 | 0
478 | 891.2959 | 4.0737 | 97.1819 | 112.7911 | 55.4959 | 6.6532 | 61.8176 | 10.5037 | 8.1006 | 60.0828 | 112.388 | 8.2415 | 204.4577 | 129.3821 | 279.9413 | 9.8102 | 56.9241 | 14.2793 | 163 | 0.926 | 140.0779 | 319.9607 | 0
479 | 863.0085 | 3.5991 | 97.1819 | 112.0373 | 55.4912 | 6.6577 | 61.7525 | 11.1736 | 6.0729 | 49.7728 | 98.3197 | 8.1751 | 185.2378 | 116.0914 | 259.2726 | 9.9037 | 56.848 | 13.7425 | 150 | 0.99672 | 132.5095 | 322.0417 | 0
480 | 833.2501 | 2.3638 | 97.1819 | 110.0571 | 55.5009 | 6.6484 | 61.9732 | 6.6119 | 6.0592 | 46.2209 | 91.02 | 7.9365 | 166.7205 | 113.138 | 257.0832 | 9.8244 | 55.4273 | 13.4402 | 127 | 0.87313 | 101.8418 | 318.669 | 0
481 | 822.7428 | 1.64 | 97.1819 | 109.635 | 53.9809 | 8.0925 | 62.6152 | 10.3524 | 6.0082 | 46.1594 | 89.0911 | 7.8732 | 159.2057 | 110.7512 | 271.3208 | 9.86 | 54.7389 | 12.3966 | 114 | 0.87184 | 88.816 | 315.0042 | 0
482 | 825.7126 | 1.9722 | 97.1819 | 109.8922 | 54.2754 | 7.8127 | 62.7007 | 14.8784 | 5.8668 | 46.8298 | 88.4844 | 7.8935 | 159.398 | 106.9627 | 261.2682 | 9.79 | 54.7292 | 12.2151 | 109 | 0.90866 | 91.288 | 318.6453 | 0
483 | 813.8414 | 1.8251 | 97.1819 | 109.661 | 53.7071 | 8.3526 | 62.5911 | 15.3355 | 5.8945 | 46.4116 | 88.6759 | 7.9069 | 158.6541 | 102.6725 | 248.8347 | 9.9003 | 54.614 | 12.1435 | 131 | 0.89941 | 91.2616 | 315.2609 | 0
484 | 812.1165 | 1.6681 | 97.1819 | 109.6416 | 54.2546 | 7.8325 | 62.0922 | 15.2207 | 5.8698 | 48.4389 | 88.6168 | 8.1175 | 159.2609 | 105.6059 | 247.7726 | 9.8471 | 54.5273 | 12.0053 | 108 | 0.93063 | 89.2319 | 311.2084 | 0
485 | 820.5751 | 2.3161 | 97.1819 | 110.54 | 54.525 | 7.5756 | 61.9718 | 15.4119 | 6.0722 | 56.9544 | 89.2287 | 7.9768 | 158.4511 | 116.5228 | 246.7207 | 9.8782 | 55.9589 | 11.9805 | 108 | 0.90285 | 87.6697 | 321.2804 | 0
486 | 827.8791 | 3.9492 | 97.1819 | 111.4896 | 54.5649 | 7.5377 | 63.146 | 15.406 | 6.6688 | 72.2342 | 90.5065 | 9.7644 | 173.7521 | 126.3845 | 253.7618 | 9.7988 | 58.4764 | 12.0479 | 110 | 0.95763 | 89.8656 | 348.027 | 0
487 | 863.3921 | 5.0189 | 97.1819 | 120.1221 | 53.6928 | 8.3662 | 72.0759 | 15.191 | 8.1528 | 99.3136 | 105.3625 | 21.6468 | 216.8534 | 185.217 | 274.0162 | 12.7538 | 57.1591 | 14.6737 | 177 | 1.4818 | 126.7976 | 393.8763 | 0
488 | 946.9811 | 6.721 | 97.1819 | 125.0258 | 45.7199 | 15.9404 | 95.9201 | 16.4955 | 15.5973 | 121.7626 | 139.9056 | 39.415 | 275.8871 | 251.6426 | 351.2283 | 25.6541 | 62.2262 | 14.3259 | 242 | 2.4063 | 171.8044 | 466.5371 | 0
489 | 1025.5527 | 8.5609 | 92.6722 | 129.7366 | 41.8933 | 19.5757 | 112.7014 | 19.0085 | 24.2238 | 124.2309 | 161.6871 | 44.707 | 322.8969 | 303.4086 | 453.005 | 36.1461 | 72.8663 | 14.722 | 319 | 4.087 | 197.2477 | 525.4322 | 0
490 | 1108.734 | 8.1578 | 92.698 | 139.4229 | 40.9027 | 20.5168 | 118.3296 | 22.8217 | 28.012 | 124.9458 | 168.6472 | 43.6884 | 370.8986 | 315.4872 | 520.959 | 43.0566 | 82.4213 | 16.3787 | 372 | 4.6984 | 213.2149 | 568.7612 | 0.12779
491 | 1157.158 | 7.6226 | 92.698 | 146.55 | 42.766 | 18.7466 | 121.089 | 15.5904 | 28.2532 | 124.4146 | 178.8833 | 42.5093 | 397.4943 | 342.1222 | 561.2007 | 45.4768 | 89.8259 | 15.6866 | 342 | 3.8438 | 228.8907 | 590.4132 | 0.14043
492 | 1193.9719 | 7.5879 | 92.698 | 145.3511 | 41.3119 | 20.128 | 121.7366 | 20.6562 | 24.9237 | 132.0417 | 184.1442 | 41.7127 | 410.7305 | 354.0397 | 560.6227 | 45.5344 | 89.9029 | 15.5593 | 352 | 3.9883 | 244.4928 | 602.033 | 0.1151
493 | 1183.4142 | 7.5746 | 92.698 | 146.2836 | 41.1298 | 20.301 | 121.4563 | 22.529 | 21.4813 | 127.9404 | 186.4185 | 40.3947 | 404.0934 | 350.9979 | 555.958 | 46.9783 | 90.3933 | 16.7877 | 365 | 4.0544 | 248.9479 | 599.0116 | 0.037793
494 | 1175.2128 | 7.0335 | 92.698 | 147.8667 | 45.3817 | 16.2617 | 120.4238 | 17.542 | 27.027 | 128.1385 | 197.3027 | 40.5622 | 402.763 | 359.7774 | 592.3978 | 47.129 | 95.8494 | 18.2379 | 330 | 3.4752 | 247.3562 | 595.7945 | 0.065869
495 | 1182.5585 | 5.2577 | 92.698 | 148.7949 | 44.2726 | 17.3153 | 114.8278 | 19.5666 | 30.2193 | 125.0308 | 198.2335 | 41.455 | 406.8199 | 355.446 | 589.0413 | 48.3861 | 96.558 | 18.5993 | 332 | 3.042 | 246.4875 | 600.6918 | 0.012728
496 | 1166.4438 | 5.014 | 92.698 | 146.6576 | 44.1364 | 17.4447 | 112.4763 | 21.4951 | 23.0697 | 116.859 | 189.3577 | 43.4493 | 398.8942 | 338.4128 | 561.1744 | 45.9662 | 94.1539 | 17.9183 | 297 | 1.7184 | 239.1466 | 579.7977 | 0.0017657
497 | 1120.9605 | 6.0127 | 92.698 | 148.0943 | 50.6307 | 11.2751 | 114.0856 | 21.0671 | 17.5743 | 119.2156 | 186.8331 | 42.007 | 373.318 | 318.5512 | 523.803 | 35.527 | 91.2569 | 16.923 | 273 | 0.74588 | 218.6351 | 531.3897 | 0
498 | 1053.8126 | 6.0134 | 92.698 | 138.8308 | 52.5029 | 9.4965 | 99.2057 | 18.4313 | 14.9117 | 122.9549 | 182.2992 | 39.9817 | 326.1552 | 257.522 | 469.4009 | 21.5354 | 82.9929 | 16.5684 | 233 | 0.31109 | 187.9665 | 451.4456 | 0
499 | 992.829 | 5.5982 | 92.698 | 120.8725 | 54.7928 | 7.3212 | 81.0759 | 16.1333 | 14.6398 | 123.4787 | 154.009 | 31.3371 | 284.1353 | 191.9043 | 407.6376 | 15.8176 | 73.8055 | 16.5389 | 231 | 0.48291 | 167.6429 | 397.725 | 0
500 | 930.9116 | 5.7036 | 92.698 | 115.1837 | 55.5152 | 6.6348 | 70.3999 | 15.3118 | 14.9692 | 116.65 | 124.8195 | 15.1152 | 254.7528 | 158.938 | 357.2458 | 14.2022 | 67.574 | 16.1662 | 214 | 0.90679 | 146.0991 | 355.5455 | 0
501 | 883.1163 | 4.6935 | 92.698 | 111.8097 | 55.4984 | 6.6508 | 67.9881 | 15.1022 | 13.8161 | 115.0285 | 116.3658 | 9.6706 | 229.0112 | 139.1256 | 318.4101 | 12.6562 | 61.1655 | 14.9101 | 211 | 1.0377 | 137.4468 | 327.2695 | 0
502 | 862.5236 | 4.2068 | 92.698 | 108.1871 | 54.8038 | 7.3107 | 64.9005 | 15.1123 | 9.1743 | 115.2613 | 114.0439 | 9.8601 | 209.0042 | 127.5724 | 308.5503 | 12.1232 | 58.4845 | 14.1184 | 207 | 1.0475 | 130.8731 | 320.4146 | 0
503 | 827.6619 | 3.2672 | 92.698 | 105.8239 | 55.2378 | 6.8984 | 63.8779 | 15.2695 | 7.4039 | 111.8649 | 98.6478 | 9.8715 | 190.2516 | 122.3871 | 293.9755 | 12.2405 | 58.9471 | 13.7611 | 185 | 1.0875 | 125.7043 | 320.7006 | 0
504 | 809.2358 | 1.9545 | 92.698 | 104.6214 | 55.4536 | 6.6934 | 65.0862 | 15.3535 | 7.1333 | 103.0374 | 88.4498 | 9.6219 | 185.6409 | 130.2051 | 279.5364 | 12.2674 | 57.7966 | 13.3477 | 171 | 0.96128 | 98.4647 | 319.0378 | 0
505 | 804.6404 | 1.5679 | 92.698 | 104.6081 | 55.514 | 6.636 | 71.1627 | 15.4571 | 7.2068 | 79.2833 | 87.5239 | 9.5711 | 191.6154 | 121.6032 | 276.3583 | 12.3036 | 56.739 | 12.6673 | 163 | 0.65893 | 86.5156 | 315.7482 | 0
506 | 792.9288 | 1.6876 | 92.698 | 104.0914 | 55.4687 | 6.679 | 66.7832 | 15.587 | 7.174 | 65.5896 | 87.4937 | 9.5882 | 196.1773 | 119.6817 | 269.3663 | 12.3798 | 56.353 | 12.4825 | 141 | 0.58134 | 84.6986 | 313.7567 | 0
507 | 791.242 | 1.5534 | 92.698 | 104.1173 | 55.5199 | 6.6304 | 63.5331 | 15.3858 | 6.8318 | 64.5677 | 87.4141 | 9.5522 | 195.0989 | 118.4529 | 265.3617 | 12.2805 | 55.7005 | 12.4941 | 157 | 0.50655 | 82.2251 | 313.6461 | 0
508 | 786.4864 | 1.638 | 92.698 | 103.7919 | 55.486 | 6.6626 | 63.2065 | 15.1097 | 6.5165 | 63.1927 | 87.5302 | 9.4432 | 186.6984 | 128.1328 | 266.2416 | 12.3068 | 55.9016 | 12.1553 | 132 | 0.089361 | 78.6722 | 309.3776 | 0
509 | 788.4353 | 2.114 | 92.698 | 103.5296 | 54.7347 | 7.3764 | 70.3475 | 15.2599 | 6.182 | 66.5015 | 87.7036 | 9.4289 | 181.6706 | 131.3148 | 259.8236 | 12.2499 | 57.2296 | 11.787 | 127 | -0.19584 | 76.9507 | 321.5335 | 0
510 | 804.9252 | 3.441 | 92.698 | 104.0388 | 55.3303 | 6.8105 | 68.092 | 15.2544 | 7.2553 | 79.7979 | 88.27 | 10.6535 | 182.7375 | 130.8337 | 248.1219 | 12.2401 | 59.569 | 11.7286 | 127 | -0.26865 | 78.0325 | 348.1859 | 0
511 | 839.5521 | 4.4998 | 92.698 | 110.0776 | 53.2453 | 8.7912 | 75.1122 | 15.2144 | 11.6473 | 111.7108 | 105.4881 | 20.1843 | 209.7096 | 186.1063 | 272.6217 | 15.4165 | 59.2471 | 11.7313 | 188 | 0.34986 | 112.3811 | 390.2763 | 0
512 | 903.6387 | 6.1046 | 92.698 | 116.1967 | 47.8788 | 13.8895 | 99.156 | 15.7998 | 18.2023 | 120.2504 | 141.809 | 37.0288 | 281.1554 | 247.1368 | 359.1887 | 28.3204 | 64.3941 | 12.4844 | 273 | 0.82172 | 163.2989 | 462.7488 | 0
513 | 991.18 | 8.2358 | 92.698 | 124.726 | 44.8598 | 16.7575 | 128.2655 | 18.1002 | 20.5957 | 113.7868 | 168.0639 | 41.0696 | 331.6555 | 304.538 | 464.5332 | 38.8709 | 72.3227 | 14.2651 | 324 | 1.2837 | 193.578 | 521.0351 | 0
514 | 1116.1143 | 7.779 | 92.698 | 136.1646 | 41.5396 | 19.9117 | 125.0099 | 20.503 | 23.8273 | 120.4798 | 179.7287 | 38.1239 | 360.24 | 324.8701 | 538.1986 | 45.2762 | 83.1327 | 15.4324 | 333 | 1.5899 | 221.6119 | 556.4568 | 0.0091368
515 | 1184.3879 | 6.8188 | 92.698 | 142.7005 | 40.2912 | 21.0977 | 118.6939 | 21.899 | 29.3162 | 113.3838 | 191.0546 | 39.2774 | 376.6684 | 338.443 | 580.2269 | 47.0688 | 91.1173 | 17.1655 | 383 | 0.86009 | 232.5197 | 569.641 | 0.014526
516 | 1205.9082 | 5.5321 | 116.0361 | 144.8534 | 44.3427 | 17.2487 | 126.3803 | 21.7537 | 27.5991 | 105.1151 | 183.772 | 40.3623 | 391.9159 | 350.6665 | 604.9792 | 44.0251 | 94.5511 | 17.5682 | 331 | 0.47777 | 239.7434 | 573.7725 | 0.040653
517 | 1178.686 | 4.1106 | 121.3914 | 145.8668 | 43.3306 | 18.2102 | 120.7435 | 21.7726 | 20.4602 | 101.4533 | 180.7258 | 38.2881 | 398.7732 | 338.4916 | 605.3797 | 44.1445 | 91.4683 | 18.4496 | 345 | 0.32605 | 242.6865 | 565.6765 | 0.061402
518 | 1165.5802 | 4.0676 | 124.2128 | 148.2623 | 42.2848 | 19.2038 | 116.4014 | 17.7326 | 18.2932 | 117.1794 | 190.1248 | 37.9106 | 406.5864 | 355.4755 | 606.1603 | 45.5728 | 96.433 | 19.2995 | 302 | 0.26449 | 241.2221 | 567.4367 | 0.050481
519 | 1174.6878 | 4.8285 | 123.7241 | 150.2658 | 44.7284 | 16.8824 | 122.6367 | 13.3815 | 18.2593 | 116.323 | 189.8102 | 36.3683 | 401.977 | 361.5835 | 604.5264 | 46.2812 | 97.1779 | 18.9639 | 287 | 0.43791 | 232.4411 | 569.9191 | 0.026683
520 | 1165.5869 | 5.0992 | 120.6832 | 145.2434 | 44.1643 | 17.4182 | 113.4639 | 11.6228 | 18.5211 | 116.1291 | 183.5604 | 34.7793 | 389.1952 | 337.6966 | 569.879 | 42.7147 | 94.8944 | 18.0847 | 302 | 0.14278 | 220.9273 | 551.3991 | 0.0054869
521 | 1108.2862 | 5.3123 | 109.3388 | 144.1979 | 51.9865 | 9.9871 | 102.1467 | 10.8739 | 18.9773 | 111.3817 | 182.9937 | 33.9509 | 358.0958 | 306.8529 | 522.7828 | 26.1121 | 88.669 | 17.4866 | 322 | -0.55448 | 199.7629 | 495.3429 | 0
522 | 1028.1224 | 4.9274 | 90.2935 | 131.7174 | 55.2565 | 6.8807 | 95.9986 | 9.1048 | 16.8463 | 104.6337 | 177.5337 | 29.2189 | 303.3264 | 231.1849 | 441.0407 | 14.7274 | 80.2505 | 17.3395 | 279 | -1.0685 | 170.9237 | 422.6486 | 0
523 | 955.2125 | 4.4177 | 69.9262 | 118.8202 | 53.9223 | 8.1481 | 84.1466 | 8.4684 | 15.5727 | 94.1465 | 149.7516 | 22.8882 | 264.9545 | 171.7364 | 384.9425 | 13.2893 | 70.3172 | 16.661 | 246 | -1.1964 | 150.3667 | 374.5383 | 0
524 | 900.2653 | 4.5993 | 63.6272 | 112.6596 | 55.0546 | 7.0724 | 70.1899 | 10.7008 | 15.7107 | 75.7969 | 119.7415 | 11.7829 | 238.254 | 142.9837 | 349.3499 | 12.3654 | 59.7286 | 16.0858 | 238 | -1.2026 | 127.8457 | 335.5003 | 0
525 | 845.0886 | 3.9078 | 62.7656 | 110.4801 | 55.5224 | 6.6281 | 66.1563 | 9.1703 | 12.9754 | 69.2229 | 100.3457 | 8.2512 | 208.5291 | 126.9751 | 312.3616 | 11.6227 | 55.7168 | 15.6077 | 213 | -1.1154 | 117.1216 | 311.16 | 0
526 | 817.0061 | 3.436 | 62.5284 | 108.6638 | 56.2774 | 5.9108 | 69.6494 | 7.8535 | 9.5538 | 65.5879 | 93.2307 | 7.7267 | 192.1598 | 110.7589 | 296.1365 | 10.6772 | 54.777 | 14.4626 | 194 | -1.2106 | 116.5964 | 306.5826 | 0
527 | 794.0962 | 3.0701 | 62.2237 | 106.7209 | 55.7158 | 6.4443 | 68.9914 | 9.6419 | 8.1155 | 62.3204 | 90.1391 | 7.4672 | 184.6 | 106.6188 | 272.582 | 9.7623 | 54.9086 | 13.2836 | 175 | -1.2316 | 112.6051 | 305.0055 | 0
528 | 777.3119 | 2.0977 | 62.1326 | 106.5053 | 55.5321 | 6.6188 | 65.6923 | 8.3766 | 7.791 | 62.3581 | 87.5358 | 7.4809 | 182.6306 | 101.0405 | 254.1656 | 9.3257 | 54.4464 | 12.8623 | 155 | -1.2323 | 87.253 | 305.4492 | 0
529 | 760.6024 | 1.6179 | 62.2906 | 106.5778 | 55.5065 | 6.6432 | 65.4673 | 8.9357 | 7.525 | 61.779 | 87.1515 | 7.5051 | 187.0391 | 99.3076 | 261.5888 | 9.38 | 55.1701 | 11.9602 | 157 | -1.1851 | 78.6686 | 295.6158 | 0
530 | 770.5021 | 1.7725 | 62.0149 | 106.21 | 56.2648 | 5.9227 | 66.8604 | 9.162 | 7.3325 | 60.7627 | 87.2868 | 7.5602 | 184.4795 | 100.4426 | 264.4359 | 9.3811 | 54.4572 | 11.5995 | 154 | -1.1003 | 77.8528 | 283.713 | 0
531 | 779.8635 | 1.8011 | 61.8624 | 106.0891 | 55.6781 | 6.4802 | 69.8596 | 7.9661 | 7.4952 | 60.8599 | 87.6342 | 7.5366 | 173.2546 | 99.6641 | 256.7574 | 9.4149 | 53.6441 | 11.5789 | 165 | -1.1626 | 75.9926 | 283.2677 | 0
532 | 768.5685 | 1.4136 | 61.9998 | 105.9988 | 55.5639 | 6.5886 | 66.107 | 9.6614 | 7.6033 | 60.8233 | 88.2285 | 7.5282 | 177.1379 | 99.0664 | 240.3578 | 9.2817 | 53.3918 | 11.576 | 145 | -1.1804 | 70.4693 | 283.282 | 0
533 | 770.7379 | 1.6759 | 61.883 | 106.0982 | 56.2233 | 5.9622 | 64.2038 | 8.7774 | 7.5138 | 62.7636 | 88.3327 | 7.5188 | 178.9738 | 96.1394 | 243.4163 | 9.2733 | 54.7222 | 11.6019 | 137 | -1.2012 | 67.4732 | 281.658 | 0
534 | 771.18 | 2.6694 | 61.7727 | 106.0942 | 55.658 | 6.4992 | 64.9749 | 8.4691 | 7.4126 | 75.3377 | 88.4638 | 7.501 | 170.5377 | 94.6542 | 247.6844 | 9.3696 | 57.5506 | 11.8235 | 131 | -1.2001 | 68.0274 | 282.2037 | 0
535 | 773.1435 | 3.4147 | 66.2754 | 107.3753 | 56.3719 | 5.821 | 71.4085 | 9.2552 | 8.6717 | 98.2189 | 89.5344 | 7.5107 | 165.0267 | 95.7624 | 254.7266 | 9.4149 | 55.1375 | 11.6875 | 124 | -0.85265 | 70.2964 | 285.6705 | 0
536 | 795.6322 | 3.2751 | 70.5929 | 110.2691 | 54.8925 | 7.2264 | 68.7595 | 7.9639 | 13.4265 | 103.8792 | 95.9847 | 9.2748 | 166.5494 | 98.9764 | 249.0947 | 9.3219 | 53.282 | 11.817 | 121 | -0.41723 | 74.2399 | 291.6719 | 0
537 | 805.6095 | 3.0892 | 80.1099 | 111.8231 | 53.7091 | 8.3507 | 66.5451 | 8.6865 | 11.3292 | 93.7925 | 120.885 | 12.9815 | 177.0884 | 100.7369 | 243.2728 | 8.8933 | 52.8301 | 12.306 | 128 | -0.93411 | 75.2783 | 291.44 | 0
538 | 830.0126 | 1.7854 | 88.1306 | 110.0713 | 53.5729 | 8.48 | 66.6783 | 8.3745 | 7.5871 | 89.4603 | 143.5928 | 7.1401 | 195.7315 | 109.7322 | 241.5935 | 8.7692 | 53.0374 | 12.3773 | 145 | -0.97726 | 104.7303 | 284.5303 | 0.017849
539 | 843.8037 | 1.2138 | 90.2657 | 107.9001 | 51.8889 | 10.0798 | 72.6979 | 7.1645 | 10.5208 | 89.3177 | 156.7495 | 4.621 | 214.4157 | 125.0325 | 227.8403 | 8.8305 | 52.8906 | 12.369 | 163 | -0.96079 | 117.533 | 287.8024 | 0.030589
540 | 857.7556 | 1.4458 | 92.7527 | 108.6141 | 52.3074 | 9.6823 | 72.3637 | 6.5961 | 12.0631 | 90.7919 | 161.5774 | 4.6704 | 222.3173 | 137.6057 | 227.5324 | 8.9099 | 53.3122 | 12.4027 | 183 | -0.56509 | 116.9123 | 291.908 | 0.024107
541 | 866.4698 | 1.6331 | 90.2015 | 109.7644 | 51.7443 | 10.2173 | 78.164 | 7.8839 | 12.5179 | 94.4996 | 152.4787 | 4.6647 | 223.8586 | 135.5769 | 237.9833 | 9.2266 | 53.6274 | 13.236 | 181 | -0.95554 | 117.5527 | 289.4151 | 0.023216
542 | 850.8436 | 1.8431 | 88.7802 | 110.903 | 51.4698 | 10.478 | 76.7237 | 9.347 | 9.6911 | 88.3294 | 123.0973 | 4.6499 | 224.7261 | 136.1633 | 237.6491 | 10.0581 | 53.8172 | 14.3417 | 185 | -1.0248 | 117.9504 | 301.1724 | 0.012848
543 | 839.2165 | 1.821 | 78.7788 | 111.2074 | 52.2918 | 9.6971 | 76.5117 | 9.8846 | 12.2007 | 79.8699 | 110.121 | 6.2839 | 220.2909 | 135.2826 | 241.5352 | 10.3526 | 53.3885 | 14.5111 | 180 | -1.0738 | 122.3508 | 293.2379 | 0.0068918
544 | 836.3399 | 3.0763 | 74.5092 | 108.4888 | 52.4759 | 9.5222 | 78.0435 | 8.183 | 13.6273 | 65.1158 | 110.7112 | 10.0985 | 224.7778 | 137.8403 | 249.9598 | 10.8125 | 53.2159 | 14.4541 | 179 | -1.1491 | 119.6319 | 283.3777 | 0.0010484
545 | 829.7961 | 3.8831 | 74.0869 | 107.1357 | 53.3002 | 8.7391 | 79.3596 | 6.9757 | 13.7653 | 46.4013 | 109.4473 | 8.5138 | 230.1149 | 150.8106 | 267.2398 | 11.9474 | 54.3569 | 15.1058 | 197 | -1.185 | 93.6083 | 285.4904 | 0
546 | 826.0607 | 3.7109 | 74.8399 | 107.5184 | 51.204 | 10.7305 | 70.0863 | 7.2917 | 12.4656 | 44.6844 | 104.6552 | 7.4947 | 224.5558 | 154.6757 | 271.5365 | 13.5254 | 55.6383 | 15.537 | 191 | -1.209 | 84.1684 | 289.2077 | 0
547 | 821.6222 | 3.5205 | 74.2551 | 107.3655 | 52.1211 | 9.8592 | 70.9603 | 8.3224 | 7.9524 | 44.388 | 93.2237 | 8.0233 | 210.6597 | 147.8248 | 269.5788 | 12.6416 | 54.9615 | 15.1592 | 188 | -1.1272 | 81.5295 | 289.5418 | 0
548 | 805.9779 | 4.1891 | 73.9842 | 108.8501 | 53.2032 | 8.8313 | 68.7752 | 8.0574 | 6.7725 | 52.6395 | 88.3983 | 8.222 | 201.6106 | 131.9025 | 255.6226 | 11.5804 | 53.9317 | 14.7531 | 196 | -1.1158 | 81.1306 | 291.4613 | 0
549 | 792.3699 | 3.8487 | 73.7627 | 108.3217 | 53.5176 | 8.5326 | 62.5284 | 7.188 | 10.3754 | 54.3731 | 87.5509 | 7.8214 | 185.7859 | 115.2854 | 237.986 | 11.2334 | 53.7547 | 14.4576 | 178 | -1.1053 | 79.2866 | 290.6003 | 0
550 | 775.0669 | 3.5845 | 73.2512 | 107.0699 | 53.4146 | 8.6305 | 60.3288 | 6.837 | 7.7661 | 47.0348 | 86.3405 | 7.7632 | 166.4221 | 115.4676 | 240.1082 | 10.8777 | 53.7044 | 13.7721 | 165 | -1.1474 | 79.5319 | 305.6919 | 0
551 | 767.0952 | 2.9152 | 72.656 | 105.328 | 53.5125 | 8.5374 | 66.6706 | 6.8325 | 6.4178 | 43.7506 | 84.286 | 7.5265 | 174.894 | 117.7913 | 239.2877 | 11.0719 | 53.4187 | 13.1188 | 158 | -1.2127 | 77.2729 | 310.1098 | 0
552 | 760.1932 | 2.0344 | 72.8697 | 104.0811 | 54.3318 | 7.7591 | 67.9079 | 7.5856 | 6.3722 | 41.8986 | 82.1805 | 7.416 | 183.5918 | 118.6458 | 245.5516 | 11.1254 | 52.9711 | 12.5571 | 147 | -1.1984 | 75.7379 | 297.1479 | 0
553 | 777.7553 | 2.0292 | 72.6813 | 102.7888 | 53.7319 | 8.329 | 62.9695 | 8.1753 | 6.572 | 41.5011 | 81.3222 | 7.4242 | 182.0024 | 114.6319 | 258.3267 | 10.6154 | 52.987 | 11.9424 | 136 | -1.1604 | 75.7036 | 286.0481 | 0
554 | 778.2264 | 1.6765 | 72.7876 | 103.9032 | 52.6625 | 9.345 | 61.2226 | 7.6838 | 6.6453 | 41.3285 | 81.352 | 7.4838 | 172.8188 | 103.1877 | 251.2216 | 9.6682 | 52.9351 | 11.735 | 138 | -0.53692 | 73.0674 | 280.0706 | 0
555 | 763.5476 | 1.6106 | 72.6576 | 104.7494 | 49.4502 | 12.3967 | 68.3759 | 6.7887 | 6.794 | 40.9337 | 81.926 | 7.4863 | 162.4147 | 96.2084 | 242.2348 | 9.2245 | 52.9358 | 11.4684 | 156 | 1.1104 | 72.9365 | 278.9607 | 0
556 | 755.1162 | 1.6689 | 72.6954 | 103.0619 | 50.017 | 11.8581 | 68.4003 | 6.5989 | 6.5493 | 40.9648 | 82.8735 | 7.662 | 160.1383 | 95.4045 | 238.4069 | 9.2171 | 53.5583 | 11.6091 | 133 | 0.57792 | 74.2688 | 274.2169 | 0
557 | 739.2056 | 1.8418 | 72.8218 | 104.9379 | 51.2519 | 10.685 | 62.5746 | 6.5394 | 6.616 | 40.349 | 83.0141 | 7.8065 | 158.1264 | 95.1771 | 252.6178 | 9.1946 | 55.1931 | 11.9945 | 126 | 0.19888 | 72.7025 | 273.8114 | 0
558 | 731.448 | 2.7169 | 72.782 | 105.5042 | 53.1264 | 8.9042 | 60.9869 | 7.1294 | 6.4338 | 51.4855 | 83.042 | 7.5577 | 160.6019 | 94.7281 | 255.2293 | 9.1849 | 57.6755 | 11.5678 | 129 | -0.83337 | 72.1072 | 267.8617 | 0
559 | 746.8733 | 3.0582 | 72.5852 | 106.5634 | 53.4832 | 8.5652 | 68.5664 | 7.7059 | 7.6208 | 74.6173 | 83.3377 | 7.4473 | 160.4833 | 95.0982 | 249.698 | 9.23 | 55.0095 | 11.3192 | 124 | -1.0916 | 70.6141 | 277.7009 | 0
560 | 762.0841 | 2.9866 | 72.7115 | 106.2965 | 53.5585 | 8.4937 | 69.2114 | 7.6301 | 11.8396 | 74.984 | 84.451 | 7.5007 | 167.957 | 95.8248 | 251.1569 | 9.276 | 52.9865 | 11.6079 | 122 | -0.71094 | 68.9491 | 276.9595 | 0
561 | 763.7395 | 3.0229 | 63.8332 | 103.7843 | 54.2455 | 7.8411 | 62.7253 | 7.3246 | 12.9034 | 67.3407 | 90.2194 | 7.042 | 168.5227 | 92.4102 | 250.0671 | 8.8827 | 51.7784 | 12.2595 | 123 | -1.0105 | 70.2696 | 265.7897 | 0
562 | 765.2868 | 2.3614 | 55.9222 | 105.218 | 55.1863 | 6.9474 | 59.9375 | 6.2363 | 12.5177 | 68.6588 | 104.5454 | 5.5467 | 168.31 | 97.755 | 245.6676 | 8.9172 | 51.4731 | 12.4281 | 135 | -1.1783 | 72.5359 | 261.4551 | 0.0082226
563 | 801.4362 | 1.3386 | 54.8478 | 104.6735 | 54.7159 | 7.3942 | 67.3515 | 5.8911 | 12.6846 | 82.1861 | 120.4484 | 4.7292 | 187.8886 | 101.8589 | 238.2863 | 10.9814 | 51.5421 | 12.4169 | 188 | -1.1875 | 74.2677 | 262.5586 | 0.030089
564 | 822.9858 | 1.0376 | 55.0102 | 104.3792 | 54.53 | 7.5708 | 81.004 | 5.6689 | 11.6201 | 87.3413 | 118.9457 | 4.6349 | 197.6015 | 120.5499 | 241.0407 | 10.8004 | 52.6992 | 12.4578 | 208 | -1.055 | 71.4355 | 262.8567 | 0.056135
565 | 831.4935 | 1.381 | 56.1592 | 104.7606 | 53.8171 | 8.2481 | 79.0172 | 5.7938 | 10.7681 | 77.8772 | 122.8051 | 4.6424 | 206.9026 | 137.6829 | 234.1613 | 10.1079 | 54.3219 | 12.7864 | 198 | -1.087 | 67.6895 | 263.7122 | 0.054116
566 | 827.7102 | 1.3806 | 56.0513 | 104.7734 | 54.2045 | 7.8801 | 68.4272 | 5.6968 | 12.3321 | 70.2492 | 118.0578 | 4.7728 | 209.9036 | 144.5728 | 223.1145 | 9.2645 | 55.1547 | 13.0433 | 240 | -1.0945 | 66.578 | 269.0823 | 0.045047
567 | 827.7586 | 1.6426 | 55.4558 | 103.6361 | 52.9615 | 9.0609 | 81.8399 | 5.5982 | 12.7761 | 66.4468 | 106.9472 | 6.3743 | 208.8477 | 150.0997 | 228.5545 | 8.9633 | 54.8311 | 13.4047 | 237 | -1.0214 | 67.8487 | 288.4768 | 0.018666
568 | 833.267 | 2.8673 | 55.1977 | 105.1901 | 53.997 | 8.0772 | 87.9799 | 6.1927 | 12.7125 | 63.1797 | 103.3392 | 10.311 | 205.3166 | 141.5986 | 248.9177 | 8.9417 | 54.5303 | 14.0933 | 215 | -1.0843 | 69.0271 | 299.2271 | 0.0018926
569 | 834.6239 | 3.7418 | 55.4804 | 104.9275 | 54.5575 | 7.5447 | 71.1048 | 6.638 | 13.0437 | 63.3954 | 105.3473 | 8.7429 | 205.8295 | 148.4097 | 284.0624 | 9.2979 | 55.8312 | 14.5506 | 237 | -1.1461 | 76.5917 | 308.2783 | 0
570 | 836.9478 | 3.9292 | 55.3025 | 102.6293 | 54.4226 | 7.6729 | 64.1332 | 6.7695 | 13.2107 | 69.6268 | 106.6467 | 7.7076 | 206.6372 | 153.811 | 291.0642 | 9.4305 | 57.2706 | 14.4491 | 237 | -1.1541 | 79.3973 | 304.5176 | 0
571 | 834.5721 | 3.5454 | 55.5761 | 100.9624 | 55.2948 | 6.8442 | 70.2314 | 6.903 | 13.4317 | 63.6761 | 107.5434 | 7.6 | 194.7006 | 135.7918 | 270.211 | 9.4163 | 55.0039 | 14.279 | 227 | -1.0474 | 80.3613 | 288.6555 | 0
572 | 834.6831 | 3.7721 | 55.1419 | 99.7368 | 54.7046 | 7.4049 | 72.4274 | 6.8726 | 8.6803 | 47.2061 | 102.646 | 7.6035 | 184.0635 | 124.9445 | 256.0159 | 9.4945 | 54.3438 | 14.0397 | 226 | -1.0831 | 83.0443 | 288.509 | 0
573 | 840.2823 | 3.3772 | 55.4388 | 101.3744 | 54.4626 | 7.6349 | 65.0688 | 6.869 | 6.8001 | 41.5826 | 90.6489 | 7.6149 | 184.169 | 119.442 | 252.1468 | 9.5601 | 54.3517 | 13.0002 | 274 | -0.99912 | 78.2312 | 293.0882 | 0
574 | 835.8735 | 3.2146 | 55.4696 | 102.7196 | 54.5452 | 7.5564 | 62.1824 | 6.4581 | 6.5827 | 42.3324 | 85.0314 | 7.8761 | 169.578 | 111.2569 | 250.5327 | 9.4749 | 53.7587 | 13.2184 | 221 | -1.0847 | 73.0403 | 284.1894 | 0
575 | 829.0225 | 2.9112 | 54.6994 | 100.1391 | 55.2936 | 6.8454 | 71.2555 | 6.3337 | 6.28 | 40.276 | 83.0817 | 7.6253 | 161.3557 | 103.0188 | 239.8558 | 9.3955 | 54.0314 | 12.1873 | 186 | -1.1391 | 70.2338 | 279.8277 | 0
576 | 812.185 | 1.7821 | 54.3345 | 98.848 | 54.7264 | 7.3843 | 69.0739 | 6.3006 | 6.4567 | 39.5195 | 81.8964 | 7.513 | 156.5145 | 98.3841 | 240.1764 | 9.4845 | 53.3685 | 11.601 | 181 | -1.1371 | 69.6237 | 278.6397 | 0
577 | 824.8238 | 1.6432 | 54.3338 | 98.616 | 53.7765 | 8.2866 | 63.0244 | 6.1659 | 6.3631 | 39.9831 | 79.8828 | 7.5197 | 162.2671 | 95.4581 | 233.12 | 9.3311 | 52.5976 | 11.5603 | 151 | -1.0977 | 70.1858 | 279.507 | 0
578 | 815.4142 | 1.3924 | 49.9842 | 98.7456 | 54.2482 | 7.8385 | 63.0833 | 6.4301 | 6.3387 | 40.7507 | 79.0872 | 7.514 | 165.6294 | 95.2801 | 229.7969 | 9.3504 | 52.3725 | 11.5598 | 139 | -1.1314 | 69.7539 | 273.554 | 0
579 | 801.4079 | 1.1859 | 47.8751 | 99.1006 | 54.508 | 7.5917 | 74.0491 | 6.8026 | 6.2969 | 39.4102 | 79.5104 | 7.9664 | 157.6615 | 99.2699 | 224.1365 | 9.5134 | 52.3663 | 11.5379 | 139 | -1.1504 | 70.4722 | 271.988 | 0
580 | 789.6608 | 1.1628 | 47.5325 | 98.8791 | 54.4479 | 7.6488 | 71.7308 | 7.2145 | 6.2894 | 41.8477 | 80.4236 | 7.8939 | 161.7952 | 108.0877 | 226.8834 | 9.4253 | 52.468 | 11.5542 | 114 | -1.1257 | 74.2553 | 273.5212 | 0
581 | 767.8676 | 2.1315 | 47.9881 | 101.009 | 54.4864 | 7.6122 | 68.167 | 7.2767 | 6.2229 | 52.5608 | 80.5965 | 7.9436 | 162.6999 | 117.5123 | 226.966 | 9.3641 | 54.0188 | 11.5262 | 106 | -1.1792 | 71.811 | 294.0267 | 0
582 | 759.322 | 3.9479 | 49.1726 | 101.0165 | 55.2685 | 6.8693 | 70.1206 | 6.9553 | 6.5149 | 68.0825 | 82.2243 | 9.0364 | 167.8576 | 119.0235 | 238.463 | 9.3606 | 56.405 | 11.5685 | 111 | -1.1574 | 73.4535 | 315.3046 | 0
583 | 803.2974 | 5.033 | 61.4238 | 109.5903 | 53.2142 | 8.8208 | 83.3368 | 6.6493 | 6.8455 | 94.0365 | 113.7982 | 19.2643 | 210.0401 | 183.01 | 283.803 | 12.3656 | 55.1589 | 12.4876 | 165 | -0.60721 | 121.8215 | 352.8062 | 0
584 | 884.5369 | 6.4522 | 92.9939 | 115.7931 | 48.5871 | 13.2166 | 99.9769 | 7.2928 | 12.6473 | 110.6647 | 144.5201 | 36.6699 | 274.6885 | 239.5486 | 388.5455 | 26.4208 | 60.3197 | 13.5008 | 273 | 0.73941 | 169.3311 | 426.7684 | 0
585 | 966.6404 | 8.6699 | 115.0059 | 120.7398 | 45.9236 | 15.7469 | 112.2579 | 8.7718 | 19.4362 | 112.2478 | 161.7773 | 44.2873 | 331.779 | 299.0597 | 489.3333 | 37.9136 | 69.9971 | 15.7719 | 309 | 1.0009 | 200.6337 | 499.7346 | 0
586 | 1108.5236 | 8.1238 | 123.5447 | 133.3606 | 43.9668 | 17.6059 | 125.0814 | 10.1189 | 24.2381 | 113.8023 | 170.3788 | 43.0128 | 374.0562 | 337.9609 | 566.9621 | 43.0934 | 82.3271 | 17.3355 | 341 | 1.2274 | 217.6314 | 529.0882 | 0.01241
587 | 1204.8195 | 7.4683 | 118.5086 | 143.7871 | 44.2521 | 17.3348 | 122.2624 | 10.7243 | 28.976 | 121.4735 | 170.8894 | 42.8351 | 405.1242 | 373.35 | 606.5866 | 44.6931 | 93.8985 | 16.6984 | 355 | 1.381 | 228.308 | 521.9997 | 0.040499
588 | 1217.1695 | 6.5921 | 123.2479 | 141.5033 | 43.0397 | 18.4866 | 126.2347 | 10.8367 | 27.8536 | 116.2079 | 183.4485 | 42.4686 | 425.3793 | 382.5407 | 615.8103 | 43.4732 | 97.5831 | 17.4211 | 345 | 1.648 | 235.0418 | 524.0932 | 0.046034
589 | 1197.2751 | 5.1733 | 124.3391 | 143.5354 | 41.781 | 19.6823 | 132.1112 | 11.0157 | 23.8673 | 107.1234 | 186.9036 | 43.5483 | 432.8912 | 376.0132 | 620.766 | 44.6524 | 96.1442 | 18.7367 | 354 | 1.827 | 233.4112 | 531.0951 | 0.048592
590 | 1204.3537 | 4.2357 | 123.8232 | 146.0011 | 42.2209 | 19.2645 | 119.7765 | 11.2436 | 28.822 | 112.3136 | 185.6911 | 44.4858 | 428.4729 | 367.8379 | 624.7465 | 47.669 | 96.4547 | 19.2433 | 368 | 0.74448 | 226.0415 | 549.1814 | 0.027847
591 | 1199.5434 | 3.5433 | 124.2071 | 147.4898 | 42.5087 | 18.9911 | 123.3503 | 11.1991 | 28.9033 | 113.1338 | 184.4672 | 46.7888 | 444.7117 | 369.9594 | 610.9042 | 48.7143 | 93.8186 | 19.4263 | 337 | 1.1185 | 235.2441 | 544.7245 | 0.024276
592 | 1177.0656 | 4.6874 | 121.9926 | 146.2353 | 42.4248 | 19.0707 | 126.1537 | 10.7109 | 19.946 | 106.2625 | 183.6909 | 46.1541 | 439.5519 | 370.3708 | 586.8933 | 45.2376 | 93.1158 | 19.9855 | 278 | 0.94261 | 222.5564 | 529.7046 | 0.0059166
593 | 1139.343 | 5.0742 | 114.9085 | 142.2717 | 50.2815 | 11.6069 | 110.6222 | 9.8204 | 16.7867 | 97.6152 | 185.5263 | 43.3683 | 412.9483 | 352.7072 | 543.3772 | 35.6485 | 90.2937 | 19.9671 | 256 | -0.63165 | 206.3116 | 486.1648 | 0
594 | 1082.0975 | 5.437 | 104.2673 | 131.7123 | 54.0988 | 7.9804 | 98.4631 | 8.1743 | 17.3067 | 90.607 | 177.6366 | 40.9954 | 345.8759 | 275.6089 | 471.6783 | 20.4571 | 82.0342 | 18.2737 | 236 | -1.1398 | 170.5918 | 401.9727 | 0
595 | 1016.3587 | 4.9881 | 99.1911 | 116.7444 | 54.4168 | 7.6783 | 92.8009 | 6.6121 | 18.9353 | 84.8475 | 148.8926 | 34.6113 | 284.0894 | 212.0167 | 411.7338 | 12.4071 | 74.246 | 16.5331 | 224 | -1.1868 | 154.8031 | 356.2709 | 0
596 | 966.4566 | 4.1536 | 86.6603 | 109.8068 | 55.3319 | 6.809 | 72.9249 | 6.1897 | 20.7407 | 60.4681 | 118.7032 | 18.1976 | 247.662 | 190.6471 | 345.8509 | 10.0036 | 68.8682 | 15.2433 | 192 | -1.1689 | 135.6156 | 315.5595 | 0
597 | 918.0343 | 4.0119 | 62.952 | 105.2138 | 54.6874 | 7.4212 | 64.8959 | 6.4336 | 18.6829 | 49.6844 | 107.8264 | 13.3227 | 210.6421 | 186.78 | 290.3488 | 9.1871 | 62.5491 | 14.667 | 173 | -1.1053 | 120.7497 | 299.2644 | 0
598 | 871.6761 | 3.7507 | 55.2033 | 101.5582 | 54.4891 | 7.6097 | 73.8751 | 6.2765 | 10.4336 | 47.7505 | 105.7458 | 12.1988 | 191.5279 | 153.2645 | 256.5193 | 9.1222 | 58.5167 | 16.2652 | 150 | -1.1656 | 115.4334 | 292.3095 | 0
599 | 839.2 | 3.2989 | 54.4109 | 100.6805 | 55.2646 | 6.873 | 72.8388 | 6.3455 | 7.3188 | 39.0117 | 95.863 | 9.7281 | 184.2168 | 126.2149 | 234.937 | 9.0482 | 56.5151 | 14.3269 | 138 | -1.2501 | 108.4479 | 290.7179 | 0
600 | 817.2742 | 1.8572 | 54.0652 | 99.7757 | 54.7212 | 7.3892 | 63.5107 | 6.9014 | 7.0053 | 33.8258 | 84.8637 | 8.3996 | 165.239 | 112.6324 | 233.4509 | 9.0717 | 56.0228 | 12.2722 | 114 | -1.2193 | 79.1138 | 288.8653 | 0
601 | 818.8674 | 1.3473 | 54.1551 | 99.1897 | 54.59 | 7.5138 | 68.8473 | 6.6894 | 6.6348 | 33.3427 | 81.7577 | 7.9626 | 164.9532 | 107.5661 | 230.9211 | 9.0054 | 56.1969 | 11.804 | 111 | -1.1992 | 66.789 | 282.4103 | 0
602 | 812.5677 | 1.5975 | 54.098 | 99.0437 | 55.2265 | 6.9092 | 74.228 | 6.431 | 6.5003 | 33.479 | 84.6932 | 7.8608 | 173.0868 | 106.1946 | 222.6342 | 8.9853 | 56.0268 | 11.752 | 109 | -1.1927 | 66.8638 | 273.6055 | 0
603 | 804.046 | 1.4326 | 54.0183 | 98.5966 | 54.6738 | 7.4342 | 74.8078 | 6.3422 | 6.5848 | 33.4145 | 88.3229 | 7.8112 | 169.5914 | 105.8864 | 222.1118 | 8.9365 | 55.7993 | 11.7514 | 122 | -1.2121 | 66.2288 | 274.5765 | 0
604 | 797.1119 | 1.2231 | 53.972 | 99.228 | 54.5359 | 7.5653 | 75.2451 | 6.4467 | 6.51 | 36.3581 | 90.0222 | 7.8116 | 156.6703 | 110.9419 | 228.2246 | 8.9556 | 55.5642 | 11.7174 | 106 | -1.2216 | 65.1076 | 270.9927 | 0
605 | 798.4471 | 1.6655 | 53.9456 | 99.2192 | 55.2929 | 6.8461 | 68.262 | 6.7362 | 6.4355 | 47.1109 | 89.0076 | 7.8498 | 150.7488 | 123.3956 | 231.3804 | 9.1315 | 57.3053 | 11.7407 | 104 | -1.2021 | 65.6156 | 291.1053 | 0
606 | 812.4125 | 3.1347 | 64.0352 | 99.3354 | 53.8895 | 8.1793 | 65.1831 | 6.5597 | 6.5061 | 61.0856 | 85.0222 | 10.0333 | 162.9571 | 129.4901 | 237.9677 | 9.054 | 60.8912 | 11.7516 | 106 | -1.1928 | 68.0836 | 318.5168 | 0
607 | 852.6948 | 4.0932 | 78.7894 | 105.6124 | 52.7503 | 9.2615 | 82.6026 | 6.4154 | 8.8198 | 93.6592 | 101.8478 | 20.3632 | 207.602 | 183.5153 | 268.2282 | 12.2289 | 59.0353 | 11.7347 | 175 | -0.43563 | 111.3449 | 369.5536 | 0
608 | 922.5031 | 5.1737 | 102.8935 | 112.7128 | 47.8888 | 13.88 | 112.2051 | 7.6324 | 17.1936 | 109.7257 | 144.7429 | 36.1987 | 277.0441 | 247.5798 | 348.6813 | 28.0812 | 64.0425 | 13.1347 | 232 | 1.9798 | 167.2668 | 433.7875 | 0
609 | 1008.6426 | 5.5099 | 115.7709 | 125.7185 | 46.4807 | 15.2176 | 119.0266 | 8.8975 | 17.979 | 95.2289 | 174.8432 | 43.3534 | 339.9836 | 289.3921 | 468.3448 | 37.1988 | 73.5827 | 16.3838 | 271 | 1.4844 | 200.6927 | 496.1029 | 0
610 | 1098.8485 | 3.8945 | 120.1114 | 139.141 | 44.1394 | 17.4419 | 121.3591 | 8.9278 | 20.1793 | 90.8285 | 184.9763 | 41.1446 | 376.2125 | 322.755 | 535.0659 | 39.848 | 83.4327 | 18.2745 | 317 | 1.9485 | 226.2704 | 523.9788 | 0.048017
611 | 1149.182 | 6.489 | 119.8537 | 146.6916 | 42.0051 | 19.4695 | 127.8637 | 8.7726 | 25.9409 | 90.8366 | 188.2027 | 40.7346 | 397.2729 | 353.7908 | 582.4665 | 42.728 | 91.9142 | 19.3715 | 340 | 3.5012 | 238.3422 | 557.0884 | 0.074442
612 | 1164.8413 | 8.9367 | 122.3714 | 146.4331 | 44.5054 | 17.0942 | 130.7347 | 7.5492 | 25.0457 | 101.9713 | 188.6007 | 39.1488 | 415.2521 | 370.6101 | 625.2358 | 42.4648 | 92.5277 | 19.3362 | 341 | 3.2316 | 245.1203 | 559.9372 | 0.10632
613 | 1144.3854 | 7.8039 | 122.1915 | 139.3647 | 46.3195 | 15.3708 | 130.8809 | 7.4405 | 20.8668 | 113.2839 | 186.7551 | 41.8685 | 415.9864 | 367.2698 | 626.7654 | 43.1924 | 89.957 | 19.5236 | 354 | 2.4904 | 239.6698 | 560.1674 | 0.083502
614 | 1135.2211 | 6.7645 | 124.1673 | 143.7552 | 44.1754 | 17.4077 | 127.7384 | 7.81 | 23.0053 | 109.7124 | 191.8381 | 43.8038 | 425.9759 | 386.8052 | 622.0265 | 46.4619 | 90.9598 | 19.9223 | 300 | 2.5639 | 232.5985 | 582.5365 | 0.052846
615 | 1146.809 | 5.8766 | 120.1407 | 149.9994 | 44.287 | 17.3017 | 119.6576 | 8.4623 | 24.1413 | 107.2633 | 196.2825 | 44.7641 | 434.214 | 395.1601 | 639.0013 | 48.8246 | 93.12 | 19.2373 | 313 | 2.6696 | 232.9702 | 581.3016 | 0.01934
616 | 1113.8722 | 5.687 | 118.785 | 149.7107 | 43.8458 | 17.7208 | 124.4548 | 8.7626 | 19.3579 | 105.0862 | 191.7423 | 39.5251 | 429.0526 | 372.1941 | 617.4531 | 44.9094 | 92.1721 | 17.8059 | 269 | 1.9538 | 230.662 | 562.2696 | 0.019385
617 | 1101.7269 | 5.7214 | 114.4874 | 143.5173 | 48.0259 | 13.7498 | 115.6342 | 8.3404 | 17.4131 | 107.6531 | 187.0013 | 35.7644 | 404.752 | 339.893 | 561.9538 | 35.4193 | 89.116 | 16.9344 | 256 | 0.48854 | 218.7313 | 526.6655 | 0
618 | 1054.2844 | 5.7597 | 107.7166 | 132.7158 | 53.4064 | 8.6382 | 95.4081 | 6.9467 | 15.159 | 99.8332 | 181.1088 | 30.0047 | 348.2329 | 271.5953 | 455.6866 | 23.3555 | 80.9937 | 15.6896 | 227 | -0.30271 | 187.8025 | 426.8168 | 0
619 | 1011.5434 | 5.3033 | 104.5215 | 119.4242 | 54.5549 | 7.5471 | 92.8292 | 5.8617 | 12.0982 | 86.798 | 151.9042 | 24.3413 | 304.8341 | 211.6506 | 387.0367 | 21.4227 | 71.3567 | 14.561 | 222 | -0.27624 | 173.6596 | 375.0004 | 0
620 | 965.3252 | 5.1878 | 93.5646 | 110.0188 | 53.7166 | 8.3436 | 86.7878 | 5.5584 | 13.0049 | 60.7311 | 124.0935 | 13.5911 | 270.8143 | 180.5418 | 341.2197 | 15.4563 | 65.546 | 13.558 | 198 | -0.30516 | 154.6441 | 328.4565 | 0
621 | 906.0962 | 4.7033 | 65.0784 | 104.4156 | 54.2628 | 7.8246 | 75.2421 | 5.2724 | 8.9004 | 51.5187 | 129.2142 | 9.6299 | 242.156 | 158.488 | 307.4976 | 11.419 | 61.216 | 12.8548 | 172 | -0.41413 | 136.0202 | 308.9471 | 0
622 | 878.8561 | 4.0019 | 55.4004 | 102.8854 | 54.4399 | 7.6564 | 67.7265 | 4.93 | 6.8038 | 48.1527 | 119.5867 | 11.5554 | 198.7194 | 144.3275 | 265.2656 | 11.1991 | 58.4384 | 13.9349 | 151 | -0.43406 | 129.2551 | 295.4982 | 0
623 | 852.0731 | 3.2122 | 55.2431 | 100.1091 | 54.518 | 7.5822 | 66.5975 | 4.907 | 6.3193 | 39.4889 | 93.9907 | 10.1217 | 182.7609 | 133.4483 | 233.6168 | 11.1605 | 56.7267 | 13.835 | 138 | -0.42129 | 122.7599 | 292.8324 | 0
624 | 832.7982 | 2.0103 | 55.3755 | 98.1127 | 54.4666 | 7.6311 | 76.2653 | 5.0586 | 6.0527 | 37.1161 | 85.6222 | 9.3247 | 178.9808 | 126.8229 | 207.3799 | 11.2144 | 56.3576 | 12.3301 | 125 | -0.45017 | 96.1692 | 293.0419 | 0
625 | 833.5462 | 1.4647 | 55.3479 | 98.0339 | 54.5538 | 7.5482 | 81.9566 | 4.9298 | 6.098 | 38.68 | 85.7788 | 9.1797 | 178.0951 | 122.6621 | 205.1582 | 11.1477 | 56.7372 | 11.8104 | 117 | -0.34031 | 86.185 | 292.1498 | 0
626 | 827.9546 | 1.3309 | 55.3382 | 98.011 | 54.4847 | 7.6138 | 77.81 | 5.1809 | 6.0419 | 38.7885 | 83.7729 | 7.9869 | 175.1981 | 119.4727 | 204.9744 | 11.1781 | 56.8593 | 11.8502 | 111 | -0.37516 | 86.3306 | 287.7839 | 0
627 | 836.4785 | 1.4889 | 55.2935 | 97.8442 | 54.4702 | 7.6276 | 70.1077 | 5.3827 | 6.1777 | 38.9709 | 83.1792 | 7.5814 | 173.0473 | 119.8127 | 202.7065 | 11.1121 | 57.7314 | 11.8279 | 127 | -0.40441 | 85.2642 | 290.2077 | 0
628 | 836.5851 | 1.4019 | 55.0773 | 98.4463 | 54.5059 | 7.5937 | 76.3854 | 5.3483 | 6.2924 | 41.524 | 83.7577 | 7.547 | 169.6345 | 119.5225 | 204.2069 | 11.1556 | 57.465 | 11.8422 | 105 | -0.38343 | 81.0952 | 285.4661 | 0
629 | 820.6235 | 1.7955 | 54.9845 | 98.574 | 54.5472 | 7.5544 | 80.5234 | 5.5222 | 6.2846 | 51.0958 | 83.6812 | 7.5275 | 157.4598 | 118.6379 | 203.8607 | 11.1323 | 58.7395 | 11.8159 | 103 | -0.33214 | 78.3959 | 295.8038 | 0
630 | 834.3542 | 2.9178 | 64.7733 | 98.5832 | 54.4592 | 7.6381 | 81.8017 | 5.392 | 6.4643 | 64.4269 | 83.733 | 9.9313 | 169.2777 | 125.0331 | 220.4147 | 11.0928 | 61.0591 | 12.028 | 107 | -0.43658 | 79.9086 | 325.9001 | 0
631 | 865.4905 | 3.9972 | 77.214 | 108.2032 | 52.9408 | 9.0806 | 89.3632 | 5.6466 | 6.8624 | 89.7777 | 101.8194 | 21.2133 | 208.3715 | 178.997 | 252.6706 | 14.4308 | 58.6777 | 12.348 | 176 | -0.069923 | 126.709 | 356.9556 | 0
632 | 935.4781 | 5.3639 | 99.9607 | 113.7198 | 47.0629 | 14.6645 | 103.2112 | 6.3795 | 13.9173 | 108.115 | 142.8376 | 37.8204 | 283.2193 | 244.1534 | 333.0391 | 28.3192 | 63.2092 | 14.5311 | 252 | 0.8084 | 175.9651 | 429.7131 | 0
633 | 1034.8874 | 6.0721 | 115.8659 | 124.2197 | 45.6375 | 16.0186 | 123.9157 | 8.7239 | 17.2955 | 111.3926 | 169.3312 | 43.4569 | 334.9887 | 298.4365 | 453.2538 | 38.4356 | 74.1 | 17.8054 | 330 | 1.1372 | 205.4369 | 491.5686 | 0
634 | 1116.9382 | 4.7811 | 117.6192 | 134.5043 | 44.5942 | 17.0098 | 134.6119 | 8.2931 | 20.6907 | 122.1724 | 179.281 | 42.0556 | 384.9793 | 332.5728 | 532.2113 | 43.1214 | 85.7127 | 17.6282 | 367 | 0.97757 | 225.4763 | 525.5084 | 0.010004
635 | 1150.5938 | 3.8344 | 114.4631 | 147.1447 | 46.0278 | 15.6479 | 139.3011 | 7.5026 | 25.8348 | 120.0153 | 188.0164 | 43.0001 | 410.1389 | 353.552 | 565.6779 | 45.3646 | 93.1 | 18.795 | 358 | 1.0761 | 236.479 | 535.0579 | 0.034872
636 | 1183.4293 | 4.0773 | 114.5116 | 149.0841 | 43.4127 | 18.1322 | 141.8962 | 7.2579 | 24.5135 | 131.4371 | 197.1399 | 43.0072 | 429.5449 | 369.0631 | 572.8855 | 43.3263 | 94.7628 | 19.3293 | 328 | 1.0896 | 230.6766 | 551.7046 | 0.0219
637 | 1168.6017 | 5.0418 | 115.407 | 147.6055 | 41.8885 | 19.5802 | 140.3155 | 7.3689 | 20.8968 | 115.863 | 192.8018 | 43.0055 | 437.7381 | 371.2898 | 566.8967 | 45.3042 | 92.2729 | 19.4189 | 381 | 1.2557 | 235.0331 | 568.1726 | 0.019495
638 | 1190.574 | 4.4753 | 114.5407 | 149.0979 | 41.539 | 19.9122 | 137.6973 | 7.5427 | 24.266 | 114.6885 | 187.8429 | 43.7674 | 437.8536 | 370.7305 | 578.0864 | 45.6062 | 92.8036 | 19.4806 | 324 | 1.0512 | 245.713 | 555.9824 | 0.0082304
639 | 1184.0705 | 4.7571 | 115.3366 | 152.9748 | 44.4671 | 17.1306 | 137.2555 | 7.1901 | 24.2679 | 115.0515 | 188.3882 | 45.3569 | 444.7791 | 390.4692 | 596.955 | 45.8013 | 95.2789 | 19.5569 | 324 | 1.0738 | 247.9645 | 562.3926 | 0.003858
640 | 1160.854 | 5.4099 | 114.334 | 150.7881 | 42.2406 | 19.2458 | 137.0323 | 7.0671 | 19.4008 | 112.4836 | 186.4488 | 45.2291 | 435.6987 | 362.8736 | 589.8723 | 42.9499 | 95.0975 | 19.5564 | 307 | 0.69302 | 238.8973 | 553.2493 | 0.0016628
641 | 1121.9212 | 5.7045 | 108.8798 | 143.7298 | 46.9126 | 14.8073 | 127.4422 | 6.9516 | 18.1367 | 114.0963 | 189.6972 | 43.4379 | 398.4269 | 340.3978 | 554.0328 | 36.8112 | 90.2444 | 18.7545 | 257 | -0.30362 | 214.2197 | 514.8172 | 0
642 | 1065.9229 | 5.4098 | 98.3048 | 127.3409 | 50.1618 | 11.7206 | 119.9388 | 6.2736 | 17.8954 | 98.1956 | 186.1878 | 38.7904 | 340.8927 | 270.4974 | 454.812 | 25.1355 | 83.7108 | 17.0443 | 251 | -0.80969 | 176.9117 | 434.9735 | 0
643 | 1015.774 | 5.2314 | 94.5821 | 112.2306 | 52.8416 | 9.1747 | 105.6606 | 5.4625 | 17.4112 | 81.3529 | 156.6779 | 28.9825 | 295.5732 | 213.0003 | 378.7123 | 19.8283 | 78.2776 | 17.2802 | 224 | -0.98973 | 160.9512 | 377.4741 | 0
644 | 970.5064 | 4.6254 | 83.682 | 105.8933 | 53.5207 | 8.5296 | 88.3367 | 5.2303 | 16.2684 | 55.31 | 125.399 | 13.1963 | 258.8101 | 193.0429 | 312.2657 | 17.0569 | 70.4133 | 17.4037 | 211 | -1.012 | 141.1856 | 321.784 | 0
645 | 934.1432 | 4.107 | 63.0358 | 103.0197 | 52.7846 | 9.229 | 82.2713 | 4.6395 | 14.5899 | 45.2489 | 118.5498 | 8.2325 | 226.798 | 166.832 | 263.901 | 12.304 | 61.9398 | 16.7554 | 182 | -0.95297 | 132.5212 | 303.2848 | 0
646 | 906.7138 | 4.0238 | 56.1983 | 100.9536 | 53.9807 | 8.0926 | 80.8314 | 4.6181 | 9.5263 | 41.6099 | 112.2337 | 8.4666 | 191.9723 | 148.413 | 242.7515 | 9.407 | 58.4417 | 15.365 | 176 | -0.98837 | 127.0597 | 298.159 | 0
647 | 876.8354 | 3.2145 | 55.71 | 98.4176 | 53.732 | 8.3289 | 80.1899 | 4.9598 | 7.0368 | 36.5326 | 94.3919 | 8.2851 | 173.5793 | 131.1789 | 230.6609 | 8.5037 | 57.8759 | 14.4876 | 154 | -1.0039 | 119.2986 | 297.6169 | 0
648 | 849.6671 | 3.2233 | 55.2802 | 97.8316 | 53.4758 | 8.5723 | 80.0045 | 4.9874 | 6.665 | 32.8646 | 86.8193 | 8.1608 | 164.5487 | 116.3748 | 208.6468 | 8.5557 | 57.9233 | 13.3146 | 131 | -0.9489 | 90.5754 | 293.2073 | 0
649 | 840.5421 | 6.339 | 54.6896 | 97.8558 | 54.2565 | 7.8306 | 79.5304 | 4.9592 | 6.6155 | 32.0789 | 85.8009 | 8.0587 | 154.6998 | 112.4357 | 201.6184 | 8.661 | 57.3858 | 12.1842 | 114 | -1.0456 | 78.9292 | 291.0464 | 0
650 | 846.2123 | 3.5198 | 50.034 | 97.789 | 53.7379 | 8.3233 | 79.1177 | 5.6228 | 6.6101 | 34.4257 | 85.3603 | 8.0499 | 159.1211 | 108.1799 | 199.5138 | 9.2849 | 57.1388 | 11.5536 | 114 | -1.0736 | 80.0721 | 280.7781 | 0
651 | 841.7422 | 1.4259 | 48.4394 | 98.7992 | 54.2609 | 7.8264 | 79.2189 | 5.5738 | 6.742 | 33.8503 | 86.0219 | 8.1833 | 158.8772 | 106.6987 | 196.969 | 9.5012 | 57.2012 | 11.4612 | 131 | -0.95234 | 84.1915 | 280.8194 | 0
652 | 828.8117 | 1.4351 | 48.4961 | 99.6084 | 53.764 | 8.2985 | 69.5484 | 5.2404 | 6.5425 | 36.1869 | 87.1254 | 8.2019 | 155.8168 | 108.5005 | 202.5038 | 9.4289 | 57.3766 | 11.478 | 106 | -0.94278 | 84.8144 | 284.3281 | 0
653 | 832.8312 | 1.9117 | 48.4779 | 98.5964 | 54.2172 | 7.868 | 66.3956 | 5.4029 | 6.3468 | 46.8474 | 87.4632 | 8.1829 | 151.2951 | 116.8817 | 206.8633 | 9.427 | 58.8138 | 11.479 | 105 | -1.0096 | 84.4277 | 294.9487 | 0
654 | 836.1582 | 3.5015 | 50.2729 | 98.297 | 53.7523 | 8.3096 | 75.9333 | 5.5815 | 6.5434 | 61.0995 | 92.9301 | 10.5713 | 173.8732 | 125.3902 | 217.3338 | 9.3881 | 61.0712 | 11.4749 | 108 | -1.0688 | 87.0256 | 326.9064 | 0
655 | 870.0975 | 4.637 | 56.5964 | 105.8137 | 51.9234 | 10.0471 | 89.2773 | 5.6747 | 10.2087 | 89.0693 | 102.169 | 21.4631 | 199.1344 | 181.142 | 252.1529 | 12.6005 | 58.8491 | 12.5871 | 184 | 0.24404 | 127.6115 | 369.3447 | 0
656 | 925.1932 | 5.4933 | 86.6911 | 113.1025 | 47.5324 | 14.2185 | 107.8189 | 6.3965 | 18.902 | 108.7279 | 144.2403 | 35.824 | 279.988 | 243.0724 | 353.0129 | 27.7267 | 65.5343 | 14.1075 | 289 | 2.6002 | 168.196 | 434.5038 | 0
657 | 1008.6294 | 6.8162 | 102.5861 | 122.3287 | 45.8413 | 15.8251 | 116.2924 | 6.984 | 22.8813 | 106.2282 | 173.8908 | 41.3024 | 345.2334 | 287.2236 | 456.8459 | 37.029 | 75.7434 | 17.2707 | 319 | 3.7153 | 200.9643 | 499.3094 | 0
658 | 1118.0728 | 5.2584 | 113.5522 | 137.0419 | 41.5213 | 19.929 | 130.5205 | 7.2602 | 23.2184 | 106.879 | 190.385 | 40.9104 | 394.51 | 330.1282 | 521.1336 | 41.5999 | 86.4959 | 18.5845 | 336 | 4.0958 | 230.2895 | 538.1673 | 0.046193
659 | 1171.4821 | 4.2848 | 118.345 | 148.7802 | 42.8939 | 18.6251 | 135.1507 | 8.1667 | 21.7243 | 114.197 | 195.4394 | 41.5842 | 413.8698 | 358.1984 | 557.5765 | 43.2 | 94.8294 | 18.0452 | 377 | 4.2042 | 240.6856 | 551.6211 | 0.065674
660 | 1198.3516 | 3.7065 | 118.9247 | 145.117 | 40.4798 | 20.9185 | 135.2831 | 9.0005 | 21.7793 | 114.1804 | 199.5056 | 42.2543 | 420.34 | 373.965 | 574.4598 | 43.76 | 96.6726 | 17.6827 | 338 | 4.9368 | 243.5567 | 562.7698 | 0.1368
661 | 1193.4171 | 4.0343 | 115.4687 | 141.346 | 44.2135 | 17.3715 | 135.9291 | 9.0136 | 24.7047 | 104.5567 | 196.6376 | 41.173 | 413.2006 | 352.0409 | 564.7371 | 44.2549 | 93.0119 | 17.8735 | 362 | 4.4698 | 235.9291 | 560.8012 | 0.09085
662 | 1198.486 | 4.209 | 116.3517 | 145.1068 | 46.9468 | 14.7748 | 137.7146 | 9.1028 | 24.3263 | 107.278 | 202.2775 | 41.0962 | 411.8406 | 342.4991 | 582.6541 | 44.2647 | 93.4882 | 18.2855 | 371 | 3.946 | 215.0171 | 555.0272 | 0.075795
663 | 1206.7429 | 4.065 | 115.3615 | 148.1698 | 47.5166 | 14.2336 | 134.972 | 8.9047 | 23.0631 | 112.9948 | 202.7895 | 41.7753 | 414.5433 | 353.8257 | 559.9228 | 44.632 | 94.053 | 18.2041 | 326 | 2.8956 | 214.7192 | 553.5583 | 0.064449
664 | 1192.8529 | 4.4149 | 114.6654 | 144.7755 | 47.4973 | 14.2518 | 132.3968 | 7.9547 | 17.5817 | 108.9848 | 199.3263 | 43.3132 | 405.8475 | 347.4048 | 541.7731 | 41.705 | 91.977 | 18.3489 | 277 | 2.2655 | 217.0827 | 551.5765 | 0.014666
665 | 1152.6455 | 5.6971 | 110.1342 | 140.0464 | 52.0734 | 9.9046 | 119.8278 | 7.6231 | 14.4856 | 103.9307 | 195.1001 | 41.0656 | 388.4287 | 333.8441 | 501.1406 | 34.3778 | 87.6645 | 18.337 | 258 | 1.6445 | 212.7434 | 516.7864 | 0
666 | 1082.1021 | 5.7918 | 102.2435 | 133.6962 | 53.5418 | 8.5096 | 117.4337 | 6.5388 | 14.0991 | 94.3218 | 188.6572 | 37.6967 | 351.2075 | 269.7071 | 443.799 | 20.8105 | 85.4991 | 18.1508 | 226 | 1.7286 | 192.5757 | 432.4961 | 0
667 | 1004.1052 | 5.2838 | 96.877 | 117.8177 | 53.4836 | 8.5649 | 103.5701 | 5.7225 | 15.4029 | 86.8885 | 156.7222 | 31.1068 | 289.792 | 204.8212 | 379.2648 | 13.6806 | 75.7314 | 17.2784 | 221 | 2.0318 | 176.2157 | 371.4783 | 0
668 | 955.143 | 4.1419 | 85.4078 | 109.3607 | 55.0979 | 7.0313 | 76.9492 | 5.5842 | 10.5088 | 86.1336 | 121.5121 | 23.0893 | 258.9805 | 175.3378 | 318.3176 | 12.4954 | 66.7486 | 16.3311 | 195 | 2.1952 | 157.3118 | 323.2011 | 0
669 | 922.8431 | 3.8335 | 63.1611 | 105.9753 | 54.764 | 7.3485 | 73.3271 | 5.7234 | 10.5125 | 86.8238 | 109.5163 | 20.3076 | 229.3874 | 145.2881 | 258.4856 | 11.7308 | 61.2174 | 15.6393 | 186 | 2.2738 | 144.9624 | 306.3706 | 0
670 | 900.4792 | 3.9282 | 55.8002 | 103.0482 | 55.9971 | 6.177 | 79.984 | 5.4407 | 7.9876 | 85.6015 | 103.5239 | 18.3346 | 207.1972 | 127.4949 | 216.2717 | 11.3598 | 58.615 | 14.8956 | 164 | 2.2596 | 138.1107 | 298.8901 | 0
671 | 879.7248 | 3.2619 | 55.5831 | 101.1798 | 56.4798 | 5.7185 | 73.2875 | 5.3945 | 6.387 | 76.3889 | 90.0949 | 10.6502 | 190.9758 | 113.9331 | 209.0073 | 11.3588 | 58.0511 | 14.0394 | 142 | 2.2295 | 128.1758 | 297.7106 | 0
672 | 857.2375 | 2.0758 | 55.3367 | 101.599 | 55.7716 | 6.3913 | 70.9575 | 5.7084 | 6.2261 | 68.213 | 84.6642 | 7.7522 | 173.0285 | 111.6183 | 206.2329 | 11.3717 | 57.2967 | 13.1916 | 117 | 2.0667 | 97.8475 | 297.48 | 0
673 | 850.9458 | 1.5042 | 55.2876 | 101.3954 | 56.2699 | 5.9179 | 78.2656 | 5.8878 | 6.1445 | 53.3445 | 84.3903 | 7.7168 | 165.0697 | 110.1373 | 222.8923 | 11.4789 | 56.9075 | 12.493 | 109 | 1.8171 | 84.5373 | 282.1767 | 0
674 | 853.1205 | 1.526 | 55.2932 | 102.1099 | 56.4881 | 5.7106 | 80.2196 | 5.7109 | 6.1415 | 48.5713 | 84.6226 | 7.7773 | 164.6039 | 106.9061 | 227.7018 | 11.4376 | 57.1432 | 12.024 | 113 | 1.716 | 82.6916 | 273.7833 | 0
675 | 850.4022 | 1.6467 | 55.4057 | 100.7312 | 55.7394 | 6.4219 | 71.2989 | 5.7288 | 6.1572 | 49.0729 | 85.0009 | 7.7854 | 165.1105 | 104.1274 | 219.1995 | 11.4463 | 57.0326 | 11.7587 | 125 | 1.7129 | 82.8025 | 267.958 | 0
676 | 847.2174 | 1.4124 | 55.3606 | 100.2932 | 56.2383 | 5.9479 | 71.1381 | 5.9965 | 6.1619 | 50.4395 | 85.7678 | 7.7598 | 164.7013 | 103.7691 | 214.8945 | 11.4889 | 57.0223 | 11.69 | 105 | 1.8027 | 77.9965 | 264.1767 | 0
677 | 843.3631 | 1.9328 | 55.3197 | 99.8526 | 55.7348 | 6.4263 | 79.2486 | 5.774 | 6.3001 | 57.0425 | 85.7898 | 7.7113 | 162.5218 | 112.5575 | 213.0553 | 11.3868 | 58.76 | 11.6709 | 101 | 1.7298 | 74.4328 | 285.0339 | 0
678 | 851.6337 | 2.9684 | 56.6305 | 100.0301 | 56.2722 | 5.9157 | 82.7174 | 5.5914 | 6.4307 | 70.1598 | 86.0442 | 9.5265 | 171.7895 | 123.7198 | 222.1959 | 11.4678 | 61.0011 | 11.6518 | 104 | 1.6216 | 75.7252 | 311.4393 | 0
679 | 888.8986 | 4.07 | 62.9239 | 108.1983 | 54.1749 | 7.9081 | 84.5139 | 5.9845 | 6.79 | 96.3438 | 109.3342 | 20.9389 | 224.3626 | 175.738 | 248.7114 | 14.5766 | 58.9791 | 11.6368 | 167 | 1.6671 | 99.8421 | 348.8073 | 0
680 | 957.6094 | 5.4666 | 89.3337 | 112.0948 | 48.2092 | 13.5756 | 101.0367 | 6.8827 | 13.6505 | 109.852 | 148.8631 | 34.8555 | 270.8797 | 241.88 | 331.9074 | 27.7294 | 64.0938 | 13.3047 | 234 | 2.0038 | 127.0155 | 429.6943 | 0
681 | 1044.0304 | 5.8043 | 102.0707 | 120.4385 | 44.8803 | 16.738 | 121.6278 | 8.1312 | 17.2901 | 104.7192 | 177.1164 | 36.1852 | 318.2358 | 288.4091 | 453.4585 | 38.0653 | 75.8558 | 16.2617 | 293 | 3.2512 | 158.6436 | 491.5168 | 0
682 | 1141.568 | 5.7131 | 110.8023 | 133.9588 | 46.8041 | 14.9104 | 128.8306 | 8.2466 | 21.0782 | 102.6029 | 190.8211 | 36.4977 | 379.0845 | 320.7431 | 557.6975 | 43.2899 | 85.7964 | 17.1406 | 338 | 1.7276 | 186.685 | 542.9343 | 0.014215
683 | 1170.1907 | 6.5035 | 115.0587 | 146.3548 | 45.9659 | 15.7067 | 130.2611 | 8.5469 | 25.7082 | 111.1528 | 196.5442 | 41.7149 | 405.56 | 345.1935 | 591.8043 | 46.0054 | 89.4493 | 17.8271 | 373 | 0.45549 | 202.1069 | 561.7946 | 0.021238
684 | 1183.6948 | 7.9885 | 115.7237 | 146.1031 | 46.2937 | 15.3953 | 130.8946 | 9.0879 | 24.7697 | 106.0176 | 195.4937 | 42.9327 | 416.1821 | 360.3353 | 587.5183 | 43.8347 | 91.8364 | 17.8295 | 352 | 0.77424 | 211.0586 | 583.4235 | 0.017541
685 | 1183.8802 | 8.9554 | 113.5794 | 146.2551 | 47.2526 | 14.4844 | 130.8253 | 9.0069 | 19.7972 | 107.4038 | 192.4157 | 43.2419 | 408.271 | 357.3912 | 568.1742 | 44.9173 | 92.0557 | 18.2903 | 351 | 0.75598 | 216.7217 | 577.1753 | 0.026617
686 | 1183.8361 | 8.6332 | 113.0456 | 146.7514 | 47.5975 | 14.1566 | 132.1471 | 9.2642 | 20.559 | 122.5298 | 191.5247 | 41.5686 | 414.467 | 358.3852 | 570.3752 | 46.5077 | 93.3071 | 18.7745 | 310 | 0.35977 | 223.3378 | 562.7611 | 0.014441
687 | 1168.8459 | 6.4037 | 110.3663 | 150.0647 | 45.8564 | 15.8108 | 131.6756 | 9.4141 | 19.9246 | 111.4926 | 193.2178 | 38.2871 | 419.0383 | 353.4219 | 583.0275 | 44.2425 | 96.2918 | 18.5534 | 285 | 0.34246 | 228.7946 | 549.5591 | 0.011515
688 | 1140.9207 | 5.4844 | 107.2384 | 144.6337 | 45.4281 | 16.2176 | 127.0394 | 9.4231 | 20.9146 | 105.0837 | 188.7503 | 38.2983 | 398.6792 | 334.1172 | 554.4098 | 40.9856 | 95.9162 | 18.0068 | 302 | 0.45786 | 220.6138 | 536.3814 | 0.0020415
689 | 1095.9646 | 5.592 | 103.67 | 143.9049 | 53.2185 | 8.8167 | 117.1275 | 8.7825 | 20.698 | 103.6975 | 185.408 | 38.8538 | 362.3105 | 309.4872 | 500.535 | 27.947 | 92.6229 | 16.5532 | 270 | -0.11106 | 194.3971 | 480.6808 | 0
690 | 1026.8612 | 5.7121 | 89.884 | 126.809 | 56.3029 | 5.8866 | 104.0636 | 6.5007 | 17.088 | 95.4312 | 181.7308 | 34.8705 | 312.1871 | 245.9921 | 417.6373 | 18.104 | 86.4156 | 15.4501 | 246 | -0.20001 | 164.0529 | 377.4016 | 0
691 | 971.7243 | 4.5936 | 61.0694 | 111.0258 | 56.4615 | 5.7359 | 96.0036 | 4.9591 | 15.8947 | 80.7112 | 153.0203 | 29.5096 | 260.1956 | 171.9919 | 330.4462 | 13.066 | 76.7359 | 14.8069 | 222 | -0.18965 | 151.1369 | 310.6924 | 0
692 | 925.5583 | 3.7259 | 51.4722 | 104.5342 | 56.5466 | 5.6551 | 88.0887 | 4.7009 | 15.79 | 65.9762 | 118.4865 | 19.1969 | 222.0923 | 141.1234 | 282.3737 | 11.1786 | 64.7301 | 14.6562 | 205 | -0.13689 | 133.9373 | 278.7866 | 0
693 | 880.7471 | 3.6751 | 49.7725 | 103.699 | 56.5017 | 5.6977 | 94.3217 | 4.8354 | 13.1443 | 61.3278 | 97.3427 | 13.9345 | 197.4444 | 125.7384 | 258.1652 | 11.0984 | 58.8981 | 13.8235 | 196 | -0.15571 | 123.8786 | 245.7453 | 0
694 | 861.6815 | 3.288 | 49.4586 | 103.0606 | 55.737 | 6.4242 | 90.9213 | 4.9811 | 8.4437 | 60.4285 | 92.8642 | 9.9398 | 183.5821 | 115.3061 | 253.1071 | 10.5038 | 57.0161 | 12.5344 | 187 | -0.042956 | 120.7253 | 236.8209 | 0
695 | 849.9421 | 2.7419 | 48.7667 | 100.3605 | 56.2401 | 5.9462 | 84.5819 | 5.0278 | 6.9425 | 57.4106 | 91.191 | 8.6172 | 175.2226 | 108.4273 | 251.6866 | 10.2844 | 56.3564 | 11.8623 | 174 | -0.13562 | 117.8113 | 240.4379 | 0
696 | 831.0538 | 1.9952 | 48.5492 | 99.3063 | 56.496 | 5.7031 | 83.291 | 5.4458 | 6.8435 | 54.5341 | 87.6014 | 8.8255 | 182.2608 | 103.3197 | 251.4462 | 10.1537 | 56.8204 | 11.7005 | 148 | -0.088309 | 88.9894 | 232.9397 | 0
697 | 820.4981 | 1.6309 | 48.7634 | 99.206 | 56.4973 | 5.7019 | 82.2378 | 5.5317 | 6.2747 | 52.8424 | 86.0849 | 8.9041 | 185.7694 | 100.1903 | 260.9619 | 10.0385 | 57.3948 | 11.7882 | 143 | -0.15502 | 72.2107 | 223.2607 | 0
698 | 817.6041 | 1.6757 | 49.2864 | 99.0522 | 57.2909 | 4.948 | 73.1515 | 5.5774 | 6.0433 | 52.638 | 85.7667 | 8.6645 | 183.3574 | 96.8141 | 242.9288 | 10.0149 | 58.3029 | 11.9878 | 136 | -0.14303 | 68.5965 | 219.3109 | 0
699 | 814.6422 | 1.5719 | 48.7062 | 101.2036 | 56.7418 | 5.4696 | 73.7355 | 5.7899 | 6.0007 | 52.5112 | 85.9334 | 8.5919 | 177.3308 | 99.8195 | 225.6358 | 10.0554 | 56.9277 | 11.9612 | 154 | -0.20252 | 71.9619 | 230.5481 | 0
700 | 811.7545 | 1.6954 | 48.4793 | 101.8709 | 55.753 | 6.409 | 79.3014 | 6.0096 | 6.2173 | 52.9589 | 86.688 | 8.574 | 164.103 | 104.1004 | 220.3108 | 10.0016 | 55.9715 | 11.7222 | 130 | -0.22474 | 71.8349 | 228.4089 | 0
701 | 803.3537 | 2.0981 | 48.2211 | 101.1284 | 56.2475 | 5.9391 | 74.0645 | 5.8234 | 6.0944 | 55.183 | 87.1534 | 8.7501 | 157.5354 | 100.4868 | 217.9835 | 10.0406 | 57.8572 | 11.6559 | 127 | -0.21633 | 68.3223 | 220.1075 | 0
702 | 805.4685 | 3.0215 | 66.3718 | 100.0578 | 56.4881 | 5.7106 | 70.3495 | 5.6937 | 6.2707 | 67.3984 | 87.6255 | 8.6637 | 154.8224 | 95.0241 | 220.2839 | 9.9531 | 60.5997 | 11.6283 | 131 | -0.19764 | 65.9932 | 220.69 | 0
703 | 825.0735 | 3.3041 | 77.0065 | 99.8152 | 56.4474 | 5.7493 | 79.248 | 5.4692 | 6.1048 | 90.4721 | 90.2295 | 8.6393 | 153.3335 | 95.5037 | 221.5195 | 10.009 | 58.26 | 11.6055 | 134 | -0.10631 | 66.5606 | 226.551 | 0
704 | 842.6729 | 3.6171 | 85.6279 | 100.1631 | 56.5431 | 5.6584 | 82.9215 | 5.3927 | 6.0437 | 95.1747 | 96.959 | 10.3303 | 161.1236 | 97.8456 | 211.5754 | 11.2197 | 56.8909 | 11.8024 | 143 | 0.2632 | 70.1454 | 242.0032 | 0
705 | 846.7351 | 3.359 | 90.1176 | 98.4213 | 56.4432 | 5.7533 | 81.0029 | 5.1134 | 5.4589 | 83.6475 | 136.1865 | 13.984 | 183.6141 | 99.22 | 204.4788 | 14.1649 | 56.0877 | 12.2982 | 152 | 0.058799 | 76.9232 | 236.992 | 0
706 | 858.2526 | 2.4554 | 92.3292 | 98.2254 | 56.5551 | 5.647 | 79.5332 | 4.5304 | 5.3141 | 77.6731 | 161.2619 | 8.4207 | 196.2126 | 106.0502 | 199.7466 | 27.5388 | 57.3175 | 12.4063 | 163 | -0.078969 | 106.7248 | 219.463 | 0.017413
707 | 888.8732 | 2.4837 | 90.1797 | 98.7362 | 55.7336 | 6.4274 | 77.8473 | 4.3723 | 5.2812 | 77.4353 | 166.4021 | 6.0216 | 220.5259 | 110.2188 | 191.0521 | 37.0627 | 57.6735 | 12.3935 | 182 | -0.001982 | 122.0126 | 224.0206 | 0.022355
708 | 898.6991 | 2.4388 | 89.9781 | 99.7268 | 54.7549 | 7.3572 | 68.7413 | 4.3904 | 5.1673 | 80.4966 | 165.1974 | 6.053 | 233.3836 | 119.7338 | 202.2835 | 38.385 | 58.5681 | 12.4167 | 208 | -0.010065 | 126.0946 | 247.2629 | 0.06897
709 | 908.6891 | 2.0207 | 90.8159 | 101.4477 | 55.2016 | 6.9328 | 72.0756 | 4.4516 | 8.8303 | 82.2961 | 155.1935 | 6.0849 | 230.8024 | 119.4107 | 222.7532 | 37.3333 | 59.3141 | 13.1439 | 197 | -0.069105 | 129.3022 | 247.213 | 0.067049
710 | 899.3761 | 1.5082 | 85.6825 | 102.7715 | 55.508 | 6.6417 | 78.2683 | 5.5994 | 11.7791 | 79.2675 | 123.5673 | 6.0524 | 227.6523 | 121.0247 | 230.2548 | 36.1043 | 58.1549 | 13.8955 | 206 | 0.00623 | 125.6711 | 249.7851 | 0.090128
711 | 894.0095 | 1.8418 | 68.4536 | 101.8878 | 56.2723 | 5.9156 | 75.5204 | 7.296 | 9.4893 | 75.2747 | 111.0742 | 7.5448 | 220.232 | 123.2354 | 227.7403 | 30.4588 | 57.8348 | 14.1745 | 207 | -0.046389 | 127.1128 | 242.8769 | 0.067927
712 | 894.9041 | 2.472 | 62.7776 | 101.0272 | 55.7295 | 6.4313 | 69.2573 | 8.7289 | 10.5573 | 58.1099 | 111.5027 | 11.244 | 207.0364 | 130.1103 | 218.9503 | 15.6368 | 59.2413 | 14.3375 | 212 | -0.081675 | 128.4521 | 239.1593 | 0.0099831
713 | 890.8297 | 3.5998 | 63.0188 | 106.7111 | 56.2452 | 5.9414 | 75.5239 | 7.9171 | 10.11 | 41.1134 | 112.6383 | 9.8365 | 202.9012 | 134.4206 | 217.738 | 9.5008 | 59.6391 | 14.5861 | 213 | -0.10075 | 103.0322 | 256.4126 | 0
714 | 884.9671 | 3.7314 | 62.5779 | 109.5298 | 56.5158 | 5.6843 | 77.5702 | 7.3048 | 9.0173 | 39.4188 | 110.7768 | 8.6296 | 201.1958 | 171.8835 | 222.7224 | 9.6706 | 58.9648 | 14.3423 | 204 | -0.076107 | 99.2493 | 265.5527 | 0
715 | 861.2228 | 3.7162 | 61.569 | 105.7757 | 56.526 | 5.6746 | 69.407 | 6.9755 | 8.119 | 38.9681 | 98.644 | 8.7779 | 186.6002 | 177.7744 | 236.6867 | 9.8313 | 57.7204 | 13.9291 | 210 | -0.13577 | 96.7262 | 261.7112 | 0
716 | 858.6889 | 3.7054 | 61.2597 | 102.4537 | 54.9279 | 7.1928 | 66.3462 | 6.8126 | 8.6604 | 37.3475 | 91.1114 | 8.7347 | 175.9418 | 146.5533 | 251.9525 | 9.7178 | 57.9281 | 13.8673 | 189 | -0.10189 | 91.3226 | 251.6682 | 0
717 | 855.7554 | 3.7182 | 61.2791 | 101.6918 | 54.503 | 7.5965 | 73.993 | 6.336 | 8.0385 | 38.5629 | 90.5971 | 8.8947 | 184.2071 | 124.5536 | 261.0582 | 9.7103 | 56.0377 | 13.4016 | 194 | -0.04637 | 84.5973 | 249.1915 | 0
718 | 838.8616 | 3.2201 | 61.407 | 100.8418 | 54.5045 | 7.5951 | 76.0974 | 6.1829 | 6.7907 | 39.2832 | 89.4671 | 8.7636 | 185.1283 | 121.0882 | 242.3728 | 9.7861 | 54.3597 | 14.6054 | 181 | -0.024945 | 82.364 | 247.0348 | 0
719 | 825.5616 | 3.8251 | 61.5317 | 100.2455 | 55.3284 | 6.8123 | 69.258 | 6.0457 | 6.5194 | 39.4034 | 87.4682 | 8.6856 | 178.3665 | 125.7354 | 217.9477 | 9.7019 | 54.0615 | 14.2747 | 176 | -0.067523 | 79.917 | 244.6609 | 0
720 | 814.8463 | 2.5918 | 61.6263 | 99.69 | 56.2286 | 5.9571 | 67.2059 | 6.0234 | 6.1103 | 38.2951 | 86.7507 | 8.7069 | 173.1213 | 119.7964 | 213.3275 | 9.7737 | 54.0921 | 13.6567 | 147 | -0.063407 | 79.1786 | 253.8995 | 0
721 | 830.1242 | 1.7071 | 61.7748 | 99.9654 | 56.5403 | 5.661 | 75.4176 | 6.1072 | 6.3055 | 37.6816 | 86.7961 | 8.8185 | 175.7105 | 105.8048 | 219.715 | 9.8068 | 54.0948 | 12.2884 | 136 | -0.041781 | 78.6926 | 275.9047 | 0
722 | 832.9806 | 1.8714 | 62.5058 | 100.1134 | 55.6826 | 6.4758 | 77.65 | 6.5004 | 6.2077 | 37.7765 | 87.015 | 9.1068 | 176.8266 | 97.0553 | 221.008 | 9.6833 | 54.2244 | 11.9911 | 148 | 0.46766 | 76.5895 | 270.1348 | 0
723 | 838.5691 | 1.748 | 62.6335 | 100.5866 | 52.4513 | 9.5456 | 69.759 | 6.4461 | 6.1669 | 37.9136 | 87.473 | 8.8911 | 167.6817 | 99.4521 | 213.2661 | 9.7691 | 54.1778 | 12.1303 | 157 | 2.1219 | 80.2578 | 253.2032 | 0
724 | 821.4966 | 1.6971 | 62.3817 | 99.5169 | 51.4439 | 10.5026 | 67.4392 | 6.5373 | 6.483 | 38.709 | 88.2584 | 8.7672 | 158.3698 | 97.0931 | 217.8837 | 9.8867 | 54.4905 | 11.8332 | 133 | 1.6654 | 79.6535 | 248.0753 | 0
725 | 794.2239 | 1.9694 | 62.144 | 99.828 | 53.0508 | 8.9761 | 77.3326 | 6.6169 | 6.3259 | 37.5592 | 88.756 | 8.7814 | 151.5966 | 97.5981 | 214.6865 | 9.8532 | 56.3295 | 11.6498 | 122 | 1.1728 | 76.3022 | 241.6344 | 0
726 | 793.1138 | 3.0599 | 61.9077 | 99.6024 | 55.8516 | 6.3153 | 74.3587 | 6.5622 | 6.3119 | 47.8112 | 89.7827 | 8.7732 | 149.9972 | 96.7882 | 214.0394 | 9.8192 | 58.9484 | 11.605 | 116 | 0.38819 | 73.8446 | 239.2901 | 0
727 | 801.8624 | 3.319 | 61.6675 | 100.2252 | 56.4825 | 5.7159 | 68.0176 | 6.5567 | 6.1932 | 69.8815 | 91.386 | 8.7581 | 149.7143 | 95.5196 | 212.6267 | 9.6925 | 56.5619 | 11.6008 | 127 | 0.073167 | 73.407 | 242.3464 | 0
728 | 822.2178 | 3.2521 | 62.3074 | 100.9406 | 55.7293 | 6.4315 | 71.3605 | 5.94 | 6.0317 | 69.9334 | 92.0866 | 8.7364 | 156.9082 | 94.8969 | 225.9878 | 9.5676 | 55.2179 | 12.34 | 131 | 0.41149 | 73.8633 | 241.9127 | 0
729 | 821.8697 | 2.6812 | 62.2066 | 98.4451 | 55.4695 | 6.6783 | 77.91 | 5.5147 | 6.8406 | 63.0328 | 92.7974 | 7.9242 | 161.5552 | 91.1514 | 229.384 | 9.3349 | 54.5319 | 13.2206 | 139 | 0.095872 | 77.7758 | 226.6739 | 0
730 | 836.3561 | 1.8443 | 61.996 | 99.0095 | 55.5154 | 6.6347 | 74.2992 | 5.226 | 10.89 | 62.354 | 91.4423 | 6.6458 | 163.6501 | 96.1678 | 219.7263 | 9.1566 | 54.2568 | 13.4016 | 163 | -0.082255 | 80.0169 | 217.3955 | 0.048855
731 | 870.4578 | 2.0799 | 62.0986 | 99.5531 | 55.5202 | 6.6301 | 66.889 | 5.0192 | 12.184 | 74.3215 | 91.3415 | 5.9221 | 183.7306 | 104.6813 | 201.9933 | 9.0028 | 54.224 | 13.4298 | 183 | -0.10341 | 80.0887 | 220.3929 | 0.12761
732 | 889.8315 | 3.0551 | 62.6021 | 100.2785 | 56.2661 | 5.9215 | 71.1952 | 4.9901 | 9.7473 | 79.4205 | 101.5833 | 6.5636 | 199.1934 | 110.7967 | 196.0564 | 8.3291 | 56.635 | 13.4385 | 164 | -0.10852 | 77.9097 | 233.7161 | 0.11489
733 | 887.3626 | 3.9598 | 62.848 | 101.3897 | 56.4928 | 5.7062 | 78.1259 | 4.7306 | 9.3613 | 66.6421 | 105.903 | 6.8225 | 207.5396 | 119.1022 | 195.0655 | 8.0894 | 60.3316 | 13.6756 | 170 | -0.087362 | 77.7305 | 258.9344 | 0.11
734 | 884.0064 | 3.1316 | 63.0041 | 105.1338 | 56.493 | 5.706 | 85.0993 | 4.8842 | 9.0927 | 57.4661 | 107.6459 | 7.5962 | 212.9916 | 129.5215 | 205.6525 | 8.449 | 61.7916 | 14.1048 | 176 | -0.037774 | 71.8058 | 264.2756 | 0.094314
735 | 877.4565 | 2.8497 | 62.4415 | 104.8083 | 56.4848 | 5.7137 | 85.8015 | 5.0882 | 7.7127 | 58.3314 | 109.0694 | 9.7336 | 216.5861 | 137.7297 | 217.5518 | 8.8601 | 60.5788 | 14.6852 | 209 | -0.088734 | 71.2377 | 242.0905 | 0.033352
736 | 862.3204 | 2.5568 | 61.9096 | 104.0694 | 56.4865 | 5.7122 | 79.0982 | 5.4054 | 8.1573 | 57.9764 | 109.2143 | 13.6162 | 212.4673 | 135.7626 | 243.1936 | 9.0284 | 59.5933 | 14.9301 | 202 | -0.13545 | 73.6365 | 232.9736 | 0.023831
737 | 859.0319 | 3.602 | 61.9093 | 102.2012 | 54.1766 | 7.9065 | 91.1698 | 5.9873 | 6.9767 | 59.1992 | 110.4362 | 12.3282 | 212.6992 | 136.4039 | 255.8661 | 9.1001 | 59.0245 | 15.5204 | 184 | -0.15347 | 80.7354 | 229.9908 | 0
738 | 859.8114 | 4.2879 | 61.5319 | 102.4834 | 54.2914 | 7.7974 | 83.6854 | 6.2711 | 12.502 | 64.603 | 111.7901 | 11.1326 | 212.8587 | 139.351 | 263.3296 | 9.3899 | 59.0226 | 15.6488 | 185 | -0.059205 | 85.1867 | 239.844 | 0
739 | 860.8666 | 8.0231 | 62.9225 | 101.6656 | 54.4949 | 7.6042 | 69.3269 | 6.7036 | 14.6733 | 56.681 | 111.1209 | 10.8639 | 206.1597 | 140.0275 | 244.3435 | 9.5682 | 56.959 | 15.3436 | 167 | 0.041638 | 85.6966 | 242.7066 | 0
740 | 844.2451 | 7.7071 | 63.7661 | 100.086 | 55.3105 | 6.8294 | 71.7508 | 6.5319 | 14.8949 | 43.7127 | 106.9069 | 10.5987 | 194.4689 | 128.5801 | 211.2803 | 9.6417 | 55.5737 | 15.0287 | 144 | 0.11994 | 91.1531 | 241.5246 | 0
741 | 819.2288 | 4.7713 | 63.6266 | 99.5682 | 55.4737 | 6.6743 | 78.3922 | 6.061 | 13.821 | 38.6866 | 96.4153 | 10.4792 | 181.8857 | 122.2407 | 211.2389 | 9.5451 | 55.1456 | 14.589 | 137 | 0.14075 | 85.8736 | 244.6787 | 0
742 | 802.0679 | 3.5035 | 63.1764 | 100.6138 | 56.2776 | 5.9106 | 72.5852 | 5.8949 | 9.6061 | 38.6757 | 91.6612 | 9.2041 | 164.0478 | 115.5925 | 205.0217 | 9.6058 | 55.1492 | 14.5847 | 130 | 0.19789 | 81.362 | 241.3218 | 0
743 | 782.3366 | 3.2369 | 62.937 | 99.8917 | 56.5104 | 5.6894 | 66.8503 | 6.047 | 7.9823 | 39.2288 | 88.6452 | 8.7228 | 155.778 | 113.7499 | 196.2538 | 9.5725 | 55.41 | 14.346 | 132 | 0.21444 | 77.6328 | 239.9702 | 0
744 | 775.835 | 2.1285 | 62.0146 | 99.8638 | 56.4951 | 5.704 | 71.4235 | 6.138 | 7.0224 | 37.697 | 85.9489 | 8.5024 | 153.3583 | 107.0419 | 200.3175 | 9.5929 | 55.8451 | 13.5385 | 111 | 0.18895 | 72.6734 | 244.1844 | 0
745 | 787.5653 | 6.3033 | 61.6512 | 99.8614 | 58.8642 | 5.7289 | 78.4021 | 6.1631 | 6.7757 | 36.6418 | 85.1227 | 8.145 | 151.4624 | 100.8334 | 209.188 | 9.6264 | 55.52 | 12.5949 | 111 | 0.15139 | 72.7583 | 239.4867 | 0
746 | 782.5445 | 8.5602 | 61.497 | 100.3514 | 58.1646 | 6.3935 | 70.2595 | 6.702 | 6.4406 | 35.8022 | 84.9548 | 8.0371 | 152.0144 | 97.9946 | 213.6548 | 9.5473 | 55.3807 | 12.1117 | 105 | 0.25268 | 72.254 | 233.1557 | 0
747 | 790.9246 | 5.3619 | 61.3332 | 100.4706 | 58.648 | 5.9343 | 67.3056 | 7.0843 | 6.4945 | 35.58 | 85.5504 | 8.4481 | 153.4028 | 101.2535 | 209.3067 | 9.5568 | 55.4519 | 12.0275 | 123 | 0.271 | 72.572 | 240.8304 | 0
748 | 794.318 | 2.1123 | 61.7477 | 101.1525 | 58.9081 | 5.6872 | 79.1919 | 7.2752 | 6.5992 | 38.7937 | 86.602 | 8.6173 | 152.1573 | 111.502 | 209.6441 | 9.6475 | 55.4522 | 12.0257 | 105 | 0.19355 | 75.8191 | 248.6162 | 0
749 | 796.2414 | 1.8151 | 62.4512 | 102.8643 | 58.8664 | 5.7268 | 81.5552 | 7.4474 | 6.3093 | 49.186 | 86.6475 | 8.3667 | 149.5542 | 122.583 | 211.4106 | 9.5516 | 56.8247 | 12.0322 | 102 | 0.15994 | 72.7797 | 264.7172 | 0
750 | 807.939 | 2.9732 | 62.7614 | 102.1338 | 57.3706 | 7.1479 | 73.4917 | 6.8591 | 6.596 | 64.8692 | 87.7618 | 10.7447 | 171.9474 | 124.3601 | 221.0971 | 9.5713 | 59.1672 | 12.0695 | 107 | 0.14767 | 77.4085 | 288.7343 | 0
751 | 855.8042 | 4.5788 | 69.0012 | 110.9373 | 54.6194 | 9.7614 | 80.0451 | 6.4888 | 10.9652 | 94.4745 | 117.0773 | 21.1774 | 206.2117 | 184.3808 | 262.9205 | 12.828 | 57.3641 | 12.8787 | 174 | 0.28243 | 121.2229 | 331.2654 | 0
752 | 963.255 | 5.7617 | 92.1389 | 118.8122 | 48.358 | 15.7098 | 109.3974 | 7.031 | 18.0455 | 112.8873 | 150.7743 | 35.7662 | 277.1574 | 237.8943 | 373.5515 | 25.1023 | 62.2032 | 13.6485 | 296 | 1.4885 | 170.0547 | 402.1877 | 0
753 | 1049.2187 | 5.2675 | 109.3387 | 125.3564 | 48.3672 | 15.701 | 120.2414 | 8.8033 | 22.1912 | 111.02 | 172.4104 | 42.2116 | 336.9807 | 291.5968 | 472.4894 | 34.9385 | 73.3701 | 17.3353 | 308 | 0.80232 | 204.0206 | 454.1264 | 0
754 | 1144.5607 | 4.3406 | 112.8697 | 140.1466 | 48.289 | 15.7754 | 123.8765 | 10.9069 | 24.3746 | 119.1133 | 184.915 | 44.6374 | 374.8562 | 343.8193 | 538.6674 | 41.8623 | 84.6412 | 17.6136 | 368 | -0.22443 | 242.1988 | 482.642 | 0.063238
755 | 1202.4965 | 3.9303 | 113.1709 | 150.6764 | 45.5952 | 18.3345 | 134.4578 | 12.1403 | 26.7755 | 116.868 | 189.008 | 43.6458 | 402.8079 | 380.8693 | 575.9514 | 44.7995 | 92.3361 | 18.7553 | 349 | -1.0066 | 248.4089 | 498.5013 | 0.096479
756 | 1221.1701 | 4.0856 | 116.2934 | 145.5574 | 45.649 | 18.2833 | 134.1496 | 12.224 | 27.4773 | 124.6909 | 188.9514 | 42.6996 | 428.3565 | 395.9146 | 617.6723 | 43.2234 | 95.5497 | 19.7338 | 338 | -1.2147 | 246.3937 | 505.7799 | 0.066692
757 | 1232.9807 | 7.4182 | 114.678 | 145.6776 | 45.8155 | 18.1251 | 132.8815 | 11.1311 | 24.4367 | 120.8798 | 188.4425 | 42.5154 | 435.5372 | 382.0541 | 628.4387 | 44.9153 | 93.9931 | 19.8749 | 364 | -0.66117 | 246.6887 | 523.9185 | 0.028516
758 | 1241.8631 | 10.8909 | 113.0896 | 151.1099 | 42.9082 | 20.8871 | 134.0168 | 10.1245 | 26.5767 | 119.8847 | 191.2448 | 43.6735 | 433.1942 | 393.8023 | 634.1379 | 46.0439 | 94.5443 | 19.3874 | 312 | -0.96706 | 253.5296 | 516.2326 | 0.030524
759 | 1232.9015 | 6.5282 | 112.8079 | 153.9942 | 43.4462 | 20.376 | 127.1038 | 9.6618 | 26.9376 | 111.4874 | 190.9457 | 45.166 | 435.819 | 399.0756 | 642.6012 | 45.1758 | 95.7775 | 19.1478 | 308 | -1.5889 | 260.1278 | 525.3315 | 0.0078817
760 | 1191.9336 | 5.1249 | 114.8894 | 152.3754 | 46.9352 | 17.0615 | 128.3633 | 9.0653 | 21.6096 | 109.8172 | 189.7712 | 46.0019 | 430.4222 | 377.2983 | 600.9939 | 42.5389 | 94.2564 | 19.5463 | 275 | -1.7326 | 246.7861 | 513.5118 | 0.0019863
761 | 1138.1276 | 5.9575 | 112.3037 | 153.6052 | 52.5538 | 11.7238 | 129.4283 | 8.6175 | 18.6827 | 109.5736 | 189.3116 | 44.691 | 413.3751 | 346.0031 | 524.496 | 34.4435 | 92.04 | 19.2719 | 274 | -2.0536 | 225.9793 | 465.8013 | 0
762 | 1081.5134 | 5.9318 | 102.5849 | 136.9962 | 54.7052 | 9.6799 | 105.4904 | 6.2492 | 19.6255 | 99.0759 | 183.3828 | 41.4276 | 354.0093 | 266.0119 | 431.0287 | 19.5718 | 84.8966 | 18.2812 | 233 | -2.2885 | 190.3126 | 379.6668 | 0
763 | 1037.4797 | 6.6685 | 98.1025 | 120.7543 | 57.1705 | 7.3379 | 95.4471 | 5.4835 | 20.5198 | 89.4549 | 152.3906 | 32.7656 | 305.4364 | 200.5801 | 383.4397 | 12.5075 | 76.668 | 16.9822 | 223 | -2.3555 | 164.5165 | 334.6899 | 0
764 | 984.2652 | 10.4591 | 87.4165 | 112.6836 | 58.6413 | 5.9407 | 88.3976 | 5.5198 | 21.1863 | 61.3598 | 119.9904 | 16.4533 | 257.9874 | 173.568 | 336.932 | 11.1395 | 67.8944 | 16.138 | 202 | -2.4224 | 143.6662 | 287.1307 | 0
765 | 928.3121 | 9.044 | 66.1982 | 106.904 | 58.1106 | 6.4449 | 84.9228 | 5.4046 | 19.8784 | 42.2362 | 110.4892 | 11.2055 | 234.1848 | 158.9428 | 278.2855 | 9.8054 | 59.971 | 15.8996 | 182 | -2.3475 | 135.2745 | 264.9219 | 0
766 | 902.0126 | 4.6635 | 59.3198 | 105.107 | 58.6851 | 5.899 | 84.6212 | 5.306 | 17.9367 | 36.3268 | 105.1762 | 9.9458 | 213.8823 | 133.9325 | 250.2212 | 9.2552 | 58.0877 | 15.1601 | 169 | -2.4991 | 129.438 | 259.3266 | 0
767 | 849.4805 | 3.3003 | 58.2188 | 101.6781 | 58.9241 | 5.672 | 83.6391 | 5.5482 | 10.7503 | 31.4189 | 99.7359 | 9.3657 | 184.8929 | 119.3785 | 227.0453 | 9.0893 | 56.6916 | 14.2109 | 141 | -2.6734 | 115.6863 | 254.1857 | 0
768 | 825.3192 | 2.3706 | 57.7433 | 99.2647 | 59.6461 | 4.9861 | 83.4407 | 5.5219 | 6.8982 | 29.8794 | 88.9033 | 9.1018 | 169.5498 | 108.341 | 214.1682 | 9.1268 | 55.4714 | 13.8465 | 123 | -2.696 | 82.5585 | 252.1224 | 0
769 | 816.7318 | 1.7169 | 57.445 | 98.7475 | 60.3305 | 5.4726 | 83.738 | 5.4008 | 6.3828 | 30.3213 | 82.7111 | 9.0743 | 162.6043 | 102.0906 | 224.7473 | 9.069 | 55.9222 | 12.8763 | 118 | -2.4494 | 70.6554 | 249.835 | 0
770 | 812.8259 | 1.4668 | 57.4095 | 98.3535 | 60.0447 | 5.7442 | 83.458 | 5.2924 | 6.5247 | 31.0095 | 84.628 | 9.0516 | 163.6717 | 98.729 | 222.9787 | 9.761 | 55.7475 | 11.9428 | 115 | -2.6348 | 71.7776 | 243.0334 | 0
771 | 802.0724 | 1.3285 | 57.4698 | 98.1894 | 60.1557 | 5.6387 | 83.2338 | 5.3968 | 6.3828 | 31.0996 | 88.1917 | 8.8169 | 164.6437 | 97.6767 | 212.2767 | 10.1181 | 54.6812 | 11.629 | 134 | -2.6954 | 76.3456 | 244.3812 | 0
772 | 798.6539 | 1.2984 | 57.5467 | 98.3905 | 60.0764 | 5.714 | 77.6244 | 5.2634 | 6.3543 | 34.7157 | 90.315 | 8.7369 | 164.471 | 102.0182 | 214.6416 | 10.1499 | 54.5414 | 11.5032 | 111 | -2.5745 | 77.6793 | 249.1533 | 0
773 | 802.7401 | 1.8525 | 57.8883 | 98.3731 | 60.1131 | 5.6792 | 76.0572 | 5.0052 | 6.3915 | 45.9781 | 89.3019 | 8.7536 | 157.8814 | 111.7953 | 213.1547 | 10.2503 | 56.3731 | 11.3595 | 112 | -2.5938 | 77.5785 | 267.6844 | 0
774 | 823.1995 | 2.7436 | 58.8397 | 99.212 | 59.2498 | 6.4993 | 82.9875 | 4.951 | 6.7838 | 61.164 | 85.7175 | 10.251 | 167.8937 | 120.186 | 222.3157 | 10.1181 | 58.8705 | 11.3202 | 118 | -2.6049 | 80.6541 | 297.7691 | 0
775 | 856.4999 | 4.1694 | 73.6865 | 105.095 | 56.8023 | 8.8244 | 96.4997 | 5.3524 | 8.5082 | 89.4402 | 105.2017 | 20.9711 | 208.1933 | 170.2342 | 252.5223 | 13.2568 | 56.4027 | 11.3144 | 179 | -2.5169 | 119.5897 | 341.7677 | 0
776 | 928.7681 | 5.5015 | 90.6124 | 113.9462 | 52.3968 | 13.0097 | 119.2846 | 6.5782 | 12.9813 | 104.8442 | 148.7474 | 36.0345 | 279.1996 | 240.4019 | 327.9208 | 27.6641 | 62.9204 | 12.2528 | 277 | -2.1041 | 165.103 | 415.2929 | 0
777 | 1027.8836 | 6.2821 | 104.741 | 125.9354 | 48.7147 | 16.5077 | 131.0282 | 8.1154 | 15.5323 | 102.5874 | 173.4596 | 38.9595 | 343.2897 | 296.904 | 451.5713 | 36.4262 | 74.6591 | 15.3235 | 324 | -2.4142 | 219.7194 | 478.4294 | 0
778 | 1141.4595 | 5.741 | 113.262 | 138.1283 | 48.6185 | 16.599 | 137.8848 | 8.3833 | 19.8546 | 107.6796 | 191.2792 | 38.9475 | 393.4114 | 335.1536 | 544.6764 | 41.2078 | 86.1733 | 18.1364 | 368 | -2.1475 | 257.0833 | 509.7035 | 0.014665
779 | 1188.1564 | 9.4643 | 115.1551 | 146.0237 | 47.5812 | 17.5845 | 143.6488 | 8.1506 | 23.4864 | 110.4353 | 194.1715 | 40.6252 | 407.8558 | 375.0523 | 589.345 | 43.4704 | 96.0178 | 19.0402 | 354 | -2.0985 | 268.5844 | 533.303 | 0.022238
780 | 1212.1765 | 9.4473 | 114.8347 | 146.3204 | 45.5338 | 19.5295 | 143.2241 | 9.096 | 23.238 | 112.0339 | 193.4927 | 40.4206 | 421.2428 | 395.3379 | 604.0615 | 41.5125 | 98.5326 | 19.4552 | 367 | -2.2409 | 265.87 | 524.3291 | 0.031297
781 | 1201.8347 | 5.6212 | 114.121 | 145.4106 | 46.7168 | 18.4057 | 136.0133 | 9.4751 | 20.9633 | 104.391 | 193.7505 | 41.6317 | 421.4504 | 380.4494 | 576.1671 | 41.3786 | 95.2368 | 19.192 | 424 | -2.3597 | 246.1778 | 503.1689 | 0.059707
782 | 1192.6506 | 4.5345 | 117.0935 | 149.2053 | 47.0564 | 18.0831 | 129.8713 | 10.2338 | 22.272 | 106.5963 | 194.6338 | 42.5418 | 419.7928 | 374.9505 | 563.005 | 43.6879 | 96.7353 | 18.9625 | 341 | -2.5352 | 247.771 | 516.1801 | 0.048205
783 | 1193.782 | 5.2152 | 115.1738 | 146.2552 | 49.5039 | 15.7579 | 124.9333 | 9.085 | 19.8173 | 109.288 | 195.1479 | 42.95 | 431.8568 | 387.7997 | 580.8875 | 43.5851 | 98.1587 | 19.1748 | 335 | -2.6422 | 267.2612 | 518.7537 | 0.021558
784 | 1163.3476 | 5.9939 | 114.4111 | 142.4332 | 47.7034 | 17.4684 | 121.453 | 8.5296 | 19.298 | 109.1914 | 195.8675 | 41.5468 | 423.2695 | 367.1054 | 553.5523 | 41.9765 | 95.335 | 19.537 | 321 | -2.4936 | 256.4316 | 522.627 | 0.0018019
785 | 1139.8469 | 6.2928 | 109.1518 | 141.6549 | 53.2491 | 12.2 | 115.8429 | 8.4686 | 19.8307 | 99.8919 | 195.3685 | 37.6543 | 405.7448 | 329.3842 | 492.2674 | 34.7743 | 92.2157 | 19.4629 | 298 | -2.9448 | 226.0007 | 477.6076 | 0
786 | 1087.6826 | 5.2354 | 101.417 | 130.6791 | 57.3862 | 8.2697 | 107.1721 | 6.6955 | 20.2187 | 92.1902 | 192.149 | 32.5518 | 359.5231 | 259.1735 | 394.2386 | 20.0572 | 86.9148 | 18.6438 | 250 | -2.9267 | 192.2042 | 385.635 | 0
787 | 1021.657 | 4.8278 | 97.204 | 115.9921 | 58.8871 | 6.8439 | 95.3196 | 5.4419 | 20.694 | 80.0139 | 159.487 | 26.0027 | 304.9072 | 202.6485 | 355.0077 | 12.6992 | 76.4946 | 16.7425 | 254 | -2.7649 | 174.2393 | 345.8489 | 0
788 | 964.2011 | 4.3609 | 86.8247 | 107.5728 | 59.9069 | 5.8751 | 76.4287 | 5.5052 | 20.566 | 55.1366 | 125.1433 | 15.396 | 272.7639 | 179.7859 | 321.724 | 12.4044 | 67.3978 | 15.4874 | 274 | -2.702 | 153.5795 | 295.2511 | 0
789 | 916.6668 | 4.587 | 65.0661 | 104.4181 | 59.3127 | 6.4396 | 78.6957 | 5.454 | 18.424 | 47.1124 | 112.7106 | 11.6797 | 245.6255 | 161.5631 | 271.5335 | 11.1909 | 61.0087 | 14.6715 | 229 | -2.8804 | 140.5681 | 270.5263 | 0
790 | 878.7118 | 9.2312 | 58.0755 | 101.4313 | 59.8739 | 5.9064 | 82.8948 | 5.5354 | 12.2387 | 44.2896 | 108.8025 | 11.2535 | 203.8468 | 144.9005 | 239.8254 | 10.4443 | 58.7853 | 13.5735 | 216 | -2.9952 | 139.5122 | 261.3584 | 0
791 | 856.065 | 6.324 | 57.6377 | 99.1801 | 60.1073 | 5.6847 | 78.6741 | 5.399 | 10.3407 | 38.3859 | 96.178 | 10.3479 | 180.4487 | 138.6464 | 223.6921 | 10.3977 | 57.7019 | 13.0256 | 192 | -2.9416 | 135.6077 | 265.5526 | 0
792 | 830.131 | 2.2966 | 56.8233 | 98.8238 | 60.0707 | 5.7195 | 71.5129 | 5.2685 | 10.15 | 34.9771 | 89.2697 | 10.0747 | 167.8713 | 134.4043 | 213.5588 | 10.4038 | 57.5129 | 12.6896 | 177 | -2.8908 | 110.1038 | 264.0157 | 0
793 | 810.3592 | 1.8703 | 56.3493 | 99.4014 | 60.101 | 5.6907 | 79.4463 | 5.2787 | 10.1067 | 34.1905 | 87.5775 | 10.0958 | 167.9807 | 130.4427 | 225.9172 | 10.4115 | 57.4231 | 12.7304 | 160 | -2.8845 | 96.1388 | 261.362 | 0
794 | 822.0818 | 1.6084 | 56.2956 | 98.7394 | 60.1063 | 5.6856 | 83.8186 | 5.5568 | 10.12 | 34.2069 | 87.0217 | 9.051 | 165.9665 | 126.524 | 228.1356 | 10.3144 | 57.5426 | 12.1392 | 146 | -2.8639 | 90.9636 | 270.3355 | 0
795 | 820.3574 | 1.3334 | 56.3608 | 99.1388 | 60.0929 | 5.6984 | 83.0912 | 5.3628 | 9.7459 | 34.4881 | 87.7046 | 8.3761 | 167.7638 | 123.4351 | 214.4686 | 10.2303 | 57.5816 | 11.6438 | 158 | -2.8829 | 89.2253 | 270.1951 | 0
796 | 821.8268 | 1.4627 | 56.1911 | 99.2214 | 60.0844 | 5.7065 | 76.935 | 5.1637 | 12.7367 | 37.9545 | 88.3636 | 8.2026 | 162.4815 | 119.2219 | 209.4665 | 10.2332 | 57.7977 | 11.4781 | 140 | -2.8872 | 89.6393 | 270.9017 | 0
797 | 821.556 | 1.7985 | 56.6682 | 98.9624 | 59.3108 | 6.4414 | 69.953 | 5.4024 | 15.8774 | 49.3327 | 88.5276 | 8.3323 | 170.9833 | 118.2013 | 215.448 | 10.3076 | 59.3323 | 11.4948 | 125 | -2.7903 | 89.8725 | 280.9198 | 0
798 | 827.7479 | 2.8493 | 56.8877 | 99.551 | 58.3039 | 7.3979 | 78.4567 | 5.6687 | 13.1307 | 64.7529 | 88.7501 | 10.5021 | 180.6102 | 125.428 | 226.283 | 10.2828 | 61.9043 | 11.5123 | 129 | -2.8686 | 91.8388 | 310.0994 | 0
799 | 857.6527 | 4.1709 | 58.0671 | 108.3051 | 57.2734 | 8.3769 | 87.3166 | 5.9583 | 13.398 | 91.0568 | 105.8842 | 20.9033 | 217.0165 | 182.2959 | 255.7657 | 13.5593 | 59.6502 | 11.5109 | 186 | -2.6275 | 133.8788 | 338.3624 | 0
800 | 934.5049 | 5.7488 | 66.3101 | 115.431 | 51.6931 | 13.6782 | 104.0652 | 6.6796 | 18.724 | 106.0136 | 149.2401 | 36.1421 | 287.5722 | 241.8931 | 351.2095 | 27.2278 | 64.6754 | 12.7784 | 280 | -1.9928 | 184.9967 | 410.6196 | 0
801 | 1021.2655 | 7.0137 | 102.2451 | 128.3421 | 49.3498 | 15.9044 | 120.6993 | 7.8067 | 21.494 | 104.6583 | 177.2838 | 42.8381 | 342.5932 | 279.6537 | 467.2222 | 36.0922 | 74.7578 | 15.9891 | 305 | -2.2068 | 230.8834 | 498.4757 | 0
802 | 1112.3156 | 7.6101 | 114.2216 | 138.8798 | 48.3106 | 16.8915 | 127.0257 | 9.1643 | 20.1212 | 109.3298 | 185.1341 | 40.5667 | 383.5962 | 312.3328 | 521.0803 | 41.2763 | 84.5598 | 17.3615 | 374 | -1.8427 | 276.5176 | 517.4455 | 0.060834
803 | 1185.9178 | 7.5898 | 112.5249 | 143.3568 | 48.0695 | 17.1206 | 121.9545 | 9.3115 | 17.4078 | 107.7435 | 196.0422 | 37.6961 | 408.8042 | 339.831 | 533.5699 | 43.529 | 89.3791 | 18.1381 | 395 | -0.78823 | 281.8513 | 536.3688 | 0.12087
804 | 1202.2699 | 7.6298 | 115.4143 | 143.4661 | 48.8146 | 16.4127 | 128.7418 | 8.5691 | 16.0537 | 116.211 | 194.9796 | 35.5922 | 419.0861 | 351.0559 | 529.0961 | 42.2481 | 91.5039 | 18.364 | 362 | -0.67732 | 275.4987 | 526.7692 | 0.089654
805 | 1206.8443 | 6.9656 | 114.0802 | 144.0739 | 49.0666 | 16.1734 | 132.3074 | 8.6981 | 16.982 | 105.0439 | 187.739 | 37.0803 | 417.5406 | 347.9173 | 520.0578 | 42.2835 | 90.6338 | 18.0527 | 359 | -0.96782 | 263.9234 | 528.3305 | 0.1446
806 | 1224.186 | 5.3553 | 115.5515 | 155.1333 | 50.6475 | 14.6715 | 128.2554 | 8.9144 | 16.4 | 105.7321 | 186.1866 | 38.4274 | 420.4344 | 356.1753 | 520.6528 | 43.1533 | 90.9144 | 19.0659 | 343 | -0.85108 | 256.6579 | 536.4452 | 0.17856
807 | 1233.6772 | 4.3439 | 105.763 | 154.7256 | 48.8771 | 16.3534 | 123.6352 | 7.864 | 14.61 | 111.8493 | 187.4527 | 37.4126 | 433.194 | 354.1274 | 517.0262 | 40.8369 | 88.199 | 19.449 | 314 | -0.96606 | 260.6855 | 530.6775 | 0.16778
808 | 1221.3547 | 4.3851 | 105.7001 | 148.7083 | 47.2796 | 17.871 | 121.7203 | 7.4042 | 14.7353 | 107.5646 | 186.9435 | 36.3436 | 422.7567 | 333.788 | 508.4647 | 39.3204 | 87.4982 | 19.3418 | 301 | -1.6237 | 262.4053 | 515.2205 | 0.085006
809 | 1175.7932 | 5.9458 | 107.0848 | 138.3167 | 54.808 | 10.7191 | 109.1972 | 7.7067 | 16.5247 | 97.2648 | 185.6479 | 34.3461 | 400.2272 | 307.1721 | 467.5127 | 33.2875 | 85.9498 | 18.915 | 276 | -2.3165 | 245.1993 | 465.2395 | 0
810 | 1126.6529 | 6.3787 | 101.4127 | 126.2487 | 57.1009 | 8.5408 | 102.4177 | 7.1551 | 18.9233 | 97.8405 | 181.1657 | 29.8848 | 370.0606 | 242.0262 | 400.0497 | 21.1677 | 81.3109 | 17.6295 | 241 | -2.4943 | 208.428 | 401.265 | 0
811 | 1062.539 | 5.1795 | 96.5361 | 114.6396 | 58.6484 | 7.0706 | 93.7291 | 7.1013 | 18.7173 | 85.6937 | 151.109 | 26.0396 | 322.6327 | 183.708 | 376.7364 | 15.0007 | 76.0271 | 16.7121 | 224 | -2.4681 | 189.0667 | 351.5399 | 0
812 | 1000.0117 | 4.6202 | 87.0408 | 108.474 | 59.8986 | 5.883 | 76.9122 | 6.825 | 15.7967 | 59.1885 | 118.7869 | 14.3313 | 268.8147 | 156.5195 | 341.2164 | 11.7336 | 69.6727 | 16.2438 | 208 | -2.4802 | 163.4508 | 298.9524 | 0
813 | 956.983 | 4.2667 | 65.7808 | 105.5928 | 58.5923 | 7.124 | 73.8901 | 6.6673 | 13.3948 | 49.5129 | 110.6539 | 10.0588 | 238.057 | 142.1974 | 283.7568 | 10.5782 | 62.9694 | 16.0738 | 177 | -2.4828 | 146.7734 | 283.4506 | 0
814 | 917.4041 | 4.1002 | 58.7881 | 103.374 | 58.7917 | 6.9346 | 78.5692 | 6.458 | 9.4102 | 45.5245 | 110.4507 | 13.7467 | 212.6263 | 120.5458 | 250.5189 | 10.4515 | 59.7534 | 15.4141 | 161 | -2.441 | 136.5685 | 283.8053 | 0
815 | 879.6046 | 3.348 | 58.592 | 100.3871 | 59.8938 | 5.8875 | 70.1031 | 6.4838 | 6.8384 | 37.3303 | 95.7166 | 10.9532 | 196.2168 | 112.9098 | 233.8742 | 10.4917 | 58.4213 | 14.7991 | 139 | -2.4431 | 126.6257 | 281.587 | 0
816 | 842.6892 | 2.0682 | 58.0848 | 99.5223 | 60.0658 | 5.7241 | 65.1969 | 6.2129 | 6.3413 | 34.0009 | 85.276 | 9.3347 | 186.1297 | 106.6134 | 214.456 | 10.4178 | 57.9907 | 14.0224 | 120 | -2.5069 | 97.3075 | 280.7239 | 0
817 | 840.3155 | 1.5516 | 57.616 | 99.4064 | 60.1334 | 5.6599 | 73.427 | 5.7603 | 6.1358 | 32.6268 | 82.8429 | 8.633 | 181.3091 | 103.0194 | 235.3683 | 10.3399 | 57.7699 | 13.5337 | 115 | -2.5189 | 83.8607 | 271.5361 | 0
818 | 836.9978 | 1.6987 | 57.5711 | 100.3023 | 59.3692 | 6.3858 | 74.5352 | 5.7683 | 6.3778 | 32.0675 | 82.718 | 8.3974 | 178.1653 | 101.6413 | 236.4076 | 10.4762 | 57.7595 | 13.3815 | 109 | -2.3666 | 81.2952 | 270.917 | 0
819 | 821.4342 | 1.5184 | 57.5689 | 100.7117 | 59.7731 | 6.0022 | 67.4028 | 5.6202 | 6.5279 | 32.1097 | 83.1373 | 8.4211 | 173.2134 | 98.3989 | 228.014 | 10.4025 | 57.9629 | 12.6478 | 125 | -2.3958 | 82.994 | 274.2997 | 0
820 | 818.0693 | 1.4507 | 57.4407 | 99.7178 | 60.0833 | 5.7075 | 66.9376 | 5.5882 | 6.1951 | 34.9302 | 83.6442 | 8.3838 | 165.9003 | 101.8837 | 219.397 | 10.3887 | 57.8603 | 12.164 | 100 | -2.5021 | 82.5798 | 277.5254 | 0
821 | 816.38 | 1.8115 | 57.6655 | 99.7589 | 60.117 | 5.6755 | 76.465 | 5.8608 | 6.2607 | 46.4208 | 84.0506 | 8.3786 | 160.4478 | 113.3264 | 213.5756 | 10.347 | 59.6624 | 12.075 | 100 | -2.5165 | 81.5106 | 294.6288 | 0
822 | 824.545 | 3.0393 | 59.1961 | 101.2657 | 59.3798 | 6.3758 | 79.5932 | 6.6209 | 6.29 | 62.3754 | 84.8225 | 9.8787 | 174.2778 | 125.5127 | 218.2941 | 10.2954 | 61.8977 | 12.1099 | 107 | -2.5277 | 82.7256 | 316.1231 | 0
823 | 863.4352 | 3.8215 | 69.0851 | 110.8358 | 56.661 | 8.9586 | 77.0269 | 7.2436 | 7.8636 | 89.3379 | 105.6837 | 19.313 | 209.3373 | 172.9821 | 245.5108 | 13.2706 | 60.0968 | 13.0838 | 183 | -2.4044 | 119.8826 | 349.7796 | 0
824 | 951.0461 | 5.6035 | 92.5808 | 116.2188 | 52.2934 | 13.1079 | 95.5644 | 7.9852 | 14.9804 | 112.3174 | 144.7857 | 34.4361 | 274.3741 | 241.3282 | 318.6474 | 27.2023 | 67.2945 | 13.7126 | 297 | -1.6991 | 163.3041 | 423.2954 | 0
825 | 1040.9267 | 5.3881 | 104.4698 | 128.367 | 49.705 | 15.5668 | 123.0891 | 8.7139 | 17.6581 | 114.2594 | 171.723 | 42.5807 | 339.3329 | 292.8283 | 424.3639 | 35.3049 | 77.5339 | 15.1017 | 313 | -1.8053 | 200.8574 | 489.8283 | 0
826 | 1113.2451 | 4.3178 | 112.1691 | 143.9595 | 48.9189 | 16.3137 | 129.7316 | 8.4021 | 21.2593 | 111.8831 | 172.4669 | 41.7633 | 386.3389 | 337.7363 | 511.0801 | 40.1943 | 87.9571 | 18.3819 | 373 | -1.5779 | 231.4147 | 550.7283 | 0.18487
827 | 1159.762 | 3.9931 | 112.0647 | 149.1733 | 46.6297 | 18.4884 | 128.5175 | 8.6043 | 24.7439 | 111.368 | 172.1783 | 45.0164 | 411.8554 | 360.4617 | 544.1066 | 41.3378 | 93.629 | 16.9424 | 375 | -0.86411 | 245.9968 | 570.0062 | 0.20468
828 | 1197.4271 | 3.9528 | 117.9645 | 146.7233 | 46.9071 | 18.2249 | 133.6314 | 8.7583 | 22.0487 | 121.1023 | 186.4503 | 48.4708 | 422.0142 | 367.7093 | 570.8245 | 42.4548 | 95.1552 | 16.7914 | 338 | -1.3996 | 249.9305 | 565.9775 | 0.19501
829 | 1179.7622 | 4.2183 | 114.9634 | 140.6922 | 47.9196 | 17.2631 | 133.8887 | 9.373 | 18.788 | 113.9226 | 190.8847 | 45.9018 | 412.2761 | 365.8481 | 565.2768 | 43.0863 | 92.802 | 17.9077 | 393 | -0.32593 | 238.3286 | 561.7155 | 0.23579
830 | 1163.4975 | 4.2399 | 115.7575 | 143.8176 | 49.047 | 16.192 | 129.0564 | 9.5598 | 21.1032 | 113.4341 | 203.9944 | 42.5206 | 419.9224 | 357.682 | 568.2374 | 42.4584 | 92.7616 | 18.0539 | 309 | -0.63074 | 233.1826 | 577.0953 | 0.20307
831 | 1157.7228 | 4.2097 | 114.6832 | 146.8946 | 49.8171 | 15.4604 | 131.8311 | 9.1141 | 21.8301 | 116.0933 | 206.5403 | 41.0252 | 427.0837 | 357.5538 | 556.7829 | 40.9129 | 91.0893 | 18.1653 | 283 | -0.8021 | 229.4231 | 572.2133 | 0.1497
832 | 1158.0699 | 4.2888 | 113.3661 | 147.8594 | 49.1845 | 16.0614 | 125.6769 | 8.7267 | 20.34 | 116.3299 | 200.3047 | 41.8719 | 419.2074 | 341.2922 | 528.602 | 40.9067 | 91.4531 | 18.9896 | 299 | -0.74575 | 221.3913 | 566.1841 | 0.037429
833 | 1112.0408 | 5.8053 | 109.4188 | 146.7443 | 52.1754 | 13.22 | 120.5198 | 8.4116 | 18.028 | 108.2191 | 192.1971 | 39.3078 | 410.1496 | 312.8752 | 490.6858 | 34.9879 | 90.8919 | 19.5661 | 277 | -1.2173 | 211.623 | 519.8157 | 0
834 | 1059.6377 | 6.0408 | 103.4298 | 135.8125 | 57.0419 | 8.5968 | 112.0191 | 8.4774 | 15.5193 | 94.1072 | 178.7241 | 35.3201 | 352.0043 | 242.4355 | 427.2959 | 19.9135 | 84.8693 | 18.9729 | 228 | -1.428 | 183.1795 | 445.6721 | 0
835 | 1001.4449 | 5.2893 | 97.3237 | 120.8167 | 57.3465 | 8.3074 | 88.1802 | 8.0988 | 13.7156 | 94.1239 | 144.9162 | 30.0271 | 297.6536 | 173.1631 | 362.3727 | 13.0643 | 76.8709 | 18.4508 | 211 | -1.5502 | 167.484 | 388.8443 | 0
836 | 946.973 | 7.1893 | 86.2345 | 112.8864 | 59.3264 | 6.4265 | 76.6339 | 6.7816 | 9.2259 | 92.7892 | 116.9559 | 15.4301 | 256.8368 | 142.9381 | 318.1711 | 12.901 | 67.273 | 18.5207 | 198 | -1.5318 | 146.2955 | 331.4858 | 0
837 | 905.387 | 7.5064 | 65.1683 | 107.8887 | 60.0704 | 5.7198 | 73.8171 | 6.2146 | 7.4826 | 90.3303 | 109.8182 | 9.9095 | 225.788 | 131.0578 | 289.2765 | 11.8153 | 60.3416 | 18.4752 | 207 | -1.4207 | 135.9489 | 312.5154 | 0
838 | 869.47 | 7.1985 | 58.0096 | 106.1136 | 59.3326 | 6.4206 | 67.4759 | 6.2303 | 7.1587 | 92.9385 | 106.0838 | 9.5511 | 206.9788 | 119.7394 | 263.8434 | 11.3125 | 57.1899 | 17.2105 | 186 | -1.5537 | 131.0809 | 293.6357 | 0
839 | 846.5859 | 5.3872 | 58.2052 | 103.6475 | 59.8709 | 5.9093 | 64.8781 | 6.3793 | 6.312 | 86.7749 | 89.2853 | 9.167 | 185.2979 | 112.0247 | 241.6096 | 11.2035 | 56.8026 | 15.6754 | 171 | -1.6102 | 120.9744 | 281.1526 | 0
840 | 822.1412 | 2.5001 | 58.1301 | 102.637 | 59.2786 | 6.472 | 73.0734 | 7.2929 | 6.26 | 75.1218 | 80.4561 | 8.4974 | 169.0879 | 103.4427 | 225.6507 | 11.1564 | 56.271 | 14.3521 | 141 | -1.579 | 91.7748 | 285.2276 | 0
841 | 828.2004 | 1.5078 | 57.5625 | 103.1414 | 59.9088 | 5.8733 | 71.3164 | 7.6336 | 6.2667 | 54.9749 | 80.0347 | 8.2806 | 161.2876 | 99.1882 | 234.6672 | 11.1504 | 56.8405 | 13.0009 | 134 | -1.5815 | 79.408 | 288.4937 | 0
842 | 822.3098 | 1.4579 | 57.3569 | 104.3391 | 60.1108 | 5.6814 | 66.1617 | 7.2326 | 6.3573 | 49.434 | 80.1138 | 8.2779 | 164.0188 | 95.1488 | 237.553 | 11.0595 | 56.5948 | 12.2687 | 123 | -1.5602 | 77.8066 | 284.0089 | 0
843 | 816.7841 | 1.3558 | 57.3193 | 103.4255 | 60.0805 | 5.7102 | 66.0761 | 6.4612 | 6.488 | 49.6391 | 80.3875 | 8.2762 | 161.1488 | 94.2273 | 217.2316 | 11.1387 | 56.2929 | 12.0342 | 138 | -1.5699 | 80.7794 | 282.7698 | 0
844 | 812.3124 | 1.3785 | 57.3591 | 102.5243 | 59.3133 | 6.439 | 74.8986 | 6.4329 | 6.3513 | 51.4461 | 81.0959 | 8.262 | 158.2244 | 101.2778 | 213.4237 | 11.1981 | 56.3408 | 12.0205 | 114 | -1.5578 | 81.3119 | 283.6418 | 0
845 | 810.5348 | 1.8014 | 57.2854 | 102.5791 | 59.857 | 5.9225 | 69.1763 | 6.3758 | 6.4513 | 57.8323 | 81.1921 | 8.2366 | 157.7817 | 112.0035 | 212.6146 | 11.0435 | 57.7867 | 11.9768 | 111 | -1.5542 | 80.1328 | 301.4477 | 0
846 | 825.163 | 3.0624 | 59.529 | 104.1831 | 58.5348 | 7.1785 | 65.5151 | 7.1297 | 6.3853 | 72.0186 | 82.7175 | 9.2573 | 170.8822 | 120.9395 | 220.9416 | 11.0997 | 60.4415 | 11.9497 | 128 | -1.6064 | 81.2776 | 326.0589 | 0
847 | 854.1499 | 4.6937 | 67.2266 | 114.4511 | 55.8051 | 9.7717 | 77.2822 | 8.2181 | 9.838 | 99.213 | 95.7819 | 19.7764 | 213.7904 | 179.7379 | 262.9193 | 14.5789 | 58.1892 | 11.9158 | 231 | -1.3676 | 119.8388 | 359.7262 | 0
848 | 918.4501 | 5.7578 | 90.1642 | 119.5315 | 50.4174 | 14.8901 | 108.4189 | 8.2406 | 15.598 | 109.6768 | 132.7839 | 36.8477 | 280.5286 | 232.1508 | 358.0775 | 28.0841 | 62.1261 | 12.9534 | 267 | -0.50185 | 163.8143 | 422.4153 | 0
849 | 1004.1337 | 5.1842 | 106.7774 | 127.5818 | 47.4862 | 17.6748 | 118.4552 | 8.8155 | 16.108 | 99.047 | 162.4078 | 40.6892 | 342.9137 | 293.4856 | 469.4581 | 36.2493 | 72.312 | 15.7607 | 340 | 0.13971 | 192.5802 | 483.8449 | 0.021422
850 | 1093.498 | 4.2082 | 107.7051 | 138.1123 | 48.7772 | 16.4483 | 120.023 | 9.1217 | 17.9998 | 96.8094 | 173.055 | 38.9214 | 396.0284 | 321.6585 | 539.7193 | 39.3988 | 83.4033 | 19.3083 | 355 | 0.12649 | 213.2606 | 538.5908 | 0.044012
851 | 1161.5299 | 4.0832 | 112.1247 | 145.7324 | 46.6844 | 18.4364 | 131.7094 | 9.2995 | 21.5694 | 96.9873 | 171.1853 | 40.2671 | 410.0991 | 351.3776 | 576.3737 | 41.0848 | 89.6939 | 19.0836 | 334 | -0.65101 | 224.8853 | 562.9849 | 0.060661
852 | 1178.6095 | 4.3359 | 114.1276 | 143.722 | 46.8605 | 18.2691 | 129.6185 | 9.8413 | 22.4733 | 100.4387 | 177.8595 | 40.9608 | 412.7892 | 370.9514 | 575.9324 | 42.2616 | 89.0508 | 18.7051 | 349 | -0.57368 | 218.9405 | 570.9685 | 0.077631
853 | 1171.6782 | 4.2564 | 114.9438 | 141.2984 | 48.6075 | 16.6095 | 127.5838 | 10.1784 | 21.0149 | 97.2142 | 181.7338 | 40.0248 | 405.6428 | 360.7892 | 549.0667 | 43.9224 | 85.333 | 19.0943 | 345 | -0.53086 | 219.933 | 568.895 | 0.074121
854 | 1174.3671 | 4.1042 | 116.5696 | 145.6181 | 47.6068 | 17.5602 | 129.7931 | 10.0113 | 20.0903 | 98.2198 | 190.2491 | 41.2266 | 417.1978 | 365.2825 | 548.9134 | 44.7535 | 90.0762 | 19.1977 | 298 | -0.46692 | 222.2085 | 579.5848 | 0.08628
855 | 1184.7989 | 4.0609 | 116.002 | 146.6351 | 50.1238 | 15.169 | 119.0644 | 9.394 | 19.4163 | 100.0158 | 191.409 | 38.8137 | 436.9785 | 357.8086 | 563.1923 | 43.1211 | 90.7188 | 18.8201 | 330 | -0.042236 | 223.9889 | 571.3724 | 0.051024
856 | 1138.4427 | 4.613 | 112.8151 | 146.5252 | 48.7848 | 16.441 | 112.9782 | 8.7632 | 17.8827 | 98.33 | 188.3758 | 36.9936 | 430.3349 | 330.1422 | 540.1684 | 39.8346 | 90.4801 | 19.0918 | 285 | -0.2901 | 208.2976 | 558.3206 | 0.014083
857 | 1090.6865 | 5.6414 | 106.2969 | 139.5783 | 55.0729 | 10.4674 | 114.0987 | 7.8882 | 16.4833 | 89.4018 | 183.0773 | 34.1503 | 386.7314 | 296.6875 | 476.5393 | 27.3215 | 87.6972 | 18.5457 | 267 | -0.96069 | 186.1192 | 495.1001 | 0
858 | 1021.4062 | 5.6636 | 88.7296 | 128.7657 | 57.1224 | 8.5203 | 97.4418 | 7.3081 | 15.578 | 89.7384 | 174.9458 | 32.3878 | 324.7372 | 229.8584 | 366.3715 | 17.6637 | 80.1444 | 17.8373 | 249 | -1.246 | 162.4811 | 408.0889 | 0
859 | 960.5839 | 6.6926 | 69.542 | 111.6606 | 59.4212 | 6.3364 | 84.1176 | 8.4742 | 13.5767 | 88.0933 | 146.041 | 27.4695 | 271.9916 | 164.222 | 309.8755 | 12.5478 | 72.1853 | 17.0376 | 235 | -1.2584 | 149.1705 | 335.784 | 0
860 | 921.7675 | 5.2969 | 64.2324 | 103.0274 | 59.2806 | 6.47 | 82.1977 | 8.715 | 8.8948 | 66.329 | 115.1417 | 16.5877 | 235.235 | 135.2327 | 268.6504 | 11.8933 | 62.4168 | 16.2791 | 222 | -1.3128 | 130.4706 | 282.623 | 0
861 | 869.303 | 4.2916 | 63.3381 | 100.3876 | 59.8588 | 5.9208 | 81.291 | 6.2172 | 7.2051 | 57.842 | 96.5089 | 10.1997 | 200.9587 | 131.6316 | 238.6056 | 10.9322 | 57.8145 | 15.0464 | 221 | -1.3283 | 124.2385 | 255.5117 | 0
862 | 834.1124 | 7.0347 | 62.4735 | 100.1354 | 60.0905 | 5.7007 | 70.861 | 5.2689 | 7.324 | 61.1135 | 91.3686 | 8.9784 | 176.0631 | 138.4912 | 233.4435 | 10.2438 | 57.2645 | 13.7475 | 208 | -1.3206 | 122.9812 | 244.0511 | 0
863 | 821.4629 | 4.5468 | 62.3684 | 98.9468 | 59.3298 | 6.4233 | 66.6879 | 5.1756 | 6.654 | 58.2993 | 89.7837 | 8.8854 | 163.2721 | 125.3251 | 250.3235 | 10.1774 | 55.5777 | 13.3287 | 174 | -1.354 | 120.1085 | 244.4455 | 0
864 | 812.9714 | 2.5557 | 62.1821 | 97.9001 | 59.9051 | 5.8768 | 75.4004 | 5.3106 | 6.456 | 52.6577 | 89.689 | 8.8715 | 161.6386 | 118.8271 | 249.4006 | 10.1313 | 55.1441 | 13.2737 | 148 | -1.3403 | 90.5275 | 242.167 | 0
865 | 803.3111 | 4.7926 | 61.9409 | 96.1779 | 60.0627 | 5.727 | 79.2701 | 5.185 | 6.326 | 50.9518 | 88.9693 | 8.9391 | 172.4535 | 106.0137 | 239.5987 | 10.0661 | 55.2189 | 13.463 | 156 | -1.2702 | 78.3535 | 243.3217 | 0
866 | 796.5181 | 2.753 | 62.0347 | 95.0063 | 60.0752 | 5.7152 | 70.5154 | 4.8184 | 6.1307 | 50.9534 | 87.0656 | 8.8902 | 176.5275 | 104.3937 | 240.5578 | 10.0131 | 54.9143 | 13.6145 | 156 | -1.3177 | 69.9243 | 235.4536 | 0
867 | 792.4622 | 1.4418 | 61.6976 | 95.1449 | 60.113 | 5.6793 | 67.0118 | 5.0899 | 6.2193 | 50.6684 | 86.7599 | 8.8758 | 167.6384 | 99.4668 | 234.2872 | 9.9406 | 54.4966 | 13.4355 | 171 | -1.3779 | 66.4826 | 232.7893 | 0
868 | 788.4724 | 4.8781 | 61.6366 | 95.1003 | 60.0772 | 5.7133 | 76.4192 | 5.0491 | 6.3067 | 50.2423 | 87.7901 | 8.9653 | 157.8851 | 96.2983 | 225.7106 | 10.0027 | 55.4358 | 13.3115 | 146 | -1.7338 | 65.8882 | 234.7393 | 0
869 | 782.4577 | 5.0388 | 62.0206 | 95.4959 | 60.1008 | 5.6909 | 81.0935 | 4.9531 | 6.2613 | 52.6014 | 88.5426 | 8.9957 | 153.1121 | 91.771 | 218.9773 | 9.9638 | 56.9313 | 13.2042 | 139 | -2.3766 | 65.8848 | 238.6526 | 0
870 | 787.5727 | 3.6386 | 62.0048 | 95.2138 | 59.3436 | 6.4102 | 81.4335 | 4.9052 | 6.3742 | 64.9118 | 91.4047 | 8.9336 | 155.8162 | 89.7938 | 219.9857 | 10.0229 | 59.3057 | 12.6187 | 129 | -2.5516 | 67.1867 | 233.9989 | 0
871 | 797.4054 | 3.1763 | 62.6362 | 95.8075 | 59.8865 | 5.8944 | 81.9822 | 5.0814 | 7.8613 | 84.454 | 92.2847 | 8.9121 | 152.357 | 89.5298 | 216.9988 | 9.9659 | 56.6179 | 12.4697 | 128 | -2.3965 | 68.7107 | 233.6213 | 0
872 | 816.8175 | 3.4786 | 67.5877 | 95.333 | 60.0431 | 5.7457 | 81.809 | 5.0138 | 11.8266 | 88.8286 | 99.5996 | 10.6198 | 161.4521 | 91.1333 | 209.3357 | 9.9015 | 54.8993 | 12.7069 | 139 | -2.5261 | 72.9413 | 238.048 | 0
873 | 831.7561 | 3.6409 | 79.4909 | 92.5223 | 59.3177 | 6.4348 | 80.1721 | 4.6816 | 12.7079 | 81.6454 | 127.7697 | 14.5179 | 178.138 | 92.2342 | 207.9469 | 8.8772 | 55.2432 | 13.1698 | 140 | -2.5988 | 75.251 | 227.9078 | 0.0072972
874 | 848.8495 | 4.0566 | 87.1531 | 91.9742 | 59.8921 | 5.8892 | 79.2037 | 4.499 | 12.3027 | 79.2501 | 149.375 | 9.1419 | 196.5654 | 102.4216 | 216.1687 | 8.3905 | 58.3774 | 13.2963 | 166 | -2.6646 | 100.6061 | 226.7275 | 0.015606
875 | 864.7205 | 3.2365 | 91.2025 | 93.6928 | 59.2587 | 6.4908 | 79.0058 | 4.3099 | 12.0394 | 79.8422 | 158.0343 | 6.0056 | 214.2544 | 112.6239 | 215.5405 | 8.289 | 62.3863 | 13.6452 | 186 | -2.6529 | 111.3494 | 228.6728 | 0.013286
876 | 873.0767 | 1.9203 | 91.9811 | 95.5213 | 59.8871 | 5.8939 | 78.2502 | 4.1091 | 12.0799 | 83.2139 | 148.0007 | 6.0317 | 228.236 | 118.6678 | 221.4158 | 8.3732 | 61.918 | 13.8117 | 195 | -2.6703 | 109.4946 | 222.4009 | 0.017109
877 | 872.3928 | 1.8006 | 90.1415 | 94.4177 | 60.0701 | 5.7201 | 78.9936 | 3.851 | 12.3767 | 84.6593 | 116.5915 | 6.0995 | 231.0849 | 121.7572 | 213.9664 | 8.2932 | 58.3079 | 14.0128 | 203 | -2.6921 | 111.2306 | 222.889 | 0.019726
878 | 875.0159 | 2.0648 | 89.5271 | 95.4277 | 60.1408 | 5.6528 | 78.7963 | 3.7502 | 8.5043 | 84.2595 | 105.5003 | 6.0288 | 227.0515 | 128.7799 | 224.5455 | 8.3543 | 56.9154 | 14.4882 | 222 | -2.6608 | 110.6113 | 223.2613 | 0.018937
879 | 869.3078 | 2.5928 | 71.0823 | 95.2946 | 60.0496 | 5.7395 | 79.3604 | 3.6883 | 5.7252 | 85.4981 | 106.12 | 7.0948 | 221.5868 | 153.6881 | 242.1249 | 8.3003 | 56.2946 | 14.8511 | 246 | -2.5815 | 110.002 | 228.7716 | 0.013564
880 | 865.2941 | 4.0048 | 63.8961 | 94.3211 | 60.1366 | 5.6569 | 79.1847 | 3.7946 | 8.6133 | 67.9455 | 106.4564 | 10.9288 | 213.2412 | 155.6439 | 251.3272 | 8.3905 | 54.9932 | 15.4033 | 232 | -2.6454 | 111.3444 | 224.6554 | 0.0099188
881 | 862.104 | 4.429 | 63.1519 | 94.5905 | 60.0561 | 5.7333 | 79.2306 | 4.109 | 6.7062 | 51.5804 | 107.3953 | 9.8402 | 210.2352 | 160.1221 | 232.4731 | 8.4464 | 55.3804 | 15.4677 | 220 | -2.6538 | 86.515 | 232.9758 | 0
882 | 864.0571 | 5.8524 | 63.3988 | 96.6188 | 59.3459 | 6.408 | 80.6952 | 4.6636 | 6.6786 | 46.8366 | 110.7313 | 8.7136 | 214.7339 | 163.107 | 216.2655 | 8.7291 | 56.4927 | 15.2753 | 203 | -2.5678 | 78.732 | 238.9756 | 0
883 | 850.6242 | 5.4681 | 63.8036 | 96.9389 | 59.082 | 6.6587 | 80.6274 | 4.806 | 11.2445 | 39.7829 | 100.9743 | 8.6014 | 202.0426 | 146.8383 | 209.3399 | 8.9334 | 54.8446 | 15.2367 | 213 | -2.5492 | 78.2081 | 237.826 | 0
884 | 832.8508 | 4.3954 | 63.1987 | 95.5551 | 59.9079 | 5.8741 | 80.1457 | 4.6676 | 9.1388 | 35.8399 | 92.4711 | 8.5698 | 185.0894 | 138.7813 | 218.895 | 8.9555 | 52.0813 | 14.9923 | 212 | -2.5588 | 77.2386 | 238.7093 | 0
885 | 819.6286 | 5.1252 | 62.3976 | 94.3299 | 60.0447 | 5.7442 | 80.4544 | 4.6789 | 7.9183 | 35.2006 | 90.5219 | 8.5139 | 182.755 | 135.8674 | 223.3297 | 8.8927 | 50.3698 | 14.5783 | 205 | -2.6449 | 75.3725 | 237.0694 | 0
886 | 813.0434 | 9.0946 | 62.1772 | 94.6771 | 60.1033 | 5.6885 | 80.2198 | 4.6495 | 7.8028 | 33.5805 | 88.3089 | 8.7145 | 182.1956 | 125.0241 | 219.1351 | 8.8578 | 49.2681 | 13.7566 | 195 | -2.665 | 73.3762 | 235.4367 | 0
887 | 809.3426 | 8.198 | 62.5696 | 94.1783 | 60.0674 | 5.7226 | 79.458 | 4.618 | 7.8562 | 31.7546 | 85.511 | 8.7982 | 176.0833 | 111.6387 | 217.2726 | 8.8855 | 48.8884 | 13.3852 | 181 | -2.6462 | 69.7209 | 231.5509 | 0
888 | 791.6706 | 3.5009 | 62.9541 | 94.1522 | 60.1435 | 5.6503 | 79.1712 | 4.6252 | 7.4881 | 31.4565 | 84.3899 | 8.6109 | 167.8886 | 113.5081 | 212.876 | 8.8555 | 49.4218 | 12.9249 | 155 | -2.6026 | 68.6209 | 232.5754 | 0
889 | 813.6672 | 1.7483 | 62.3034 | 93.9412 | 60.0723 | 5.7179 | 79.1529 | 4.8604 | 6.9475 | 31.804 | 84.4826 | 8.568 | 167.3322 | 120.9548 | 218.2613 | 8.9468 | 49.657 | 12.7998 | 143 | -2.6137 | 67.8215 | 232.6284 | 0
890 | 816.0687 | 1.4966 | 61.8926 | 94.7701 | 59.3521 | 6.4021 | 79.3356 | 4.7216 | 6.3197 | 31.3281 | 84.4773 | 8.5574 | 169.5724 | 111.0261 | 220.6076 | 8.9352 | 49.8028 | 12.4411 | 138 | -2.0597 | 67.9271 | 233.6923 | 0
891 | 793.0618 | 1.6077 | 61.9648 | 94.4376 | 56.7284 | 8.8947 | 79.0723 | 4.2605 | 6.0782 | 30.9423 | 84.8276 | 8.5505 | 168.0988 | 102.7874 | 221.066 | 8.8881 | 49.8783 | 11.5649 | 158 | -0.52128 | 68.0822 | 236.0803 | 0
892 | 798.6922 | 1.5566 | 61.7794 | 93.8091 | 57.6286 | 8.0394 | 79.272 | 4.1501 | 6.2482 | 31.1619 | 85.444 | 8.5372 | 156.3794 | 98.8792 | 212.8181 | 8.9003 | 49.5367 | 11.2662 | 135 | -1.6396 | 68.2101 | 234.6811 | 0
893 | 787.9966 | 1.867 | 61.8271 | 94.3817 | 58.1347 | 7.5586 | 80.1381 | 4.1563 | 6.0853 | 31.6067 | 85.9775 | 8.5296 | 150.4734 | 99.1611 | 200.8391 | 8.8502 | 51.1007 | 11.274 | 132 | -2.2716 | 67.054 | 230.2224 | 0
894 | 783.5368 | 2.84 | 62.1723 | 94.1092 | 59.6072 | 6.1598 | 79.5901 | 4.3591 | 6.328 | 42.8232 | 86.0925 | 8.4884 | 151.6047 | 97.5956 | 197.475 | 8.9117 | 53.7515 | 11.2407 | 132 | -2.7889 | 66.813 | 231.2658 | 0
895 | 789.5899 | 2.9968 | 62.1541 | 94.037 | 60.0282 | 5.7599 | 79.5584 | 4.7282 | 6.2247 | 66.5389 | 87.9646 | 8.5075 | 148.7459 | 97.0827 | 197.0382 | 9.0842 | 51.4221 | 11.2725 | 133 | -2.8899 | 67.2535 | 232.1893 | 0
896 | 805.8026 | 3.0571 | 62.5649 | 95.2028 | 60.1206 | 5.6721 | 79.3999 | 4.6743 | 10.6249 | 65.1948 | 87.1644 | 8.511 | 156.7415 | 94.9194 | 202.6829 | 9.5263 | 49.4072 | 11.5404 | 130 | -2.8627 | 67.2798 | 230.2861 | 0
897 | 804.9082 | 1.9373 | 62.3751 | 92.917 | 60.0737 | 5.7166 | 78.6839 | 4.5914 | 12.3057 | 56.1428 | 87.2431 | 8.1412 | 161.9055 | 92.8896 | 198.5096 | 9.1021 | 48.6242 | 12.1745 | 131 | -2.9056 | 69.1243 | 218.5426 | 0.036653
898 | 810.9293 | 1.6358 | 62.3799 | 92.7654 | 60.1191 | 5.6735 | 77.733 | 4.5092 | 12.6514 | 57.0733 | 89.2963 | 6.3396 | 166.5935 | 100.5243 | 206.0309 | 8.6234 | 48.3854 | 12.3346 | 149 | -2.9311 | 73.7553 | 228.7041 | 0.064813
899 | 842.0554 | 1.563 | 62.2014 | 94.9283 | 59.368 | 6.387 | 77.3435 | 4.2077 | 9.9837 | 68.495 | 97.8062 | 5.7667 | 183.6182 | 123.226 | 201.3391 | 8.3636 | 48.7542 | 12.3462 | 189 | -2.9463 | 77.2665 | 236.3587 | 0.14736
900 | 868.5504 | 2.1894 | 62.9434 | 101.8335 | 59.856 | 5.9234 | 77.3287 | 4.0513 | 11.3853 | 75.1801 | 103.4394 | 5.7346 | 197.4556 | 133.1353 | 194.9471 | 8.4305 | 49.8889 | 12.3269 | 195 | -2.9802 | 76.7809 | 242.3661 | 0.13756
901 | 882.6304 | 2.5067 | 63.8217 | 98.289 | 60.0359 | 5.7525 | 77.2412 | 4.2265 | 11.6809 | 60.9523 | 111.7034 | 6.0434 | 205.7641 | 143.377 | 209.3092 | 8.3374 | 51.1178 | 12.4253 | 203 | -2.9917 | 77.7786 | 239.7557 | 0.065736
902 | 870.4664 | 2.2493 | 63.3738 | 94.2678 | 60.1487 | 5.6454 | 86.6515 | 4.2728 | 7.6041 | 54.4149 | 124.5178 | 6.3447 | 213.5926 | 152.7588 | 222.1001 | 8.4038 | 51.4293 | 13.3237 | 215 | -2.9946 | 79.7071 | 249.6925 | 0.058578
903 | 877.1272 | 3.3222 | 63.1732 | 98.7928 | 60.061 | 5.7287 | 91.8448 | 4.2447 | 6.4841 | 54.8789 | 122.2835 | 7.8248 | 213.519 | 159.3954 | 226.0644 | 8.384 | 51.0407 | 14.2247 | 210 | -3.0179 | 82.2545 | 260.3595 | 0.01399
904 | 880.1243 | 4.5899 | 63.3242 | 100.1508 | 60.0697 | 5.7204 | 83.9002 | 3.9086 | 10.8753 | 56.3451 | 113.5342 | 11.8464 | 208.546 | 154.8271 | 231.8715 | 8.3852 | 50.5276 | 14.6485 | 234 | -3.0396 | 84.5299 | 253.9789 | 0.0083649
905 | 877.8319 | 4.523 | 64.2333 | 98.4534 | 60.1049 | 5.687 | 80.0167 | 4.0412 | 12.6872 | 60.7115 | 112.9198 | 10.6607 | 212.383 | 153.8092 | 259.7662 | 8.8348 | 50.8882 | 14.7313 | 207 | -3.0751 | 81.464 | 246.8494 | 0
906 | 881.0299 | 6.4702 | 64.0957 | 99.6004 | 59.3591 | 6.3955 | 79.1012 | 4.231 | 9.8847 | 65.2646 | 113.8539 | 10.4387 | 212.3351 | 153.6803 | 277.8844 | 9.6516 | 51.7763 | 14.9242 | 191 | -3.0377 | 80.7535 | 240.8212 | 0
907 | 883.6506 | 6.2625 | 64.6895 | 100.2289 | 59.0728 | 6.6675 | 78.8688 | 4.2648 | 11.2187 | 58.1739 | 112.4217 | 12.6954 | 196.2104 | 149.7616 | 247.15 | 9.4914 | 52.2448 | 14.6212 | 174 | -2.9615 | 78.9031 | 242.9679 | 0
908 | 872.3201 | 4.565 | 64.3562 | 96.4942 | 59.8471 | 5.9319 | 78.9124 | 4.5461 | 8.9853 | 45.8563 | 111.4208 | 12.9715 | 183.7821 | 145.2992 | 209.7112 | 9.0484 | 51.5915 | 14.033 | 157 | -2.8802 | 75.9665 | 242.8932 | 0
909 | 839.2727 | 3.6475 | 62.9843 | 94.8243 | 60.0976 | 5.6939 | 79.026 | 4.5158 | 7.882 | 41.3049 | 100.3133 | 10.3539 | 183.3774 | 139.6672 | 196.3087 | 8.8774 | 50.6514 | 13.5199 | 141 | -2.9333 | 71.9649 | 243.2916 | 0
910 | 823.6749 | 5.9022 | 62.2491 | 94.6124 | 60.8373 | 4.9912 | 79.1405 | 4.6504 | 7.868 | 41.8615 | 93.6094 | 9.4661 | 173.1876 | 133.3356 | 196.4833 | 9.0528 | 50.1716 | 13.9249 | 136 | -2.9366 | 68.6155 | 237.2832 | 0
911 | 804.2364 | 4.2454 | 62.635 | 95.1241 | 60.3602 | 5.4444 | 79.088 | 4.811 | 7.64 | 43.4822 | 89.5786 | 9.2114 | 168.9671 | 128.0899 | 201.8062 | 9.5953 | 49.9198 | 13.7043 | 128 | -2.9268 | 66.8204 | 240.3586 | 0
912 | 784.5759 | 2.1409 | 63.0532 | 95.5268 | 60.1036 | 5.6882 | 79.1415 | 4.8866 | 6.6901 | 38.8408 | 86.8839 | 9.1027 | 159.6348 | 122.8976 | 211.54 | 9.7859 | 49.884 | 12.8456 | 113 | -2.9324 | 66.5157 | 234.2826 | 0
913 | 788.6246 | 1.4962 | 62.8246 | 95.166 | 60.0612 | 5.7284 | 79.9118 | 4.9371 | 6.3829 | 35.8379 | 86.6812 | 9.1131 | 153.8499 | 113.6633 | 225.8201 | 9.9441 | 49.9769 | 12.7186 | 108 | -2.8665 | 67.4496 | 238.0349 | 0
914 | 781.8177 | 1.2337 | 62.2744 | 94.678 | 60.0855 | 5.7054 | 80.1536 | 5.1567 | 6.3084 | 35.2747 | 86.6018 | 9.1249 | 151.0604 | 108.3692 | 219.2233 | 9.9661 | 50.0472 | 12.1685 | 110 | -2.8513 | 67.4716 | 238.7566 | 0
915 | 776.8226 | 3.1171 | 61.9566 | 95.117 | 60.0932 | 5.6981 | 80.0113 | 5.1987 | 6.1847 | 36.262 | 86.9074 | 9.3849 | 153.3291 | 109.0212 | 211.0554 | 10.009 | 49.4203 | 11.9247 | 127 | -2.8762 | 68.4587 | 239.0318 | 0
916 | 782.4481 | 2.4733 | 62.3011 | 94.925 | 60.0877 | 5.7033 | 74.7929 | 5.0567 | 6.216 | 38.4482 | 87.882 | 9.6422 | 152.4976 | 115.6729 | 205.9265 | 9.9721 | 49.3072 | 11.9069 | 109 | -2.8527 | 72.2527 | 244.1554 | 0
917 | 790.3428 | 1.9022 | 63.9788 | 96.9821 | 60.0732 | 5.7171 | 76.5687 | 5.0291 | 6.2327 | 50.2753 | 87.9868 | 9.5875 | 158.1859 | 125.0005 | 197.7573 | 9.903 | 50.6087 | 11.8905 | 110 | -2.8902 | 69.9711 | 272.1095 | 0
918 | 801.3037 | 2.8932 | 62.9656 | 95.8764 | 59.3037 | 6.4481 | 80.6102 | 5.0698 | 6.186 | 65.6611 | 88.5276 | 10.9371 | 172.7541 | 125.934 | 204.8727 | 9.8224 | 52.7986 | 11.9856 | 113 | -2.9462 | 71.3376 | 287.4949 | 0
919 | 825.4332 | 4.1849 | 69.2448 | 101.5109 | 57.5435 | 8.1203 | 89.0075 | 5.0091 | 7.8273 | 93.3912 | 113.0028 | 20.2371 | 212.6754 | 177.7293 | 246.4852 | 12.9628 | 50.8039 | 12.7142 | 176 | -2.5746 | 125.2668 | 324.4424 | 0
920 | 905.8262 | 6.3777 | 86.636 | 113.5838 | 53.9255 | 11.5574 | 107.158 | 6.0947 | 13.0207 | 109.3304 | 149.5837 | 36.1725 | 285.7712 | 235.1048 | 345.7565 | 25.737 | 57.5247 | 13.0948 | 282 | -2.4044 | 170.2432 | 395.3262 | 0
921 | 1006.171 | 7.9947 | 101.3664 | 122.696 | 49.9216 | 15.3611 | 125.0315 | 7.3668 | 16.208 | 114.5653 | 175.1951 | 43.243 | 356.6813 | 295.1506 | 450.6002 | 36.075 | 70.893 | 17.1885 | 308 | -2.0594 | 195.3461 | 455.2332 | 0.0051441
922 | 1098.9198 | 8.6971 | 104.2892 | 137.163 | 49.0787 | 16.1619 | 129.1768 | 8.3841 | 19.906 | 118.3283 | 189.0847 | 44.0172 | 404.0905 | 338.3115 | 531.1574 | 43.5511 | 82.0098 | 18.0158 | 355 | -1.3324 | 223.6958 | 490.2476 | 0.0069101
923 | 1139.3523 | 8.392 | 105.6183 | 149.9425 | 48.4742 | 16.7362 | 118.2048 | 8.7821 | 24.6287 | 112.6954 | 198.468 | 44.9376 | 414.5783 | 368.485 | 568.0532 | 46.0422 | 83.7919 | 18.8476 | 405 | -1.4911 | 239.9798 | 516.7104 | 0.0081837
924 | 1157.8403 | 8.5879 | 111.9467 | 150.9877 | 48.8957 | 16.3357 | 127.3794 | 9.0242 | 24.1187 | 122.841 | 196.3979 | 46.0362 | 431.6646 | 382.0081 | 612.6752 | 44.3723 | 87.7812 | 19.3577 | 345 | -1.276 | 252.678 | 520.1634 | 0.0094568
925 | 1169.7289 | 7.9975 | 111.504 | 143.2804 | 48.1542 | 17.0401 | 133.2786 | 9.5288 | 21.9618 | 121.7322 | 193.8889 | 43.5388 | 431.1092 | 374.0428 | 605.1073 | 45.7394 | 87.4593 | 19.0291 | 361 | 2.4178 | 247.0768 | 523.4821 | 0.020307
926 | 1162.2802 | 6.7165 | 114.1955 | 147.1397 | 48.2226 | 16.9752 | 133.4586 | 9.9971 | 24.9255 | 109.4358 | 203.4691 | 43.0254 | 436.7824 | 375.7087 | 596.4786 | 46.3562 | 88.5392 | 19.7258 | 307 | 2.7195 | 236.138 | 518.8503 | 0.024569
927 | 1200.9001 | 5.8105 | 116.8893 | 147.3094 | 46.6629 | 18.4569 | 134.0934 | 8.8929 | 25.622 | 110.8572 | 201.2946 | 42.6672 | 445.1695 | 388.3209 | 586.3479 | 44.9685 | 86.3143 | 20.0578 | 311 | 3.5868 | 241.1116 | 531.8839 | 0.01561
928 | 1159.0682 | 5.0497 | 116.5606 | 147.4796 | 43.7748 | 21.2006 | 131.9534 | 7.7612 | 22.1867 | 104.7195 | 191.6355 | 41.3409 | 436.2543 | 372.8142 | 567.2493 | 42.6437 | 85.6795 | 20.2674 | 287 | 4.109 | 235.892 | 549.2992 | 0.009579
929 | 1110.7698 | 5.5974 | 107.3117 | 141.3436 | 51.4962 | 13.8653 | 120.7441 | 7.3909 | 18.0887 | 95.449 | 186.1354 | 38.4291 | 410.2374 | 346.3851 | 511.3815 | 34.0203 | 80.756 | 19.7555 | 262 | 2.3605 | 213.2694 | 495.9607 | 0
930 | 1048.4613 | 6.0541 | 98.8401 | 133.8209 | 56.4501 | 9.159 | 108.3659 | 6.2493 | 18.4747 | 94.4731 | 181.1007 | 38.848 | 356.4633 | 271.5115 | 418.2887 | 19.9698 | 78.8827 | 18.8989 | 235 | 1.7783 | 174.252 | 398.2697 | 0
931 | 1003.5774 | 5.2323 | 93.4937 | 120.0361 | 57.7922 | 7.884 | 103.0765 | 5.3221 | 16.2382 | 85.0703 | 151.9216 | 32.2081 | 309.7676 | 202.298 | 374.3803 | 13.7545 | 81.0382 | 17.4669 | 215 | 1.871 | 152.6347 | 344.5508 | 0
932 | 954.8809 | 4.5517 | 81.8831 | 109.2721 | 58.1181 | 7.5745 | 95.1977 | 5.1586 | 10.0937 | 60.1959 | 121.3911 | 15.2686 | 270.2699 | 166.9715 | 324.6564 | 11.2587 | 67.7751 | 15.7224 | 199 | 1.8717 | 133.7586 | 295.8722 | 0
933 | 922.7645 | 3.9575 | 65.5676 | 103.3548 | 58.1381 | 7.5554 | 84.2038 | 5.0558 | 10.4334 | 48.2307 | 111.5999 | 9.0059 | 238.0245 | 140.5874 | 278.609 | 10.4619 | 57.2081 | 14.2787 | 180 | 1.7091 | 125.3488 | 274.3996 | 0
934 | 885.489 | 4.0531 | 61.2103 | 98.9575 | 58.0297 | 7.6584 | 79.8912 | 4.8659 | 13.6 | 42.0729 | 110.0819 | 8.5455 | 196.0774 | 129.035 | 250.474 | 10.4154 | 53.1032 | 13.4365 | 162 | 1.7218 | 119.0935 | 264.5762 | 0
935 | 840.3264 | 3.3263 | 60.9769 | 96.137 | 58.9186 | 6.814 | 71.5118 | 4.7911 | 8.98 | 38.0049 | 103.6219 | 8.375 | 172.085 | 115.9742 | 216.3748 | 10.4328 | 51.7297 | 12.7032 | 136 | 1.7481 | 111.7225 | 267.7687 | 0
936 | 813.2926 | 2.0322 | 60.5632 | 95.2961 | 59.1026 | 6.6391 | 73.5101 | 4.612 | 6.4667 | 34.5702 | 91.6655 | 8.3924 | 163.803 | 108.6718 | 208.8493 | 10.5692 | 50.7279 | 12.5718 | 116 | 1.8584 | 82.7777 | 264.9537 | 0
937 | 808.1585 | 1.3476 | 60.857 | 95.8938 | 59.0466 | 6.6924 | 77.5563 | 4.5216 | 6.2727 | 32.3674 | 88.183 | 8.4421 | 166.1553 | 103.5028 | 224.8766 | 10.5971 | 50.1557 | 12.4936 | 106 | 1.9505 | 69.8522 | 258.3204 | 0
938 | 806.4341 | 1.2289 | 60.6403 | 96.6335 | 59.0988 | 6.6428 | 77.1514 | 4.7793 | 6.2113 | 31.878 | 89.7127 | 8.4365 | 173.5348 | 100.142 | 218.6491 | 10.5662 | 50.2431 | 12.539 | 106 | 1.9515 | 67.5678 | 259.1882 | 0
939 | 806.4026 | 1.314 | 60.4812 | 95.7278 | 59.0771 | 6.6634 | 67.4255 | 4.9095 | 6.102 | 32.1465 | 91.9804 | 8.4274 | 171.4805 | 98.7025 | 209.011 | 10.6274 | 50.4155 | 12.5482 | 123 | 1.9554 | 68.2397 | 254.9382 | 0
940 | 817.6286 | 1.2226 | 60.3672 | 96.9112 | 59.1203 | 6.6224 | 72.8535 | 4.8427 | 6.2533 | 34.9321 | 93.5326 | 8.4412 | 165.0153 | 103.8326 | 206.7933 | 10.5671 | 50.4406 | 12.5489 | 104 | 1.9134 | 67.7108 | 259.6405 | 0
941 | 810.7785 | 1.5461 | 60.309 | 95.8177 | 58.3602 | 7.3444 | 78.8391 | 5.006 | 6.21 | 47.0198 | 93.5726 | 8.4272 | 161.5626 | 115.1623 | 208.5911 | 10.6441 | 51.7954 | 12.5739 | 102 | 1.9442 | 67.7097 | 276.7563 | 0
942 | 820.9411 | 2.6356 | 60.7151 | 96.335 | 58.8602 | 6.8694 | 77.2912 | 5.2518 | 6.2727 | 62.5684 | 91.1427 | 10.0046 | 169.9334 | 123.6766 | 213.5026 | 10.4478 | 54.5785 | 12.537 | 112 | 1.9006 | 71.1823 | 308.6001 | 0
943 | 854.4389 | 4.1813 | 63.0747 | 104.4492 | 56.6834 | 8.9374 | 78.349 | 5.2099 | 10.5423 | 99.1812 | 102.3873 | 21.072 | 214.4995 | 174.1211 | 248.1661 | 13.4071 | 52.5449 | 12.5202 | 179 | 1.6621 | 114.1307 | 346.2135 | 0
944 | 934.6653 | 6.9911 | 84.0303 | 110.5809 | 51.4163 | 13.9412 | 106.6145 | 6.4503 | 15.5761 | 109.7365 | 143.631 | 36.1686 | 289.1995 | 247.6616 | 344.0448 | 29.9998 | 57.362 | 13.4798 | 238 | 2.24 | 157.1869 | 419.368 | 0
945 | 1029.6548 | 9.1715 | 104.6323 | 124.4536 | 50.1212 | 15.1715 | 125.2749 | 7.9775 | 15.0463 | 93.4283 | 172.5832 | 38.2458 | 352.7131 | 312.4199 | 467.7359 | 38.7919 | 68.4557 | 17.5484 | 335 | 2.3356 | 190.5001 | 493.5982 | 0.0089943
946 | 1130.9087 | 7.9691 | 110.9666 | 138.2544 | 47.1329 | 18.0104 | 130.6399 | 9.1886 | 16.6373 | 94.624 | 189.656 | 39.2665 | 407.0741 | 347.5829 | 543.7875 | 40.2697 | 89.4583 | 19.3116 | 327 | 2.658 | 219.0232 | 546.8049 | 0.032436
947 | 1181.7457 | 7.2349 | 113.2281 | 140.6602 | 45.9883 | 19.0978 | 128.7411 | 9.0388 | 19.9847 | 97.2054 | 200.4431 | 41.3554 | 434.1385 | 371.1735 | 581.2917 | 42.1872 | 107.541 | 19.7282 | 357 | 2.558 | 222.0544 | 546.9527 | 0.045476
948 | 1213.1632 | 6.5204 | 110.2642 | 141.5887 | 46.7392 | 18.3844 | 133.3039 | 8.7909 | 20.2427 | 112.7341 | 200.4675 | 39.8944 | 443.7846 | 386.8869 | 593.8083 | 41.4181 | 112.7218 | 19.5187 | 333 | 2.9584 | 220.4514 | 560.7303 | 0.073382
949 | 1208.2396 | 5.4568 | 110.0267 | 144.2019 | 48.7829 | 16.4429 | 133.0129 | 7.7726 | 19.8607 | 110.9924 | 196.5792 | 40.0455 | 442.4866 | 367.7842 | 584.5572 | 41.6252 | 109.1513 | 19.633 | 366 | 2.7535 | 218.3164 | 591.9195 | 0.075324
950 | 1214.1171 | 3.8328 | 105.46 | 148.6637 | 47.3852 | 17.7707 | 129.1844 | 7.805 | 20.8094 | 113.8624 | 200.5606 | 41.1744 | 434.9388 | 365.3099 | 602.4 | 44.1534 | 109.9478 | 19.5501 | 321 | 2.1956 | 226.4102 | 602.7252 | 0.052127
951 | 1197.6811 | 3.551 | 106.5759 | 148.7716 | 45.4948 | 19.5666 | 126.9003 | 7.5291 | 21.1932 | 108.5001 | 202.7639 | 41.068 | 439.6025 | 377.6973 | 610.5055 | 46.0302 | 109.9534 | 19.4151 | 309 | 2.9059 | 227.5363 | 597.5392 | 0.02941
952 | 1175.9123 | 5.4747 | 102.8173 | 144.861 | 42.8584 | 22.0711 | 126.993 | 7.6771 | 18.9475 | 105.2561 | 204.6981 | 37.7279 | 433.6488 | 363.7937 | 597.7092 | 42.7003 | 109.6931 | 19.3665 | 287 | 3.77 | 222.0662 | 578.3716 | 0.010907
953 | 1141.9446 | 7.1716 | 97.9136 | 137.8993 | 50.0426 | 15.2462 | 126.3693 | 7.6399 | 18.0671 | 101.2093 | 204.2797 | 34.2439 | 414.8213 | 327.9955 | 557.5157 | 34.4593 | 107.1083 | 18.7575 | 248 | 2.6225 | 213.8203 | 514.2222 | 0
954 | 1076.1464 | 9.9497 | 93.3567 | 126.4181 | 54.3069 | 11.1951 | 116.5856 | 6.6857 | 17.2793 | 91.738 | 195.1944 | 32.2318 | 374.1386 | 267.9722 | 444.9148 | 19.9306 | 86.8078 | 18.0593 | 224 | 1.84 | 182.0235 | 433.8971 | 0
955 | 1005.3354 | 13.0082 | 91.2373 | 110.0417 | 55.8347 | 9.7436 | 110.3918 | 5.2824 | 15.448 | 80.6556 | 159.9912 | 27.3741 | 320.0207 | 215.5103 | 364.0166 | 13.3591 | 71.2349 | 16.8569 | 222 | 1.7224 | 161.8684 | 370.5564 | 0
956 | 962.5618 | 11.1822 | 82.1967 | 104.8406 | 56.8814 | 8.7493 | 94.414 | 4.9793 | 9.5633 | 58.0935 | 126.4387 | 12.6653 | 276.7736 | 192.2678 | 323.8075 | 12.1458 | 62.2603 | 16.6177 | 190 | 1.6999 | 143.3458 | 324.5266 | 0
957 | 919.8499 | 9.7392 | 66.7012 | 101.9815 | 57.1216 | 8.5211 | 83.7547 | 4.9538 | 7.0287 | 47.8344 | 114.978 | 8.0057 | 245.5453 | 181.4627 | 283.395 | 11.8081 | 55.6638 | 15.8443 | 163 | 1.5511 | 131.7844 | 296.9542 | 0
958 | 891.9674 | 9.3222 | 62.0804 | 98.3451 | 57.8462 | 7.8327 | 69.7136 | 5.0519 | 6.6413 | 43.4459 | 110.3993 | 7.7729 | 218.4148 | 159.6805 | 246.4863 | 10.9188 | 52.4404 | 14.4214 | 163 | 1.6045 | 129.8203 | 300.2345 | 0
959 | 873.1567 | 6.715 | 61.5824 | 95.4344 | 58.0768 | 7.6137 | 69.0631 | 5.5563 | 6.184 | 37.0723 | 96.5373 | 7.8216 | 187.1652 | 148.3443 | 228.2697 | 10.5333 | 52.0604 | 13.6012 | 142 | 1.678 | 117.9231 | 294.392 | 0
960 | 851.5957 | 2.8923 | 60.9584 | 96.4412 | 58.0996 | 7.592 | 77.2714 | 5.6705 | 6.084 | 35.0232 | 88.3273 | 7.546 | 172.6211 | 138.7618 | 209.4409 | 10.5136 | 51.7959 | 13.1972 | 126 | 1.6824 | 93.5723 | 300.8925 | 0
961 | 842.1178 | 1.7614 | 60.8104 | 96.7375 | 58.8783 | 6.8522 | 71.782 | 5.2275 | 6.166 | 35.0961 | 87.222 | 7.3472 | 165.5854 | 142.8043 | 232.9938 | 10.3824 | 51.4445 | 12.9482 | 113 | 1.6911 | 84.0955 | 295.3544 | 0
962 | 836.3125 | 1.82 | 60.6675 | 95.559 | 59.1412 | 6.6025 | 66.5589 | 5.0496 | 6.1313 | 35.703 | 87.4589 | 7.3193 | 170.9669 | 130.9064 | 228.921 | 10.4158 | 51.3374 | 13.0551 | 109 | 1.7589 | 83.1879 | 295.7631 | 0
963 | 821.822 | 6.3012 | 60.7122 | 95.4676 | 58.2652 | 7.4347 | 67.1928 | 5.0653 | 6.176 | 35.966 | 88.233 | 7.4601 | 167.8393 | 122.2631 | 216.608 | 10.4153 | 51.3014 | 12.3951 | 125 | 1.7504 | 81.0595 | 290.2581 | 0
964 | 820.8753 | 6.4987 | 60.5877 | 96.8259 | 58.8313 | 6.8969 | 76.243 | 5.3912 | 6.1047 | 38.7642 | 88.9018 | 7.3401 | 163.303 | 117.544 | 219.7066 | 10.5099 | 51.2097 | 11.717 | 103 | 1.8244 | 78.092 | 293.8066 | 0
965 | 827.338 | 3.0252 | 60.7401 | 96.1231 | 59.0743 | 6.666 | 71.7956 | 5.3401 | 6.1156 | 50.0353 | 88.9088 | 7.2501 | 160.6577 | 116.1392 | 216.555 | 10.3945 | 52.776 | 11.5634 | 102 | 1.757 | 77.6168 | 310.1419 | 0
966 | 831.5695 | 2.8449 | 60.9275 | 96.9584 | 58.3043 | 7.3976 | 67.4702 | 5.3195 | 6.306 | 65.2485 | 88.9089 | 9.1387 | 176.7873 | 123.7536 | 229.0382 | 10.3802 | 55.3744 | 11.5649 | 109 | 1.7478 | 82.7161 | 343.1425 | 0
967 | 867.806 | 4.4169 | 68.8293 | 107.4458 | 56.6017 | 9.015 | 78.9232 | 5.6121 | 8.1137 | 94.3808 | 101.0759 | 23.1085 | 211.3873 | 168.9157 | 255.8221 | 13.5758 | 52.8402 | 11.5222 | 186 | 1.9201 | 128.7664 | 377.0263 | 0
968 | 943.9743 | 6.7864 | 86.8659 | 113.828 | 49.7964 | 15.48 | 111.8914 | 6.5277 | 13.9567 | 108.0131 | 146.5948 | 36.3375 | 290.1663 | 230.2951 | 347.9754 | 27.8863 | 57.8377 | 12.4794 | 264 | 2.395 | 176.185 | 446.8844 | 0
969 | 1035.0385 | 8.291 | 105.715 | 127.9552 | 48.1599 | 17.0347 | 121.5573 | 7.7334 | 18.358 | 101.9342 | 178.9083 | 36.9511 | 362.5941 | 274.1602 | 456.907 | 38.219 | 67.9596 | 15.8617 | 281 | 2.6591 | 202.1949 | 521.3563 | 0.029072
970 | 1123.6956 | 7.6584 | 113.4223 | 134.4542 | 49.5955 | 15.6709 | 126.3923 | 8.7836 | 19.9007 | 112.8356 | 192.5182 | 37.5467 | 416.2304 | 315.4389 | 524.5727 | 42.9246 | 75.9056 | 17.8729 | 343 | 2.8985 | 229.6911 | 563.986 | 0.037981
971 | 1163.0629 | 6.8851 | 113.8104 | 137.4519 | 49.3361 | 15.9173 | 137.997 | 9.0089 | 21.296 | 114.5536 | 196.4569 | 43.854 | 443.3321 | 348.0132 | 571.3059 | 45.3522 | 81.5232 | 19.3563 | 365 | 3.9258 | 240.2611 | 568.4526 | 0.045683
972 | 1185.296 | 5.3498 | 116.1284 | 135.5967 | 48.3115 | 16.8907 | 140.2908 | 8.8887 | 22.0353 | 106.9135 | 196.853 | 43.3486 | 449.729 | 355.8859 | 598.6658 | 45.1066 | 82.735 | 20.0141 | 354 | 3.8953 | 234.6263 | 582.4789 | 0.093061
973 | 1170.8898 | 4.5437 | 114.2402 | 135.9752 | 46.4596 | 18.65 | 133.8184 | 8.5822 | 22.3553 | 107.3159 | 195.9007 | 39.6608 | 443.4416 | 357.5496 | 596.4291 | 44.7007 | 81.7872 | 20.3826 | 368 | 3.3532 | 232.0459 | 593.784 | 0.10952
974 | 1187.5623 | 3.8966 | 118.7625 | 136.2878 | 47.8581 | 17.3214 | 132.5517 | 8.0775 | 22.0267 | 111.9619 | 198.6681 | 37.2516 | 452.4494 | 379.6043 | 580.329 | 45.0811 | 90.5209 | 21.0359 | 307 | 3.2153 | 238.3286 | 609.1415 | 0.080285
975 | 1177.1727 | 4.0788 | 117.9159 | 137.8329 | 48.0715 | 17.1187 | 131.3748 | 7.2869 | 21.3447 | 112.4791 | 201.2566 | 36.3361 | 459.1263 | 388.6678 | 564.7792 | 43.8918 | 100.945 | 21.1673 | 307 | 3.3792 | 239.1539 | 585.7104 | 0.050329
976 | 1159.8896 | 4.7019 | 115.7338 | 141.7144 | 46.4846 | 18.6263 | 119.8889 | 6.874 | 19.2727 | 111.073 | 199.013 | 35.7188 | 449.5565 | 367.4015 | 562.5674 | 41.4949 | 104.4735 | 21.4871 | 310 | 3.7464 | 228.7248 | 565.1839 | 0.017354
977 | 1133.9656 | 5.7446 | 112.768 | 133.996 | 53.0608 | 12.3789 | 114.5897 | 7.4065 | 19.7047 | 110.9996 | 193.473 | 37.9921 | 425.4674 | 336.1455 | 510.0506 | 34.3017 | 105.4814 | 21.5119 | 274 | 3.1507 | 205.918 | 526.0073 | 0
978 | 1086.2718 | 5.9506 | 103.6731 | 123.9459 | 57.4014 | 8.2553 | 105.5675 | 7.0822 | 20.7773 | 103.1363 | 185.6779 | 39.3047 | 373.3615 | 265.8661 | 408.9833 | 19.5168 | 87.6517 | 20.8304 | 261 | 2.8717 | 180.2218 | 463.2032 | 0
979 | 1027.4773 | 5.3603 | 98.7914 | 112.0593 | 58.9161 | 6.8163 | 86.2314 | 6.9741 | 18.116 | 87.3706 | 153.1623 | 35.8618 | 324.7328 | 202.1854 | 345.7649 | 12.3824 | 69.1456 | 18.7533 | 258 | 2.9215 | 168.1106 | 404.5507 | 0
980 | 957.2562 | 4.8978 | 88.0668 | 105.4167 | 59.812 | 5.9653 | 80.6153 | 6.0828 | 12.4619 | 58.1409 | 125.4876 | 20.1226 | 281.0662 | 172.2222 | 308.4071 | 11.3711 | 60.9627 | 16.9267 | 226 | 2.984 | 149.9851 | 345.6984 | 0
981 | 915.548 | 4.7573 | 67.1691 | 99.8471 | 59.2963 | 6.4551 | 78.4397 | 5.6086 | 10.355 | 48.6788 | 116.4674 | 17.478 | 251.3343 | 152.9474 | 274.0632 | 11.3592 | 55.4454 | 15.3882 | 204 | 3.0103 | 142.5158 | 329.5008 | 0
982 | 876.3812 | 4.2796 | 61.3659 | 97.4877 | 59.8878 | 5.8933 | 70.8551 | 5.3396 | 10.0328 | 45.9334 | 113.4736 | 12.0621 | 211.908 | 131.8947 | 237.3512 | 10.2527 | 52.2103 | 13.8856 | 178 | 3.0428 | 137.2088 | 322.4563 | 0
983 | 842.2663 | 3.2829 | 60.9193 | 95.8883 | 59.299 | 6.4525 | 71.1733 | 5.402 | 9.2083 | 37.594 | 101.9835 | 9.2229 | 192.4708 | 124.0065 | 225.9556 | 9.8946 | 51.4353 | 13.6827 | 154 | 3.0744 | 123.9383 | 315.9398 | 0
984 | 820.227 | 1.94 | 60.0618 | 95.5708 | 59.9607 | 5.824 | 80.072 | 5.418 | 9.2626 | 33.1855 | 92.2349 | 8.609 | 185.96 | 121.4353 | 222.6098 | 9.8371 | 51.3254 | 13.5079 | 133 | 3.1495 | 94.758 | 312.6605 | 0
985 | 809.0608 | 4.8035 | 59.7327 | 96.7069 | 60.0859 | 5.705 | 73.2906 | 5.5179 | 9.3055 | 31.4937 | 88.4644 | 8.4373 | 184.8224 | 116.1459 | 244.2658 | 9.8451 | 51.4192 | 12.5707 | 112 | 3.1469 | 83.2867 | 305.9545 | 0
986 | 812.2565 | 8.0354 | 59.5698 | 96.7757 | 59.2528 | 6.4965 | 68.044 | 5.7208 | 8.9046 | 31.4314 | 88.2676 | 8.4819 | 187.5445 | 110.2234 | 249.5976 | 9.8093 | 52.3396 | 12.1425 | 111 | 3.2432 | 81.9895 | 295.8883 | 0
987 | 803.1158 | 8.6446 | 59.7352 | 96.5968 | 59.0789 | 6.6617 | 74.5053 | 5.6134 | 7.956 | 31.4796 | 89.8938 | 8.5081 | 188.0957 | 109.254 | 237.5282 | 9.7371 | 51.8897 | 12.0956 | 126 | 3.288 | 82.5706 | 289.8217 | 0
988 | 806.0227 | 5.492 | 59.7989 | 96.0528 | 59.1554 | 6.589 | 81.2039 | 5.4774 | 6.824 | 33.9158 | 90.5458 | 8.4831 | 181.558 | 114.9383 | 224.6055 | 9.7719 | 51.7009 | 12.1225 | 105 | 3.3802 | 80.8281 | 296.6503 | 0
989 | 810.6975 | 2.5772 | 59.6961 | 95.5251 | 59.0935 | 6.6478 | 74.331 | 5.5368 | 6.454 | 46.05 | 90.8638 | 8.4906 | 171.0835 | 115.6893 | 220.3589 | 9.8138 | 53.0708 | 12.102 | 104 | 3.2176 | 79.6048 | 316.4756 | 0
990 | 815.989 | 2.8299 | 60.7796 | 96.1733 | 58.2706 | 7.4295 | 69.1079 | 5.6085 | 6.5473 | 61.317 | 92.2409 | 9.893 | 177.6135 | 123.277 | 228.6907 | 9.7126 | 55.6342 | 12.1053 | 105 | 3.3016 | 85.9702 | 340.8027 | 0
991 | 859.5996 | 4.4908 | 66.9332 | 103.5743 | 56.4832 | 9.1276 | 80.4838 | 5.4271 | 12.6529 | 94.2699 | 103.4487 | 20.5425 | 223.1651 | 169.2961 | 288.1402 | 12.9357 | 53.5841 | 13.0067 | 185 | 3.5528 | 127.475 | 388.0143 | 0
992 | 926.2673 | 5.6696 | 91.2934 | 109.4073 | 51.4824 | 13.8783 | 112.7502 | 6.1671 | 18.6013 | 110.6045 | 147.6883 | 34.5013 | 298.0251 | 227.6475 | 377.5087 | 27.5541 | 58.578 | 13.6738 | 282 | 3.7011 | 174.3039 | 453.8374 | 0
993 | 1034.0849 | 5.1836 | 103.9646 | 118.4016 | 48.5468 | 16.6672 | 121.2232 | 7.1142 | 18.7278 | 108.8969 | 180.0075 | 38.9489 | 355.2734 | 276.5002 | 463.4389 | 37.3047 | 69.2638 | 16.4153 | 299 | 3.2909 | 203.8398 | 517.6128 | 0.01432
994 | 1134.4159 | 4.3697 | 110.2724 | 128.5157 | 49.6169 | 15.6505 | 126.5965 | 7.8029 | 19.1707 | 116.2604 | 189.6512 | 40.111 | 399.4326 | 325.6503 | 536.927 | 42.2036 | 79.2254 | 18.6077 | 302 | 3.3436 | 238.949 | 550.4475 | 0.02531
995 | 1186.1626 | 3.7002 | 111.5992 | 137.8295 | 49.3728 | 15.8825 | 135.2973 | 8.4088 | 20.382 | 104.4501 | 193.9272 | 41.8248 | 437.1257 | 348.1024 | 561.3424 | 43.857 | 86.2172 | 18.4546 | 350 | 3.7276 | 255.0261 | 579.1828 | 0.10338
996 | 1211.9798 | 4.0877 | 115.1007 | 141.3147 | 48.3061 | 16.8958 | 129.5183 | 9.0252 | 21.0033 | 107.6029 | 196.9712 | 41.1545 | 449.7099 | 360.5338 | 592.8643 | 44.2975 | 86.4606 | 18.1359 | 315 | 4.0436 | 256.9903 | 587.1103 | 0.066136
997 | 1205.9754 | 4.5252 | 115.5847 | 139.0522 | 48.0589 | 17.1307 | 133.1588 | 8.9092 | 18.7633 | 105.0674 | 197.8291 | 42.6851 | 444.4379 | 354.7979 | 594.2687 | 44.3492 | 84.7048 | 18.9896 | 347 | 3.7278 | 249.1516 | 598.1279 | 0.098306
998 | 1207.6483 | 4.0657 | 116.3443 | 141.7592 | 47.4294 | 17.7287 | 129.5256 | 9.6834 | 22.9553 | 102.9487 | 204.5036 | 41.2366 | 442.4446 | 352.7828 | 579.4005 | 43.5564 | 86.4938 | 19.7092 | 307 | 3.4003 | 250.8466 | 587.8355 | 0.0579
999 | 1195.9262 | 5.5145 | 116.6979 | 149.5515 | 48.5071 | 16.7048 | 116.492 | 9.1981 | 23.3673 | 102.8802 | 209.0895 | 41.2034 | 449.482 | 347.7147 | 583.7741 | 44.5193 | 88.172 | 20.1032 | 298 | 3.6036 | 244.38 | 575.7733 | 0.047577
1000 | 1163.4938 | 10.9988 | 110.7663 | 143.8643 | 47.591 | 17.5752 | 122.7699 | 8.5336 | 21.0607 | 101.1594 | 202.2727 | 39.4549 | 441.8406 | 331.5078 | 596.5209 | 42.9528 | 86.4704 | 20.2095 | 281 | 3.1625 | 234.833 | 554.45 | 0.015134
1001 | 1158.0371 | 13.0356 | 104.4055 | 134.5375 | 55.6482 | 9.9208 | 117.9615 | 8.271 | 19.178 | 96.8422 | 196.5065 | 38.0087 | 425.0297 | 311.4261 | 549.0265 | 34.8716 | 81.5837 | 19.9821 | 255 | 2.8061 | 217.9633 | 489.1072 | 0.0012545
1002 | 1080.7125 | 12.6202 | 100.1138 | 124.6575 | 58.0963 | 7.5952 | 100.0505 | 7.7927 | 18.3389 | 91.6466 | 186.0592 | 35.4366 | 368.239 | 252.4443 | 463.9471 | 21.3948 | 74.8662 | 18.8172 | 237 | 2.79 | 199.344 | 408.1437 | 0
1003 | 992.7322 | 11.9743 | 94.4775 | 114.0089 | 58.8469 | 6.882 | 94.4019 | 6.704 | 16.2118 | 95.3255 | 148.5521 | 30.0167 | 316.1371 | 204.5111 | 398.4309 | 14.2923 | 68.6078 | 17.5677 | 230 | 2.8333 | 183.8171 | 343.9305 | 0
1004 | 957.6007 | 7.7872 | 79.8327 | 111.4841 | 59.0641 | 6.6757 | 79.2908 | 6.1851 | 12.1586 | 96.3972 | 113.5801 | 17.234 | 272.6488 | 184.8234 | 356.3887 | 11.2725 | 63.1327 | 16.7503 | 204 | 2.9762 | 166.0665 | 295.0525 | 0
1005 | 927.8998 | 4.3458 | 59.1494 | 108.1483 | 59.143 | 6.6008 | 69.2368 | 6.0458 | 15.2307 | 89.9752 | 104.582 | 12.015 | 232.7556 | 167.2928 | 293.148 | 10.4183 | 58.8628 | 15.6254 | 184 | 3.0159 | 152.5738 | 274.7389 | 0
1006 | 892.7192 | 3.6759 | 52.7648 | 105.1122 | 59.8147 | 5.9627 | 66.5479 | 5.9092 | 15.3793 | 84.1979 | 100.3971 | 11.7704 | 203.4008 | 132.4419 | 251.9954 | 10.3888 | 55.0457 | 15.6772 | 176 | 2.9077 | 138.6625 | 265.5518 | 0
1007 | 866.2088 | 3.1852 | 52.4683 | 101.6441 | 59.274 | 6.4763 | 74.8259 | 6.5388 | 9.7599 | 81.1002 | 86.9802 | 11.455 | 189.26 | 121.6468 | 247.6946 | 10.1847 | 53.0622 | 14.9856 | 153 | 2.933 | 128.4519 | 264.7729 | 0
1008 | 839.8872 | 3.3844 | 52.0488 | 99.6322 | 59.9094 | 5.8727 | 72.8222 | 7.2106 | 7.2058 | 74.7918 | 80.9181 | 11.3216 | 182.382 | 110.3833 | 234.0845 | 10.3356 | 53.1474 | 14.3234 | 138 | 3.1244 | 101.1467 | 262.9625 | 0
1009 | 838.4875 | 7.3569 | 51.8306 | 98.8437 | 59.3217 | 6.431 | 67.384 | 7.3276 | 6.9563 | 57.2192 | 80.2553 | 11.5237 | 176.0092 | 102.5859 | 228.8043 | 10.25 | 52.9874 | 13.5946 | 133 | 3.2041 | 89.309 | 258.2282 | 0
1010 | 831.6927 | 6.2694 | 52.002 | 98.5364 | 57.5081 | 8.1539 | 67.0421 | 6.8344 | 6.4807 | 52.5618 | 80.1955 | 11.4031 | 174.1895 | 99.7697 | 226.6236 | 10.3501 | 53.0887 | 12.8064 | 129 | 3.2995 | 86.1931 | 258.6754 | 0
1011 | 830.9257 | 2.7268 | 51.8268 | 100.9396 | 59.4852 | 6.2757 | 75.4867 | 6.5211 | 6.398 | 51.8497 | 80.6408 | 11.3766 | 165.1108 | 96.97 | 233.3391 | 10.3089 | 52.9385 | 12.6084 | 146 | 3.3886 | 85.7937 | 258.9709 | 0
1012 | 822.5806 | 1.4929 | 51.9698 | 99.5566 | 59.2533 | 6.496 | 70.6717 | 6.8874 | 6.5547 | 52.4125 | 81.4331 | 11.3665 | 163.5426 | 101.0116 | 239.6657 | 10.3243 | 53.1201 | 12.6156 | 116 | 3.4431 | 84.5301 | 263.0731 | 0
1013 | 820.7132 | 1.7487 | 51.9596 | 98.8753 | 59.9186 | 5.8639 | 66.4649 | 8.8908 | 6.327 | 59.5669 | 82.5172 | 11.2389 | 166.8805 | 110.7987 | 232.0983 | 10.3337 | 54.5929 | 12.5976 | 112 | 3.368 | 81.0597 | 287.6315 | 0
1014 | 826.7352 | 2.9192 | 52.3923 | 101.5352 | 59.2693 | 6.4808 | 66.6259 | 8.0353 | 7.2413 | 72.8194 | 83.0299 | 13.4146 | 171.602 | 118.6134 | 233.1032 | 10.3047 | 57.0027 | 12.6084 | 110 | 3.2876 | 86.0936 | 306.7226 | 0
1015 | 868.5976 | 4.4165 | 54.0027 | 109.8214 | 56.7483 | 8.8758 | 82.7512 | 7.1555 | 8.1567 | 98.6488 | 94.5297 | 24.2768 | 211.3519 | 170.5521 | 276.173 | 13.1882 | 54.8254 | 12.5872 | 178 | 3.4654 | 126.6256 | 351.1164 | 0
1016 | 930.0983 | 5.6253 | 75.5809 | 109.5212 | 49.9139 | 15.3684 | 99.3578 | 10.3527 | 12.0219 | 107.2742 | 135.9169 | 35.046 | 283.3424 | 232.9031 | 405.9287 | 27.3433 | 58.2572 | 13.9185 | 298 | 4.9407 | 170.0626 | 419.3333 | 0
1017 | 1035.6239 | 4.7634 | 99.7118 | 121.9506 | 48.836 | 16.3924 | 109.0242 | 10.4819 | 15.1564 | 104.17 | 170.1795 | 35.2854 | 352.5614 | 289.8796 | 481.3033 | 35.2479 | 66.8035 | 18.8765 | 293 | 7.945 | 200.4969 | 488.1782 | 0.15849
1018 | 1107.2805 | 4.2021 | 104.3999 | 136.5727 | 49.1226 | 16.1202 | 117.4464 | 9.9576 | 18.5633 | 109.316 | 182.7072 | 34.4902 | 395.9926 | 319.4519 | 520.2508 | 39.5463 | 75.2462 | 17.9349 | 346 | 9.8527 | 231.4302 | 528.5182 | 0.20783
1019 | 1144.2882 | 4.1848 | 106.3583 | 144.9369 | 48.4017 | 16.8051 | 122.0604 | 11.702 | 21.8307 | 108.4017 | 187.6301 | 38.8733 | 413.1486 | 343.6123 | 536.6007 | 42.6084 | 82.0757 | 16.6789 | 406 | 10.5125 | 247.5865 | 556.1016 | 0.20973
1020 | 1181.4978 | 3.8972 | 108.8363 | 140.7498 | 49.6362 | 15.6322 | 116.0036 | 10.99 | 21.9404 | 113.5357 | 189.6565 | 40.6703 | 429.5124 | 355.7292 | 544.105 | 41.7133 | 83.9674 | 16.0073 | 355 | 10.5414 | 243.3297 | 565.3372 | 0.22949
1021 | 1168.2502 | 4.1119 | 108.6981 | 134.6699 | 48.5003 | 16.7113 | 118.2694 | 9.8803 | 20.3979 | 111.4777 | 191.9157 | 39.8874 | 421.7999 | 337.9032 | 541.88 | 41.8374 | 80.8021 | 15.6652 | 396 | 8.7933 | 237.0103 | 555.4625 | 0.21964
1022 | 1176.2678 | 4.1098 | 109.6136 | 137.0432 | 44.4447 | 20.5642 | 116.8277 | 9.2371 | 17.9346 | 112.2644 | 193.2897 | 36.5669 | 422.8061 | 334.5899 | 534.5438 | 41.422 | 81.4333 | 16.805 | 323 | 6.9847 | 229.1253 | 555.6075 | 0.22467
1023 | 1191.4653 | 4.2611 | 110.0731 | 132.952 | 46.7341 | 18.3892 | 109.5777 | 8.9914 | 16.3441 | 110.7919 | 193.2869 | 35.2533 | 427.0819 | 330.0661 | 548.6113 | 39.1957 | 82.3383 | 17.0725 | 299 | 7.6664 | 225.2964 | 553.0857 | 0.20962
1024 | 1191.0206 | 3.9439 | 101.5175 | 131.9189 | 48.8296 | 16.3985 | 112.9817 | 9.8564 | 17.7518 | 108.1006 | 191.2184 | 33.553 | 408.8918 | 314.0418 | 552.7623 | 37.7505 | 79.6797 | 16.917 | 293 | 7.7501 | 216.9145 | 529.4489 | 0.094757
1025 | 1131.8166 | 4.7527 | 98.4659 | 132.8832 | 54.5063 | 11.0057 | 105.2893 | 9.4776 | 17.6273 | 96.1952 | 183.7874 | 31.5425 | 382.1717 | 300.1869 | 500.0424 | 25.3984 | 77.3835 | 16.6003 | 285 | 6.279 | 188.4252 | 460.6299 | 0.017039
1026 | 1063.3428 | 5.4093 | 86.9253 | 122.9343 | 57.6576 | 8.0119 | 91.1554 | 7.5759 | 15.7587 | 91.948 | 174.9643 | 31.1569 | 332.222 | 239.5997 | 399.4344 | 16.4858 | 73.3038 | 15.946 | 238 | 5.9404 | 167.252 | 383.9536 | 0
1027 | 1003.3157 | 4.6197 | 69.5828 | 110.8564 | 59.6586 | 6.1109 | 90.8635 | 6.7417 | 14.872 | 86.9498 | 146.0641 | 26.6738 | 287.9163 | 180.8146 | 348.7452 | 12.9534 | 66.0541 | 15.5514 | 245 | 6.015 | 155.2682 | 328.3236 | 0
1028 | 957 | 3.9395 | 64.3309 | 102.8569 | 59.2715 | 6.4787 | 76.9938 | 7.0011 | 10.275 | 70.9772 | 116.4913 | 12.7384 | 250.9375 | 159.4096 | 287.7899 | 13.203 | 57.6189 | 15.1108 | 214 | 6.0578 | 139.6123 | 304.477 | 0
1029 | 899.6636 | 3.841 | 63.5923 | 101.3525 | 59.8968 | 5.8847 | 76.683 | 8.5691 | 7.4872 | 67.715 | 98.5959 | 7.8657 | 227.53 | 152.5503 | 242.0428 | 11.0844 | 53.2406 | 14.1208 | 183 | 5.5797 | 134.1872 | 285.6384 | 0
1030 | 867.6382 | 3.9948 | 63.314 | 100.0134 | 59.2976 | 6.4539 | 79.472 | 8.373 | 6.9904 | 66.4628 | 90.4345 | 7.6956 | 206.2065 | 142.8858 | 230.7048 | 9.8945 | 51.061 | 12.4908 | 171 | 5.4682 | 129.4151 | 265.3998 | 0
1031 | 843.8497 | 3.244 | 62.9742 | 98.7053 | 59.8674 | 5.9126 | 77.4928 | 7.4297 | 6.6933 | 62.3999 | 86.717 | 7.865 | 189.2052 | 133.4018 | 240.4899 | 9.7863 | 50.3957 | 12.4057 | 161 | 5.5138 | 120.7874 | 258.7099 | 0
1032 | 840.1595 | 2.2755 | 62.7225 | 99.7495 | 59.3172 | 6.4353 | 70.281 | 9.1445 | 6.534 | 61.0775 | 84.8482 | 7.7693 | 186.3518 | 124.2692 | 246.6836 | 9.7888 | 51.3969 | 12.9196 | 146 | 5.6561 | 92.9979 | 258.4967 | 0
1033 | 833.2126 | 1.6994 | 63.1196 | 100.4253 | 59.883 | 5.8978 | 67.5705 | 8.3851 | 6.8033 | 60.0468 | 84.9912 | 7.7218 | 188.1041 | 115.0418 | 256.1607 | 9.7422 | 51.402 | 12.9903 | 143 | 5.6573 | 82.5863 | 255.9609 | 0
1034 | 832.6799 | 1.7059 | 63.3346 | 99.3224 | 59.2802 | 6.4704 | 67.6712 | 7.1523 | 7.0108 | 59.7382 | 84.8796 | 8.3426 | 188.0123 | 107.229 | 252.7474 | 9.8468 | 51.0005 | 12.7733 | 137 | 5.7799 | 80.2443 | 257.2724 | 0
1035 | 815.4317 | 1.6011 | 63.3499 | 100.0384 | 57.5857 | 8.0802 | 73.6233 | 8.8478 | 6.9774 | 57.9566 | 83.6104 | 8.1593 | 183.3908 | 100.0682 | 247.381 | 9.7926 | 50.8099 | 12.2924 | 147 | 5.9275 | 78.3263 | 255.4714 | 0
1036 | 825.616 | 1.5532 | 63.1567 | 100.0894 | 59.4489 | 6.3102 | 69.7871 | 8.5243 | 6.7238 | 57.3415 | 83.4661 | 8.0177 | 179.722 | 93.7172 | 246.9902 | 9.8619 | 50.7913 | 11.8556 | 136 | 5.7085 | 79.5112 | 253.2322 | 0
1037 | 816.863 | 1.8583 | 62.803 | 99.51 | 59.2776 | 6.4729 | 67.1845 | 7.1235 | 6.4787 | 60.1129 | 83.3772 | 7.8061 | 170.3544 | 93.354 | 236.1103 | 9.7272 | 52.3914 | 11.7883 | 118 | 5.6636 | 79.2053 | 250.0905 | 0
1038 | 812.5989 | 2.8356 | 62.9984 | 99.0912 | 59.8408 | 5.9379 | 67.507 | 7.2923 | 6.31 | 73.0106 | 83.498 | 7.7165 | 158.4593 | 108.523 | 231.5853 | 9.8065 | 54.4467 | 11.6604 | 126 | 5.5983 | 80.4031 | 249.6294 | 0
1039 | 826.6337 | 3.2326 | 67.4799 | 100.3909 | 59.3421 | 6.4117 | 75.8056 | 8.9229 | 7.6707 | 96.798 | 84.0777 | 7.6808 | 155.9185 | 100.1867 | 235.4291 | 9.7901 | 51.9168 | 11.5917 | 110 | 5.5739 | 81.017 | 256.5015 | 0
1040 | 846.175 | 3.4626 | 78.1466 | 101.3135 | 59.8763 | 5.9041 | 72.9997 | 7.4379 | 9.192 | 100.0299 | 90.0821 | 8.7364 | 166.2787 | 95.7481 | 231.89 | 9.6257 | 49.7147 | 11.7599 | 117 | 5.6676 | 83.8566 | 263.0024 | 0
1041 | 855.6462 | 2.5945 | 82.2882 | 99.9004 | 58.488 | 7.223 | 71.9944 | 6.2474 | 6.458 | 91.5468 | 118.3791 | 11.5591 | 179.5321 | 90.911 | 214.768 | 9.3561 | 49.072 | 12.1749 | 120 | 5.5773 | 90.6075 | 257.1066 | 0.01732
1042 | 881.4074 | 1.8814 | 84.7912 | 99.4995 | 57.3046 | 8.3473 | 68.8086 | 5.7591 | 9.7153 | 88.2693 | 143.4561 | 7.4051 | 204.4369 | 97.9978 | 210.7012 | 9.2131 | 49.595 | 12.3487 | 139 | 5.4206 | 116.1118 | 264.4097 | 0.02682
1043 | 893.2495 | 2.0409 | 86.2141 | 100.3038 | 58.6819 | 7.0388 | 74.6875 | 6.4144 | 10.3933 | 88.8976 | 153.7956 | 5.1472 | 227.7609 | 109.3717 | 219.0148 | 9.2496 | 52.2826 | 12.7185 | 155 | 5.3725 | 127.4626 | 268.0192 | 0.075034
1044 | 904.2479 | 1.8765 | 87.8683 | 101.2442 | 59.844 | 5.9349 | 67.8692 | 6.9692 | 9.5661 | 88.6264 | 145.1858 | 5.0033 | 241.2933 | 114.3036 | 216.7606 | 9.3355 | 51.7529 | 12.8034 | 198 | 5.3645 | 127.5296 | 263.8508 | 0.067178
1045 | 914.425 | 2.1194 | 86.7102 | 101.1489 | 59.3753 | 6.3801 | 63.6797 | 7.655 | 12.1138 | 92.611 | 115.141 | 4.9998 | 246.8322 | 120.2095 | 242.1268 | 9.3645 | 50.1245 | 13.1995 | 211 | 5.3589 | 131.2332 | 260.4059 | 0.066267
1046 | 910.8482 | 2.1284 | 80.6872 | 103.0153 | 59.8315 | 5.9467 | 65.9535 | 8.8952 | 10.2195 | 88.3796 | 104.313 | 5.0038 | 242.2291 | 129.6426 | 235.3936 | 9.2643 | 50.5097 | 13.6146 | 192 | 5.3463 | 130.3985 | 266.0406 | 0.075095
1047 | 900.0045 | 1.8595 | 63.3528 | 103.9712 | 59.3198 | 6.4328 | 73.6163 | 7.8304 | 12.1773 | 81.4952 | 104.2001 | 5.7937 | 236.2304 | 136.964 | 227.8153 | 9.2136 | 50.3608 | 13.8718 | 207 | 5.3858 | 131.5244 | 276.5081 | 0.051877
1048 | 904.0992 | 1.5873 | 58.2881 | 102.3874 | 57.5879 | 8.0781 | 69.1225 | 6.401 | 13.2013 | 64.8247 | 104.4164 | 8.793 | 229.9542 | 126.3696 | 224.2311 | 9.1691 | 50.698 | 13.5688 | 213 | 5.3462 | 130.2295 | 267.8939 | 0.03253
1049 | 899.8395 | 2.4329 | 57.9956 | 99.5981 | 57.0533 | 8.586 | 64.9383 | 6.1082 | 13.158 | 44.1544 | 104.1093 | 8.7493 | 229.1493 | 116.0123 | 230.9712 | 9.2616 | 51.3353 | 13.2958 | 203 | 5.3203 | 104.9048 | 252.9125 | 0.0038491
1050 | 899.1915 | 4.0308 | 58.4941 | 102.908 | 57.873 | 7.8073 | 69.3539 | 7.2249 | 13.7293 | 41.8165 | 103.8484 | 7.3417 | 232.9418 | 121.1399 | 246.2179 | 9.5042 | 53.2301 | 13.876 | 228 | 5.4902 | 100.4019 | 251.0781 | 0
1051 | 890.8172 | 4.0842 | 58.7457 | 104.0325 | 58.8726 | 6.8577 | 72.7311 | 8.7571 | 12.5613 | 43.5202 | 95.796 | 7.6836 | 229.7075 | 119.4333 | 277.8512 | 9.7424 | 52.5711 | 14.2161 | 210 | 5.6236 | 100.7982 | 250.3273 | 0
1052 | 874.4733 | 3.7937 | 60.3934 | 103.6313 | 59.1126 | 6.6296 | 68.1628 | 7.8275 | 7.88 | 42.9473 | 90.8801 | 8.4582 | 217.971 | 119.3731 | 270.5135 | 9.6842 | 51.8279 | 14.7466 | 194 | 5.6705 | 94.7387 | 250.7781 | 0
1053 | 861.101 | 3.7269 | 60.7321 | 101.5583 | 59.883 | 5.8978 | 65.9578 | 7.2714 | 6.6313 | 42.4429 | 90.7195 | 8.3037 | 202.4074 | 112.6188 | 249.8405 | 9.7383 | 52.1539 | 14.7033 | 202 | 5.6724 | 90.7813 | 259.0497 | 0
1054 | 852.1323 | 3.901 | 60.7936 | 102.3609 | 59.2778 | 6.4727 | 69.1815 | 9.4734 | 6.9573 | 42.1358 | 88.8857 | 8.4328 | 189.6528 | 107.4202 | 237.2906 | 9.7791 | 51.547 | 13.7379 | 180 | 5.8297 | 88.6736 | 282.6348 | 0
1055 | 835.4928 | 3.519 | 60.3966 | 103.7118 | 59.1003 | 6.6413 | 70.6011 | 8.5823 | 6.996 | 42.3602 | 86.8434 | 8.3596 | 185.1786 | 105.9398 | 249.9084 | 9.7726 | 51.506 | 12.7735 | 162 | 5.9946 | 86.9465 | 275.3743 | 0
1056 | 809.5278 | 2.3741 | 60.0347 | 103.2238 | 59.8676 | 5.9124 | 67.8461 | 9.8429 | 6.738 | 41.3747 | 84.4985 | 8.4091 | 180.7624 | 103.5304 | 254.2113 | 9.7669 | 51.2701 | 12.5722 | 143 | 5.8389 | 88.8023 | 263.5523 | 0
1057 | 823.4348 | 1.7121 | 59.261 | 103.6784 | 58.5438 | 7.17 | 65.948 | 8.4771 | 6.4227 | 39.8538 | 83.8402 | 8.0271 | 180.4331 | 93.8956 | 251.9554 | 9.6269 | 51.0285 | 12.0574 | 137 | 5.7611 | 87.0195 | 262.454 | 0
1058 | 832.2722 | 1.8367 | 58.8876 | 102.8081 | 56.5194 | 9.0932 | 65.5764 | 9.7555 | 6.3107 | 39.5957 | 83.447 | 7.8424 | 175.5656 | 89.8682 | 252.8421 | 9.7277 | 50.7462 | 11.8366 | 152 | 6.0813 | 87.7607 | 269.1734 | 0
1059 | 816.5498 | 1.7241 | 59.1485 | 103.4774 | 55.2958 | 10.2556 | 70.3869 | 8.9411 | 6.2413 | 39.2008 | 83.2297 | 8.1449 | 162.8594 | 103.2914 | 258.4626 | 9.6908 | 50.9909 | 12.5024 | 161 | 6.068 | 86.8041 | 267.5732 | 0
1060 | 798.9447 | 1.6862 | 59.4474 | 102.8052 | 56.6271 | 8.9909 | 67.8518 | 9.9386 | 6.3447 | 39.713 | 83.7552 | 7.9412 | 156.7604 | 95.1397 | 235.4478 | 9.7408 | 51.0275 | 11.8112 | 141 | 5.7213 | 85.2984 | 260.4237 | 0
1061 | 786.2461 | 1.7591 | 59.304 | 103.0198 | 57.8854 | 7.7955 | 65.6464 | 9.8359 | 6.2213 | 39.8443 | 84.2122 | 7.8151 | 153.5071 | 94.4864 | 229.0437 | 9.7016 | 52.6058 | 11.3638 | 145 | 5.3899 | 84.9047 | 255.7685 | 0
1062 | 784.7995 | 2.9151 | 60.8077 | 102.8381 | 58.9092 | 6.8229 | 66.1459 | 9.149 | 6.0867 | 51.6503 | 84.4428 | 7.8345 | 152.7173 | 89.7458 | 250.4035 | 9.6362 | 54.8435 | 11.3496 | 137 | 4.2626 | 84.285 | 255.5159 | 0
1063 | 790.3592 | 3.1523 | 61.6797 | 101.8208 | 59.8277 | 5.9503 | 69.9572 | 9.2449 | 6.06 | 75.496 | 84.5977 | 7.8671 | 152.0387 | 87.7672 | 247.7114 | 9.7044 | 52.3734 | 11.3456 | 134 | 3.9775 | 83.0753 | 256.9493 | 0
1064 | 802.7783 | 2.9024 | 60.3702 | 100.6357 | 59.3458 | 6.4082 | 68.0609 | 8.9648 | 5.6127 | 72.7763 | 82.7026 | 6.8374 | 161.7314 | 86.6078 | 231.7943 | 9.4821 | 49.9192 | 11.5857 | 124 | 3.9956 | 82.4287 | 250.877 | 0
1065 | 810.6299 | 2.0692 | 59.2764 | 99.1532 | 59.8224 | 5.9554 | 64.8203 | 9.8409 | 5.2153 | 68.0375 | 83.8601 | 5.4579 | 166.3727 | 87.0686 | 228.4532 | 9.2511 | 50.129 | 12.2016 | 116 | 3.9236 | 82.4843 | 246.5111 | 0.03577
1066 | 820.8863 | 1.8877 | 58.7027 | 98.319 | 58.606 | 7.111 | 64.3266 | 8.5376 | 5.1593 | 70.9984 | 85.8122 | 4.9686 | 165.38 | 90.3233 | 241.8606 | 9.1794 | 52.855 | 12.4223 | 174 | 3.837 | 83.9648 | 241.667 | 0.09204
1067 | 853.1326 | 1.9348 | 58.2952 | 98.9361 | 59.5948 | 6.1716 | 65.6669 | 6.9138 | 9.3353 | 82.1286 | 95.5092 | 4.9145 | 185.451 | 105.8785 | 243.4109 | 9.0552 | 53.457 | 12.4037 | 180 | 3.9284 | 85.3467 | 242.1044 | 0.14162
1068 | 862.6208 | 2.3389 | 59.0314 | 102.5936 | 59.3117 | 6.4405 | 72.7011 | 7.2456 | 12.3753 | 82.9603 | 102.285 | 4.9695 | 200.4611 | 108.4432 | 243.931 | 8.5963 | 54.1781 | 12.4259 | 162 | 4.0021 | 88.6824 | 242.342 | 0.19177
1069 | 864.3607 | 2.1273 | 59.4898 | 103.3914 | 59.0823 | 6.6584 | 70.453 | 7.5886 | 12.974 | 75.7181 | 100.4848 | 5.3201 | 204.5523 | 111.4806 | 254.4404 | 8.3512 | 53.1897 | 12.5879 | 162 | 3.9768 | 91.8451 | 236.1015 | 0.19454
1070 | 862.8355 | 2.2638 | 58.4959 | 100.6347 | 59.8752 | 5.9052 | 73.9001 | 7.1092 | 13.0267 | 65.1887 | 100.3114 | 5.2466 | 206.7534 | 118.6742 | 252.2134 | 8.2371 | 51.3153 | 12.6917 | 172 | 3.895 | 88.5624 | 237.3967 | 0.2372
1071 | 857.297 | 1.8282 | 58.2307 | 99.6817 | 60.1106 | 5.6816 | 74.6922 | 6.4264 | 13.4287 | 60.6268 | 100.814 | 6.1907 | 210.768 | 125.8213 | 256.138 | 8.3682 | 50.7806 | 12.6836 | 172 | 3.8849 | 84.9892 | 242.9575 | 0.1872
1072 | 860.7112 | 1.6722 | 58.3864 | 100.3583 | 59.3542 | 6.4001 | 74.8025 | 6.0574 | 13.4013 | 62.6119 | 101.511 | 8.2295 | 206.9828 | 122.62 | 220.2951 | 8.6294 | 50.4213 | 13.2854 | 168 | 3.9197 | 85.8426 | 245.9679 | 0.10303
1073 | 867.4492 | 2.3315 | 58.8305 | 102.6999 | 59.8385 | 5.9401 | 67.4117 | 6.3245 | 13.1493 | 63.5071 | 102.4089 | 6.3091 | 210.667 | 120.6017 | 220.7407 | 9.083 | 50.3067 | 13.6084 | 179 | 3.8548 | 88.9592 | 247.1473 | 0.023668
1074 | 871.5029 | 3.8869 | 60.1592 | 112.1642 | 59.2738 | 6.4765 | 65.4539 | 8.9185 | 12.0167 | 67.8725 | 103.8231 | 7.5709 | 227.1801 | 121.6184 | 243.8766 | 9.4191 | 51.105 | 13.9423 | 161 | 3.9328 | 94.9922 | 253.8287 | 0
1075 | 866.7125 | 3.6872 | 60.6009 | 108.9631 | 58.3544 | 7.35 | 69.0363 | 8.0352 | 12.0993 | 67.3092 | 108.2554 | 8.5827 | 229.6455 | 122.4478 | 267.0357 | 9.733 | 51.037 | 14.0796 | 134 | 4.0551 | 100.5698 | 259.5295 | 0
1076 | 852.3553 | 3.3692 | 60.3026 | 103.9152 | 58.0758 | 7.6146 | 73.1345 | 7.2567 | 9.3147 | 49.5333 | 107.2245 | 8.5587 | 213.8297 | 117.711 | 247.6569 | 9.7839 | 52.0519 | 14.2248 | 133 | 4.1219 | 99.9285 | 269.0457 | 0
1077 | 824.8484 | 4.1149 | 60.2547 | 102.6947 | 59.6432 | 6.1256 | 69.8001 | 9.8646 | 8.4307 | 41.8674 | 95.3913 | 8.5405 | 200.0362 | 113.6451 | 235.7653 | 9.6766 | 51.5266 | 13.854 | 117 | 4.1917 | 96.05 | 268.832 | 0
1078 | 806.2302 | 3.9785 | 59.3469 | 102.463 | 59.323 | 6.4298 | 66.6297 | 8.4771 | 8.3387 | 41.0622 | 88.0112 | 8.4281 | 192.8359 | 106.2452 | 224.7625 | 9.7354 | 50.3179 | 12.8314 | 113 | 4.1108 | 90.3895 | 258.6162 | 0
1079 | 791.8618 | 3.2526 | 59.0375 | 100.953 | 59.0804 | 6.6602 | 66.2047 | 9.6709 | 8.2287 | 40.4489 | 86.0434 | 8.3738 | 183.459 | 100.6019 | 232.5901 | 9.6658 | 49.6587 | 12.0154 | 118 | 4.0024 | 83.4622 | 258.0839 | 0
1080 | 784.9921 | 1.9976 | 59.0825 | 101.4087 | 59.8484 | 5.9306 | 70.5275 | 8.5918 | 7.7627 | 40.3541 | 84.9635 | 8.4362 | 176.2948 | 98.6367 | 240.3881 | 9.7589 | 49.3582 | 11.7232 | 114 | 4.0901 | 82.2246 | 258.9931 | 0
1081 | 778.5846 | 1.5596 | 58.8111 | 101.7887 | 59.3282 | 6.4248 | 67.9587 | 9.7675 | 6.764 | 39.3888 | 82.8368 | 8.4224 | 165.7863 | 99.2257 | 256.1755 | 9.6797 | 49.7002 | 11.6867 | 106 | 4.1006 | 83.2423 | 261.6298 | 0
1082 | 775.5387 | 1.3905 | 58.632 | 102.1205 | 59.0776 | 6.6629 | 66.1202 | 11.1544 | 6.5407 | 39.5617 | 83.2922 | 8.4395 | 159.9834 | 96.8487 | 260.1289 | 9.6547 | 50.7181 | 11.7069 | 103 | 4.0858 | 84.9729 | 260.8748 | 0
1083 | 763.7351 | 1.3722 | 58.6448 | 101.0442 | 59.8857 | 5.8952 | 66.2255 | 9.0619 | 6.3573 | 39.8969 | 83.4093 | 8.8094 | 158.0607 | 98.9847 | 245.1606 | 9.6898 | 50.3496 | 11.7459 | 117 | 4.1763 | 86.8884 | 266.9517 | 0
1084 | 758.5447 | 1.2766 | 58.8873 | 100.9994 | 59.3267 | 6.4262 | 70.8495 | 10.0382 | 6.368 | 42.5193 | 83.3323 | 8.943 | 154.7461 | 108.4839 | 227.4416 | 9.7732 | 50.0447 | 11.7359 | 98 | 4.125 | 88.1539 | 270.8955 | 0
1085 | 768.8282 | 1.886 | 59.625 | 102.7422 | 59.0638 | 6.6761 | 70.5379 | 11.2133 | 6.3267 | 52.8757 | 83.279 | 8.9337 | 152.1713 | 115.537 | 224.832 | 9.7119 | 51.4351 | 11.7543 | 100 | 4.0672 | 86.4757 | 295.6465 | 0
1086 | 778.8403 | 3.0839 | 60.1957 | 102.4238 | 59.0875 | 6.6535 | 68.1974 | 11.4094 | 6.366 | 67.6806 | 83.9931 | 10.0279 | 162.2495 | 116.209 | 238.4779 | 9.7487 | 54.1302 | 11.759 | 103 | 4.0578 | 91.4641 | 315.9294 | 0
1087 | 819.5336 | 4.1098 | 75.7033 | 110.2044 | 56.7891 | 8.8369 | 77.1455 | 11.4915 | 10.4967 | 97.1217 | 108.8732 | 20.7811 | 213.0853 | 176.8655 | 273.6269 | 12.4318 | 51.9352 | 14.4786 | 157 | 4.2912 | 142.5139 | 364.8988 | 0
1088 | 908.0902 | 5.7124 | 87.1734 | 113.6958 | 52.1898 | 13.2063 | 100.3097 | 9.7766 | 17.3507 | 108.7069 | 143.2886 | 36.3396 | 280.5954 | 236.1933 | 332.7895 | 25.251 | 56.8928 | 14.4671 | 255 | 5.0002 | 180.919 | 429.6586 | 0
1089 | 992.9438 | 7.1009 | 100.0657 | 119.9541 | 50.2503 | 15.0489 | 118.066 | 11.7564 | 17.628 | 105.8637 | 166.3776 | 43.2659 | 358.9178 | 291.6149 | 433.7129 | 32.9077 | 68.0282 | 18.5933 | 283 | 5.1995 | 208.01 | 479.4984 | 0.051793
1090 | 1060.9889 | 7.5082 | 104.0703 | 129.8427 | 48.5167 | 16.6957 | 117.1469 | 10.625 | 18.67 | 107.5105 | 181.2745 | 42.2736 | 406.797 | 332.9946 | 543.3242 | 33.3138 | 76.9917 | 20.0182 | 319 | 4.852 | 236.2132 | 528.2996 | 0.073334
1091 | 1119.6402 | 7.3618 | 105.4971 | 138.3017 | 47.2942 | 17.8572 | 114.3016 | 10.2087 | 21.8147 | 108.0145 | 194.7329 | 42.357 | 421.4444 | 342.5606 | 573.7793 | 32.3816 | 81.7455 | 18.2975 | 343 | 5.7416 | 251.1274 | 559.0045 | 0.16712
1092 | 1159.1926 | 7.293 | 107.5776 | 138.2158 | 49.5211 | 15.7416 | 123.023 | 12.713 | 21.4493 | 116.4618 | 197.1078 | 43.4033 | 438.1809 | 361.135 | 574.4634 | 32.1805 | 83.7349 | 17.4784 | 301 | 6.8087 | 256.1396 | 560.2265 | 0.23246
1093 | 1143.4409 | 6.1637 | 109.7643 | 134.9097 | 50.109 | 15.183 | 119.6289 | 11.596 | 19.3667 | 112.2822 | 189.8339 | 43.9537 | 436.4277 | 357.7353 | 587.9673 | 33.3344 | 81.0107 | 17.6307 | 340 | 6.6278 | 242.8101 | 559.2795 | 0.27034
1094 | 1157.8524 | 4.4588 | 108.4943 | 135.5366 | 48.4976 | 16.7139 | 115.0712 | 10.5802 | 24.1407 | 116.9979 | 191.2648 | 44.4729 | 431.076 | 366.9758 | 617.7984 | 33.0824 | 81.1503 | 18.9611 | 341 | 7.4216 | 244.9768 | 573.2024 | 0.27334
1095 | 1178.0002 | 3.3891 | 105.5606 | 138.6834 | 48.9032 | 16.3286 | 122.3766 | 10.3741 | 25.1 | 119.7537 | 196.9261 | 44.1001 | 449.3281 | 370.7523 | 625.0966 | 31.6977 | 81.2019 | 19.2122 | 356 | 7.215 | 246.1552 | 581.2667 | 0.24212
1096 | 1170.0378 | 3.6191 | 104.0415 | 141.6592 | 49.1075 | 16.1345 | 117.2859 | 11.6001 | 22.8187 | 115.3931 | 192.7684 | 41.4196 | 447.1855 | 349.2092 | 594.028 | 32.0685 | 78.3706 | 19.4409 | 278 | 6.095 | 232.9861 | 562.1672 | 0.15651
1097 | 1156.4807 | 4.4519 | 102.3699 | 137.265 | 52.1266 | 13.2664 | 112.7238 | 11.3248 | 21.6507 | 108.6677 | 185.8115 | 38.7913 | 408.0887 | 308.1988 | 519.6472 | 27.7751 | 76.5275 | 18.63 | 239 | 5.363 | 209.8925 | 485.2203 | 0.034422
1098 | 1072.8055 | 5.5727 | 95.8462 | 126.8945 | 54.724 | 10.7988 | 97.2749 | 9.4643 | 18.7887 | 90.6454 | 176.3709 | 37.8223 | 371.667 | 243.1492 | 407.3553 | 15.5882 | 72.989 | 18.1921 | 219 | 5.1428 | 186.8446 | 406.5106 | 0
1099 | 1012.7745 | 5.5252 | 91.983 | 117.5794 | 58.1816 | 7.5141 | 81.6453 | 8.694 | 15.1187 | 69.7452 | 146.7372 | 32.3948 | 314.1703 | 184.9297 | 352.3199 | 11.1919 | 67.6035 | 16.8316 | 199 | 5.1531 | 170.4787 | 352.8527 | 0
1100 | 962.2986 | 4.7233 | 81.2976 | 112.5121 | 59.0907 | 6.6505 | 69.1228 | 9.9919 | 9.8573 | 53.5234 | 118.4606 | 14.9448 | 267.4659 | 144.8409 | 338.4036 | 11.0043 | 61.044 | 15.686 | 188 | 5.1391 | 159.0511 | 303.331 | 0
1101 | 928.3329 | 4.6162 | 62.6097 | 107.6615 | 59.1303 | 6.6128 | 68.9778 | 8.4319 | 7.7573 | 43.8145 | 110.5828 | 9.1179 | 238.285 | 125.8244 | 302.4921 | 11.1447 | 54.1032 | 14.6886 | 181 | 5.2145 | 148.3842 | 282.5087 | 0
1102 | 894.6342 | 4.1124 | 57.1418 | 104.6926 | 59.0784 | 6.6622 | 65.3393 | 7.9407 | 7.1517 | 40.1796 | 104.8103 | 8.3478 | 207.018 | 113.8884 | 266.2983 | 11.1901 | 51.0748 | 13.7483 | 167 | 5.2622 | 139.4567 | 279.6198 | 0
1103 | 857.878 | 3.4598 | 56.9382 | 102.2895 | 59.1095 | 6.6326 | 62.6171 | 9.3736 | 6.8017 | 36.7257 | 92.7324 | 8.0989 | 211.3931 | 106.786 | 258.5396 | 11.1004 | 50.6936 | 14.7803 | 140 | 5.3148 | 127.8428 | 281.9005 | 0
1104 | 846.5202 | 2.0143 | 57.4126 | 101.5339 | 59.8395 | 5.9391 | 62.7006 | 8.6364 | 6.8085 | 36.5596 | 86.6002 | 8.326 | 210.5664 | 106.6942 | 254.9523 | 11.1487 | 51.1104 | 14.5951 | 114 | 5.382 | 102.6062 | 280.736 | 0
1105 | 851.5536 | 1.4351 | 57.2 | 102.4038 | 58.4701 | 7.24 | 67.3183 | 9.8182 | 6.2538 | 36.4689 | 85.2001 | 7.7608 | 194.1027 | 101.4209 | 255.8905 | 11.0865 | 51.7153 | 13.93 | 115 | 5.4011 | 94.0208 | 281.9468 | 0
1106 | 838.6243 | 2.0324 | 56.5958 | 102.5531 | 59.7244 | 6.0484 | 64.2326 | 10.4349 | 5.9585 | 37.195 | 87.5407 | 7.5494 | 178.9657 | 93.8828 | 233.2784 | 11.1358 | 51.2607 | 13.2964 | 108 | 5.4191 | 92.5752 | 282.4409 | 0
1107 | 822.0427 | 1.9431 | 56.4732 | 100.9674 | 59.2684 | 6.4817 | 62.3782 | 9.2037 | 6.0183 | 37.3222 | 91.1123 | 7.5957 | 172.2361 | 93.4394 | 226.5464 | 11.0661 | 50.6891 | 12.553 | 123 | 5.4326 | 91.4725 | 283.1541 | 0
1108 | 816.9268 | 1.4758 | 56.5883 | 100.3867 | 59.0739 | 6.6664 | 63.3087 | 10.498 | 6.072 | 40.1737 | 93.0117 | 7.5754 | 191.6179 | 93.1714 | 245.6215 | 11.1757 | 50.6455 | 12.3455 | 100 | 5.4429 | 90.5877 | 287.0645 | 0
1109 | 821.0989 | 1.7066 | 57.0142 | 100.5818 | 59.0762 | 6.6643 | 62.8971 | 11.4388 | 6.234 | 51.2098 | 91.6595 | 7.5293 | 199.1244 | 92.2267 | 245.2502 | 11.1181 | 52.1671 | 12.3491 | 98 | 5.5545 | 90.9664 | 305.4937 | 0
1110 | 825.7613 | 3.1409 | 57.5747 | 101.2616 | 59.1258 | 6.6171 | 66.2684 | 11.5087 | 6.268 | 57.2711 | 86.8757 | 8.8465 | 214.1613 | 105.7287 | 236.7131 | 11.0525 | 54.55 | 12.3096 | 114 | 5.2582 | 96.1024 | 325.0214 | 0
1111 | 869.4342 | 4.7892 | 66.9885 | 107.857 | 56.7535 | 8.8708 | 73.9976 | 11.5785 | 7.866 | 75.734 | 102.0527 | 19.7145 | 219.8168 | 173.4126 | 273.6886 | 14.2021 | 53.0411 | 12.3547 | 184 | 5.5574 | 137.0228 | 374.8048 | 0
1112 | 937.0001 | 5.989 | 88.1072 | 111.2456 | 52.2472 | 13.1518 | 96.7919 | 9.8576 | 14.434 | 99.9908 | 141.2637 | 36.8088 | 271.7835 | 236.2865 | 372.1744 | 27.52 | 54.7486 | 13.0133 | 249 | 6.9984 | 179.0819 | 434.9405 | 0
1113 | 1038.9506 | 4.8454 | 100.6032 | 118.6073 | 50.4525 | 14.8567 | 116.7807 | 11.8281 | 19.844 | 93.505 | 170.9603 | 42.7953 | 332.6417 | 289.0933 | 476.2655 | 33.3382 | 65.9757 | 16.0411 | 278 | 6.3024 | 207.5966 | 503.2503 | 0.18798
1114 | 1132.4712 | 4.1193 | 109.3457 | 134.1791 | 49.0644 | 16.1754 | 124.5947 | 10.8877 | 20.5873 | 92.7635 | 181.6 | 40.3529 | 398.3036 | 322.1551 | 536.5343 | 33.4348 | 75.2598 | 19.1853 | 350 | 6.3664 | 234.2231 | 556.898 | 0.23349
1115 | 1136.9543 | 4.152 | 113.3881 | 145.4256 | 48.4189 | 16.7887 | 125.5854 | 10.119 | 20.122 | 102.3427 | 189.1584 | 41.2027 | 399.5039 | 341.243 | 582.7901 | 33.6219 | 82.2245 | 18.5937 | 348 | 6.8446 | 249.7491 | 572.7243 | 0.24259
1116 | 1102.0804 | 4.0779 | 114.8826 | 142.7972 | 48.8622 | 16.3675 | 126.1672 | 10.3673 | 20.142 | 111.6241 | 193.3958 | 40.922 | 439.559 | 356.2789 | 601.0178 | 33.5703 | 84.7221 | 17.9978 | 318 | 6.4367 | 257.5347 | 577.6932 | 0.24914
1117 | 1101.7404 | 4.2037 | 116.0336 | 141.8215 | 49.1108 | 16.1313 | 130.0516 | 10.1036 | 21.3267 | 110.3045 | 192.7561 | 40.2549 | 444.0648 | 356.7934 | 575.7404 | 33.5903 | 84.358 | 18.1558 | 361 | 6.7312 | 254.274 | 569.0145 | 0.29285
1118 | 1145.7418 | 4.1096 | 113.2425 | 143.3882 | 50.6274 | 14.6906 | 125.2204 | 9.7836 | 23.4487 | 115.8245 | 198.0115 | 41.7039 | 448.0905 | 355.9418 | 580.6716 | 34.4102 | 84.6164 | 19.2219 | 296 | 6.8891 | 245.7089 | 573.6402 | 0.28469
1119 | 1172.4093 | 4.0092 | 113.1818 | 142.6872 | 50.3601 | 14.9445 | 124.1149 | 9.3395 | 22.684 | 114.4227 | 205.305 | 39.2379 | 458.1875 | 353.4102 | 602.2831 | 33.5201 | 83.2792 | 19.7339 | 291 | 7.3557 | 249.1331 | 544.4408 | 0.24895
1120 | 1154.7628 | 3.9905 | 115.6701 | 147.6044 | 47.7907 | 17.3855 | 131.7072 | 8.7762 | 20.024 | 113.6963 | 201.4195 | 39.4615 | 432.3127 | 336.5297 | 615.3833 | 32.2288 | 81.9037 | 19.7134 | 290 | 7.1195 | 239.6299 | 522.4809 | 0.16196
1121 | 1131.4251 | 4.6746 | 108.9988 | 141.5756 | 54.0037 | 11.4832 | 119.759 | 8.7681 | 18.338 | 108.7649 | 199.8947 | 38.3725 | 404.04 | 311.5476 | 558.9939 | 27.5182 | 79.9213 | 18.8871 | 238 | 6.3695 | 226.6207 | 460.5793 | 0.040312
1122 | 1075.8627 | 5.9068 | 102.5501 | 127.6885 | 56.8904 | 8.7408 | 108.0467 | 7.985 | 18.142 | 90.2903 | 180.7691 | 37.432 | 347.2561 | 253.8673 | 471.8593 | 16.8768 | 79.2427 | 18.0399 | 237 | 5.7118 | 206.6019 | 385.1709 | 0
1123 | 1015.4107 | 5.4584 | 99.151 | 116.3149 | 57.8258 | 7.8521 | 95.371 | 7.03 | 16.6207 | 68.1721 | 144.2404 | 30.901 | 292.7412 | 216.2597 | 413.7801 | 12.3298 | 72.7982 | 17.5095 | 223 | 5.4815 | 197.3465 | 337.7307 | 0
1124 | 965.1547 | 4.3359 | 88.3013 | 111.3719 | 58.899 | 6.8326 | 84.041 | 6.9049 | 11.0413 | 52.3677 | 119.6892 | 14.0427 | 252.2348 | 192.5424 | 353.4059 | 10.3415 | 66.0702 | 16.4283 | 186 | 5.4816 | 183.968 | 293.5182 | 0
1125 | 923.6414 | 3.9041 | 64.5703 | 109.5667 | 59.096 | 6.6454 | 81.5331 | 6.8627 | 8.714 | 50.0935 | 110.9647 | 12.4448 | 229.1268 | 165.2027 | 311.2075 | 9.5593 | 58.9422 | 15.4289 | 178 | 5.5197 | 162.8923 | 277.8601 | 0
1126 | 898.2551 | 4.0038 | 58.6069 | 108.4468 | 59.8345 | 5.9439 | 79.8917 | 7.4186 | 7.5327 | 47.1848 | 105.5408 | 19.5308 | 196.5618 | 144.8165 | 267.6548 | 9.4786 | 54.6943 | 15.4684 | 161 | 5.6246 | 148.9124 | 267.545 | 0
1127 | 866.9408 | 3.2785 | 58.6634 | 104.7424 | 59.2973 | 6.4542 | 75.6494 | 7.8735 | 6.7227 | 40.8809 | 92.0729 | 16.1614 | 180.3632 | 135.6316 | 247.962 | 9.449 | 53.8974 | 16.1866 | 141 | 5.4874 | 132.322 | 263.8324 | 0
1128 | 854.796 | 2.0129 | 58.2839 | 101.0708 | 59.9255 | 5.8574 | 69.7425 | 7.7488 | 6.4133 | 39.4898 | 84.9422 | 9.6684 | 167.1244 | 135.1269 | 234.4396 | 9.5141 | 53.475 | 15.0164 | 116 | 5.4128 | 103.0431 | 260.9108 | 0
1129 | 843.7401 | 1.8548 | 57.8454 | 100.1076 | 60.0536 | 5.7357 | 68.017 | 6.9492 | 6.2207 | 38.7067 | 82.2333 | 7.9924 | 160.0483 | 126.9377 | 235.3717 | 9.4457 | 53.0332 | 14.4248 | 112 | 5.4621 | 93.0024 | 259.0597 | 0
1130 | 833.3425 | 1.7445 | 53.2328 | 100.6633 | 59.3842 | 6.3717 | 76.0158 | 6.589 | 6.39 | 39.5713 | 81.0725 | 8.0098 | 163.0125 | 120.8559 | 244.1695 | 9.4515 | 52.1925 | 14.1097 | 107 | 5.4694 | 91.3666 | 254.8922 | 0
1131 | 830.0942 | 1.6231 | 51.5115 | 100.049 | 59.8178 | 5.9598 | 74.6359 | 6.8261 | 6.2573 | 40.1571 | 81.4886 | 7.9989 | 162.0761 | 118.7381 | 244.463 | 9.4526 | 52.0734 | 13.215 | 125 | 5.5025 | 90.2956 | 255.3325 | 0
1132 | 824.1532 | 1.6004 | 51.5089 | 100.8797 | 59.2885 | 6.4625 | 69.5672 | 6.7634 | 6.4733 | 42.8261 | 82.137 | 7.7916 | 168.3073 | 117.1529 | 238.5944 | 9.4275 | 51.8774 | 12.7655 | 104 | 5.4469 | 89.8553 | 257.115 | 0
1133 | 824.4357 | 2.1098 | 51.7283 | 101.8388 | 59.8838 | 5.897 | 68.2082 | 6.9837 | 6.338 | 51.9158 | 82.2652 | 7.7214 | 166.8889 | 116.0661 | 240.9852 | 9.4337 | 53.3316 | 12.743 | 102 | 5.5011 | 89.8732 | 271.7933 | 0
1134 | 844.4662 | 3.0642 | 52.917 | 103.8092 | 58.5266 | 7.1864 | 77.6542 | 7.7019 | 6.272 | 58.6361 | 82.2899 | 9.0903 | 173.1848 | 119.6911 | 240.4065 | 9.4167 | 55.7131 | 12.7402 | 108 | 5.3719 | 96.6813 | 298.439 | 0
1135 | 883.8183 | 4.0821 | 60.5048 | 111.2663 | 56.5255 | 9.0874 | 83.5584 | 7.574 | 12.022 | 77.2954 | 97.2351 | 19.8096 | 216.0507 | 175.5697 | 258.8255 | 12.5937 | 53.6828 | 12.7371 | 165 | 5.7478 | 140.6378 | 339.767 | 0
1136 | 948.0162 | 5.2881 | 85.1704 | 114.5357 | 52.218 | 13.1795 | 100.0481 | 8.0608 | 17.9527 | 98.4923 | 134.5386 | 34.2487 | 287.8941 | 234.9583 | 338.7798 | 26.4574 | 60.3029 | 13.8413 | 271 | 6.1247 | 190.0772 | 410.3131 | 0
1137 | 1027.8634 | 4.5534 | 107.8392 | 122.695 | 51.0676 | 14.2724 | 115.8254 | 8.9467 | 19.196 | 109.3831 | 168.3228 | 39.6099 | 347.9754 | 276.8429 | 472.1436 | 34.1476 | 80.3659 | 16.0802 | 291 | 7.1626 | 213.4822 | 474.4934 | 0.031
1138 | 1113.4182 | 3.871 | 112.9053 | 135.7252 | 49.543 | 15.7207 | 128.5896 | 9.9127 | 18.4067 | 120.7225 | 183.3317 | 40.6973 | 393.1521 | 309.9404 | 549.3455 | 34.5112 | 93.9191 | 16.507 | 356 | 7.6845 | 237.2433 | 510.1757 | 0.050997
1139 | 1178.4145 | 3.3846 | 114.2802 | 142.7429 | 46.862 | 18.2677 | 126.2335 | 9.8841 | 18.976 | 122.362 | 188.4108 | 41.6671 | 414.8066 | 339.4403 | 576.35 | 34.4002 | 99.4422 | 18.0525 | 354 | 6.9157 | 249.2341 | 513.9775 | 0.087943
1140 | 1190.4233 | 3.748 | 115.9647 | 147.8114 | 48.3388 | 16.8648 | 126.2614 | 9.2612 | 19.2433 | 116.3491 | 188.7556 | 42.9015 | 436.5858 | 350.3917 | 585.3767 | 36.2943 | 101.8758 | 18.7498 | 313 | 6.6857 | 251.3975 | 527.4732 | 0.10129
1141 | 1195.8016 | 3.9211 | 117.2739 | 149.6588 | 49.1696 | 16.0755 | 129.0969 | 9.5227 | 20.0733 | 123.7488 | 191.0596 | 44.7421 | 430.4492 | 357.5776 | 598.8969 | 35.4171 | 101.4139 | 18.9401 | 333 | 6.7751 | 250.8621 | 525.2572 | 0.17231
1142 | 1201.0425 | 4.1635 | 117.9923 | 159.4797 | 49.7753 | 15.5001 | 119.6864 | 9.0953 | 23.0787 | 122.2801 | 193.2979 | 45.2591 | 430.1577 | 376.4341 | 605.365 | 35.1341 | 101.2776 | 19.3402 | 304 | 7.1677 | 241.0991 | 537.7271 | 0.13936
1143 | 1204.4027 | 3.8829 | 119.8294 | 161.3432 | 50.8505 | 14.4786 | 117.7759 | 9.06 | 23.7447 | 121.9551 | 197.3739 | 44.1616 | 430.9968 | 378.2628 | 596.4617 | 36.5698 | 100.8345 | 19.4554 | 280 | 7.5626 | 243.5429 | 542.3029 | 0.16701
1144 | 1187.7655 | 3.8508 | 116.2169 | 148.7901 | 48.7467 | 16.4773 | 124.6327 | 9.3814 | 20.198 | 121.4679 | 199.0916 | 41.1172 | 419.4463 | 357.1656 | 579.4246 | 34.4788 | 101.7667 | 19.8178 | 263 | 7.3462 | 237.0484 | 525.0711 | 0.086643
1145 | 1161.7637 | 4.6537 | 110.9595 | 146.5579 | 48.9444 | 16.2894 | 114.3681 | 9.2527 | 18.0993 | 117.2818 | 192.3285 | 38.1231 | 391.2988 | 327.7049 | 520.7767 | 29.0815 | 99.7145 | 19.4761 | 230 | 6.4884 | 216.4681 | 453.6074 | 0.037785
1146 | 1102.1215 | 5.8077 | 102.7938 | 134.3987 | 49.0548 | 16.1846 | 105.9098 | 9.2567 | 17.9733 | 93.9471 | 180.7521 | 37.0261 | 343.5128 | 263.6524 | 433.2543 | 17.0684 | 94.9889 | 18.5267 | 210 | 6.1627 | 191.3332 | 372.1389 | 0
1147 | 1042.1867 | 5.3133 | 100.3981 | 122.5051 | 56.0475 | 9.5415 | 95.8099 | 9.5552 | 16.2358 | 72.3671 | 152.0236 | 29.6145 | 303.6221 | 196.0801 | 392.3359 | 11.3274 | 77.475 | 17.7829 | 206 | 6.2802 | 177.5591 | 326.3991 | 0
1148 | 973.9727 | 4.297 | 90.4703 | 120.3495 | 58.8855 | 6.8454 | 77.172 | 9.2295 | 10.3277 | 55.9244 | 125.0731 | 13.4739 | 271.007 | 164.632 | 346.2508 | 10.8202 | 64.5861 | 17.1058 | 192 | 6.3744 | 159.1152 | 281.8122 | 0
1149 | 930.2264 | 3.7752 | 74.5218 | 116.0153 | 59.1164 | 6.6261 | 70.853 | 7.9649 | 8.4619 | 51.0367 | 116.2298 | 8.071 | 237.9857 | 140.2421 | 308.2213 | 10.7804 | 56.9171 | 16.5389 | 181 | 6.3814 | 147.7216 | 265.1496 | 0
1150 | 899.166 | 4.0224 | 69.2572 | 111.6024 | 59.8755 | 5.9049 | 77.0187 | 7.0936 | 7.8847 | 47.0653 | 111.5172 | 8.479 | 205.4866 | 115.3075 | 284.2457 | 10.8044 | 53.4505 | 15.7151 | 161 | 6.4406 | 135.7385 | 263.1492 | 0
1151 | 874.958 | 3.3445 | 69.5941 | 107.5545 | 59.2831 | 6.4677 | 73.9841 | 7.0564 | 7.1327 | 43.7339 | 98.5529 | 7.9555 | 183.1111 | 112.9743 | 270.6396 | 10.7499 | 53.2786 | 14.8351 | 141 | 6.5211 | 125.2232 | 265.9529 | 0
1152 | 848.5308 | 2.1308 | 69.3415 | 107.7028 | 59.9073 | 5.8747 | 69.6498 | 6.9214 | 6.6293 | 40.6534 | 89.6378 | 7.4841 | 169.9765 | 116.1143 | 255.7665 | 10.7636 | 53.5755 | 14.2427 | 118 | 6.4578 | 98.3577 | 259.8509 | 0
1153 | 848.4645 | 1.5848 | 68.5244 | 103.6532 | 59.2833 | 6.4675 | 68.7529 | 7.2357 | 6.2487 | 39.3834 | 88.7939 | 7.4243 | 163.191 | 107.0489 | 259.5357 | 10.6958 | 52.7131 | 13.8424 | 116 | 6.4036 | 86.7016 | 256.2969 | 0
1154 | 835.8436 | 1.5759 | 68.125 | 99.4358 | 59.8754 | 5.905 | 75.7516 | 7.945 | 6.084 | 39.2428 | 88.2462 | 7.2271 | 161.3106 | 98.9124 | 258.1332 | 10.7316 | 52.153 | 13.3972 | 107 | 6.3749 | 84.8463 | 259.6748 | 0
1155 | 836.4615 | 1.782 | 66.607 | 98.2148 | 60.0699 | 5.7202 | 73.3437 | 8.1747 | 6.1652 | 38.1182 | 87.5289 | 7.1277 | 160.4895 | 96.2082 | 244.056 | 10.6351 | 51.2405 | 13.4183 | 121 | 6.3536 | 88.6119 | 250.6349 | 0
1156 | 825.4914 | 1.508 | 62.4977 | 99.0813 | 60.115 | 5.6774 | 69.0256 | 7.3164 | 6.1836 | 39.9479 | 87.9915 | 7.1027 | 160.3986 | 95.7177 | 239.1343 | 10.7182 | 51.5759 | 13.3185 | 102 | 6.303 | 87.9266 | 249.3482 | 0
1157 | 833.6709 | 1.6805 | 61.3132 | 100.3793 | 59.3056 | 6.4463 | 68.0196 | 6.7608 | 6.0252 | 50.1884 | 88.122 | 7.0914 | 159.0329 | 94.9319 | 246.5623 | 10.6828 | 53.0177 | 13.0415 | 99 | 6.2968 | 85.8525 | 263.4984 | 0
1158 | 854.3311 | 2.9786 | 63.1658 | 101.2426 | 58.3098 | 7.3923 | 76.6553 | 6.7202 | 6.366 | 57.579 | 91.1555 | 10.0629 | 172.7396 | 106.8734 | 246.2681 | 10.7057 | 55.4965 | 12.6684 | 103 | 6.2298 | 92.4595 | 290.1521 | 0
1159 | 887.2991 | 3.6708 | 71.2287 | 110.2892 | 56.5231 | 9.0897 | 82.0993 | 7.0072 | 7.9987 | 75.9921 | 108.1157 | 20.3642 | 215.093 | 172.232 | 260.6229 | 13.6561 | 53.3972 | 12.9662 | 197 | 6.6181 | 134.1242 | 335.8127 | 0
1160 | 955.7298 | 4.1829 | 87.7468 | 110.4404 | 52.9388 | 12.4948 | 95.4349 | 9.0108 | 13.16 | 103.3745 | 142.3347 | 35.0094 | 282.2318 | 230.3083 | 361.9255 | 25.1769 | 59.5536 | 13.1753 | 277 | 6.8868 | 186.5877 | 407.0396 | 0
1161 | 1042.9604 | 4.3808 | 106.6794 | 117.4372 | 51.3976 | 13.9589 | 108.0818 | 9.5392 | 16.6147 | 104.2133 | 174.3644 | 40.3435 | 340.3692 | 276.8355 | 456.5508 | 30.5785 | 82.4374 | 16.091 | 314 | 6.4728 | 213.628 | 494.4838 | 0.020132
1162 | 1139.6785 | 4.1145 | 112.0526 | 132.4468 | 51.0542 | 14.2851 | 123.6315 | 9.6281 | 20.1347 | 108.2804 | 175.6151 | 41.9905 | 397.9398 | 322.1969 | 536.2027 | 32.9042 | 98.5893 | 15.8735 | 340 | 6.8209 | 233.9407 | 576.0593 | 0.065457
1163 | 1198.005 | 3.9507 | 113.4262 | 142.9688 | 47.956 | 17.2284 | 122.8277 | 9.2842 | 24.7807 | 119.5608 | 174.3755 | 41.6569 | 425.3424 | 351.2784 | 594.1336 | 33.7823 | 105.1781 | 16.3699 | 349 | 7.2701 | 251.6608 | 583.4086 | 0.095599
1164 | 1215.671 | 4.059 | 116.6879 | 143.7679 | 47.9691 | 17.216 | 118.689 | 9.0698 | 24.0147 | 116.5947 | 185.669 | 38.644 | 438.3542 | 364.5875 | 619.4762 | 33.5636 | 105.9534 | 16.7687 | 334 | 7.6642 | 258.4879 | 578.9486 | 0.046053
1165 | 1202.0501 | 4.1365 | 113.7234 | 151.622 | 48.726 | 16.4969 | 125.3864 | 9.7146 | 18.4705 | 107.6232 | 188.5593 | 38.9955 | 434.0212 | 358.0417 | 580.6505 | 34.0614 | 103.0082 | 17.9586 | 389 | 7.7047 | 258.4265 | 575.0434 | 0.040958
1166 | 1200.9963 | 3.8605 | 117.4363 | 159.148 | 49.1151 | 16.1273 | 122.0501 | 10.3609 | 16.9666 | 121.0387 | 189.7638 | 39.6687 | 437.1305 | 358.9514 | 572.5886 | 34.7128 | 104.7909 | 19.4614 | 314 | 7.4248 | 256.7072 | 586.2503 | 0.057036
1167 | 1203.0625 | 3.503 | 120.1616 | 152.7098 | 50.0214 | 15.2663 | 118.5387 | 9.3069 | 18.1856 | 116.1221 | 192.6768 | 36.3304 | 450.9752 | 356.2854 | 578.6749 | 34.849 | 105.989 | 20.1659 | 283 | 7.9155 | 267.093 | 583.2561 | 0.046659
1168 | 1191.1589 | 3.9076 | 115.7055 | 148.3936 | 49.9316 | 15.3516 | 124.1896 | 8.7898 | 18.8536 | 112.8161 | 191.2925 | 34.8675 | 447.3688 | 338.3177 | 573.5192 | 33.8254 | 103.1056 | 20.1671 | 283 | 8.9428 | 242.8668 | 561.991 | 0.025878
1169 | 1140.0732 | 4.895 | 108.3294 | 147.7569 | 50.1089 | 15.1832 | 114.1218 | 9.4407 | 17.3881 | 107.294 | 183.8785 | 33.3643 | 416.7016 | 315.8957 | 512.6485 | 28.2896 | 99.7145 | 20.2079 | 246 | 7.2699 | 213.4803 | 499.259 | 0.0024958
1170 | 1073.0751 | 5.9935 | 101.2032 | 133.3813 | 54.7548 | 10.7696 | 102.3685 | 8.9758 | 17.7655 | 90.3934 | 174.7568 | 34.4162 | 374.526 | 248.8363 | 433.9673 | 16.7427 | 88.5264 | 19.9246 | 219 | 6.2887 | 191.9759 | 423.5227 | 0
1171 | 1011.8968 | 5.0956 | 96.0898 | 119.0687 | 57.6706 | 7.9996 | 95.5091 | 8.1435 | 14.4524 | 75.0864 | 146.6234 | 31.4188 | 323.6777 | 179.0249 | 367.4188 | 12.2235 | 69.5804 | 18.8815 | 212 | 6.4079 | 179.1371 | 372.066 | 0
1172 | 964.0784 | 4.2214 | 87.1071 | 114.1027 | 58.9005 | 6.8312 | 81.0442 | 6.8966 | 9.1405 | 70.3154 | 121.7695 | 17.9504 | 281.4781 | 147.2764 | 307.0728 | 11.9676 | 60.3192 | 17.8235 | 196 | 6.2828 | 158.6138 | 327.0722 | 0
1173 | 917.374 | 3.6518 | 72.1012 | 108.0955 | 59.0947 | 6.6467 | 70.6171 | 6.2231 | 7.7967 | 66.8264 | 113.6448 | 9.8531 | 240.7614 | 138.7969 | 263.7663 | 12.0837 | 55.885 | 16.8171 | 168 | 6.3201 | 148.2937 | 307.5138 | 0
1174 | 880.4222 | 3.4487 | 67.691 | 104.6597 | 59.1457 | 6.5982 | 68.3212 | 6.131 | 6.9847 | 64.5633 | 104.526 | 8.1728 | 212.6608 | 126.819 | 255.9054 | 12.0368 | 53.2619 | 15.4678 | 157 | 6.3988 | 138.7346 | 301.9794 | 0
1175 | 854.1146 | 3.195 | 67.5749 | 101.7496 | 59.802 | 5.9748 | 75.8127 | 6.361 | 6.4621 | 59.2736 | 92.8912 | 7.9722 | 192.7802 | 119.2638 | 247.9524 | 12.0187 | 52.5278 | 14.5796 | 131 | 6.3875 | 123.3599 | 295.6406 | 0
1176 | 831.5937 | 2.1637 | 67.6028 | 101.2052 | 59.2927 | 6.4586 | 70.7308 | 6.5396 | 6.3769 | 56.7543 | 87.7182 | 7.9478 | 178.4076 | 117.4171 | 238.9502 | 12.0148 | 53.2418 | 13.8044 | 111 | 6.5223 | 94.7734 | 300.9925 | 0
1177 | 819.8607 | 1.624 | 67.5655 | 102.5908 | 59.8974 | 5.8841 | 67.3406 | 6.505 | 6.2317 | 54.8072 | 85.746 | 7.6368 | 175.2507 | 110.5466 | 257.7425 | 11.9328 | 52.9913 | 13.2203 | 109 | 6.4094 | 85.6344 | 287.2562 | 0
1178 | 812.5831 | 1.4062 | 68.0198 | 103.0708 | 58.5256 | 7.1873 | 70.4038 | 6.5805 | 6.1727 | 54.893 | 84.8519 | 7.5726 | 175.953 | 104.9298 | 258.9699 | 11.896 | 52.4783 | 12.3245 | 102 | 6.4027 | 89.9968 | 287.7268 | 0
1179 | 805.4193 | 2.3023 | 67.6952 | 101.1384 | 58.8211 | 6.9066 | 77.798 | 6.9137 | 6.2765 | 53.3333 | 84.087 | 7.9074 | 162.7529 | 103.5266 | 244.1633 | 11.9949 | 52.3546 | 11.7353 | 121 | 6.4455 | 86.3297 | 289.1882 | 0
1180 | 801.3524 | 2.2505 | 67.3594 | 100.1259 | 58.3538 | 7.3505 | 70.5637 | 6.7372 | 6.0272 | 54.2424 | 84.4167 | 7.6264 | 153.8102 | 101.5016 | 225.8129 | 11.9853 | 52.3278 | 11.6083 | 98 | 6.4305 | 81.3079 | 286.3437 | 0
1181 | 808.697 | 2.5334 | 67.2721 | 100.3859 | 59.6499 | 6.1192 | 66.6339 | 6.7519 | 6.1283 | 60.2902 | 84.9239 | 7.5315 | 150.8638 | 97.3911 | 218.6855 | 11.9375 | 54.1447 | 11.6355 | 97 | 6.4473 | 80.7644 | 308.4772 | 0
1182 | 818.5197 | 3.2071 | 68.7597 | 102.1879 | 59.3245 | 6.4283 | 71.466 | 6.8617 | 6.3613 | 64.7639 | 85.4268 | 8.5665 | 163.5911 | 109.6001 | 224.913 | 11.8927 | 56.6585 | 11.6328 | 102 | 6.4887 | 85.6988 | 334.8782 | 0
1183 | 853.4317 | 4.2608 | 74.7832 | 108.3606 | 55.9819 | 9.6039 | 86.3934 | 6.8535 | 10.3433 | 81.014 | 100.7169 | 18.4269 | 209.5452 | 182.6542 | 255.8131 | 15.0724 | 54.5401 | 11.6195 | 176 | 6.6455 | 134.2172 | 376.9423 | 0
1184 | 928.7436 | 5.4565 | 92.4485 | 110.0328 | 53.5619 | 11.9029 | 101.1694 | 7.2556 | 15.224 | 99.1543 | 136.7981 | 29.056 | 277.5793 | 239.2693 | 353.8201 | 26.2935 | 58.135 | 13.0599 | 231 | 7.6234 | 185.7563 | 442.5283 | 0
1185 | 1016.766 | 4.9222 | 105.5806 | 123.5422 | 53.0316 | 12.4066 | 118.0765 | 7.5306 | 17.5873 | 95.9691 | 165.1834 | 32.2687 | 339.5074 | 266.7457 | 442.7534 | 31.1 | 67.5387 | 18.3269 | 299 | 7.6267 | 211.5998 | 529.2031 | 0.022105
1186 | 1100.9078 | 3.9333 | 109.4268 | 143.0871 | 52.3748 | 13.0306 | 131.5194 | 8.4243 | 19.0167 | 102.4532 | 173.4116 | 36.1997 | 378.1218 | 293.657 | 535.831 | 32.5074 | 79.0767 | 18.2949 | 333 | 8.0534 | 238.6204 | 575.3592 | 0.030258
1187 | 1147.8995 | 3.4478 | 114.3411 | 145.4798 | 52.0824 | 13.3084 | 126.4913 | 8.8885 | 21.9273 | 110.2263 | 181.36 | 41.0643 | 400.8413 | 309.7932 | 577.4193 | 32.9731 | 86.3983 | 17.6714 | 350 | 9.2952 | 249.0822 | 592.6334 | 0.033208
1188 | 1172.1773 | 3.8409 | 113.6278 | 140.0537 | 51.2752 | 14.0751 | 123.8923 | 9.8512 | 21.9993 | 125.5173 | 185.8732 | 40.7471 | 417.365 | 334.3886 | 576.7564 | 33.4343 | 86.0884 | 17.6894 | 303 | 9.3901 | 253.6924 | 593.8145 | 0.035643
1189 | 1177.2125 | 4.0938 | 110.5569 | 142.7411 | 50.5144 | 14.7979 | 130.2491 | 11.3632 | 19.9938 | 114.943 | 187.2763 | 33.0714 | 423.9093 | 336.9505 | 556.1895 | 33.1267 | 84.4313 | 17.7618 | 334 | 7.8724 | 246.9556 | 588.1578 | 0.037415
1190 | 1186.8005 | 5.7709 | 113.6736 | 147.013 | 49.0646 | 16.1753 | 122.2223 | 12.1038 | 20.34 | 109.6767 | 195.4812 | 38.5062 | 420.4481 | 352.5995 | 557.4691 | 34.1378 | 87.1121 | 18.2962 | 299 | 7.2112 | 242.0883 | 590.8456 | 0.032317
1191 | 1188.347 | 9.9659 | 110.5934 | 144.394 | 47.5854 | 17.5805 | 114.0775 | 12.3413 | 20.0007 | 114.124 | 195.0433 | 39.0251 | 410.335 | 342.5958 | 553.3053 | 33.6619 | 88.0119 | 18.6336 | 327 | 6.994 | 244.4609 | 576.6904 | 0.026789
1192 | 1151.3733 | 11.5585 | 107.5778 | 140.7008 | 48.7696 | 16.4556 | 124.1185 | 11.0837 | 18.4255 | 113.5445 | 191.0165 | 38.384 | 410.7098 | 321.0763 | 525.5934 | 32.0708 | 83.7391 | 18.3006 | 297 | 6.7528 | 238.3624 | 536.3838 | 0.011868
1193 | 1106.2741 | 7.2295 | 103.7272 | 136.7498 | 54.4655 | 11.0444 | 118.2358 | 9.6526 | 17.7347 | 109.829 | 188.0505 | 37.0295 | 388.5958 | 291.7293 | 478.0233 | 18.8092 | 78.9589 | 17.3589 | 283 | 6.3767 | 223.631 | 476.5723 | 0.0017593
1194 | 1023.9322 | 5.3275 | 89.9655 | 127.7016 | 57.5816 | 8.0841 | 95.6704 | 7.5277 | 15.966 | 99.205 | 176.2767 | 35.0386 | 331.0188 | 241.7205 | 401.8878 | 10.44 | 74.3568 | 15.9958 | 243 | 6.1624 | 201.1302 | 400.0016 | 0
1195 | 962.0414 | 4.9119 | 70.7327 | 114.5086 | 58.8957 | 6.8357 | 90.6343 | 6.4653 | 14.448 | 78.7721 | 142.0397 | 28.5565 | 276.9673 | 195.0467 | 337.2428 | 9.2556 | 68.5534 | 14.788 | 232 | 6.2034 | 186.4503 | 342.9363 | 0
1196 | 921.2055 | 4.4124 | 65.0828 | 106.7921 | 58.3483 | 7.3557 | 78.0197 | 6.5667 | 10.204 | 68.4096 | 111.9541 | 17.1633 | 239.3705 | 172.6019 | 306.891 | 9.4113 | 59.2332 | 14.3426 | 211 | 6.3626 | 167.5924 | 312.2141 | 0
1197 | 879.4248 | 3.9708 | 64.1648 | 103.0222 | 58.8364 | 6.892 | 69.189 | 6.6618 | 8.4867 | 66.0668 | 93.8782 | 13.5577 | 217.2301 | 150.0439 | 293.889 | 9.2491 | 54.8298 | 13.971 | 208 | 6.2349 | 153.1437 | 296.6764 | 0
1198 | 849.208 | 3.9273 | 63.3557 | 102.5322 | 59.063 | 6.6768 | 71.4982 | 6.8405 | 8.872 | 64.2844 | 87.9189 | 13.3975 | 196.7509 | 135.0239 | 279.0239 | 9.34 | 53.6673 | 13.4368 | 199 | 6.1291 | 147.4465 | 290.4399 | 0
1199 | 837.2599 | 3.5567 | 63.2051 | 100.5972 | 58.2859 | 7.415 | 76.8431 | 6.6601 | 8.0452 | 59.6617 | 86.9022 | 13.5615 | 183.6551 | 130.1934 | 270.0545 | 9.3769 | 52.4546 | 13.3519 | 171 | 6.1135 | 141.9715 | 287.4608 | 0
1200 | 829.013 | 2.8445 | 63.4196 | 99.563 | 58.9323 | 6.8009 | 70.446 | 6.5907 | 7.821 | 56.1095 | 85.0612 | 13.49 | 182.5745 | 130.0458 | 252.2311 | 9.2962 | 52.5152 | 12.5935 | 145 | 6.3122 | 113.0998 | 282.4228 | 0
1201 | 824.2218 | 6.6402 | 63.5053 | 99.4912 | 59.0661 | 6.6739 | 67.3548 | 6.8111 | 7.4229 | 53.6197 | 83.1449 | 13.4291 | 181.7976 | 129.2655 | 250.5026 | 9.3434 | 51.9726 | 12.61 | 159 | 6.3112 | 101.0053 | 279.014 | 0
1202 | 815.0665 | 4.0508 | 63.5053 | 99.5084 | 59.0655 | 6.6744 | 73.3386 | 6.7314 | 7.2136 | 53.3052 | 81.6803 | 13.3709 | 181.135 | 125.6756 | 241.4694 | 9.2077 | 51.1609 | 12.3288 | 143 | 6.3248 | 98.768 | 279.7771 | 0
1203 | 799.4738 | 1.669 | 63.3285 | 97.8822 | 58.3887 | 7.3173 | 71.7327 | 6.6201 | 7.4567 | 52.9242 | 81.4428 | 13.3645 | 167.8748 | 109.1741 | 225.4687 | 9.3058 | 51.176 | 12.3267 | 168 | 6.3307 | 98.3864 | 281.9432 | 0
1204 | 797.5457 | 1.6176 | 63.0011 | 98.2699 | 58.8781 | 6.8525 | 67.7537 | 6.6101 | 7.4473 | 52.6456 | 82.1503 | 13.3718 | 160.9368 | 97.8853 | 219.5987 | 9.2495 | 51.1307 | 12.2188 | 147 | 6.3177 | 97.6146 | 280.3543 | 0
1205 | 800.4491 | 1.9265 | 62.9463 | 100.5966 | 59.0339 | 6.7044 | 67.4634 | 6.8914 | 7.3 | 55.2138 | 82.3593 | 13.3588 | 159.3465 | 96.1325 | 218.2277 | 9.2603 | 52.5054 | 12.1004 | 135 | 6.3022 | 96.8199 | 279.7138 | 0
1206 | 803.5684 | 2.981 | 63.0772 | 100.0514 | 59.0804 | 6.6603 | 77.2186 | 6.8279 | 7.3333 | 59.4451 | 82.4538 | 13.334 | 159.5509 | 98.4536 | 216.3651 | 9.306 | 55.2646 | 12.0088 | 120 | 6.2178 | 95.2219 | 279.7969 | 0
1207 | 817.234 | 3.4657 | 66.0194 | 102.9109 | 58.2934 | 7.4079 | 73.4269 | 6.7036 | 8.5478 | 63.1922 | 83.0813 | 13.2993 | 160.6948 | 97.2326 | 222.8788 | 9.2546 | 52.433 | 12.0271 | 137 | 6.2637 | 97.5344 | 284.6204 | 0
1208 | 838.9709 | 3.2059 | 71.2174 | 107.5595 | 58.9026 | 6.8291 | 68.5312 | 6.6508 | 11.149 | 61.1987 | 87.4183 | 13.8967 | 165.4797 | 95.8313 | 238.1469 | 9.1308 | 50.3135 | 12.203 | 129 | 6.3269 | 104.4658 | 293.2513 | 0
1209 | 841.2799 | 2.6323 | 84.183 | 108.0635 | 58.3612 | 7.3435 | 69.407 | 6.3462 | 9.5826 | 63.4764 | 116.2339 | 16.9993 | 183.6028 | 99.6263 | 249.2686 | 8.9504 | 50.04 | 12.6647 | 129 | 6.0253 | 107.7721 | 298.6475 | 0.0084002
1210 | 875.7295 | 2.0933 | 93.025 | 108.0466 | 58.8402 | 6.8885 | 76.6599 | 6.3873 | 11.0453 | 81.5869 | 141.8349 | 12.5472 | 203.1771 | 104.9369 | 261.6377 | 8.9351 | 51.9033 | 12.8116 | 142 | 6.3046 | 135.6157 | 295.9275 | 0.0090797
1211 | 900.7159 | 1.4923 | 89.4283 | 107.3887 | 59.0963 | 6.6451 | 76.2565 | 6.182 | 7.9933 | 86.8941 | 150.0189 | 10.5433 | 220.3117 | 123.5806 | 258.9002 | 8.8886 | 54.9769 | 13.0836 | 165 | 7.1997 | 144.0337 | 302.8669 | 0.014604
1212 | 888.6296 | 1.7163 | 84.4129 | 108.4767 | 59.8097 | 5.9674 | 69.6627 | 5.933 | 7.1987 | 88.9926 | 142.9697 | 10.5592 | 229.0755 | 136.6685 | 259.5698 | 8.854 | 56.7355 | 13.0571 | 171 | 6.008 | 142.1195 | 304.3045 | 0.01988
1213 | 891.9786 | 1.8333 | 83.3417 | 109.9387 | 60.1393 | 5.6543 | 68.0907 | 5.8073 | 12.8477 | 89.9861 | 112.4504 | 10.6977 | 232.4112 | 140.1087 | 248.1882 | 8.8798 | 55.3415 | 12.6338 | 168 | 5.5959 | 145.2201 | 289.9471 | 0.015149
1214 | 884.3902 | 1.9453 | 80.9456 | 109.7618 | 60.0915 | 5.6997 | 94.6718 | 6.5797 | 14.5489 | 85.8037 | 101.0836 | 10.9398 | 233.0034 | 152.1803 | 236.8984 | 8.939 | 55.0938 | 12.8856 | 207 | 5.3379 | 149.0893 | 286.5224 | 0.035456
1215 | 887.5998 | 2.11 | 63.5673 | 100.2633 | 60.099 | 5.6926 | 94.6102 | 8.2123 | 14.7153 | 80.4015 | 101.3563 | 11.7801 | 235.9957 | 150.6413 | 254.0432 | 8.7444 | 57.3722 | 13.1885 | 228 | 5.3495 | 148.8123 | 281.0308 | 0.04695
1216 | 886.6726 | 2.4448 | 56.9888 | 95.9891 | 59.3007 | 6.451 | 85.951 | 6.9577 | 15.604 | 61.5783 | 101.276 | 14.8516 | 233.2848 | 154.1948 | 283.4539 | 8.8651 | 59.5262 | 13.3297 | 223 | 5.1943 | 133.7925 | 292.7737 | 0.052387
1217 | 874.4062 | 3.3601 | 56.1802 | 95.5031 | 58.3411 | 7.3626 | 86.5109 | 5.8186 | 14.228 | 37.7595 | 100.8936 | 14.6888 | 228.2577 | 158.1192 | 292.3039 | 8.7326 | 58.7119 | 13.3581 | 222 | 5.1776 | 101.7815 | 285.1544 | 0.0071525
1218 | 876.753 | 4.2413 | 55.8223 | 97.7096 | 58.8264 | 6.9015 | 83.6703 | 6.2065 | 13.884 | 34.5757 | 99.1466 | 13.3504 | 222.1112 | 160.659 | 276.3607 | 9.0653 | 59.8644 | 13.8846 | 205 | 5.1848 | 90.8973 | 293.1607 | 0
1219 | 864.7433 | 5.0554 | 55.9987 | 99.7851 | 58.3174 | 7.3851 | 73.1683 | 6.6095 | 13.4007 | 39.7647 | 92.552 | 13.5 | 220.2284 | 161.4877 | 267.6383 | 9.3801 | 59.9343 | 14.4491 | 200 | 5.4758 | 99.8769 | 298.4495 | 0
1220 | 839.4462 | 6.9678 | 55.8951 | 99.2972 | 58.8933 | 6.838 | 67.8112 | 6.7512 | 9.604 | 40.2364 | 88.0654 | 12.3015 | 206.8765 | 147.6458 | 276.8386 | 9.326 | 56.9369 | 14.2713 | 199 | 5.5128 | 104.0922 | 303.2287 | 0
1221 | 829.3486 | 10.0706 | 55.6227 | 98.0545 | 59.096 | 6.6455 | 73.3078 | 6.7457 | 7.904 | 39.482 | 83.7221 | 10.4944 | 180.533 | 138.3068 | 260.3942 | 9.34 | 53.4213 | 13.6615 | 205 | 5.2796 | 106.1397 | 294.7194 | 0
1222 | 808.5506 | 10.7642 | 55.8623 | 96.7425 | 59.0455 | 6.6934 | 73.5932 | 6.855 | 7.6402 | 37.2302 | 81.8543 | 10.1064 | 171.6618 | 133.0874 | 243.944 | 9.2263 | 52.2095 | 13.0483 | 184 | 5.2956 | 103.6337 | 289.1847 | 0
1223 | 801.3371 | 10.1557 | 55.5775 | 96.0971 | 59.8485 | 5.9306 | 65.7111 | 6.7044 | 7.3967 | 35.7928 | 80.699 | 9.5237 | 176.9965 | 127.7792 | 240.351 | 9.4172 | 51.961 | 12.8262 | 160 | 5.3628 | 96.1529 | 284.8711 | 0
1224 | 805.9799 | 4.3191 | 55.631 | 96.2948 | 60.1147 | 5.6777 | 65.6052 | 6.6501 | 7.4391 | 36.467 | 81.3428 | 9.5289 | 173.9808 | 112.7509 | 243.7082 | 9.3386 | 52.3238 | 12.1284 | 154 | 5.3285 | 93.0381 | 275.7978 | 0
1225 | 833.0569 | 1.6778 | 55.8787 | 96.4326 | 60.1273 | 5.6657 | 77.2206 | 6.6388 | 7.5301 | 36.7082 | 81.1418 | 9.4127 | 170.9435 | 108.9094 | 246.5978 | 9.4347 | 52.1596 | 11.7647 | 148 | 5.4652 | 94.5198 | 287.2077 | 0
1226 | 836.571 | 1.6735 | 55.7715 | 95.9944 | 57.8019 | 7.8749 | 71.9803 | 6.7444 | 7.5573 | 36.6001 | 80.1255 | 9.4889 | 173.6523 | 110.2989 | 233.5752 | 9.3834 | 52.1701 | 11.2994 | 145 | 5.8061 | 94.443 | 283.1749 | 0
1227 | 826.7848 | 1.5937 | 55.6491 | 95.839 | 55.4762 | 10.0843 | 67.3214 | 7.063 | 7.2813 | 35.2226 | 80.0262 | 9.3774 | 167.2196 | 104.7072 | 232.1707 | 9.3369 | 52.0657 | 11.0334 | 160 | 7.5225 | 94.3786 | 279.3889 | 0
1228 | 817.3255 | 1.4834 | 55.7394 | 95.6097 | 55.1133 | 10.429 | 70.6034 | 6.9192 | 7.29 | 35.7331 | 80.7859 | 9.3164 | 159.4213 | 97.545 | 240.2593 | 9.3814 | 52.0526 | 10.9759 | 153 | 6.5984 | 90.2739 | 273.6468 | 0
1229 | 795.1513 | 1.9268 | 55.7373 | 96.2005 | 56.5945 | 9.0218 | 75.7898 | 6.6444 | 7.4107 | 36.2051 | 80.9904 | 9.2896 | 152.4887 | 101.6911 | 232.4906 | 9.3489 | 53.4897 | 10.9867 | 137 | 6.0041 | 87.3837 | 272.4976 | 0
1230 | 789.6909 | 3.1403 | 55.6897 | 98.1752 | 59.505 | 6.2569 | 69.225 | 6.422 | 7.3227 | 37.5644 | 81.2727 | 9.2748 | 156.5473 | 99.371 | 221.0696 | 9.3702 | 56.0805 | 11.0055 | 134 | 5.5444 | 88.1113 | 269.4479 | 0
1231 | 805.2233 | 3.3612 | 55.8695 | 96.854 | 60.0926 | 5.6986 | 65.9593 | 6.3222 | 7.2873 | 41.6816 | 81.7767 | 9.2933 | 157.4552 | 101.0869 | 218.9014 | 9.3593 | 53.3224 | 10.9913 | 126 | 5.3966 | 88.355 | 273.7272 | 0
1232 | 819.9132 | 3.6194 | 55.9928 | 94.3032 | 59.2887 | 6.4624 | 73.8567 | 6.2197 | 7.774 | 33.9578 | 78.462 | 7.8265 | 152.9539 | 96.3684 | 212.7598 | 8.967 | 50.7081 | 11.2485 | 115 | 5.3354 | 87.2268 | 257.6841 | 0
1233 | 817.931 | 2.14 | 55.9136 | 93.4365 | 58.2732 | 7.4271 | 72.9936 | 6.3653 | 11.8073 | 40.1626 | 81.3757 | 6.2627 | 163.6572 | 101.6017 | 218.0421 | 8.7652 | 50.3257 | 11.872 | 122 | 5.2913 | 89.1864 | 251.8503 | 0.078413
1234 | 832.1824 | 1.6316 | 55.9595 | 93.5344 | 58.9115 | 6.8207 | 64.3805 | 5.7818 | 11.8093 | 62.052 | 85.3807 | 5.026 | 173.186 | 113.3203 | 215.1515 | 8.8337 | 51.0888 | 12.0965 | 155 | 5.3089 | 91.6408 | 248.1288 | 0.094019
1235 | 855.2504 | 2.4887 | 56.0271 | 93.6104 | 59.8536 | 5.9257 | 70.8149 | 5.3723 | 12.9207 | 78.682 | 97.9073 | 4.7603 | 191.3276 | 125.8164 | 207.8646 | 8.3697 | 52.3381 | 12.4167 | 173 | 5.3744 | 93.8841 | 252.2149 | 0.17142
1236 | 870.7994 | 2.3229 | 56.1677 | 93.9296 | 60.1009 | 5.6907 | 87.8162 | 5.2653 | 13.9133 | 82.8107 | 104.1844 | 5.0898 | 205.4434 | 132.825 | 220.0243 | 7.8693 | 52.5491 | 12.4763 | 159 | 5.2883 | 94.6293 | 253.0923 | 0.1916
1237 | 886.6523 | 1.9066 | 56.1946 | 94.7205 | 60.0596 | 5.73 | 84.2434 | 4.9204 | 13.8693 | 73.3583 | 105.6211 | 5.121 | 213.4546 | 136.2832 | 231.5468 | 7.7176 | 52.3943 | 12.4263 | 156 | 5.2904 | 91.0322 | 260.4056 | 0.11383
1238 | 888.2779 | 1.8648 | 56.5065 | 95.9599 | 60.0547 | 5.7346 | 71.023 | 5.0359 | 13.9193 | 65.5835 | 107.483 | 5.0477 | 217.0015 | 141.3893 | 246.7405 | 8.3118 | 53.1027 | 12.7875 | 161 | 5.3573 | 89.8672 | 263.5026 | 0.10041
1239 | 894.4957 | 2.033 | 56.2249 | 97.3349 | 60.0919 | 5.6993 | 70.0559 | 5.4026 | 10.58 | 59.8985 | 111.3725 | 6.3742 | 219.3857 | 146.7015 | 264.6964 | 8.7134 | 53.3751 | 13.4864 | 170 | 5.2887 | 91.1695 | 259.7111 | 0.079544
1240 | 897.3149 | 2.3928 | 55.75 | 97.3284 | 57.0173 | 8.6202 | 80.7755 | 5.4285 | 6.7447 | 54.9948 | 109.8927 | 8.578 | 214.4795 | 147.0955 | 284.3163 | 8.4044 | 52.553 | 13.6028 | 162 | 5.2301 | 91.3849 | 265.9201 | 0.06377
1241 | 899.8081 | 3.4798 | 55.7995 | 97.4865 | 59.1958 | 6.5506 | 82.6803 | 5.6078 | 6.662 | 47.2162 | 107.91 | 7.0414 | 214.5829 | 149.7884 | 294.5831 | 8.5954 | 52.5311 | 13.881 | 171 | 5.1693 | 92.9771 | 268.2323 | 0.0071685
1242 | 907.5533 | 4.3861 | 55.7142 | 101.701 | 59.2679 | 6.4822 | 73.8563 | 5.9779 | 11.7379 | 53.0016 | 111.1646 | 9.0465 | 214.1867 | 142.8933 | 287.1303 | 8.8334 | 54.2659 | 14.79 | 161 | 5.3229 | 91.1678 | 266.0496 | 0
1243 | 905.6039 | 8.7175 | 55.5843 | 101.2375 | 59.8827 | 5.898 | 74.323 | 6.0553 | 12.6586 | 49.4967 | 114.7924 | 9.1957 | 206.6293 | 135.4916 | 275.653 | 9.1726 | 55.4335 | 14.773 | 139 | 5.4567 | 96.5199 | 266.6977 | 0
1244 | 889.7771 | 6.3501 | 55.6745 | 97.0727 | 60.114 | 5.6784 | 75.4628 | 6.0468 | 7.9737 | 42.7894 | 108.6248 | 8.4845 | 189.5832 | 125.6471 | 268.6499 | 9.2463 | 52.6991 | 14.0903 | 123 | 5.4908 | 99.8039 | 268.9068 | 0
1245 | 860.8792 | 4.7146 | 55.7285 | 95.5966 | 57.7638 | 7.911 | 69.8653 | 6.3584 | 6.3831 | 38.9692 | 96.0691 | 8.3171 | 181.3566 | 121.4683 | 263.2581 | 9.2172 | 51.3289 | 14.1047 | 121 | 5.5655 | 95.0681 | 265.6205 | 0
1246 | 836.4542 | 4.1838 | 55.5961 | 96.1129 | 59.4003 | 6.3563 | 67.7736 | 6.1634 | 6.3442 | 37.8832 | 91.4053 | 8.717 | 173.2955 | 116.691 | 246.1391 | 9.2825 | 51.0347 | 13.4934 | 118 | 5.5365 | 93.9811 | 271.5314 | 0
1247 | 831.8484 | 3.2332 | 55.6057 | 96.3335 | 59.3273 | 6.4257 | 77.847 | 6.0645 | 6.6323 | 37.0516 | 88.5788 | 8.8972 | 166.9331 | 110.0853 | 234.5537 | 9.1437 | 51.8563 | 12.8946 | 116 | 5.4318 | 87.1544 | 263.3693 | 0
1248 | 819.2084 | 1.9527 | 55.8033 | 96.2503 | 59.9054 | 5.8765 | 73.5662 | 6.0687 | 6.4068 | 36.6423 | 85.0286 | 7.9341 | 154.8768 | 105.731 | 232.9021 | 9.2809 | 51.754 | 12.2362 | 110 | 5.5766 | 86.0159 | 266.2087 | 0
1249 | 812.1353 | 1.4371 | 55.5658 | 95.465 | 60.1069 | 5.6851 | 67.2768 | 6.0694 | 6.3927 | 35.6991 | 83.1271 | 7.5194 | 147.8536 | 102.7111 | 241.2479 | 9.2455 | 51.114 | 11.6487 | 114 | 5.4995 | 90.0854 | 262.7385 | 0
1250 | 805.8142 | 1.6122 | 55.5259 | 95.0447 | 60.1067 | 5.6853 | 70.7828 | 6.1552 | 6.3053 | 34.0555 | 81.2027 | 7.5688 | 147.5988 | 103.6382 | 236.6051 | 9.3113 | 50.8036 | 11.4295 | 114 | 5.5102 | 91.1224 | 266.6073 | 0
1251 | 799.9558 | 1.646 | 55.7381 | 95.0414 | 60.0743 | 5.716 | 77.0178 | 6.4752 | 6.524 | 33.2478 | 80.6439 | 7.7905 | 148.3085 | 107.4118 | 226.4679 | 9.3584 | 50.5364 | 11.361 | 126 | 5.4842 | 90.3303 | 267.123 | 0
1252 | 793.2113 | 1.6997 | 55.7584 | 94.9461 | 59.2385 | 6.51 | 69.3188 | 6.3002 | 6.7769 | 36.0633 | 81.1953 | 7.8227 | 152.2065 | 110.8566 | 216.6841 | 9.2011 | 50.5302 | 11.3344 | 111 | 5.393 | 90.8583 | 271.0397 | 0
1253 | 800.7825 | 1.8877 | 56.5891 | 97.7301 | 59.899 | 5.8826 | 66.2832 | 6.3885 | 6.2822 | 46.8412 | 81.4297 | 7.7944 | 148.1539 | 107.0118 | 212.7464 | 9.249 | 52.2146 | 11.3249 | 106 | 5.3382 | 89.0764 | 293.6061 | 0
1254 | 809.473 | 3.0299 | 56.5743 | 97.0167 | 60.1147 | 5.6777 | 74.1743 | 6.4771 | 6.3856 | 52.3952 | 82.3204 | 9.286 | 167.8617 | 110.832 | 221.3619 | 9.2126 | 54.9984 | 11.5575 | 109 | 5.3584 | 91.1555 | 309.7755 | 0
1255 | 841.7046 | 5.052 | 68.3525 | 103.461 | 57.0033 | 8.6335 | 82.8475 | 6.5295 | 8.0447 | 69.6455 | 106.2064 | 18.6864 | 208.6569 | 178.9573 | 259.6266 | 12.3857 | 52.616 | 12.2502 | 158 | 5.5898 | 145.4171 | 355.9691 | 0
1256 | 929.9967 | 5.8571 | 90.1825 | 108.236 | 52.1973 | 13.1992 | 97.9059 | 7.8302 | 13.34 | 95.9322 | 138.6301 | 31.435 | 281.9337 | 238.582 | 373.3196 | 26.0106 | 57.3127 | 12.7509 | 275 | 6.1034 | 187.6768 | 417.9258 | 0
1257 | 1026.2652 | 4.7562 | 104.8015 | 122.0983 | 50.2273 | 15.0707 | 114.9518 | 9.555 | 17.7828 | 106.1171 | 164.7379 | 38.2978 | 356.4076 | 286.4766 | 495.6145 | 34.0977 | 66.6289 | 16.1201 | 290 | 6.5872 | 211.0309 | 513.0034 | 0.071216
1258 | 1097.6362 | 3.9234 | 112.0944 | 133.7157 | 49.3367 | 15.9167 | 128.9806 | 9.5797 | 21.3949 | 107.2289 | 179.9316 | 42.1672 | 392.613 | 319.5347 | 546.3818 | 38.2247 | 76.7248 | 16.7064 | 351 | 7.0366 | 234.2941 | 553.7041 | 0.10357
1259 | 1137.2833 | 3.9108 | 112.6213 | 138.1387 | 48.3879 | 16.8182 | 124.3534 | 9.7249 | 24.4477 | 109.4064 | 185.5951 | 43.8959 | 406.4426 | 339.1251 | 571.8447 | 38.8866 | 88.1008 | 17.3159 | 372 | 7.496 | 237.3236 | 552.7975 | 0.13209
1260 | 1190.9122 | 4.2834 | 112.142 | 139.2075 | 50.5444 | 14.7695 | 125.5775 | 9.7592 | 23.5877 | 109.7727 | 185.9836 | 41.9584 | 425.5064 | 357.8795 | 601.1298 | 38.9061 | 98.5618 | 17.4442 | 338 | 8.2895 | 235.0398 | 563.7376 | 0.12475
1261 | 1197.3922 | 4.1676 | 111.603 | 138.3479 | 49.646 | 15.623 | 129.7579 | 10.1818 | 20.3661 | 109.7436 | 185.9996 | 40.7416 | 434.7236 | 354.3232 | 593.9505 | 41.2892 | 96.423 | 17.2922 | 350 | 8.1823 | 228.5017 | 571.9386 | 0.13235
1262 | 1198.3539 | 4.3182 | 114.8771 | 140.7906 | 48.3537 | 16.8506 | 131.6272 | 10.1372 | 22.77 | 114.514 | 195.8096 | 42.1971 | 433.6098 | 356.8599 | 585.012 | 43.8542 | 97.5452 | 17.536 | 338 | 7.5359 | 234.2575 | 583.6746 | 0.068887
1263 | 1205.8993 | 4.3653 | 113.9032 | 142.7485 | 49.6297 | 15.6384 | 128.7493 | 9.9218 | 22.6393 | 121.3496 | 196.6477 | 42.8078 | 444.4242 | 365.1816 | 583.7808 | 44.545 | 97.8286 | 18.6573 | 316 | 8.3512 | 236.9778 | 584.9195 | 0.037308
1264 | 1179.3569 | 4.0771 | 113.0254 | 145.75 | 50.0138 | 15.2735 | 121.2129 | 10.2952 | 19.2495 | 113.425 | 191.661 | 42.868 | 447.3387 | 347.6057 | 571.8594 | 41.4011 | 96.2307 | 19.4486 | 289 | 8.3614 | 237.1091 | 576.8872 | 0.018305
1265 | 1139.0486 | 5.2254 | 108.7374 | 145.2796 | 54.6908 | 10.8304 | 115.4511 | 10.3635 | 16.9199 | 105.6504 | 188.225 | 40.796 | 420.0089 | 325.1814 | 521.6047 | 32.0532 | 92.1743 | 19.0835 | 257 | 7.0647 | 224.8689 | 504.1253 | 0.0048935
1266 | 1072.8681 | 6.469 | 102.2393 | 132.0019 | 56.0941 | 9.4972 | 116.994 | 9.1342 | 16.4457 | 83.7855 | 184.1597 | 38.347 | 365.8408 | 250.6686 | 422.1684 | 17.882 | 86.3042 | 18.4174 | 232 | 6.8225 | 195.6735 | 432.8546 | 0
1267 | 1031.3107 | 9.6026 | 98.8852 | 119.4234 | 55.2262 | 10.3217 | 102.7001 | 7.7434 | 16.6217 | 68.4461 | 156.1335 | 30.0366 | 317.2228 | 193.7558 | 373.1545 | 11.5185 | 78.4209 | 17.6113 | 220 | 7.0522 | 176.0419 | 373.2682 | 0
1268 | 980.2379 | 6.2511 | 93.2514 | 111.228 | 55.1443 | 10.3995 | 88.461 | 6.4657 | 15.0253 | 62.3326 | 121.6509 | 13.273 | 283.5334 | 170.2578 | 331.1301 | 11.4116 | 64.3015 | 16.8678 | 205 | 7.1495 | 158.3146 | 336.1422 | 0
1269 | 934.9997 | 4.5237 | 76.1066 | 103.5353 | 57.3858 | 8.2701 | 81.1341 | 6.0917 | 11.4133 | 55.9561 | 109.9343 | 7.5965 | 248.9713 | 156.9184 | 290.281 | 10.3689 | 56.0294 | 15.5102 | 183 | 7.1976 | 146.021 | 306.9046 | 0
1270 | 887.9326 | 4.2834 | 68.5969 | 99.4887 | 58.8505 | 6.8786 | 69.9946 | 5.9141 | 12.3073 | 45.8648 | 107.6448 | 7.5785 | 217.172 | 146.0055 | 268.3963 | 9.7501 | 54.308 | 14.2475 | 157 | 7.0022 | 132.9812 | 279.3491 | 0
1271 | 851.3294 | 3.3051 | 67.555 | 97.5739 | 58.3358 | 7.3676 | 65.5956 | 6.3256 | 8.2413 | 38.2898 | 93.6017 | 7.5864 | 190.8312 | 129.5854 | 247.0805 | 9.5597 | 52.7345 | 13.4448 | 130 | 6.8877 | 123.5808 | 275.1086 | 0
1272 | 835.5934 | 2.1821 | 67.2521 | 95.8324 | 58.0585 | 7.6311 | 72.5315 | 6.5018 | 6.368 | 34.2501 | 83.7445 | 7.398 | 192.2564 | 117.3717 | 228.9286 | 9.5379 | 51.7715 | 13.2501 | 119 | 6.9302 | 99.3635 | 272.3421 | 0
1273 | 828.0093 | 1.8085 | 67.1739 | 96.5659 | 58.8535 | 6.8758 | 75.8746 | 6.4131 | 6.4007 | 32.8692 | 82.2159 | 7.3456 | 175.0922 | 111.441 | 230.4378 | 9.5788 | 51.7307 | 13.0068 | 115 | 7.0794 | 89.7081 | 269.8861 | 0
1274 | 823.546 | 1.6884 | 67.2992 | 95.3557 | 59.1636 | 6.5812 | 68.6907 | 6.3554 | 6.3671 | 32.7403 | 85.8914 | 7.3815 | 167.6587 | 104.354 | 221.5253 | 9.5403 | 51.9528 | 12.4073 | 120 | 7.1723 | 90.1465 | 269.4969 | 0
1275 | 809.5626 | 1.5404 | 67.2914 | 94.7996 | 59.037 | 6.7015 | 65.973 | 6.7137 | 6.4547 | 32.4748 | 90.1856 | 7.3981 | 166.7052 | 100.0191 | 220.7408 | 9.5917 | 52.1064 | 12.2006 | 130 | 7.243 | 92.647 | 270.4226 | 0
1276 | 813.5843 | 1.3793 | 67.4322 | 94.7509 | 59.115 | 6.6274 | 76.1602 | 6.6936 | 6.4358 | 35.5904 | 90.979 | 7.4237 | 160.4443 | 95.163 | 227.1781 | 9.5562 | 52.1566 | 12.0809 | 114 | 7.2628 | 92.4505 | 271.0869 | 0
1277 | 818.5174 | 1.7533 | 66.4609 | 96.4112 | 59.1229 | 6.6198 | 72.3114 | 6.3812 | 6.3607 | 46.6736 | 89.0731 | 7.5074 | 156.1777 | 93.6577 | 224.0994 | 9.4867 | 53.5377 | 11.9771 | 99 | 7.1273 | 90.8762 | 291.1669 | 0
1278 | 831.1438 | 2.9371 | 66.7998 | 97.4716 | 58.309 | 7.3931 | 65.3564 | 6.2975 | 6.469 | 52.6116 | 86.9099 | 8.9657 | 170.3779 | 104.9686 | 225.1534 | 9.452 | 55.7627 | 11.9571 | 107 | 6.9839 | 94.3551 | 318.223 | 0
1279 | 862.2717 | 4.6374 | 58.401 | 104.8835 | 57.2834 | 8.3674 | 74.8654 | 6.4803 | 10.8057 | 71.2876 | 101.4444 | 18.8251 | 231.4033 | 168.5074 | 260.9432 | 13.1168 | 53.7929 | 12.0114 | 184 | 7.3066 | 126.9725 | 371.286 | 0
1280 | 944.3608 | 5.37 | 55.1467 | 108.2063 | 51.5775 | 13.788 | 107.705 | 7.2789 | 15.2756 | 90.9248 | 138.6949 | 33.1091 | 301.9517 | 235.2612 | 348.8673 | 27.5952 | 57.9304 | 13.0204 | 310 | 8.8998 | 179.7323 | 431.7758 | 0
1281 | 1043.9234 | 4.6516 | 83.3756 | 118.264 | 50.8924 | 14.4388 | 122.8959 | 7.6094 | 18.2188 | 82.0774 | 175.0625 | 40.8463 | 361.5572 | 282.9444 | 468.6423 | 36.552 | 67.1798 | 17.2677 | 281 | 12.5957 | 203.5751 | 520.6847 | 0.070139
1282 | 1122.5212 | 4.3245 | 99.6584 | 129.9454 | 51.965 | 13.4199 | 124.1046 | 7.3571 | 19.038 | 86.6532 | 192.1315 | 43.8282 | 391.2629 | 316.1147 | 546.1328 | 39.3164 | 77.0995 | 18.9121 | 344 | 14.5518 | 227.8654 | 584.3876 | 0.086963
1283 | 1181.919 | 4.0652 | 100.6022 | 137.7936 | 49.7274 | 15.5456 | 131.867 | 7.9925 | 20.1241 | 88.5238 | 198.9364 | 45.1199 | 413.3813 | 352.3619 | 597.7458 | 41.0531 | 84.1766 | 19.2056 | 366 | 14.6109 | 239.4091 | 595.8975 | 0.11546
1284 | 1212.7042 | 4.0392 | 104.1089 | 139.9202 | 49.1103 | 16.1318 | 138.0167 | 8.2048 | 20.9706 | 100.1643 | 206.0723 | 42.8665 | 427.0722 | 362.2925 | 632.7519 | 40.4894 | 84.5552 | 18.9483 | 322 | 14.5515 | 239.2861 | 590.2139 | 0.10751
1285 | 1202.0784 | 4.3294 | 103.6865 | 134.3814 | 49.8307 | 15.4475 | 129.4264 | 8.302 | 21.3207 | 106.3805 | 199.4294 | 38.392 | 422.2463 | 352.0194 | 613.1649 | 41.5683 | 83.082 | 18.8716 | 376 | 14.5019 | 229.7891 | 603.5326 | 0.11831
1286 | 1202.9885 | 4.2978 | 102.508 | 138.0245 | 49.4551 | 15.8043 | 136.1567 | 8.1737 | 20.5558 | 109.1601 | 207.1597 | 40.9664 | 434.1062 | 355.3687 | 614.0156 | 43.2313 | 84.3722 | 19.6069 | 339 | 13.8558 | 225.8344 | 622.5382 | 0.18093
1287 | 1178.7096 | 4.2534 | 106.8257 | 142.5825 | 48.2511 | 16.9481 | 137.4942 | 8.1086 | 21.6992 | 109.9779 | 210.6572 | 42.645 | 447.7514 | 358.5031 | 611.2541 | 43.3824 | 84.3283 | 19.986 | 337 | 14.1972 | 231.7023 | 605.6185 | 0.18176
1288 | 1166.4327 | 6.0379 | 103.4249 | 138.9252 | 46.5144 | 18.598 | 132.9933 | 8.7118 | 20.6203 | 106.1037 | 205.7894 | 41.4748 | 449.6579 | 339.6708 | 604.9398 | 41.4881 | 82.3294 | 19.956 | 308 | 13.6971 | 231.7221 | 580.8255 | 0.081162
1289 | 1160.0882 | 7.7057 | 99.5096 | 129.4744 | 54.5928 | 10.9235 | 111.8742 | 8.7414 | 19.6351 | 91.437 | 205.8159 | 36.9602 | 428.0298 | 311.2671 | 537.822 | 33.6257 | 79.0927 | 19.5633 | 272 | 13.1086 | 212.8094 | 514.4646 | 0.023573
1290 | 1095.0197 | 8.8019 | 92.1452 | 120.8646 | 56.1863 | 9.4096 | 102.7434 | 8.0689 | 21.0838 | 74.5001 | 189.0724 | 32.0558 | 366.9863 | 257.2459 | 419.2319 | 19.2933 | 76.9766 | 18.2501 | 241 | 12.9223 | 192.4038 | 444.0325 | 0
1291 | 1022.4352 | 8.1438 | 87.7052 | 116.6124 | 57.7243 | 7.9486 | 92.4477 | 7.4973 | 19.0558 | 56.2922 | 150.8608 | 27.389 | 322.1017 | 211.2772 | 352.5405 | 12.4053 | 72.3657 | 16.842 | 225 | 12.9657 | 182.038 | 386.6469 | 0
1292 | 984.774 | 6.3218 | 81.953 | 111.6067 | 58.1305 | 7.5626 | 75.5434 | 7.9203 | 12.8393 | 45.5554 | 121.287 | 14.0338 | 282.0201 | 191.357 | 316.8403 | 11.3806 | 65.026 | 15.4466 | 184 | 13.0761 | 165.5776 | 342.4626 | 0
1293 | 946.7909 | 4.306 | 61.5682 | 107.1289 | 58.8156 | 6.9118 | 71.4776 | 7.9056 | 9.6173 | 43.0546 | 113.9081 | 9.5818 | 241.7371 | 169.1284 | 290.9314 | 11.0632 | 59.1161 | 14.9349 | 180 | 13.1171 | 156.7839 | 319.7046 | 0
1294 | 917.7225 | 3.5951 | 54.3968 | 104.7466 | 58.3639 | 7.341 | 74.7813 | 7.6852 | 7.9265 | 38.7451 | 108.0793 | 9.5021 | 201.3539 | 151.9672 | 260.7131 | 10.0119 | 56.4124 | 14.1382 | 167 | 12.7171 | 142.0065 | 311.4801 | 0
1295 | 877.7612 | 3.2527 | 54.7164 | 101.8298 | 57.2621 | 8.3876 | 67.9861 | 7.9031 | 6.9747 | 34.8501 | 90.6888 | 9.0931 | 175.0229 | 137.8708 | 248.6757 | 9.6455 | 55.2386 | 14.085 | 132 | 12.7256 | 125.4215 | 314.1139 | 0
1296 | 863.9587 | 2.2749 | 54.9127 | 102.2327 | 57.8834 | 7.7974 | 63.8639 | 7.9607 | 6.8588 | 33.9001 | 81.9191 | 8.9022 | 166.9374 | 128.911 | 232.2548 | 9.5946 | 55.187 | 13.7136 | 115 | 12.8833 | 94.5675 | 308.486 | 0
1297 | 865.7508 | 1.6234 | 54.4852 | 103.5168 | 58.132 | 7.5612 | 67.2037 | 7.7806 | 6.8167 | 34.8947 | 81.1574 | 8.8836 | 165.3204 | 126.839 | 233.5426 | 9.5746 | 54.8369 | 13.2012 | 115 | 12.8698 | 82.9756 | 301.471 | 0
1298 | 849.431 | 1.3646 | 54.6196 | 103.3776 | 58.0986 | 7.5929 | 72.0658 | 7.5029 | 6.724 | 35.2066 | 81.0708 | 8.921 | 166.5406 | 118.9815 | 243.7634 | 9.6158 | 54.8084 | 11.9987 | 109 | 12.9765 | 85.3993 | 307.9142 | 0
1299 | 832.4268 | 1.312 | 54.8255 | 104.8502 | 58.0924 | 7.5989 | 69.1663 | 7.347 | 6.81 | 35.3742 | 80.8481 | 8.9332 | 168.3081 | 117.3862 | 236.9736 | 9.7107 | 54.6917 | 11.5742 | 127 | 13.0342 | 83.2931 | 310.2039 | 0
1300 | 826.9336 | 1.3754 | 54.6355 | 105.1607 | 58.6581 | 7.0614 | 67.1462 | 7.4102 | 6.7577 | 37.9853 | 81.0568 | 8.9436 | 167.7308 | 117.366 | 228.8236 | 9.6192 | 54.7716 | 12.1881 | 105 | 13.0156 | 80.6755 | 310.2203 | 0
1301 | 832.9339 | 1.6905 | 54.7248 | 103.9575 | 58.3876 | 7.3184 | 69.7777 | 7.4306 | 6.6438 | 48.6688 | 80.9742 | 8.8931 | 173.8492 | 114.63 | 220.7443 | 9.6629 | 55.8885 | 11.8702 | 103 | 12.9605 | 78.9348 | 322.4775 | 0
1302 | 841.7954 | 2.6916 | 55.2563 | 104.7948 | 57.472 | 8.1883 | 74.6891 | 7.447 | 8.0278 | 54.7629 | 81.5338 | 10.6264 | 203.0314 | 120.7809 | 224.3847 | 9.5209 | 58.3999 | 11.4984 | 113 | 12.834 | 84.1569 | 350.991 | 0
1303 | 887.3609 | 4.4524 | 63.8875 | 113.398 | 57.1296 | 8.5135 | 79.1109 | 8.2818 | 12.4623 | 73.7106 | 98.5961 | 21.8429 | 227.6857 | 164.4652 | 257.4427 | 12.8084 | 56.6175 | 11.4637 | 199 | 13.033 | 124.0828 | 393.1749 | 0
1304 | 962.8527 | 5.3168 | 83.4489 | 113.9627 | 53.2265 | 12.2214 | 96.1452 | 9.5648 | 15.3556 | 96.6223 | 139.2695 | 31.9855 | 263.7876 | 227.1346 | 368.3163 | 26.6288 | 60.6184 | 12.6586 | 263 | 15.1046 | 171.6106 | 458.1376 | 0
1305 | 1054.5023 | 4.6066 | 100.2828 | 120.1091 | 49.7218 | 15.5509 | 113.6173 | 10.1842 | 17.2588 | 97.0436 | 175.6311 | 29.8529 | 345.7514 | 272.9989 | 470.1292 | 34.7158 | 72.1021 | 17.4208 | 285 | 15.7725 | 209 | 527.0274 | 0.14703
1306 | 1138.6732 | 4.2397 | 107.5081 | 133.0936 | 46.781 | 18.3447 | 132.053 | 11.7082 | 18.3633 | 109.9089 | 194.2713 | 31.9758 | 409.4535 | 306.6495 | 531.8044 | 38.3825 | 99.2159 | 16.755 | 359 | 16.7224 | 238.3577 | 575.3925 | 0.18198
1307 | 1191.0288 | 4.143 | 106.5836 | 140.6415 | 47.6082 | 17.5589 | 126.0455 | 9.955 | 20.196 | 125.2956 | 192.7113 | 39.3918 | 434.2054 | 332.079 | 554.0783 | 41.1612 | 114.0511 | 17.1526 | 349 | 16.3029 | 247.4172 | 596.1105 | 0.18007
1308 | 1200.5403 | 4.3192 | 107.5494 | 139.6545 | 48.8405 | 16.3882 | 125.2761 | 8.3963 | 20.186 | 120.0701 | 184.3882 | 40.7716 | 442.2177 | 336.613 | 576.1944 | 41.6459 | 102.5145 | 17.3262 | 355 | 15.5118 | 250.4898 | 595.7845 | 0.22185
1309 | 1183.0731 | 3.8984 | 105.338 | 139.0829 | 47.7561 | 17.4184 | 131.7008 | 8.6687 | 19.5857 | 119.0267 | 179.4931 | 39.4211 | 435.1652 | 334.9827 | 572.2642 | 40.643 | 87.7382 | 17.6527 | 351 | 15.0468 | 238.3074 | 588.2539 | 0.25044
1310 | 1184.6731 | 3.8721 | 108.1101 | 139.0498 | 47.7954 | 17.381 | 134.8313 | 9.4472 | 18.8253 | 120.0688 | 187.3846 | 39.9135 | 434.9059 | 337.145 | 593.2924 | 39.8237 | 86.7768 | 18.3453 | 288 | 15.683 | 231.9326 | 594.5011 | 0.24853
1311 | 1187.4099 | 3.9611 | 109.2227 | 142.0565 | 46.7696 | 18.3556 | 130.9758 | 8.6653 | 18.5566 | 122.088 | 185.8243 | 39.8204 | 451.1862 | 338.2613 | 610.522 | 39.2163 | 85.483 | 18.9248 | 271 | 16.8753 | 238.5559 | 586.3699 | 0.14977
1312 | 1162.1658 | 4.0634 | 104.6868 | 142.5222 | 47.3621 | 17.7926 | 123.3766 | 8.0946 | 19.0551 | 116.628 | 186.8927 | 38.2839 | 446.0938 | 328.4462 | 590.3127 | 37.4342 | 83.8118 | 18.3412 | 295 | 15.9968 | 230.6398 | 570.766 | 0.13857
1313 | 1128.6603 | 4.6939 | 98.9383 | 135.811 | 51.9236 | 13.4592 | 123.5959 | 8.3813 | 20.1926 | 109.1769 | 184.5913 | 36.3069 | 418.4999 | 311.6754 | 531.1747 | 32.0318 | 81.1545 | 17.7005 | 251 | 14.9743 | 212.7098 | 505.4267 | 0.070814
1314 | 1082.9028 | 5.3433 | 97.7243 | 123.3103 | 56.1043 | 9.4875 | 107.3937 | 8.1596 | 20.3007 | 90.2199 | 172.2409 | 35.3888 | 364.7981 | 239.9521 | 453.3577 | 18.6784 | 75.8815 | 17.0595 | 219 | 14.6336 | 183.9799 | 418.3034 | 0
1315 | 1041.5894 | 5.1804 | 90.9114 | 113.3831 | 58.6422 | 7.0765 | 98.2068 | 8.2594 | 18.9193 | 70.3202 | 136.0094 | 29.5336 | 315.2883 | 187.2509 | 391.8378 | 12.3135 | 71.4002 | 17.5571 | 211 | 14.7085 | 168.1411 | 377.9171 | 0
1316 | 982.7979 | 4.585 | 79.1914 | 108.6364 | 59.8682 | 5.9118 | 85.9958 | 7.4324 | 13.0087 | 55.9601 | 107.9332 | 13.1447 | 280.9279 | 153.6974 | 351.1534 | 11.782 | 66.0317 | 17.3835 | 189 | 14.8859 | 151.9533 | 339.25 | 0
1317 | 936.9218 | 4.181 | 57.5811 | 107.0921 | 60.1515 | 5.6428 | 72.416 | 7.1045 | 9.6567 | 56.1248 | 97.6137 | 8.0894 | 252.0321 | 140.2468 | 305.7362 | 10.3206 | 59.0083 | 16.2807 | 171 | 14.9625 | 140.3616 | 319.5883 | 0
1318 | 907.4702 | 4.1509 | 50.55 | 103.8755 | 59.2704 | 6.4798 | 68.6095 | 6.9647 | 9.3507 | 55.3358 | 92.8591 | 8.444 | 215.318 | 132.7659 | 274.311 | 9.6147 | 55.1663 | 15.0388 | 157 | 14.6223 | 132.7423 | 306.2332 | 0
1319 | 881.1763 | 3.2419 | 50.4187 | 99.8398 | 59.9037 | 5.8782 | 74.6269 | 6.9674 | 7.8819 | 46.981 | 79.665 | 7.9949 | 193.9322 | 126.8684 | 261.2557 | 9.4636 | 54.257 | 14.1541 | 151 | 14.5653 | 120.5253 | 307.2719 | 0
1320 | 850.0789 | 2.0764 | 50.218 | 98.7233 | 60.076 | 5.7144 | 73.3372 | 6.9788 | 6.836 | 38.3612 | 72.9156 | 7.4279 | 176.8105 | 112.3696 | 243.8854 | 9.4299 | 54.383 | 13.6241 | 141 | 14.5865 | 94.482 | 304.2669 | 0
1321 | 843.5517 | 1.5812 | 50.0324 | 99.8789 | 60.106 | 5.6859 | 67.3207 | 7.2082 | 6.7113 | 36.0268 | 73.5577 | 7.5965 | 181.6715 | 101.1468 | 235.7891 | 9.4222 | 54.4106 | 13.4663 | 121 | 14.6548 | 85.172 | 300.3237 | 0
1322 | 831.4849 | 1.5005 | 49.8721 | 101.6325 | 59.3191 | 6.4335 | 66.9423 | 7.1673 | 6.5833 | 35.3844 | 72.6266 | 7.4498 | 184.6184 | 98.3192 | 224.5668 | 9.4412 | 54.3999 | 13.44 | 109 | 14.7215 | 83.5846 | 305.7884 | 0
1323 | 827.8741 | 1.5029 | 50.2484 | 102.4179 | 59.7935 | 5.9828 | 76.2276 | 7.0953 | 6.6107 | 35.3133 | 72.2864 | 7.5684 | 179.2791 | 99.4147 | 218.6328 | 9.4656 | 54.3049 | 13.7294 | 125 | 14.8375 | 82.124 | 304.5678 | 0
1324 | 820.519 | 1.3813 | 50.2173 | 103.298 | 59.3517 | 6.4025 | 72.9869 | 7.1598 | 6.4493 | 38.4933 | 73.057 | 7.4238 | 166.464 | 95.757 | 216.8897 | 9.4538 | 53.9903 | 13.3661 | 106 | 14.7895 | 81.8861 | 307.0431 | 0
1325 | 831.8047 | 1.6216 | 50.0391 | 101.5444 | 59.9079 | 5.8741 | 68.5898 | 7.2189 | 6.3971 | 49.0888 | 73.1618 | 7.3403 | 161.2088 | 102.1047 | 214.3668 | 9.3828 | 55.4486 | 12.4014 | 101 | 14.708 | 80.786 | 320.7344 | 0
1326 | 846.8466 | 2.8354 | 50.8985 | 100.4182 | 59.2623 | 6.4874 | 69.9923 | 6.935 | 7.8488 | 56.7116 | 74.2778 | 10.8012 | 172.6492 | 124.1623 | 224.7424 | 9.3767 | 57.9085 | 11.8723 | 117 | 14.651 | 85.8716 | 353.4495 | 0
1327 | 891.817 | 4.181 | 60.5274 | 106.8819 | 56.8169 | 8.8106 | 87.0443 | 6.7519 | 15.4894 | 74.8378 | 91.3771 | 21.5921 | 248.7284 | 175.4538 | 249.5607 | 12.403 | 55.9965 | 12.8483 | 178 | 15.1108 | 129.0362 | 398.7637 | 0
1328 | 971.0902 | 4.8072 | 78.1571 | 112.0751 | 51.4377 | 13.9208 | 102.5314 | 7.4358 | 18.3313 | 95.2343 | 129.9992 | 34.2098 | 299.7727 | 228.7822 | 342.5627 | 27.6492 | 60.343 | 13.7865 | 270 | 16.5893 | 178.6234 | 442.9089 | 0
1329 | 1051.4103 | 4.3743 | 94.072 | 122.4534 | 49.3008 | 15.9509 | 121.4427 | 8.743 | 19.97 | 94.5397 | 171.3575 | 40.9527 | 339.0034 | 283.225 | 452.5168 | 36.3749 | 68.1866 | 16.2226 | 332 | 15.5557 | 216.3745 | 494.1733 | 0.063963
1330 | 1118.3009 | 4.2949 | 103.281 | 142.5864 | 49.1504 | 16.0937 | 130.7528 | 9.5013 | 19.6867 | 110.8792 | 187.7072 | 43.4735 | 378.0444 | 319.7067 | 535.817 | 39.0181 | 78.364 | 16.7425 | 339 | 12.5858 | 244.1111 | 534.3085 | 0.10335
1331 | 1167.686 | 3.8732 | 103.8437 | 147.5157 | 48.4425 | 16.7662 | 134.1121 | 9.4027 | 19.9477 | 118.123 | 193.7096 | 44.7365 | 410.7881 | 347.6688 | 560.0317 | 39.9335 | 84.0691 | 16.6597 | 393 | 6.68 | 258.7225 | 564.9854 | 0.13472
1332 | 1176.6158 | 3.6642 | 108.4524 | 147.8526 | 47.1412 | 18.0025 | 132.938 | 9.4525 | 20.17 | 131.0269 | 193.6527 | 43.3433 | 423.4965 | 359.6966 | 581.354 | 40.5589 | 86.2327 | 16.4179 | 360 | 5.467 | 262.5761 | 575.2633 | 0.13326
1333 | 1165.642 | 5.6832 | 104.5169 | 144.5676 | 48.6925 | 16.5288 | 137.1235 | 9.6111 | 21.2497 | 114.5025 | 194.9928 | 39.7677 | 415.3854 | 351.4966 | 570.4921 | 41.741 | 86.1853 | 17.483 | 374 | 5.4155 | 262.4797 | 561.0888 | 0.14948
1334 | 1162.668 | 9.1188 | 105.1015 | 145.8525 | 49.8449 | 15.434 | 139.4905 | 9.6472 | 22.4247 | 105.6635 | 200.7227 | 39.1528 | 416.2729 | 354.1327 | 578.5411 | 40.9205 | 88.2824 | 18.1599 | 324 | 5.441 | 252.264 | 566.2556 | 0.17416
1335 | 1165.14 | 9.4286 | 107.7001 | 148.4784 | 50.8488 | 14.4802 | 129.5263 | 9.7085 | 21.8447 | 110.8108 | 199.6079 | 39.3663 | 425.1887 | 356.3957 | 578.0324 | 39.4659 | 88.3222 | 18.4053 | 307 | 5.4504 | 244.9677 | 565.8008 | 0.13381
1336 | 1166.5228 | 5.2559 | 107.1024 | 143.5648 | 48.7213 | 16.5014 | 132.7412 | 10.0877 | 19.2713 | 108.3179 | 197.0411 | 38.1646 | 412.9045 | 336.9919 | 573.5218 | 38.4939 | 87.419 | 19.0707 | 304 | 5.0205 | 235.3928 | 559.3782 | 0.077674
1337 | 1134.6228 | 4.8578 | 107.3793 | 133.84 | 50.4862 | 14.8248 | 126.9041 | 10.9453 | 17.3793 | 105.3226 | 199.2947 | 35.0634 | 390.9673 | 317.3409 | 530.1228 | 31.772 | 86.4293 | 19.3296 | 272 | 4.511 | 223.2333 | 512.7238 | 0.015193
1338 | 1054.6373 | 5.5747 | 99.4051 | 119.1485 | 56.4753 | 9.135 | 116.401 | 9.497 | 16.6233 | 97.0513 | 183.672 | 34.6518 | 347.5237 | 254.4314 | 428.04 | 17.2295 | 77.9598 | 17.6413 | 253 | 4.2198 | 201.5783 | 441.6543 | 0
1339 | 998.3782 | 4.8493 | 94.7872 | 114.0731 | 58.0885 | 7.6025 | 104.1957 | 7.6588 | 15.5 | 81.6707 | 146.1701 | 30.7624 | 309.7158 | 192.2187 | 387.7631 | 10.3466 | 70.5919 | 16.9875 | 233 | 4.1804 | 188.8238 | 392.1957 | 0
1340 | 955.1055 | 4.2321 | 84.7836 | 113.4782 | 59.6168 | 6.1507 | 81.4267 | 6.7058 | 12.0307 | 68.381 | 115.3293 | 19.793 | 276.6971 | 165.9492 | 365.0007 | 9.8069 | 63.9205 | 16.4809 | 204 | 4.0791 | 172.8255 | 348.9888 | 0
1341 | 915.1154 | 4.587 | 55.6962 | 107.6987 | 59.3242 | 6.4286 | 72.4579 | 6.7496 | 10.262 | 63.8792 | 106.4579 | 18.6473 | 233.1566 | 144.9237 | 299.7496 | 9.843 | 58.3178 | 15.7509 | 195 | 4.1706 | 163.1657 | 330.8166 | 0
1342 | 895.7127 | 4.0505 | 46.5524 | 102.6354 | 57.4972 | 8.1643 | 75.5455 | 6.8444 | 8.358 | 60.1789 | 98.0209 | 16.9074 | 205.2177 | 123.7869 | 254.5471 | 9.6549 | 56.1396 | 15.2517 | 168 | 4.1459 | 154.6321 | 315.5709 | 0
1343 | 869.4247 | 3.1547 | 46.2798 | 101.4651 | 59.4683 | 6.2917 | 77.4672 | 6.9279 | 7.1375 | 56.9173 | 81.3283 | 12.6981 | 190.0382 | 114.0141 | 249.213 | 9.7837 | 55.6217 | 14.7571 | 149 | 4.2131 | 145.3958 | 320.925 | 0
1344 | 835.3834 | 2.0616 | 45.5264 | 102.707 | 59.286 | 6.4649 | 73.8095 | 7.6075 | 6.7038 | 56.8204 | 73.2598 | 11.0843 | 178.6894 | 116.6949 | 249.1667 | 9.7257 | 54.9621 | 14.2316 | 137 | 4.1231 | 118.6725 | 318.3151 | 0
1345 | 832.9859 | 1.4849 | 44.9389 | 101.9263 | 59.8999 | 5.8817 | 72.0282 | 7.6133 | 6.692 | 49.3958 | 72.5141 | 11.3855 | 176.2707 | 112.1037 | 253.5576 | 9.7356 | 54.5761 | 13.3845 | 117 | 4.1079 | 105.9831 | 314.7203 | 0
1346 | 834.2865 | 1.4129 | 44.8645 | 100.5462 | 60.0527 | 5.7366 | 77.5829 | 7.4628 | 6.8011 | 44.1328 | 72.58 | 11.0266 | 174.2508 | 102.5863 | 248.9309 | 9.7327 | 54.5558 | 13.3304 | 119 | 4.1501 | 103.0919 | 307.5415 | 0
1347 | 823.2422 | 1.7226 | 44.6317 | 101.0287 | 59.352 | 6.4023 | 79.229 | 7.7306 | 6.9117 | 45.5889 | 72.9105 | 10.7487 | 163.7299 | 98.7324 | 243.202 | 9.6939 | 54.8049 | 13.1983 | 129 | 4.1679 | 102.4569 | 309.2479 | 0
1348 | 817.4302 | 1.4554 | 44.8073 | 101.1446 | 59.8888 | 5.8923 | 73.9835 | 7.9701 | 6.8153 | 49.7604 | 73.7073 | 10.6584 | 165.3811 | 97.9239 | 254.6035 | 9.8114 | 54.4623 | 13.0301 | 106 | 4.212 | 100.947 | 311.9296 | 0
1349 | 823.7674 | 2.1559 | 44.8012 | 99.6554 | 59.3156 | 6.4369 | 71.6186 | 7.9032 | 6.616 | 59.9386 | 73.7838 | 10.6059 | 166.9196 | 95.6374 | 235.3073 | 9.6489 | 55.4535 | 12.3089 | 102 | 4.1304 | 100.3526 | 328.7078 | 0
1350 | 837.6491 | 3.6307 | 53.2366 | 98.2531 | 59.8208 | 5.9569 | 78.3136 | 7.3631 | 7.9387 | 66.6491 | 73.7284 | 13.4938 | 169.9586 | 105.3901 | 224.9586 | 9.6494 | 58.4079 | 11.7689 | 116 | 4.05 | 105.2834 | 357.6147 | 0
1351 | 880.6969 | 4.9419 | 81.1551 | 104.7218 | 57.1016 | 8.5401 | 86.7966 | 7.2688 | 12.1759 | 81.9489 | 88.0268 | 21.7335 | 202.221 | 169.5428 | 255.9032 | 12.5513 | 56.6187 | 11.634 | 187 | 4.2682 | 148.3775 | 405.6292 | 0
1352 | 945.9645 | 4.7772 | 94.3337 | 111.4147 | 52.1922 | 13.204 | 106.1192 | 8.666 | 15.2188 | 96.9693 | 127.4761 | 34.4898 | 272.1537 | 225.5424 | 347.1878 | 22.2075 | 59.8312 | 12.3852 | 236 | 5.0222 | 198.9913 | 452.4571 | 0
1353 | 1033.3993 | 6.6807 | 103.9985 | 120.0398 | 51.174 | 14.1713 | 120.9326 | 9.2884 | 17.9769 | 94.0584 | 162.3731 | 35.7714 | 342.5226 | 270.8632 | 451.9217 | 28.3495 | 67.7436 | 15.4003 | 327 | 4.9463 | 227.6147 | 519.6035 | 0.16519
1354 | 1102.029 | 7.8075 | 106.4359 | 133.7653 | 50.9622 | 14.3726 | 133.6572 | 9.126 | 19.3678 | 100.4255 | 179.7717 | 36.1987 | 391.93 | 294.9649 | 524.4406 | 30.216 | 75.7208 | 16.2061 | 349 | 4.822 | 247.4337 | 573.9551 | 0.1196
1355 | 1144.4915 | 7.6821 | 106.8959 | 138.9627 | 51.1412 | 14.2025 | 135.7752 | 9.4926 | 21.1665 | 106.9773 | 194.9668 | 37.8666 | 411.3789 | 313.0421 | 556.6061 | 30.5587 | 81.57 | 17.2547 | 400 | 5.097 | 255.7782 | 586.9738 | 0.16735
1356 | 1158.412 | 7.6451 | 107.866 | 132.1553 | 51.8642 | 13.5156 | 130.1329 | 9.2097 | 21.7373 | 108.4367 | 192.5058 | 37.2761 | 418.5772 | 324.4457 | 565.3494 | 30.1239 | 82.4947 | 17.2343 | 328 | 4.2712 | 259.8836 | 594.9935 | 0.23369
1357 | 1148.5378 | 7.468 | 106.4914 | 133.4586 | 50.5929 | 14.7234 | 136.3199 | 8.472 | 21.9013 | 99.1204 | 185.9475 | 31.8335 | 412.097 | 312.4734 | 577.2545 | 29.7578 | 81.0282 | 17.0441 | 336 | 3.0388 | 253.7175 | 605.3216 | 0.28945
1358 | 1164.5494 | 6.9116 | 109.2992 | 140.0504 | 49.3547 | 15.8997 | 130.8059 | 8.5719 | 20.4121 | 96.6135 | 187.1065 | 32.043 | 415.9761 | 323.2379 | 568.3295 | 30.3279 | 85.3917 | 18.3215 | 329 | 2.5379 | 240.6948 | 620.2121 | 0.30913
1359 | 1162.3065 | 5.601 | 115.3025 | 138.1493 | 49.86 | 15.4196 | 118.6694 | 8.2632 | 18.3344 | 98.1372 | 190.5021 | 32.9564 | 421.1673 | 328.5161 | 574.7165 | 30.0137 | 97.4828 | 18.7939 | 305 | 3.0239 | 240.495 | 618.1718 | 0.26464
1360 | 1125.7026 | 4.5955 | 110.9712 | 134.634 | 50.0057 | 15.2812 | 123.9374 | 7.8595 | 17.6802 | 96.6746 | 188.1417 | 32.2358 | 416.4397 | 316.0234 | 555.6529 | 28.8164 | 95.153 | 17.8822 | 286 | 2.4087 | 241.2425 | 591.1127 | 0.16152
1361 | 1092.6903 | 3.9486 | 107.6349 | 132.8688 | 55.4784 | 10.0822 | 118.0949 | 7.8827 | 17.7407 | 89.5597 | 181.205 | 29.958 | 379.2712 | 294.3046 | 485.2705 | 19.1347 | 84.1738 | 17.1961 | 302 | 2.1196 | 221.353 | 516.1172 | 0.079302
1362 | 1025.9317 | 4.735 | 93.9196 | 121.7137 | 57.8884 | 7.7926 | 101.805 | 7.2927 | 18.7747 | 75.9408 | 165.7807 | 29.0502 | 328.7216 | 235.5726 | 413.6015 | 12.784 | 76.5412 | 15.8191 | 301 | 2.0642 | 199.2102 | 424.1646 | 0
1363 | 976.3075 | 4.4936 | 76.8353 | 109.8141 | 58.0296 | 7.6585 | 94.9556 | 7.1552 | 19.6167 | 59.8339 | 138.091 | 27.7251 | 289.4467 | 188.6162 | 361.1096 | 11.6577 | 71.2559 | 14.8473 | 247 | 2.0845 | 186.037 | 365.3114 | 0
1364 | 919.958 | 4.3022 | 71.2166 | 102.7551 | 58.906 | 6.826 | 76.4937 | 7.0996 | 15.346 | 55.1801 | 106.6048 | 14.227 | 246.9334 | 162.3071 | 314.5342 | 9.8963 | 61.8949 | 14.4431 | 235 | 2.1451 | 169.6693 | 328.8544 | 0
1365 | 868.8409 | 3.8546 | 70.0318 | 102.3459 | 59.047 | 6.692 | 70.3762 | 7.0954 | 11.9553 | 55.2803 | 84.799 | 8.1096 | 222.6131 | 146.4959 | 290.2444 | 9.1479 | 57.5043 | 13.7719 | 195 | 2.1035 | 158.5369 | 316.647 | 0
1366 | 844.0984 | 3.985 | 69.7044 | 101.0797 | 59.8902 | 5.8909 | 76.3403 | 7.0231 | 11.2367 | 55.2386 | 73.1506 | 7.7857 | 200.8622 | 128.2147 | 278.7837 | 9.1191 | 55.2196 | 12.9666 | 191 | 2.1442 | 144.2955 | 312.2124 | 0
1367 | 826.0663 | 3.2698 | 69.4761 | 99.7257 | 59.333 | 6.4203 | 77.5486 | 6.9621 | 10.3813 | 54.6075 | 67.9146 | 15.0343 | 179.2926 | 117.3642 | 264.8764 | 9.0154 | 53.9285 | 12.93 | 169 | 2.0862 | 131.5364 | 314.6036 | 0
1368 | 806.8233 | 2.1084 | 69.2491 | 99.8701 | 59.3307 | 6.4225 | 72.4794 | 7.0969 | 9.9445 | 53.5145 | 65.9782 | 12.5333 | 162.4989 | 110.276 | 248.8673 | 9.1491 | 53.4557 | 12.8634 | 167 | 2.1156 | 105.7762 | 316.5462 | 0
1369 | 808.488 | 1.6369 | 69.2417 | 99.8936 | 59.66 | 6.1097 | 72.5646 | 7.1121 | 9.0245 | 50.8371 | 65.7601 | 8.385 | 159.1595 | 107.6258 | 253.041 | 9.067 | 53.4172 | 12.7159 | 159 | 2.1673 | 96.4969 | 311.4225 | 0
1370 | 812.59 | 1.673 | 69.2283 | 99.9331 | 59.9994 | 5.7872 | 80.9212 | 7.1324 | 8.2243 | 49.9515 | 66.7589 | 7.3427 | 157.6812 | 106.1627 | 254.1894 | 9.1164 | 53.7596 | 12.5679 | 161 | 2.2544 | 96.0892 | 312.3801 | 0
1371 | 804.6902 | 1.6879 | 69.2125 | 100.4048 | 59.3111 | 6.4411 | 74.776 | 7.1388 | 8.2267 | 49.9235 | 66.426 | 7.3766 | 155.5949 | 104.2335 | 243.9024 | 9.1147 | 54.1026 | 12.0784 | 178 | 2.2961 | 94.8154 | 311.3746 | 0
1372 | 796.6727 | 1.5874 | 66.6627 | 100.5867 | 59.1415 | 6.6022 | 70.6239 | 7.2811 | 8.39 | 50.6746 | 66.7668 | 7.3866 | 155.2392 | 98.3016 | 247.1732 | 9.0744 | 54.0323 | 12.4966 | 145 | 2.2913 | 94.6213 | 309.2115 | 0
1373 | 793.9721 | 1.9807 | 63.0634 | 100.5569 | 59.8693 | 5.9108 | 72.9962 | 7.6033 | 8.3936 | 55.9411 | 66.8084 | 7.505 | 150.5377 | 95.8884 | 247.1266 | 9.0709 | 55.432 | 12.3663 | 133 | 2.2253 | 93.2763 | 309.0302 | 0
1374 | 789.432 | 2.8588 | 62.5083 | 100.6911 | 59.299 | 6.4526 | 79.6089 | 7.8322 | 9.5605 | 61.2383 | 66.8516 | 7.3644 | 148.37 | 102.5329 | 239.3503 | 9.1147 | 57.846 | 12.2222 | 129 | 2.1915 | 92.4484 | 308.9593 | 0
1375 | 807.6356 | 3.4093 | 64.3502 | 102.4536 | 59.874 | 5.9064 | 72.0984 | 7.9055 | 12.8672 | 64.5684 | 66.1145 | 6.9435 | 146.0947 | 98.7477 | 226.0095 | 8.9962 | 54.7882 | 12.0984 | 122 | 2.1785 | 93.1073 | 322.1326 | 0
1376 | 821.834 | 2.8165 | 70.1158 | 100.7346 | 59.2924 | 6.4588 | 67.2172 | 7.5776 | 14.01 | 60.2135 | 69.2692 | 6.8828 | 161.159 | 91.1138 | 217.508 | 8.6943 | 52.3706 | 11.7952 | 123 | 2.3482 | 97.7634 | 330.1777 | 0
1377 | 834.0737 | 1.5956 | 77.0503 | 98.2632 | 58.2931 | 7.4082 | 70.3141 | 7.0636 | 14.6 | 57.4505 | 104.3846 | 10.675 | 168.7026 | 90.2248 | 222.1835 | 8.5094 | 52.9699 | 12.2192 | 128 | 2.2785 | 102.0628 | 327.7173 | 0.15703
1378 | 862.3312 | 1.5011 | 81.911 | 97.6467 | 59.6739 | 6.0964 | 81.4542 | 6.6536 | 13.5973 | 71.7365 | 133.8271 | 6.4606 | 189.4716 | 101.9771 | 227.0381 | 8.5609 | 54.0288 | 12.6024 | 139 | 2.1131 | 125.7838 | 330.4224 | 0.16234
1379 | 867.6379 | 1.8515 | 85.1403 | 97.5521 | 59.3415 | 6.4122 | 85.1185 | 5.9233 | 13.0811 | 77.741 | 145.6998 | 4.4848 | 213.7096 | 115.0219 | 226.5935 | 8.4053 | 57.0934 | 12.7374 | 169 | 2.1979 | 136.7057 | 331.3893 | 0.15946
1380 | 877.0245 | 2.1761 | 84.3143 | 97.0547 | 59.8697 | 5.9104 | 78.7996 | 5.224 | 14.2733 | 80.9345 | 138.7673 | 4.5133 | 223.5663 | 120.1368 | 237.8454 | 7.9334 | 58.6505 | 13.2466 | 192 | 2.1773 | 138.3479 | 330.1102 | 0.15861
1381 | 887.1546 | 2.4208 | 83.6281 | 97.1657 | 59.314 | 6.4383 | 89.6099 | 5.5574 | 15.5362 | 78.6695 | 106.5072 | 4.8105 | 224.4218 | 129.5079 | 250.9132 | 7.6899 | 57.8023 | 13.4463 | 195 | 2.2447 | 139.5995 | 329.2402 | 0.16864
1382 | 889.8043 | 2.0795 | 74.8892 | 98.6183 | 59.8685 | 5.9115 | 93.4108 | 7.972 | 15.798 | 75.999 | 93.9031 | 5.1177 | 222.2847 | 130.9677 | 246.8188 | 7.716 | 57.1284 | 13.352 | 196 | 2.1799 | 137.6224 | 331.6166 | 0.15052
1383 | 890.9155 | 2.0393 | 59.3211 | 97.851 | 59.3441 | 6.4097 | 76.0215 | 7.5813 | 16.0907 | 72.6463 | 97.1425 | 5.8641 | 218.6872 | 131.2172 | 261.713 | 7.5932 | 56.7258 | 13.5055 | 210 | 2.0655 | 133.7998 | 321.6548 | 0.11692
1384 | 891.4485 | 1.9987 | 54.659 | 97.018 | 59.8485 | 5.9305 | 72.9751 | 6.4672 | 15.7967 | 61.7608 | 97.5639 | 8.6876 | 218.634 | 123.5572 | 296.1707 | 7.58 | 56.6364 | 13.3419 | 207 | 1.9937 | 126.9852 | 308.866 | 0.15775
1385 | 887.6729 | 1.6855 | 54.5616 | 96.1139 | 60.0616 | 5.7281 | 80.5801 | 6.3848 | 15.2027 | 48.0416 | 97.0902 | 10.1107 | 226.6547 | 126.2752 | 278.6788 | 8.0184 | 58.0579 | 13.467 | 217 | 2.0351 | 109.7123 | 310.8712 | 0.087999
1386 | 875.4133 | 2.9857 | 54.2339 | 97.1669 | 59.3196 | 6.433 | 73.7419 | 6.4916 | 14.38 | 44.2778 | 95.4188 | 9.9803 | 227.0262 | 129.0714 | 269.7541 | 8.5055 | 59.7156 | 14.178 | 209 | 2.207 | 103.4091 | 318.819 | 0
1387 | 860.9309 | 5.5777 | 54.8092 | 98.8181 | 56.8012 | 8.8254 | 71.0474 | 6.8457 | 12.974 | 46.8704 | 86.8924 | 8.6172 | 217.6411 | 130.9813 | 267.9215 | 8.8656 | 59.6573 | 15.1153 | 198 | 2.3388 | 110.7632 | 325.1688 | 0
1388 | 850.3991 | 8.458 | 55.7519 | 99.0416 | 59.1486 | 6.5954 | 78.1188 | 6.9093 | 9.0813 | 47.316 | 78.8829 | 7.9792 | 210.1036 | 127.6258 | 263.419 | 9.0918 | 58.492 | 14.9031 | 193 | 2.3545 | 111.5537 | 325.2675 | 0
1389 | 835.4337 | 7.324 | 54.6336 | 99.5851 | 59.3303 | 6.4228 | 74.0122 | 7.151 | 7.4093 | 45.7176 | 76.381 | 8.0016 | 205.11 | 119.8727 | 250.4137 | 9.0296 | 57.9641 | 14.7643 | 190 | 2.342 | 103.0882 | 326.5543 | 0
1390 | 821.7509 | 7.4616 | 54.1226 | 101.822 | 59.0865 | 6.6545 | 67.3126 | 7.4431 | 6.82 | 46.0827 | 73.9571 | 7.6339 | 192.2227 | 114.6319 | 243.0712 | 9.0265 | 55.6063 | 13.9325 | 188 | 2.168 | 100.1881 | 322.2584 | 0
1391 | 801.4217 | 4.5374 | 54.3703 | 103.6498 | 59.8419 | 5.9368 | 68.8547 | 7.216 | 8.046 | 47.272 | 71.468 | 7.4718 | 181.5612 | 108.7611 | 251.1263 | 8.9907 | 54.3552 | 13.5233 | 155 | 2.1806 | 100.6052 | 324.4539 | 0
1392 | 781.4868 | 2.0931 | 54.0192 | 101.7184 | 60.0704 | 5.7198 | 75.9944 | 6.9808 | 12.0847 | 46.2875 | 70.2272 | 7.4509 | 177.3337 | 110.7122 | 260.9488 | 8.9966 | 54.1265 | 13.6852 | 137 | 2.2613 | 97.0503 | 335.6267 | 0
1393 | 799.3714 | 1.6058 | 53.9286 | 100.9675 | 59.3824 | 6.3734 | 71.2657 | 6.929 | 13.1443 | 42.4842 | 70.3184 | 7.648 | 164.8471 | 106.3399 | 257.5887 | 9.0839 | 54.2619 | 13.4462 | 134 | 2.265 | 94.5503 | 350.3197 | 0
1394 | 784.9263 | 1.7113 | 53.8201 | 100.3853 | 58.2936 | 7.4077 | 68.1588 | 7.1315 | 13.2339 | 39.6546 | 68.7574 | 7.5389 | 158.3496 | 99.8376 | 248.7765 | 9.0065 | 54.5777 | 12.8137 | 144 | 2.521 | 93.0236 | 339.6779 | 0
1395 | 772.9757 | 1.4738 | 53.6738 | 100.1806 | 54.9966 | 10.5399 | 75.285 | 7.1037 | 13.1098 | 40.166 | 68.1241 | 7.4658 | 153.6127 | 94.9437 | 238.5386 | 9.0018 | 54.4192 | 12.1502 | 152 | 3.857 | 91.9811 | 325.4946 | 0
1396 | 760.8571 | 1.3879 | 53.771 | 99.7601 | 55.5299 | 10.0333 | 74.2348 | 6.9944 | 13.018 | 40.5246 | 68.9836 | 7.47 | 151.7287 | 93.8707 | 225.7779 | 9.0004 | 54.102 | 11.5434 | 127 | 3.3891 | 91.3846 | 343.32 | 0
1397 | 746.0773 | 1.654 | 53.8978 | 99.7115 | 56.1788 | 9.4168 | 69.1198 | 6.8996 | 13.3033 | 38.5726 | 69.234 | 7.4534 | 151.1299 | 94.6876 | 220.2922 | 8.9438 | 55.5458 | 11.3687 | 122 | 2.742 | 90.1506 | 346.3482 | 0
1398 | 744.2248 | 2.981 | 53.8036 | 98.3224 | 59.206 | 6.541 | 69.4826 | 6.9428 | 13.124 | 39.2837 | 69.3975 | 7.4401 | 150.8542 | 94.9272 | 220.764 | 8.9875 | 58.0524 | 11.3761 | 119 | 2.2729 | 89.914 | 336.0101 | 0
1399 | 752.3586 | 3.3236 | 53.5547 | 99.4456 | 60.0965 | 5.695 | 76.1634 | 7.0501 | 12.9687 | 40.0612 | 68.5152 | 7.2707 | 148.4745 | 103.0833 | 218.2273 | 8.8999 | 55.1405 | 11.3744 | 119 | 2.2312 | 90.0477 | 327.0964 | 0
1400 | 760.5499 | 2.7069 | 54.0122 | 98.5741 | 59.3196 | 6.433 | 68.0726 | 6.7714 | 12.466 | 34.9009 | 65.7556 | 5.2814 | 156.8321 | 94.9027 | 216.2079 | 8.6695 | 53.3839 | 11.601 | 118 | 2.1651 | 89.073 | 312.6102 | 0
1401 | 765.8945 | 1.5449 | 53.8785 | 100.3229 | 59.0662 | 6.6737 | 64.5037 | 6.3392 | 12.3487 | 41.5215 | 67.6903 | 4.5776 | 162.0738 | 93.2822 | 221.0552 | 8.5529 | 53.3718 | 12.235 | 121 | 2.0983 | 90.4548 | 318.6877 | 0.020065
1402 | 779.4401 | 1.4599 | 53.7747 | 101.0327 | 56.0152 | 9.5721 | 69.4748 | 5.8778 | 12.3113 | 60.5777 | 72.6769 | 4.5404 | 168.4519 | 97.1136 | 218.1138 | 8.5001 | 53.4036 | 12.4326 | 149 | 2.066 | 93.1944 | 321.0993 | 0.071966
1403 | 810.5572 | 1.9129 | 53.9524 | 101.2704 | 58.1993 | 7.4973 | 75.9239 | 5.3728 | 13.0013 | 73.0559 | 87.4775 | 4.7653 | 187.6901 | 111.3875 | 210.5861 | 8.272 | 54.2002 | 12.4355 | 174 | 2.0247 | 91.6283 | 321.7612 | 0.045071
1404 | 836.063 | 1.7096 | 53.9231 | 102.4626 | 58.2545 | 7.4449 | 69.9269 | 5.0196 | 13.5313 | 76.2413 | 97.3201 | 4.6203 | 203.1498 | 128.3908 | 220.0307 | 7.934 | 55.5975 | 12.5198 | 192 | 2.0381 | 89.5943 | 319.3671 | 0.10914
1405 | 833.0991 | 1.9812 | 53.9016 | 100.7417 | 59.6597 | 6.1099 | 66.6541 | 5.1358 | 13.7327 | 72.0659 | 93.4899 | 4.8118 | 209.5449 | 133.6485 | 233.9794 | 8.0028 | 55.8193 | 12.6831 | 204 | 2.064 | 89.7703 | 318.2054 | 0.092241
1406 | 835.6926 | 1.9484 | 54.5965 | 98.7454 | 59.3301 | 6.423 | 74.9215 | 5.6945 | 14.21 | 69.5315 | 89.8916 | 4.6531 | 215.4802 | 131.1637 | 250.082 | 7.9998 | 55.3512 | 12.7215 | 184 | 2.073 | 89.9248 | 324.7998 | 0.13397
1407 | 837.4602 | 1.8926 | 54.2438 | 99.7103 | 59.8809 | 5.8998 | 83.5642 | 5.6068 | 13.7833 | 66.3232 | 92.5206 | 5.9953 | 220.817 | 130.5667 | 260.9645 | 7.6404 | 54.4845 | 12.849 | 205 | 2.0905 | 92.5887 | 325.913 | 0.15784
1408 | 841.9032 | 1.5652 | 53.9601 | 101.022 | 58.5263 | 7.1866 | 82.5873 | 5.4323 | 14.2153 | 58.74 | 91.6882 | 8.0172 | 217.4915 | 124.3187 | 272.4335 | 7.6085 | 54.2246 | 12.944 | 181 | 2.1164 | 93.3747 | 304.9741 | 0.11262
1409 | 844.2145 | 1.8708 | 53.8035 | 103.2153 | 56.5435 | 9.0703 | 74.1811 | 5.9041 | 14.6187 | 43.3324 | 89.8695 | 5.8277 | 212.7752 | 118.3242 | 270.0315 | 7.9751 | 53.6517 | 13.1142 | 171 | 2.1202 | 95.625 | 300.117 | 0.055862
1410 | 838.2222 | 4.4755 | 53.6314 | 103.3298 | 57.6914 | 7.9798 | 79.0153 | 6.5231 | 14.526 | 38.7959 | 90.7882 | 5.2499 | 213.999 | 119.5498 | 276.0011 | 8.3794 | 53.7974 | 13.8135 | 152 | 2.2472 | 98.4954 | 313.1668 | 0
1411 | 832.2166 | 4.1956 | 53.4803 | 102.7623 | 58.778 | 6.9475 | 72.3772 | 7.1777 | 13.282 | 43.8603 | 94.1705 | 6.8656 | 204.5648 | 127.1239 | 267.175 | 8.9108 | 55.2948 | 14.1981 | 141 | 2.2722 | 101.2437 | 320.0793 | 0
1412 | 817.5226 | 3.9329 | 53.4556 | 101.8118 | 59.0964 | 6.6451 | 65.7161 | 7.1245 | 8.626 | 44.3097 | 89.7668 | 7.3948 | 190.9238 | 119.8885 | 260.3897 | 9.0198 | 54.5647 | 13.7777 | 133 | 2.2731 | 99.8172 | 317.5066 | 0
1413 | 795.4452 | 3.8227 | 53.6871 | 102.7458 | 59.8709 | 5.9093 | 69.3982 | 6.9763 | 6.9287 | 42.6101 | 77.4696 | 7.4413 | 180.1601 | 113.3019 | 251.5995 | 9.039 | 55.4071 | 13.3109 | 121 | 2.3625 | 100.4761 | 320.584 | 0
1414 | 781.3527 | 3.5538 | 53.6845 | 102.7499 | 59.3199 | 6.4328 | 75.3671 | 7.027 | 6.8627 | 42.522 | 72.4247 | 7.4604 | 168.9157 | 107.0616 | 228.8796 | 9.0876 | 54.9286 | 13.1707 | 121 | 2.4579 | 100.7425 | 320.9789 | 0
1415 | 765.6299 | 2.9623 | 53.5034 | 101.2331 | 59.1461 | 6.5978 | 70.7315 | 6.9533 | 6.816 | 41.1581 | 71.0912 | 7.4543 | 162.8754 | 98.831 | 216.9403 | 8.9944 | 54.0291 | 13.3981 | 118 | 2.4047 | 94.7623 | 312.639 | 0
1416 | 755.7116 | 1.8129 | 53.5439 | 100.1877 | 59.8367 | 5.9418 | 67.6804 | 6.9224 | 6.7267 | 40.2386 | 68.4899 | 7.6077 | 150.6771 | 94.219 | 218.413 | 9.0653 | 54.1162 | 12.3317 | 107 | 2.2923 | 91.7981 | 310.1628 | 0
1417 | 756.7779 | 1.3369 | 53.4224 | 100.007 | 59.2778 | 6.4728 | 75.056 | 7.0636 | 6.7807 | 39.8268 | 66.3359 | 7.4286 | 150.399 | 93.7854 | 226.2084 | 8.9103 | 53.5168 | 11.7729 | 105 | 2.2389 | 91.9708 | 307.0031 | 0
1418 | 749.4405 | 1.2919 | 53.4522 | 99.2155 | 59.8805 | 5.9001 | 76.1649 | 7.4971 | 7.1107 | 38.5468 | 64.804 | 7.4128 | 150.6173 | 94.5147 | 225.0327 | 9.0287 | 53.1707 | 11.7173 | 106 | 2.2719 | 91.5509 | 307.5555 | 0
1419 | 745.9099 | 1.2195 | 53.465 | 98.8674 | 60.1141 | 5.6783 | 69.7262 | 7.5818 | 7.0293 | 38.3498 | 64.6119 | 7.7553 | 150.277 | 100.1211 | 218.9848 | 9.0781 | 53.0999 | 11.689 | 123 | 2.275 | 93.8198 | 309.738 | 0
1420 | 744.2551 | 1.3222 | 53.4076 | 98.695 | 59.3402 | 6.4134 | 67.8347 | 7.4621 | 6.9967 | 41.0081 | 65.3096 | 7.8048 | 149.9914 | 102.1331 | 217.7999 | 8.953 | 52.8852 | 11.6953 | 102 | 2.2361 | 96.4672 | 313.8373 | 0
1421 | 750.107 | 1.7349 | 53.815 | 100.8147 | 59.849 | 5.9301 | 74.841 | 7.4675 | 6.8707 | 51.8045 | 65.5865 | 7.8331 | 159.6382 | 97.9603 | 216.2486 | 9.0202 | 54.5593 | 11.6901 | 98 | 2.2096 | 94.593 | 338.3668 | 0
1422 | 762.0623 | 3.0264 | 54.4774 | 100.3677 | 59.269 | 6.4811 | 74.8622 | 7.5701 | 8.1547 | 57.827 | 66.109 | 9.1707 | 169.0114 | 101.9201 | 222.3398 | 8.8818 | 57.1381 | 11.8097 | 101 | 2.1728 | 96.6498 | 357.1963 | 0
1423 | 803.103 | 4.8191 | 67.9476 | 108.5098 | 56.7908 | 8.8354 | 75.8336 | 8.1455 | 15.57 | 76.1381 | 91.2044 | 18.626 | 197.2506 | 174.976 | 253.7823 | 12.1987 | 55.0548 | 12.6038 | 177 | 2.3888 | 147.1635 | 423.1017 | 0
1424 | 871.1452 | 5.7354 | 89.6736 | 113.2433 | 52.9899 | 12.4463 | 97.3084 | 8.3006 | 19.674 | 105.4645 | 126.2339 | 32.7109 | 285.8408 | 223.3027 | 336.2078 | 25.256 | 58.4646 | 13.131 | 280 | 3.8397 | 199.14 | 470.9899 | 0.0079679
1425 | 963.5573 | 5.0603 | 103.6642 | 120.3776 | 48.9848 | 16.2511 | 124.4707 | 8.6573 | 19.942 | 117.5203 | 151.519 | 40.1315 | 356.8739 | 272.7707 | 464.2851 | 34.748 | 67.8345 | 16.6959 | 326 | 4.4997 | 233.4295 | 533.1061 | 0.018212
1426 | 1046.1541 | 6.7451 | 111.0345 | 131.6888 | 47.402 | 17.7547 | 133.1942 | 8.6716 | 22.1913 | 118.2945 | 169.8269 | 41.7337 | 417.2406 | 313.6236 | 561.8091 | 39.2127 | 76.8929 | 18.0607 | 322 | 4.2751 | 252.7443 | 581.855 | 0.030952
1427 | 1097.6888 | 5.3137 | 111.1189 | 141.3502 | 48.7717 | 16.4535 | 133.389 | 8.5278 | 25.4995 | 120.4212 | 172.0634 | 42.9518 | 442.9665 | 344.9484 | 604.3325 | 41.2425 | 85.4882 | 18.6147 | 336 | 4.5474 | 249.5689 | 603.5952 | 0.042435
1428 | 1118.5431 | 3.9066 | 112.7506 | 136.5262 | 49.7235 | 15.5493 | 143.1414 | 8.535 | 24.8959 | 118.5112 | 171.7267 | 45.3626 | 446.9539 | 358.7826 | 618.029 | 39.4638 | 85.6733 | 18.8119 | 310 | 5.7127 | 251.197 | 613.4276 | 0.046826
1429 | 1101.8799 | 3.9884 | 113.6868 | 138.2396 | 48.4743 | 16.7361 | 137.5637 | 9.1486 | 21.4854 | 116.2974 | 173.8888 | 43.8462 | 444.019 | 348.4659 | 609.0509 | 41.0642 | 81.9495 | 19.413 | 351 | 6.8038 | 243.1697 | 616.1706 | 0.067353
1430 | 1128.1382 | 3.8623 | 114.3417 | 141.7492 | 48.8687 | 16.3614 | 137.4223 | 10.4912 | 23.3567 | 112.4574 | 179.5792 | 43.4482 | 432.443 | 361.9812 | 604.3415 | 42.427 | 82.9979 | 20.0562 | 291 | 5.0081 | 246.9592 | 615.5473 | 0.12362
1431 | 1147.7392 | 3.9388 | 114.5977 | 140.0764 | 49.9473 | 15.3367 | 141.8057 | 9.5861 | 23.5667 | 112.5419 | 185.9281 | 45.1285 | 442.0072 | 361.2021 | 585.0464 | 41.8407 | 82.919 | 20.2157 | 275 | 4.1399 | 254.9549 | 603.1642 | 0.13327
1432 | 1124.7278 | 4.3714 | 113.0599 | 139.3054 | 49.2544 | 15.9949 | 130.1437 | 8.6069 | 19.8427 | 104.7787 | 186.5563 | 42.0761 | 443.4752 | 344.4564 | 565.2773 | 38.5031 | 81.9653 | 20.1146 | 261 | 3.3176 | 246.0221 | 581.1026 | 0.15008
1433 | 1077.8051 | 4.4372 | 109.149 | 132.346 | 54.6075 | 10.9095 | 127.5468 | 9.0474 | 17.0708 | 99.3267 | 183.6639 | 39.4384 | 399.9721 | 315.3895 | 512.8009 | 31.16 | 81.4526 | 19.9204 | 218 | 1.6767 | 229.8888 | 524.1998 | 0.088165
1434 | 1034.2048 | 5.4234 | 101.797 | 128.7029 | 57.6088 | 8.0583 | 117.6526 | 8.8554 | 16.4641 | 91.8949 | 174.0891 | 37.9374 | 363.4462 | 237.1707 | 433.2253 | 18.1594 | 79.7151 | 19.0924 | 205 | 0.53606 | 210.8671 | 437.2487 | 0
1435 | 996.6527 | 5.8525 | 98.1538 | 122.3494 | 58.0397 | 7.6489 | 94.1784 | 8.19 | 16.3458 | 77.1449 | 142.6842 | 32.4348 | 320.6929 | 175.8389 | 383.9548 | 12.2183 | 73.3767 | 17.552 | 204 | 0.3241 | 193.6769 | 394.2925 | 0
1436 | 930.8584 | 5.2134 | 87.2454 | 113.3822 | 58.8878 | 6.8433 | 79.3635 | 7.5994 | 15.3053 | 56.6713 | 113.2631 | 14.6186 | 269.5772 | 153.0466 | 350.1116 | 11.453 | 65.8877 | 16.1632 | 195 | 0.24723 | 171.0748 | 362.8011 | 0
1437 | 889.4765 | 4.55 | 58.2192 | 107.406 | 58.2929 | 7.4084 | 81.0235 | 7.8112 | 11.5887 | 48.2689 | 102.9835 | 8.1498 | 236.1261 | 138.9236 | 307.3531 | 10.5917 | 61.0118 | 14.9438 | 182 | 0.38343 | 162.0622 | 346.0516 | 0
1438 | 838.911 | 4.1651 | 48.185 | 104.3956 | 58.8801 | 6.8505 | 74.1315 | 8.2715 | 14.242 | 46.46 | 97.5466 | 7.7661 | 214.0654 | 124.7888 | 294.2332 | 9.7677 | 57.1385 | 13.6801 | 164 | 0.30438 | 154.0013 | 336.9795 | 0
1439 | 802.6483 | 3.8078 | 48.1025 | 100.2729 | 59.1216 | 6.6211 | 68.4012 | 8.7229 | 12.8927 | 41.0331 | 81.7995 | 7.7158 | 203.6773 | 113.6414 | 273.3554 | 9.3108 | 55.0578 | 13.2782 | 128 | 0.19613 | 140.7608 | 327.4124 | 0
1440 | 784.7082 | 2.6279 | 47.9765 | 98.8066 | 59.0741 | 6.6662 | 69.0858 | 8.8702 | 8.1207 | 38.4154 | 74.5684 | 7.6272 | 179.2762 | 114.5581 | 254.5284 | 9.329 | 54.5858 | 13.1851 | 114 | 0.28291 | 116.2636 | 329.0266 | 0
1441 | 790.9281 | 5.9807 | 47.9472 | 99.4132 | 65.2204 | 6.7042 | 75.5785 | 7.9861 | 6.3833 | 38.6402 | 75.0535 | 7.4729 | 167.4134 | 108.7824 | 245.6335 | 9.3996 | 54.196 | 12.4339 | 112 | 0.30175 | 108.6832 | 325.629 | 0
1442 | 782.7708 | 3.3121 | 46.3729 | 99.4457 | 65.3155 | 6.6138 | 73.1402 | 7.8142 | 6.2573 | 36.8482 | 77.2745 | 7.4489 | 174.6258 | 101.5012 | 252.8416 | 9.2143 | 54.2381 | 12.4921 | 105 | 0.32324 | 105.973 | 321.586 | 0
1443 | 773.9163 | 1.6177 | 42.5872 | 100.8761 | 65.2614 | 6.6652 | 70.7179 | 8.4891 | 6.6633 | 35.971 | 80.2673 | 7.4003 | 162.8659 | 96.8988 | 253.6633 | 9.3725 | 54.0772 | 13.1454 | 120 | 0.29494 | 103.9995 | 320.7701 | 0
1444 | 769.4949 | 1.3942 | 41.4898 | 100.6607 | 65.2651 | 6.6617 | 71.7752 | 9.5752 | 6.766 | 39.5667 | 82.0943 | 7.3762 | 153.9682 | 94.8427 | 238.2532 | 9.3272 | 53.9807 | 12.8661 | 103 | 0.31726 | 103.3602 | 323.4346 | 0
1445 | 771.9705 | 1.6079 | 41.4601 | 100.3805 | 65.2856 | 6.6423 | 76.2391 | 8.8122 | 6.8087 | 50.2732 | 80.5137 | 7.3598 | 153.361 | 94.2663 | 228.9192 | 9.3234 | 55.3584 | 12.6836 | 101 | 0.23584 | 103.2567 | 351.5236 | 0
1446 | 787.0429 | 2.7997 | 43.9383 | 102.8994 | 65.2815 | 6.6461 | 71.3572 | 7.6054 | 6.764 | 57.0094 | 76.6863 | 9.6869 | 166.8806 | 109.8372 | 232.9179 | 9.3863 | 57.9423 | 12.6763 | 117 | 0.19733 | 107.6817 | 381.5006 | 0
1447 | 823.5236 | 4.6021 | 61.7868 | 109.4114 | 62.9816 | 8.831 | 76.5054 | 7.2614 | 7.972 | 73.0331 | 89.4326 | 21.0524 | 205.007 | 164.9191 | 252.6309 | 12.4257 | 55.2093 | 12.6363 | 173 | 0.57844 | 153.0127 | 431.3502 | 0
1448 | 891.8194 | 6.0814 | 84.665 | 110.9896 | 58.5003 | 13.0882 | 111.655 | 8.4204 | 13.5771 | 96.5513 | 128.2336 | 34.3487 | 266.9499 | 243.2583 | 350.6578 | 26.0659 | 59.2996 | 12.9773 | 240 | 4.0362 | 185.9651 | 489.2568 | 0.042452
1449 | 985.2934 | 7.4371 | 98.4167 | 121.1526 | 56.4204 | 15.0642 | 141.4799 | 10.9134 | 17.6135 | 105.569 | 167.3493 | 37.6242 | 333.52 | 285.7038 | 476.9815 | 35.1945 | 70.8145 | 16.3017 | 295 | 5.4748 | 211.4391 | 553.5125 | 0.079161
1450 | 1090.4105 | 7.7974 | 108.1463 | 135.846 | 57.1006 | 14.4179 | 138.6709 | 11.9241 | 20.3752 | 118.8429 | 185.3553 | 41.4726 | 385.5574 | 316.7431 | 572.069 | 38.4126 | 81.4884 | 17.371 | 347 | 8.0949 | 238.7187 | 594.1069 | 0.069322
1451 | 1155.0463 | 7.4681 | 107.2846 | 140.3727 | 55.0074 | 16.4065 | 134.4379 | 11.2486 | 23.6287 | 119.3377 | 186.9053 | 45.7146 | 410.946 | 333.8683 | 598.1306 | 39.3034 | 86.307 | 18.4667 | 352 | 7.3486 | 248.5613 | 600.3002 | 0.1537
1452 | 1195.6058 | 7.7512 | 108.3216 | 139.3776 | 55.7628 | 15.6889 | 143.469 | 10.0826 | 23.7895 | 117.4421 | 191.6247 | 42.6758 | 420.2048 | 355.4953 | 612.0098 | 38.9174 | 87.0981 | 18.9172 | 346 | 5.9022 | 243.9883 | 608.6687 | 0.15018
1453 | 1177.9921 | 7.9785 | 110.9974 | 139.5921 | 56.1734 | 15.2988 | 144.2764 | 11.0171 | 21.5293 | 117.1833 | 185.2889 | 40.0414 | 424.8122 | 354.1363 | 605.2758 | 40.9315 | 84.6592 | 19.1586 | 372 | 8.8359 | 240.0396 | 623.087 | 0.11169
1454 | 1175.2732 | 7.1088 | 107.6267 | 142.407 | 57.5869 | 13.956 | 136.6127 | 10.9891 | 18.1679 | 116.9596 | 190.6973 | 44.2702 | 438.0543 | 346.2181 | 612.2771 | 43.4744 | 83.5042 | 19.7519 | 325 | 5.6642 | 241.6333 | 633.98 | 0.14699
1455 | 1169.2921 | 5.2107 | 109.8295 | 144.2855 | 58.5422 | 13.0484 | 139.109 | 11.0554 | 16.9758 | 117.452 | 193.6361 | 42.5325 | 443.088 | 338.5453 | 598.6581 | 44.3587 | 84.021 | 19.4575 | 313 | 8.8614 | 240.8742 | 624.7883 | 0.10385
1456 | 1151.5895 | 4.2397 | 109.725 | 143.8227 | 55.1985 | 16.2249 | 135.9862 | 10.9677 | 15.6551 | 121.8103 | 193.5171 | 38.3614 | 431.5545 | 332.7295 | 592.7276 | 41.7664 | 83.8438 | 19.0495 | 280 | 6.2505 | 237.039 | 605.431 | 0.077882
1457 | 1121.7988 | 4.4811 | 107.2908 | 138.067 | 58.905 | 12.7038 | 128.1443 | 10.1632 | 15.8893 | 116.7497 | 182.7911 | 34.8059 | 396.3454 | 313.5031 | 548.261 | 34.5268 | 83.2188 | 18.4868 | 250 | 4.6412 | 223.0074 | 534.236 | 0.009715
1458 | 1070.3216 | 6.0593 | 100.6813 | 123.7379 | 63.4661 | 8.3708 | 127.3802 | 8.3499 | 18.8673 | 90.8492 | 168.8734 | 31.7638 | 359.0522 | 252.8153 | 445.9697 | 19.9688 | 76.5779 | 17.816 | 217 | 6.6047 | 201.4215 | 446.4889 | 0
1459 | 1001.1193 | 10.6212 | 96.9478 | 116.63 | 64.1961 | 7.6772 | 107.54 | 7.3414 | 20.1447 | 64.0639 | 141.1388 | 27.6807 | 313.1378 | 207.7166 | 386.6823 | 13.0708 | 70.9906 | 17.0389 | 220 | 3.4569 | 191.4895 | 406.5683 | 0
1460 | 944.8617 | 11.4694 | 90.6067 | 112.7022 | 65.8451 | 6.1107 | 87.4059 | 6.8697 | 12.9109 | 50.6746 | 111.5082 | 14.186 | 273.1933 | 181.6766 | 340.4663 | 12.6995 | 65.7987 | 16.6182 | 192 | 0.83948 | 176.8185 | 362.2511 | 0
1461 | 904.5857 | 6.5083 | 59.7656 | 108.9572 | 65.5062 | 6.4326 | 83.2538 | 6.8027 | 9.0378 | 48.5946 | 101.6215 | 8.6833 | 243.4567 | 164.533 | 298.0066 | 11.9856 | 60.0212 | 16.102 | 183 | 0.45042 | 163.3759 | 344.796 | 0
1462 | 873.6349 | 6.5459 | 48.2804 | 106.8076 | 65.2324 | 6.6928 | 72.9636 | 6.7161 | 8.5387 | 43.7948 | 97.507 | 7.9128 | 220.7764 | 145.0273 | 286.7076 | 11.0867 | 56.5583 | 15.3041 | 166 | 0.27897 | 154.5006 | 335.795 | 0
1463 | 839.7822 | 9.0825 | 48.0113 | 104.5783 | 66.0571 | 5.9093 | 67.8963 | 6.9649 | 7.7527 | 38.6807 | 83.8752 | 8.0202 | 187.7652 | 133.9228 | 278.5704 | 11.0074 | 54.8772 | 14.6755 | 149 | 0.53901 | 140.4873 | 327.3605 | 0
1464 | 809.58 | 5.8467 | 47.9007 | 103.311 | 65.5182 | 6.4212 | 77.7786 | 6.9506 | 6.832 | 36.0429 | 76.0885 | 7.7722 | 175.5949 | 130.3831 | 265.9228 | 11.0482 | 54.513 | 14.4347 | 128 | 0.80884 | 111.5253 | 324.1365 | 0
1465 | 807.1021 | 2.2582 | 47.9855 | 102.8511 | 69.1391 | 5.9187 | 77.1952 | 6.7745 | 6.1967 | 35.0678 | 72.7923 | 7.3991 | 171.3951 | 123.4822 | 254.7108 | 10.9109 | 55.6986 | 13.4202 | 115 | 0.8694 | 93.2114 | 321.864 | 0
1466 | 813.7558 | 5.9061 | 47.8559 | 103.9031 | 68.6217 | 6.4102 | 72.4001 | 6.8298 | 6.1432 | 35.3014 | 70.8665 | 7.318 | 168.3411 | 118.0435 | 236.9083 | 11.0329 | 55.1807 | 12.6236 | 110 | 0.90517 | 89.9135 | 317.9787 | 0
1467 | 804.0962 | 8.1608 | 47.8888 | 103.5548 | 68.407 | 6.6141 | 73.9101 | 6.9894 | 6.1158 | 36.2622 | 70.9337 | 7.3344 | 168.6908 | 115.5469 | 239.6178 | 10.9106 | 54.6581 | 12.8662 | 127 | 0.9457 | 89.4923 | 315.9564 | 0
1468 | 803.8238 | 3.6487 | 47.8352 | 105.7425 | 69.1396 | 5.9182 | 79.8642 | 7.0132 | 5.9739 | 38.7659 | 71.4123 | 7.2916 | 168.4953 | 114.8006 | 228.2745 | 11.0711 | 54.4936 | 12.6544 | 107 | 0.89286 | 88.7553 | 323.0329 | 0
1469 | 800.5994 | 1.7869 | 47.823 | 106.4396 | 69.286 | 5.7791 | 74.6821 | 6.8267 | 6.0024 | 49.1617 | 73.0327 | 7.2775 | 167.2983 | 113.9556 | 218.8795 | 11.0033 | 55.7039 | 12.2953 | 108 | 0.86754 | 89.1204 | 342.8982 | 0
1470 | 803.0712 | 2.879 | 48.8012 | 107.1776 | 67.8462 | 7.1469 | 71.3259 | 6.8313 | 6.2501 | 54.9605 | 73.9578 | 8.565 | 177.8653 | 117.6937 | 225.5489 | 11.0172 | 58.0913 | 12.2178 | 114 | 0.78435 | 95.8869 | 375.2759 | 0
1471 | 846.5497 | 4.9743 | 70.8369 | 115.4747 | 66.5665 | 8.3626 | 87.0827 | 6.987 | 11.4413 | 72.1884 | 86.9106 | 18.9186 | 223.5946 | 171.6171 | 245.3165 | 13.8523 | 55.6403 | 12.5692 | 176 | 0.88061 | 146.3323 | 426.1701 | 0
1472 | 933.4343 | 5.3836 | 92.0251 | 118.3253 | 62.4691 | 12.2551 | 109.855 | 7.6696 | 16.2553 | 97.5648 | 124.5524 | 34.8162 | 290.1052 | 233.109 | 327.1869 | 27.2904 | 58.402 | 14.1737 | 280 | 4.2419 | 194.4832 | 478.2253 | 0.0054777
1473 | 1014.3568 | 4.56 | 104.259 | 133.5143 | 59.8428 | 14.7501 | 125.9405 | 8.8909 | 17.7773 | 98.9193 | 154.0535 | 38.6879 | 372.1065 | 278.7328 | 460.6648 | 36.1136 | 67.8243 | 17.5866 | 323 | 8.5069 | 221.9891 | 542.8122 | 0.013321
1474 | 1099.0959 | 4.0957 | 107.2719 | 142.8504 | 57.7996 | 16.6912 | 139.9212 | 10.0048 | 19.084 | 108.3737 | 171.2942 | 37.9364 | 428.802 | 318.5375 | 560.6736 | 40.5427 | 77.8848 | 18.0418 | 353 | 12.6095 | 237.7426 | 591.5636 | 0.016707
1475 | 1148.6047 | 3.9635 | 101.585 | 151.0419 | 57.5076 | 16.9686 | 146.7786 | 9.7323 | 19.042 | 131.7082 | 177.0198 | 41.6407 | 444.0662 | 347.736 | 604.5615 | 42.6692 | 84.8427 | 18.9337 | 343 | 16.7739 | 251.9077 | 590.5783 | 0.01794
1476 | 1144.1803 | 4.0538 | 104.3341 | 159.2346 | 61.0858 | 13.5693 | 146.3112 | 9.8028 | 18.4229 | 129.0837 | 183.3035 | 41.3455 | 462.6264 | 354.844 | 628.0009 | 42.6641 | 87.6073 | 19.0267 | 350 | 12.4458 | 262.985 | 605.4021 | 0.023222
1477 | 1142.6878 | 4.3121 | 112.8741 | 158.0503 | 59.4441 | 15.1289 | 144.5443 | 9.5945 | 18.4041 | 113.8568 | 179.8924 | 40.2422 | 465.9937 | 349.3274 | 611.7497 | 44.2198 | 85.24 | 19.0715 | 318 | 14.8829 | 255.6248 | 617.923 | 0.057168
1478 | 1138.7838 | 4.1025 | 115.646 | 163.975 | 58.3175 | 16.1991 | 148.8727 | 9.4898 | 22.0593 | 114.1515 | 176.5785 | 42.4525 | 456.2623 | 364.7124 | 612.1122 | 45.5749 | 88.2331 | 19.2284 | 321 | 14.0061 | 254.4274 | 621.9826 | 0.034729
1479 | 1125.2062 | 3.4538 | 118.9306 | 162.97 | 58.3678 | 16.1514 | 141.4125 | 9.6483 | 22.4977 | 113.6398 | 177.1907 | 43.7055 | 456.7225 | 366.2632 | 612.4198 | 45.8936 | 89.6428 | 19.6563 | 288 | 15.2842 | 254.9344 | 626.4222 | 0.017044
1480 | 1133.3518 | 3.9985 | 113.5649 | 161.424 | 58.3582 | 16.1605 | 138.8493 | 9.2033 | 18.422 | 110.4178 | 176.8868 | 40.7103 | 451.2873 | 348.1434 | 606.1977 | 42.8687 | 88.3238 | 20.6386 | 262 | 15.1148 | 246.3074 | 620.3098 | 0.011999
1481 | 1111.4864 | 5.5034 | 109.5375 | 150.5403 | 63.7423 | 11.0456 | 135.6185 | 8.819 | 15.9187 | 105.3897 | 173.8585 | 37.5131 | 407.893 | 320.5662 | 556.3108 | 36.5091 | 86.2362 | 20.0926 | 239 | 15.9469 | 230.0263 | 550.4855 | 0.0046783
1482 | 1062.841 | 6.057 | 103.3266 | 134.994 | 66.1276 | 8.7796 | 128.5672 | 7.6685 | 15.9987 | 85.3885 | 167.3763 | 32.6548 | 351.3206 | 240.53 | 465.7031 | 20.9166 | 78.8513 | 18.763 | 229 | 15.7318 | 205.3271 | 458.5473 | 0
1483 | 1004.202 | 5.5449 | 98.5896 | 126.0801 | 67.1805 | 7.7793 | 123.5745 | 6.9427 | 15.52 | 60.0298 | 139.0544 | 26.3181 | 317.2388 | 179.6866 | 393.7868 | 12.6727 | 70.9375 | 17.1078 | 233 | 14.7941 | 187.3869 | 430.3735 | 0
1484 | 959.6703 | 5.2705 | 76.7114 | 123.0127 | 67.3924 | 7.578 | 105.4727 | 6.7131 | 10.6747 | 46.4179 | 108.8041 | 13.9163 | 269.3787 | 154.2816 | 334.9828 | 10.9452 | 65.398 | 15.3431 | 209 | 14.4601 | 166.7969 | 380.2855 | 0
1485 | 919.7531 | 4.3633 | 69.0825 | 118.784 | 67.3574 | 7.6112 | 93.3872 | 6.2322 | 8.6333 | 42.9893 | 99.8123 | 10.0606 | 240.9851 | 134.1053 | 289.9147 | 10.0682 | 60.5787 | 14.3296 | 205 | 14.5779 | 154.6857 | 359.5808 | 0
1486 | 890.7227 | 3.9527 | 55 | 115.6824 | 68.1548 | 6.8537 | 82.3946 | 6.1835 | 8.1113 | 41.9798 | 98.3445 | 9.7535 | 219.3915 | 121.7055 | 262.5692 | 9.7212 | 58.4611 | 13.2837 | 166 | 14.7259 | 145.1929 | 348.1421 | 0
1487 | 867.5251 | 3.3155 | 49.8857 | 111.7788 | 67.5529 | 7.4255 | 85.763 | 6.2241 | 7.3907 | 40.0073 | 85.5555 | 8.5943 | 206.4427 | 113.3048 | 250.219 | 9.8083 | 57.0418 | 13.2152 | 136 | 14.9762 | 131.9137 | 340.949 | 0
1488 | 830.0066 | 2.4706 | 49.8357 | 109.4034 | 67.3272 | 7.6399 | 79.9389 | 6.253 | 6.7913 | 38.34 | 78.7492 | 8.1497 | 186.7559 | 104.6031 | 237.9309 | 9.7551 | 56.3811 | 12.8684 | 133 | 14.9371 | 105.2832 | 337.2969 | 0
1489 | 806.6373 | 1.7575 | 49.5917 | 105.6128 | 68.1768 | 6.8328 | 74.8357 | 6.3831 | 6.826 | 36.3404 | 78.6691 | 8.0216 | 170.348 | 101.9771 | 236.7491 | 9.8177 | 55.8391 | 12.0686 | 119 | 14.606 | 93.3517 | 331.6699 | 0
1490 | 811.7457 | 1.4148 | 49.546 | 106.3185 | 67.5709 | 7.4084 | 80.2314 | 6.4564 | 6.6333 | 35.8147 | 76.0118 | 7.9882 | 172.6168 | 97.1716 | 251.4094 | 9.7571 | 55.564 | 11.8532 | 118 | 14.5471 | 90.3437 | 330.7733 | 0
1491 | 811.4473 | 1.3159 | 49.6711 | 107.0619 | 68.215 | 6.7966 | 84.7269 | 6.3912 | 6.6353 | 35.417 | 74.6929 | 7.9868 | 169.3183 | 94.4753 | 235.2592 | 9.6556 | 55.7382 | 11.8568 | 124 | 14.581 | 89.5508 | 328.6642 | 0
1492 | 798.4711 | 1.3596 | 49.6068 | 107.4297 | 67.5979 | 7.3827 | 78.9957 | 6.0932 | 6.7947 | 37.9523 | 75.328 | 7.9994 | 161.4801 | 93.816 | 226.3486 | 9.8297 | 55.8878 | 11.8779 | 101 | 14.6053 | 88.602 | 323.7693 | 0
1493 | 797.6574 | 1.8754 | 49.6121 | 105.5714 | 67.3399 | 7.6279 | 78.1334 | 6.2231 | 6.8473 | 48.5888 | 75.6681 | 8.0061 | 159.2398 | 94.0413 | 224.4743 | 9.6675 | 57.596 | 12.3793 | 101 | 14.6642 | 87.9402 | 346.1456 | 0
1494 | 817.2469 | 3.2169 | 65.0663 | 104.1209 | 66.5393 | 8.3885 | 88.1771 | 6.2065 | 8.0747 | 54.8236 | 76.0067 | 10.3519 | 175.318 | 105.3918 | 230.1509 | 9.6634 | 59.918 | 12.3626 | 105 | 14.6244 | 92.355 | 382.802 | 0
1495 | 854.3485 | 4.8576 | 84.8731 | 110.8553 | 63.3112 | 11.4551 | 90.3706 | 6.1433 | 15.1567 | 72.314 | 91.0716 | 21.3042 | 209.3064 | 164.9973 | 257.9861 | 13.0316 | 57.178 | 12.5505 | 161 | 15.0939 | 136.797 | 437.0789 | 0
1496 | 928.7792 | 5.9959 | 97.5368 | 111.0137 | 60.1388 | 14.4689 | 111.4418 | 6.9747 | 17.2253 | 96.7595 | 132.2385 | 35.2036 | 282.9947 | 228.9352 | 339.9073 | 26.7473 | 61.903 | 12.9134 | 274 | 15.3362 | 179.5874 | 483.402 | 0.013186
1497 | 1028.8088 | 7.4962 | 109.8481 | 119.1319 | 59.3717 | 15.1977 | 138.0497 | 7.951 | 18.4347 | 100.0405 | 163.4582 | 39.9553 | 354.9146 | 279.4773 | 461.6658 | 35.2324 | 72.1481 | 15.6214 | 328 | 14.6533 | 213.5843 | 546.844 | 0.048465
1498 | 1116.3906 | 10.4339 | 109.8234 | 135.4977 | 59.1979 | 15.3628 | 143.5689 | 8.3084 | 20.2767 | 107.3942 | 178.569 | 41.3356 | 413.0295 | 322.8897 | 558.4229 | 39.735 | 82.1374 | 16.1638 | 355 | 14.36 | 230.2088 | 588.9199 | 0.088144
1499 | 1164.628 | 7.3427 | 112.2372 | 144.3363 | 60.2396 | 14.3732 | 140.0085 | 8.4908 | 21.5693 | 110.2963 | 185.0599 | 44.0681 | 443.8624 | 343.6372 | 589.1286 | 41.3584 | 88.4034 | 16.4362 | 345 | 13.6809 | 244.2537 | 603.6559 | 0.085789
1500 | 1197.4225 | 4.5083 | 116.5028 | 142.2718 | 60.3184 | 14.2983 | 147.3756 | 8.8499 | 21.7867 | 120.8817 | 186.3817 | 38.875 | 459.8212 | 357.6425 | 590.9716 | 43.019 | 90.6083 | 16.7552 | 347 | 9.0984 | 249.7915 | 617.2215 | 0.10359
1501 | 1178.8865 | 4.1946 | 116.4097 | 144.7254 | 59.678 | 14.9067 | 148.0729 | 9.1941 | 21.3053 | 119.9244 | 185.4636 | 34.8556 | 456.3673 | 354.5032 | 585.3622 | 44.1476 | 88.2986 | 18.3449 | 328 | 7.105 | 245.6115 | 603.8969 | 0.092077
1502 | 1179.5456 | 4.1783 | 115.0557 | 152.232 | 60.2325 | 14.3799 | 143.6055 | 9.6377 | 21.8807 | 112.7833 | 193.0643 | 37.9413 | 455.9445 | 348.1095 | 596.327 | 43.9885 | 90.91 | 19.8499 | 289 | 6.7688 | 237.1654 | 602.8523 | 0.13039
1503 | 1195.1617 | 4.1379 | 115.996 | 151.9066 | 59.5144 | 15.0621 | 146.7147 | 9.4074 | 22.238 | 111.1742 | 196.0753 | 39.2191 | 463.2927 | 347.1372 | 584.3436 | 42.8293 | 91.9909 | 20.2973 | 304 | 8.0917 | 244.3574 | 608.1945 | 0.15559
1504 | 1183.7099 | 3.9227 | 112.4793 | 145.8262 | 57.627 | 16.8551 | 148.648 | 8.9598 | 20.66 | 108.8323 | 192.2987 | 36.1613 | 447.7695 | 335.0694 | 567.2716 | 39.4593 | 88.8514 | 19.9985 | 274 | 7.7351 | 246.8909 | 612.4259 | 0.13721
1505 | 1140.2873 | 4.0747 | 106.405 | 138.9456 | 62.9672 | 11.782 | 132.6374 | 8.7502 | 18.9982 | 97.3299 | 186.1912 | 32.1034 | 427.0094 | 310.7556 | 509.0264 | 32.1754 | 86.6662 | 19.3515 | 255 | 7.3842 | 226.9197 | 534.433 | 0.049481
1506 | 1091.5149 | 5.5732 | 101.8171 | 124.9394 | 65.8993 | 8.9965 | 127.8279 | 7.4789 | 16.0512 | 84.427 | 173.9978 | 31.5418 | 372.8934 | 246.0648 | 422.3453 | 18.3173 | 80.7996 | 18.4103 | 229 | 7.0836 | 202.8748 | 451.9825 | 0
1507 | 1023.4697 | 5.2505 | 98.0954 | 114.8394 | 66.3569 | 8.5617 | 114.5266 | 6.8808 | 14.384 | 70.0418 | 141.5118 | 28.4457 | 319.0172 | 183.1826 | 372.4122 | 12.0941 | 72.4482 | 17.9821 | 214 | 6.8272 | 186.3409 | 395.3127 | 0
1508 | 980.0847 | 4.8243 | 88.6869 | 108.4182 | 66.4425 | 8.4804 | 96.6709 | 6.6563 | 9.5863 | 63.1059 | 111.2476 | 15.0234 | 274.0496 | 177.4062 | 326.1796 | 10.8646 | 66.6548 | 17.237 | 191 | 6.8544 | 168.5536 | 350.1046 | 0
1509 | 942.9961 | 4.8133 | 59.131 | 103.4295 | 67.1793 | 7.7804 | 89.6502 | 6.7267 | 7.6885 | 61.4357 | 99.05 | 8.5792 | 229.5606 | 162.7115 | 283.4379 | 10.4746 | 61.5168 | 16.2995 | 170 | 6.8994 | 156.331 | 325.1817 | 0
1510 | 902.4721 | 4.1111 | 48.2552 | 100.483 | 67.2622 | 7.7017 | 79.75 | 6.8867 | 7.6458 | 57.6022 | 91.4078 | 8.0275 | 219.4907 | 142.6464 | 279.5423 | 10.3128 | 58.2117 | 15.0436 | 165 | 6.7366 | 146.7948 | 316.4615 | 0
1511 | 867.4786 | 3.8796 | 47.9694 | 97.3746 | 68.1198 | 6.887 | 72.179 | 6.979 | 6.7454 | 51.8364 | 79.2177 | 7.6066 | 191.9425 | 122.3861 | 272.9297 | 10.2779 | 57.109 | 14.2164 | 135 | 6.6981 | 135.9897 | 308.0768 | 0
1512 | 838.0953 | 2.2647 | 47.9107 | 96.9372 | 67.6097 | 7.3716 | 74.5267 | 6.9399 | 6.146 | 49.0828 | 73.6051 | 7.508 | 184.7776 | 110.276 | 261.4417 | 10.399 | 56.8089 | 13.9376 | 132 | 6.7686 | 108.0126 | 297.3213 | 0
1513 | 827.5751 | 2.3666 | 47.8593 | 96.6875 | 67.4379 | 7.5348 | 84.777 | 6.9906 | 6.172 | 46.1723 | 72.9313 | 7.3905 | 185.3943 | 106.2549 | 241.2815 | 10.2301 | 57.0533 | 13.7804 | 118 | 6.8651 | 97.3589 | 302.606 | 0
1514 | 807.1091 | 1.8718 | 47.8941 | 96.8381 | 67.3498 | 7.6184 | 78.6789 | 7.0461 | 6.0467 | 44.7207 | 73.7742 | 7.3936 | 184.1088 | 102.314 | 240.0283 | 10.4213 | 57.0174 | 13.6154 | 115 | 6.8464 | 97.21 | 301.1587 | 0
1515 | 787.3133 | 1.5548 | 47.8721 | 96.4922 | 66.5998 | 8.331 | 73.9125 | 6.9595 | 6.1192 | 43.8636 | 73.4029 | 7.3679 | 174.7283 | 97.0439 | 241.1405 | 10.4461 | 56.9405 | 13.1796 | 128 | 6.9083 | 97.4572 | 295.5122 | 0
1516 | 781.3606 | 1.3823 | 47.7546 | 98.2224 | 67.1024 | 7.8535 | 81.3995 | 6.9789 | 5.9647 | 47.6093 | 73.0622 | 7.3256 | 165.0827 | 95.7139 | 236.4123 | 10.314 | 56.2152 | 12.0931 | 102 | 6.792 | 97.1114 | 293.4482 | 0
1517 | 780.8945 | 2.1727 | 47.5927 | 98.1835 | 67.3443 | 7.6237 | 80.2994 | 6.975 | 5.912 | 58.7864 | 73.1157 | 7.3078 | 163.5843 | 96.0758 | 227.8273 | 10.4039 | 57.6789 | 11.7494 | 105 | 6.7455 | 95.0904 | 316.3964 | 0
1518 | 790.0778 | 3.8627 | 60.3051 | 98.3859 | 67.3358 | 7.6318 | 75.6756 | 7.371 | 6.2573 | 64.476 | 73.6352 | 8.0534 | 177.5945 | 106.7699 | 225.0946 | 10.3807 | 60.5523 | 11.7203 | 118 | 6.6839 | 100.2487 | 351.3422 | 0
1519 | 841.2273 | 4.9555 | 80.989 | 102.6976 | 62.8128 | 11.9286 | 84.6071 | 7.5843 | 8.6548 | 82.2792 | 87.1565 | 15.9066 | 239.1335 | 172.4269 | 247.4909 | 13.3016 | 58.3033 | 11.6897 | 174 | 6.8563 | 148.4551 | 409.6672 | 0
1520 | 924.5105 | 6.7518 | 94.9439 | 103.7192 | 56.6636 | 17.7703 | 115.1627 | 7.3705 | 15.2732 | 96.0631 | 131.0127 | 25.1299 | 315.6203 | 234.5739 | 328.7038 | 25.5815 | 62.9586 | 12.4376 | 231 | 10.3153 | 190.637 | 457.063 | 0.011303
1521 | 1018.5959 | 11.4333 | 104.1077 | 123.0035 | 56.22 | 18.1918 | 129.8659 | 7.2411 | 19.3281 | 87.2156 | 163.4254 | 28.3073 | 371.4698 | 286.3029 | 450.8035 | 35.1598 | 72.6129 | 14.9082 | 305 | 13.2643 | 214.9791 | 523.4893 | 0.029505
1522 | 1100.9486 | 9.7911 | 110.9415 | 139.8925 | 57.8351 | 16.6574 | 132.5213 | 7.8834 | 19.486 | 90.844 | 176.1149 | 31.4853 | 409.9127 | 311.0047 | 532.4597 | 41.0033 | 81.9364 | 17.6886 | 330 | 17.4348 | 236.6318 | 587.6841 | 0.048089
1523 | 1151.1094 | 7.401 | 110.2857 | 146.8899 | 57.6386 | 16.8441 | 137.5537 | 8.3679 | 20.5347 | 98.5554 | 183.0003 | 38.4987 | 454.654 | 343.285 | 567.5545 | 42.2805 | 88.2873 | 18.3421 | 369 | 24.497 | 242.6829 | 597.746 | 0.05031
1524 | 1198.1199 | 7.3298 | 112.6251 | 142.446 | 58.966 | 15.5831 | 154.1687 | 7.8909 | 20.7087 | 97.8373 | 181.6247 | 40.9584 | 461.4616 | 346.8219 | 586.6795 | 40.5552 | 91.1643 | 17.8869 | 348 | 27.1996 | 249.1403 | 596.7214 | 0.036228
1525 | 1190.0992 | 6.7421 | 113.9871 | 139.8135 | 57.7551 | 16.7334 | 145.3936 | 7.963 | 20.6833 | 97.4349 | 177.3317 | 38.4675 | 451.2741 | 346.1419 | 588.9646 | 42.4228 | 89.1971 | 18.5025 | 360 | 31.401 | 244.3778 | 599.0721 | 0.061329
1526 | 1195.5792 | 5.5746 | 118.462 | 143.1438 | 55.7421 | 18.6458 | 142.2495 | 8.1425 | 20.1747 | 103.1808 | 177.5082 | 36.7182 | 451.394 | 341.494 | 593.5044 | 44.1671 | 90.0071 | 18.4846 | 327 | 28.8417 | 241.0789 | 609.6704 | 0.031224
1527 | 1181.4046 | 4.5289 | 114.2175 | 147.2799 | 57.7922 | 16.6982 | 140.6265 | 8.0209 | 19.518 | 105.2449 | 177.4523 | 38.4129 | 450.4695 | 344.083 | 596.2319 | 44.9552 | 93.3164 | 17.9528 | 293 | 27.4727 | 234.2246 | 584.6733 | 0.058562
1528 | 1151.8913 | 3.9712 | 112.6333 | 142.8857 | 58.4645 | 16.0595 | 130.2179 | 7.5374 | 19.7233 | 102.1082 | 175.4421 | 38.481 | 437.5368 | 332.9208 | 579.6676 | 41.8866 | 90.8495 | 17.404 | 285 | 24.9952 | 226.9175 | 557.6916 | 0.020427
1529 | 1092.0047 | 5.0195 | 106.2611 | 137.7285 | 63.7685 | 11.0207 | 126.9284 | 7.3593 | 19.1789 | 96.5833 | 169.1243 | 34.1796 | 415.5231 | 300.1847 | 536.2746 | 25.5836 | 88.0979 | 16.9461 | 259 | 23.0517 | 204.8481 | 501.1742 | 0.013544
1530 | 1017.2713 | 5.5507 | 99.9993 | 124.4568 | 66.9169 | 8.0297 | 117.9683 | 6.0933 | 18.7308 | 88.7254 | 156.6531 | 27.7977 | 356.372 | 216.2092 | 431.264 | 13.5938 | 79.7234 | 16.4245 | 232 | 21.8557 | 178.0193 | 411.529 | 0
1531 | 952.4244 | 4.4239 | 95.614 | 110.6386 | 67.3212 | 7.6457 | 99.3033 | 5.5923 | 17.1011 | 74.1695 | 131.2225 | 24.9407 | 301.2239 | 167.6217 | 353.3242 | 10.8225 | 70.5477 | 15.9253 | 236 | 21.6628 | 166.2955 | 356.2056 | 0
1532 | 890.4155 | 3.9134 | 84.0928 | 102.2449 | 68.1331 | 6.8744 | 89.189 | 5.6 | 12.3233 | 60.681 | 98.7207 | 16.2364 | 252.9227 | 161.0955 | 327.8641 | 9.6962 | 60.7945 | 15.3769 | 215 | 21.7952 | 152.813 | 317.7845 | 0
1533 | 845.8071 | 3.5209 | 57.3742 | 99.9544 | 67.6574 | 7.3263 | 77.9899 | 5.7317 | 9.2518 | 55.8501 | 79.7579 | 13.069 | 215.3153 | 146.1676 | 277.516 | 9.2866 | 55.2488 | 14.8517 | 204 | 21.9258 | 140.8271 | 298.3516 | 0
1534 | 821.1088 | 3.4077 | 48.2179 | 100.0303 | 67.2933 | 7.6722 | 70.1667 | 6.0164 | 10.4486 | 53.3846 | 74.8721 | 13.5729 | 199.263 | 126.1498 | 254.9608 | 9.2468 | 53.5026 | 13.7485 | 202 | 21.4466 | 132.3758 | 297.8295 | 0
1535 | 800.9991 | 3.0688 | 47.6867 | 102.6997 | 68.1853 | 6.8247 | 77.0542 | 6.2218 | 9.1971 | 48.296 | 73.0334 | 12.9604 | 192.404 | 107.1592 | 255.6369 | 9.2958 | 53.2237 | 13.3266 | 172 | 21.2224 | 122.7247 | 302.1375 | 0
1536 | 775.6243 | 6.4388 | 47.7318 | 103.7634 | 67.5961 | 7.3845 | 78.739 | 6.2328 | 8.6 | 46.3513 | 70.7084 | 10.6093 | 195.775 | 108.4126 | 267.6148 | 9.1681 | 53.6542 | 13.4155 | 135 | 21.4107 | 99.5014 | 293.0102 | 0
1537 | 774.3358 | 4.4115 | 48.2882 | 101.8516 | 68.1518 | 6.8566 | 74.8451 | 6.2423 | 7.3831 | 46.8945 | 69.7165 | 8.1336 | 193.6024 | 102.3502 | 284.2616 | 9.1932 | 53.29 | 13.3759 | 135 | 21.5754 | 90.1361 | 299.7553 | 0
1538 | 773.4176 | 2.2751 | 48.2438 | 101.3936 | 67.5822 | 7.3977 | 76.2194 | 6.3666 | 7.0001 | 45.4468 | 69.0516 | 7.5426 | 197.45 | 96.2393 | 264.4117 | 9.2832 | 53.2667 | 13.423 | 135 | 21.7631 | 87.3386 | 300.5208 | 0
1539 | 768.4344 | 1.9602 | 47.7347 | 101.1489 | 68.1197 | 6.887 | 80.8968 | 6.3817 | 7.0644 | 45.0645 | 68.976 | 7.5734 | 187.2742 | 94.3105 | 253.7235 | 9.1726 | 53.3882 | 13.5416 | 151 | 21.7789 | 83.1048 | 298.8307 | 0
1540 | 759.7289 | 3.3511 | 47.5387 | 102.4151 | 67.6569 | 7.3267 | 75.644 | 6.3038 | 6.6986 | 46.7111 | 69.6691 | 7.5169 | 179.8917 | 92.7209 | 249.9539 | 9.1471 | 52.7533 | 13.403 | 128 | 21.6427 | 80.8612 | 290.8901 | 0
1541 | 760.2072 | 7.7661 | 47.5716 | 102.7684 | 68.1207 | 6.8861 | 72.3174 | 6.1609 | 6.8254 | 52.6868 | 70.0189 | 7.5234 | 161.5305 | 91.5556 | 243.0501 | 9.1776 | 54.467 | 13.3693 | 126 | 21.6718 | 78.6095 | 279.3831 | 0
1542 | 758.6639 | 10.3086 | 47.5369 | 101.8502 | 67.6669 | 7.3173 | 82.7127 | 6.3921 | 6.8798 | 57.744 | 70.3088 | 7.5336 | 156.8553 | 91.5074 | 222.7201 | 9.1626 | 57.1311 | 13.2683 | 127 | 21.7045 | 78.266 | 281.8824 | 0
1543 | 777.3733 | 10.3242 | 56.0997 | 100.2836 | 67.2827 | 7.6822 | 78.4804 | 6.5445 | 6.7976 | 59.9027 | 69.1757 | 7.1744 | 155.6571 | 93.1593 | 210.3767 | 9.0208 | 54.2251 | 12.3527 | 126 | 21.5612 | 78.5957 | 280.4325 | 0
1544 | 792.5749 | 6.2692 | 68.6379 | 96.7101 | 67.3918 | 7.5786 | 72.743 | 5.895 | 11.212 | 55.0646 | 73.2948 | 7.1458 | 161.8072 | 91.5815 | 209.3311 | 9.1388 | 51.7563 | 12.0133 | 128 | 21.8177 | 78.1899 | 276.4801 | 0.029004
1545 | 799.4127 | 2.3502 | 79.9768 | 96.2984 | 67.3492 | 7.619 | 77.9018 | 5.7472 | 9.4033 | 52.7344 | 103.9161 | 10.9546 | 179.0471 | 94.3956 | 212.0658 | 10.0434 | 51.5545 | 12.5956 | 158 | 22.8694 | 83.6705 | 275.6708 | 0.099138
1546 | 826.4942 | 1.4543 | 90.9411 | 96.1662 | 67.3355 | 7.632 | 78.0494 | 5.6966 | 10.3488 | 67.5866 | 129.7776 | 10.4011 | 206.072 | 104.1597 | 217.226 | 9.5496 | 52.2065 | 13.0166 | 174 | 22.7983 | 114.0828 | 279.2995 | 0.070867
1547 | 854.5441 | 1.5164 | 91.7033 | 96.8826 | 67.3745 | 7.595 | 70.8467 | 5.2891 | 9.8734 | 75.3607 | 141.2651 | 9.3985 | 229.3388 | 116.4087 | 216.9806 | 9.3691 | 52.7273 | 13.11 | 192 | 22.5268 | 125.4934 | 287.7749 | 0.090176
1548 | 865.0777 | 1.801 | 90.7641 | 100.4636 | 67.3711 | 7.5982 | 72.3526 | 5.718 | 11.7964 | 79.4219 | 133.7824 | 6.4386 | 242.7344 | 124.1922 | 225.2301 | 9.3291 | 56.4866 | 13.0955 | 203 | 23.1972 | 126.6668 | 286.5034 | 0.16579
1549 | 867.4935 | 1.6568 | 91.2017 | 100.9809 | 68.1208 | 6.886 | 89.0927 | 7.0652 | 13.6135 | 79.2908 | 103.5127 | 7.7458 | 244.5967 | 127.84 | 234.2822 | 9.2818 | 58.8806 | 13.1813 | 205 | 21.9326 | 123.6809 | 284.2806 | 0.11454
1550 | 866.1573 | 2.0132 | 92.1895 | 102.2791 | 67.6387 | 7.344 | 99.828 | 7.5851 | 13.0935 | 77.1975 | 92.0292 | 10.0148 | 240.9659 | 134.7231 | 239.0606 | 9.1856 | 55.4822 | 13.338 | 204 | 21.5105 | 122.3342 | 290.6592 | 0.1436
1551 | 870.9543 | 2.235 | 90.4571 | 101.7951 | 67.3406 | 7.6273 | 100.4444 | 6.2132 | 9.778 | 71.6589 | 93.6645 | 9.9143 | 237.2581 | 142.4026 | 252.9744 | 9.0347 | 54.0903 | 13.218 | 212 | 21.2544 | 122.9237 | 307.735 | 0.092677
1552 | 872.5044 | 2.8156 | 88.5082 | 100.3008 | 68.2131 | 6.7984 | 89.6252 | 5.5075 | 7.9508 | 61.3448 | 93.8798 | 10.8844 | 230.9044 | 133.8558 | 262.6358 | 9.3748 | 54.5195 | 13.3897 | 221 | 21.0545 | 118.4713 | 302.2367 | 0.024582
1553 | 868.6256 | 4.3413 | 70.1044 | 99.8364 | 67.5702 | 7.4091 | 80.5042 | 5.5543 | 8.1321 | 41.6894 | 90.6063 | 8.8427 | 228.9663 | 133.415 | 255.3031 | 9.6293 | 54.6938 | 13.6775 | 222 | 21.1319 | 93.8192 | 299.567 | 0.007918
1554 | 866.69 | 4.3965 | 63.1033 | 98.0023 | 68.1227 | 6.8842 | 74.2512 | 5.5826 | 11.4132 | 35.494 | 85.7787 | 7.5407 | 228.4576 | 136.5292 | 262.936 | 9.2302 | 55.2535 | 14.4892 | 216 | 21.3151 | 88.7316 | 311.6082 | 0
1555 | 831.4834 | 4.5404 | 63.142 | 99.1345 | 67.5729 | 7.4066 | 86.9997 | 5.7314 | 13.2818 | 37.4633 | 78.9823 | 8.0206 | 219.1649 | 129.5418 | 274.6194 | 9.2723 | 57.7275 | 14.9891 | 212 | 21.6501 | 93.0423 | 312.3775 | 0
1556 | 817.0518 | 4.205 | 62.7083 | 99.326 | 68.1814 | 6.8284 | 84.2399 | 5.8466 | 9.7479 | 38.5461 | 74.9297 | 8.0986 | 204.2827 | 123.5592 | 278.4612 | 9.4175 | 55.9473 | 15.0721 | 201 | 22.0323 | 97.931 | 308.8252 | 0
1557 | 822.8095 | 3.8968 | 62.822 | 98.0585 | 67.5769 | 7.4027 | 76.2672 | 5.9619 | 8.1074 | 38.0633 | 73.3346 | 7.8254 | 195.3516 | 119.3948 | 268.6054 | 9.3365 | 53.7757 | 14.5692 | 217 | 21.8048 | 97.6313 | 301.3556 | 0
1558 | 809.8221 | 7.6849 | 62.4247 | 98.2246 | 67.3462 | 7.6219 | 80.9286 | 5.8836 | 7.1762 | 34.7769 | 72.8193 | 7.4952 | 187.2498 | 109.8665 | 258.9716 | 9.4108 | 53.2512 | 13.5808 | 223 | 21.505 | 93.3343 | 305.6689 | 0
1559 | 794.1787 | 5.0437 | 62.202 | 100.908 | 67.4058 | 7.5653 | 79.5509 | 5.9602 | 6.9432 | 33.6395 | 71.3943 | 7.4265 | 180.7638 | 103.698 | 236.035 | 9.4896 | 53.3579 | 13.1465 | 202 | 21.4756 | 92.1108 | 327.0433 | 0
1560 | 779.7301 | 1.9804 | 62.2833 | 100.4765 | 68.0863 | 6.9188 | 73.1503 | 6.0506 | 6.6975 | 35.074 | 71.9501 | 7.4682 | 178.0415 | 103.1407 | 233.5722 | 9.4156 | 53.5441 | 13.0642 | 204 | 21.827 | 88.1038 | 327.2368 | 0
1561 | 805.892 | 4.2384 | 62.1866 | 100.3754 | 67.649 | 7.3342 | 73.3749 | 6.1684 | 6.8686 | 35.571 | 70.6971 | 7.4713 | 175.4399 | 106.5572 | 244.5288 | 9.4178 | 53.1094 | 12.8896 | 205 | 21.6197 | 85.7486 | 314.4296 | 0
1562 | 802.9309 | 7.7141 | 61.8549 | 100.2758 | 64.3148 | 10.5017 | 79.8514 | 6.1737 | 9.317 | 36.5427 | 69.8784 | 7.8834 | 172.4937 | 98.17 | 239.3707 | 9.3773 | 53.1397 | 12.7721 | 206 | 21.8876 | 79.5473 | 306.7633 | 0
1563 | 783.2448 | 8.5217 | 61.9073 | 100.1546 | 63.3127 | 11.4537 | 73.4626 | 6.0701 | 7.874 | 35.8999 | 70.2379 | 7.6509 | 170.509 | 96.8615 | 232.0244 | 9.4309 | 53.0813 | 12.3218 | 214 | 27.5101 | 77.0417 | 292.0323 | 0
1564 | 771.6008 | 4.145 | 62.7133 | 99.4494 | 63.4159 | 11.3557 | 70.127 | 6.1948 | 6.6399 | 35.0068 | 71.2789 | 7.485 | 171.4958 | 93.9857 | 232.1537 | 9.4572 | 52.6231 | 12.1339 | 177 | 26.0006 | 78.1891 | 296.3237 | 0
1565 | 757.0281 | 2.8744 | 62.1631 | 99.5373 | 64.0838 | 10.7211 | 79.7357 | 6.2375 | 6.7235 | 34.8212 | 71.2554 | 7.4615 | 167.6328 | 92.4749 | 219.5671 | 9.3275 | 54.2035 | 11.8365 | 157 | 22.8373 | 77.2373 | 295.5384 | 0
1566 | 747.7092 | 6.7538 | 61.796 | 105.9328 | 67.4748 | 7.4997 | 75.6082 | 6.2732 | 6.5677 | 36.064 | 71.279 | 7.4834 | 162.722 | 90.3592 | 227.1365 | 9.3209 | 57.198 | 11.3838 | 139 | 21.8367 | 76.4603 | 295.231 | 0
1567 | 762.2487 | 9.6588 | 66.3734 | 107.1281 | 67.6374 | 7.3453 | 68.0691 | 6.5256 | 6.2799 | 36.5268 | 69.154 | 6.764 | 156.1906 | 88.2479 | 221.8175 | 9.1404 | 54.0735 | 11.2711 | 147 | 21.5538 | 76.1354 | 283.8313 | 0
1568 | 781.7536 | 8.2305 | 81.7453 | 105.4501 | 67.3266 | 7.6405 | 75.2597 | 6.3537 | 5.9401 | 32.5367 | 67.0758 | 5.1631 | 157.2567 | 88.2436 | 210.0583 | 9.1305 | 51.7729 | 11.4902 | 142 | 21.484 | 75.6335 | 277.9395 | 0.011918
1569 | 783.8785 | 3.2279 | 87.9711 | 104.6015 | 68.1963 | 6.8143 | 85.4788 | 6.084 | 5.7763 | 40.8373 | 69.5883 | 6.9429 | 161.0755 | 91.1813 | 210.6024 | 9.4536 | 51.5221 | 12.4698 | 156 | 21.4603 | 79.1873 | 278.6068 | 0.041477
1570 | 788.4887 | 1.4362 | 89.7128 | 106.5885 | 67.5887 | 7.3915 | 77.4827 | 5.8856 | 9.227 | 63.3582 | 77.7809 | 9.2422 | 170.919 | 97.5693 | 206.4085 | 9.6643 | 51.8691 | 13.4534 | 204 | 21.2352 | 82.3814 | 282.468 | 0.038231
1571 | 819.6632 | 1.721 | 90.113 | 108.4412 | 66.6418 | 8.2911 | 71.8362 | 5.7241 | 12.578 | 75.3888 | 94.6299 | 7.8296 | 193.5371 | 110.5678 | 201.2732 | 9.9471 | 52.8073 | 13.7373 | 188 | 21.0745 | 83.8279 | 279.6989 | 0.079237
1572 | 831.554 | 1.7291 | 90.5494 | 111.4822 | 67.0859 | 7.8692 | 79.9924 | 5.7194 | 13.0232 | 78.5135 | 113.6548 | 5.9267 | 209.1981 | 127.3983 | 203.2485 | 9.9957 | 53.395 | 13.9466 | 199 | 21.159 | 87.4425 | 283.8616 | 0.08406
1573 | 847.6535 | 1.6618 | 90.312 | 113.1075 | 68.1322 | 6.8752 | 74.7702 | 6.1034 | 9.9373 | 72.5418 | 113.147 | 9.3139 | 213.571 | 137.9405 | 214.2717 | 10.0245 | 54.0672 | 13.5133 | 193 | 21.1939 | 89.1583 | 280.7643 | 0.082281
1574 | 840.3829 | 1.8773 | 89.9656 | 111.4797 | 67.628 | 7.3541 | 70.4315 | 6.1464 | 12.468 | 66.9414 | 99.4221 | 11.2124 | 213.0943 | 143.974 | 258.9813 | 9.971 | 55.1171 | 13.256 | 189 | 21.0587 | 88.5667 | 287.3342 | 0.0711
1575 | 844.8848 | 1.733 | 90.4742 | 110.9963 | 67.3931 | 7.5774 | 85.3727 | 6.3976 | 13.371 | 61.721 | 93.6308 | 11.4202 | 216.3759 | 153.311 | 291.6485 | 9.9515 | 56.0505 | 13.5972 | 191 | 20.9937 | 91.2062 | 292.8907 | 0.059151
1576 | 852.8754 | 1.6537 | 86.8948 | 112.7695 | 67.283 | 7.682 | 92.0586 | 6.7346 | 12.9818 | 57.0209 | 93.1411 | 10.5697 | 216.0466 | 169.5988 | 284.645 | 9.7502 | 55.337 | 13.544 | 172 | 21.1588 | 92.0879 | 292.8788 | 0.019723
1577 | 851.878 | 2.6775 | 69.1058 | 112.3808 | 68.1298 | 6.8775 | 96.8569 | 6.7382 | 13.1827 | 42.7126 | 92.4207 | 10.3536 | 217.7715 | 164.706 | 272.3487 | 9.3943 | 54.3646 | 13.8418 | 166 | 21.0091 | 93.8024 | 284.5632 | 0.013291
1578 | 862.4479 | 3.863 | 62.6275 | 112.4428 | 68.3772 | 6.6425 | 94.1646 | 7.5852 | 11.7987 | 37.6763 | 89.3091 | 10.5653 | 218.2813 | 140.5562 | 306.771 | 8.8886 | 54.5191 | 13.8102 | 157 | 21.1165 | 95.6662 | 294.9847 | 0
1579 | 849.1754 | 3.8873 | 63.3219 | 111.6882 | 67.624 | 7.358 | 92.2323 | 7.4571 | 7.5253 | 40.9401 | 92.3571 | 9.4811 | 212.616 | 134.3705 | 303.9004 | 9.0689 | 57.0485 | 13.8168 | 133 | 21.4506 | 94.4564 | 316.4148 | 0
1580 | 838.5316 | 3.537 | 63.0477 | 108.8981 | 67.3384 | 7.6293 | 79.1875 | 6.619 | 6.1421 | 40.8211 | 89.059 | 8.3386 | 204.7005 | 126.0304 | 262.0563 | 9.2275 | 56.2142 | 13.8005 | 131 | 21.6966 | 90.4849 | 311.3933 | 0
1581 | 810.8484 | 4.0595 | 63.2783 | 108.3935 | 68.1704 | 6.8389 | 80.2243 | 6.3265 | 6.1002 | 37.5062 | 76.7832 | 7.9797 | 193.9826 | 115.2154 | 240.2576 | 9.1773 | 54.1291 | 13.6066 | 143 | 21.6151 | 84.5393 | 295.8813 | 0
1582 | 788.9616 | 3.7064 | 63.2699 | 108.2554 | 67.5884 | 7.3918 | 85.675 | 6.3135 | 5.9391 | 36.4847 | 70.8397 | 7.5819 | 187.7381 | 109.3156 | 234.0771 | 9.1616 | 53.3211 | 12.6539 | 132 | 21.3806 | 79.855 | 294.5252 | 0
1583 | 777.7153 | 2.8495 | 63.0539 | 107.6337 | 67.3786 | 7.5911 | 73.1898 | 6.3568 | 5.9004 | 37.6021 | 69.2938 | 7.426 | 171.0117 | 102.9819 | 229.9644 | 9.1471 | 53.3415 | 12.3252 | 114 | 21.3202 | 75.0456 | 291.9696 | 0
1584 | 772.3586 | 4.9193 | 62.3164 | 106.8887 | 68.0706 | 6.9337 | 75.3619 | 6.5436 | 5.8583 | 37.5184 | 69.0185 | 7.4232 | 160.5285 | 98.1419 | 241.0892 | 9.2181 | 53.1086 | 12.3122 | 111 | 21.4624 | 75.954 | 292.3118 | 0
1585 | 765.9904 | 5.0839 | 61.9964 | 106.227 | 67.5938 | 7.3867 | 88.0366 | 6.7102 | 6.0673 | 36.1832 | 67.6986 | 7.4441 | 152.5982 | 94.6461 | 264.128 | 9.2492 | 53.3717 | 12.3438 | 111 | 21.5141 | 78.9674 | 295.098 | 0
1586 | 758.3267 | 2.2449 | 62.1219 | 105.8886 | 67.3412 | 7.6267 | 81.3191 | 6.5298 | 6.304 | 36.3693 | 66.4478 | 7.4927 | 150.5031 | 92.1401 | 253.3072 | 9.1338 | 53.528 | 12.3297 | 112 | 21.5498 | 77.8459 | 294.3795 | 0
1587 | 752.4851 | 1.3439 | 62.2147 | 106.0937 | 66.6377 | 8.2949 | 71.9595 | 6.4601 | 6.1327 | 36.9294 | 66.9267 | 7.8507 | 150.1756 | 95.7063 | 226.5732 | 9.1875 | 53.5227 | 12.3379 | 129 | 21.6194 | 79.4875 | 297.6562 | 0
1588 | 752.5475 | 1.918 | 62.4649 | 105.8893 | 66.4493 | 8.4739 | 72.0544 | 6.5175 | 6.2802 | 39.1012 | 67.6959 | 7.9327 | 154.4297 | 99.0747 | 215.879 | 9.2441 | 53.5794 | 12.2811 | 107 | 21.5956 | 82.4983 | 300.9767 | 0
1589 | 748.6738 | 1.9502 | 62.7801 | 106.7705 | 66.2547 | 8.6589 | 79.4646 | 6.5776 | 6.2999 | 49.1575 | 68.4223 | 8.3278 | 156.0496 | 95.0841 | 211.7908 | 9.1764 | 54.815 | 11.788 | 104 | 21.4819 | 81.318 | 332.4006 | 0
1590 | 763.5903 | 2.9001 | 63.0996 | 105.0799 | 65.6417 | 9.2412 | 74.1047 | 6.8121 | 7.0632 | 55.2571 | 68.6495 | 8.4835 | 162.6349 | 104.8511 | 216.0607 | 9.2218 | 57.3243 | 11.5693 | 111 | 21.3485 | 84.1238 | 349.7604 | 0
1591 | 806.7459 | 4.2623 | 73.1293 | 106.7811 | 63.0967 | 11.659 | 79.8248 | 7.0973 | 10.1733 | 70.636 | 89.2604 | 18.2274 | 212.7276 | 167.5753 | 261.1284 | 11.9713 | 54.449 | 12.1678 | 161 | 20.5224 | 130.8118 | 391.9157 | 0
1592 | 868.1737 | 5.1889 | 96.0314 | 113.9315 | 60.8634 | 13.7805 | 105.9808 | 7.8158 | 14.522 | 95.0263 | 108.3204 | 33.7272 | 285.003 | 217.4967 | 336.7147 | 26.2525 | 57.9539 | 14.2201 | 246 | 19.0535 | 185.0178 | 450.5388 | 0.010271
1593 | 974.4513 | 11.375 | 109.5842 | 126.9986 | 60.4855 | 14.1396 | 125.497 | 8.0664 | 14.6465 | 99.1589 | 112.3752 | 42.7215 | 375.0181 | 265.3089 | 442.1941 | 34.6619 | 67.8302 | 16.7517 | 313 | 18.5136 | 221.5867 | 518.3828 | 0.017966
1594 | 1072.1622 | 13.7911 | 112.4076 | 139.2841 | 58.7603 | 15.7785 | 130.3358 | 9.0083 | 15.2401 | 119.6963 | 117.942 | 44.4076 | 433.4332 | 308.8697 | 534.0945 | 39.8405 | 76.9081 | 18.5783 | 387 | 18.6074 | 243.4849 | 543.7706 | 0.031179
1595 | 1122.6144 | 11.8246 | 110.8756 | 145.9626 | 57.6008 | 16.88 | 139.0013 | 9.9918 | 16.2862 | 114.9204 | 124.1615 | 44.7683 | 454.2491 | 337.7074 | 578.5644 | 42.1708 | 86.1535 | 18.988 | 352 | 19.7213 | 250.7974 | 545.494 | 0.038921
1596 | 1141.6195 | 9.1025 | 114.7428 | 146.6413 | 58.9627 | 15.5862 | 135.4547 | 9.7623 | 16.8151 | 106.6755 | 126.6757 | 44.5686 | 468.4189 | 347.7271 | 616.4284 | 41.0622 | 90.17 | 18.9614 | 346 | 21.3266 | 260.7309 | 545.0636 | 0.066807
1597 | 1129.8139 | 7.7335 | 114.7663 | 139.2044 | 57.7642 | 16.7248 | 134.4325 | 9.3826 | 18.3309 | 97.7579 | 126.0938 | 44.0983 | 467.7721 | 351.9838 | 623.7225 | 41.5766 | 87.1336 | 18.783 | 389 | 22.9135 | 258.5937 | 545.6569 | 0.055402
1598 | 1137.6295 | 6.5446 | 114.6264 | 143.2198 | 58.0645 | 16.4395 | 137.3809 | 9.5469 | 23.6773 | 105.0825 | 152.424 | 42.0459 | 464.3013 | 357.6458 | 615.3627 | 41.4772 | 84.8523 | 18.6551 | 334 | 22.166 | 261.6571 | 553.0939 | 0.058901
1599 | 1144.03 | 5.1456 | 115.0034 | 144.4472 | 58.379 | 16.1407 | 130.2699 | 9.661 | 22.7557 | 120.0297 | 182.0836 | 44.2178 | 461.7859 | 351.8814 | 623.3546 | 40.0167 | 87.2258 | 18.5801 | 328 | 18.1385 | 259.5725 | 552.2867 | 0.030254
1600 | 1122.2749 | 6.4117 | 112.0695 | 142.1114 | 58.4944 | 16.0311 | 131.7639 | 9.2325 | 18.8365 | 108.6548 | 187.4248 | 38.6987 | 452.3981 | 328.5615 | 585.2948 | 39.4823 | 85.8979 | 18.3153 | 275 | 13.1351 | 239.5432 | 553.2881 | 0.028472
1601 | 1105.1639 | 6.2701 | 107.0224 | 134.8473 | 63.6671 | 11.1171 | 121.9342 | 8.3555 | 15.52 | 91.0696 | 181.6727 | 34.7964 | 426.295 | 307.2553 | 533.9948 | 32.7398 | 81.9702 | 18.2318 | 252 | 10.7708 | 215.937 | 499.5806 | 0.011623
1602 | 1070.03 | 6.1885 | 102.9895 | 122.4097 | 63.7617 | 11.0272 | 114.5005 | 7.2808 | 15.0814 | 80.2342 | 164.6063 | 32.7795 | 373.1882 | 260.6757 | 459.3044 | 17.8304 | 75.3599 | 17.226 | 228 | 10.4173 | 188.8661 | 405.1542 | 0
1603 | 1014.1014 | 5.499 | 102.3615 | 113.4971 | 66.4637 | 8.4603 | 104.4859 | 6.7 | 15.0218 | 66.269 | 136.3932 | 28.3791 | 328.3236 | 216.0147 | 404.0081 | 11.5443 | 71.3663 | 16.0844 | 206 | 10.3037 | 174.0969 | 354.0675 | 0
1604 | 964.2924 | 5.3313 | 90.7693 | 109.6587 | 67.3639 | 7.6051 | 83.6679 | 6.5626 | 14.8011 | 51.9521 | 112.0472 | 15.8161 | 280.9238 | 174.6413 | 358.2665 | 10.2281 | 66.4938 | 15.8307 | 191 | 10.6062 | 158.2982 | 307.6986 | 0
1605 | 915.9448 | 4.5535 | 58.7686 | 106.6205 | 66.6045 | 8.3265 | 74.4696 | 6.5866 | 15.5042 | 47.5679 | 101.0489 | 10.228 | 244.9089 | 149.4284 | 309.1343 | 9.8198 | 61.4068 | 15.7571 | 166 | 10.7476 | 146.9522 | 287.8842 | 0
1606 | 870.728 | 3.922 | 48.4299 | 103.3712 | 66.3836 | 8.5363 | 76.164 | 6.5566 | 11.842 | 43.0423 | 93.9374 | 8.9938 | 212.2115 | 143.0813 | 281.3255 | 9.7903 | 58.5024 | 15.0795 | 151 | 10.5489 | 134.8399 | 280.1645 | 0
1607 | 834.3046 | 3.0234 | 48.5285 | 98.9998 | 67.9052 | 7.0909 | 76.0066 | 6.4462 | 7.6593 | 38.4831 | 81.2897 | 8.3152 | 189.8461 | 128.3592 | 262.3521 | 9.725 | 56.7946 | 14.3198 | 136 | 10.4408 | 119.7929 | 277.7664 | 0
1608 | 813.861 | 2.0055 | 48.275 | 99.3869 | 67.5984 | 7.3823 | 72.7153 | 6.7359 | 6.5001 | 35.4503 | 73.7314 | 8.0708 | 178.5853 | 111.7753 | 246.9072 | 9.6923 | 55.8642 | 13.8149 | 122 | 10.5908 | 89.2828 | 276.7935 | 0
1609 | 809.0406 | 1.3354 | 47.5142 | 100.4023 | 67.3636 | 7.6054 | 74.329 | 6.6132 | 6.3733 | 35.9123 | 73.7494 | 8.0807 | 173.5358 | 110.1428 | 241.0628 | 9.7024 | 55.4748 | 13.4962 | 113 | 10.7014 | 77.9622 | 271.7613 | 0
1610 | 798.3748 | 1.2442 | 43.781 | 100.7415 | 67.3247 | 7.6424 | 81.5718 | 6.4366 | 6.372 | 35.0217 | 75.4008 | 8.111 | 173.1885 | 96.567 | 232.1254 | 9.6867 | 55.135 | 13.1759 | 102 | 10.6833 | 75.993 | 270.3305 | 0
1611 | 782.6719 | 1.4187 | 41.2394 | 100.804 | 66.6075 | 8.3237 | 75.4082 | 6.4322 | 6.4167 | 34.1059 | 77.894 | 8.1062 | 170.125 | 90.7857 | 230.2093 | 9.6864 | 55.0711 | 12.6521 | 120 | 10.6721 | 76.3717 | 268.7821 | 0
1612 | 775.5318 | 1.2659 | 40.7957 | 99.2586 | 67.2007 | 7.7601 | 71.3563 | 6.4854 | 6.5042 | 37.0079 | 79.5575 | 8.282 | 168.4616 | 90.002 | 230.8898 | 9.6691 | 55.056 | 12.2593 | 97 | 10.6559 | 79.0302 | 269.5857 | 0
1613 | 788.4153 | 1.5673 | 40.7294 | 99.1427 | 67.3882 | 7.582 | 79.9685 | 6.7587 | 6.5948 | 47.2465 | 78.3606 | 8.1581 | 171.8258 | 90.5013 | 226.7085 | 9.6833 | 56.6848 | 11.8381 | 98 | 10.6792 | 79.7684 | 293.9712 | 0
1614 | 793.6851 | 2.8425 | 48.8761 | 100.3098 | 66.6353 | 8.2973 | 78.5747 | 6.6492 | 6.6343 | 54.5431 | 74.8613 | 10.9009 | 176.0429 | 104.1207 | 231.5246 | 9.7144 | 59.1781 | 11.6468 | 101 | 10.7382 | 85.4216 | 325.378 | 0
1615 | 832.8944 | 4.7949 | 74.1887 | 103.6321 | 64.0106 | 10.7907 | 79.0586 | 6.713 | 8.3095 | 67.2901 | 85.057 | 18.5854 | 224.4127 | 168.032 | 258.7105 | 13.0426 | 56.2808 | 11.5095 | 161 | 10.7809 | 127.3438 | 369.0751 | 0
1616 | 901.4288 | 5.0938 | 91.2235 | 107.8654 | 60.2827 | 14.3322 | 106.4128 | 7.4108 | 17.0659 | 84.8461 | 126.2962 | 31.5528 | 304.4874 | 229.2775 | 356.2845 | 27.5718 | 61.0608 | 12.3481 | 288 | 16.3676 | 171.3116 | 433.9983 | 0.020296
1617 | 997.8418 | 4.5287 | 101.6582 | 122.2785 | 57.8043 | 16.6867 | 127.4757 | 8.054 | 19.9587 | 82.5556 | 162.7155 | 34.7767 | 390.3024 | 287.9975 | 488.4026 | 34.8766 | 71.299 | 16.9507 | 301 | 19.0501 | 201.9779 | 493.6506 | 0.05178
1618 | 1102.0136 | 4.072 | 108.9321 | 137.8212 | 59.746 | 14.8421 | 133.9644 | 8.9505 | 19.8373 | 86.1673 | 177.9845 | 37.5929 | 441.3838 | 324.5136 | 590.9564 | 38.2795 | 81.911 | 18.2705 | 337 | 18.127 | 232.9686 | 525.381 | 0.10006
1619 | 1162.1441 | 3.9041 | 112.0686 | 141.7631 | 56.558 | 17.8707 | 144.3896 | 9.6873 | 20.789 | 90.8517 | 189.1054 | 40.2751 | 459.2422 | 351.0555 | 633.9335 | 39.2225 | 88.6879 | 18.832 | 342 | 20.4364 | 253.7692 | 546.3632 | 0.083844
1620 | 1188.3184 | 4.1258 | 113.2869 | 140.9717 | 58.3817 | 16.1381 | 145.2842 | 9.5306 | 21.481 | 100.6202 | 187.7053 | 40.9959 | 461.7235 | 360.1711 | 632.4301 | 38.9434 | 89.341 | 18.9845 | 328 | 19.2051 | 252.2108 | 559.3436 | 0.093696
1621 | 1157.1907 | 6.1507 | 113.5934 | 139.5581 | 58.5598 | 15.969 | 140.0604 | 9.7079 | 20.698 | 103.4721 | 184.7455 | 41.1472 | 462.8651 | 355.1243 | 602.2312 | 40.9727 | 87.1 | 18.8528 | 357 | 21.6573 | 235.1898 | 549.5393 | 0.14673
1622 | 1144.8095 | 8.4895 | 115.0462 | 141.6163 | 56.0798 | 18.325 | 147.1023 | 10.449 | 20.0473 | 115.9915 | 194.1687 | 41.5883 | 468.1523 | 363.3617 | 607.5456 | 42.4172 | 86.3213 | 18.9659 | 304 | 20.4526 | 237.4764 | 543.1075 | 0.063908
1623 | 1147.8779 | 5.6005 | 112.1509 | 142.7083 | 58.4955 | 16.03 | 144.4417 | 10.0501 | 20.0655 | 116.9985 | 205.0474 | 41.5164 | 472.9462 | 379.0698 | 602.7325 | 41.7334 | 86.5799 | 19.4426 | 264 | 20.0893 | 246.7214 | 551.4616 | 0.10929
1624 | 1148.1431 | 4.1145 | 111.1151 | 144.0121 | 58.5674 | 15.9618 | 139.4549 | 8.6009 | 19.707 | 112.1801 | 206.0763 | 40.5828 | 455.0689 | 356.2734 | 572.4366 | 39.9786 | 88.0996 | 19.5023 | 290 | 18.2291 | 245.0937 | 549.0912 | 0.092618
1625 | 1114.1338 | 4.419 | 107.1442 | 140.2896 | 57.6351 | 16.8474 | 129.0861 | 7.8659 | 18.506 | 107.4 | 194.0299 | 37.904 | 421.924 | 335.8878 | 517.8019 | 34.2628 | 85.8456 | 18.3547 | 266 | 16.415 | 224.4302 | 485.1131 | 0.046587
1626 | 1075.3707 | 5.4808 | 102.4862 | 121.1507 | 64.9859 | 9.8642 | 105.8765 | 8.6269 | 18.1456 | 91.8901 | 175.8729 | 33.4777 | 365.1239 | 274.0689 | 431.6384 | 19.8675 | 79.6366 | 17.1334 | 222 | 15.6971 | 208.0384 | 388.2211 | 0.0029637
1627 | 1026.8283 | 5.174 | 99.2701 | 109.5646 | 68.162 | 6.8468 | 96.3799 | 7.3119 | 16.3833 | 70.2447 | 143.8747 | 28.8721 | 313.5334 | 223.5459 | 379.431 | 12.8168 | 73.5662 | 16.1188 | 203 | 15.515 | 190.7979 | 349.2992 | 0
1628 | 982.9787 | 4.1514 | 90.3576 | 105.9873 | 68.4152 | 6.6064 | 84.8558 | 6.5904 | 10.8983 | 55.5757 | 114.9261 | 15.2153 | 278.5381 | 192.9479 | 349.5259 | 11.4214 | 65.2226 | 15.3636 | 186 | 15.4708 | 171.6119 | 306.9398 | 0
1629 | 928.2018 | 4.1933 | 60.5942 | 103.3185 | 66.8113 | 8.13 | 70.6491 | 6.3611 | 7.8948 | 52.3718 | 106.7573 | 12.229 | 251.5837 | 171.2565 | 304.8785 | 10.7486 | 57.6178 | 15.1592 | 179 | 15.6117 | 157.8655 | 293.5087 | 0
1630 | 885.2587 | 4.0575 | 48.9892 | 100.7294 | 68.6864 | 6.3487 | 65.7301 | 6.3588 | 7.0523 | 48.3917 | 100.6066 | 12.7779 | 211.0607 | 155.6544 | 262.8293 | 10.455 | 55.0835 | 14.0704 | 167 | 15.738 | 145.1053 | 283.6475 | 0
1631 | 858.1341 | 3.3557 | 48.5442 | 98.2174 | 68.6163 | 6.4153 | 73.3663 | 6.4428 | 6.3623 | 41.8389 | 85.0752 | 10.1059 | 183.5417 | 144.0473 | 249.0002 | 10.4834 | 53.7929 | 12.7913 | 139 | 15.4962 | 128.3281 | 285.7222 | 0
1632 | 829.9516 | 2.029 | 48.5583 | 97.4058 | 69.0827 | 5.9722 | 69.1057 | 6.3816 | 6.2583 | 37.145 | 78.3585 | 8.2162 | 169.6231 | 137.8952 | 243.1631 | 10.6286 | 53.5669 | 11.9613 | 116 | 15.3543 | 101.1021 | 278.9496 | 0
1633 | 823.5534 | 1.5259 | 47.8879 | 98.0548 | 68.6102 | 6.4211 | 66.0267 | 6.4295 | 6.2427 | 37.2779 | 79.297 | 8.1476 | 164.1777 | 142.7362 | 248.1476 | 10.5319 | 53.7064 | 11.8112 | 109 | 15.6534 | 88.8693 | 273.825 | 0
1634 | 827.7833 | 1.371 | 47.6947 | 99.8118 | 67.6197 | 7.3621 | 71.6914 | 6.6789 | 6.1833 | 37.8039 | 79.7962 | 8.0335 | 166.5075 | 132.0555 | 249.5629 | 10.5593 | 53.5364 | 11.8915 | 106 | 15.832 | 87.314 | 274.4047 | 0
1635 | 815.2215 | 1.3348 | 47.6054 | 99.6066 | 68.1213 | 6.8855 | 75.6276 | 6.6037 | 6.4193 | 36.5102 | 79.5862 | 8.163 | 166.9974 | 125.6215 | 240.7489 | 10.5036 | 53.4937 | 11.77 | 121 | 15.6101 | 86.8265 | 273.0625 | 0
1636 | 808.3914 | 1.5366 | 47.6213 | 100.014 | 69.1712 | 5.8882 | 68.9123 | 6.5824 | 6.3452 | 37.4491 | 79.6399 | 8.003 | 167.5294 | 120.5004 | 231.1848 | 10.5294 | 53.2851 | 11.701 | 103 | 15.6135 | 86.9294 | 275.6197 | 0
1637 | 802.1295 | 2.126 | 47.774 | 105.239 | 69.3472 | 5.7209 | 66.1656 | 6.6409 | 5.9948 | 48.5442 | 79.3257 | 7.9213 | 163.725 | 119.005 | 225.8295 | 10.4678 | 54.8903 | 11.6746 | 100 | 15.6671 | 85.5845 | 292.1737 | 0
1638 | 822.535 | 3.1107 | 64.489 | 108.7284 | 67.8283 | 7.1639 | 75.3053 | 6.5499 | 7.5475 | 55.2311 | 79.6881 | 9.136 | 176.1022 | 123.0129 | 231.1213 | 10.5109 | 57.3804 | 11.6842 | 118 | 15.273 | 89.7307 | 328.022 | 0
1639 | 861.6721 | 4.3456 | 84.7472 | 113.2652 | 64.2734 | 10.5411 | 82.7591 | 6.9574 | 10.4091 | 68.9505 | 91.1424 | 19.6364 | 211.1987 | 163.1093 | 259.0213 | 13.427 | 55.0656 | 11.6399 | 170 | 15.3928 | 131.8974 | 372.6127 | 0
1640 | 928.4001 | 5.0507 | 95.4822 | 117.7905 | 61.1716 | 13.4877 | 102.4854 | 7.5467 | 13.708 | 90.5174 | 130.3063 | 32.2135 | 290.3103 | 228.6327 | 362.3983 | 28.0501 | 59.1939 | 12.5584 | 281 | 20.4246 | 176.5227 | 431.6915 | 0.027272
1641 | 1004.5332 | 11.3349 | 103.8458 | 130.5136 | 59.4703 | 15.104 | 115.7869 | 8.7337 | 15.4671 | 96.725 | 161.1016 | 34.8034 | 367.9782 | 283.5151 | 465.9912 | 36.963 | 66.0021 | 14.2946 | 280 | 22.5871 | 215.4641 | 511.7331 | 0.074332
1642 | 1098.8689 | 12.7023 | 110.8695 | 140.3131 | 57.7927 | 16.6977 | 136.3841 | 9.6129 | 17.9056 | 104.927 | 175.4752 | 35.9291 | 413.4401 | 315.9994 | 529.2936 | 40.5713 | 77.5074 | 15.778 | 313 | 24.0798 | 250.1667 | 559.5214 | 0.1604
1643 | 1161.5871 | 9.1286 | 110.9265 | 142.6945 | 56.6694 | 17.7649 | 147.7884 | 8.8437 | 21.3467 | 121.2463 | 181.2304 | 38.6175 | 423.7358 | 344.0788 | 555.75 | 43.0421 | 85.7487 | 17.429 | 348 | 27.8587 | 262.6419 | 577.0861 | 0.15809
1644 | 1194.0371 | 7.79 | 115.0741 | 141.9967 | 58.6937 | 15.8418 | 147.1819 | 9.1115 | 24.1313 | 121.472 | 183.277 | 42.3391 | 428.5883 | 359.7528 | 576.5118 | 41.5985 | 88.0935 | 18.0167 | 313 | 27.3273 | 253.6385 | 587.7168 | 0.21004
1645 | 1194.0092 | 7.4236 | 112.4863 | 141.892 | 60.134 | 14.4735 | 153.7308 | 9.1653 | 23.951 | 118.1326 | 181.9081 | 42.4193 | 425.7366 | 360.9114 | 570.3374 | 41.8896 | 87.102 | 17.9199 | 329 | 27.6314 | 235.1558 | 598.6462 | 0.23706
1646 | 1199.5206 | 5.9218 | 113.3424 | 141.2396 | 59.5977 | 14.983 | 150.5174 | 9.7378 | 22.8939 | 114.1116 | 195.7034 | 40.871 | 428.3915 | 363.9809 | 561.8209 | 41.2834 | 85.325 | 17.9816 | 327 | 27.7654 | 242.1196 | 587.0957 | 0.17305
1647 | 1214.9008 | 4.7473 | 112.4832 | 142.4285 | 57.0982 | 17.3575 | 148.3309 | 9.2306 | 21.8008 | 114.6359 | 195.5913 | 41.985 | 429.2247 | 370.1424 | 562.4863 | 39.5102 | 84.5543 | 18.0095 | 278 | 27.5764 | 240.3277 | 600.6228 | 0.16261
1648 | 1209.0756 | 4.4494 | 110.0575 | 147.3254 | 56.367 | 18.0521 | 150.065 | 8.5744 | 20.9729 | 128.046 | 191.344 | 42.6548 | 415.3392 | 349.6447 | 553.0271 | 36.9979 | 83.7329 | 18.3634 | 295 | 24.5946 | 229.2776 | 589.0491 | 0.14727
1649 | 1176.7355 | 5.4525 | 105.8055 | 135.7131 | 60.2047 | 14.4063 | 147.1757 | 8.0971 | 20.6597 | 113.2818 | 187.4525 | 39.8516 | 387.6447 | 315.8545 | 516.5817 | 31.9092 | 81.9818 | 18.5792 | 273 | 23.472 | 206.2541 | 509.1418 | 0.050945
1650 | 1099.2063 | 5.4915 | 101.9032 | 118.4691 | 64.4751 | 10.3494 | 143.0489 | 7.1562 | 18.2335 | 85.3845 | 171.7298 | 37.9734 | 339.5076 | 247.4562 | 427.6048 | 20.6429 | 75.2935 | 17.4353 | 240 | 24.2918 | 184.3338 | 425.0691 | 0.008972
1651 | 1037.774 | 4.9599 | 98.299 | 109.0046 | 66.7866 | 8.1535 | 131.0384 | 6.9816 | 16.487 | 61.8108 | 141.9282 | 36.7652 | 301.9217 | 207.5972 | 370.9925 | 13.0147 | 69.9663 | 17.5178 | 232 | 23.2141 | 177.359 | 406.4863 | 0
1652 | 1005.0184 | 4.5651 | 86.9332 | 105.6314 | 68.1305 | 6.8768 | 108.9779 | 7.0293 | 11.4912 | 51.2275 | 114.9315 | 25.9881 | 273.2623 | 181.6704 | 319.1558 | 10.4615 | 64.8268 | 16.9306 | 198 | 22.1222 | 167.6761 | 369.1296 | 0
1653 | 949.4776 | 4.0309 | 58.2752 | 102.6201 | 69.1839 | 5.8761 | 98.9796 | 6.8351 | 8.749 | 49.3163 | 105.8888 | 18.315 | 232.3737 | 161.7353 | 281.0881 | 9.7534 | 58.6072 | 15.6801 | 178 | 21.415 | 155.6635 | 344.852 | 0
1654 | 906.8758 | 4.2191 | 48.41 | 99.3309 | 69.3719 | 5.6974 | 89.2024 | 6.7865 | 7.9106 | 45.0912 | 102.4498 | 19.1334 | 208.4559 | 139.4083 | 256.6682 | 9.5108 | 55.6527 | 14.8041 | 156 | 18.2028 | 144.4231 | 331.906 | 0
1655 | 872.4126 | 3.4373 | 47.5258 | 97.8724 | 67.0971 | 7.8586 | 86.6789 | 6.5871 | 6.5836 | 38.5364 | 87.2563 | 16.1285 | 181.7721 | 119.1452 | 243.1339 | 9.6025 | 55.4206 | 13.7708 | 135 | 17.5551 | 124.7577 | 330.6485 | 0
1656 | 848.4227 | 2.3563 | 46.7341 | 98.0213 | 68.6571 | 6.3765 | 83.6968 | 6.7645 | 5.9599 | 36.6855 | 77.6254 | 10.6937 | 168.5679 | 110.645 | 233.7288 | 9.5435 | 55.2716 | 13.2344 | 120 | 17.6279 | 97.3131 | 332.4043 | 0
1657 | 841.3466 | 1.7784 | 46.4248 | 102.1727 | 69.3722 | 5.6972 | 72.0922 | 6.9865 | 5.7439 | 37.0098 | 75.2677 | 9.2103 | 165.9279 | 110.7659 | 225.6616 | 9.5475 | 55.2071 | 14.2691 | 113 | 17.533 | 87.7679 | 326.4098 | 0
1658 | 831.8928 | 1.6053 | 46.4424 | 105.2927 | 69.3856 | 5.6845 | 72.9313 | 6.9133 | 5.7846 | 36.9056 | 76.536 | 9.064 | 173.3868 | 105.1374 | 221.0032 | 9.5778 | 54.5302 | 14.5634 | 105 | 17.5901 | 85.3412 | 321.7037 | 0
1659 | 822.8287 | 2.064 | 46.6394 | 103.5059 | 68.6611 | 6.3727 | 81.4329 | 6.8322 | 6.0923 | 37.113 | 77.3611 | 8.9832 | 168.6387 | 96.8804 | 219.448 | 9.5149 | 53.7928 | 14.3463 | 123 | 17.4432 | 83.0244 | 323.3506 | 0
1660 | 809.9494 | 1.6814 | 46.7698 | 101.3144 | 69.067 | 5.9871 | 75.2625 | 7.1967 | 5.9473 | 39.3522 | 76.7534 | 9.1438 | 164.8165 | 93.6389 | 218.7848 | 9.6094 | 53.3378 | 14.347 | 101 | 17.4248 | 83.9454 | 324.7489 | 0
1661 | 810.3285 | 1.9348 | 46.2115 | 101.7253 | 69.328 | 5.7392 | 71.7046 | 6.9518 | 5.886 | 50.9545 | 76.0344 | 9.1211 | 162.6952 | 93.0688 | 215.7715 | 9.4464 | 54.9847 | 13.7416 | 102 | 17.477 | 83.5324 | 344.7389 | 0
1662 | 827.6979 | 2.8857 | 46.8555 | 101.6085 | 67.8301 | 7.1622 | 81.1102 | 6.6788 | 5.9807 | 58.0269 | 77.4519 | 10.2019 | 171.1505 | 104.9724 | 221.3296 | 9.4971 | 57.5692 | 13.1582 | 118 | 17.4909 | 87.7285 | 380.4202 | 0
1663 | 867.2648 | 4.7944 | 59.0224 | 107.0882 | 66.6232 | 8.3088 | 84.8718 | 6.6491 | 8.1293 | 69.0956 | 88.8706 | 17.4607 | 211.9275 | 164.3054 | 236.6349 | 12.0348 | 54.5496 | 13.3693 | 192 | 18.2325 | 132.0549 | 422.3978 | 0
1664 | 948.2518 | 4.6146 | 82.2121 | 112.4105 | 62.5011 | 12.2247 | 104.2541 | 7.694 | 15.588 | 95.1772 | 127.2451 | 31.91 | 273.7501 | 223.1779 | 329.5109 | 26.657 | 58.2675 | 13.5635 | 269 | 26.3938 | 176.4249 | 494.2696 | 0.18392
1665 | 1052.4837 | 7.1868 | 97.0341 | 123.955 | 60.5971 | 14.0335 | 122.2885 | 8.4969 | 18.218 | 100.5844 | 159.2043 | 40.4416 | 352.8725 | 272.5661 | 436.5279 | 37.007 | 66.8688 | 15.7231 | 305 | 27.8673 | 207.5394 | 545.6561 | 0.24627
1666 | 1131.5675 | 9.4515 | 106.4332 | 135.1719 | 56.5296 | 17.8977 | 137.6192 | 8.3585 | 18.2649 | 105.9575 | 175.4112 | 42.2451 | 402.8185 | 319.5617 | 516.5667 | 41.642 | 76.0894 | 17.3671 | 345 | 26.9232 | 235.5834 | 568.7348 | 0.25929
1667 | 1158.2716 | 6.399 | 111.5141 | 138.8318 | 55.5032 | 18.8727 | 141.5809 | 7.7492 | 20.0075 | 107.5817 | 181.119 | 45.5757 | 421.9789 | 352.93 | 556.3651 | 41.9943 | 80.3047 | 17.6921 | 325 | 25.0654 | 253.4099 | 581.9313 | 0.23203
1668 | 1187.8452 | 4.3998 | 112.3277 | 139.9882 | 56.7704 | 17.6689 | 156.4889 | 7.6466 | 21.1555 | 114.2867 | 184.7315 | 40.1546 | 427.6709 | 373.8043 | 578.456 | 42.8293 | 83.4716 | 17.3166 | 327 | 23.8059 | 255.719 | 582.3416 | 0.23325
1669 | 1200.5123 | 4.2423 | 110.3713 | 138.3058 | 57.3364 | 17.1312 | 170.6503 | 7.7693 | 20.1362 | 112.3592 | 184.4346 | 38.678 | 423.1286 | 364.3294 | 557.5748 | 44.4549 | 84.4042 | 17.2799 | 340 | 24.756 | 239.7799 | 595.1438 | 0.22352
1670 | 1194.6885 | 4.1056 | 111.2773 | 141.8058 | 55.0635 | 19.2905 | 163.0678 | 7.8779 | 22.9193 | 121.1993 | 191.751 | 38.8084 | 432.924 | 358.0557 | 550.3535 | 44.7615 | 88.1207 | 17.5197 | 294 | 21.4221 | 242.9011 | 607.3572 | 0.11186
1671 | 1198.8632 | 3.8557 | 111.8921 | 145.3039 | 55.324 | 19.043 | 147.8475 | 7.5996 | 23.4974 | 114.1504 | 189.8417 | 41.0013 | 443.0181 | 365.01 | 575.1617 | 44.115 | 87.034 | 17.8359 | 298 | 22.105 | 245.9568 | 606.0132 | 0.1209
1672 | 1181.5574 | 3.9305 | 111.0009 | 148.9318 | 53.7291 | 20.5582 | 163.1668 | 7.194 | 20.8449 | 109.3372 | 184.1083 | 39.1693 | 432.8969 | 348.6091 | 569.9718 | 41.1271 | 85.3962 | 18.4064 | 308 | 20.2796 | 237.3553 | 593.5262 | 0.076865
1673 | 1135.654 | 4.1638 | 106.4796 | 142.5488 | 57.1831 | 17.2769 | 159.0789 | 6.7803 | 19.213 | 104.0179 | 180.4745 | 36.6285 | 398.6313 | 327.5017 | 513.5899 | 33.7449 | 82.6968 | 18.8665 | 279 | 17.4468 | 227.9615 | 508.7653 | 0.03234
1674 | 1074.8195 | 5.1003 | 104.2945 | 123.2681 | 63.0071 | 11.7441 | 148.2955 | 6.2727 | 17.8627 | 87.7236 | 170.281 | 34.7279 | 341.2254 | 264.2201 | 405.1302 | 17.8662 | 76.1061 | 19.6021 | 231 | 16.8546 | 195.4447 | 410.7588 | 0.0024287
1675 | 1014.4075 | 4.9662 | 101.4439 | 112.4258 | 67.4739 | 7.5006 | 125.7046 | 6.1246 | 15.7281 | 69.1727 | 140.9895 | 31.2068 | 299.6742 | 218.6799 | 352.5802 | 11.401 | 70.6684 | 18.9063 | 206 | 17.0752 | 174.4731 | 363.7335 | 0
1676 | 962.4364 | 4.1449 | 91.4757 | 107.2967 | 69.1383 | 5.9194 | 98.6276 | 6.2344 | 10.3194 | 58.3269 | 112.693 | 23.705 | 260.3181 | 196.5763 | 328.8121 | 10.413 | 63.1776 | 17.7018 | 183 | 16.7127 | 158.6966 | 320.7004 | 0
1677 | 929.4176 | 3.8361 | 58.342 | 103.5788 | 68.5867 | 6.4435 | 89.4174 | 6.1252 | 8.3939 | 54.8941 | 103.991 | 20.3554 | 231.7204 | 164.5324 | 318.6661 | 10.0547 | 57.1221 | 16.4268 | 175 | 16.7424 | 152.9461 | 292.497 | 0
1678 | 890.9057 | 4.0249 | 42.5724 | 101.2953 | 69.1213 | 5.9355 | 85.4306 | 6.1866 | 8.0339 | 53.4758 | 99.1965 | 19.7466 | 212.0886 | 135.832 | 307.7665 | 10.0199 | 55.2748 | 14.8154 | 173 | 16.7788 | 147.6043 | 272.8305 | 0
1679 | 861.1831 | 3.3498 | 39.8882 | 99.9712 | 69.3779 | 5.6918 | 85.4525 | 6.5756 | 7.5027 | 46.235 | 85.5652 | 19.1708 | 197.3581 | 120.6151 | 286.2555 | 9.9918 | 54.8917 | 14.1195 | 145 | 16.8116 | 135.1914 | 265.5357 | 0
1680 | 835.477 | 1.938 | 38.5584 | 99.798 | 68.5856 | 6.4445 | 84.6043 | 6.7286 | 7.0721 | 42.6903 | 78.2708 | 14.8196 | 174.8993 | 115.3732 | 246.5738 | 9.9717 | 55.1816 | 13.8403 | 119 | 16.7719 | 102.9103 | 264.0792 | 0
1681 | 833.8563 | 1.5731 | 38.6605 | 98.9269 | 69.0959 | 5.9597 | 74.7127 | 6.6427 | 7.2088 | 44.0409 | 76.6087 | 9.0986 | 167.2901 | 109.2436 | 230.3518 | 9.9742 | 55.2331 | 13.5826 | 108 | 16.8422 | 92.3232 | 257.1752 | 0
1682 | 831.8307 | 1.5644 | 38.9586 | 97.8381 | 68.634 | 6.3985 | 71.4919 | 6.6372 | 7.2638 | 46.3336 | 76.3078 | 7.5232 | 166.2441 | 103.2363 | 225.3899 | 9.9467 | 54.642 | 13.2768 | 105 | 16.9629 | 93.9577 | 258.6122 | 0
1683 | 817.8701 | 1.6394 | 38.4909 | 97.2981 | 69.1509 | 5.9074 | 81.8817 | 6.9183 | 7.1913 | 46.4619 | 76.7277 | 7.718 | 164.4909 | 98.9478 | 220.9766 | 10.018 | 54.5532 | 12.7068 | 122 | 16.9829 | 91.8136 | 262.7155 | 0
1684 | 817.1301 | 1.6347 | 38.3368 | 97.2826 | 67.9231 | 7.0739 | 80.2312 | 6.9507 | 7.1271 | 48.5267 | 77.1746 | 7.6027 | 164.7275 | 95.1097 | 216.9577 | 10.0448 | 54.6863 | 12.8172 | 101 | 16.9297 | 90.7894 | 263.8246 | 0
1685 | 805.6051 | 1.9424 | 38.3574 | 97.4081 | 67.3392 | 7.6286 | 73.9047 | 7.3047 | 7.1821 | 58.6976 | 78.6426 | 7.5056 | 164.6458 | 94.2492 | 214.2859 | 9.9849 | 56.3627 | 12.585 | 100 | 16.9215 | 90.8694 | 288.9495 | 0
1686 | 812.8141 | 3.0748 | 46.4717 | 98.9147 | 67.3306 | 7.6367 | 73.7872 | 7.4023 | 7.4142 | 63.7482 | 80.0016 | 9.6203 | 168.6929 | 106.4435 | 218.0359 | 9.9202 | 59.5527 | 12.4083 | 122 | 16.8282 | 94.9929 | 321.8563 | 0
1687 | 860.3034 | 4.4806 | 74.707 | 104.3406 | 66.572 | 8.3574 | 92.1973 | 7.9812 | 9.8537 | 71.8232 | 89.9206 | 14.7229 | 205.2448 | 162.4904 | 236.6054 | 12.6766 | 56.4926 | 12.2697 | 177 | 17.3677 | 138.4337 | 374.3891 | 0
1688 | 946.229 | 4.4858 | 84.0817 | 104.9872 | 60.992 | 13.6584 | 113.9142 | 7.9189 | 14.7105 | 90.2924 | 130.543 | 26.911 | 265.6906 | 233.8317 | 338.721 | 26.187 | 59.9196 | 13.6759 | 233 | 21.6972 | 180.7239 | 432.3684 | 0.04501
1689 | 1027.8101 | 4.3041 | 102.1915 | 115.0536 | 58.6795 | 15.8552 | 122.9082 | 8.0826 | 15.3733 | 99.0601 | 167.7029 | 34.3166 | 334.0629 | 271.5148 | 464.0713 | 35.5573 | 68.9238 | 15.4081 | 316 | 23.541 | 206.7585 | 496.3594 | 0.067007
1690 | 1102.4265 | 3.9649 | 114.9825 | 129.3045 | 58.3567 | 16.1619 | 138.435 | 7.9348 | 17.4478 | 103.7085 | 183.1085 | 33.7491 | 383.2013 | 292.8231 | 541.7454 | 40.2113 | 81.6251 | 15.4722 | 340 | 24.4222 | 228.666 | 526.8668 | 0.20807
1691 | 1146.205 | 4.2681 | 112.3311 | 135.8071 | 58.3941 | 16.1264 | 148.9172 | 7.8041 | 20.421 | 102.7241 | 183.5677 | 37.8607 | 403.5109 | 321.3549 | 564.0912 | 42.7866 | 88.9159 | 16.4785 | 346 | 26.1458 | 236.5325 | 517.0682 | 0.15062
1692 | 1174.6428 | 4.315 | 115.7007 | 134.1597 | 57.4959 | 16.9797 | 151.5117 | 7.5288 | 20.953 | 105.8034 | 185.1037 | 40.0246 | 408.7731 | 333.939 | 568.8435 | 42.2022 | 87.55 | 16.8141 | 354 | 22.2392 | 234.3134 | 519.6222 | 0.20055
1693 | 1153.2782 | 4.139 | 117.7581 | 135.3083 | 57.4354 | 17.0371 | 152.3608 | 7.3275 | 19.2642 | 106.4542 | 183.0285 | 39.6252 | 405.4971 | 326.0071 | 550.3692 | 44.434 | 85.3674 | 16.7347 | 374 | 24.3359 | 219.5308 | 514.6246 | 0.16869
1694 | 1139.0194 | 3.9065 | 117.661 | 139.3199 | 58.1097 | 16.3965 | 144.2449 | 7.812 | 19.8714 | 105.1294 | 183.2091 | 39.9442 | 406.0332 | 344.5028 | 542.3954 | 44.4973 | 86.4356 | 17.8964 | 308 | 24.884 | 226.8574 | 577.9897 | 0.14254
1695 | 1123.9821 | 4.0386 | 116.8113 | 141.8571 | 57.5779 | 16.9018 | 136.8107 | 7.5868 | 19.0926 | 105.2603 | 184.8721 | 40.193 | 409.1926 | 342.0893 | 539.4361 | 41.2933 | 86.6877 | 18.3129 | 278 | 24.3858 | 229.107 | 595.3755 | 0.063117
1696 | 1116.3448 | 3.9826 | 114.2833 | 138.083 | 54.3801 | 19.9397 | 132.5055 | 6.6627 | 19.0555 | 108.206 | 182.5645 | 39.4509 | 394.1587 | 334.5381 | 516.1328 | 37.1686 | 85.5426 | 18.6372 | 290 | 21.6548 | 222.5453 | 575.7806 | 0.15645
1697 | 1087.0972 | 3.7678 | 110.1767 | 131.7634 | 61.7429 | 12.945 | 124.2083 | 6.1336 | 21.6399 | 104.7042 | 172.0296 | 38.1413 | 365.6633 | 297.0769 | 457.2615 | 24.6844 | 81.4653 | 18.7772 | 272 | 19.1466 | 199.9503 | 510.6868 | 0.067257
1698 | 1031.6539 | 3.8839 | 101.6411 | 120.2304 | 67.4466 | 7.5265 | 111.8358 | 5.7329 | 22.0124 | 85.9269 | 157.0614 | 34.4143 | 319.8523 | 223.4276 | 384.0675 | 17.4117 | 74.1021 | 19.1232 | 245 | 18.8678 | 177.1096 | 428.9619 | 0.0046448
1699 | 969.2991 | 4.3325 | 97.0604 | 108.9189 | 68.3558 | 6.6628 | 101.4845 | 6.0044 | 20.6267 | 63.6842 | 128.6327 | 31.7215 | 273.2283 | 172.8049 | 329.5185 | 17.8265 | 68.2848 | 19.5688 | 220 | 18.6446 | 166.2637 | 380.8202 | 0
1700 | 906.9093 | 3.9984 | 84.939 | 104.6041 | 69.1527 | 5.9057 | 89.1451 | 5.8437 | 12.5565 | 53.1157 | 99.1371 | 21.7729 | 245.4505 | 160.6063 | 284.9547 | 18.7991 | 62.4745 | 18.3863 | 199 | 18.4344 | 147.459 | 351.9803 | 0
1701 | 869.9676 | 3.9442 | 51.4456 | 103.9185 | 69.3529 | 5.7155 | 91.5677 | 5.8281 | 9.1181 | 50.8972 | 80.7166 | 15.2224 | 223.022 | 148.5977 | 255.954 | 22.834 | 58.1536 | 17.2645 | 185 | 18.4498 | 134.275 | 334.9586 | 0
1702 | 847.9879 | 3.4869 | 41.1956 | 101.5964 | 69.352 | 5.7164 | 85.8782 | 5.9184 | 8.4707 | 50.1703 | 76.8679 | 14.7282 | 207.1259 | 141.0247 | 257.4155 | 27.1198 | 56.6753 | 17.7871 | 167 | 18.4736 | 127.1037 | 324.2653 | 0
1703 | 834.8567 | 3.1577 | 40.9573 | 99.7762 | 69.4195 | 5.6523 | 71.445 | 5.9271 | 7.1046 | 46.0483 | 74.0366 | 14.0497 | 187.9402 | 130.537 | 252.611 | 29.0615 | 56.0423 | 16.1377 | 136 | 18.2729 | 116.4082 | 319.4857 | 0
1704 | 811.7317 | 2.0754 | 40.8076 | 99.2062 | 68.5903 | 6.44 | 70.8562 | 5.7914 | 6.7171 | 44.7753 | 71.6662 | 13.633 | 180.6285 | 123.6768 | 249.2536 | 28.736 | 56.0014 | 15.0935 | 131 | 18.8481 | 88.9686 | 314.8171 | 0
1705 | 814.0516 | 1.5793 | 40.2951 | 97.4371 | 69.1499 | 5.9084 | 80.0792 | 5.9887 | 6.6253 | 45.5201 | 71.091 | 13.0114 | 178.6569 | 120.4603 | 240.7461 | 28.2255 | 55.8188 | 14.8102 | 120 | 19.0265 | 78.9671 | 318.5294 | 0
1706 | 802.0794 | 1.4806 | 39.7781 | 96.595 | 69.3496 | 5.7187 | 72.7632 | 5.9651 | 6.8276 | 45.4079 | 71.2473 | 12.4543 | 164.1081 | 118.1136 | 240.9456 | 29.4143 | 55.7455 | 14.4824 | 128 | 19.1366 | 78.2673 | 326.1296 | 0
1707 | 788.5317 | 1.4451 | 39.8787 | 96.182 | 69.3529 | 5.7155 | 65.325 | 5.8686 | 6.5786 | 45.1473 | 72.4326 | 12.3331 | 154.352 | 103.3856 | 240.4178 | 28.7642 | 55.6597 | 13.8935 | 142 | 19.1801 | 75.0344 | 325.6133 | 0
1708 | 788.6323 | 1.5834 | 39.8176 | 96.6772 | 69.3631 | 5.7059 | 74.1498 | 5.9707 | 6.7112 | 46.3227 | 74.011 | 12.3331 | 151.0308 | 98.0252 | 238.3006 | 26.1936 | 55.8149 | 13.0653 | 107 | 18.4679 | 70.4957 | 328.6399 | 0
1709 | 784.8804 | 1.7516 | 39.7244 | 97.1247 | 68.631 | 6.4013 | 71.414 | 6.1027 | 6.5055 | 51.859 | 73.5009 | 12.3282 | 149.8406 | 92.166 | 235.1208 | 23.6666 | 57.3041 | 13.4804 | 105 | 18.2823 | 69.373 | 321.1217 | 0
1710 | 774.8395 | 3.4948 | 39.9671 | 98.7847 | 69.1029 | 5.953 | 66.8253 | 6.279 | 6.6945 | 56.6169 | 72.9907 | 12.6521 | 151.2266 | 89.4452 | 229.5432 | 21.5317 | 59.5951 | 14.3153 | 107 | 17.9907 | 72.0608 | 317.1382 | 0
1711 | 788.4615 | 3.7049 | 55.8813 | 96.0884 | 68.6359 | 6.3967 | 73.3172 | 6.1226 | 7.7173 | 58.1126 | 70.2198 | 11.1708 | 153.9936 | 87.4112 | 221.8507 | 17.4433 | 56.6626 | 14.1345 | 113 | 17.9553 | 74.6101 | 309.5556 | 0
1712 | 808.2509 | 2.6569 | 72.5951 | 95.3657 | 69.1725 | 5.8869 | 78.3288 | 5.742 | 11.8973 | 56.077 | 74.7891 | 14.1262 | 162.2887 | 103.6725 | 214.1096 | 16.2918 | 54.9322 | 13.1339 | 112 | 18.5957 | 76.2193 | 318.2922 | 0.015967
1713 | 815.4133 | 1.5415 | 77.5551 | 97.6729 | 69.3537 | 5.7148 | 72.7629 | 5.7184 | 13.1763 | 56.427 | 105.3895 | 20.5833 | 187.8248 | 123.7039 | 223.9237 | 18.5328 | 55.0449 | 13.2642 | 119 | 18.5333 | 87.6926 | 324.8377 | 0.034741
1714 | 838.8922 | 1.3468 | 79.0403 | 102.2802 | 69.3129 | 5.7535 | 75.442 | 5.571 | 13.2592 | 72.5197 | 130.9912 | 17.5587 | 216.7411 | 143.033 | 243.3217 | 20.9521 | 56.3179 | 14.5036 | 153 | 18.6816 | 117.0454 | 334.0038 | 0.056867
1715 | 867.6751 | 1.7879 | 77.3628 | 103.7483 | 66.3066 | 8.6095 | 95.7721 | 5.192 | 13.9948 | 79.854 | 143.5498 | 15.9145 | 236.236 | 167.8863 | 266.4699 | 23.3399 | 57.8226 | 15.6709 | 187 | 18.6149 | 130.9984 | 345.2466 | 0.070823
1716 | 887.277 | 1.7836 | 78.2026 | 102.9197 | 66.9158 | 8.0308 | 90.6288 | 5.7846 | 14.2594 | 80.0716 | 136.826 | 16.847 | 248.991 | 167.4942 | 281.9882 | 26.4656 | 58.1446 | 16.2045 | 178 | 18.3682 | 135.7139 | 383.7387 | 0.06205
1717 | 911.7067 | 1.6645 | 79.2758 | 101.8927 | 68.9479 | 6.1002 | 91.4532 | 7.5017 | 15.3797 | 83.7708 | 108.0095 | 14.9676 | 255.1752 | 165.4966 | 277.0012 | 25.1941 | 60.958 | 16.9691 | 196 | 18.336 | 137.8204 | 398.8099 | 0.083319
1718 | 886.7347 | 1.6697 | 79.268 | 102.8438 | 67.0576 | 7.8961 | 99.2366 | 7.5235 | 16.0319 | 78.0482 | 96.4427 | 15.4871 | 250.5061 | 174.2296 | 279.9625 | 25.6121 | 62.5509 | 17.4952 | 192 | 18.6591 | 130.3382 | 397.723 | 0.10934
1719 | 872.6508 | 2.3513 | 77.1492 | 102.1627 | 65.5462 | 9.3319 | 98.3518 | 6.0029 | 15.8877 | 74.0997 | 96.8207 | 19.4084 | 249.1728 | 170.2672 | 291.5015 | 25.4505 | 60.3144 | 18.5255 | 199 | 18.6552 | 126.7124 | 380.4608 | 0.084918
1720 | 870.5782 | 1.7709 | 75.3453 | 102.5696 | 65.3485 | 9.5197 | 93.9545 | 5.0964 | 15.8 | 67.7918 | 98.2356 | 25.8375 | 241.7594 | 158.7165 | 295.9339 | 25.4741 | 59.1009 | 18.8276 | 200 | 17.8219 | 113.7297 | 385.1668 | 0.040834
1721 | 865.0899 | 1.4217 | 57.4931 | 103.0197 | 66.9105 | 8.0358 | 93.7833 | 5.3186 | 16.7533 | 60.4571 | 94.6403 | 25.508 | 235.4065 | 153.7662 | 286.711 | 26.196 | 59.6905 | 18.5019 | 196 | 17.7433 | 86.9753 | 366.5538 | 0.017035
1722 | 854.2358 | 2.6283 | 46.5536 | 103.3686 | 68.9394 | 6.1084 | 86.2144 | 5.4318 | 16.462 | 57.608 | 90.145 | 22.6354 | 233.3635 | 156.1068 | 280.1801 | 26.4761 | 58.6214 | 18.2473 | 190 | 18.1274 | 79.5578 | 364.1802 | 0.002548
1723 | 840.6991 | 3.3467 | 45.2336 | 103.6903 | 68.6501 | 6.3832 | 73.8671 | 5.9142 | 14.145 | 65.4522 | 85.0768 | 20.0153 | 221.8226 | 153.5637 | 283.5388 | 25.5942 | 58.0757 | 17.9645 | 184 | 18.3868 | 81.2252 | 377.3715 | 0
1724 | 832.1512 | 3.5035 | 45.693 | 100.0462 | 68.3453 | 6.6727 | 76.765 | 6.2393 | 8.9816 | 68.3901 | 81.1889 | 15.7032 | 208.2906 | 142.3243 | 273.7912 | 23.1495 | 57.9008 | 17.4837 | 190 | 18.6868 | 80.388 | 377.538 | 0
1725 | 816.5359 | 3.7283 | 45.5499 | 98.2752 | 69.1403 | 5.9175 | 84.6314 | 6.3538 | 6.8243 | 56.184 | 80.1847 | 13.6783 | 189.8753 | 130.8758 | 262.497 | 22.0223 | 57.2737 | 16.7929 | 181 | 18.7897 | 76.0268 | 373.9979 | 0
1726 | 800.1217 | 3.8635 | 45.4274 | 100.2249 | 68.6393 | 6.3934 | 76.7377 | 6.7915 | 6.3877 | 46.3247 | 79.0485 | 13.7103 | 174.3249 | 122.4399 | 255.4179 | 23.347 | 56.6161 | 15.6033 | 167 | 18.6471 | 72.938 | 369.7788 | 0
1727 | 777.9055 | 3.4044 | 45.3505 | 100.4637 | 69.086 | 5.9691 | 70.7816 | 7.4045 | 6.3947 | 47.1237 | 75.7447 | 12.9467 | 163.8472 | 113.5826 | 249.0389 | 23.4201 | 56.2169 | 15.1161 | 139 | 18.4808 | 69.82 | 367.7769 | 0
1728 | 772.42 | 2.4896 | 45.7872 | 98.0983 | 69.338 | 5.7297 | 78.5266 | 7.8761 | 7.9686 | 47.6095 | 74.9881 | 12.832 | 158.308 | 107.7878 | 237.9017 | 15.8901 | 56.3815 | 14.1026 | 123 | 18.6488 | 68.7457 | 368.6909 | 0
1729 | 794.4066 | 1.8656 | 45.4023 | 99.2163 | 68.5705 | 6.4588 | 78.6145 | 8.089 | 11.4014 | 47.4448 | 74.7011 | 12.9202 | 156.2419 | 105.3169 | 229.6631 | 11.2931 | 56.2497 | 13.2616 | 116 | 18.9233 | 67.7425 | 369.6611 | 0
1730 | 785.8947 | 1.652 | 45.3459 | 99.8506 | 66.8792 | 8.0656 | 72.3628 | 7.6916 | 9.5468 | 47.5321 | 74.047 | 12.7852 | 153.4676 | 102.422 | 222.8447 | 10.8268 | 55.4045 | 12.4228 | 116 | 19.1722 | 67.4834 | 371.7635 | 0
1731 | 776.62 | 1.5486 | 45.3864 | 99.1446 | 63.3194 | 11.4474 | 68.9533 | 7.1607 | 9.9759 | 47.4115 | 74.244 | 12.9929 | 151.2255 | 97.8333 | 216.6964 | 10.653 | 55.0781 | 12.2199 | 131 | 24.7607 | 67.0373 | 373.7958 | 0
1732 | 769.8982 | 1.3621 | 45.3219 | 99.0864 | 63.9207 | 10.8761 | 77.7891 | 6.8569 | 8.6695 | 44.3072 | 75.136 | 12.7237 | 151.2371 | 94.7919 | 214.6666 | 10.732 | 55.3264 | 11.6564 | 111 | 25.5999 | 64.8704 | 370.2366 | 0
1733 | 755.6955 | 2.4207 | 45.1797 | 100.0977 | 65.891 | 9.0044 | 75.8878 | 7.2024 | 6.8083 | 40.7384 | 75.5518 | 12.5494 | 149.6492 | 94.844 | 213.9101 | 10.6692 | 56.9091 | 11.4591 | 107 | 24.3058 | 64.2339 | 368.4737 | 0
1734 | 752.1609 | 3.1938 | 45.359 | 99.1672 | 67.8711 | 7.1232 | 71.6201 | 7.0467 | 7.5046 | 40.5481 | 76.3318 | 12.6904 | 147.5878 | 94.0696 | 214.092 | 10.6716 | 59.7695 | 11.4493 | 108 | 20.1696 | 64.8885 | 367.5404 | 0
1735 | 770.0431 | 3.1403 | 45.4079 | 96.2788 | 69.1401 | 5.9177 | 71.0442 | 6.6671 | 10.1573 | 39.9932 | 74.3285 | 11.1821 | 153.1337 | 93.3372 | 208.2992 | 10.3268 | 56.9442 | 11.4239 | 113 | 18.8869 | 65.6053 | 360.9483 | 0
1736 | 783.4957 | 1.8283 | 48.7129 | 97.1998 | 67.8137 | 7.1778 | 80.9332 | 6.2522 | 12.549 | 36.6486 | 73.1632 | 10.0646 | 158.2269 | 98.4788 | 210.3665 | 10.0574 | 54.8088 | 11.7082 | 111 | 18.6979 | 65.4438 | 357.7658 | 0.040581
1737 | 798.1397 | 1.5375 | 64.6146 | 98.5935 | 68.163 | 6.846 | 83.2393 | 5.8772 | 12.748 | 46.3106 | 75.3241 | 11.1492 | 168.4226 | 110.0422 | 228.0703 | 10.0927 | 55.2032 | 13.225 | 120 | 18.4934 | 68.6831 | 361.6298 | 0.027635
1738 | 823.7388 | 1.587 | 71.687 | 101.9409 | 67.6768 | 7.3078 | 86.2067 | 5.7514 | 13.0814 | 69.5027 | 77.1924 | 15.1197 | 185.967 | 128.7394 | 239.9486 | 10.153 | 55.5982 | 15.6112 | 172 | 18.543 | 68.3985 | 360.5587 | 0.044336
1739 | 851.8545 | 1.4512 | 77.0015 | 102.4721 | 66.7168 | 8.2198 | 90.9736 | 6.0312 | 14.1726 | 81.6324 | 81.3247 | 16.0182 | 229.3793 | 146.3758 | 251.8193 | 10.0837 | 56.0988 | 16.8951 | 170 | 18.4256 | 71.7632 | 361.5073 | 0.052351
1740 | 875.3285 | 1.2949 | 76.496 | 102.1824 | 65.6566 | 9.227 | 97.1345 | 5.8333 | 13.9233 | 83.6309 | 91.9867 | 12.9667 | 247.9273 | 155.1248 | 277.1296 | 10.08 | 58.2612 | 17.258 | 174 | 18.3734 | 74.5458 | 364.1658 | 0.048323
1741 | 879.9109 | 1.4026 | 75.023 | 102.9901 | 66.899 | 8.0467 | 85.8699 | 5.6972 | 13.744 | 77.546 | 99.0538 | 14.9527 | 252.1013 | 167.2949 | 293.9373 | 10.2089 | 60.5661 | 18.0257 | 197 | 18.409 | 77.143 | 366.162 | 0.053523
1742 | 878.7609 | 2.5313 | 78.5408 | 102.1964 | 65.8409 | 9.0519 | 87.1588 | 5.5571 | 13.031 | 77.5789 | 99.7476 | 17.4018 | 253.2154 | 178.3569 | 290.2469 | 11.1421 | 59.1213 | 19.1916 | 186 | 18.2478 | 76.3845 | 373.7483 | 0.047581
1743 | 869.4545 | 2.4403 | 78.5751 | 103.4648 | 66.8234 | 8.1186 | 95.7382 | 5.5966 | 13.326 | 78.413 | 98.7847 | 16.8198 | 259.6354 | 175.7205 | 292.2563 | 12.2678 | 59.4258 | 19.576 | 194 | 18.2079 | 78.8008 | 377.9455 | 0.036507
1744 | 878.5121 | 1.5524 | 65.6785 | 103.7461 | 68.8801 | 6.1647 | 87.2053 | 5.6964 | 13.905 | 73.6899 | 97.7798 | 15.6742 | 248.7124 | 170.2858 | 280.6413 | 12.7499 | 61.7439 | 20.0284 | 180 | 18.1899 | 80.0936 | 369.5812 | 0.041962
1745 | 865.4543 | 1.9256 | 42.1189 | 101.9011 | 68.6375 | 6.3951 | 83.4257 | 5.7792 | 15.279 | 56.4169 | 96.8982 | 15.7929 | 242.6694 | 155.8537 | 281.2989 | 13.1828 | 58.529 | 19.6985 | 173 | 18.1197 | 81.6998 | 364.4035 | 0.013229
1746 | 857.4197 | 3.5258 | 34.1153 | 103.046 | 69.0767 | 5.9779 | 97.2237 | 5.7816 | 15.2145 | 48.0713 | 95.0994 | 16.7822 | 235.3936 | 150.199 | 295.6597 | 13.0073 | 57.0277 | 19.3542 | 162 | 18.2202 | 81.6247 | 364.0448 | 0.0010508
1747 | 855.8194 | 3.7082 | 34.2211 | 105.6314 | 69.3612 | 5.7077 | 96.55 | 5.9195 | 13.2614 | 44.9138 | 96.2991 | 16.3452 | 231.3325 | 154.6807 | 296.725 | 10.7887 | 57.3031 | 19.2031 | 141 | 18.5013 | 80.3996 | 380.0814 | 0
1748 | 845.6392 | 3.7807 | 33.7327 | 103.3688 | 68.6425 | 6.3904 | 79.8323 | 6.0746 | 9.083 | 40.1128 | 94.235 | 16.7121 | 226.8257 | 157.2788 | 299.3804 | 9.7675 | 57.465 | 18.7284 | 127 | 18.7409 | 76.1339 | 383.7421 | 0
1749 | 829.3301 | 3.7501 | 33.2229 | 100.6546 | 68.3544 | 6.6641 | 69.863 | 5.9985 | 7.556 | 38.2964 | 82.7031 | 17.569 | 212.8059 | 145.8222 | 298.808 | 9.7308 | 56.0815 | 16.9661 | 133 | 18.3014 | 68.2689 | 376.9456 | 0
1750 | 812.2147 | 3.6373 | 33.2858 | 98.5166 | 68.4123 | 6.6091 | 78.5372 | 6.335 | 8.3483 | 39.0398 | 77.2513 | 15.6973 | 189.5925 | 126.2555 | 268.1438 | 9.6049 | 55.9625 | 15.1997 | 117 | 18.1861 | 65.9254 | 369.8216 | 0
1751 | 792.7456 | 2.9536 | 33.4003 | 97.4373 | 68.3926 | 6.6278 | 83.0509 | 6.1297 | 7.3597 | 38.2843 | 75.3884 | 13.1616 | 175.4458 | 116.8212 | 248.5098 | 9.6591 | 55.8695 | 13.9743 | 117 | 18.2807 | 64.3064 | 367.307 | 0
1752 | 778.2274 | 1.7875 | 32.9856 | 97.2167 | 68.3583 | 6.6604 | 73.9639 | 6.0328 | 6.499 | 36.7371 | 73.093 | 12.6349 | 167.378 | 110.5241 | 255.3763 | 9.6785 | 56.7537 | 13.277 | 110 | 18.3964 | 63.2487 | 358.9882 | 0
1753 | 765.6035 | 1.3958 | 32.9286 | 97.0768 | 69.0962 | 5.9594 | 74.6171 | 6.0723 | 6.174 | 35.5347 | 71.2493 | 12.4686 | 159.7649 | 110.1375 | 253.8242 | 9.6788 | 56.5689 | 12.2684 | 112 | 18.6304 | 62.265 | 352.3341 | 0
1754 | 762.7185 | 1.3716 | 32.7831 | 96.6243 | 68.6327 | 6.3997 | 79.8052 | 6.0947 | 6.118 | 34.5084 | 70.3876 | 12.3318 | 153.7407 | 103.6561 | 235.4107 | 9.5974 | 55.1356 | 11.7267 | 112 | 18.5881 | 61.369 | 345.3451 | 0
1755 | 755.2066 | 1.4107 | 32.9395 | 96.6234 | 69.1251 | 5.932 | 71.7223 | 6.0848 | 6.109 | 34.1593 | 70.6375 | 12.671 | 150.6469 | 101.8724 | 220.6686 | 9.6429 | 54.5711 | 11.6463 | 135 | 18.4447 | 63.891 | 346.2447 | 0
1756 | 747.4763 | 1.3371 | 32.9637 | 99.4507 | 69.3276 | 5.7395 | 72.2094 | 5.9621 | 6.065 | 36.8239 | 71.6709 | 12.8377 | 150.0258 | 104.0662 | 211.919 | 9.6321 | 54.3944 | 11.6845 | 103 | 18.4433 | 66.2269 | 349.9613 | 0
1757 | 753.23 | 1.7523 | 33.872 | 99.903 | 68.6858 | 6.3493 | 82.0506 | 6.2947 | 6.077 | 47.769 | 73.2298 | 12.7738 | 149.3102 | 100.9231 | 205.8808 | 9.6409 | 56.1724 | 11.6731 | 97 | 18.2983 | 64.2092 | 374.9628 | 0
1758 | 779.4525 | 2.6717 | 42.5196 | 98.0983 | 68.3577 | 6.6609 | 76.3917 | 6.1629 | 6.5006 | 53.8435 | 75.0356 | 15.5778 | 161.547 | 110.1068 | 211.6781 | 9.5598 | 58.6898 | 11.7736 | 96 | 18.1736 | 75.541 | 396.8161 | 0
1759 | 826.7282 | 4.5705 | 56.581 | 102.154 | 66.1549 | 8.7537 | 78.5606 | 6.257 | 9.2735 | 72.7542 | 95.8762 | 20.5898 | 217.0764 | 174.4771 | 239.6356 | 12.537 | 56.3656 | 12.3993 | 161 | 18.0639 | 119.0336 | 459.6252 | 0
1760 | 885.165 | 4.7331 | 83.6894 | 107.1608 | 62.4268 | 12.2953 | 119.9124 | 6.6534 | 16.463 | 96.5208 | 132.2196 | 28.7996 | 292.956 | 231.2006 | 296.1084 | 24.7923 | 59.7036 | 14.4093 | 280 | 21.8686 | 159.3215 | 521.0196 | 0.050536
1761 | 975.7812 | 8.0812 | 96.963 | 120.2782 | 60.6195 | 14.0122 | 143.1938 | 7.3493 | 19.917 | 96.9219 | 160.284 | 30.4331 | 351.599 | 282.1044 | 400.8129 | 34.0348 | 70.7593 | 16.771 | 312 | 22.1 | 189.8393 | 571.8292 | 0.051449
1762 | 1041.1293 | 6.1564 | 104.1331 | 135.4631 | 58.8247 | 15.7173 | 145.9692 | 7.2948 | 20.385 | 97.243 | 170.3475 | 29.1284 | 429.1113 | 315.9304 | 525.5648 | 38.1115 | 80.6954 | 16.1971 | 337 | 25.3332 | 214.8597 | 608.2887 | 0.078889
1763 | 1094.7314 | 3.7948 | 107.4722 | 140.7923 | 55.3819 | 18.988 | 151.4149 | 7.0774 | 20.731 | 96.233 | 178.7014 | 28.7495 | 474.1326 | 349.1527 | 566.9958 | 39.2447 | 87.3488 | 16.2751 | 381 | 26.2347 | 220.1244 | 615.717 | 0.059234
1764 | 1140.73 | 4.3097 | 111.7685 | 140.0591 | 54.944 | 19.4039 | 152.0705 | 7.3447 | 20.7516 | 99.8916 | 178.6602 | 28.2787 | 465.9086 | 368.2826 | 574.2827 | 37.4679 | 90.9844 | 16.8207 | 349 | 23.8051 | 223.1671 | 614.3347 | 0.19747
1765 | 1144.3905 | 6.7793 | 106.4539 | 140.2812 | 56.7798 | 17.66 | 148.807 | 6.4203 | 20.1926 | 105.3783 | 175.7894 | 28.5862 | 448.2814 | 370.0204 | 569.6699 | 39.3746 | 90.4907 | 17.7082 | 374 | 23.5962 | 222.0661 | 603.5225 | 0.15397
1766 | 1150.5425 | 6.845 | 107.736 | 145.3131 | 57.4611 | 17.0128 | 141.1424 | 5.2044 | 20.6422 | 121.7012 | 182.6675 | 33.5594 | 441.143 | 371.1186 | 563.7022 | 41.6754 | 98.5856 | 18.2884 | 337 | 20.5774 | 220.6714 | 609.5844 | 0.20782
1767 | 1156.6356 | 6.9139 | 109.2711 | 144.6046 | 58.9663 | 15.5828 | 145.2402 | 6.0759 | 20.0341 | 114.8641 | 182.0292 | 36.9153 | 457.9558 | 371.0942 | 551.0883 | 41.4762 | 116.6023 | 18.7816 | 318 | 20.1655 | 218.716 | 600.844 | 0.098026
1768 | 1143.9632 | 5.9272 | 108.3008 | 140.2227 | 59.1477 | 15.4105 | 143.9823 | 6.1514 | 19.9051 | 107.8321 | 181.6903 | 34.8702 | 448.7334 | 350.8658 | 537.1322 | 40.5466 | 122.3245 | 19.1101 | 306 | 19.9282 | 218.8895 | 597.3834 | 0.08793
1769 | 1098.4666 | 4.5315 | 105.3632 | 134.9364 | 61.9137 | 12.7827 | 129.768 | 5.7402 | 19.8105 | 103.7505 | 174.9737 | 32.8273 | 420.8408 | 327.983 | 492.4297 | 32.3786 | 110.4061 | 18.7169 | 282 | 18.3204 | 196.945 | 535.9034 | 0.064723
1770 | 1056.7133 | 4.4097 | 101.0833 | 126.7442 | 63.1738 | 11.5857 | 115.1316 | 4.7604 | 20.1989 | 89.3618 | 158.3823 | 31.5815 | 370.6142 | 256.2515 | 433.752 | 17.9578 | 86.0431 | 17.8536 | 235 | 16.8761 | 173.4689 | 457.5394 | 0.0031146
1771 | 1006.9559 | 5.1574 | 99.1243 | 115.5701 | 67.7117 | 7.2747 | 103.1305 | 4.504 | 18.5131 | 62.3803 | 135.1009 | 28.5763 | 323.4551 | 188.1517 | 399.015 | 11.9958 | 72.6945 | 17.2496 | 206 | 16.3341 | 159.7681 | 396.3926 | 0
1772 | 955.0757 | 4.7611 | 85.8105 | 108.0765 | 68.6749 | 6.3596 | 89.0171 | 3.9512 | 18.015 | 46.234 | 111.3626 | 20.0634 | 291.4357 | 159.8574 | 362.3797 | 11.2424 | 67.4112 | 16.746 | 186 | 16.1711 | 146.3077 | 332.4443 | 0
1773 | 898.7027 | 3.8432 | 57.6054 | 101.3313 | 69.0817 | 5.9732 | 83.2938 | 3.9395 | 17.128 | 43.4397 | 101.0969 | 16.4221 | 261.5411 | 145.7424 | 317.1932 | 10.5323 | 61.0498 | 16.4743 | 174 | 16.2221 | 137.1053 | 308.0264 | 0
1774 | 872.387 | 8.0182 | 43.3301 | 97.319 | 68.6273 | 6.4049 | 82.5422 | 4.3729 | 14.842 | 39.9806 | 97.422 | 16.4906 | 224.3188 | 133.9761 | 290.7377 | 10.5769 | 58.4951 | 15.4306 | 150 | 16.3083 | 124.1046 | 303.2161 | 0
1775 | 834.587 | 9.913 | 40.997 | 94.7918 | 68.4053 | 6.6157 | 81.6599 | 4.7457 | 13.696 | 33.0143 | 85.0619 | 15.3303 | 201.2503 | 121.5463 | 266.3469 | 10.973 | 57.5296 | 14.3173 | 127 | 16.356 | 109.2313 | 293.9839 | 0
1776 | 809.6444 | 9.6661 | 40.8227 | 93.9312 | 69.1239 | 5.9331 | 81.1689 | 4.7729 | 10.3209 | 30.651 | 76.8455 | 12.5391 | 190.1661 | 115.9362 | 241.0928 | 11.1461 | 56.6675 | 13.8951 | 110 | 16.5541 | 81.5789 | 292.4219 | 0
1777 | 806.1179 | 8.8005 | 40.751 | 93.8265 | 68.6267 | 6.4054 | 81.8804 | 4.7878 | 7.3439 | 31.1011 | 74.9351 | 11.5228 | 190.5324 | 110.9329 | 227.8073 | 11.1312 | 56.3199 | 10.5825 | 105 | 16.6099 | 70.2967 | 289.1614 | 0
1778 | 797.7369 | 4.076 | 40.2529 | 94.4141 | 69.1134 | 5.9431 | 81.3605 | 5.0796 | 6.3131 | 31.1304 | 77.2553 | 11.5311 | 191.5005 | 103.2175 | 218.6541 | 11.1395 | 56.2469 | 5.0984 | 101 | 16.6265 | 70.0338 | 282.3144 | 0
1779 | 789.5267 | 1.6456 | 37.5941 | 94.1834 | 67.1198 | 7.837 | 71.5653 | 5.2875 | 6.2844 | 31.2622 | 80.9977 | 11.5445 | 184.0991 | 98.7461 | 217.0863 | 11.0813 | 56.0593 | 2.9692 | 123 | 16.607 | 70.9959 | 281.252 | 0
1780 | 796.7113 | 1.3037 | 34.4909 | 94.0791 | 67.8243 | 7.1677 | 71.4013 | 5.3434 | 6.451 | 34.5924 | 82.8679 | 11.5435 | 180.1073 | 96.2393 | 221.8531 | 11.2007 | 56.2078 | 2.8779 | 99 | 16.6179 | 70.4951 | 280.4102 | 0
1781 | 803.2791 | 1.6745 | 33.9092 | 94.2166 | 69.13 | 5.9273 | 78.166 | 5.2844 | 6.4893 | 46.1322 | 81.3909 | 11.527 | 188.2067 | 93.3148 | 224.4584 | 11.2541 | 58.5397 | 2.8741 | 99 | 16.6647 | 71.0374 | 307.8608 | 0
1782 | 817.0982 | 2.7977 | 42.7909 | 96.0369 | 67.9231 | 7.0739 | 73.8402 | 5.2333 | 6.7624 | 52.8686 | 77.7495 | 13.4846 | 207.1162 | 105.58 | 222.065 | 11.0919 | 60.2926 | 2.8699 | 120 | 16.5479 | 75.2646 | 341.3476 | 0
1783 | 851.6242 | 4.3807 | 58.2601 | 98.9438 | 66.621 | 8.3108 | 75.7282 | 5.0801 | 8.553 | 65.1821 | 85.5366 | 20.4085 | 240.798 | 156.4662 | 229.7052 | 13.9293 | 57.3342 | 2.6971 | 192 | 17.0553 | 114.3307 | 381.1504 | 0
1784 | 903.7978 | 8.0836 | 88.3534 | 102.3482 | 64.1368 | 10.6708 | 118.8797 | 5.2562 | 16.711 | 90.0133 | 124.9765 | 26.9126 | 308.4049 | 217.7522 | 302.074 | 27.0473 | 61.4552 | 4.9261 | 310 | 21.1826 | 159.2416 | 446.5188 | 0.15917
1785 | 992.3252 | 13.9743 | 106.1275 | 117.6579 | 61.1338 | 13.5237 | 148.4284 | 5.5951 | 20.88 | 91.6931 | 159.5223 | 28.5644 | 364.4002 | 280.8763 | 431.9013 | 36.4024 | 74.3332 | 12.8228 | 284 | 22.2201 | 184.6968 | 501.8447 | 0.11139
1786 | 1093.1209 | 12.7307 | 111.7567 | 129.6133 | 60.3731 | 14.2464 | 149.5887 | 6.5075 | 21.006 | 84.1581 | 163.8718 | 28.1476 | 391.32 | 310.4903 | 519.3051 | 39.577 | 94.1817 | 19.0008 | 334 | 22.9952 | 207.8406 | 553.0641 | 0.13494
1787 | 1157.7903 | 10.702 | 113.3087 | 131.0092 | 58.1302 | 16.3771 | 142.8543 | 7.1496 | 21.286 | 91.8093 | 161.4423 | 34.4232 | 429.6656 | 334.5463 | 559.3287 | 40.1234 | 113.6485 | 20.2549 | 335 | 25.8036 | 212.1825 | 552.3685 | 0.20779
1788 | 1157.7174 | 9.1165 | 115.2833 | 131.8721 | 57.4155 | 17.0561 | 138.9219 | 6.8604 | 21.495 | 89.2812 | 168.1536 | 40.6372 | 439.9096 | 349.2845 | 578.1053 | 39.9134 | 110.4514 | 19.7126 | 317 | 26.2392 | 210.6246 | 529.3926 | 0.16735
1789 | 1135.3895 | 5.617 | 116.9425 | 130.4125 | 59.6171 | 14.9646 | 149.7978 | 5.5249 | 21.468 | 89.8184 | 172.2895 | 41.4707 | 439.1378 | 345.1771 | 572.5718 | 41.0215 | 92.6553 | 19.8115 | 329 | 26.5232 | 206.7252 | 523.768 | 0.23745
1790 | 1154.0457 | 4.0229 | 115.5072 | 133.5513 | 59.5884 | 14.9918 | 150.0585 | 5.219 | 21.275 | 102.5666 | 175.6866 | 40.8224 | 446.807 | 349.3308 | 556.4746 | 42.6852 | 97.8522 | 19.7317 | 286 | 24.0968 | 203.7129 | 522.796 | 0.22733
1791 | 1178.6606 | 3.7277 | 112.3637 | 139.1576 | 60.9487 | 13.6995 | 146.6598 | 4.5157 | 20.941 | 111.0878 | 179.9727 | 40.2643 | 454.6309 | 350.6333 | 557.7507 | 42.8502 | 112.4426 | 19.7027 | 277 | 23.7495 | 205.9728 | 529.8713 | 0.17662
1792 | 1162.5339 | 4.2152 | 112.7539 | 135.6513 | 59.7938 | 14.7967 | 153.5217 | 4.637 | 20.62 | 111.0822 | 181.9363 | 40.2303 | 447.3358 | 330.9939 | 553.731 | 39.9823 | 107.8956 | 19.8638 | 351 | 24.5946 | 204.2351 | 514.5509 | 0.11019
1793 | 1134.7371 | 4.7243 | 108.9303 | 127.3285 | 63.7461 | 11.042 | 145.0938 | 4.973 | 21.111 | 102.3067 | 177.9117 | 38.9708 | 409.8879 | 309.1524 | 511.3919 | 32.4813 | 88.1277 | 19.7727 | 291 | 20.2032 | 189.5946 | 465.2188 | 0.039674
1794 | 1079.5485 | 4.4432 | 103.6775 | 113.3054 | 67.6208 | 7.3611 | 160.0721 | 4.1031 | 21.052 | 89.6716 | 163.1484 | 37.6062 | 362.425 | 253.2964 | 427.5554 | 18.5916 | 74.6975 | 19.3134 | 230 | 18.3351 | 173.3655 | 388.7311 | 0.0018772
1795 | 1013.7838 | 3.9871 | 99.9755 | 104.0441 | 66.8902 | 8.0551 | 150.2614 | 3.0797 | 17.406 | 70.9301 | 130.7991 | 35.8942 | 308.62 | 213.5569 | 390.6345 | 11.8708 | 69.4688 | 18.4565 | 208 | 18.3209 | 160.9698 | 345.8009 | 0
1796 | 962.8933 | 3.8133 | 87.045 | 102.0038 | 68.6081 | 6.4231 | 104.3268 | 3.3203 | 10.23 | 53.2682 | 104.6649 | 28.6147 | 265.3268 | 194.3661 | 338.0768 | 10.3115 | 64.7835 | 17.118 | 184 | 18.3214 | 146.4128 | 299.5238 | 0
1797 | 922.352 | 3.525 | 56.838 | 99.848 | 68.6031 | 6.4279 | 85.575 | 3.9739 | 7.8 | 50.4134 | 95.4535 | 17.2853 | 234.533 | 172.7893 | 274.4461 | 9.6721 | 58.0123 | 10.5004 | 176 | 18.647 | 137.1167 | 269.1765 | 0
1798 | 895.2303 | 3.7734 | 41.6591 | 96.7663 | 69.1033 | 5.9527 | 82.5991 | 4.5219 | 7.443 | 47.8315 | 91.7034 | 10.3865 | 210.2725 | 154.5605 | 248.2843 | 9.9159 | 55.1974 | 6.3196 | 163 | 18.8246 | 130.2098 | 255.7818 | 0
1799 | 862.6568 | 3.1599 | 39.6812 | 95.9016 | 68.6077 | 6.4235 | 80.9172 | 4.5934 | 6.8759 | 39.0407 | 79.7803 | 8.5238 | 198.8341 | 142.0211 | 245.2253 | 10.2521 | 54.0641 | 5.266 | 148 | 19.0052 | 118.9982 | 259.2721 | 0
1800 | 845.1369 | 2.005 | 39.8286 | 94.523 | 68.4347 | 6.5878 | 80.9221 | 4.6171 | 6.8813 | 35.4087 | 73.6324 | 8.1372 | 193.3603 | 130.5008 | 229.7855 | 10.4806 | 53.4882 | 4.5708 | 130 | 19.2712 | 92.8909 | 253.5198 | 0
1801 | 841.606 | 1.4388 | 39.5864 | 94.2651 | 69.1112 | 5.9452 | 80.9588 | 4.8613 | 6.6888 | 35.5443 | 73.2524 | 7.7295 | 176.6533 | 127.5233 | 226.6806 | 10.4428 | 53.3709 | 4.25 | 120 | 19.2232 | 77.952 | 250.7142 | 0
1802 | 832.8788 | 1.4084 | 39.2381 | 94.2112 | 68.6125 | 6.4189 | 77.7857 | 5.2542 | 6.598 | 35.7746 | 73.3862 | 7.5572 | 164.3743 | 126.6231 | 232.0445 | 10.4542 | 53.633 | 4.1868 | 105 | 19.0749 | 76.696 | 252.0383 | 0
1803 | 820.94 | 1.4252 | 38.9856 | 94.5958 | 68.3922 | 6.6282 | 69.2903 | 5.2602 | 6.561 | 34.6833 | 74.0615 | 7.551 | 161.3921 | 118.7063 | 233.0142 | 10.5914 | 53.4713 | 3.3782 | 123 | 19.1734 | 75.8701 | 256.8151 | 0
1804 | 813.3744 | 1.3734 | 38.9527 | 94.2912 | 69.0604 | 5.9934 | 75.2985 | 5.3249 | 6.463 | 35.5302 | 74.7638 | 7.5371 | 168.5518 | 113.4039 | 227.9575 | 10.4852 | 53.4895 | 2.9872 | 100 | 19.1194 | 72.571 | 257.4544 | 0
1805 | 816.2806 | 1.6643 | 39.0604 | 94.8853 | 68.6456 | 6.3875 | 75.8112 | 5.4259 | 6.472 | 46.028 | 74.7048 | 7.3905 | 168.6742 | 111.7933 | 216.7021 | 10.5005 | 55.2789 | 2.981 | 103 | 18.8602 | 71.2476 | 277.9574 | 0
1806 | 815.7714 | 2.7071 | 42.2889 | 96.3182 | 67.6297 | 7.3526 | 68.1987 | 5.3093 | 6.672 | 53.4889 | 75.3916 | 8.6846 | 173.3208 | 117.2354 | 218.8813 | 10.5131 | 57.6029 | 3.0201 | 115 | 18.8103 | 78.4874 | 314.3733 | 0
1807 | 854.8001 | 4.2809 | 56.369 | 100.1278 | 66.6015 | 8.3293 | 83.7009 | 5.2163 | 10.215 | 64.9957 | 86.5368 | 14.1813 | 234.2733 | 165.0079 | 237.0719 | 13.538 | 55.2685 | 3.0918 | 203 | 19.1696 | 118.5838 | 350.5332 | 0
1808 | 926.6634 | 4.5636 | 86.4027 | 103.2838 | 62.02 | 12.6818 | 117.5134 | 5.752 | 14.4575 | 91.8788 | 127.0586 | 22.7156 | 292.4479 | 226.3673 | 318.1602 | 26.3666 | 59.3955 | 6.0077 | 287 | 22.5992 | 161.285 | 419.0993 | 0.029084
1809 | 1016.0713 | 10.5733 | 103.1658 | 115.9134 | 59.682 | 14.9029 | 128.7446 | 6.2223 | 15.0043 | 94.0862 | 163.4345 | 28.2491 | 358.323 | 286.171 | 431.3842 | 36.1493 | 70.3413 | 12.946 | 287 | 24.522 | 196.4732 | 489.8229 | 0.030781
1810 | 1084.6577 | 11.6802 | 109.1067 | 129.7466 | 59.1786 | 15.3811 | 142.1755 | 7.1876 | 14.4565 | 88.2347 | 181.0358 | 32.8794 | 417.2707 | 314.2373 | 505.38 | 41.4494 | 99.9265 | 19.68 | 335 | 25.3913 | 227.4225 | 542.1438 | 0.052414
1811 | 1125.8931 | 8.5439 | 113.9044 | 136.0343 | 60.1992 | 14.4115 | 149.5238 | 7.3575 | 14.6967 | 85.9534 | 182.7763 | 35.289 | 445.6165 | 335.5576 | 539.3866 | 43.7284 | 116.8077 | 19.9617 | 363 | 25.7047 | 232.0872 | 545.6506 | 0.072095
1812 | 1156.5518 | 7.813 | 111.6988 | 136.1765 | 58.128 | 16.3792 | 148.2894 | 7.6058 | 16.243 | 90.7647 | 179.5305 | 34.8842 | 454.5672 | 351.3155 | 555.3659 | 43.3031 | 100.1545 | 19.5131 | 373 | 26.2713 | 224.0871 | 542.8909 | 0.19669
1813 | 1140.7729 | 7.066 | 112.3933 | 137.3712 | 58.8672 | 15.677 | 146.1944 | 7.0136 | 17.701 | 90.9675 | 179.7582 | 33.9682 | 442.2856 | 353.2976 | 542.9985 | 43.036 | 87.4094 | 19.8912 | 369 | 28.5667 | 211.351 | 542.9297 | 0.24345
1814 | 1148.2776 | 5.5937 | 113.2058 | 139.0553 | 58.7102 | 15.8261 | 143.0258 | 6.3007 | 18.966 | 106.7904 | 180.6229 | 36.4253 | 438.6506 | 353.2365 | 535.3164 | 43.0615 | 104.5179 | 19.984 | 310 | 26.1365 | 206.8939 | 534.8901 | 0.28214
1815 | 1148.2865 | 4.384 | 110.7714 | 140.3736 | 60.6747 | 13.9598 | 138.4865 | 5.3975 | 20.2571 | 108.8657 | 181.3786 | 39.0703 | 441.496 | 357.232 | 527.5327 | 41.4709 | 109.6748 | 19.8313 | 284 | 24.2392 | 207.1202 | 536.7635 | 0.27335
1816 | 1155.5498 | 4.2646 | 111.0188 | 139.8917 | 56.9127 | 17.5337 | 136.7646 | 5.0338 | 20.8462 | 103.7781 | 180.8873 | 39.7447 | 426.381 | 348.4926 | 505.7809 | 37.8935 | 113.1295 | 19.6592 | 279 | 12.9652 | 209.2183 | 536.9797 | 0.21436
1817 | 1127.2593 | 5.042 | 107.3876 | 128.1038 | 59.6526 | 14.9308 | 133.6373 | 4.0437 | 19.4487 | 99.4182 | 172.3043 | 36.0703 | 398.2282 | 329.2026 | 454.4387 | 31.1191 | 111.4953 | 19.2807 | 276 | 8.219 | 188.6337 | 492.5619 | 0.13792
1818 | 1080.6543 | 8.6782 | 100.8414 | 112.9968 | 61.456 | 13.2176 | 128.7154 | 4.9126 | 19.573 | 83.9249 | 158.2881 | 32.9529 | 350.1157 | 268.8007 | 376.3418 | 18.768 | 84.6466 | 18.9122 | 236 | 8.2589 | 162.8834 | 397.8394 | 0.03747
1819 | 1015.5231 | 6.7294 | 96.055 | 106.753 | 66.4676 | 8.4565 | 118.0519 | 5.2258 | 17.268 | 66.7312 | 129.6098 | 34.7036 | 288.5105 | 218.0799 | 332.7733 | 12.6027 | 69.6348 | 18.0824 | 205 | 8.1935 | 152.4273 | 342.7576 | 0
1820 | 963.4875 | 4.5146 | 82.4851 | 106.3709 | 67.5862 | 7.3939 | 106.6633 | 4.5713 | 12.493 | 49.811 | 105.0559 | 30.2047 | 253.5444 | 191.6848 | 310.3693 | 10.7149 | 63.0339 | 17.2004 | 178 | 8.3428 | 139.4811 | 301.5537 | 0
1821 | 916.3758 | 3.9468 | 52.0694 | 104.7987 | 68.8649 | 6.1791 | 93.7626 | 4.5875 | 10.118 | 45.1379 | 98.8267 | 21.6548 | 236.2158 | 164.4294 | 269.3005 | 10.0165 | 57.715 | 16.4378 | 161 | 8.405 | 136.4977 | 288.4479 | 0
1822 | 886.7179 | 3.5876 | 36.4545 | 102.0821 | 69.4465 | 5.6266 | 84.2495 | 4.566 | 8.6595 | 43.6946 | 95.8539 | 13.8625 | 204.5474 | 133.7462 | 248.1415 | 9.8694 | 55.3908 | 15.167 | 145 | 8.3884 | 135.2454 | 303.3921 | 0
1823 | 869.1584 | 2.9244 | 34.5153 | 99.3309 | 68.6235 | 6.4084 | 72.3998 | 4.5554 | 7.6644 | 40.6158 | 84.1057 | 10.1268 | 181.0806 | 116.2727 | 246.8096 | 9.8883 | 55.0421 | 14.5081 | 131 | 8.4711 | 120.6613 | 302.7486 | 0
1824 | 847.9104 | 1.6679 | 34.3456 | 97.3666 | 69.0654 | 5.9887 | 74.1304 | 4.6245 | 6.7351 | 37.9056 | 76.2236 | 9.0232 | 172.2318 | 109.6797 | 239.473 | 9.9772 | 55.243 | 14.3309 | 119 | 8.5754 | 90.7021 | 288.402 | 0
1825 | 835.6973 | 1.2804 | 33.8402 | 96.9478 | 69.3536 | 5.7149 | 80.4108 | 4.8879 | 6.461 | 35.8919 | 73.2511 | 8.3878 | 164.5258 | 111.2886 | 230.3847 | 9.9058 | 54.9327 | 14.0989 | 113 | 8.614 | 73.1596 | 281.802 | 0
1826 | 832.2499 | 1.5554 | 33.6788 | 95.671 | 69.3588 | 5.7099 | 76.2174 | 4.8406 | 6.533 | 35.6506 | 71.9278 | 7.5978 | 159.1903 | 103.7545 | 222.0896 | 10.0281 | 54.9791 | 13.9143 | 108 | 8.6469 | 67.6322 | 275.6843 | 0
1827 | 820.2916 | 1.8074 | 33.642 | 95.1344 | 69.3851 | 5.6849 | 69.1431 | 4.7155 | 6.826 | 35.4823 | 72.0707 | 7.3322 | 157.8847 | 96.9624 | 211.7822 | 9.9835 | 54.8425 | 13.6957 | 125 | 8.6718 | 66.5628 | 274.1365 | 0
1828 | 817.9124 | 1.4401 | 33.6042 | 94.5948 | 68.6225 | 6.4094 | 76.058 | 4.7471 | 6.506 | 38.2355 | 72.7616 | 7.305 | 157.2415 | 94.7516 | 209.3669 | 9.876 | 54.8025 | 13.4499 | 103 | 8.5758 | 65.7587 | 270.931 | 0
1829 | 824.873 | 1.5899 | 33.622 | 94.2977 | 69.153 | 5.9054 | 77.4131 | 4.9459 | 6.3094 | 48.8765 | 73.0287 | 7.2561 | 160.7614 | 94.7237 | 208.4202 | 9.8672 | 56.4879 | 12.5043 | 99 | 8.4631 | 64.9298 | 291.7839 | 0
1830 | 844.0492 | 3.2021 | 36.0641 | 95.3803 | 67.8595 | 7.1343 | 69.3034 | 4.862 | 6.6247 | 57.6783 | 74.2692 | 10.702 | 178.18 | 109.0175 | 214.5255 | 9.7932 | 58.7279 | 12.3766 | 109 | 8.4531 | 69.573 | 322.4287 | 0
1831 | 865.5489 | 4.4913 | 56.1359 | 98.4433 | 66.5796 | 8.3502 | 84.1866 | 4.6369 | 8.0659 | 69.2249 | 85.8504 | 17.0785 | 220.189 | 164.1067 | 227.8156 | 12.7114 | 56.2779 | 14.0572 | 181 | 9.2117 | 111.6073 | 365.6968 | 0
1832 | 933.9133 | 7.4462 | 87.97 | 102.5806 | 62.6924 | 12.043 | 126.1686 | 5.6795 | 14.458 | 84.9338 | 121.8891 | 23.9345 | 287.6634 | 233.1449 | 312.9966 | 26.1355 | 60.2235 | 15.877 | 275 | 15.3049 | 161.5922 | 425.7752 | 0.020132
1833 | 1032.0695 | 9.202 | 102.3351 | 115.4907 | 59.2155 | 15.346 | 146.5028 | 6.8217 | 16.127 | 78.7733 | 157.7837 | 26.5794 | 376.7432 | 282.4214 | 435.7915 | 35.1831 | 70.6827 | 16.6416 | 265 | 19.2025 | 194.1826 | 493.5845 | 0.026901
1834 | 1122.4899 | 5.7007 | 109.6643 | 131.0387 | 58.312 | 16.2044 | 158.3213 | 6.8277 | 15.077 | 76.4408 | 175.1566 | 36.5653 | 447.5356 | 306.14 | 523.81 | 40.1043 | 100.4394 | 19.3316 | 347 | 22.236 | 213.1207 | 518.4003 | 0.046979
1835 | 1154.7552 | 3.944 | 110.5419 | 136.5094 | 59.0949 | 15.4606 | 162.3457 | 6.6894 | 15.8497 | 76.0497 | 181.4662 | 42.8504 | 473.4801 | 337.7661 | 568.7418 | 41.2872 | 118.4154 | 20.1526 | 336 | 21.8136 | 221.0729 | 520.8599 | 0.075449
1836 | 1195.3447 | 4.0015 | 110.2968 | 136.3877 | 59.4804 | 15.0944 | 155.4374 | 6.9838 | 17.3739 | 76.6784 | 186.0889 | 43.1467 | 473.3519 | 343.2327 | 595.1682 | 41.2542 | 107.5223 | 19.6178 | 358 | 17.9426 | 219.8489 | 526.9576 | 0.058278
1837 | 1213.2697 | 3.8364 | 111.6439 | 135.192 | 56.5908 | 17.8395 | 150.7137 | 6.5122 | 19.7092 | 92.7121 | 183.6893 | 41.2015 | 464.2163 | 337.5121 | 590.4568 | 42.5085 | 91.4659 | 19.266 | 423 | 17.2021 | 217.0995 | 531.637 | 0.067563
1838 | 1185.862 | 3.7459 | 115.1579 | 140.7123 | 56.844 | 17.599 | 151.9878 | 6.316 | 21.3468 | 109.4753 | 188.9682 | 40.771 | 469.0532 | 336.5558 | 580.066 | 43.5178 | 88.7286 | 19.5018 | 328 | 16.9331 | 221.8142 | 533.5634 | 0.051064
1839 | 1169.2396 | 3.8649 | 116.4704 | 145.3614 | 58.0166 | 16.485 | 152.7184 | 6.2807 | 21.8972 | 106.0394 | 185.083 | 40.5356 | 474.4165 | 352.8512 | 558.2293 | 42.2279 | 89.1955 | 19.4615 | 334 | 18.4536 | 219.3085 | 527.8804 | 0.029265
1840 | 1137.5303 | 3.6203 | 113.4383 | 141.102 | 49.5994 | 24.4814 | 148.5864 | 6.3881 | 22.0452 | 103.9954 | 177.427 | 39.5632 | 452.2521 | 336.6909 | 536.1069 | 41.0419 | 87.9916 | 19.7716 | 313 | 15.7006 | 215.6872 | 520.6949 | 0.02071
1841 | 1102.3622 | 4.7542 | 107.7461 | 132.8312 | 48.3936 | 25.6269 | 148.1082 | 6.7676 | 21.834 | 104.4757 | 172.6401 | 39.0107 | 413.3278 | 313.2229 | 475.8211 | 32.6587 | 86.2621 | 19.6425 | 291 | 13.2108 | 204.2317 | 482.13 | 0.011413
1842 | 1064.4761 | 5.8909 | 102.1965 | 121.8155 | 54.5788 | 19.7509 | 138.5774 | 6.2089 | 21.0572 | 84.5591 | 161.1343 | 37.1725 | 378.7226 | 250.4311 | 401.3985 | 17.8486 | 78.4253 | 19.0659 | 245 | 12.7399 | 184.1437 | 398.9042 | 0.001988
1843 | 1014.5164 | 4.9849 | 99.633 | 112.0073 | 62.2653 | 12.4488 | 114.4758 | 5.446 | 16.1259 | 67.4223 | 133.2115 | 33.3597 | 346.1361 | 196.386 | 368.3173 | 11.6272 | 70.0651 | 18.4055 | 222 | 12.8016 | 168.9572 | 344.656 | 0
1844 | 971.6316 | 4.6463 | 86.812 | 107.3751 | 65.1986 | 9.6621 | 95.6008 | 4.9989 | 9.7444 | 59.4282 | 108.7078 | 23.0387 | 313.0509 | 178.1209 | 335.4134 | 10.7663 | 63.8168 | 17.6839 | 183 | 12.8983 | 153.384 | 312.8938 | 0
1845 | 928.9118 | 3.9814 | 57.3453 | 104.1607 | 67.4894 | 7.4859 | 83.4619 | 5.0142 | 8.9817 | 56.8972 | 101.463 | 19.7162 | 272.323 | 153.4801 | 304.457 | 10.3324 | 58.5985 | 17.4356 | 161 | 13.0765 | 145.8979 | 299.5781 | 0
1846 | 891.7912 | 3.5044 | 42.6758 | 100.8712 | 69.0523 | 6.0011 | 74.7972 | 4.9562 | 12.2443 | 51.1461 | 95.1791 | 16.9314 | 241.5026 | 127.1084 | 290.3844 | 10.358 | 55.9773 | 15.4274 | 174 | 13.1283 | 136.851 | 289.2552 | 0
1847 | 835.5257 | 3.4386 | 40.6553 | 100.3195 | 69.399 | 5.6717 | 79.8916 | 4.9109 | 11.4732 | 42.8206 | 82.8751 | 14.9138 | 230.1836 | 114.0561 | 277.8699 | 10.3641 | 55.3025 | 13.9908 | 136 | 13.1017 | 123.6378 | 297.1465 | 0
1848 | 813.4988 | 2.3002 | 40.0425 | 101.2414 | 69.3391 | 5.7286 | 92.9876 | 5.1093 | 7.744 | 39.9269 | 77.3762 | 14.2525 | 209.9623 | 110.1893 | 274.472 | 10.2561 | 55.2853 | 13.7093 | 121 | 13.2521 | 97.5008 | 307.2763 | 0
1849 | 807.9125 | 1.527 | 39.9022 | 100.3371 | 69.3802 | 5.6896 | 87.1952 | 5.1191 | 6.5091 | 38.5402 | 76.8812 | 14.2247 | 200.4466 | 109.2566 | 272.0457 | 10.28 | 56.1115 | 13.4737 | 109 | 13.2989 | 82.1407 | 292.2699 | 0
1850 | 808.9356 | 1.3253 | 39.926 | 100.2446 | 68.6363 | 6.3963 | 79.2426 | 5.1343 | 6.599 | 38.0484 | 75.024 | 13.1053 | 196.2457 | 102.7116 | 261.3585 | 10.265 | 55.8297 | 13.2629 | 107 | 13.2789 | 77.3732 | 280.9986 | 0
1851 | 798.3321 | 1.2847 | 39.8398 | 100.7525 | 69.1108 | 5.9455 | 79.2142 | 5.091 | 6.5128 | 38.1925 | 74.3422 | 12.2507 | 191.0126 | 101.6657 | 236.5749 | 10.2477 | 55.3214 | 13.5279 | 127 | 13.3068 | 76.48 | 276.0983 | 0
1852 | 791.1068 | 2.022 | 39.9057 | 100.7457 | 69.3992 | 5.6716 | 72.174 | 5.4653 | 6.4607 | 41.1593 | 75.0612 | 12.1711 | 188.4498 | 99.3587 | 221.7952 | 10.2905 | 55.2314 | 13.7571 | 102 | 13.246 | 75.7587 | 279.5709 | 0
1853 | 799.1574 | 2.4494 | 39.9494 | 99.8377 | 69.4183 | 5.6534 | 73.523 | 5.5095 | 6.4873 | 51.1639 | 75.4127 | 12.1918 | 188.3258 | 98.1409 | 218.0789 | 10.259 | 56.7396 | 13.7209 | 103 | 13.167 | 74.6854 | 304.5162 | 0
1854 | 816.1739 | 3.3411 | 46.2263 | 99.7171 | 68.574 | 6.4555 | 92.2904 | 5.348 | 6.8046 | 58.6498 | 75.6751 | 13.6558 | 205.5715 | 112.7614 | 225.1513 | 10.0849 | 58.8243 | 13.5999 | 111 | 13.1331 | 78.4601 | 338.446 | 0
1855 | 860.0038 | 4.9694 | 67.9245 | 102.7041 | 64.7662 | 10.0729 | 93.683 | 5.248 | 8.0188 | 72.7657 | 87.0486 | 19.4847 | 250.2458 | 171.7831 | 246.1827 | 13.2175 | 56.507 | 12.9325 | 178 | 13.0045 | 122.262 | 384.1647 | 0
1856 | 931.5553 | 6.5761 | 91.7755 | 99.2419 | 62.66 | 12.0738 | 114.2755 | 5.9526 | 15.7981 | 105.6733 | 122.5729 | 34.0696 | 327.8 | 228.1196 | 311.7686 | 26.2365 | 60.5479 | 13.2447 | 234 | 14.1163 | 166.3119 | 455.8454 | 0.037231
1857 | 991.4573 | 10.8681 | 104.6783 | 106.9171 | 60.8603 | 13.7835 | 143.3668 | 5.9547 | 20.7882 | 114.5754 | 157.1041 | 42.0958 | 387.2561 | 263.5501 | 417.1111 | 35.491 | 69.6226 | 14.6253 | 277 | 14.508 | 183.4993 | 514.1718 | 0.087284
1858 | 1055.6623 | 10.7729 | 108.6141 | 123.5808 | 61.0007 | 13.6501 | 149.2621 | 5.8361 | 21.4526 | 112.5538 | 171.6609 | 42.3802 | 426.2866 | 282.101 | 499.4148 | 38.647 | 79.5897 | 16.1451 | 367 | 15.7036 | 198.9505 | 561.0044 | 0.1197
1859 | 1115.8982 | 9.6908 | 109.7146 | 127.8667 | 57.898 | 16.5977 | 142.2225 | 6.1772 | 21.3808 | 113.3718 | 178.6918 | 44.0544 | 436.7469 | 310.2285 | 532.2319 | 38.7151 | 87.184 | 17.4341 | 356 | 16.599 | 204.5699 | 557.5665 | 0.20731
1860 | 1148.6777 | 6.6216 | 111.0699 | 124.6568 | 57.7953 | 16.6952 | 148.6771 | 5.4374 | 21.3134 | 112.2142 | 180.6727 | 44.6837 | 428.8323 | 322.7336 | 537.2846 | 37.5501 | 86.9042 | 17.8136 | 336 | 15.4804 | 203.8621 | 546.9145 | 0.21963
1861 | 1144.7726 | 8.0223 | 110.8882 | 127.6593 | 56.1524 | 18.256 | 150.2374 | 5.3538 | 20.1762 | 112.892 | 176.3937 | 42.9379 | 419.9515 | 308.9009 | 534.4829 | 39.5678 | 83.6469 | 17.2461 | 371 | 14.8562 | 204.4736 | 541.4563 | 0.30773
1862 | 1127.1204 | 10.5463 | 111.2437 | 135.1122 | 58.2246 | 16.2874 | 148.7404 | 5.598 | 21.382 | 112.3493 | 175.9116 | 41.7475 | 417.7425 | 311.8938 | 518.8792 | 41.6654 | 84.393 | 16.4391 | 331 | 11.4755 | 199.0709 | 550.0121 | 0.29304
1863 | 1122.7058 | 10.8857 | 110.4 | 135.1024 | 60.1683 | 14.4409 | 153.5429 | 5.5673 | 22.139 | 117.3472 | 179.6059 | 39.7744 | 420.1664 | 316.1419 | 506.7017 | 40.5859 | 81.5269 | 16.2184 | 343 | 10.4409 | 196.0647 | 533.2384 | 0.2543
1864 | 1105.2756 | 11.4762 | 111.492 | 131.0535 | 59.5143 | 15.0622 | 144.6654 | 4.9009 | 22.2372 | 112.9992 | 176.4856 | 38.5075 | 403.3412 | 297.7104 | 496.1858 | 37.0307 | 79.9198 | 15.9157 | 311 | 8.6485 | 187.1246 | 511.6491 | 0.12739
1865 | 1052.3448 | 7.9699 | 108.6697 | 126.1046 | 61.5605 | 13.1183 | 138.388 | 4.2042 | 21.7248 | 107.3725 | 168.3241 | 37.3096 | 371.1911 | 263.5082 | 443.7466 | 22.0285 | 77.5439 | 15.4053 | 318 | 7.6459 | 170.3589 | 448.3312 | 0.093371
1866 | 1000.1337 | 4.3564 | 92.0609 | 113.6012 | 67.5335 | 7.444 | 131.4257 | 4.3442 | 20.6606 | 86.3061 | 156.956 | 35.7628 | 342.8035 | 210.935 | 352.6599 | 11.5967 | 71.6049 | 15.1145 | 261 | 7.4931 | 154.6805 | 375.1859 | 0.020861
1867 | 952.073 | 3.9796 | 61.3457 | 102.319 | 70.1174 | 4.9893 | 114.953 | 4.4022 | 15.4488 | 63.6117 | 130.3001 | 27.8596 | 288.1324 | 163.5811 | 301.6785 | 9.9538 | 66.0852 | 14.7784 | 238 | 7.4996 | 144.5808 | 324.79 | 0
1868 | 907.811 | 3.7268 | 48.0828 | 96.2692 | 68.1415 | 6.8664 | 95.1106 | 4.4753 | 9.8606 | 56.2664 | 102.5532 | 14.6417 | 244.4381 | 154.6694 | 271.6979 | 9.8833 | 60.6666 | 14.6594 | 247 | 7.6336 | 128.954 | 299.7446 | 0
1869 | 859.322 | 4.1304 | 42.0045 | 95.0433 | 68.121 | 6.8858 | 90.3855 | 4.7935 | 8.0145 | 54.4575 | 87.7069 | 9.8192 | 207.3242 | 150.3448 | 244.4415 | 9.6445 | 56.214 | 8.9618 | 224 | 7.6981 | 121.8377 | 290.1836 | 0
1870 | 835.8088 | 3.9825 | 40.2105 | 95.1401 | 69.1834 | 5.8766 | 90.8694 | 4.8009 | 7.4522 | 52.9488 | 81.0278 | 9.2847 | 185.1264 | 121.5852 | 244.6887 | 9.4906 | 55.1338 | 4.972 | 208 | 7.7272 | 117.8781 | 275.8037 | 0
1871 | 831.1565 | 3.5502 | 40.69 | 93.1021 | 68.5835 | 6.4465 | 77.4766 | 4.7448 | 6.8336 | 48.838 | 77.4419 | 8.1246 | 174.9742 | 106.6848 | 242.493 | 9.5664 | 54.91 | 4.0342 | 186 | 7.7405 | 111.4802 | 275.5245 | 0
1872 | 814.1614 | 2.3277 | 40.469 | 90.7398 | 69.0689 | 5.9854 | 76.5041 | 4.6653 | 6.4745 | 44.934 | 76.0133 | 7.748 | 169.7535 | 104.3918 | 229.0984 | 9.4947 | 54.1716 | 3.745 | 160 | 7.8324 | 83.2302 | 271.8682 | 0
1873 | 799.5711 | 1.5316 | 40.2198 | 91.7407 | 69.3981 | 5.6726 | 80.4303 | 4.905 | 6.5377 | 43.4724 | 76.2947 | 7.7674 | 162.3587 | 101.7934 | 231.6792 | 9.5515 | 53.8148 | 3.6511 | 165 | 7.8666 | 72.5472 | 265.4599 | 0
1874 | 798.8636 | 1.4098 | 40.3712 | 91.0571 | 69.3893 | 5.6809 | 72.066 | 4.9162 | 6.3403 | 43.3802 | 75.5608 | 7.6855 | 157.9454 | 100.5392 | 235.0364 | 9.5352 | 53.7517 | 3.6799 | 153 | 7.8238 | 71.2616 | 275.1168 | 0
1875 | 795.9025 | 1.5105 | 40.1831 | 90.3272 | 69.3265 | 5.7406 | 72.3742 | 4.8357 | 6.5422 | 42.6871 | 75.4213 | 7.7604 | 155.7364 | 98.2675 | 233.4382 | 9.5175 | 53.7653 | 3.6001 | 172 | 7.9045 | 70.3934 | 278.167 | 0
1876 | 797.7182 | 1.5403 | 40.0547 | 90.4932 | 69.367 | 5.7022 | 79.8514 | 4.8216 | 6.5655 | 42.146 | 76.1469 | 7.5276 | 156.7965 | 98.4045 | 228.3936 | 9.5121 | 53.8901 | 3.2922 | 151 | 7.9058 | 69.3181 | 282.0219 | 0
1877 | 802.7968 | 2.0591 | 40.2493 | 91.621 | 69.3892 | 5.6811 | 72.7504 | 4.8937 | 6.426 | 46.7031 | 76.4975 | 7.4391 | 158.3706 | 101.6244 | 224.5441 | 9.489 | 55.6705 | 3.1594 | 144 | 7.8129 | 69.4792 | 279.4336 | 0
1878 | 804.4896 | 2.9406 | 40.3238 | 90.5967 | 68.6515 | 6.3819 | 69.4583 | 5.2232 | 6.2054 | 51.8373 | 76.0729 | 7.4154 | 159.3893 | 93.5647 | 218.8624 | 9.5117 | 57.754 | 3.1303 | 136 | 7.7859 | 70.5381 | 280.3631 | 0
1879 | 817.954 | 3.0313 | 53.8475 | 88.527 | 69.1112 | 5.9452 | 82.683 | 4.9604 | 7.4208 | 52.4621 | 73.5951 | 5.4679 | 165.6044 | 86.2943 | 205.4941 | 9.21 | 54.3548 | 2.9603 | 124 | 7.7783 | 66.6926 | 266.4046 | 0
1880 | 824.3918 | 1.9652 | 68.5299 | 88.4147 | 69.369 | 5.7003 | 96.8938 | 4.5151 | 14.9627 | 61.7304 | 79.1325 | 15.817 | 176.854 | 84.8882 | 206.2449 | 11.32 | 52.1148 | 3.0767 | 127 | 7.7572 | 66.7387 | 274.4662 | 0.05414
1881 | 830.0914 | 1.6691 | 76.1855 | 88.674 | 67.8451 | 7.1479 | 105.9591 | 4.2441 | 19.9055 | 68.6023 | 115.5748 | 25.7621 | 212.924 | 88.4405 | 211.2454 | 20.5569 | 53.4035 | 3.2856 | 127 | 7.8573 | 78.8413 | 277.7501 | 0.09354
1882 | 837.7359 | 2.0364 | 79.7588 | 88.8322 | 68.8637 | 6.1803 | 124.2732 | 4.0386 | 20.464 | 76.3186 | 147.9714 | 26.8821 | 231.444 | 96.6333 | 213.5666 | 21.4483 | 54.5419 | 5.2561 | 167 | 8.2578 | 114.2853 | 274.5573 | 0.18402
1883 | 868.4037 | 6.6983 | 84.1773 | 89.1349 | 69.3586 | 5.7102 | 136.2953 | 3.9522 | 19.7343 | 75.3807 | 156.3183 | 26.4486 | 240.4131 | 109.9913 | 215.6117 | 20.827 | 55.2982 | 10.4204 | 161 | 9.3576 | 120.1204 | 279.1265 | 0.19196
1884 | 885.2182 | 4.9969 | 84.5664 | 89.9188 | 69.4006 | 5.6702 | 134.5786 | 4.2186 | 18.9634 | 76.8417 | 144.5219 | 26.4276 | 254.9988 | 129.0831 | 231.8395 | 20.9917 | 58.0083 | 12.7517 | 171 | 9.4629 | 121.1928 | 281.5481 | 0.26874
1885 | 879.4222 | 3.6161 | 84.1722 | 90.5562 | 69.3396 | 5.7282 | 120.0771 | 4.8364 | 17.3037 | 76.7089 | 116.606 | 24.3172 | 259.5875 | 151.4014 | 241.5437 | 22.3865 | 59.879 | 13.1241 | 180 | 8.6378 | 123.1094 | 273.1733 | 0.32107
1886 | 856.0358 | 5.6573 | 80.377 | 91.0198 | 69.3649 | 5.7041 | 120.1587 | 6.1349 | 16.0423 | 80.5098 | 104.5352 | 13.2212 | 255.3721 | 148.452 | 234.8362 | 23.0631 | 58.3994 | 13.308 | 191 | 8.4922 | 120.8149 | 276.219 | 0.31919
1887 | 868.1555 | 3.7205 | 62.0986 | 91.1577 | 69.3895 | 5.6808 | 131.9147 | 5.0961 | 15.8383 | 77.5181 | 103.7196 | 7.2298 | 249.6101 | 144.2078 | 225.4399 | 17.7564 | 57.3264 | 13.1909 | 221 | 8.5155 | 111.1113 | 278.1314 | 0.30036
1888 | 885.2567 | 4.933 | 54.1131 | 90.9107 | 69.3556 | 5.713 | 128.6748 | 3.9859 | 15.6577 | 67.1698 | 99.2378 | 9.273 | 242.5112 | 148.071 | 235.6062 | 11.6461 | 59.1195 | 13.0424 | 202 | 7.9856 | 97.8453 | 286.7735 | 0.22312
1889 | 884.8216 | 5.1542 | 53.4218 | 91.2299 | 66.4767 | 8.4479 | 117.0936 | 2.7931 | 14.8855 | 56.777 | 95.3271 | 9.5921 | 235.3144 | 141.7892 | 245.5533 | 9.726 | 59.0756 | 13.2518 | 201 | 7.5253 | 76.1205 | 281.3875 | 0.13698
1890 | 880.1188 | 3.4469 | 53.2736 | 91.7182 | 68.3062 | 6.7099 | 111.0346 | 3.7811 | 14.8313 | 50.7076 | 92.9823 | 10.0974 | 229.3952 | 127.6734 | 241.6505 | 8.7975 | 58.7382 | 13.7311 | 208 | 7.3709 | 70.9309 | 281.7139 | 0.054403
1891 | 867.3801 | 3.4307 | 53.1451 | 92.5872 | 69.3719 | 5.6975 | 110.9232 | 5.0988 | 13.0403 | 37.3436 | 83.9167 | 12.2396 | 212.9423 | 116.5816 | 241.0115 | 8.7952 | 59.1047 | 14.356 | 212 | 7.2749 | 70.834 | 281.9306 | 0
1892 | 853.8929 | 3.6009 | 53.4113 | 93.5469 | 69.4208 | 5.651 | 99.4064 | 5.3378 | 8.5421 | 27.2773 | 80.6505 | 12.4928 | 196.1647 | 124.6374 | 247.5912 | 9.2951 | 57.7181 | 12.4527 | 201 | 7.3714 | 74.1955 | 280.6267 | 0
1893 | 845.0934 | 3.4734 | 53.5131 | 93.2958 | 69.2856 | 5.7795 | 76.808 | 5.4851 | 6.7368 | 24.7928 | 82.861 | 12.1087 | 176.6188 | 118.4979 | 255.2865 | 9.3423 | 55.4614 | 7.2014 | 199 | 7.4799 | 77.8058 | 277.853 | 0
1894 | 833.8565 | 3.3636 | 53.5025 | 92.599 | 68.6415 | 6.3914 | 73.432 | 5.7317 | 6.7687 | 25.6337 | 81.5547 | 10.0907 | 170.4552 | 104.8183 | 259.1809 | 9.3293 | 54.5551 | 4.4204 | 210 | 7.5832 | 77.0027 | 274.7533 | 0
1895 | 813.2246 | 3.0532 | 53.3586 | 91.2427 | 69.1313 | 5.926 | 76.1024 | 5.9962 | 6.8627 | 26.9663 | 78.0962 | 7.9604 | 176.4514 | 100.4401 | 253.9406 | 9.425 | 54.6597 | 3.7626 | 183 | 7.6332 | 76.6518 | 276.3928 | 0
1896 | 805.6845 | 7.0137 | 53.8106 | 90.1216 | 68.6481 | 6.3851 | 69.0466 | 5.9834 | 6.8338 | 25.7254 | 75.7822 | 7.4894 | 177.7547 | 96.8517 | 251.4752 | 9.4073 | 54.5432 | 3.5402 | 157 | 7.5893 | 73.3676 | 270.5284 | 0
1897 | 833.4223 | 8.5059 | 53.6964 | 91.4004 | 69.0554 | 5.9982 | 68.9063 | 6.0057 | 7.0082 | 26.0883 | 74.6479 | 7.5572 | 174.6697 | 96.1346 | 256.6787 | 9.4644 | 54.6558 | 3.1031 | 155 | 7.6129 | 69.2101 | 275.1244 | 0
1898 | 831.4413 | 3.9751 | 53.3922 | 90.1972 | 67.1023 | 7.8536 | 74.6566 | 6.0132 | 11.0946 | 26.8507 | 74.9825 | 10.0903 | 175.2984 | 93.9372 | 260.4534 | 9.3811 | 54.6491 | 2.9878 | 144 | 7.8838 | 67.2622 | 283.5987 | 0
1899 | 817.3672 | 1.6872 | 53.667 | 89.844 | 64.1954 | 10.6151 | 69.6048 | 6.0026 | 8.4897 | 26.9024 | 75.8651 | 14.5687 | 178.2352 | 94.192 | 252.2511 | 9.4289 | 54.7783 | 3.4431 | 159 | 13.2739 | 66.3896 | 287.6158 | 0
1900 | 806.2077 | 1.5483 | 53.8706 | 90.5012 | 64.1155 | 10.6911 | 65.8304 | 5.9083 | 6.671 | 27.2007 | 75.9161 | 10.2415 | 175.3785 | 94.7408 | 238.4622 | 9.5356 | 54.7052 | 3.7799 | 130 | 13.9622 | 66.3407 | 289.9417 | 0
1901 | 776.9192 | 1.9291 | 53.6706 | 89.553 | 65.8825 | 9.0124 | 75.6505 | 5.7742 | 9.0084 | 26.6436 | 79.1227 | 7.9559 | 162.9733 | 91.7982 | 222.3907 | 9.4357 | 56.2772 | 4.0078 | 126 | 12.5244 | 66.0727 | 291.1447 | 0
1902 | 768.6535 | 2.9469 | 53.6597 | 88.9266 | 67.798 | 7.1927 | 73.1968 | 5.7352 | 7.5773 | 26.5001 | 77.1877 | 7.6393 | 157.9413 | 89.7747 | 212.0131 | 9.379 | 58.4966 | 3.6108 | 120 | 8.8995 | 65.6391 | 283.3992 | 0
1903 | 782.7817 | 3.415 | 53.3316 | 87.5705 | 68.392 | 6.6284 | 65.6925 | 5.2809 | 8.9396 | 23.7735 | 71.4845 | 5.5435 | 152.6617 | 87.3945 | 203.7008 | 9.0998 | 55.1488 | 3.2 | 116 | 7.6704 | 65.3359 | 271.6486 | 0
1904 | 791.6587 | 2.0188 | 53.3041 | 87.366 | 69.1048 | 5.9512 | 72.0789 | 4.568 | 8.484 | 20.3248 | 72.9495 | 4.6022 | 160.989 | 86.7886 | 201.7645 | 8.9093 | 53.298 | 3.0183 | 111 | 7.6121 | 62.231 | 257.6181 | 0.048474
1905 | 800.8227 | 1.4448 | 53.3185 | 88.0993 | 68.6817 | 6.3531 | 81.83 | 4.3705 | 6.3108 | 31.0159 | 84.8288 | 4.5351 | 177.5588 | 89.8121 | 200.8688 | 9.4848 | 53.7602 | 3.2078 | 116 | 7.5743 | 62.1243 | 254.1152 | 0.083596
1906 | 807.2795 | 1.6145 | 53.1501 | 88.4574 | 66.128 | 8.7791 | 82.5053 | 3.8429 | 5.4659 | 52.7764 | 90.0306 | 4.5002 | 184.5312 | 96.4109 | 191.4554 | 9.8577 | 57.1132 | 3.298 | 151 | 7.4965 | 63.5659 | 262.3343 | 0.13487
1907 | 836.1918 | 1.6397 | 53.8983 | 89.2788 | 67.5763 | 7.4033 | 82.0505 | 3.3552 | 5.7206 | 60.5976 | 92.1842 | 4.4595 | 188.2682 | 103.0807 | 186.3217 | 10.1167 | 60.1246 | 5.1836 | 165 | 7.4244 | 64.333 | 266.594 | 0.24505
1908 | 856.2493 | 1.7901 | 54.215 | 89.3592 | 69.0921 | 5.9633 | 80.8324 | 3.1838 | 11.0814 | 58.9716 | 93.337 | 4.4626 | 205.9343 | 110.7037 | 196.4087 | 10.0839 | 58.3265 | 10.2941 | 163 | 7.4903 | 66.4356 | 262.4292 | 0.28367
1909 | 859.2098 | 1.9913 | 54.201 | 89.1701 | 67.9295 | 7.0677 | 80.7678 | 3.4328 | 13.3018 | 52.2614 | 94.3834 | 4.4393 | 214.4464 | 132.0118 | 204.2332 | 9.5704 | 56.6687 | 12.3361 | 180 | 7.549 | 68.3206 | 245.2187 | 0.30967
1910 | 849.5445 | 1.8391 | 54.3654 | 89.9061 | 68.0656 | 6.9385 | 81.6859 | 3.5912 | 13.9002 | 47.9816 | 95.8757 | 4.589 | 216.1064 | 138.0361 | 212.3493 | 9.6201 | 56.52 | 12.4517 | 195 | 7.5825 | 69.85 | 233.9799 | 0.30735
1911 | 849.2121 | 2.2169 | 54.3625 | 90.3581 | 67.655 | 7.3285 | 81.894 | 3.8323 | 14.4933 | 43.6685 | 96.3134 | 5.6278 | 215.5762 | 138.2219 | 224.1891 | 9.9393 | 58.2884 | 12.8087 | 198 | 7.5511 | 70.2769 | 231.9856 | 0.28394
1912 | 862.4166 | 2.0335 | 54.1667 | 90.4193 | 68.8351 | 6.2075 | 81.9165 | 3.6353 | 13.5198 | 39.4929 | 95.7633 | 7.4465 | 214.6735 | 126.6631 | 234.5772 | 10.0398 | 59.6296 | 12.9231 | 167 | 7.5884 | 67.1223 | 232.1953 | 0.20739
1913 | 870.0825 | 1.8751 | 53.7026 | 92.3138 | 68.5751 | 6.4545 | 90.5238 | 2.8548 | 13.1398 | 26.0909 | 95.8911 | 5.7431 | 211.8791 | 123.1435 | 246.982 | 9.9244 | 57.0862 | 12.7308 | 176 | 7.4616 | 64.4668 | 230.3098 | 0.085375
1914 | 851.7591 | 2.1585 | 53.8013 | 92.4061 | 69.1266 | 5.9305 | 96.7872 | 3.6446 | 12.4839 | 21.4015 | 94.3135 | 4.5112 | 207.0562 | 136.1097 | 262.2231 | 8.7711 | 54.8997 | 12.7723 | 167 | 7.4095 | 63.9444 | 232.4554 | 0.015218
1915 | 852.7289 | 3.1669 | 54.4793 | 92.2022 | 69.4456 | 5.6275 | 89.0236 | 4.3362 | 8.3729 | 21.5115 | 95.373 | 5.6793 | 210.3138 | 155.3197 | 271.2976 | 8.77 | 55.012 | 13.3387 | 145 | 7.4526 | 64.8934 | 239.1286 | 0
1916 | 847.3648 | 3.3821 | 54.848 | 91.6682 | 69.3654 | 5.7037 | 83.1861 | 4.573 | 6.5212 | 23.0233 | 94.8391 | 6.9766 | 197.5846 | 141.1055 | 274.7703 | 9.2105 | 55.2093 | 11.3769 | 138 | 7.5018 | 67.5967 | 255.3036 | 0
1917 | 823.9028 | 3.8005 | 55.0014 | 91.8873 | 69.3658 | 5.7033 | 81.4851 | 5.1584 | 6.3092 | 23.8148 | 85.6094 | 7.3608 | 182.3276 | 121.6906 | 271.4212 | 9.354 | 54.7299 | 5.9573 | 125 | 7.5015 | 68.3159 | 259.0323 | 0
1918 | 805.7188 | 3.5663 | 55.1088 | 91.1368 | 69.3332 | 5.7342 | 80.4144 | 5.2307 | 6.3325 | 23.2874 | 80.9849 | 7.3711 | 177.7801 | 107.9282 | 242.8605 | 9.4397 | 54.541 | 3.9979 | 121 | 7.5387 | 65.982 | 259.1237 | 0
1919 | 802.083 | 6.7848 | 55.3782 | 89.9182 | 68.602 | 6.4289 | 74.0097 | 5.1409 | 6.5512 | 22.7165 | 80.0882 | 7.3583 | 179.0341 | 104.1348 | 231.8258 | 9.3127 | 54.9158 | 3.7933 | 104 | 7.5401 | 64.6968 | 256.0354 | 0
1920 | 791.4424 | 8.2627 | 54.3925 | 89.1945 | 69.1112 | 5.9452 | 68.0763 | 5.2147 | 6.3475 | 23.0618 | 78.2908 | 7.3602 | 177.1135 | 97.3662 | 230.5831 | 9.4111 | 55.491 | 3.7339 | 102 | 7.6031 | 64.9478 | 246.6259 | 0
1921 | 784.2515 | 3.8028 | 53.6955 | 88.4807 | 69.3677 | 5.7014 | 75.1864 | 5.4036 | 6.3427 | 23.2575 | 77.4486 | 7.2743 | 166.6698 | 91.6972 | 233.3939 | 9.4084 | 55.5105 | 3.5526 | 103 | 7.5736 | 66.5619 | 251.0695 | 0
1922 | 781.3205 | 1.5132 | 53.6514 | 88.4695 | 69.3957 | 5.6749 | 73.7737 | 5.4807 | 6.42 | 23.4782 | 77.3931 | 7.2188 | 159.2949 | 91.0588 | 229.9204 | 9.3789 | 55.132 | 3.3491 | 99 | 7.5869 | 66.0371 | 256.765 | 0
1923 | 767.3918 | 1.3885 | 53.499 | 88.1843 | 69.3595 | 5.7093 | 67.2246 | 5.917 | 6.4457 | 24.0329 | 77.7913 | 7.5544 | 156.8045 | 95.6044 | 222.9408 | 9.4679 | 54.9791 | 2.9262 | 116 | 7.6339 | 66.7556 | 260.1725 | 0
1924 | 763.8169 | 1.3856 | 53.5194 | 88.4448 | 68.6928 | 6.3426 | 70.1849 | 6.1583 | 6.6148 | 28.3518 | 77.6751 | 7.7601 | 155.73 | 99.4848 | 219.8754 | 9.4104 | 55.1243 | 2.7339 | 98 | 7.6 | 69.2543 | 264.8566 | 0
1925 | 770.6273 | 1.8937 | 54.602 | 90.2885 | 69.1017 | 5.9542 | 71.8665 | 5.9756 | 6.5807 | 38.3683 | 76.7001 | 7.783 | 152.9138 | 95.5967 | 217.4656 | 9.3883 | 56.5216 | 2.748 | 98 | 7.522 | 66.8411 | 302.1268 | 0
1926 | 784.6281 | 3.2228 | 55.0167 | 88.901 | 68.6126 | 6.4188 | 67.2911 | 6.0012 | 6.3728 | 43.2824 | 75.2439 | 8.7229 | 165.5872 | 102.7604 | 213.0482 | 9.2594 | 58.7521 | 2.8777 | 99 | 7.5305 | 72.5887 | 318.9859 | 0
1927 | 825.9533 | 3.9859 | 65.8109 | 91.7177 | 65.465 | 9.409 | 73.1336 | 5.8247 | 9.3613 | 59.6858 | 99.4921 | 18.4884 | 214.7384 | 160.2043 | 248.5406 | 12.4067 | 56.5576 | 5.6069 | 165 | 8.4313 | 115.8571 | 378.1241 | 0.13257
1928 | 924.9493 | 4.6929 | 91.8619 | 99.1465 | 61.4024 | 13.2685 | 105.1742 | 6.2929 | 16.7769 | 90.2071 | 133.6902 | 32.7495 | 278.9213 | 218.404 | 346.2778 | 24.8233 | 60.8495 | 12.2915 | 280 | 11.9209 | 161.9016 | 448.2939 | 0.23042
1929 | 998.0856 | 9.3674 | 105.0923 | 111.0793 | 58.1108 | 16.3956 | 118.62 | 7.0976 | 21.7708 | 92.4881 | 156.7722 | 38.7872 | 339.8771 | 260.0294 | 446.3608 | 33.3261 | 70.4961 | 15.3364 | 317 | 13.7783 | 193.8457 | 514.6408 | 0.23502
1930 | 1072.1052 | 10.0407 | 112.2455 | 119.9317 | 58.9314 | 15.616 | 128.2202 | 7.2121 | 23.1547 | 92.3953 | 168.7253 | 38.715 | 378.874 | 289.1833 | 518.8959 | 37.4181 | 81.4268 | 16.4533 | 320 | 15.468 | 210.2102 | 557.9014 | 0.24732
1931 | 1110.6337 | 6.346 | 113.298 | 130.3439 | 60.0889 | 14.5164 | 137.7975 | 6.9831 | 24.3995 | 85.5921 | 174.0918 | 38.5409 | 407.7122 | 311.5262 | 549.8732 | 38.7045 | 88.8383 | 16.9983 | 369 | 16.3128 | 213.2947 | 575.6152 | 0.21254
1932 | 1145.5152 | 4.4821 | 114.3573 | 133.3908 | 58.2655 | 16.2486 | 140.3026 | 7.2864 | 23.0723 | 89.4138 | 175.5058 | 39.4718 | 435.3455 | 338.0736 | 539.8466 | 38.3894 | 90.5082 | 17.2849 | 341 | 15.3724 | 207.1908 | 571.2974 | 0.1913
1933 | 1133.2269 | 4.8369 | 112.5002 | 130.6451 | 58.0437 | 16.4592 | 138.4207 | 7.5278 | 20.5695 | 88.7497 | 173.7845 | 40.5059 | 444.1728 | 336.1966 | 535.1912 | 39.8692 | 87.511 | 16.7902 | 356 | 16.3764 | 202.4864 | 553.7465 | 0.2332
1934 | 1150.3118 | 6.3475 | 109.6887 | 131.4044 | 56.127 | 18.2801 | 138.3615 | 6.8891 | 24.2475 | 90.7677 | 175.0652 | 40.9556 | 437.7143 | 334.7774 | 540.423 | 42.8043 | 87.1352 | 16.1124 | 302 | 17.3041 | 208.9795 | 536.0537 | 0.18475
1935 | 1158.2053 | 6.7394 | 111.1187 | 128.7671 | 56.8643 | 17.5797 | 137.4448 | 5.3175 | 24.8234 | 88.3676 | 180.3566 | 41.9386 | 447.1717 | 337.4942 | 548.8163 | 41.9076 | 85.7822 | 16.1749 | 275 | 20.5526 | 214.3654 | 534.883 | 0.23679
1936 | 1143.8003 | 5.5541 | 108.3633 | 129.8107 | 57.283 | 17.1819 | 132.8 | 5.1577 | 21.9605 | 88.8875 | 178.8676 | 38.9819 | 432.0925 | 325.0778 | 532.5395 | 39.4865 | 84.1556 | 16.0085 | 272 | 13.9437 | 204.1716 | 526.577 | 0.21895
1937 | 1117.1836 | 4.5465 | 103.9706 | 128.3612 | 60.6556 | 13.978 | 121.3238 | 5.6714 | 21.0906 | 80.8659 | 171.4458 | 35.4455 | 412.7437 | 295.8814 | 477.7327 | 30.8197 | 80.5144 | 16.1428 | 241 | 7.4787 | 183.3235 | 479.2243 | 0.13252
1938 | 1057.3549 | 4.7806 | 100.0418 | 118.0015 | 61.8898 | 12.8054 | 107.1516 | 5.4947 | 21.165 | 61.5998 | 159.7074 | 32.4029 | 335.0567 | 232.185 | 388.695 | 15.9055 | 73.5892 | 16.0476 | 212 | 5.9443 | 155.8264 | 392.7538 | 0.053166
1939 | 991.1741 | 4.961 | 98.0267 | 105.9532 | 65.9224 | 8.9745 | 98.8479 | 5.1054 | 17.2195 | 43.4522 | 139.0728 | 27.4136 | 283.3414 | 181.5766 | 343.1765 | 10.1612 | 68.7718 | 14.9013 | 208 | 5.9042 | 137.8752 | 348.2189 | 0
1940 | 945.4989 | 4.079 | 86.0001 | 101.1097 | 68.1322 | 6.8752 | 89.8277 | 4.8555 | 10.3402 | 36.6795 | 113.0219 | 15.8437 | 254.5088 | 165.4806 | 303.065 | 9.7143 | 62.7421 | 14.0641 | 191 | 6.029 | 120.6119 | 322.1115 | 0
1941 | 913.3506 | 4.561 | 59.9301 | 98.261 | 67.6389 | 7.3439 | 85.7579 | 4.811 | 7.836 | 35.0271 | 101.7788 | 10.7426 | 229.6813 | 143.9494 | 263.5849 | 9.4963 | 57.1148 | 9.1301 | 173 | 6.0726 | 118.9531 | 304.134 | 0
1942 | 886.1717 | 4.0468 | 48.7956 | 96.5903 | 67.3779 | 7.5917 | 75.8632 | 4.6871 | 7.514 | 31.8637 | 95.8496 | 9.895 | 212.2413 | 122.5531 | 257.3441 | 9.5404 | 55.3521 | 5.2349 | 151 | 6.1209 | 115.8581 | 290.4442 | 0
1943 | 859.4683 | 2.8697 | 46.643 | 94.0173 | 68.0917 | 6.9137 | 78.3779 | 4.6093 | 6.7918 | 27.1415 | 83.9374 | 9.3633 | 201.3894 | 109.2114 | 247.56 | 9.4382 | 54.6448 | 4.6482 | 126 | 6.1462 | 104.6545 | 280.644 | 0
1944 | 836.3031 | 1.8599 | 42.684 | 92.2964 | 68.3402 | 6.6776 | 84.5549 | 4.7476 | 6.5578 | 23.0468 | 78.0544 | 9.2576 | 197.6395 | 100.5839 | 230.373 | 9.4794 | 54.0873 | 4.3347 | 123 | 6.221 | 81.2022 | 278.8403 | 0
1945 | 827.7039 | 1.3307 | 40.8129 | 92.6602 | 68.3592 | 6.6596 | 80.5763 | 4.8181 | 6.4365 | 22.1914 | 75.4001 | 9.2438 | 194.6542 | 99.457 | 227.3777 | 9.3764 | 53.8706 | 3.2566 | 112 | 6.1801 | 66.2183 | 268.0659 | 0
1946 | 820.0567 | 1.3575 | 40.4763 | 95.2274 | 67.6636 | 7.3204 | 73.62 | 4.6931 | 6.575 | 22.4619 | 76.535 | 9.239 | 188.3382 | 98.0889 | 231.9643 | 9.4264 | 53.5471 | 2.6733 | 106 | 6.1687 | 63.2017 | 272.6689 | 0
1947 | 812.3742 | 1.5959 | 40.4446 | 111.9941 | 68.0365 | 6.9661 | 80.7957 | 4.9385 | 6.6708 | 22.5764 | 80.1574 | 9.3846 | 172.9494 | 95.8444 | 248.2186 | 9.5117 | 53.5207 | 2.6236 | 119 | 6.2965 | 64.9821 | 273.4098 | 0
1948 | 807.6287 | 1.3353 | 40.3576 | 97.6037 | 68.3512 | 6.6672 | 79.0003 | 5.1156 | 6.5732 | 25.714 | 81.9185 | 9.3261 | 160.1686 | 95.3715 | 249.1297 | 9.4432 | 53.257 | 2.6093 | 99 | 6.2752 | 67.4084 | 275.679 | 0
1949 | 811.4281 | 1.7 | 40.2978 | 88.6182 | 68.4111 | 6.6103 | 71.1375 | 5.3238 | 6.462 | 36.3148 | 80.1838 | 9.2031 | 156.3878 | 94.6584 | 238.7113 | 9.4492 | 55.6851 | 2.6093 | 99 | 6.1847 | 67.8153 | 299.6553 | 0
1950 | 829.2706 | 3.0214 | 40.7731 | 88.3837 | 67.6847 | 7.3004 | 76.0485 | 5.2353 | 6.348 | 41.4386 | 75.6013 | 11.4419 | 169.7426 | 109.013 | 233.1486 | 9.3912 | 57.4913 | 2.9929 | 123 | 6.1411 | 73.1973 | 332.7662 | 0
1951 | 875.6705 | 3.8694 | 70.1712 | 93.1959 | 65.8422 | 9.0507 | 83.9811 | 5.4417 | 7.6131 | 57.8505 | 88.9526 | 20.0062 | 211.1163 | 162.5323 | 252.3048 | 12.2553 | 55.4579 | 3.0964 | 238 | 7.1914 | 114.7975 | 374.8301 | 0.11613
1952 | 943.9732 | 4.2025 | 83.09 | 99.7133 | 61.6386 | 13.0441 | 102.0413 | 5.9737 | 16.3461 | 85.889 | 127.7507 | 31.1746 | 285.7794 | 219.8236 | 332.9627 | 26.6119 | 59.9615 | 6.2588 | 246 | 13.7384 | 159.934 | 450.0045 | 0.04244
1953 | 1030.8809 | 8.4576 | 100.736 | 127.89 | 60.612 | 14.0194 | 125.118 | 6.8647 | 23.1961 | 93.8183 | 160.6813 | 39.1216 | 354.4594 | 266.2042 | 454.8511 | 36.1396 | 71.4335 | 13.4752 | 265 | 14.8647 | 187.5569 | 523.0147 | 0.050069
1954 | 1105.9529 | 10.0756 | 108.413 | 131.8971 | 59.5872 | 14.993 | 140.3969 | 7.552 | 24.6265 | 92.4011 | 179.4431 | 41.3971 | 395.4851 | 302.6527 | 546.3022 | 37.4854 | 86.143 | 15.9457 | 332 | 15.0405 | 204.7165 | 574.9195 | 0.15871
1955 | 1153.4833 | 7.0492 | 111.8604 | 136.1765 | 57.7802 | 16.7096 | 144.679 | 7.5377 | 21.9141 | 89.68 | 182.6483 | 40.5281 | 411.0981 | 330.9046 | 566.0132 | 38.8262 | 102.6804 | 16.7431 | 352 | 15.3743 | 218.9636 | 579.468 | 0.16084
1956 | 1163.0326 | 4.8045 | 87.0411 | 134.0626 | 55.236 | 19.1266 | 144.7309 | 7.1943 | 20.0655 | 94.6688 | 179.469 | 37.1712 | 416.53 | 334.2275 | 561.1216 | 39.7644 | 106.834 | 16.7726 | 336 | 14.2088 | 228.7026 | 565.7379 | 0.22002
1957 | 1158.2597 | 4.1652 | 75.3727 | 132.3794 | 56.5176 | 17.9091 | 143.5655 | 6.8827 | 21.1474 | 88.8827 | 181.8234 | 38.5805 | 422.4951 | 336.85 | 568.5695 | 41.9372 | 111.7401 | 16.7495 | 326 | 13.685 | 213.7697 | 559.07 | 0.21467
1958 | 1156.9124 | 4.0409 | 75.3727 | 132.711 | 57.2687 | 17.1955 | 142.9606 | 6.7765 | 21.7765 | 84.5763 | 183.8239 | 39.8751 | 424.8766 | 338.7104 | 573.2904 | 43.0015 | 115.1534 | 16.8351 | 294 | 13.6651 | 206.9595 | 558.1526 | 0.24024
1959 | 1163.3506 | 4.0338 | 75.3727 | 133.2076 | 58.1519 | 16.3565 | 143.3504 | 5.9744 | 22.4172 | 86.3756 | 181.1333 | 39.7932 | 426.8377 | 337.7946 | 574.3716 | 42.2414 | 114.6849 | 16.7589 | 299 | 13.4053 | 214.0909 | 559.3639 | 0.18667
1960 | 1159.0223 | 4.0137 | 75.3727 | 133.3373 | 57.5097 | 16.9666 | 136.0367 | 5.5535 | 18.7213 | 86.2728 | 181.3771 | 38.8985 | 425.0896 | 320.7764 | 563.1473 | 41.0001 | 114.1062 | 16.8179 | 293 | 11.3251 | 211.2157 | 542.2676 | 0.13119
1961 | 1126.1708 | 3.8915 | 75.3727 | 123.7465 | 60.2897 | 14.3256 | 123.716 | 6.3123 | 16.9294 | 76.9946 | 179.0042 | 37.5271 | 399.3494 | 300.3476 | 522.4363 | 33.8349 | 111.8259 | 17.3652 | 256 | 9.6046 | 193.3977 | 483.8 | 0.041688
1962 | 1063.6022 | 3.5111 | 75.3727 | 110.8747 | 65.1105 | 9.7458 | 110.1216 | 6.5349 | 18.371 | 65.801 | 166.5254 | 31.7598 | 352.3429 | 239.3612 | 430.8454 | 18.9375 | 104.084 | 17.3397 | 217 | 9.315 | 167.0854 | 387.8816 | 0.00891
1963 | 997.7255 | 4.1039 | 75.3727 | 102.2731 | 67.8256 | 7.1665 | 104.4409 | 6.8532 | 16.628 | 42.6059 | 135.2919 | 25.9519 | 314.3002 | 210.9961 | 386.1001 | 12.1167 | 98.7748 | 16.8689 | 218 | 9.2949 | 157.3345 | 330.3373 | 0
1964 | 953.0836 | 5.0362 | 75.3727 | 97.0257 | 69.1876 | 5.8726 | 87.8197 | 6.8423 | 10.566 | 31.696 | 112.35 | 16.7164 | 278.3719 | 201.9909 | 348.2673 | 10.7835 | 95.9308 | 16.402 | 187 | 9.3383 | 143.7417 | 290.8196 | 0
1965 | 927.8018 | 4.5502 | 75.3727 | 94.1212 | 69.3461 | 5.722 | 77.8162 | 6.0107 | 7.6495 | 30.5473 | 104.5199 | 13.3823 | 239.553 | 178.4887 | 298.0378 | 10.3799 | 90.2436 | 10.2318 | 175 | 9.4653 | 133.211 | 279.5872 | 0
1966 | 897.7268 | 3.9938 | 75.3727 | 94.2062 | 68.5935 | 6.4369 | 82.7835 | 5.7697 | 7.1605 | 28.5092 | 94.5466 | 13.2537 | 200.3323 | 148.5008 | 249.1785 | 10.3607 | 86.7404 | 5.4442 | 167 | 9.6743 | 126.063 | 275.3339 | 0
1967 | 868.1027 | 3.3071 | 75.3727 | 91.3576 | 69.0867 | 5.9684 | 81.6162 | 5.585 | 6.75 | 23.5422 | 77.817 | 13.242 | 182.1994 | 131.4516 | 237.947 | 10.1856 | 81.8411 | 4.3219 | 144 | 9.6345 | 108.5282 | 274.8824 | 0
1968 | 840.0186 | 1.8469 | 75.3727 | 89.0345 | 69.4041 | 5.6669 | 73.8355 | 5.4322 | 6.5518 | 21.9061 | 68.9689 | 12.8865 | 173.0473 | 121.4932 | 232.283 | 10.2825 | 77.6913 | 3.9594 | 118 | 9.5906 | 81.2414 | 269.2357 | 0
1969 | 834.6975 | 1.611 | 75.3727 | 89.2402 | 69.3728 | 5.6967 | 80.0278 | 5.6494 | 6.6407 | 22.0137 | 67.6994 | 12.5972 | 165.8638 | 120.9169 | 229.1298 | 10.3411 | 64.5012 | 3.4707 | 108 | 9.5697 | 67.4752 | 266.5358 | 0
1970 | 816.9902 | 1.4512 | 75.3727 | 88.7842 | 69.3342 | 5.7333 | 82.1322 | 5.7641 | 6.6135 | 22.4263 | 67.8712 | 12.5399 | 163.7488 | 115.1451 | 226.3173 | 10.3099 | 57.6497 | 3.3923 | 103 | 9.5813 | 63.8215 | 267.3316 | 0
1971 | 801.7095 | 1.2311 | 75.3727 | 88.4668 | 68.6143 | 6.4172 | 73.2985 | 5.6251 | 6.559 | 22.8403 | 68.5759 | 12.5516 | 163.2089 | 112.1212 | 225.7871 | 10.4064 | 57.6942 | 3.2817 | 122 | 9.6147 | 62.3345 | 270.3391 | 0
1972 | 799.935 | 1.3091 | 75.3727 | 88.3246 | 69.11 | 5.9463 | 78.4548 | 5.5134 | 6.578 | 25.3352 | 69.2113 | 12.5074 | 161.6138 | 111.1778 | 223.3773 | 10.327 | 57.4246 | 3.0984 | 101 | 9.6002 | 61.3608 | 269.8889 | 0
1973 | 806.306 | 1.6961 | 75.3727 | 89.3163 | 69.3763 | 5.6933 | 82.4731 | 5.5198 | 6.786 | 35.6001 | 69.3857 | 12.5219 | 160.7314 | 110.5904 | 219.5154 | 10.3536 | 59.0388 | 3.023 | 101 | 9.6027 | 62.403 | 283.8471 | 0
1974 | 825.6188 | 2.9352 | 75.3727 | 89.5422 | 67.8672 | 7.1269 | 73.656 | 5.7858 | 6.59 | 40.6529 | 67.8567 | 13.8403 | 171.4417 | 114.3899 | 218.7347 | 10.2418 | 61.0676 | 3.0261 | 119 | 9.6576 | 71.1664 | 325.5268 | 0
1975 | 864.2685 | 4.0166 | 75.3727 | 93.6464 | 66.6445 | 8.2885 | 86.276 | 5.5075 | 9.438 | 55.8668 | 77.6589 | 17.576 | 210.1533 | 157.8365 | 260.4034 | 13.1826 | 58.8893 | 3.2887 | 184 | 9.8631 | 112.7546 | 374.3683 | 0.019348
1976 | 964.2185 | 5.2696 | 75.3727 | 101.7491 | 63.0183 | 11.7334 | 110.7725 | 6.3576 | 18.4415 | 78.8162 | 126.5785 | 32.5722 | 297.812 | 233.1635 | 367.7661 | 28.0131 | 70.6631 | 9.6897 | 278 | 12.081 | 172.6372 | 456.1084 | 0.1185
1977 | 1009.8083 | 5.7531 | 75.3727 | 104.3956 | 61.8561 | 12.8375 | 118.6543 | 6.9582 | 21.755 | 86.22 | 150.8127 | 38.4297 | 331.2291 | 255.8125 | 408.8977 | 35.2627 | 77.7253 | 12.5 | 296 | 12.8543 | 189.4556 | 481.923 | 0.17509
1978 | 1075.7574 | 6.6869 | 96.9174 | 116.3958 | 60.87 | 13.7742 | 133.8982 | 8.379 | 23.2775 | 97.0971 | 165.8008 | 40.5239 | 377.9812 | 288.6409 | 502.2337 | 38.5759 | 101.8113 | 14.557 | 314 | 13.5552 | 213.968 | 500.4415 | 0.21683
1979 | 1147.5943 | 5.198 | 109.7759 | 124.9736 | 58.9454 | 15.6027 | 139.8924 | 8.4552 | 23.006 | 103.846 | 177.8315 | 42.0842 | 404.9554 | 310.8585 | 554.5245 | 41.6366 | 116.1386 | 16.2777 | 327 | 12.7033 | 233.683 | 526.3602 | 0.21913
1980 | 1167.8996 | 4.1563 | 111.3332 | 128.8198 | 59.7295 | 14.8577 | 137.5496 | 6.9478 | 21.616 | 102.8267 | 177.0882 | 39.1712 | 410.7683 | 330.4318 | 547.9787 | 41.4939 | 120.1602 | 17.0888 | 322 | 12.9241 | 239.0832 | 528.3928 | 0.28044
1981 | 1159.04 | 4.0768 | 110.1806 | 129.9066 | 60.3461 | 14.2719 | 136.8909 | 6.0936 | 20.735 | 95.0495 | 176.2071 | 38.2829 | 414.2039 | 323.7455 | 539.0761 | 40.9941 | 117.3619 | 17.7722 | 353 | 14.0738 | 224.5447 | 544.2445 | 0.29048
1982 | 1169.8825 | 4.221 | 110.4825 | 130.5624 | 59.6637 | 14.9202 | 134.6814 | 5.7807 | 20.673 | 95.981 | 177.2675 | 39.3149 | 418.8676 | 324.2701 | 550.2858 | 39.6767 | 118.2587 | 17.7304 | 300 | 13.3898 | 224.4012 | 546.7668 | 0.29476
1983 | 1179.275 | 4.0825 | 108.5138 | 132.9544 | 59.384 | 15.186 | 132.9348 | 5.3665 | 19.365 | 103.6617 | 178.1235 | 38.9452 | 420.199 | 329.6837 | 556.3196 | 37.8472 | 119.6955 | 18.2172 | 271 | 12.9524 | 221.9637 | 546.239 | 0.25771
1984 | 1132.195 | 3.9952 | 109.0564 | 133.2884 | 59.4359 | 15.1367 | 129.7268 | 5.7316 | 18.633 | 100.5948 | 172.7492 | 38.1745 | 407.3183 | 311.9341 | 558.1119 | 36.616 | 118.8994 | 18.5561 | 276 | 11.644 | 211.5033 | 530.3157 | 0.21616
1985 | 1094.8904 | 3.9784 | 105.4519 | 126.9932 | 61.5502 | 13.1281 | 122.0148 | 5.1523 | 18.087 | 96.4986 | 167.9373 | 32.1535 | 391.826 | 280.582 | 491.695 | 29.2702 | 115.6607 | 18.7247 | 279 | 10.1926 | 193.0557 | 465.2547 | 0.15867
1986 | 1052.2319 | 4.0186 | 99.9974 | 110.9358 | 65.3426 | 9.5253 | 111.2032 | 5.123 | 16.627 | 73.1126 | 160.6745 | 28.9336 | 351.8109 | 212.8876 | 375.181 | 15.5719 | 107.9927 | 18.0267 | 229 | 9.7935 | 165.208 | 375.0032 | 0.081508
1987 | 995.909 | 4.1537 | 96.9864 | 98.0074 | 67.0793 | 7.8754 | 102.4627 | 5.4434 | 14.753 | 45.5917 | 134.2167 | 24.188 | 311.411 | 150.3417 | 321.666 | 10.6431 | 99.792 | 16.8564 | 220 | 9.8461 | 142.6606 | 324.3387 | 0
1988 | 943.9176 | 3.9091 | 83.896 | 95.8531 | 67.373 | 7.5964 | 93.759 | 4.9536 | 10.323 | 30.9821 | 109.4002 | 11.8513 | 273.6364 | 131.8014 | 322.0672 | 10.1663 | 89.5759 | 16.3608 | 201 | 10.0415 | 132.1273 | 285.2152 | 0
1989 | 900.2423 | 4.0729 | 54.5794 | 96.0251 | 68.8532 | 6.1902 | 87.2972 | 4.8823 | 8.488 | 26.6468 | 104.0251 | 6.8877 | 228.8983 | 120.6554 | 319.0569 | 9.6619 | 78.6389 | 10.5795 | 177 | 10.0499 | 128.8424 | 262.2997 | 0
1990 | 873.4582 | 3.8526 | 35.8705 | 95.7134 | 68.6459 | 6.3872 | 76.157 | 5.1037 | 7.773 | 24.4761 | 97.6435 | 6.6307 | 205.5977 | 111.7133 | 283.267 | 9.6348 | 74.1909 | 11.877 | 175 | 9.9776 | 120.1987 | 262.459 | 0
1991 | 849.3245 | 3.1376 | 32.1642 | 93.7552 | 68.3504 | 6.6679 | 78.9519 | 5.2947 | 6.968 | 22.7041 | 81.8095 | 6.793 | 184.9898 | 105.8988 | 255.1742 | 9.5119 | 72.728 | 13.7062 | 149 | 9.9639 | 108.1482 | 258.0201 | 0
1992 | 829.7564 | 2.2277 | 32.3465 | 92.8662 | 68.3606 | 6.6582 | 80.2012 | 5.6563 | 6.495 | 22.0321 | 73.3937 | 6.9838 | 176.5204 | 101.6616 | 251.3926 | 9.5289 | 71.3961 | 13.4506 | 131 | 10.0189 | 82.5071 | 252.3471 | 0
1993 | 825.1207 | 1.8214 | 32.3472 | 90.5144 | 68.3548 | 6.6637 | 73.9806 | 5.7507 | 6.558 | 21.6405 | 71.5286 | 6.9219 | 174.0396 | 97.3651 | 255.0532 | 9.5874 | 66.7461 | 13.568 | 124 | 10.1458 | 71.1234 | 252.0146 | 0
1994 | 823.3805 | 1.7203 | 32.3499 | 89.6027 | 69.1398 | 5.918 | 74.682 | 5.9409 | 6.581 | 22.1994 | 70.6536 | 6.8156 | 167.4337 | 92.6626 | 249.235 | 9.6461 | 58.5775 | 13.2846 | 126 | 10.0369 | 69.232 | 249.4313 | 0
1995 | 819.1664 | 1.4778 | 32.3117 | 89.5233 | 69.4001 | 5.6707 | 80.2646 | 6.1558 | 6.532 | 22.8837 | 70.6462 | 6.5381 | 157.8221 | 89.3472 | 239.3138 | 9.6764 | 55.3817 | 12.0726 | 141 | 10.0784 | 69.2369 | 253.3365 | 0
1996 | 812.8299 | 1.3546 | 32.4083 | 89.8348 | 68.6784 | 6.3563 | 74.985 | 6.4857 | 6.3901 | 26.6421 | 71.332 | 6.3547 | 158.2147 | 87.713 | 231.8177 | 9.7158 | 55.3828 | 11.6258 | 116 | 10.07 | 69.2154 | 255.101 | 0
1997 | 822.7251 | 1.7251 | 32.4727 | 90.0282 | 69.0571 | 5.9966 | 71.313 | 6.3557 | 6.3074 | 36.9604 | 71.5745 | 6.3212 | 158.9427 | 87.5173 | 220.5611 | 9.6042 | 57.0593 | 11.6148 | 114 | 10.001 | 69.5859 | 275.6573 | 0
1998 | 831.8616 | 2.8968 | 40.7049 | 88.9519 | 68.6173 | 6.4143 | 79.6675 | 6.1333 | 6.1165 | 41.7368 | 70.1575 | 7.0061 | 171.1871 | 103.2006 | 218.0725 | 9.4538 | 58.8087 | 11.5509 | 122 | 10.069 | 74.9681 | 307.9832 | 0
1999 | 896.7476 | 4.0574 | 51.5358 | 93.0168 | 66.1107 | 8.7956 | 84.5613 | 6.0453 | 9.624 | 57.4942 | 98.0584 | 16.3222 | 202.0679 | 157.6089 | 264.5608 | 18.4135 | 58.991 | 11.9034 | 178 | 10.3611 | 112.6128 | 351.9096 | 0.14084
2000 | 932.2111 | 4.3997 | 77.4649 | 98.0851 | 62.3938 | 12.3267 | 106.0373 | 6.0134 | 15.626 | 88.8978 | 114.5895 | 28.3958 | 310.2506 | 199.1429 | 355.524 | 22.3559 | 58.8698 | 13.1447 | 276 | 10.055 | 151.921 | 410.5547 | 0.2419
2001 | 1021.5401 | 10.4387 | 102.8024 | 107.1665 | 59.1284 | 15.4288 | 125.6356 | 6.6323 | 16.665 | 95.456 | 151.5123 | 33.8567 | 388.6925 | 237.978 | 423.7394 | 31.7971 | 69.6189 | 14.5348 | 315 | 10.4272 | 180.2111 | 474.9502 | 0.30495
2002 | 1120.3284 | 13.537 | 110.6195 | 118.2997 | 58.4318 | 16.0906 | 137.4069 | 5.8097 | 16.304 | 93.9234 | 174.2455 | 36.4865 | 383.4434 | 271.3407 | 476.2836 | 37.7347 | 90.469 | 15.3198 | 347 | 11.8969 | 186.5157 | 510.4046 | 0.24741
2003 | 1149.4526 | 9.735 | 109.1754 | 124.6105 | 58.3764 | 16.1432 | 145.4022 | 4.9786 | 15.022 | 78.5164 | 175.877 | 37.7408 | 386.0524 | 303.1543 | 511.176 | 37.4864 | 101.8673 | 15.9693 | 358 | 12.5705 | 197.4469 | 552.764 | 0.20709
2004 | 1134.9291 | 7.3954 | 110.3077 | 127.7029 | 58.7123 | 15.8241 | 142.2104 | 5.9334 | 12.251 | 76.2036 | 173.4202 | 38.918 | 386.8295 | 315.7326 | 515.7647 | 35.4584 | 99.2584 | 16.2239 | 329 | 10.4125 | 192.2488 | 526.1253 | 0.27143
2005 | 1127.0002 | 7.201 | 111.1754 | 128.4895 | 58.8371 | 15.7055 | 139.6273 | 6.515 | 11.3 | 78.4463 | 171.9437 | 39.3473 | 384.6573 | 317.1465 | 513.9939 | 34.5454 | 96.9688 | 16.2446 | 340 | 9.5995 | 188.8037 | 510.4032 | 0.24322
2006 | 1119.8818 | 6.5387 | 111.7889 | 130.598 | 59.3055 | 15.2605 | 134.942 | 6.2231 | 10.887 | 80.2967 | 174.7147 | 37.8782 | 385.1922 | 319.0522 | 512.2975 | 32.5562 | 97.7422 | 16.6084 | 331 | 6.9903 | 192.6888 | 505.276 | 0.27495
2007 | 1083.7519 | 4.9557 | 108.115 | 125.4667 | 60.0165 | 14.5851 | 129.6216 | 4.4316 | 11.872 | 82.7194 | 175.3376 | 37.0757 | 380.4566 | 286.3956 | 511.201 | 31.4321 | 98.2547 | 16.6557 | 299 | 6.3499 | 189.1837 | 500.3308 | 0.23924
2008 | 1051.648 | 3.5269 | 104.3407 | 125.4081 | 59.7144 | 14.8721 | 126.4661 | 3.65 | 10.781 | 87.5767 | 172.9641 | 35.7432 | 362.921 | 260.7337 | 481.4865 | 30.8541 | 97.6044 | 16.6113 | 291 | 6.0529 | 182.5183 | 473.0123 | 0.15733
2009 | 1011.9972 | 2.7133 | 98.2851 | 122.0159 | 65.2235 | 9.6385 | 120.0987 | 3.8833 | 9.799 | 89.3374 | 169.5541 | 31.8035 | 343.6153 | 247.3789 | 428.675 | 25.5966 | 92.6635 | 16.3043 | 280 | 5.7905 | 169.6639 | 398.8877 | 0.040965
2010 | 952.0388 | 3.1127 | 84.3022 | 112.6643 | 66.6043 | 8.3267 | 107.812 | 3.959 | 9.572 | 80.014 | 160.4111 | 29.3156 | 308.9385 | 196.0796 | 351.2196 | 14.1185 | 78.586 | 15.5524 | 226 | 5.7455 | 149.9366 | 319.6187 | 0.0089289
2011 | 914.0441 | 3.4268 | 57.8523 | 99.058 | 67.9293 | 7.068 | 98.7611 | 4.0018 | 9.551 | 66.1415 | 130.0672 | 26.3132 | 271.1024 | 161.5206 | 308.086 | 10.025 | 66.7527 | 15.5177 | 212 | 5.713 | 134.9216 | 281.3799 | 0
2012 | 874.8784 | 3.6726 | 48.1115 | 93.461 | 69.0843 | 5.9707 | 89.3961 | 4.3288 | 8.748 | 58.5577 | 103.2335 | 17.8823 | 247.8794 | 152.575 | 291.4495 | 10.5124 | 60.5385 | 15.0691 | 213 | 5.751 | 120.3374 | 258.8492 | 0
2013 | 848.8704 | 3.6372 | 47.4729 | 92.0928 | 68.5653 | 6.4638 | 86.6346 | 4.3815 | 8.2149 | 52.7382 | 86.4589 | 13.982 | 229.0398 | 142.2111 | 296.6893 | 10.8158 | 56.2546 | 14.4231 | 194 | 5.9359 | 115.1202 | 246.5477 | 0
2014 | 830.2374 | 3.4415 | 47.224 | 91.4354 | 69.1319 | 5.9255 | 79.1287 | 4.3494 | 7.6413 | 50.126 | 75.375 | 9.925 | 208.187 | 114.9698 | 290.6989 | 10.7844 | 54.4223 | 13.8084 | 175 | 5.9963 | 111.9759 | 245.8847 | 0
2015 | 808.7182 | 2.9282 | 47.138 | 89.6953 | 68.6115 | 6.4198 | 73.0292 | 4.2872 | 7.1172 | 47.0363 | 70.0737 | 9.1112 | 199.1626 | 105.3044 | 275.5341 | 10.7986 | 54.1196 | 13.5943 | 166 | 5.9916 | 104.2866 | 243.0315 | 0
2016 | 791.6195 | 1.982 | 46.428 | 88.9348 | 69.173 | 5.8865 | 82.1588 | 4.6104 | 7.1578 | 43.5137 | 68.8746 | 8.4002 | 194.2968 | 95.83 | 263.6288 | 10.7963 | 53.5185 | 13.5673 | 164 | 6.1421 | 81.8349 | 242.9624 | 0
2017 | 776.5495 | 1.5408 | 44.7056 | 89.0303 | 69.3603 | 5.7085 | 85.6188 | 4.5539 | 7.0059 | 35.1797 | 68.4151 | 7.6989 | 199.0571 | 90.5943 | 263.5278 | 10.8132 | 51.4884 | 9.3157 | 156 | 6.0755 | 73.7859 | 239.0677 | 0
2018 | 771.9937 | 1.8282 | 44.0897 | 88.9388 | 69.4104 | 5.6609 | 84.6677 | 4.4527 | 6.5897 | 29.4145 | 68.1593 | 7.4786 | 187.8871 | 90.7757 | 264.3285 | 10.7903 | 50.6996 | 5.8221 | 155 | 5.9929 | 72.4003 | 232.7179 | 0
2019 | 765.0339 | 1.6297 | 44.0876 | 90.5286 | 69.3508 | 5.7175 | 75.9309 | 4.4018 | 6.4073 | 29.6736 | 68.2585 | 7.5657 | 179.3971 | 88.5132 | 260.6401 | 10.7267 | 50.7257 | 4.8639 | 161 | 5.907 | 70.3503 | 235.3923 | 0
2020 | 751.8909 | 1.3749 | 44.1366 | 89.6773 | 68.654 | 6.3795 | 77.4296 | 4.5916 | 6.5779 | 30.693 | 69.0039 | 8.0535 | 165.1671 | 86.904 | 245.173 | 10.8769 | 50.881 | 4.0186 | 135 | 5.8214 | 67.569 | 232.1806 | 0
2021 | 754.6722 | 1.7088 | 44.1706 | 88.5431 | 69.098 | 5.9577 | 83.2208 | 4.6316 | 6.415 | 31.5191 | 69.1489 | 7.8672 | 166.1652 | 81.5113 | 232.2011 | 10.8491 | 52.3063 | 2.8688 | 115 | 5.7779 | 65.9818 | 249.2273 | 0
2022 | 750.6842 | 2.7647 | 44.0354 | 88.424 | 69.3565 | 5.7121 | 85.1453 | 4.4886 | 6.212 | 35.3082 | 68.7853 | 7.4826 | 167.3799 | 88.6461 | 224.1162 | 10.6834 | 54.5762 | 2.9906 | 103 | 5.8347 | 66.0044 | 270.015 | 0
2023 | 760.8975 | 3.2573 | 43.8664 | 87.4842 | 68.6052 | 6.4259 | 78.8849 | 4.2738 | 5.827 | 46.6096 | 71.6345 | 5.7656 | 167.7109 | 98.2772 | 225.2012 | 10.4377 | 51.6928 | 3.3541 | 110 | 5.8243 | 68.5395 | 260.6633 | 0.0081737
2024 | 776.521 | 3.0908 | 44.1711 | 87.1658 | 64.6251 | 10.207 | 84.3892 | 4.096 | 5.323 | 62.4889 | 87.5096 | 4.7692 | 164.1884 | 116.9357 | 247.2257 | 10.2178 | 50.763 | 4.7051 | 117 | 5.7462 | 71.351 | 255.4027 | 0.024295
2025 | 796.3816 | 1.9079 | 44.3737 | 86.5428 | 62.6678 | 12.0663 | 96.5337 | 4.2159 | 5.24 | 62.8491 | 98.0668 | 4.6306 | 172.5216 | 133.6371 | 269.6407 | 10.2285 | 52.0032 | 10.3517 | 138 | 5.646 | 75.4724 | 250.4326 | 0.037458
2026 | 815.3045 | 1.3701 | 44.5264 | 86.8202 | 63.9569 | 10.8418 | 100.1034 | 4.3399 | 6.0495 | 58.5181 | 101.035 | 4.6359 | 204.2399 | 140.7795 | 282.8477 | 10.2356 | 53.0755 | 12.8619 | 140 | 5.6571 | 74.395 | 254.6864 | 0.050693
2027 | 832.5375 | 1.3797 | 44.6587 | 87.4847 | 65.0159 | 9.8357 | 99.6598 | 4.0489 | 6.3786 | 56.4533 | 105.258 | 4.6289 | 212.3745 | 152.1631 | 291.2905 | 10.2714 | 57.4389 | 12.8497 | 141 | 5.6252 | 82.1296 | 252.5731 | 0.046982
2028 | 847.0746 | 1.5755 | 44.7929 | 88.418 | 65.3372 | 9.5305 | 98.1129 | 3.9253 | 6.3789 | 54.4994 | 112.8968 | 4.6321 | 218.1371 | 158.0845 | 290.3425 | 10.2762 | 59.3626 | 12.8439 | 139 | 5.6204 | 83.0687 | 257.9058 | 0.056684
2029 | 865.3425 | 1.5584 | 45.0989 | 88.7139 | 64.6399 | 10.1929 | 94.874 | 4.2817 | 5.813 | 58.0457 | 120.0593 | 4.6399 | 220.0526 | 164.8065 | 296.6937 | 10.137 | 57.2876 | 13.0514 | 136 | 5.6317 | 79.0126 | 258.5277 | 0.051594
2030 | 850.5211 | 1.9393 | 44.8044 | 90.4686 | 65.1461 | 9.712 | 89.719 | 6.3871 | 6.039 | 58.4075 | 122.2635 | 4.6795 | 211.9021 | 165.3205 | 305.0054 | 10.1325 | 58.7835 | 13.9372 | 130 | 5.6149 | 84.512 | 248.6863 | 0.07264
2031 | 844.4769 | 1.7107 | 44.6912 | 92.1592 | 65.3035 | 9.5625 | 86.1718 | 5.4874 | 6.478 | 59.2613 | 122.8318 | 4.7109 | 210.9079 | 164.6273 | 302.5681 | 10.1409 | 60.8155 | 13.7973 | 124 | 5.6107 | 83.591 | 259.6814 | 0.047062
2032 | 851.9703 | 1.7392 | 45.2046 | 90.9909 | 63.8937 | 10.9018 | 85.4503 | 4.1672 | 6.426 | 58.7697 | 123.2585 | 4.6375 | 204.9805 | 167.6681 | 308.6822 | 10.1424 | 58.1673 | 13.4901 | 123 | 5.5475 | 81.1679 | 270.662 | 0.03829
2033 | 846.4527 | 2.4955 | 44.7444 | 89.9603 | 67.8948 | 7.1008 | 84.0841 | 4.1948 | 7.025 | 59.0129 | 122.536 | 4.5919 | 206.855 | 168.676 | 287.227 | 10.1258 | 56.2967 | 13.4695 | 123 | 5.5285 | 75.6132 | 274.1253 | 0.012622
2034 | 825.0845 | 1.9157 | 44.3052 | 88.599 | 69.3485 | 5.7197 | 82.3572 | 4.0454 | 6.512 | 48.6096 | 113.0273 | 4.63 | 202.8845 | 146.8546 | 251.3356 | 9.4666 | 58.2492 | 13.1314 | 126 | 5.6286 | 72.1526 | 245.2447 | 0.012452
2035 | 805.5563 | 2.6989 | 44.2026 | 86.7597 | 69.3737 | 5.6958 | 82.3266 | 4.354 | 6.086 | 31.9769 | 85.0192 | 4.9951 | 189.1593 | 126.7098 | 257.6863 | 9.6254 | 58.3188 | 13.0358 | 128 | 5.6809 | 70.9166 | 237.6357 | 0
2036 | 789.178 | 4.1561 | 44.3397 | 89.5506 | 68.6455 | 6.3876 | 82.7387 | 4.8924 | 6.61 | 29.771 | 73.2957 | 6.9626 | 182.8918 | 121.649 | 265.6089 | 10.4583 | 54.7036 | 13.1543 | 129 | 5.736 | 72.3489 | 235.6769 | 0
2037 | 780.2327 | 3.6927 | 44.3266 | 91.9361 | 69.1124 | 5.9441 | 79.6761 | 5.116 | 6.885 | 31.3598 | 73.769 | 7.6082 | 177.138 | 110.6775 | 258.0897 | 10.7039 | 52.4115 | 7.4364 | 136 | 5.6277 | 72.0916 | 237.7765 | 0
2038 | 775.3405 | 3.2485 | 44.321 | 90.6884 | 69.3531 | 5.7154 | 70.6091 | 5.1778 | 6.739 | 31.638 | 74.0353 | 7.6203 | 162.8448 | 98.9379 | 243.8442 | 10.6549 | 51.7111 | 3.6242 | 128 | 5.6581 | 69.5203 | 240.5509 | 0
2039 | 759.4668 | 2.9171 | 44.2022 | 88.7495 | 67.8642 | 7.1298 | 73.9453 | 5.1118 | 6.432 | 32.3522 | 71.7004 | 7.6997 | 155.9573 | 92.3445 | 225.0749 | 10.6622 | 51.5725 | 2.8099 | 124 | 5.6194 | 66.2232 | 240.5343 | 0
2040 | 740.2921 | 2.1913 | 44.8126 | 88.368 | 68.8555 | 6.1881 | 81.1798 | 5.0141 | 6.365 | 32.095 | 69.6541 | 7.7758 | 151.3113 | 88.4285 | 220.8356 | 10.7219 | 51.8548 | 2.5848 | 121 | 5.6298 | 64.9859 | 235.7012 | 0
2041 | 726.6363 | 1.7409 | 46.868 | 89.0376 | 69.3952 | 5.6753 | 83.4999 | 5.1354 | 6.366 | 32.7062 | 69.5889 | 7.6394 | 150.5092 | 85.7871 | 233.9578 | 10.6698 | 52.0427 | 2.5719 | 118 | 5.6496 | 65.1719 | 236.6355 | 0
2042 | 715.0558 | 1.553 | 47.5704 | 88.5556 | 69.3402 | 5.7276 | 73.8837 | 5.547 | 6.486 | 33.0851 | 70.9048 | 7.5697 | 151.7437 | 84.8489 | 236.6831 | 10.7482 | 52.1299 | 2.7138 | 113 | 5.6931 | 66.7727 | 240.3422 | 0
2043 | 702.514 | 1.4801 | 47.4741 | 88.3099 | 69.376 | 5.6936 | 67.8083 | 6.0569 | 6.589 | 31.7361 | 70.4005 | 7.5075 | 151.0513 | 85.2365 | 223.866 | 10.6348 | 51.7461 | 3.0358 | 125 | 5.6121 | 66.9649 | 247.4686 | 0
2044 | 706.9859 | 1.5224 | 47.402 | 88.4002 | 69.3799 | 5.6899 | 77.5619 | 5.885 | 6.61 | 32.4844 | 70.3461 | 7.4541 | 148.3525 | 84.8146 | 214.5753 | 10.5982 | 51.8359 | 3.121 | 99 | 5.5575 | 64.4918 | 244.6816 | 0
2045 | 705.4831 | 1.9738 | 47.2396 | 88.4536 | 68.6334 | 6.399 | 80.6545 | 5.7785 | 6.407 | 36.7237 | 70.6172 | 7.4949 | 146.094 | 84.9135 | 210.6255 | 10.6265 | 53.6206 | 3.1007 | 96 | 5.5829 | 62.5625 | 243.993 | 0
2046 | 701.0877 | 3.0835 | 47.2256 | 86.828 | 69.8425 | 5.2504 | 71.3306 | 5.5371 | 5.977 | 37.0553 | 67.7739 | 6.6047 | 146.0047 | 82.861 | 204.9821 | 10.4656 | 55.0992 | 3.0309 | 98 | 5.5839 | 62.8934 | 240.3816 | 0
2047 | 707.8009 | 1.9035 | 47.3532 | 85.6768 | 69.603 | 5.4779 | 67.4769 | 4.9585 | 5.851 | 37.8537 | 65.5598 | 5.1288 | 146.6295 | 80.9123 | 200.6373 | 10.3213 | 51.7359 | 2.8531 | 96 | 5.6116 | 64.8593 | 230.4175 | 0.043395
2048 | 718.1606 | 1.2581 | 47.5245 | 86.2481 | 68.6699 | 6.3643 | 77.1578 | 4.5756 | 5.825 | 36.6617 | 66.1469 | 4.6352 | 153.4304 | 82.4549 | 197.734 | 10.1602 | 49.5588 | 3.0453 | 102 | 5.6 | 72.653 | 228.1752 | 0.099922
2049 | 723.1993 | 1.5255 | 47.3349 | 87.0981 | 67.5578 | 7.4209 | 82.2374 | 4.6338 | 5.334 | 41.7106 | 68.4248 | 4.9131 | 170.0675 | 85.5623 | 200.847 | 10.118 | 50.0737 | 3.6611 | 109 | 5.6249 | 71.8423 | 225.8973 | 0.089702
2050 | 730.0606 | 1.6247 | 47.0255 | 86.6085 | 68.8389 | 6.2038 | 73.6729 | 3.9149 | 5.578 | 60.4668 | 69.8677 | 8.1717 | 178.2788 | 90.3381 | 202.1292 | 9.9464 | 50.5167 | 5.7628 | 115 | 5.8688 | 66.7955 | 227.8276 | 0.16049
2051 | 739.699 | 1.9834 | 47.5543 | 86.6652 | 69.3668 | 5.7024 | 68.1979 | 3.3993 | 6.218 | 62.7224 | 70.3149 | 9.0454 | 180.6311 | 93.271 | 202.3685 | 9.2785 | 52.6457 | 11.0009 | 122 | 5.9195 | 72.597 | 225.5288 | 0.25446
2052 | 750.942 | 2.1523 | 47.786 | 87.9364 | 69.4015 | 5.6694 | 76.998 | 2.7549 | 6.207 | 57.4965 | 69.8836 | 5.8937 | 182.3934 | 99.5243 | 203.8968 | 9.2129 | 54.4223 | 12.8842 | 117 | 5.8049 | 72.7888 | 232.8498 | 0.27973
2053 | 746.0945 | 1.6977 | 47.8018 | 88.8275 | 69.3931 | 5.6773 | 81.403 | 3.0395 | 6.407 | 56.3479 | 69.4019 | 4.7068 | 187.0397 | 103.885 | 203.1549 | 9.1094 | 53.7948 | 12.8537 | 111 | 5.6454 | 67.1611 | 226.8744 | 0.26777
2054 | 751.1171 | 1.5041 | 47.6537 | 89.4889 | 69.325 | 5.742 | 81.5917 | 3.3739 | 6.901 | 56.8076 | 70.0623 | 4.711 | 189.9922 | 110.8127 | 211.4974 | 9.1206 | 51.4203 | 13.081 | 113 | 5.7078 | 71.1891 | 222.2466 | 0.28752
2055 | 755.2215 | 1.6803 | 47.8475 | 89.7782 | 70.132 | 4.9754 | 82.0261 | 3.6414 | 7.291 | 57.1013 | 70.027 | 7.2672 | 189.1483 | 112.8914 | 220.6058 | 9.2315 | 53.3059 | 13.2364 | 114 | 5.7234 | 69.3826 | 215.7997 | 0.21421
2056 | 748.3945 | 1.5357 | 47.9581 | 89.1755 | 69.633 | 5.4494 | 81.699 | 3.5638 | 6.872 | 49.7878 | 70.4281 | 9.2396 | 192.9531 | 108.5 | 225.4489 | 9.1363 | 54.9831 | 13.3589 | 114 | 5.6951 | 66.8394 | 211.3738 | 0.16436
2057 | 749.0932 | 1.6186 | 47.4302 | 89.492 | 69.3815 | 5.6883 | 81.6257 | 2.3243 | 6.79 | 33.5861 | 68.7869 | 7.0737 | 194.047 | 103.7569 | 214.146 | 9.1381 | 52.2895 | 13.4253 | 118 | 5.8263 | 61.1382 | 214.7047 | 0.093499
2058 | 748.3853 | 1.8301 | 47.1151 | 89.0487 | 69.3604 | 5.7084 | 81.5303 | 3.2327 | 6.143 | 28.1251 | 65.812 | 5.2125 | 197.6788 | 101.9592 | 206.5345 | 9.1748 | 51.0543 | 13.3312 | 115 | 5.8843 | 61.1303 | 214.4556 | 0.035737
2059 | 749.0746 | 3.1465 | 46.9533 | 89.0057 | 69.3633 | 5.7057 | 81.5746 | 4.1787 | 6.008 | 28.672 | 66.2395 | 5.3322 | 189.2276 | 103.3176 | 202.9783 | 9.1983 | 50.1771 | 13.1036 | 115 | 5.6836 | 61.2288 | 221.3248 | 0
2060 | 737.4697 | 3.5744 | 47.2827 | 89.6234 | 69.3787 | 5.691 | 82.3146 | 4.3871 | 6.801 | 31.5282 | 71.0122 | 7.1006 | 195.7048 | 105.6349 | 208.7585 | 9.9333 | 50.3503 | 11.2347 | 112 | 5.6867 | 60.0423 | 231.1698 | 0
2061 | 735.7801 | 3.3879 | 47.5505 | 91.3995 | 69.3615 | 5.7073 | 83.0261 | 4.6905 | 6.949 | 32.863 | 71.5812 | 7.7244 | 200.4598 | 99.6828 | 219.6374 | 10.3985 | 50.5829 | 6.1513 | 114 | 5.6876 | 62.3297 | 245.8682 | 0
2062 | 737.6761 | 3.2845 | 47.5824 | 91.369 | 69.3716 | 5.6978 | 83.0292 | 5.0353 | 6.467 | 33.4722 | 71.9401 | 7.542 | 195.2114 | 91.6783 | 229.1293 | 10.5666 | 50.3804 | 3.6811 | 122 | 5.7415 | 63.287 | 236.8735 | 0
2063 | 737.9075 | 3.3043 | 47.636 | 90.6837 | 69.3837 | 5.6862 | 83.044 | 4.9468 | 6.157 | 34.3849 | 71.0761 | 7.4516 | 185.5447 | 88.4869 | 229.8386 | 10.6022 | 50.1648 | 2.8778 | 106 | 5.6776 | 60.2618 | 247.1424 | 0
2064 | 719.1449 | 2.2469 | 47.1663 | 89.2602 | 69.3587 | 5.71 | 82.9633 | 4.7956 | 6.065 | 33.2948 | 70.7026 | 7.4773 | 178.76 | 86.9983 | 217.4721 | 10.5971 | 50.2126 | 2.5758 | 107 | 5.6943 | 58.2633 | 263.1905 | 0
2065 | 723.3057 | 1.6617 | 45.2649 | 88.5117 | 69.3826 | 5.6873 | 82.6848 | 4.8144 | 6.148 | 31.4619 | 69.7656 | 7.4926 | 165.5662 | 84.7014 | 210.2115 | 10.6412 | 50.2122 | 2.3743 | 101 | 5.8583 | 57.5517 | 261.5319 | 0
2066 | 720.7005 | 1.4659 | 44.6758 | 89.2268 | 69.336 | 5.7316 | 82.8248 | 4.8512 | 5.945 | 31.6184 | 69.4847 | 7.5252 | 156.4093 | 84.3758 | 201.9885 | 10.2033 | 50.0709 | 2.3239 | 107 | 5.7374 | 55.8985 | 254.4032 | 0
2067 | 712.22 | 1.5379 | 44.6916 | 88.6428 | 67.8752 | 7.1194 | 83.0406 | 4.7737 | 0 | 16.7208 | 35.336 | 7.5374 | -1.3459 | 44.6616 | 107.0407 | 9.8472 | 25.1948 | 2.3383 | 99 | 5.9149 | 56.6168 | 98.5767 | 0
2068 | 718.3 | 1.9902 | 44.7052 | 88.2842 | 65.1227 | 9.7342 | 82.9384 | 4.9879 | 6.225 | 34.2982 | 70.8229 | 7.5463 | 153.0908 | 85.4603 | 201.0379 | 9.7066 | 51.3238 | 2.3141 | 108 | 5.8324 | 56.3313 | 237.3489 | 0
2069 | 720.7201 | 2.8511 | 44.8464 | 88.0234 | 65.1234 | 9.7335 | 83.0198 | 4.84 | 6.075 | 37.2592 | 71.073 | 7.5572 | 151.8547 | 85.2732 | 202.002 | 9.6541 | 53.3819 | 2.3404 | 116 | 5.9442 | 55.5114 | 234.1532 | 0
2070 | 728.4308 | 3.0731 | 44.6913 | 86.7282 | 68.369 | 6.6502 | 85.5799 | 4.5804 | 5.94 | 39.9586 | 69.946 | 7.7538 | 151.6197 | 84.0251 | 199.9553 | 9.5644 | 52.9653 | 2.3296 | 113 | 5.9573 | 55.4835 | 230.3561 | 0
2071 | 735.6477 | 1.7362 | 44.3846 | 85.4196 | 69.3603 | 5.7085 | 89.7939 | 4.3203 | 5.989 | 37.9416 | 67.5598 | 6.5548 | 148.2651 | 81.8253 | 197.4047 | 9.2216 | 50.1048 | 2.5499 | 108 | 5.7764 | 56.5367 | 219.1204 | 0.04722
2072 | 732.4853 | 1.122 | 44.2565 | 85.526 | 68.6436 | 6.3894 | 84.3104 | 3.8985 | 6.213 | 38.429 | 67.1351 | 6.0022 | 153.1583 | 81.7857 | 197.8359 | 9.1065 | 48.3426 | 3.1985 | 104 | 5.4975 | 58.1555 | 212.9186 | 0.099989
2073 | 756.2815 | 1.3197 | 44.1698 | 85.7059 | 66.1473 | 8.7609 | 80.5898 | 3.6455 | 5.803 | 49.9207 | 68.4987 | 5.9702 | 159.3867 | 85.8642 | 201.6445 | 9.1694 | 48.1007 | 3.4153 | 105 | 6.2248 | 60.1173 | 211.8528 | 0.15537
2074 | 770.6642 | 1.4229 | 44.6557 | 91.2828 | 67.6006 | 7.3802 | 79.56 | 2.412 | 5.59 | 58.4461 | 69.3334 | 5.9126 | 177.8137 | 91.8973 | 211.6573 | 9.049 | 49.2466 | 5.2559 | 119 | 6.53 | 59.343 | 211.2636 | 0.15579
2075 | 785.7956 | 1.3621 | 44.7995 | 94.0614 | 68.3622 | 6.6567 | 60.9075 | 2.8611 | 6.36 | 56.1235 | 73.8758 | 6.1133 | 182.3677 | 95.1156 | 221.7359 | 9.1958 | 52.7393 | 10.354 | 130 | 5.8523 | 59.0957 | 210.1334 | 0.15476
2076 | 796.9932 | 1.2092 | 44.784 | 93.3165 | 69.8736 | 5.2209 | 72.079 | 3.2803 | 6.424 | 53.7905 | 83.1429 | 8.8567 | 181.916 | 102.3816 | 221.9097 | 9.1768 | 56.2991 | 12.2827 | 138 | 5.5918 | 59.2318 | 207.0307 | 0.15175
2077 | 800.0101 | 1.314 | 44.9349 | 93.3678 | 69.6394 | 5.4433 | 89.2807 | 3.4174 | 6.128 | 55.2452 | 88.9238 | 10.4849 | 173.4643 | 116.1901 | 219.7221 | 9.0946 | 56.1246 | 12.2973 | 134 | 5.5705 | 59.5289 | 208.8871 | 0.10264
2078 | 791.0706 | 1.8283 | 45.0553 | 92.7327 | 69.3137 | 5.7528 | 85.2526 | 3.6593 | 5.875 | 57.7292 | 89.9986 | 9.8631 | 169.4297 | 124.6749 | 233.245 | 9.172 | 53.0043 | 12.5746 | 121 | 5.5982 | 60.4795 | 213.1439 | 0.050406
2079 | 799.466 | 2.4406 | 44.9253 | 92.1938 | 68.6752 | 6.3593 | 81.3928 | 3.8034 | 5.884 | 56.4343 | 91.2162 | 7.0715 | 179.0424 | 126.745 | 254.5297 | 9.5887 | 50.1608 | 13.0662 | 126 | 5.8397 | 62.0993 | 216.1778 | 0.020828
2080 | 793.6653 | 1.6981 | 44.2674 | 89.0628 | 69.1 | 5.9558 | 80.9481 | 3.9255 | 5.976 | 46.2885 | 91.1967 | 6.0025 | 199.5916 | 124.9153 | 262.4244 | 10.1474 | 50.525 | 13.5438 | 136 | 5.5698 | 63.4406 | 218.5643 | 0.013946
2081 | 780.4133 | 1.6256 | 43.9618 | 86.6831 | 70.0812 | 5.0236 | 81.4364 | 4.2217 | 6.5073 | 32.9183 | 87.8722 | 5.9554 | 215.8035 | 120.9705 | 251.5974 | 10.3822 | 52.6731 | 13.7075 | 118 | 5.4104 | 62.4534 | 221.3036 | 0.032448
2082 | 774.3178 | 2.3044 | 44.0265 | 87.4967 | 69.6218 | 5.4601 | 90.2661 | 4.2134 | 6.6497 | 26.1074 | 79.545 | 5.9668 | 213.1699 | 113.7251 | 244.4798 | 10.2162 | 52.0817 | 13.0835 | 116 | 5.5063 | 63.1164 | 220.8328 | 0.010596
2083 | 767.5503 | 3.0398 | 44.0738 | 87.298 | 69.3956 | 5.6749 | 82.0874 | 4.2807 | 6.722 | 24.9256 | 71.3991 | 6.6766 | 201.0476 | 106.4642 | 251.6951 | 10.3577 | 49.9895 | 10.5473 | 124 | 5.7088 | 61.5135 | 219.7886 | 0
2084 | 770.2509 | 3.6547 | 44.317 | 90.5633 | 67.881 | 7.1138 | 86.0736 | 4.5697 | 6.343 | 25.5156 | 70.8253 | 8.086 | 201.5122 | 103.3413 | 248.0656 | 10.6978 | 49.7187 | 5.4076 | 116 | 5.8007 | 62.6584 | 229.9308 | 0
2085 | 778.0804 | 3.8225 | 44.6002 | 91.5245 | 68.8329 | 6.2095 | 93.3423 | 4.5476 | 6.37 | 26.555 | 73.182 | 7.7791 | 198.8351 | 101.3957 | 233.2078 | 10.7529 | 50.1835 | 2.9127 | 109 | 5.9196 | 65.7047 | 240.9465 | 0
2086 | 766.0408 | 3.056 | 44.6895 | 89.309 | 69.3579 | 5.7108 | 87.1988 | 4.4237 | 6.047 | 26.9519 | 73.5644 | 7.4543 | 182.2083 | 98.106 | 216.3136 | 10.6623 | 50.2747 | 2.6062 | 99 | 5.8549 | 64.6957 | 243.6448 | 0
2087 | 756.0997 | 1.9203 | 44.644 | 88.4514 | 68.6973 | 6.3384 | 83.4769 | 4.4307 | 5.814 | 26.8756 | 72.746 | 7.6933 | 174.2087 | 93.8612 | 207.6792 | 10.6582 | 50.2568 | 2.6012 | 101 | 5.9303 | 62.6022 | 239.6552 | 0
2088 | 747.213 | 1.4814 | 44.5712 | 88.396 | 69.0797 | 5.975 | 83.5546 | 4.65 | 5.8957 | 26.6631 | 71.9081 | 7.7742 | 174.2129 | 90.2713 | 212.959 | 10.6706 | 50.282 | 2.8685 | 97 | 5.9661 | 63.5158 | 235.158 | 0
2089 | 747.0799 | 1.3132 | 44.5763 | 88.541 | 69.3433 | 5.7247 | 82.2099 | 4.5101 | 5.8562 | 26.5204 | 70.7499 | 7.563 | 167.5281 | 88.3382 | 219.1492 | 10.6006 | 50.6787 | 3.1751 | 99 | 5.7645 | 60.5947 | 234.3741 | 0
2090 | 745.7505 | 1.2451 | 44.8536 | 88.4885 | 69.3287 | 5.7385 | 81.1127 | 4.5485 | 5.8401 | 26.9417 | 69.9596 | 7.4968 | 157.9136 | 91.01 | 213.7467 | 10.6258 | 50.8803 | 2.8234 | 117 | 5.8086 | 58.2194 | 235.506 | 0
2091 | 741.8961 | 1.519 | 45.1256 | 88.7805 | 69.3954 | 5.6751 | 82.5324 | 4.7935 | 5.85 | 28.6517 | 70.2194 | 7.5108 | 152.8166 | 95.8248 | 207.4985 | 10.7802 | 50.4822 | 2.6149 | 98 | 5.8081 | 57.4073 | 238.0169 | 0
2092 | 739.7926 | 1.8397 | 45.6317 | 88.3555 | 69.3873 | 5.6829 | 80.9537 | 4.8823 | 6.081 | 30.9159 | 70.6917 | 7.5065 | 147.2187 | 94.7818 | 206.7439 | 10.6557 | 50.9983 | 2.6188 | 97 | 5.7656 | 56.7307 | 252.4498 | 0
2093 | 747.2015 | 2.8839 | 44.8806 | 88.3464 | 69.4042 | 5.6668 | 70.6694 | 4.9476 | 6.236 | 33.9755 | 71.3091 | 7.7921 | 145.0563 | 93.4744 | 205.4266 | 10.6726 | 52.9354 | 2.7139 | 99 | 5.7834 | 56.529 | 270.9986 | 0
2094 | 751.6688 | 3.3719 | 44.3791 | 87.4856 | 68.6461 | 6.387 | 76.4877 | 5.0732 | 6.477 | 42.2928 | 75.611 | 6.7784 | 147.325 | 102.1878 | 208.4062 | 10.4884 | 53.0636 | 4.4357 | 99 | 5.8076 | 58.8145 | 269.6697 | 0
2095 | 774.7726 | 2.5094 | 44.8685 | 85.566 | 65.4098 | 9.4614 | 86.7421 | 4.8455 | 6.381 | 57.558 | 86.0002 | 5.1682 | 148.1453 | 116.0612 | 228.0602 | 10.2298 | 50.9596 | 9.6533 | 112 | 5.7187 | 67.2805 | 260.4228 | 0.034996
2096 | 781.3006 | 2.1936 | 45.1499 | 84.9255 | 64.3478 | 10.4704 | 93.4859 | 4.142 | 6.433 | 66.4747 | 96.0701 | 4.9353 | 155.6816 | 128.0341 | 254.3417 | 10.0327 | 49.7379 | 12.378 | 119 | 5.5404 | 72.497 | 252.4237 | 0.089495
2097 | 800.0365 | 1.9494 | 44.8882 | 85.6939 | 63.524 | 11.253 | 96.4501 | 4.003 | 6.784 | 63.346 | 101.9981 | 5.4548 | 184.9967 | 136.8487 | 272.5493 | 9.4983 | 49.8581 | 12.909 | 120 | 5.4781 | 71.1568 | 247.5133 | 0.21187
2098 | 843.4951 | 1.842 | 44.5865 | 86.2879 | 64.1573 | 10.6514 | 90.6206 | 3.8099 | 6.238 | 56.621 | 109.0257 | 5.0145 | 209.5888 | 143.3585 | 286.2494 | 9.0951 | 50.7577 | 13.4476 | 118 | 5.4654 | 74.74 | 244.571 | 0.2756
2099 | 863.5231 | 1.8524 | 44.6781 | 86.4182 | 64.4115 | 10.4098 | 84.1657 | 3.4115 | 6.426 | 52.6709 | 116.0471 | 4.7755 | 209.1023 | 149.8537 | 297.3909 | 9.1654 | 52.9565 | 13.5744 | 121 | 5.543 | 76.6882 | 242.3159 | 0.24299
2100 | 859.8225 | 2.4638 | 44.8086 | 87.2868 | 65.1261 | 9.731 | 80.5657 | 2.081 | 6.763 | 53.0169 | 119.8232 | 4.848 | 205.5546 | 156.2573 | 305.3999 | 9.1631 | 56.1714 | 13.6168 | 121 | 5.5243 | 74.8322 | 244.5744 | 0.25436
2101 | 850.6226 | 2.1416 | 44.7283 | 88.4309 | 64.6295 | 10.2027 | 74.7585 | 2.6561 | 7.702 | 55.7133 | 122.3956 | 5.0282 | 205.3963 | 159.7068 | 315.7871 | 9.1641 | 57.4648 | 13.6458 | 137 | 5.4917 | 78.3171 | 246.6972 | 0.29379
2102 | 836.257 | 1.5807 | 44.7266 | 89.2775 | 63.5562 | 11.2224 | 75.3583 | 3.0464 | 8.689 | 59.0783 | 124.8026 | 5.0229 | 205.954 | 163.7719 | 322.0298 | 9.0909 | 56.6458 | 14.0205 | 131 | 5.4168 | 75.2252 | 243.5392 | 0.26417
2103 | 848.2164 | 1.2354 | 44.6861 | 93.2123 | 63.3967 | 11.374 | 80.3267 | 1.9993 | 8.971 | 61.7759 | 125.4781 | 4.8809 | 201.1561 | 171.0396 | 320.3067 | 9.0665 | 56.0482 | 14.4783 | 127 | 5.5701 | 70.432 | 238.3931 | 0.20627
2104 | 853.6922 | 1.1274 | 44.6372 | 93.0342 | 67.8356 | 7.157 | 74.6984 | 2.3998 | 8.679 | 63.5766 | 123.6372 | 5.3072 | 204.5116 | 176.5805 | 309.1316 | 9.1282 | 56.0293 | 14.4681 | 135 | 5.6953 | 66.0796 | 234.7948 | 0.16788
2105 | 849.2781 | 1.663 | 44.1977 | 91.9317 | 70.0972 | 5.0084 | 66.9314 | 3.0508 | 8.158 | 56.0921 | 117.2515 | 4.9497 | 207.1283 | 163.7875 | 288.0771 | 9.1588 | 55.1596 | 13.8213 | 135 | 5.7473 | 62.9648 | 226.7483 | 0.09995
2106 | 833.3965 | 5.8407 | 44.0919 | 90.8362 | 70.3852 | 4.7348 | 55.4319 | 2.9051 | 7.941 | 38.2931 | 104.5105 | 4.854 | 213.8628 | 137.2525 | 277.8114 | 9.2139 | 52.9412 | 13.3059 | 135 | 5.7534 | 61.846 | 213.6385 | 0.046977
2107 | 804.0334 | 5.458 | 43.9619 | 89.8983 | 69.6353 | 5.4473 | 69.5947 | 2.7451 | 7.731 | 25.5544 | 91.7738 | 5.677 | 216.9664 | 118.5976 | 274.7271 | 9.2592 | 50.9337 | 13.2842 | 138 | 5.6331 | 62.8767 | 207.3067 | 0
2108 | 776.4765 | 3.8049 | 44.5176 | 90.6745 | 69.3934 | 5.6771 | 81.8354 | 3.435 | 7.503 | 24.6593 | 80.8282 | 7.1464 | 202.2632 | 110.587 | 264.886 | 9.4439 | 50.1088 | 8.238 | 123 | 5.7518 | 62.4412 | 211.6946 | 0
2109 | 755.9422 | 3.9197 | 44.6384 | 90.1329 | 69.3522 | 5.7162 | 83.8104 | 3.8683 | 7.6025 | 26.7287 | 71.282 | 7.3573 | 185.6644 | 106.6552 | 241.1572 | 9.6333 | 50.0186 | 4.339 | 114 | 5.7931 | 62.8787 | 221.3426 | 0
2110 | 738.5038 | 2.8688 | 44.7479 | 90.9499 | 69.3564 | 5.7122 | 84.2186 | 4.0747 | 7.0298 | 26.6307 | 66.096 | 7.2784 | 172.9519 | 100.6557 | 221.1364 | 9.7507 | 50.1494 | 3.0541 | 107 | 5.876 | 60.054 | 227.0611 | 0
2111 | 726.5682 | 2.0473 | 45.3077 | 90.766 | 69.3925 | 5.6779 | 84.2452 | 4.1969 | 6.3177 | 26.1561 | 64.1587 | 7.5053 | 166.452 | 94.8914 | 213.1989 | 9.6024 | 50.7273 | 2.7501 | 105 | 5.8893 | 58.1565 | 227.4195 | 0
2112 | 742.0647 | 1.478 | 47.0896 | 89.5891 | 69.3496 | 5.7186 | 84.3862 | 4.2353 | 6.21 | 25.7407 | 63.7247 | 7.438 | 160.6703 | 90.5994 | 215.9435 | 9.6351 | 52.4266 | 2.7357 | 100 | 5.947 | 61.2296 | 223.1908 | 0
2113 | 750.8224 | 1.1929 | 47.7096 | 89.2363 | 69.3432 | 5.7248 | 84.1525 | 4.2599 | 6.1 | 25.5085 | 64.9475 | 7.3836 | 158.3027 | 85.3783 | 218.0206 | 9.5974 | 54.0942 | 2.7625 | 99 | 5.9206 | 61.8924 | 222.1603 | 0
2114 | 743.9791 | 1.2542 | 47.6109 | 88.9445 | 69.3749 | 5.6947 | 84.0893 | 4.6656 | 6.152 | 25.5232 | 67.9757 | 7.4005 | 161.0636 | 81.9378 | 212.1707 | 10.0145 | 54.512 | 2.7508 | 121 | 5.9855 | 61.6436 | 227.8157 | 0
2115 | 740.0428 | 1.2901 | 47.5808 | 88.8771 | 69.3793 | 5.6905 | 84.254 | 4.7843 | 6.109 | 27.1886 | 70.7787 | 7.3858 | 159.02 | 81.9742 | 208.7432 | 10.644 | 54.549 | 2.7573 | 96 | 6.0257 | 61.8857 | 228.8628 | 0
2116 | 748.9981 | 1.7053 | 47.5951 | 88.9809 | 68.6682 | 6.366 | 84.0281 | 4.7053 | 6.147 | 34.2636 | 71.0438 | 7.3558 | 155.0607 | 83.0073 | 209.7708 | 10.6207 | 55.3959 | 2.7646 | 99 | 6.0243 | 62.6058 | 235.392 | 0
2117 | 765.4846 | 1.8763 | 56.1106 | 90.7864 | 68.3077 | 6.7084 | 84.6001 | 4.6877 | 6.054 | 43.1297 | 68.544 | 8.6917 | 153.5623 | 88.1669 | 210.3853 | 10.5189 | 57.0929 | 2.7883 | 112 | 5.9017 | 66.37 | 259.9272 | 0
2118 | 795.1123 | 3.4352 | 75.1779 | 92.8194 | 66.8738 | 8.0707 | 94.0725 | 4.4814 | 6.175 | 53.63 | 72.5286 | 15.0019 | 158.4799 | 117.6961 | 220.2284 | 13.838 | 56.806 | 3.4927 | 142 | 6.4393 | 99.6196 | 301.9217 | 0
2119 | 845.4788 | 4.4338 | 91.7263 | 94.7231 | 64.1942 | 10.6163 | 116.9186 | 5.0163 | 5.914 | 70.6629 | 96.0972 | 26.672 | 200.5132 | 164.9647 | 261.371 | 24.8665 | 58.5192 | 3.6038 | 215 | 10.0642 | 139.456 | 365.4592 | 0.02945
2120 | 949.2911 | 6.241 | 103.2642 | 111.1116 | 60.389 | 14.2313 | 128.1261 | 5.9146 | 5.7 | 75.9431 | 131.1862 | 28.5579 | 248.4046 | 218.0329 | 356.9887 | 30.6185 | 67.8158 | 4.9695 | 208 | 11.2848 | 153.0651 | 445.1489 | 0.085642
2121 | 995.346 | 7.0955 | 106.369 | 117.7506 | 59.309 | 15.2572 | 129.3405 | 6.2235 | 9.821 | 67.6303 | 153.7329 | 27.6614 | 302.7978 | 255.8835 | 445.9882 | 31.0089 | 76.6871 | 5.6335 | 296 | 11.2914 | 154.3286 | 497.2261 | 0.054495
2122 | 1044.7531 | 6.0263 | 107.5703 | 120.9167 | 57.2457 | 17.2173 | 125.9067 | 6.8134 | 11.6 | 61.9545 | 163.4653 | 26.8941 | 321.9898 | 283.2335 | 491.6913 | 30.208 | 82.0186 | 5.8324 | 292 | 11.1407 | 162.4727 | 510.8976 | 0.054996
2123 | 1071.4277 | 4.2207 | 107.0928 | 124.5688 | 57.8043 | 16.6867 | 123.7876 | 7.7237 | 8.2033 | 63.1044 | 171.0644 | 27.6408 | 355.4343 | 304.6498 | 519.3279 | 30.27 | 85.798 | 9.429 | 278 | 11.0076 | 165.8377 | 511.0853 | 0.13553
2124 | 1078.27 | 3.9598 | 105.5414 | 125.277 | 57.6667 | 16.8174 | 123.3319 | 8.1241 | 6.8552 | 67.4449 | 172.9341 | 29.573 | 366.6276 | 302.4954 | 519.7424 | 29.7756 | 86.4215 | 14.467 | 283 | 11.2596 | 165.7677 | 507.9608 | 0.15725
2125 | 1090.1889 | 3.8407 | 106.1219 | 123.2757 | 56.2746 | 18.1399 | 121.4101 | 7.1061 | 7.6645 | 73.7084 | 174.0279 | 29.513 | 362.4348 | 298.6941 | 509.2186 | 29.6726 | 88.6709 | 16.6214 | 249 | 10.611 | 165.8011 | 512.8897 | 0.072563
2126 | 1095.1026 | 3.6792 | 106.6126 | 122.5161 | 55.8476 | 18.5456 | 120.5439 | 6.5122 | 7.9025 | 81.4054 | 178.3595 | 29.2127 | 379.9245 | 302.1748 | 505.1535 | 29.8367 | 92.574 | 16.9055 | 221 | 10.3388 | 165.8923 | 520.9266 | 0.080198
2127 | 1085.7842 | 3.7875 | 103.7221 | 125.1975 | 56.2115 | 18.1998 | 125.8989 | 7.4121 | 7.865 | 82.258 | 178.6548 | 29.0931 | 388.962 | 294.9375 | 500.4489 | 29.2309 | 95.6459 | 17.0489 | 203 | 8.9474 | 162.9885 | 522.1679 | 0.070305
2128 | 1061.5033 | 3.2372 | 102.5233 | 116.9354 | 63.7807 | 11.0091 | 119.0902 | 7.5847 | 6.6435 | 73.8234 | 172.9056 | 27.7723 | 393.3237 | 276.9205 | 469.2957 | 24.2755 | 97.2168 | 16.2034 | 173 | 7.2211 | 147.2335 | 492.6631 | 0.11957
2129 | 999.5377 | 2.9481 | 96.383 | 105.085 | 67.1638 | 7.7952 | 105.8516 | 5.7485 | 6.043 | 59.2886 | 161.3672 | 24.6028 | 379.8901 | 238.6145 | 405.902 | 13.6112 | 93.5823 | 15.4489 | 160 | 6.6495 | 137.9791 | 417.1773 | 0.035716
2130 | 954.5356 | 2.4264 | 92.7524 | 96.547 | 68.1131 | 6.8933 | 95.7481 | 4.1527 | 5.814 | 41.5392 | 138.7973 | 19.6147 | 338.8523 | 186.0107 | 347.7696 | 9.3369 | 88.2149 | 14.6281 | 171 | 6.571 | 131.0395 | 343.3573 | 0.012452
2131 | 923.4435 | 2.5288 | 80.833 | 92.1774 | 68.3581 | 6.6606 | 84.8094 | 3.9378 | 5.4715 | 26.1123 | 111.5779 | 10.158 | 295.5732 | 153.2809 | 310.924 | 9.4389 | 84.0429 | 14.0372 | 154 | 6.6067 | 118.1122 | 294.3215 | 0
2132 | 883.3384 | 1.9614 | 54.8343 | 93.9933 | 66.8532 | 8.0902 | 80.8295 | 4.2116 | 5.7142 | 22.1825 | 97.258 | 8.4628 | 254.1165 | 144.3006 | 276.1984 | 9.9502 | 79.4509 | 14.0163 | 142 | 6.6727 | 112.9462 | 268.254 | 0
2133 | 848.8731 | 1.6419 | 41.7768 | 93.8395 | 67.8418 | 7.1511 | 80.1915 | 4.2448 | 6.6424 | 24.5439 | 91.7539 | 9.0457 | 228.0368 | 139.5006 | 240.4395 | 10.5984 | 76.3489 | 14.6403 | 138 | 6.631 | 107.4824 | 267.2763 | 0
2134 | 827.9759 | 1.8066 | 40.0934 | 92.5151 | 68.3751 | 6.6445 | 80.4295 | 4.331 | 6.662 | 23.8968 | 81.2631 | 8.9003 | 197.2713 | 130.9048 | 220.0738 | 10.6893 | 71.046 | 14.3699 | 133 | 6.4771 | 96.714 | 269.9753 | 0
2135 | 812.3209 | 1.8625 | 40.0131 | 90.998 | 67.644 | 7.339 | 80.0185 | 4.256 | 6.117 | 21.9633 | 71.4845 | 8.9019 | 179.2614 | 123.0692 | 223.2234 | 10.8374 | 63.2569 | 13.3644 | 132 | 6.4583 | 70.1547 | 266.8262 | 0
2136 | 792.587 | 1.4992 | 39.9327 | 90.6599 | 68.0711 | 6.9332 | 80.411 | 4.2084 | 6.038 | 21.5073 | 68.6466 | 8.9366 | 168.9109 | 118.5587 | 232.9658 | 10.929 | 59.3943 | 12.7103 | 115 | 6.5506 | 62.7452 | 259.1954 | 0
2137 | 791.0055 | 1.2626 | 39.9925 | 90.5607 | 67.6786 | 7.3061 | 80.0909 | 4.4435 | 6.024 | 21.6562 | 67.9367 | 11.1635 | 165.306 | 115.2342 | 236.8332 | 10.8311 | 58.918 | 12.0815 | 111 | 6.5777 | 63.5514 | 256.1643 | 0
2138 | 783.8775 | 1.2476 | 40.0398 | 90.8718 | 68.0772 | 6.9275 | 79.3546 | 4.7526 | 6.112 | 21.9311 | 67.6396 | 12.6626 | 165.145 | 112.5447 | 228.2089 | 10.8956 | 58.7503 | 11.8806 | 126 | 6.5767 | 61.284 | 257.6223 | 0
2139 | 784.3582 | 1.2658 | 39.8899 | 91.1868 | 68.3603 | 6.6585 | 79.0723 | 4.6462 | 6.013 | 23.3828 | 68.0704 | 12.8403 | 162.4734 | 111.6267 | 215.1483 | 10.8684 | 58.119 | 11.8527 | 102 | 6.5153 | 59.5112 | 258.0969 | 0
2140 | 789.3522 | 1.5695 | 39.8063 | 90.612 | 68.3432 | 6.6747 | 79.3883 | 4.5492 | 6.167 | 29.8117 | 68.3535 | 12.7718 | 164.8543 | 112.018 | 209.8915 | 10.9698 | 58.4208 | 11.8729 | 105 | 6.4208 | 58.4249 | 267.5577 | 0
2141 | 808.7364 | 2.7124 | 48.1484 | 90.8599 | 68.3681 | 6.6511 | 79.2897 | 4.6074 | 6.05 | 38.1655 | 69.2252 | 14.23 | 163.3445 | 116.184 | 213.029 | 10.9698 | 60.4192 | 11.8728 | 102 | 6.4126 | 61.6233 | 298.1105 | 0
2142 | 841.6934 | 4.2858 | 62.9295 | 96.058 | 66.1183 | 8.7884 | 74.2698 | 4.5348 | 6.212 | 54.0639 | 76.1802 | 20.8973 | 170.6487 | 148.5653 | 225.4726 | 13.9831 | 60.6757 | 11.8156 | 155 | 7.0699 | 94.6716 | 351.0313 | 0
2143 | 898.4492 | 5.6667 | 92.2044 | 97.902 | 61.6764 | 13.0082 | 99.1585 | 5.3093 | 6.712 | 76.9557 | 100.5063 | 28.2799 | 200.5938 | 201.62 | 267.8753 | 25.2227 | 61.9582 | 12.8863 | 228 | 10.2215 | 138.2505 | 407.3622 | 0.014907
2144 | 973.2633 | 7.9212 | 103.8063 | 106.9045 | 58.8903 | 15.655 | 119.7359 | 6.4544 | 6.915 | 81.1124 | 135.1014 | 29.7414 | 257.2336 | 243.7657 | 360.9642 | 30.5665 | 67.9614 | 14.0411 | 216 | 12.5616 | 161.8452 | 460.1667 | 0.031981
2145 | 1058.0282 | 9.0731 | 104.0585 | 115.2101 | 58.5149 | 16.0116 | 128.0765 | 7.7322 | 6.853 | 68.7502 | 159.7191 | 27.3038 | 307.2403 | 270.7982 | 463.5731 | 30.4402 | 75.9217 | 14.8984 | 293 | 12.9566 | 162.1554 | 520.1956 | 0.08037
2146 | 1100.4554 | 7.6705 | 105.3337 | 120.3764 | 58.212 | 16.2994 | 133.1082 | 7.7732 | 5.7993 | 60.1437 | 170.4842 | 26.3769 | 350.5202 | 293.3604 | 519.0457 | 30.2673 | 83.1655 | 15.9401 | 333 | 6.4558 | 117.3869 | 554.1916 | 0.10374
2147 | 1114.7467 | 6.0213 | 107.0699 | 123.3402 | 56.8857 | 17.5594 | 133.3343 | 6.2138 | 5.7304 | 58.7109 | 173.9747 | 26.257 | 392.8617 | 313.4139 | 526.7101 | 29.9037 | 86.2638 | 16.6256 | 254 | 6.4558 | 117.3869 | 552.7157 | 0.11187
2148 | 1110.0573 | 5.196 | 106.274 | 126.9454 | 57.1602 | 17.2986 | 130.9118 | 6.534 | 6.1029 | 61.0647 | 175.0147 | 26.1989 | 402.3843 | 318.8873 | 519.843 | 29.8479 | 84.4818 | 16.5143 | 274 | 6.4558 | 117.3869 | 548.1286 | 0.14909
2149 | 1118.9308 | 3.854 | 104.7039 | 128.4231 | 54.4014 | 19.9195 | 125.679 | 7.0639 | 6.7387 | 67.5994 | 176.3519 | 29.2467 | 396.0924 | 320.2663 | 526.3811 | 30.1749 | 83.2578 | 16.9823 | 249 | 6.4558 | 117.3869 | 554.2414 | 0.10415
2150 | 1115.0977 | 3.5049 | 103.5733 | 130.2766 | 54.8044 | 19.5366 | 122.4362 | 6.6954 | 7.3395 | 78.6704 | 176.7395 | 35.3351 | 382.067 | 326.3939 | 529.3626 | 29.5685 | 85.7736 | 17.3456 | 244 | 6.4558 | 117.3869 | 558.2925 | 0.13352
2151 | 1105.9538 | 3.2518 | 102.0815 | 130.3055 | 53.9543 | 20.3442 | 120.2137 | 5.4548 | 8.3543 | 84.9106 | 173.5906 | 37.0426 | 380.2007 | 319.9871 | 510.0051 | 28.8818 | 87.5048 | 17.6765 | 215 | 6.4558 | 117.3869 | 548.9593 | 0.11191
2152 | 1075.384 | 3.2866 | 100.0128 | 124.746 | 57.8042 | 16.6868 | 113.0444 | 4.7167 | 8.3457 | 82.467 | 170.4912 | 32.5944 | 379.5431 | 297.539 | 478.1635 | 23.5956 | 84.8809 | 17.9457 | 180 | 6.4558 | 117.3869 | 526.9321 | 0.076099
2153 | 1023.71 | 3.3664 | 95.5379 | 108.7011 | 65.3065 | 9.5596 | 101.3754 | 4.7901 | 8.3772 | 69.7931 | 164.9376 | 27.9686 | 369.6685 | 248.1261 | 423.0156 | 13.3541 | 79.616 | 17.4536 | 164 | 6.4558 | 117.3869 | 476.5003 | 0.04755
2154 | 956.5143 | 3.2061 | 92.7162 | 96.0367 | 67.3979 | 7.5728 | 91.6513 | 4.4845 | 8.8344 | 50.0268 | 145.4886 | 20.996 | 350.3264 | 179.3266 | 358.689 | 8.9153 | 74.9187 | 16.5374 | 164 | 6.4558 | 117.3869 | 410.1388 | 0.013498
2155 | 899.4251 | 3.8343 | 89.9174 | 93.6308 | 68.0371 | 6.9656 | 82.2074 | 4.1482 | 7.853 | 35.1807 | 118.6132 | 11.1285 | 315.2083 | 137.7581 | 317.4363 | 9.4261 | 69.2868 | 15.4465 | 150 | 6.4558 | 117.3869 | 357.0712 | 0
2156 | 860.7236 | 3.8485 | 77.1623 | 94.2547 | 68.3966 | 6.624 | 77.7803 | 4.2922 | 6.5627 | 29.373 | 104.1384 | 8.3798 | 290.0242 | 128.7502 | 285.7835 | 10.0806 | 62.7114 | 14.5599 | 164 | 6.4558 | 117.3869 | 327.6095 | 0
2157 | 840.008 | 3.5961 | 65.0745 | 93.2946 | 68.3892 | 6.6311 | 77.6125 | 4.344 | 6.8022 | 28.5412 | 100.1466 | 8.9214 | 274.7145 | 123.232 | 256.1948 | 10.3329 | 58.9377 | 13.479 | 136 | 6.4558 | 117.3869 | 321.8478 | 0
2158 | 814.8871 | 3.5993 | 61.7512 | 92.1971 | 68.3625 | 6.6564 | 78.2235 | 4.3087 | 6.6196 | 27.21 | 91.8059 | 8.9749 | 261.3902 | 113.9835 | 231.919 | 10.3208 | 57.8493 | 13.0245 | 134 | 6.4558 | 117.3869 | 318.7159 | 0
2159 | 795.0448 | 2.183 | 61.8091 | 90.7519 | 68.3926 | 6.6279 | 77.8885 | 4.5286 | 6.0415 | 25.5363 | 81.1084 | 10.4492 | 226.5301 | 107.8525 | 221.4419 | 10.3548 | 57.1336 | 12.7905 | 119 | 6.4558 | 117.3869 | 310.4396 | 0
2160 | 797.7061 | 1.4032 | 61.5553 | 92.4493 | 69.0891 | 5.9662 | 77.0515 | 4.6038 | 5.987 | 25.1432 | 76.8461 | 9.8174 | 202.1732 | 104.7548 | 229.645 | 10.3346 | 56.2409 | 12.1899 | 112 | 6.4558 | 117.3869 | 303.3856 | 0
2161 | 787.1335 | 1.2782 | 61.6708 | 93.909 | 68.6278 | 6.4043 | 77.1049 | 4.5813 | 5.9514 | 25.2948 | 76.8004 | 9.0522 | 192.9358 | 99.8111 | 239.6286 | 10.4074 | 55.4379 | 11.7002 | 105 | 6.4558 | 117.3869 | 297.9988 | 0
2162 | 781.3583 | 1.2685 | 61.7053 | 91.0377 | 68.3292 | 6.688 | 76.763 | 4.7694 | 5.894 | 25.451 | 77.5943 | 9.0076 | 185.5084 | 95.364 | 234.9496 | 10.4517 | 54.9979 | 11.6854 | 121 | 6.4558 | 117.3869 | 300.152 | 0
2163 | 785.7749 | 1.3425 | 61.6153 | 89.5431 | 68.4404 | 6.5824 | 76.6052 | 5.1705 | 6.0481 | 27.2167 | 77.9672 | 9.0103 | 181.7316 | 93.7165 | 222.6952 | 10.4208 | 54.9719 | 11.7535 | 105 | 6.4558 | 117.3869 | 304.1136 | 0
2164 | 787.4121 | 1.8108 | 62.6208 | 89.3844 | 68.3102 | 6.7061 | 76.8403 | 5.2354 | 6.0834 | 34.0144 | 77.3292 | 8.9709 | 181.4865 | 91.9196 | 216.3208 | 10.3804 | 55.8566 | 12.0385 | 98 | 6.4558 | 117.3869 | 313.6913 | 0
2165 | 803.1708 | 2.8523 | 63.7049 | 90.4806 | 68.3732 | 6.6462 | 77.1713 | 4.9912 | 6.1661 | 42.6388 | 76.8918 | 10.5912 | 179.3878 | 98.3972 | 218.2123 | 10.4098 | 57.7208 | 11.8138 | 105 | 6.4558 | 117.3869 | 341.6877 | 0
2166 | 827.2246 | 4.5458 | 74.188 | 92.3266 | 66.1572 | 8.7515 | 84.2484 | 4.7172 | 6.3479 | 52.9721 | 82.6347 | 16.8304 | 197.1744 | 131.7638 | 229.8736 | 14.0507 | 57.7793 | 11.4685 | 144 | 6.4558 | 117.3869 | 383.1995 | 0
2167 | 876.7331 | 4.043 | 93.3076 | 95.3436 | 61.7061 | 12.98 | 102.0588 | 5.3123 | 6.2744 | 68.1393 | 106.5841 | 28.7357 | 222.2065 | 186.4937 | 268.4389 | 24.4474 | 59.5472 | 11.7276 | 219 | 6.4558 | 117.3869 | 437.5997 | 0.018514
2168 | 985.5076 | 3.7925 | 102.1225 | 112.6551 | 58.3237 | 16.1933 | 116.0835 | 5.9478 | 6.1308 | 74.8336 | 143.3601 | 28.735 | 290.1708 | 243.5626 | 356.9591 | 29.8508 | 68.7672 | 13.479 | 224 | 6.4558 | 117.3869 | 518.985 | 0.074059
2169 | 1040.0869 | 4.1099 | 102.9739 | 120.791 | 59.4141 | 15.1574 | 119.5319 | 6.0563 | 9.5352 | 70.7653 | 167.9016 | 26.2162 | 357.8321 | 279.5683 | 440.889 | 29.8335 | 78.0775 | 14.3385 | 263 | 6.4558 | 117.3869 | 584.9046 | 0.099616
2170 | 1070.4238 | 4.1208 | 105.6607 | 124.6999 | 58.5082 | 16.018 | 121.9275 | 6.0673 | 11.3903 | 70.3438 | 174.2017 | 28.0008 | 376.4887 | 295.1733 | 485.5377 | 29.6751 | 82.6644 | 16.6816 | 269 | 6.4558 | 117.3869 | 602.7792 | 0.17587
2171 | 1108.9365 | 4.045 | 107.6753 | 127.8409 | 56.0893 | 18.3159 | 124.5472 | 6.2065 | 12.4001 | 73.1643 | 174.1998 | 27.0737 | 386.8796 | 308.0723 | 517.1192 | 29.3679 | 85.6115 | 17.7703 | 270 | 6.4558 | 117.3869 | 598.7079 | 0.22209
2172 | 1114.7873 | 3.8345 | 105.512 | 128.4322 | 57.2807 | 17.1841 | 125.1747 | 6.077 | 13.3869 | 74.1562 | 173.407 | 27.3477 | 394.991 | 310.177 | 523.2173 | 29.3074 | 89.3914 | 17.5374 | 273 | 6.4558 | 117.3869 | 588.9844 | 0.17075
2173 | 1101.9651 | 3.6972 | 105.8559 | 131.9524 | 59.7253 | 14.8618 | 123.7708 | 5.5611 | 10.2226 | 80.5363 | 175.7284 | 31.9632 | 395.6103 | 310.5633 | 518.4762 | 29.4054 | 94.5037 | 17.9038 | 270 | 6.4558 | 117.3869 | 583.0316 | 0.097241
2174 | 1114.8427 | 3.6148 | 106.3448 | 133.7599 | 59.7336 | 14.8539 | 121.5249 | 6.2048 | 8.6487 | 89.2011 | 179.5709 | 33.4965 | 399.211 | 317.1478 | 525.309 | 29.5362 | 99.1547 | 18.0934 | 273 | 6.4558 | 117.3869 | 569.3567 | 0.13212
2175 | 1033.3758 | 3.7109 | 89.4624 | 116.6508 | 63.2936 | 11.4719 | 106.916 | 6.328 | 9.0557 | 80.5395 | 164.3155 | 24.8971 | 390.2714 | 276.6306 | 471.8169 | 22.6705 | 95.1444 | 15.8269 | 246 | 6.4558 | 117.3869 | 487.0271 | 0.18912
2176 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.8811 | 61.8942 | 133.7666 | 18.8817 | 389.4759 | 209.3265 | 373.9404 | 16.2398 | 81.5479 | 14.0082 | 213 | 6.4558 | 117.3869 | 378.2992 | 0.20372
2177 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 180 | 6.4558 | 117.3869 | 339.4893 | 0.17516
2178 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 177 | 6.4558 | 117.3869 | 339.4893 | 0.11329
2179 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 165 | 6.4558 | 117.3869 | 339.4893 | 0
2180 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 152 | 6.4558 | 117.3869 | 339.4893 | 0
2181 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 153 | 6.4558 | 117.3869 | 339.4893 | 0
2182 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 143 | 6.4558 | 117.3869 | 339.4893 | 0
2183 | 941.6597 | 3.8451 | 77.6393 | 104.7628 | 65.2911 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 129 | 6.4558 | 117.3869 | 339.4893 | 0
2184 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 265.5518 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 115 | 6.4558 | 117.3869 | 339.4893 | 0
2185 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 110 | 6.4558 | 117.3869 | 339.4893 | 0
2186 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 124 | 6.4558 | 117.3869 | 339.4893 | 0
2187 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 104 | 6.4558 | 117.3869 | 339.4893 | 0
2188 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 102 | 6.4558 | 117.3869 | 339.4893 | 0
2189 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 105 | 6.4558 | 117.3869 | 339.4893 | 0
2190 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 139 | 6.4558 | 117.3869 | 339.4893 | 0
2191 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 208 | 6.4558 | 117.3869 | 339.4893 | 0.17686
2192 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 226 | 6.4558 | 117.3869 | 339.4893 | 0.26374
2193 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 268 | 6.4558 | 117.3869 | 339.4893 | 0.31527
2194 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 282 | 6.4558 | 117.3869 | 339.4893 | 0.30099
2195 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 286 | 6.4558 | 117.3869 | 339.4893 | 0.28073
2196 | 940.98 | 3.8451 | 77.6393 | 104.7628 | 75.081 | 9.5743 | 95.4756 | 5.6313 | 8.9278 | 54.3572 | 119.527 | 18.8817 | 264.6569 | 183.9349 | 334.0142 | 16.2398 | 74.1162 | 14.0082 | 289 | 6.4558 | 117.3869 | 339.4893 | 0.28891
2197 | 1009.9117 | 3.9588 | 95.5363 | 116.2427 | 71.4063 | 13.0653 | 108.1803 | 5.8176 | 8.9278 | 61.2139 | 132.8159 | 26.6524 | 211.2339 | 219.4107 | 375.327 | 22.6561 | 76.9071 | 15.6988 | 260 | 6.4558 | 117.3869 | 404.6928 | 0.30742
2198 | 1087.5558 | 3.7499 | 108.5943 | 125.62 | 69.7966 | 14.5945 | 120.2554 | 6.0624 | 11.5957 | 77.2741 | 161.0157 | 35.2768 | 306.8035 | 275.2467 | 454.329 | 29.3236 | 83.0764 | 17.4469 | 219 | 6.4558 | 117.3869 | 509.3515 | 0.33637
2199 | 1073.3211 | 3.4104 | 103.0084 | 126.7425 | 68.8803 | 15.4649 | 118.5451 | 6.1124 | 14.06 | 87.3262 | 175.8735 | 35.0516 | 400.6965 | 289.7092 | 483.8739 | 27.776 | 85.8484 | 17.3765 | 222 | 6.4558 | 117.3869 | 537.1212 | 0.30062
2200 | 1045.3827 | 3.1968 | 98.5679 | 126.2745 | 74.4603 | 10.1639 | 112.3049 | 5.7555 | 13.6864 | 83.035 | 174.1888 | 32.0609 | 391.9775 | 269.25 | 443.3307 | 18.2111 | 82.6139 | 16.6575 | 196 | 6.4558 | 117.3869 | 480.7373 | 0.21172
2201 | 1007.9959 | 2.6511 | 84.8353 | 117.3174 | 78.766 | 6.0735 | 102.7517 | 5.1302 | 11.9076 | 66.707 | 166.0735 | 30.5688 | 375.3512 | 224.6572 | 371.6804 | 8.2869 | 77.4801 | 15.6258 | 159 | 6.4558 | 117.3869 | 380.4893 | 0.1432
2202 | 950.3178 | 1.8943 | 60.1918 | 103.1022 | 79.1999 | 5.6613 | 93.3094 | 4.6882 | 10.7447 | 44.4992 | 144.437 | 24.61 | 350.2458 | 172.6787 | 315.8145 | 7.3983 | 77.4786 | 14.7488 | 161 | 6.4558 | 117.3869 | 291.5286 | 0.079495
2203 | 900.9551 | 1.6784 | 45.8327 | 94.3303 | 79.1726 | 5.6873 | 83.8997 | 4.555 | 8.9243 | 30.4702 | 114.7305 | 13.8192 | 302.2102 | 145.7902 | 298.1921 | 7.7837 | 84.1868 | 14.3405 | 145 | 6.4558 | 117.3869 | 237.9583 | 0
2204 | 867.5491 | 1.952 | 41.3441 | 95.7365 | 79.1015 | 5.7548 | 80.0823 | 4.8722 | 6.8203 | 29.731 | 94.2147 | 9.2563 | 263.703 | 136.2012 | 282.5296 | 8.3656 | 88.9206 | 14.2057 | 144 | 6.4558 | 117.3869 | 213.0244 | 0
2205 | 849.8599 | 1.929 | 39.2632 | 97.7386 | 79.1519 | 5.707 | 80.2502 | 4.9938 | 6.7885 | 33.495 | 84.8807 | 10.2213 | 225.8775 | 126.1476 | 253.0029 | 8.5508 | 89.5358 | 13.8007 | 134 | 6.4558 | 117.3869 | 211.3334 | 0
2206 | 827.9607 | 1.7122 | 39.3341 | 94.4241 | 79.1874 | 5.6732 | 79.5993 | 4.7999 | 6.979 | 34.0778 | 80.0278 | 10.0971 | 197.5862 | 113.6098 | 233.2293 | 8.6519 | 89.296 | 12.8208 | 119 | 6.4558 | 117.3869 | 215.2143 | 0
2207 | 808.4024 | 1.529 | 39.3856 | 92.7666 | 78.5123 | 6.3145 | 79.174 | 4.8884 | 6.4234 | 32.7701 | 78.4259 | 10.0834 | 189.7377 | 103.7277 | 225.7983 | 8.6182 | 82.6188 | 12.0307 | 109 | 6.4558 | 117.3869 | 223.8407 | 0
2208 | 805.152 | 1.8035 | 39.5333 | 92.6353 | 83.6591 | 6.0739 | 78.8349 | 4.8613 | 6.1296 | 32.593 | 77.8193 | 10.0723 | 174.3546 | 102.0898 | 225.3797 | 8.7207 | 67.6224 | 11.9693 | 118 | 6.4558 | 117.3869 | 233.3332 | 0
2209 | 798.7485 | 1.9015 | 39.4837 | 91.5967 | 83.4183 | 6.3027 | 78.8661 | 4.715 | 6.0622 | 32.9988 | 76.3645 | 9.8255 | 160.1978 | 101.83 | 230.456 | 8.7907 | 56.9628 | 12.0869 | 119 | 6.4558 | 117.3869 | 227.4485 | 0
2210 | 790.415 | 1.5945 | 39.375 | 91.5734 | 83.7578 | 5.9802 | 78.2548 | 4.7464 | 6.0205 | 33.136 | 75.4134 | 9.6942 | 155.6791 | 96.0864 | 230.9718 | 8.7405 | 54.8517 | 12.2576 | 137 | 6.4558 | 117.3869 | 216.3169 | 0
2211 | 794.4725 | 1.4927 | 39.4054 | 91.2973 | 84.029 | 5.7225 | 77.8872 | 4.75 | 6.1175 | 33.7606 | 76.0027 | 9.8423 | 155.4538 | 90.6786 | 223.316 | 8.8295 | 54.5501 | 12.1776 | 112 | 6.4558 | 117.3869 | 213.3182 | 0
2212 | 794.5536 | 1.8977 | 39.4815 | 90.7259 | 84.0351 | 5.7168 | 78.0401 | 4.9587 | 6.2002 | 36.8649 | 77.1073 | 10.0012 | 153.4713 | 88.5173 | 219.073 | 8.7657 | 55.367 | 12.6685 | 110 | 6.4558 | 117.3869 | 213.9698 | 0
2213 | 787.4827 | 2.8478 | 42.7897 | 90.8659 | 83.5036 | 6.2216 | 78.2462 | 4.9086 | 6.2539 | 41.804 | 77.8747 | 9.8787 | 153.1088 | 87.8948 | 217.8521 | 8.7244 | 57.5447 | 13.0806 | 109 | 6.4558 | 117.3869 | 212.2012 | 0
2214 | 796.4148 | 3.2884 | 52.8965 | 89.2876 | 83.6414 | 6.0907 | 79.2109 | 4.5242 | 6.1375 | 45.2114 | 77.1786 | 8.8139 | 155.0512 | 87.0352 | 211.1256 | 8.7001 | 57.5519 | 12.9583 | 104 | 6.4558 | 117.3869 | 211.113 | 0
2215 | 808.0933 | 2.3618 | 64.7573 | 88.1477 | 83.9898 | 5.7598 | 90.4447 | 4.2577 | 7.4595 | 44.4705 | 78.329 | 9.6083 | 161.6073 | 87.8053 | 203.088 | 10.6584 | 54.9258 | 13.3842 | 109 | 6.4558 | 117.3869 | 218.1536 | 0.032981
2216 | 814.2581 | 1.4895 | 76.1982 | 88.7345 | 83.4114 | 6.3092 | 107.8924 | 4.0217 | 10.731 | 45.4585 | 95.6357 | 12.6707 | 169.7377 | 95.5792 | 204.7006 | 16.288 | 53.5056 | 13.9667 | 123 | 6.4558 | 117.3869 | 226.2378 | 0.059441
2217 | 833.1764 | 1.4924 | 82.6163 | 89.2825 | 83.6853 | 6.049 | 120.7657 | 3.7242 | 13.3146 | 55.5469 | 126.0844 | 12.1793 | 172.9692 | 109.7405 | 217.3864 | 14.4733 | 54.0926 | 14.3601 | 135 | 6.4558 | 117.3869 | 227.9836 | 0.064807
2218 | 863.284 | 1.4482 | 81.6421 | 89.7066 | 82.7713 | 6.9173 | 128.013 | 2.9984 | 13.0227 | 65.9687 | 145.9181 | 10.0482 | 196.2964 | 122.613 | 239.0015 | 8.8583 | 55.2046 | 14.8413 | 144 | 6.4558 | 117.3869 | 231.4409 | 0.080273
2219 | 893.84 | 1.2646 | 80.7647 | 90.7556 | 82.738 | 6.949 | 115.8771 | 3.1485 | 11.3653 | 69.7099 | 145.72 | 9.5702 | 217.7866 | 135.0923 | 262.5613 | 12.8574 | 56.8521 | 15.6361 | 143 | 6.4558 | 117.3869 | 235.1852 | 0.1162
2220 | 900.7226 | 1.4617 | 81.2786 | 91.8825 | 83.0793 | 6.6248 | 110.3032 | 5.0684 | 10.6461 | 68.7454 | 127.905 | 10.3234 | 229.5505 | 149.5741 | 271.4023 | 15.2102 | 59.2672 | 16.1451 | 164 | 6.4558 | 117.3869 | 236.8804 | 0.13232
2221 | 885.4345 | 1.7478 | 72.7023 | 92.1225 | 84.287 | 5.4774 | 120.2938 | 5.5624 | 11.7 | 64.0215 | 108.3943 | 11.3549 | 225.9202 | 162.8109 | 267.911 | 16.8045 | 60.4378 | 16.1525 | 173 | 6.4558 | 117.3869 | 241.4463 | 0.16815
2222 | 880.5962 | 1.5395 | 56.9687 | 91.9619 | 84.4097 | 5.3609 | 128.3705 | 3.9717 | 12.0412 | 58.9914 | 102.1818 | 11.7794 | 221.7132 | 168.1668 | 267.7412 | 20.1448 | 58.7208 | 16.3844 | 230 | 6.4558 | 117.3869 | 244.2967 | 0.080658
2223 | 870.1085 | 1.5791 | 48.9789 | 92.7445 | 84.0622 | 5.691 | 126.2515 | 3.2079 | 11.9679 | 48.3431 | 104.3417 | 11.3422 | 223.5913 | 158.4547 | 271.4909 | 15.9164 | 57.3118 | 16.7554 | 228 | 6.4558 | 117.3869 | 246.2224 | 0.073599
2224 | 862.1895 | 1.593 | 48.1984 | 95.199 | 84.6516 | 5.131 | 118.4249 | 2.5925 | 12.831 | 31.334 | 105.1293 | 10.4528 | 227.5116 | 144.4518 | 274.2129 | 10.3081 | 58.4593 | 16.4299 | 220 | 6.4558 | 117.3869 | 251.0866 | 0.065424
2225 | 864.16 | 1.4043 | 48.1423 | 94.9013 | 84.4813 | 5.2928 | 116.2883 | 2.3367 | 13.0392 | 21.7638 | 99.0815 | 9.0952 | 225.9138 | 137.0641 | 268.4663 | 7.8344 | 58.5427 | 15.7557 | 248 | 6.4558 | 117.3869 | 253.6979 | 0.034405
2226 | 843.4431 | 1.5877 | 48.552 | 93.0933 | 84.1 | 5.6551 | 101.7891 | 3.1892 | 12.9373 | 20.5983 | 90.3121 | 6.4394 | 225.6451 | 134.4038 | 250.9966 | 7.5089 | 56.1721 | 15.3951 | 219 | 6.4558 | 117.3869 | 247.4411 | 0.015754
2227 | 821.5723 | 2.5335 | 48.5109 | 93.286 | 84.6156 | 5.1653 | 90.6851 | 3.6284 | 11.5439 | 20.4401 | 83.1067 | 6.9379 | 232.9205 | 133.4447 | 236.7105 | 7.481 | 54.2788 | 15.1896 | 263 | 6.4558 | 117.3869 | 232.9424 | 0
2228 | 812.8374 | 3.8167 | 48.4992 | 94.4324 | 84.4264 | 5.345 | 93.1071 | 3.9371 | 8.1473 | 21.2637 | 83.8099 | 14.475 | 194.9764 | 126.7269 | 239.1057 | 7.7098 | 54.2887 | 14.5903 | 223 | 6.4558 | 117.3869 | 224.4407 | 0
2229 | 801.8685 | 3.8478 | 48.4099 | 93.628 | 83.481 | 6.2431 | 89.7566 | 4.1426 | 6.5058 | 22.8241 | 92.7047 | 19.015 | 177.4955 | 114.5865 | 245.4009 | 7.9499 | 55.3176 | 13.4042 | 216 | 6.4558 | 117.3869 | 224.5639 | 0
2230 | 790.5218 | 3.0315 | 48.2642 | 92.7147 | 83.0283 | 6.6732 | 80.7423 | 4.2628 | 6.5303 | 23.0375 | 94.5846 | 13.2351 | 183.4799 | 106.9086 | 243.1244 | 7.9092 | 55.9467 | 13.615 | 190 | 6.4558 | 117.3869 | 220.7811 | 0
2231 | 776.5731 | 2.1372 | 48.6267 | 92.487 | 83.0065 | 6.6939 | 75.9086 | 4.1659 | 6.3548 | 22.3043 | 86.1568 | 7.4982 | 187.9768 | 101.4515 | 234.9868 | 7.9538 | 55.7153 | 13.7746 | 194 | 6.4558 | 117.3869 | 214.4802 | 0
2232 | 788.0583 | 4.5288 | 48.5449 | 92.0411 | 83.681 | 6.0531 | 76.2177 | 4.0043 | 7.7959 | 21.8283 | 78.3095 | 7.1602 | 178.4469 | 93.4883 | 228.4261 | 7.9142 | 54.9275 | 12.6628 | 170 | 6.4558 | 117.3869 | 211.2751 | 0
2233 | 797.7219 | 4.6627 | 48.1401 | 91.6129 | 82.1052 | 7.5501 | 76.4403 | 3.8057 | 7.5085 | 21.5433 | 75.4689 | 7.0711 | 168.4279 | 88.2113 | 225.8639 | 7.9569 | 54.1792 | 12.2119 | 144 | 6.4558 | 117.3869 | 211.6884 | 0
2234 | 784.153 | 1.7973 | 48.2828 | 91.1913 | 79.1932 | 10.3166 | 75.7799 | 4.0708 | 6.086 | 21.3735 | 74.8624 | 7.0354 | 168.1195 | 86.7352 | 219.5113 | 7.9373 | 53.9721 | 12.379 | 155 | 6.4558 | 117.3869 | 219.3491 | 0
2235 | 771.1697 | 1.4512 | 48.2819 | 90.9968 | 79.335 | 10.1818 | 75.6237 | 4.1641 | 8.26 | 21.3646 | 75.1423 | 7.0725 | 165.56 | 86.1353 | 210.6793 | 7.8891 | 54.0717 | 12.4014 | 129 | 6.4558 | 117.3869 | 228.8191 | 0
2236 | 754.4265 | 1.7804 | 48.0406 | 90.8685 | 81.3073 | 8.3081 | 76.0792 | 3.961 | 7.9793 | 21.384 | 75.746 | 7.0995 | 166.4003 | 86.002 | 203.7644 | 7.953 | 55.0254 | 12.3533 | 123 | 6.4558 | 117.3869 | 230.2396 | 0
2237 | 751.3048 | 2.6741 | 48.2131 | 90.8096 | 83.296 | 6.4189 | 75.92 | 4.0544 | 8.0587 | 21.9348 | 76.0699 | 7.0937 | 164.979 | 86.0447 | 202.0352 | 7.9063 | 56.8208 | 12.5991 | 108 | 6.4558 | 117.3869 | 220.994 | 0
2238 | 765.9063 | 2.652 | 48.513 | 89.0136 | 84.0549 | 5.6979 | 75.1478 | 3.9883 | 9.4487 | 22.2834 | 74.7528 | 5.8082 | 161.0772 | 84.6326 | 201.1495 | 8.1472 | 56.5468 | 12.3552 | 109 | 6.4558 | 117.3869 | 204.9017 | 0
2239 | 782.8646 | 1.6725 | 48.49 | 88.6967 | 83.4662 | 6.2572 | 74.6917 | 4.1522 | 7.5873 | 21.4329 | 72.2387 | 4.4591 | 163.7602 | 84.2739 | 198.2373 | 8.2549 | 54.4124 | 12.1848 | 112 | 6.4558 | 117.3869 | 192.1793 | 0.047476
2240 | 790.0635 | 1.279 | 48.2874 | 91.4166 | 83.7055 | 6.0299 | 75.8725 | 4.2629 | 7.8893 | 26.7731 | 72.56 | 5.5798 | 171.1925 | 91.7266 | 201.4433 | 8.3651 | 53.5204 | 12.7613 | 111 | 6.4558 | 117.3869 | 191.6338 | 0.068687
2241 | 797.3669 | 1.5463 | 47.9355 | 92.1491 | 82.7772 | 6.9117 | 76.7274 | 3.7765 | 7.654 | 42.6857 | 76.7937 | 8.3861 | 176.731 | 111.2525 | 212.7147 | 8.8156 | 53.5926 | 13.2663 | 124 | 6.4558 | 117.3869 | 201.0838 | 0.07989
2242 | 826.862 | 1.7437 | 47.7447 | 91.1508 | 82.157 | 7.5009 | 78.8459 | 3.4995 | 7.9353 | 56.9619 | 84.8378 | 9.7009 | 182.1469 | 136.1735 | 228.4684 | 8.926 | 53.8495 | 13.6239 | 129 | 6.4558 | 117.3869 | 213.4855 | 0.10037
2243 | 852.6053 | 1.9315 | 47.7474 | 91.3738 | 83.3303 | 6.3863 | 83.9449 | 2.8356 | 8.6563 | 62.7392 | 93.3444 | 10.3649 | 188.9428 | 151.6815 | 245.2645 | 8.9941 | 54.4751 | 14.4755 | 137 | 6.4558 | 117.3869 | 228.3534 | 0.15924
2244 | 847.6987 | 1.7154 | 47.6646 | 92.5116 | 84.0457 | 5.7067 | 98.5406 | 3.0698 | 10.1527 | 60.3628 | 95.8456 | 10.4828 | 211.3018 | 158.7147 | 255.4901 | 8.9155 | 55.3095 | 15.4195 | 138 | 6.4558 | 117.3869 | 241.7289 | 0.11727
2245 | 836.7061 | 1.409 | 47.7075 | 95.5571 | 84.0266 | 5.7249 | 110.8503 | 4.7654 | 10.99 | 52.0908 | 94.6787 | 9.4552 | 231.9221 | 164.4985 | 260.7492 | 8.766 | 55.4656 | 15.9014 | 137 | 6.4558 | 117.3869 | 243.6481 | 0.10599
2246 | 848.7794 | 1.5295 | 47.7465 | 95.0073 | 84.1004 | 5.6547 | 100.5477 | 4.4303 | 10.0321 | 47.8135 | 94.5083 | 11.1166 | 231.5381 | 166.3676 | 274.3791 | 9.0185 | 54.3453 | 15.9034 | 143 | 6.4558 | 117.3869 | 235.8835 | 0.071155
2247 | 854.1953 | 1.5937 | 47.6632 | 92.6845 | 84.0661 | 5.6873 | 86.7604 | 4.1068 | 13.3162 | 43.6167 | 94.2375 | 11.8348 | 224.0086 | 168.2788 | 290.5811 | 9.3969 | 53.5509 | 15.8326 | 150 | 6.4558 | 117.3869 | 226.5159 | 0.045964
2248 | 844.7041 | 1.5577 | 47.6683 | 93.8874 | 84.6328 | 5.1489 | 80.5859 | 4.5117 | 15.2217 | 32.8816 | 91.8132 | 9.4386 | 225.869 | 166.8663 | 296.7764 | 9.1635 | 53.9251 | 16.1578 | 143 | 6.4558 | 117.3869 | 217.7734 | 0.035803
2249 | 841.0304 | 1.7579 | 47.8281 | 94.2844 | 84.4299 | 5.3417 | 84.9782 | 3.9716 | 13.87 | 24.2746 | 87.4367 | 7.8353 | 222.326 | 153.0561 | 300.3333 | 8.0717 | 54.3861 | 16.397 | 129 | 6.4558 | 117.3869 | 213.8286 | 0.027703
2250 | 834.0718 | 2.7165 | 47.6491 | 92.3371 | 84.0663 | 5.6871 | 91.0276 | 4.048 | 13.435 | 21.7803 | 83.9286 | 6.8304 | 215.7638 | 134.6029 | 301.2936 | 7.3304 | 54.3213 | 16.0694 | 125 | 6.4558 | 117.3869 | 215.6428 | 0.0075567
2251 | 819.6102 | 3.4974 | 47.3718 | 91.5109 | 84.0798 | 5.6743 | 89.7311 | 4.1893 | 12.055 | 21.5492 | 81.0978 | 6.1605 | 208.7839 | 120.3296 | 290.9476 | 7.3347 | 53.6326 | 15.3627 | 130 | 6.4558 | 117.3869 | 222.6027 | 0
2252 | 803.5889 | 3.431 | 47.382 | 92.1399 | 84.0242 | 5.7271 | 91.1949 | 3.6186 | 8.91 | 20.7843 | 75.0886 | 5.4113 | 205.4155 | 111.9342 | 272.3401 | 7.423 | 52.7132 | 14.3379 | 111 | 6.4558 | 117.3869 | 234.6092 | 0
2253 | 790.9659 | 3.5234 | 47.4651 | 91.6351 | 84.0592 | 5.6938 | 85.1595 | 3.0822 | 7.1891 | 18.8688 | 67.8569 | 4.6622 | 204.12 | 106.7304 | 243.2097 | 7.3409 | 52.4381 | 12.8709 | 111 | 6.4558 | 117.3869 | 239.9393 | 0
2254 | 785.5058 | 2.9973 | 47.6131 | 89.7356 | 83.4087 | 6.3118 | 75.8873 | 3.335 | 6.2809 | 18.527 | 64.1669 | 5.8586 | 199.0539 | 102.6331 | 209.7402 | 7.3324 | 52.5803 | 11.9485 | 107 | 6.4558 | 117.3869 | 234.501 | 0
2255 | 776.5479 | 1.7363 | 47.7723 | 90.847 | 83.0376 | 6.6644 | 75.2251 | 3.7679 | 5.49 | 21.0317 | 62.3795 | 7.4221 | 181.247 | 98.7745 | 195.7288 | 7.3802 | 52.5173 | 11.7593 | 100 | 6.4558 | 117.3869 | 231.101 | 0
2256 | 768.5618 | 1.3195 | 47.8218 | 92.69 | 83.066 | 6.6374 | 75.7432 | 4.0534 | 5.5128 | 23.1508 | 60.7859 | 7.6977 | 157.6146 | 91.9197 | 200.251 | 7.3996 | 52.1827 | 11.4224 | 101 | 6.4558 | 117.3869 | 233.0633 | 0
2257 | 754.7344 | 1.2436 | 47.7714 | 92.5466 | 83.647 | 6.0855 | 75.6893 | 4.0715 | 5.5442 | 23.6337 | 60.2057 | 7.7206 | 154.0758 | 86.8918 | 206.9665 | 7.4199 | 51.741 | 11.2021 | 96 | 6.4558 | 117.3869 | 233.5644 | 0
2258 | 740.5884 | 1.1345 | 47.6074 | 92.5462 | 84.042 | 5.7101 | 74.7471 | 3.9186 | 5.5148 | 23.6116 | 60.2846 | 8.0154 | 153.4966 | 88.5012 | 204.9168 | 7.3251 | 51.4381 | 11.1955 | 115 | 6.4558 | 117.3869 | 229.7925 | 0
2259 | 745.7186 | 1.2575 | 47.9421 | 92.4602 | 84.085 | 5.6694 | 74.5166 | 4.065 | 5.5152 | 25.293 | 60.8318 | 8.2392 | 150.904 | 91.1947 | 198.5014 | 7.4012 | 51.1946 | 11.1993 | 97 | 6.4558 | 117.3869 | 229.0639 | 0
2260 | 754.8422 | 1.8191 | 48.8703 | 93.7723 | 84.1092 | 5.6464 | 75.1385 | 4.1045 | 5.5088 | 31.4999 | 61.3982 | 8.1205 | 151.8008 | 89.2614 | 195.3683 | 7.4228 | 51.8781 | 11.1969 | 96 | 6.4558 | 117.3869 | 246.3522 | 0
2261 | 777.3937 | 3.0812 | 48.957 | 93.9697 | 83.4843 | 6.24 | 76.039 | 3.934 | 5.4885 | 39.457 | 62.2854 | 9.7467 | 152.6602 | 92.3396 | 197.7334 | 7.37 | 53.6558 | 12.0857 | 102 | 6.4558 | 117.3869 | 273.422 | 0
2262 | 815.6336 | 4.5117 | 61.1172 | 97.0779 | 80.7104 | 8.8752 | 86.6947 | 3.7334 | 5.7356 | 52.8635 | 74.5251 | 18.213 | 164.8278 | 118.0641 | 217.8836 | 11.8162 | 54.3289 | 12.6447 | 149 | 6.4558 | 117.3869 | 310.5615 | 0
2263 | 877.8645 | 6.6965 | 88.8994 | 105.8153 | 76.7461 | 12.6413 | 116.3699 | 4.1671 | 8.4493 | 82.2 | 106.3337 | 29.1165 | 211.9538 | 166.1962 | 277.503 | 23.6722 | 56.7135 | 12.5129 | 260 | 6.4558 | 117.3869 | 373.5458 | 0.051201
2264 | 984.3962 | 11.8131 | 107.1625 | 118.5338 | 73.8421 | 15.4001 | 147.5437 | 5.2524 | 14.3354 | 109.475 | 141.9258 | 33.0672 | 278.9412 | 218.0677 | 372.5482 | 33.4545 | 64.6285 | 13.5837 | 267 | 6.4558 | 117.3869 | 441.9912 | 0.18727
2265 | 1091.9306 | 10.9373 | 110.9066 | 129.9577 | 73.4839 | 15.7403 | 159.6937 | 6.0837 | 17.9282 | 114.2535 | 166.8804 | 33.0648 | 332.9044 | 256.9942 | 461.9946 | 36.0871 | 74.5099 | 15.5455 | 308 | 6.4558 | 117.3869 | 500.8833 | 0.19884
2266 | 1147.4176 | 4.6765 | 111.5183 | 133.1263 | 74.0869 | 15.1676 | 162.0277 | 6.1546 | 17.8872 | 111.8628 | 179.6858 | 33.3905 | 364.8281 | 280.918 | 513.6385 | 36.9779 | 83.3257 | 16.6554 | 316 | 6.4558 | 117.3869 | 545.4306 | 0.17753
2267 | 1166.4625 | 5.7926 | 111.5573 | 135.2747 | 75.7981 | 13.5419 | 168.9813 | 6.3712 | 17.8581 | 111.9373 | 183.6159 | 32.8731 | 397.0412 | 296.4165 | 530.3835 | 37.1095 | 88.749 | 16.6096 | 303 | 6.4558 | 117.3869 | 562.1297 | 0.19144
2268 | 1178.985 | 9.1977 | 110.7873 | 140.2683 | 76.5105 | 12.8652 | 163.7329 | 6.5259 | 17.953 | 104.8836 | 182.0889 | 31.9141 | 414.6156 | 306.4618 | 536.92 | 38.0154 | 88.9822 | 16.648 | 348 | 6.4558 | 117.3869 | 560.1257 | 0.20524
2269 | 1185.6149 | 8.1376 | 112.9364 | 148.2949 | 73.6312 | 15.6005 | 165.0869 | 6.0603 | 16.5139 | 93.5434 | 180.9205 | 31.5839 | 421.1677 | 310.804 | 540.6411 | 40.4807 | 87.6741 | 16.7097 | 343 | 6.4558 | 117.3869 | 550.8968 | 0.1946
2270 | 1180.9322 | 7.791 | 115.6696 | 148.082 | 72.0028 | 17.1474 | 166.8661 | 5.4856 | 14.87 | 88.7469 | 181.4719 | 31.5339 | 423.1827 | 315.6623 | 530.896 | 40.1513 | 87.8495 | 17.0478 | 290 | 6.4558 | 117.3869 | 541.7063 | 0.13088
2271 | 1160.9596 | 10.8959 | 111.648 | 139.438 | 71.5342 | 17.5926 | 151.2117 | 4.8575 | 15.4392 | 86.7945 | 180.1151 | 31.7438 | 430.0862 | 315.7726 | 510.8335 | 38.9754 | 87.4413 | 17.1257 | 251 | 6.4558 | 117.3869 | 529.8816 | 0.16524
2272 | 1131.5893 | 8.3791 | 106.7747 | 130.9379 | 74.6303 | 14.6513 | 152.8593 | 5.0868 | 16.6958 | 78.5754 | 176.8155 | 31.1571 | 421.0114 | 295.1408 | 477.4546 | 32.3636 | 84.9825 | 16.9956 | 234 | 6.4558 | 117.3869 | 490.4113 | 0.10028
2273 | 1056.9676 | 4.295 | 99.4787 | 116.0991 | 80.578 | 9.0009 | 140.6651 | 4.0604 | 18.05 | 66.8324 | 165.761 | 30.1428 | 381.4654 | 245.9793 | 420.7024 | 17.6109 | 80.1671 | 16.7592 | 217 | 6.4558 | 117.3869 | 426.871 | 0.056519
2274 | 986.8322 | 3.1383 | 93.624 | 102.7152 | 83.0748 | 6.6291 | 124.9226 | 2.8217 | 17.3423 | 52.7921 | 142.7852 | 24.4525 | 335.5443 | 184.547 | 357.7329 | 9.9387 | 74.5967 | 16.0209 | 184 | 6.4558 | 117.3869 | 363.7168 | 0.0098155
2275 | 944.6558 | 3.314 | 81.7702 | 98.1946 | 82.4889 | 7.1856 | 115.1238 | 2.9535 | 13.954 | 37.4151 | 116.2454 | 13.8085 | 292.5363 | 142.7229 | 317.6826 | 9.0547 | 69.6776 | 15.1001 | 164 | 6.4558 | 117.3869 | 312.46 | 0.00044164
2276 | 915.7055 | 3.2231 | 56.9227 | 96.7901 | 82.6734 | 7.0104 | 100.801 | 2.7597 | 10.5137 | 30.3037 | 101.383 | 9.3121 | 258.4208 | 123.6906 | 299.4782 | 8.6885 | 64.1266 | 14.2338 | 149 | 6.4558 | 117.3869 | 281.9398 | 0
2277 | 889.8155 | 3.3911 | 41.519 | 95.2531 | 83.6309 | 6.1007 | 99.1821 | 3.3901 | 8.39 | 29.8723 | 97.8378 | 10.1242 | 241.9916 | 114.1511 | 286.7328 | 8.9431 | 59.9414 | 13.5034 | 136 | 6.4558 | 117.3869 | 270.8873 | 0
2278 | 862.6209 | 3.0658 | 39.1544 | 94.9186 | 84.0596 | 5.6935 | 87.8556 | 3.6467 | 7.41 | 26.8841 | 92.0497 | 10.0724 | 225.3818 | 108.5467 | 267.3602 | 8.9268 | 58.1971 | 13.2428 | 123 | 6.4558 | 117.3869 | 266.862 | 0
2279 | 842.6068 | 2.072 | 39.1057 | 95.0676 | 84.078 | 5.676 | 75.9295 | 3.0785 | 6.705 | 21.8829 | 83.1236 | 9.9416 | 209.222 | 102.6976 | 244.8696 | 8.9983 | 57.2023 | 13.1433 | 117 | 6.4558 | 117.3869 | 261.1507 | 0
2280 | 829.4475 | 1.6115 | 39.1551 | 93.5577 | 84.0091 | 5.7415 | 81.9654 | 2.949 | 6.29 | 19.5877 | 78.1071 | 9.7984 | 196.5631 | 96.3041 | 230.347 | 9.0205 | 56.376 | 13.0384 | 118 | 6.4558 | 117.3869 | 254.4759 | 0
2281 | 816.6412 | 1.3286 | 39.0739 | 91.9404 | 84.0551 | 5.6977 | 85.4577 | 3.6948 | 6.135 | 19.6619 | 77.6832 | 9.7992 | 187.2282 | 92.4358 | 218.9444 | 8.8921 | 55.6241 | 12.8832 | 111 | 6.4558 | 117.3869 | 250.4379 | 0
2282 | 807.4289 | 1.1315 | 38.989 | 92.0205 | 84.1189 | 5.6372 | 86.8425 | 3.7993 | 6.2966 | 19.7574 | 79.9737 | 9.8022 | 183.8121 | 90.8503 | 211.4312 | 8.9514 | 55.1978 | 12.3618 | 126 | 6.4558 | 117.3869 | 248.3851 | 0
2283 | 814.9313 | 1.1597 | 39.019 | 91.8157 | 84.0369 | 5.7151 | 83.2722 | 3.3404 | 6.4197 | 21.7112 | 82.38 | 9.8113 | 179.0314 | 89.6329 | 209.7051 | 8.9737 | 55.4519 | 11.7453 | 107 | 6.4558 | 117.3869 | 247.6089 | 0
2284 | 814.471 | 1.4888 | 39.1973 | 90.9901 | 84.0123 | 5.7384 | 76.8974 | 3.07 | 6.3386 | 28.7572 | 83.4001 | 9.6613 | 175.2381 | 88.4319 | 211.5811 | 8.9493 | 56.6862 | 11.4819 | 105 | 6.4558 | 117.3869 | 257.8182 | 0
2285 | 819.3384 | 2.563 | 41.1668 | 92.3262 | 82.8025 | 6.8877 | 78.6284 | 3.681 | 6.255 | 37.8664 | 83.914 | 10.6122 | 166.2309 | 95.7155 | 213.8454 | 9.0332 | 58.4062 | 11.4933 | 133 | 6.4558 | 117.3869 | 281.637 | 0
2286 | 865.795 | 4.2771 | 65.0614 | 94.1429 | 80.907 | 8.6885 | 90.7291 | 4.2584 | 6.8316 | 51.4246 | 92.0056 | 16.7707 | 174.9899 | 129.7114 | 226.4822 | 12.8662 | 58.629 | 11.427 | 169 | 6.4558 | 117.3869 | 323.718 | 0
2287 | 933.8215 | 5.9213 | 96.3134 | 99.008 | 78.2692 | 11.1943 | 120.0275 | 5.0661 | 9.6311 | 77.4478 | 116.3605 | 27.7195 | 214.4091 | 186.917 | 284.3329 | 24.749 | 60.2713 | 11.8557 | 222 | 6.4558 | 117.3869 | 387.0344 | 0.012966
2288 | 1013.8182 | 9.1494 | 109.1745 | 113.6745 | 76.3483 | 13.0192 | 144.8081 | 6.1081 | 15.7373 | 101.9152 | 147.0071 | 34.9237 | 280.4648 | 239.187 | 391.3716 | 35.4687 | 68.0453 | 13.1423 | 244 | 6.4558 | 117.3869 | 458.1811 | 0.026084
2289 | 1092.7748 | 14.6415 | 111.8576 | 127.7058 | 74.867 | 14.4265 | 151.12 | 7.3489 | 19.735 | 109.0002 | 168.2029 | 35.741 | 348.3313 | 275.5617 | 484.1924 | 38.2464 | 79.0225 | 15.2128 | 292 | 6.4558 | 117.3869 | 510.9166 | 0.02649
2290 | 1145.8078 | 17.4974 | 110.1777 | 133.9517 | 73.4817 | 15.7425 | 150.2164 | 8.3251 | 20.12 | 108.3794 | 179.0378 | 36.3715 | 388.178 | 300.8805 | 525.4357 | 40.7824 | 87.7964 | 17.5413 | 331 | 6.4558 | 117.3869 | 525.0653 | 0.033075
2291 | 1151.331 | 11.5902 | 109.1473 | 135.5998 | 73.0319 | 16.1698 | 146.5311 | 7.8254 | 20.3278 | 110.553 | 184.2428 | 38.1494 | 407.626 | 314.1655 | 538.3008 | 41.6115 | 91.228 | 18.7305 | 322 | 6.4558 | 117.3869 | 523.9032 | 0.041881
2292 | 1138.181 | 4.5206 | 109.3483 | 136.0145 | 74.8825 | 14.4117 | 144.7442 | 7.987 | 20.1895 | 108.1968 | 185.2891 | 39.1606 | 411.6696 | 317.1252 | 539.9907 | 41.5529 | 90.641 | 19.3986 | 331 | 6.4558 | 117.3869 | 532.8642 | 0.050808
2293 | 1137.4172 | 3.6292 | 109.5096 | 139.346 | 75.5352 | 13.7916 | 150.2692 | 8.0094 | 20.0584 | 97.6874 | 186.4319 | 38.2037 | 416.6865 | 317.7206 | 538.2105 | 42.4453 | 90.2108 | 20.064 | 290 | 6.4558 | 117.3869 | 544.0473 | 0.072563
2294 | 1141.3444 | 3.5687 | 110.1861 | 140.307 | 75.0455 | 14.2569 | 158.6104 | 6.1914 | 18.3643 | 92.8031 | 187.922 | 36.8182 | 425.4465 | 316.4201 | 545.9713 | 41.238 | 90.377 | 19.538 | 273 | 6.4558 | 117.3869 | 550.7173 | 0.18012
2295 | 1122.2564 | 3.8278 | 109.8869 | 134.8463 | 73.8083 | 15.4322 | 160.2627 | 5.4399 | 15.52 | 94.0948 | 183.5031 | 36.1862 | 441.274 | 310.8177 | 549.9631 | 38.9001 | 89.775 | 18.474 | 273 | 6.4558 | 117.3869 | 555.5619 | 0.10815
2296 | 1087.3312 | 4.3274 | 106.9143 | 127.8818 | 77.7345 | 11.7023 | 152.1802 | 4.8643 | 13.94 | 91.7761 | 175.094 | 35.282 | 440.1108 | 300.8138 | 518.1187 | 31.4968 | 87.2279 | 17.6815 | 219 | 6.4558 | 117.3869 | 526.2519 | 0.13633
2297 | 1036.8063 | 3.7748 | 99.8137 | 114.3227 | 82.2994 | 7.3656 | 133.2556 | 3.9466 | 13.8021 | 81.7066 | 162.3609 | 33.7256 | 411.4197 | 270.3628 | 442.8474 | 18.3121 | 80.4997 | 16.9381 | 192 | 6.4558 | 117.3869 | 451.4019 | 0.035987
2298 | 980.2586 | 3.0281 | 95.7023 | 101.3058 | 83.7189 | 6.0172 | 111.4889 | 3.4704 | 13.6796 | 59.5059 | 136.7448 | 26.8644 | 366.0266 | 224.2241 | 367.9481 | 12.0999 | 72.077 | 16.4151 | 192 | 6.4558 | 117.3869 | 377.2293 | 0.012885
2299 | 933.3998 | 3.5648 | 83.508 | 97.2063 | 83.4711 | 6.2526 | 90.3449 | 3.5304 | 12.6677 | 36.7656 | 106.6869 | 14.8815 | 310.3815 | 193.6646 | 327.8294 | 10.4898 | 66.3921 | 16.1127 | 169 | 6.4558 | 117.3869 | 323.5485 | 0.0006113
2300 | 903.4259 | 3.7972 | 57.7382 | 95.9142 | 83.5771 | 6.1519 | 81.3591 | 3.9781 | 10.8357 | 27.488 | 94.2906 | 9.185 | 273.6751 | 177.1777 | 298.341 | 9.4694 | 61.9278 | 15.3627 | 149 | 6.4558 | 117.3869 | 292.9299 | 0
2301 | 875.1471 | 3.5819 | 43.3351 | 94.368 | 84.0649 | 5.6884 | 81.2039 | 3.7718 | 8.82 | 26.3355 | 94.0024 | 11.5069 | 257.1827 | 157.7215 | 265.5086 | 9.4141 | 58.3924 | 14.5979 | 151 | 6.4558 | 117.3869 | 288.6396 | 0
2302 | 838.2819 | 2.9128 | 42.2077 | 93.204 | 84.0588 | 5.6943 | 81.2569 | 3.1714 | 7.77 | 24.3275 | 87.4441 | 13.9016 | 237.9822 | 137.9749 | 239.5446 | 9.3295 | 57.2405 | 13.3302 | 142 | 6.4558 | 117.3869 | 289.3799 | 0
2303 | 819.736 | 1.9786 | 41.175 | 92.1782 | 83.4115 | 6.3092 | 80.3676 | 3.4919 | 7.065 | 21.4826 | 78.6969 | 12.5611 | 224.8944 | 125.5474 | 233.6763 | 9.4303 | 56.7767 | 11.8329 | 135 | 6.4558 | 117.3869 | 283.7072 | 0
2304 | 821.3842 | 1.3251 | 41.1827 | 91.941 | 83.6442 | 6.0881 | 79.9798 | 4.0016 | 6.4739 | 20.4744 | 76.0401 | 9.3019 | 210.2435 | 121.9709 | 239.7992 | 9.3514 | 56.3591 | 11.6096 | 125 | 6.4558 | 117.3869 | 279.033 | 0
2305 | 817.9123 | 1.1443 | 41.2162 | 92.4009 | 84.0829 | 5.6713 | 79.8702 | 4.1794 | 6.6239 | 20.8077 | 76.6326 | 8.0234 | 194.4138 | 119.5765 | 236.027 | 9.311 | 56.2534 | 8.6591 | 119 | 6.4558 | 117.3869 | 277.0385 | 0
2306 | 801.0968 | 1.0879 | 41.3173 | 91.6572 | 84.0928 | 5.6619 | 79.0488 | 4.0857 | 6.6873 | 21.3292 | 76.5018 | 8.022 | 190.3451 | 115.0547 | 228.418 | 9.3223 | 55.9629 | 4.279 | 135 | 6.4558 | 117.3869 | 274.2877 | 0
2307 | 797.0585 | 1.1413 | 41.2739 | 90.7963 | 83.998 | 5.752 | 78.7693 | 4.1134 | 6.6607 | 23.2799 | 76.9209 | 8.0228 | 186.8201 | 112.6511 | 225.325 | 9.2639 | 55.4187 | 2.9328 | 112 | 6.4558 | 117.3869 | 271.7141 | 0
2308 | 799.1308 | 1.6494 | 41.1734 | 90.5481 | 83.4166 | 6.3043 | 78.8978 | 4.2988 | 6.5473 | 29.6418 | 77.4024 | 8.3265 | 182.2672 | 110.5599 | 223.5246 | 9.3299 | 55.8945 | 3.2461 | 111 | 6.4558 | 117.3869 | 280.4189 | 0
2309 | 804.0954 | 2.6701 | 46.2061 | 91.4544 | 83.0786 | 6.6254 | 80.0008 | 4.4413 | 6.4709 | 38.4335 | 77.334 | 10.0216 | 180.9837 | 111.4605 | 223.6713 | 9.418 | 57.6703 | 3.3663 | 122 | 6.4558 | 117.3869 | 305.6138 | 0
2310 | 836.3753 | 4.0337 | 64.8986 | 93.2391 | 80.7259 | 8.8605 | 90.7017 | 4.2862 | 6.8962 | 52.0118 | 83.6435 | 15.3398 | 208.0317 | 134.9957 | 245.5372 | 13.984 | 57.6157 | 2.879 | 198 | 6.4558 | 117.3869 | 345.8645 | 0
2311 | 917.4295 | 7.3027 | 89.8641 | 97.3281 | 76.6862 | 12.6982 | 117.887 | 4.5517 | 8.8918 | 77.1631 | 105.5565 | 22.5274 | 260.2382 | 181.6876 | 307.7058 | 25.1789 | 57.7588 | 5.023 | 306 | 6.4558 | 117.3869 | 408.5716 | 0.012945
2312 | 1023.0877 | 8.1848 | 105.1987 | 111.3062 | 74.8533 | 14.4394 | 141.6459 | 5.5027 | 11.8685 | 98.4129 | 138.9462 | 28.5575 | 308.8022 | 226.4502 | 395.4864 | 36.641 | 64.4726 | 10.65 | 334 | 6.4558 | 117.3869 | 480.9605 | 0.02415
2313 | 1103.4438 | 5.0671 | 109.2039 | 125.2421 | 72.5598 | 16.6183 | 146.7277 | 6.5049 | 12.8453 | 101.973 | 165.5829 | 31.7297 | 359.3415 | 259.9631 | 475.4471 | 42.6403 | 76.181 | 14.0763 | 384 | 6.4558 | 117.3869 | 534.8354 | 0.033899
2314 | 1136.3786 | 3.6928 | 110.4407 | 132.6421 | 71.7 | 17.4351 | 146.591 | 6.7636 | 11.8325 | 99.6577 | 174.8462 | 32.7573 | 412.6857 | 284.8302 | 522.845 | 43.4635 | 85.8006 | 13.5478 | 375 | 6.4558 | 117.3869 | 562.0621 | 0.081277
2315 | 1146.8371 | 3.3194 | 110.6283 | 136.3333 | 72.0955 | 17.0594 | 146.4494 | 6.2552 | 10.2787 | 97.0258 | 174.0437 | 32.4649 | 440.8252 | 303.0021 | 542.1075 | 41.8691 | 89.9979 | 15.0255 | 334 | 6.4558 | 117.3869 | 568.0188 | 0.078074
2316 | 1129.4377 | 3.6499 | 110.5281 | 137.501 | 73.373 | 15.8457 | 145.3653 | 6.2681 | 11.2567 | 93.6882 | 173.2156 | 32.085 | 448.3192 | 312.8683 | 551.2965 | 42.2701 | 89.7807 | 17.8268 | 337 | 6.4558 | 117.3869 | 567.8839 | 0.087869
2317 | 1123.8083 | 3.6572 | 110.4921 | 140.3958 | 74.0319 | 15.2198 | 141.3344 | 6.916 | 13.6185 | 94.0262 | 174.2423 | 32.0011 | 454.1519 | 317.0638 | 562.2495 | 43.6991 | 88.2702 | 17.9036 | 314 | 6.4558 | 117.3869 | 570.9866 | 0.13558
2318 | 1134.7765 | 3.7949 | 110.4921 | 140.7307 | 73.9154 | 15.3305 | 137.6041 | 7.916 | 13.7227 | 97.9442 | 174.6789 | 31.4688 | 454.4168 | 319.357 | 560.8508 | 42.5531 | 89.1037 | 17.5565 | 288 | 6.4558 | 117.3869 | 574.0612 | 0.098601
2319 | 1118.777 | 3.9392 | 108.5875 | 137.6177 | 73.5131 | 15.7127 | 133.3581 | 7.9082 | 14.8053 | 101.6883 | 172.9684 | 30.7967 | 449.2036 | 317.0289 | 523.4724 | 39.12 | 91.1787 | 17.6388 | 295 | 6.4558 | 117.3869 | 576.7796 | 0.1311
2320 | 1095.44 | 3.7982 | 106.8278 | 130.3561 | 77.9536 | 11.4941 | 123.4328 | 6.7631 | 16.3695 | 101.573 | 168.6263 | 29.7177 | 437.868 | 307.0667 | 463.4817 | 31.2792 | 90.7811 | 17.2889 | 280 | 6.4558 | 117.3869 | 556.5378 | 0.083738
2321 | 1054.6613 | 3.7366 | 87.5176 | 119.2893 | 82.8697 | 6.8239 | 111.5164 | 5.6363 | 15.6033 | 91.5825 | 157.6934 | 27.7967 | 409.6278 | 264.7403 | 394.2303 | 19.0693 | 84.9063 | 16.5689 | 265 | 6.4558 | 117.3869 | 488.9056 | 0.054209
2322 | 972.7714 | 3.1976 | 68.7322 | 105.564 | 84.0143 | 5.7365 | 105.852 | 5.1601 | 14.7598 | 67.9486 | 133.332 | 20.9618 | 344.7063 | 194.4037 | 327.9022 | 11.6161 | 75.3522 | 16.091 | 234 | 6.4558 | 117.3869 | 404.2087 | 0.039628
2323 | 915.9172 | 3.5745 | 68.7322 | 96.4954 | 84.0933 | 5.6614 | 98.0396 | 5.0167 | 12.9551 | 43.1595 | 105.2034 | 11.3493 | 290.3465 | 148.3201 | 287.3915 | 9.9519 | 67.6907 | 15.8481 | 217 | 6.4558 | 117.3869 | 345.2075 | 0.003367
2324 | 884.184 | 4.0499 | 68.7322 | 95.9402 | 84.0523 | 5.7004 | 88.647 | 5.6521 | 9.2177 | 31.3463 | 94.1328 | 11.9863 | 260.3289 | 134.2554 | 263.096 | 9.8606 | 61.8521 | 15.734 | 187 | 6.4558 | 117.3869 | 318.7371 | 0
2325 | 854.2516 | 3.5136 | 68.7322 | 95.2819 | 83.4972 | 6.2277 | 86.8688 | 5.4377 | 7.7477 | 29.5218 | 93.3123 | 17.7888 | 230.4573 | 123.2087 | 247.6704 | 10.0278 | 57.4947 | 15.5133 | 176 | 6.4558 | 117.3869 | 313.7638 | 0
2326 | 832.618 | 2.8164 | 54.4358 | 92.394 | 84.2329 | 5.5288 | 84.9074 | 4.8789 | 7.8137 | 29.1282 | 85.1646 | 14.8895 | 209.6014 | 111.1578 | 239.175 | 10.0819 | 55.9323 | 15.0812 | 147 | 6.4558 | 117.3869 | 314.1569 | 0
2327 | 824.8779 | 2.0057 | 39.7264 | 91.442 | 83.8312 | 5.9105 | 83.7619 | 4.9114 | 7.983 | 27.7911 | 73.8393 | 9.193 | 189.841 | 105.4552 | 230.3037 | 10.017 | 55.7688 | 14.4412 | 120 | 6.4558 | 117.3869 | 310.4714 | 0
2328 | 825.9996 | 1.4851 | 39.7264 | 91.711 | 83.6509 | 6.0818 | 84.2038 | 4.4428 | 7.755 | 26.302 | 68.9147 | 7.3854 | 171.8459 | 102.2335 | 230.5836 | 10.047 | 55.5775 | 13.4168 | 111 | 6.4558 | 117.3869 | 296.998 | 0
2329 | 811.8687 | 1.2358 | 39.7293 | 91.2682 | 84.6625 | 5.1207 | 83.1424 | 4.3061 | 6.94 | 25.6085 | 68.7911 | 7.4096 | 163.1827 | 97.9299 | 233.8593 | 10.0852 | 55.4238 | 12.5181 | 108 | 6.4558 | 117.3869 | 278.8696 | 0
2330 | 796.4756 | 1.1596 | 39.7546 | 91.9325 | 84.4054 | 5.3649 | 82.2489 | 4.351 | 6.75 | 25.734 | 69.103 | 7.4345 | 163.9239 | 95.0558 | 227.5371 | 10.0793 | 55.4778 | 11.8885 | 124 | 6.4558 | 117.3869 | 268.712 | 0
2331 | 804.0293 | 1.1727 | 39.7546 | 91.667 | 84.0848 | 5.6695 | 82.0204 | 4.3231 | 6.495 | 27.6347 | 69.6075 | 7.395 | 164.8138 | 94.1757 | 214.7799 | 10.0016 | 55.6553 | 11.5342 | 105 | 6.4558 | 117.3869 | 266.1083 | 0
2332 | 810.692 | 1.5961 | 43.0815 | 90.501 | 84.027 | 5.7244 | 81.7027 | 4.6657 | 6.405 | 34.0681 | 69.8122 | 7.3568 | 162.178 | 93.5254 | 208.8634 | 10.4142 | 56.5089 | 11.5311 | 103 | 6.4558 | 117.3869 | 275.5866 | 0
2333 | 821.554 | 2.6351 | 46.4378 | 90.7707 | 82.8313 | 6.8604 | 82.4436 | 5.0035 | 6.39 | 42.7524 | 69.6837 | 8.3732 | 165.1885 | 102.8114 | 211.5146 | 11.053 | 57.7242 | 12.355 | 121 | 6.4558 | 117.3869 | 301.717 | 0
2334 | 861.3053 | 5.9014 | 58.9656 | 92.0784 | 80.8768 | 8.7171 | 92.6044 | 4.9202 | 6.7953 | 55.3277 | 75.5613 | 14.6328 | 175.5866 | 137.8516 | 233.2628 | 14.6281 | 57.474 | 12.9499 | 170 | 6.4558 | 117.3869 | 348.0959 | 0
2335 | 905.8329 | 11.4762 | 87.0243 | 96.2633 | 76.5004 | 12.8747 | 116.7141 | 5.3138 | 8.851 | 73.6044 | 97.5782 | 25.4221 | 222.6094 | 192.6097 | 282.9766 | 25.2598 | 58.697 | 12.8413 | 305 | 6.4558 | 117.3869 | 417.466 | 0.016457
2336 | 988.0516 | 15.4164 | 104.4575 | 107.4222 | 75.8665 | 13.477 | 136.0868 | 6.456 | 11.8448 | 84.7392 | 131.086 | 32.2549 | 295.0135 | 243.5197 | 354.9497 | 35.6462 | 65.9594 | 13.8517 | 344 | 6.4558 | 117.3869 | 491.6182 | 0.032399
2337 | 1071.343 | 14.2096 | 107.4848 | 120.1669 | 74.6842 | 14.6001 | 141.8017 | 7.3379 | 13.4621 | 82.5185 | 157.3333 | 32.5525 | 357.7459 | 277.1055 | 427.6137 | 38.7207 | 76.8435 | 14.7032 | 349 | 6.4558 | 117.3869 | 544.4254 | 0.063346
2338 | 1119.3303 | 14.3088 | 109.3359 | 126.7977 | 73.1398 | 16.0673 | 143.6325 | 7.7632 | 12.9418 | 75.8208 | 169.5867 | 33.7973 | 396.2768 | 294.581 | 469.964 | 39.9299 | 87.0476 | 15.1021 | 389 | 6.4558 | 117.3869 | 562.8797 | 0.15887
2339 | 1150.4715 | 17.6013 | 107.697 | 129.7102 | 73.651 | 15.5816 | 143.1934 | 7.5553 | 11.115 | 69.9245 | 175.2516 | 37.1865 | 406.0371 | 300.8462 | 485.4142 | 41.235 | 92.3587 | 15.7191 | 330 | 6.4558 | 117.3869 | 558.5613 | 0.14063
2340 | 1148.6077 | 15.8202 | 106.0846 | 129.9802 | 72.1947 | 16.9651 | 142.9917 | 6.8074 | 10.145 | 67.4387 | 176.4358 | 37.4121 | 407.9967 | 304.5273 | 503.6413 | 43.1295 | 92.251 | 16.6609 | 321 | 6.4558 | 117.3869 | 556.0064 | 0.14853
2341 | 1156.3161 | 11.2779 | 108.7006 | 131.5937 | 73.4267 | 15.7947 | 139.905 | 6.4484 | 11.12 | 74.3915 | 175.5355 | 36.4394 | 409.5688 | 308.809 | 516.4047 | 43.9011 | 91.3149 | 17.582 | 316 | 6.4558 | 117.3869 | 557.4348 | 0.14583
2342 | 1166.8199 | 6.6936 | 109.3267 | 137.7419 | 75.7064 | 13.629 | 138.4308 | 7.8282 | 12.31 | 86.0974 | 176.5517 | 37.3358 | 415.5607 | 308.7105 | 506.0171 | 41.5073 | 91.4614 | 17.684 | 294 | 6.4558 | 117.3869 | 557.3959 | 0.17311
2343 | 1160.8301 | 4.3589 | 103.8189 | 135.1262 | 75.4729 | 13.8508 | 141.3302 | 8.5054 | 12.885 | 92.8543 | 175.9565 | 37.6612 | 425.7534 | 302.588 | 486.8127 | 38.8952 | 91.5333 | 17.7938 | 281 | 6.4558 | 117.3869 | 559.663 | 0.093322
2344 | 1123.5561 | 4.3756 | 100.3136 | 125.3574 | 79.2125 | 10.2982 | 137.3994 | 7.3825 | 13.08 | 93.0379 | 172.1314 | 34.644 | 417.2249 | 288.0447 | 450.4195 | 31.3764 | 90.133 | 17.9207 | 239 | 6.4558 | 117.3869 | 534.099 | 0.058084
2345 | 1058.3694 | 4.1126 | 100.3136 | 112.1154 | 80.8332 | 8.7585 | 124.7824 | 5.322 | 13.515 | 83.2454 | 161.198 | 31.5829 | 378.1259 | 248.9962 | 401.4255 | 17.6711 | 85.3795 | 17.766 | 236 | 6.4558 | 117.3869 | 460.4087 | 0.043489
2346 | 996.6228 | 3.2325 | 100.3136 | 99.2287 | 81.7692 | 7.8693 | 104.7898 | 4.1739 | 14.495 | 61.1613 | 134.5983 | 26.2523 | 333.0312 | 197.2697 | 368.9872 | 9.6414 | 76.4223 | 17.1158 | 215 | 6.4558 | 117.3869 | 381.7894 | 0.023681
2347 | 941.2318 | 3.3649 | 85.8159 | 96.4693 | 83.6171 | 6.1139 | 85.7323 | 4.2524 | 13.1331 | 39.6718 | 104.3566 | 16.5226 | 282.9675 | 169.7395 | 339.7884 | 8.6732 | 66.7161 | 16.1572 | 186 | 6.4558 | 117.3869 | 330.9958 | 0.0018564
2348 | 912.7339 | 3.5827 | 57.2802 | 97.6906 | 84.04 | 5.7121 | 81.0467 | 4.5764 | 8.5176 | 32.9984 | 91.8388 | 10.6034 | 239.923 | 158.9967 | 298.3321 | 8.828 | 60.4175 | 15.4029 | 175 | 6.4558 | 117.3869 | 305.8659 | 0
2349 | 896.8446 | 3.7621 | 41.7482 | 95.0352 | 84.0668 | 5.6866 | 80.5814 | 4.8695 | 6.4654 | 35.2124 | 90.3676 | 9.5569 | 223.0233 | 140.7395 | 265.7626 | 9.2909 | 57.552 | 14.4935 | 170 | 6.4558 | 117.3869 | 299.1863 | 0
2350 | 875.1958 | 3.1621 | 39.6814 | 91.169 | 84.0485 | 5.704 | 79.0387 | 4.8472 | 6.6724 | 35.8129 | 84.1466 | 9.4215 | 202.9298 | 119.6318 | 254.2438 | 9.3052 | 56.5452 | 13.5306 | 133 | 6.4558 | 117.3869 | 299.1033 | 0
2351 | 859.5585 | 1.8874 | 39.7193 | 90.5454 | 84.0699 | 5.6836 | 79.2675 | 4.9509 | 6.3498 | 34.6632 | 75.6336 | 9.4483 | 186.6044 | 110.8338 | 251.7074 | 9.2268 | 56.2057 | 13.0483 | 118 | 6.4558 | 117.3869 | 294.6208 | 0
2352 | 842.4872 | 1.4495 | 39.6409 | 90.6547 | 84.0196 | 5.7315 | 79.4671 | 5.1085 | 6.3033 | 33.657 | 71.8453 | 9.4618 | 182.5407 | 110.0292 | 246.178 | 9.3156 | 55.5769 | 13.0438 | 111 | 6.4558 | 117.3869 | 284.6585 | 0
2353 | 829.7817 | 1.3622 | 39.5814 | 90.5217 | 84.085 | 5.6693 | 79.4668 | 5.0513 | 6.4982 | 33.0655 | 70.9309 | 9.4634 | 176.614 | 103.7134 | 238.0182 | 9.3283 | 55.102 | 13.4774 | 108 | 6.4558 | 117.3869 | 275.03 | 0
2354 | 826.8548 | 1.391 | 39.5976 | 90.2196 | 84.108 | 5.6475 | 79.2753 | 5.0098 | 6.3952 | 32.9422 | 70.29 | 9.4792 | 172.5146 | 95.0436 | 233.7866 | 9.2972 | 55.0731 | 13.2989 | 127 | 6.4558 | 117.3869 | 269.3336 | 0
2355 | 827.8639 | 1.4402 | 42.0925 | 89.9776 | 84.0186 | 5.7324 | 79.0797 | 5.2233 | 6.4442 | 34.5939 | 70.5944 | 9.472 | 163.1661 | 91.0529 | 228.2085 | 9.3447 | 55.0789 | 12.9098 | 105 | 6.4558 | 117.3869 | 267.4171 | 0
2356 | 831.0035 | 2.0436 | 44.6886 | 90.5442 | 84.043 | 5.7092 | 79.0557 | 5.423 | 6.5158 | 40.6466 | 71.0596 | 9.4623 | 155.7891 | 90.3817 | 216.6216 | 9.3258 | 55.9259 | 13.1121 | 104 | 6.4558 | 117.3869 | 279.3122 | 0
2357 | 839.6827 | 3.1735 | 44.6886 | 91.3464 | 84.0412 | 5.7109 | 80.054 | 5.3596 | 6.33 | 48.5373 | 71.0133 | 11.19 | 156.5198 | 98.2798 | 213.1291 | 9.2375 | 57.5621 | 12.8041 | 113 | 6.4558 | 117.3869 | 306.1886 | 0
2358 | 884.4076 | 4.3887 | 60.8352 | 91.2588 | 79.1838 | 10.3254 | 90.8155 | 5.0715 | 6.38 | 58.3559 | 78.0848 | 16.5648 | 173.238 | 129.5424 | 227.54 | 13.084 | 57.3672 | 12.1063 | 191 | 6.4558 | 117.3869 | 345.0152 | 0
2359 | 939.5759 | 4.8238 | 91.8233 | 95.1741 | 76.1721 | 13.1866 | 119.8548 | 5.7603 | 8.21 | 75.9719 | 105.7632 | 24.3504 | 220.5422 | 182.916 | 275.2092 | 24.8173 | 57.7938 | 12.3357 | 259 | 6.4558 | 117.3869 | 407.7377 | 0.039665
2360 | 1021.2788 | 4.0969 | 106.0812 | 106.6997 | 74.7445 | 14.5428 | 143.7351 | 7.3911 | 10.6556 | 92.6422 | 141.5443 | 29.3434 | 285.4637 | 232.6828 | 354.2177 | 35.7152 | 64.9209 | 13.5522 | 314 | 6.4558 | 117.3869 | 475.6128 | 0.10551
2361 | 1114.0327 | 4.7064 | 107.4048 | 122.7088 | 73.0223 | 16.1789 | 150.0563 | 8.0694 | 10.0944 | 96.271 | 161.7539 | 31.1848 | 344.6994 | 264.3796 | 421.9692 | 40.3619 | 77.6376 | 14.9924 | 337 | 6.4558 | 117.3869 | 522.3492 | 0.16221
2362 | 1138.6662 | 7.9807 | 107.1962 | 130.2814 | 73.8225 | 15.4187 | 151.2177 | 7.0818 | 10.535 | 91.9932 | 170.47 | 33.0836 | 390.0728 | 285.7732 | 459.0536 | 41.9989 | 88.6733 | 16.1144 | 364 | 6.4558 | 117.3869 | 558.1287 | 0.17019
2363 | 1143.0559 | 10.8089 | 108.7717 | 127.0886 | 74.3338 | 14.933 | 150.318 | 6.9497 | 12.52 | 89.8954 | 174.5868 | 34.5473 | 410.7089 | 301.034 | 482.6116 | 41.7189 | 93.3727 | 16.4474 | 324 | 6.4558 | 117.3869 | 584.7449 | 0.2121
2364 | 1133.9838 | 8.9541 | 111.8649 | 126.9952 | 72.9977 | 16.2023 | 146.6041 | 8.1443 | 10.8445 | 104.1276 | 173.2 | 33.6681 | 407.9795 | 304.6765 | 503.6679 | 41.5328 | 93.6843 | 16.6581 | 357 | 6.4558 | 117.3869 | 589.7995 | 0.18796
2365 | 1127.5392 | 6.9006 | 111.9788 | 129.9298 | 70.0999 | 18.9552 | 143.7303 | 8.3539 | 11.138 | 92.0615 | 170.9674 | 32.6217 | 398.3384 | 300.4754 | 517.953 | 41.2372 | 92.9452 | 16.9394 | 324 | 6.4558 | 117.3869 | 586.8752 | 0.13524
2366 | 1126.6008 | 6.7645 | 110.6411 | 133.3914 | 71.4042 | 17.7161 | 139.6569 | 7.8769 | 13.335 | 71.4892 | 170.7625 | 31.8937 | 394.2289 | 299.0107 | 523.8141 | 40.3459 | 92.1012 | 17.0461 | 307 | 6.4558 | 117.3869 | 584.5372 | 0.17319
2367 | 1102.7998 | 5.3092 | 106.8547 | 135.3026 | 75.0315 | 14.2701 | 133.6153 | 6.8885 | 13.3438 | 80.415 | 171.1352 | 30.9485 | 393.6228 | 294.5967 | 522.5926 | 37.6594 | 90.3661 | 16.9537 | 302 | 6.4558 | 117.3869 | 572.8084 | 0.10845
2368 | 1048.5719 | 3.3877 | 102.485 | 130.369 | 79.6662 | 9.8672 | 130.7241 | 5.6348 | 12.7452 | 78.4003 | 169.191 | 29.4393 | 376.9043 | 271.7304 | 490.893 | 26.5753 | 86.1459 | 16.5985 | 316 | 6.4558 | 117.3869 | 534.8287 | 0.0964
2369 | 994.1883 | 3.2668 | 88.9037 | 114.4952 | 83.2257 | 6.4857 | 127.907 | 4.6913 | 12.9235 | 63.2673 | 159.5076 | 28.6526 | 341.847 | 225.1181 | 421.6424 | 13.0037 | 78.9022 | 16.0507 | 306 | 6.4558 | 117.3869 | 463.3901 | 0.047944
2370 | 950.0498 | 3.0528 | 64.0496 | 99.0974 | 84.0118 | 5.7389 | 112.2329 | 4.4851 | 14.17 | 44.9519 | 134.4187 | 23.918 | 303.7074 | 176.3966 | 353.5416 | 10.2181 | 70.8762 | 15.5413 | 264 | 6.4558 | 117.3869 | 392.1053 | 0.035155
2371 | 903.6794 | 2.9536 | 48.2552 | 93.5931 | 83.4025 | 6.3177 | 90.1263 | 4.4805 | 12.8469 | 33.0972 | 102.7772 | 12.5593 | 271.861 | 149.4291 | 303.4467 | 9.5025 | 63.794 | 15.4996 | 224 | 6.4558 | 117.3869 | 349.321 | 0.0052089
2372 | 864.0659 | 3.6204 | 43.4003 | 93.2777 | 83.0279 | 6.6736 | 82.1306 | 5.0792 | 8.6503 | 31.9032 | 84.2262 | 7.9391 | 240.7222 | 136.7031 | 271.5853 | 9.3463 | 58.3079 | 15.025 | 225 | 6.4558 | 117.3869 | 333.347 | 0
2373 | 850.4834 | 3.4246 | 41.2665 | 94.3236 | 83.7014 | 6.0338 | 82.1217 | 5.3547 | 7.1585 | 35.7552 | 77.9475 | 9.6659 | 217.8903 | 128.2358 | 258.034 | 9.735 | 55.3702 | 14.0381 | 198 | 6.4558 | 117.3869 | 334.0095 | 0
2374 | 839.3018 | 2.9823 | 41.2455 | 93.3146 | 83.482 | 6.2422 | 81.6909 | 5.4803 | 7.4163 | 37.7122 | 75.2938 | 10.1251 | 210.2785 | 120.4302 | 256.0339 | 9.829 | 54.0381 | 13.4131 | 185 | 6.4558 | 117.3869 | 335.5469 | 0
2375 | 824.6347 | 2.3104 | 41.0472 | 92.5977 | 83.6513 | 6.0813 | 80.4402 | 5.5068 | 6.7776 | 38.1685 | 73.6902 | 10.1473 | 198.0769 | 109.0182 | 255.7696 | 9.8772 | 53.5717 | 13.2943 | 167 | 6.4558 | 117.3869 | 328.3732 | 0
2376 | 824.4007 | 1.8704 | 40.872 | 92.6281 | 84.0448 | 5.7076 | 81.0562 | 5.3527 | 6.5854 | 38.8842 | 72.1017 | 10.208 | 178.4259 | 98.4015 | 256.8679 | 9.7919 | 53.6972 | 13.1082 | 153 | 6.4558 | 117.3869 | 316.7651 | 0
2377 | 820.9286 | 1.7411 | 40.872 | 92.7195 | 84.053 | 5.6997 | 81.6056 | 5.3392 | 6.58 | 37.8238 | 71.4588 | 9.9042 | 170.4127 | 92.2166 | 260.4281 | 9.7756 | 53.7539 | 12.8617 | 141 | 6.4558 | 117.3869 | 311.7934 | 0
2378 | 809.3871 | 1.6585 | 40.872 | 92.5418 | 83.4525 | 6.2702 | 80.962 | 5.5089 | 6.5 | 35.4828 | 71.6191 | 9.4517 | 168.5169 | 89.7236 | 255.6889 | 9.7789 | 53.8036 | 12.749 | 159 | 6.4558 | 117.3869 | 314.3679 | 0
2379 | 808.9329 | 1.6028 | 40.872 | 92.3378 | 83.6606 | 6.0725 | 80.8582 | 5.7428 | 6.525 | 34.787 | 72.2088 | 9.3186 | 159.9496 | 90.1588 | 245.5779 | 9.7552 | 53.9142 | 12.4982 | 126 | 6.4558 | 117.3869 | 315.9798 | 0
2380 | 805.6181 | 1.9598 | 43.6064 | 92.4829 | 83.441 | 6.2812 | 81.2329 | 5.8064 | 6.65 | 37.5448 | 72.8058 | 9.4647 | 154.9165 | 90.799 | 244.284 | 9.8251 | 54.8411 | 12.4769 | 115 | 6.4558 | 117.3869 | 315.6714 | 0
2381 | 799.2154 | 2.8724 | 46.388 | 91.7092 | 83.6038 | 6.1265 | 80.638 | 5.7187 | 6.555 | 41.9917 | 72.2052 | 8.7708 | 151.8177 | 88.5566 | 243.8596 | 9.645 | 56.5002 | 12.5542 | 117 | 6.4558 | 117.3869 | 314.7396 | 0
2382 | 815.5983 | 2.6655 | 64.615 | 89.7168 | 84.1363 | 5.6206 | 88.471 | 5.6007 | 6.2864 | 44.2447 | 69.8039 | 6.2688 | 151.2022 | 85.4772 | 232.4626 | 9.3773 | 55.8047 | 12.362 | 127 | 6.4558 | 117.3869 | 314.685 | 0
2383 | 830.9131 | 2.0777 | 81.324 | 89.1452 | 84.0479 | 5.7046 | 113.6042 | 5.3618 | 7.6488 | 42.5831 | 71.012 | 7.0361 | 150.3457 | 91.8967 | 232.9584 | 9.3203 | 53.3057 | 12.5171 | 175 | 6.4558 | 117.3869 | 317.381 | 0.1118
2384 | 845.6935 | 1.7666 | 82.966 | 90.1899 | 84.012 | 5.7387 | 130.6838 | 4.8425 | 10.8859 | 43.2831 | 87.2375 | 10.6002 | 158.7571 | 112.177 | 257.9529 | 9.2349 | 52.4086 | 13.0757 | 166 | 6.4558 | 117.3869 | 323.2192 | 0.1936
2385 | 873.7316 | 1.3872 | 84.9348 | 92.2682 | 84.0223 | 5.7289 | 127.4617 | 4.4624 | 12.5214 | 52.9368 | 114.9344 | 10.8784 | 184.8135 | 130.9005 | 272.4217 | 8.8115 | 53.1184 | 13.331 | 168 | 6.4558 | 117.3869 | 335.2171 | 0.18211
2386 | 895.2853 | 1.5787 | 84.9348 | 95.315 | 83.4585 | 6.2645 | 123.4725 | 4.3742 | 12.0913 | 63.2145 | 131.6743 | 9.7377 | 207.6593 | 140.2665 | 266.1656 | 8.2326 | 55.0844 | 13.3501 | 190 | 6.4558 | 117.3869 | 349.9126 | 0.19553
2387 | 905.1613 | 1.5684 | 83.9329 | 95.2648 | 83.6993 | 6.0358 | 120.079 | 4.4456 | 13.5739 | 67.7893 | 123.918 | 9.5372 | 215.2844 | 151.1289 | 260.4442 | 8.174 | 56.8579 | 13.3466 | 190 | 6.4558 | 117.3869 | 362.2499 | 0.19613
2388 | 913.4854 | 1.7777 | 72.3407 | 93.022 | 82.8493 | 6.8432 | 117.2946 | 4.6088 | 13.062 | 71.8123 | 103.4278 | 9.8265 | 215.6977 | 168.2779 | 267.0054 | 8.2896 | 56.1738 | 13.3917 | 182 | 6.4558 | 117.3869 | 372.6815 | 0.20738
2389 | 910.2686 | 1.809 | 62.101 | 93.9059 | 82.64 | 7.0421 | 113.7111 | 4.7894 | 12.5461 | 75.173 | 91.5349 | 11.8242 | 211.916 | 183.1436 | 278.8144 | 8.237 | 54.5187 | 13.5363 | 191 | 6.4558 | 117.3869 | 369.2566 | 0.24785
2390 | 910.5514 | 1.7095 | 62.101 | 95.7166 | 83.6237 | 6.1076 | 107.2428 | 4.4907 | 13.3841 | 71.6122 | 89.8862 | 16.6841 | 209.3347 | 185.2906 | 283.4203 | 8.2612 | 54.433 | 13.5595 | 197 | 6.4558 | 117.3869 | 349.2591 | 0.25015
2391 | 907.731 | 1.808 | 51.4648 | 95.0966 | 83.5266 | 6.1998 | 102.012 | 3.7481 | 13.1063 | 57.7702 | 90.1387 | 16.6562 | 211.2694 | 175.7345 | 288.5666 | 8.2068 | 56.2641 | 13.4526 | 192 | 6.4558 | 117.3869 | 333.3311 | 0.28031
2392 | 905.8867 | 1.8151 | 41.2364 | 93.1665 | 83.6363 | 6.0956 | 97.4765 | 3.3081 | 10.6514 | 40.7739 | 90.937 | 11.6419 | 215.6278 | 159.9448 | 288.9736 | 8.1807 | 57.5482 | 13.4 | 187 | 6.4558 | 117.3869 | 321.0894 | 0.22551
2393 | 897.0138 | 1.757 | 40.7752 | 93.3183 | 83.9968 | 5.7531 | 89.3656 | 3.0569 | 10.7523 | 32.4408 | 89.6659 | 9.2966 | 218.8883 | 138.0929 | 265.6781 | 8.2664 | 55.8104 | 13.3661 | 190 | 6.4558 | 117.3869 | 307.9757 | 0.22197
2394 | 875.9285 | 2.0226 | 40.0428 | 93.1566 | 84.0795 | 5.6746 | 83.0118 | 3.6449 | 14.1849 | 32.3293 | 84.9755 | 9.3189 | 217.6415 | 117.374 | 237.4444 | 8.2542 | 53.9391 | 13.3928 | 198 | 6.4558 | 117.3869 | 296.6221 | 0.14591
2395 | 847.2184 | 3.0413 | 39.5247 | 91.0419 | 84.0409 | 5.7112 | 78.5431 | 5.1123 | 13.5823 | 32.0295 | 83.2517 | 8.5938 | 203.7666 | 107.9078 | 227.9702 | 8.4265 | 53.6063 | 13.49 | 195 | 6.4558 | 117.3869 | 286.9206 | 0.027435
2396 | 839.2344 | 3.9964 | 39.5247 | 91.4111 | 84.0298 | 5.7217 | 77.8036 | 5.6639 | 9.865 | 29.7865 | 85.4797 | 7.4172 | 186.4815 | 111.5677 | 233.0984 | 8.9997 | 53.3599 | 13.3225 | 190 | 6.4558 | 117.3869 | 287.81 | 0
2397 | 844.8438 | 3.9171 | 39.5247 | 93.184 | 83.4564 | 6.2665 | 78.7125 | 5.9637 | 7.2363 | 28.7103 | 84.4885 | 7.322 | 179.9099 | 118.0327 | 244.9639 | 9.5436 | 53.5697 | 12.7139 | 195 | 6.4558 | 117.3869 | 298.6727 | 0
2398 | 840.7095 | 3.0776 | 39.6755 | 93.7398 | 83.6513 | 6.0813 | 79.0615 | 6.1068 | 6.8674 | 29.4344 | 79.164 | 7.5348 | 175.5072 | 113.5974 | 252.0293 | 9.5908 | 53.7793 | 12.32 | 175 | 6.4558 | 117.3869 | 308.6341 | 0
2399 | 827.6166 | 2.1266 | 39.8418 | 93.9914 | 83.474 | 6.2498 | 79.0569 | 6.3045 | 6.7936 | 30.4618 | 74.372 | 7.5424 | 175.4124 | 103.1018 | 250.1704 | 9.5639 | 53.6692 | 12.5646 | 161 | 6.4558 | 117.3869 | 311.1298 | 0
2400 | 844.1672 | 2.1273 | 39.8329 | 93.4281 | 83.6712 | 6.0624 | 78.9394 | 6.5137 | 6.8321 | 29.0839 | 72.0119 | 7.5388 | 176.5478 | 98.572 | 248.7843 | 9.6069 | 53.667 | 12.7598 | 148 | 6.4558 | 117.3869 | 310.1147 | 0
2401 | 851.8066 | 2.3158 | 39.9339 | 92.4736 | 81.6979 | 7.9371 | 78.7162 | 6.8646 | 8.3984 | 25.7337 | 70.9249 | 7.371 | 174.6124 | 100.4392 | 247.3083 | 9.6739 | 53.6645 | 12.7764 | 144 | 6.4558 | 117.3869 | 310.0835 | 0
2402 | 831.9227 | 1.6531 | 39.9734 | 92.2831 | 79.4888 | 10.0358 | 78.7806 | 7.0458 | 8.5 | 23.9282 | 70.3572 | 7.221 | 174.8371 | 103.0841 | 239.9143 | 9.5687 | 53.6374 | 12.9429 | 167 | 6.4558 | 117.3869 | 307.3909 | 0
2403 | 823.0033 | 1.5451 | 39.9788 | 93.04 | 78.9267 | 10.5698 | 78.8627 | 6.8213 | 7.1 | 23.7496 | 70.1841 | 7.2405 | 167.742 | 101.8068 | 233.9303 | 9.5938 | 53.6742 | 12.9703 | 146 | 6.4558 | 117.3869 | 303.6337 | 0
2404 | 807.2182 | 1.9189 | 40.0534 | 92.8514 | 80.3219 | 9.2443 | 78.6727 | 6.8735 | 8.9136 | 23.9673 | 70.5561 | 7.4172 | 159.1408 | 97.1329 | 235.4243 | 9.6116 | 54.6973 | 12.682 | 139 | 6.4558 | 117.3869 | 302.6204 | 0
2405 | 800.0872 | 2.8165 | 39.9574 | 91.4066 | 82.796 | 6.8939 | 78.5751 | 6.8559 | 10.7825 | 24.5639 | 70.0592 | 6.9884 | 157.8497 | 91.6808 | 235.9524 | 9.4728 | 56.3544 | 12.5015 | 128 | 6.4558 | 117.3869 | 301.2655 | 0
2406 | 805.1195 | 2.5118 | 39.8844 | 89.8953 | 83.4062 | 6.3142 | 78.3429 | 6.5683 | 9.3385 | 24.6874 | 67.7914 | 5.4281 | 156.5194 | 88.6638 | 228.7755 | 9.2057 | 55.8921 | 12.1148 | 123 | 6.4558 | 117.3869 | 294.7338 | 0
2407 | 820.2585 | 1.3963 | 39.7462 | 89.7936 | 83.7152 | 6.0207 | 77.8976 | 6.386 | 6.7421 | 23.1649 | 66.0497 | 4.492 | 155.6342 | 90.4423 | 220.894 | 9.0698 | 53.9385 | 11.977 | 138 | 6.4558 | 117.3869 | 287.1525 | 0.15478
2408 | 828.6179 | 1.1434 | 39.6536 | 90.8004 | 83.4818 | 6.2424 | 79.6168 | 5.6783 | 5.7915 | 26.819 | 68.1052 | 4.5051 | 155.5134 | 92.642 | 219.7694 | 9.0004 | 53.0809 | 12.4941 | 151 | 6.4558 | 117.3869 | 286.3473 | 0.26567
2409 | 836.3485 | 1.1844 | 39.5113 | 91.1398 | 82.4738 | 7.2 | 87.2402 | 4.3254 | 5.6732 | 41.7553 | 71.8086 | 6.9253 | 160.8536 | 92.3882 | 214.7986 | 8.4753 | 52.9412 | 12.732 | 209 | 6.4558 | 117.3869 | 281.2126 | 0.29707
2410 | 854.8944 | 1.757 | 39.362 | 92.3661 | 82.6822 | 7.002 | 90.1586 | 3.9759 | 8.0051 | 56.9892 | 75.3373 | 9.0903 | 182.4301 | 94.5023 | 201.8046 | 8.3171 | 52.9865 | 12.7209 | 159 | 6.4558 | 117.3869 | 269.9822 | 0.2867
2411 | 880.0391 | 2.0592 | 39.362 | 93.0309 | 83.602 | 6.1282 | 83.7794 | 4.2052 | 12.8302 | 63.1083 | 84.6638 | 6.7318 | 213.3361 | 101.6774 | 194.0027 | 8.2483 | 53.5282 | 12.7272 | 176 | 6.4558 | 117.3869 | 262.1939 | 0.23811
2412 | 902.6134 | 1.675 | 39.362 | 93.6806 | 83.9634 | 5.7848 | 75.557 | 3.3276 | 15.5233 | 61.7183 | 101.5052 | 4.3915 | 229.7551 | 116.7179 | 196.8172 | 8.1767 | 55.3535 | 12.7652 | 182 | 6.4558 | 117.3869 | 255.3838 | 0.24947
2413 | 899.1485 | 1.5973 | 39.3616 | 95.5979 | 84.0989 | 5.6561 | 80.9381 | 3.0966 | 16.2081 | 56.9223 | 117.9105 | 4.4036 | 234.215 | 136.1691 | 207.6989 | 8.318 | 57.7182 | 12.7438 | 184 | 6.4558 | 117.3869 | 252.889 | 0.2444
2414 | 889.4025 | 1.553 | 39.225 | 95.1176 | 84.0972 | 5.6577 | 103.7995 | 3.8104 | 16.7229 | 53.8148 | 121.3643 | 7.2134 | 235.7405 | 144.61 | 225.9101 | 8.2729 | 57.5806 | 12.7406 | 165 | 6.4558 | 117.3869 | 253.0896 | 0.1827
2415 | 884.0842 | 1.7022 | 39.2058 | 94.9186 | 84.041 | 5.7111 | 104.3218 | 3.3691 | 16.641 | 49.615 | 109.7413 | 9.6709 | 230.2724 | 145.2212 | 243.4695 | 8.3494 | 55.426 | 12.7841 | 157 | 6.4558 | 117.3869 | 250.1235 | 0.17316
2416 | 880.5655 | 1.6322 | 39.1155 | 96.032 | 83.9974 | 5.7526 | 84.0134 | 3.5576 | 16.438 | 39.9018 | 99.1304 | 7.4009 | 222.5341 | 148.2352 | 243.5514 | 8.2684 | 54.0344 | 12.7847 | 168 | 6.4558 | 117.3869 | 246.1032 | 0.12075
2417 | 871.4201 | 1.3902 | 38.9215 | 95.642 | 82.859 | 6.8341 | 77.0765 | 4.7229 | 16.5081 | 30.782 | 95.7177 | 4.8942 | 218.3267 | 138.2933 | 238.3105 | 8.2756 | 53.5297 | 12.9032 | 162 | 6.4558 | 117.3869 | 244.4541 | 0.07343
2418 | 865.196 | 1.55 | 38.9158 | 93.7158 | 82.1024 | 7.5528 | 88.0948 | 5.4013 | 16.4904 | 28.2807 | 93.3037 | 4.3601 | 212.8702 | 116.8801 | 252.6404 | 8.302 | 53.2661 | 13.1814 | 127 | 6.4558 | 117.3869 | 243.5165 | 0.028613
2419 | 851.6372 | 2.6368 | 39.003 | 91.9155 | 82.6122 | 7.0685 | 96.8254 | 4.8404 | 13.9352 | 28.1431 | 88.9194 | 4.4438 | 197.5909 | 107.6855 | 273.7195 | 8.2612 | 52.8679 | 13.3537 | 133 | 6.4558 | 117.3869 | 243.9212 | 0.0016836
2420 | 840.2433 | 4.1368 | 39.4068 | 93.1315 | 82.4101 | 7.2605 | 85.4801 | 4.0741 | 9.109 | 27.5895 | 81.9957 | 6.0401 | 187.156 | 108.4146 | 278.7372 | 8.5733 | 52.6118 | 13.3126 | 131 | 6.4558 | 117.3869 | 252.6286 | 0
2421 | 820.2107 | 4.0047 | 39.7434 | 94.0511 | 82.6568 | 7.0262 | 77.1821 | 4.5051 | 6.8507 | 28.1311 | 76.6007 | 7.5033 | 186.2874 | 106.605 | 264.644 | 8.7699 | 53.139 | 13.2885 | 131 | 6.4558 | 117.3869 | 262.4452 | 0
2422 | 796.0555 | 3.0281 | 39.6896 | 93.4446 | 83.6959 | 6.039 | 77.1606 | 4.6223 | 6.8773 | 27.1008 | 74.5553 | 7.4256 | 180.9311 | 103.4247 | 248.0151 | 8.7647 | 53.5952 | 12.8871 | 123 | 6.4558 | 117.3869 | 260.0084 | 0
2423 | 788.3197 | 1.9219 | 39.6249 | 93.1693 | 84.0821 | 5.6721 | 77.2596 | 4.612 | 6.7248 | 24.533 | 73.1703 | 7.3318 | 174.0579 | 102.0237 | 240.1401 | 9.0685 | 53.6734 | 12.3187 | 114 | 6.4558 | 117.3869 | 253.2023 | 0
2424 | 797.084 | 1.3102 | 39.7291 | 92.7514 | 83.4688 | 6.2547 | 77.5913 | 4.7339 | 6.6806 | 23.0078 | 72.0344 | 7.419 | 168.8658 | 100.4826 | 235.9477 | 9.4205 | 53.8669 | 12.2869 | 111 | 6.4558 | 117.3869 | 253.4783 | 0
2425 | 802.6227 | 1.3435 | 38.7872 | 92.3734 | 83.6212 | 6.11 | 77.5868 | 4.9634 | 6.7189 | 22.2374 | 71.4912 | 7.4703 | 159.6945 | 97.4094 | 225.0164 | 9.3674 | 53.8637 | 12.2545 | 107 | 6.4558 | 117.3869 | 255.4454 | 0
2426 | 792.152 | 1.3174 | 37.7818 | 92.2148 | 84.0305 | 5.7211 | 77.2358 | 5.1018 | 6.6957 | 22.0545 | 71.524 | 7.828 | 153.188 | 96.1391 | 210.5675 | 9.3581 | 53.6339 | 12.1152 | 120 | 6.4558 | 117.3869 | 256.5891 | 0
2427 | 784.1079 | 1.186 | 37.7818 | 92.7996 | 84.0493 | 5.7032 | 78.0041 | 4.9963 | 6.7995 | 23.9846 | 72.2175 | 8 | 152.0402 | 97.2671 | 203.2211 | 9.6355 | 53.5602 | 12.1287 | 103 | 6.4558 | 117.3869 | 261.8265 | 0
2428 | 784.1714 | 1.6828 | 36.3675 | 93.6284 | 83.3807 | 6.3384 | 78.2047 | 5.1108 | 6.7498 | 30.4224 | 72.7966 | 7.9603 | 150.9742 | 95.3269 | 202.6383 | 9.6426 | 54.6353 | 12.1566 | 100 | 6.4558 | 117.3869 | 281.1614 | 0
2429 | 792.1118 | 3.0383 | 57.7213 | 92.749 | 81.8924 | 7.7523 | 77.8378 | 5.0983 | 6.642 | 37.6585 | 72.6621 | 8.6015 | 160.7173 | 98.8928 | 206.2631 | 9.466 | 56.3814 | 12.2488 | 106 | 6.4558 | 117.3869 | 309.7724 | 0
2430 | 818.3707 | 6.6711 | 77.9952 | 94.2948 | 80.5334 | 9.0433 | 89.2654 | 5.2751 | 6.6638 | 48.1038 | 82.8124 | 13.8453 | 174.0125 | 129.1785 | 222.4228 | 13.0244 | 56.5298 | 12.2814 | 201 | 6.4558 | 117.3869 | 350.296 | 0
2431 | 882.3707 | 11.1547 | 77.9952 | 103.5822 | 78.7892 | 10.7003 | 115.7038 | 5.8916 | 9.0293 | 68.098 | 113.3462 | 26.1727 | 201.5793 | 182.3817 | 282.1797 | 23.7484 | 58.4342 | 13.0723 | 274 | 6.4558 | 117.3869 | 416.1524 | 0.15477
2432 | 981.128 | 13.2307 | 77.9952 | 117.1795 | 76.9002 | 12.4949 | 137.7141 | 6.7173 | 17.3621 | 83.1589 | 147.2804 | 33.8624 | 271.7019 | 232.8884 | 389.0942 | 33.1358 | 65.9732 | 15.3004 | 281 | 6.4558 | 117.3869 | 479.6166 | 0.26566
2433 | 1058.4309 | 9.2036 | 90.6245 | 129.3026 | 76.6128 | 12.7679 | 152.8593 | 7.1786 | 24.5653 | 87.9679 | 168.7548 | 34.9757 | 324.0658 | 272.4427 | 490.7893 | 36.7147 | 75.6502 | 16.6272 | 310 | 6.4558 | 117.3869 | 514.1641 | 0.29708
2434 | 1092.7068 | 3.9853 | 103.3536 | 134.0483 | 75.8375 | 13.5045 | 156.7542 | 6.6683 | 26.1408 | 92.3486 | 177.0875 | 36.6678 | 355.5866 | 298.2043 | 551.3244 | 38.859 | 83.2737 | 17.23 | 345 | 6.4558 | 117.3869 | 526.2816 | 0.2867
2435 | 1117.4754 | 4.1805 | 107.7197 | 134.5853 | 75.6758 | 13.6581 | 156.7381 | 5.7249 | 25.6096 | 95.3643 | 177.8543 | 34.2625 | 385.6045 | 308.9515 | 570.9333 | 39.7356 | 87.1947 | 18.0258 | 343 | 6.4558 | 117.3869 | 531.1314 | 0.24698
2436 | 1128.8576 | 6.0372 | 110.7676 | 134.8163 | 76.7537 | 12.6341 | 171.913 | 5.625 | 22.7347 | 94.3904 | 177.3571 | 33.228 | 395.1157 | 308.9268 | 570.1287 | 40.5481 | 87.7217 | 18.2667 | 384 | 6.4558 | 117.3869 | 536.885 | 0.24948
2437 | 1136.7819 | 7.7605 | 108.9009 | 139.4364 | 75.9294 | 13.4172 | 174.2523 | 6.3185 | 20.6504 | 91.2755 | 178.5224 | 38.6072 | 405.3955 | 303.8892 | 567.6336 | 41.9573 | 86.5367 | 18.6099 | 329 | 6.4558 | 117.3869 | 538.4502 | 0.24441
2438 | 1173.0688 | 5.7669 | 106.8643 | 142.7675 | 75.025 | 14.2763 | 172.9546 | 5.6598 | 23.2771 | 90.6767 | 182.403 | 41.7657 | 414.4159 | 309.239 | 560.9577 | 40.806 | 85.8587 | 18.8647 | 344 | 6.4558 | 117.3869 | 532.7842 | 0.18272
2439 | 1162.5865 | 4.4834 | 105.2912 | 136.4758 | 75.5276 | 13.7989 | 182.9999 | 5.0734 | 24.185 | 90.5519 | 183.189 | 39.2696 | 413.1918 | 316.0414 | 544.7914 | 38.5098 | 85.998 | 18.7518 | 288 | 6.4558 | 117.3869 | 511.7039 | 0.17318
2440 | 1111.2493 | 4.708 | 103.7907 | 127.5179 | 80.2425 | 9.3197 | 179.7638 | 4.2945 | 19.0902 | 84.5315 | 178.3662 | 33.8097 | 403.2073 | 303.0291 | 509.7104 | 30.1744 | 84.0678 | 18.2115 | 276 | 6.4558 | 117.3869 | 456.7075 | 0.12077
2441 | 1052.875 | 4.085 | 98.2978 | 115.8239 | 82.4268 | 7.2446 | 166.5135 | 2.8827 | 15.6202 | 69.5746 | 167.0271 | 29.6362 | 384.618 | 254.8271 | 442.3114 | 16.1906 | 77.9592 | 17.0774 | 244 | 6.4558 | 117.3869 | 377.921 | 0.073437
2442 | 990.6555 | 3.3227 | 94.2531 | 103.277 | 83.2549 | 6.458 | 146.4119 | 3.152 | 15.2687 | 49.2642 | 141.652 | 22.4143 | 344.3364 | 184.355 | 367.9083 | 9.7202 | 70.6415 | 15.7824 | 227 | 6.4558 | 117.3869 | 306.6724 | 0.028617
2443 | 946.5978 | 2.8343 | 75.6167 | 96.5303 | 84.0884 | 5.6661 | 117.4566 | 3.6289 | 12.7132 | 32.2616 | 110.9613 | 10.6047 | 288.202 | 139.8118 | 327.4417 | 9.5098 | 64.5706 | 14.9861 | 197 | 6.4558 | 117.3869 | 257.7 | 0.0016836
2444 | 910.6398 | 3.4355 | 57.9995 | 93.8933 | 83.4815 | 6.2427 | 88.7434 | 3.6874 | 8.5987 | 23.8988 | 97.5271 | 5.6476 | 256.3236 | 129.0732 | 319.6496 | 8.9203 | 59.0949 | 14.1742 | 185 | 6.4558 | 117.3869 | 235.0975 | 0
2445 | 872.0318 | 3.5873 | 48.531 | 93.157 | 83.6285 | 6.103 | 78.3048 | 3.9253 | 7.2593 | 23.6518 | 97.1261 | 7.0575 | 239.0322 | 124.8449 | 312.9067 | 8.9505 | 55.9393 | 13.3826 | 178 | 6.4558 | 117.3869 | 234.6968 | 0
2446 | 837.9118 | 2.8961 | 39.4654 | 92.1254 | 83.4099 | 6.3107 | 80.7668 | 4.1787 | 7.7633 | 24.6923 | 91.7092 | 7.6092 | 214.0636 | 117.2104 | 282.831 | 9.0168 | 55.4791 | 13.0347 | 138 | 6.4558 | 117.3869 | 237.8203 | 0
2447 | 817.8975 | 2.0439 | 39.4654 | 91.2696 | 83.6514 | 6.0813 | 80.9507 | 4.3788 | 7.4827 | 23.6915 | 82.4603 | 7.6693 | 198.1317 | 110.582 | 252.2395 | 9.4491 | 55.4646 | 12.8454 | 121 | 6.4558 | 117.3869 | 237.3852 | 0
2448 | 821.1622 | 1.4125 | 39.3629 | 91.1005 | 83.486 | 6.2384 | 80.8371 | 4.2991 | 7.208 | 22.4289 | 77.9789 | 7.6364 | 186.8473 | 105.4317 | 238.5886 | 9.8725 | 55.2698 | 12.952 | 109 | 6.4558 | 117.3869 | 234.9592 | 0
2449 | 811.0851 | 1.2033 | 39.3159 | 91.0373 | 83.6407 | 6.0914 | 80.8056 | 4.1674 | 7.0437 | 21.4424 | 78.4801 | 7.6548 | 182.4629 | 99.8364 | 231.2778 | 9.8165 | 54.9095 | 12.7352 | 105 | 6.4558 | 117.3869 | 229.6706 | 0
2450 | 786.4218 | 1.3039 | 39.3653 | 91.8981 | 84.0546 | 5.6982 | 81.0494 | 4.3013 | 6.945 | 21.2117 | 82.0339 | 7.6346 | 179.7372 | 95.7801 | 225.7224 | 9.8653 | 54.2086 | 12.4287 | 124 | 6.4558 | 117.3869 | 226.5984 | 0
2451 | 782.7259 | 1.27 | 39.3653 | 91.7372 | 82.2545 | 7.4084 | 81.4471 | 4.9041 | 7.0978 | 23.3034 | 85.429 | 7.6193 | 181.2025 | 92.7684 | 223.0031 | 9.7807 | 53.9399 | 12.2044 | 100 | 6.4558 | 117.3869 | 226.0247 | 0
2452 | 790.8493 | 1.9175 | 47.954 | 91.0412 | 82.2985 | 7.3665 | 81.0321 | 5.0832 | 7.271 | 30.1178 | 84.9809 | 7.6258 | 181.6517 | 89.6225 | 223.4962 | 9.7269 | 55.005 | 11.8912 | 99 | 6.4558 | 117.3869 | 237.3856 | 0
2453 | 810.5865 | 3.0904 | 56.2089 | 90.1978 | 82.417 | 7.254 | 80.9542 | 4.9063 | 7.3957 | 37.9445 | 81.1489 | 8.6493 | 173.2867 | 95.1369 | 226.9646 | 9.6257 | 56.5554 | 11.84 | 106 | 6.4558 | 117.3869 | 264.6826 | 0
2454 | 839.7565 | 3.9835 | 56.2089 | 91.5412 | 81.4255 | 8.1959 | 90.5446 | 4.9849 | 7.1626 | 49.2931 | 83.2262 | 14.9347 | 189.8716 | 123.1939 | 237.3948 | 13.5503 | 56.694 | 11.6689 | 205 | 6.4558 | 117.3869 | 305.821 | 0.10394
2455 | 903.67 | 5.5637 | 79.3077 | 98.2727 | 78.1449 | 11.3124 | 114.3306 | 5.8619 | 8.698 | 70.1737 | 104.7288 | 25.1055 | 227.794 | 177.5263 | 280.3179 | 25.2758 | 58.9789 | 12.4255 | 241 | 6.4558 | 117.3869 | 373.7969 | 0.20705
2456 | 1008.6487 | 7.0831 | 104.7516 | 110.916 | 75.4402 | 13.8818 | 135.8503 | 6.9782 | 15.7894 | 85.2052 | 139.9672 | 28.976 | 276.9338 | 240.5142 | 378.8135 | 34.7617 | 67.2288 | 14.1757 | 292 | 6.4558 | 117.3869 | 460.7125 | 0.29961
2457 | 1096.6444 | 10.3045 | 108.0668 | 125.1315 | 75.5034 | 13.8219 | 149.3814 | 6.4792 | 22.0976 | 88.5802 | 168.1931 | 32.2291 | 341.4772 | 290.0444 | 497.2199 | 38.5435 | 77.069 | 15.3885 | 375 | 6.4558 | 117.3869 | 523.9873 | 0.32025
2458 | 1146.0399 | 15.6591 | 108.0668 | 132.8551 | 75.5381 | 13.7889 | 158.4399 | 6.1444 | 24.3084 | 93.5128 | 179.3825 | 39.8944 | 383.4191 | 320.9009 | 573.5943 | 40.5162 | 84.0454 | 16.5383 | 380 | 6.4558 | 117.3869 | 538.0454 | 0.31646
2459 | 1166.3904 | 15.144 | 110.8033 | 134.8559 | 74.5454 | 14.7319 | 172.3489 | 6.3344 | 25.1356 | 100.731 | 180.3728 | 41.5291 | 410.7306 | 337.8736 | 597.7983 | 38.8516 | 87.3879 | 17.5844 | 352 | 6.4558 | 117.3869 | 533.5414 | 0.29692
2460 | 1177.6759 | 8.5839 | 113.5003 | 134.3689 | 75.1754 | 14.1335 | 190.3977 | 5.244 | 22.6803 | 101.997 | 178.8487 | 39.2645 | 418.6586 | 337.4429 | 591.0374 | 38.678 | 86.6162 | 18.2172 | 372 | 6.4558 | 117.3869 | 523.5707 | 0.3041
2461 | 1201.0289 | 4.3661 | 113.5003 | 139.134 | 76.0397 | 13.3124 | 197.071 | 4.3203 | 20.1275 | 97.2087 | 179.6475 | 39.2911 | 406.0707 | 327.801 | 574.0038 | 40.841 | 84.8506 | 18.7571 | 290 | 6.4558 | 117.3869 | 501.0772 | 0.32233
2462 | 1199.4929 | 4.0697 | 107.2017 | 145.5529 | 74.8469 | 14.4455 | 195.7504 | 4.3769 | 22.4365 | 95.4205 | 184.7322 | 39.3749 | 392.9109 | 325.9203 | 565.6066 | 41.3225 | 85.1353 | 18.8696 | 296 | 6.4558 | 117.3869 | 485.0199 | 0.32547
2463 | 1156.1535 | 4.4681 | 101.1311 | 142.2014 | 74.0278 | 15.2236 | 196.3935 | 4.0366 | 22.9485 | 95.4955 | 187.4804 | 38.5964 | 402.5024 | 326.1362 | 565.8626 | 39.5949 | 84.7796 | 18.9448 | 281 | 6.4558 | 117.3869 | 471.8155 | 0.3231
2464 | 1116.5893 | 4.5094 | 101.1311 | 134.2128 | 78.322 | 11.1442 | 194.3866 | 3.0902 | 18.8353 | 86.8247 | 184.7092 | 35.1646 | 398.4917 | 315.1379 | 544.5182 | 30.7814 | 82.3672 | 18.6801 | 254 | 6.4558 | 117.3869 | 429.5805 | 0.24831
2465 | 1058.7283 | 3.4502 | 101.1311 | 121.2211 | 82.2165 | 7.4444 | 184.0935 | 2.4031 | 16.267 | 70.9907 | 170.9673 | 33.0812 | 383.1711 | 271.2047 | 469.07 | 16.3154 | 78.1556 | 17.147 | 226 | 6.4558 | 117.3869 | 354.3559 | 0.23458
2466 | 998.3932 | 2.6899 | 101.1311 | 106.8744 | 83.6151 | 6.1157 | 163.0799 | 2.2505 | 16.9951 | 53.4061 | 139.7163 | 29.7296 | 355.0647 | 207.5146 | 375.4422 | 10.6801 | 73.9871 | 15.2867 | 202 | 6.4558 | 117.3869 | 286.6714 | 0.16422
2467 | 964.2148 | 2.7999 | 71.0561 | 98.2732 | 84.1067 | 5.6488 | 133.0619 | 2.8865 | 16.0443 | 34.7872 | 107.4113 | 15.3056 | 311.5174 | 167.9818 | 322.6167 | 10.1566 | 72.3136 | 12.1911 | 175 | 6.4558 | 117.3869 | 247.0814 | 0.03665
2468 | 926.5321 | 3.1229 | 43.0694 | 94.0477 | 84.0232 | 5.728 | 101.4831 | 3.213 | 11.8511 | 24.7276 | 95.1857 | 9.6382 | 271.7961 | 153.1087 | 291.4357 | 8.9114 | 69.8852 | 7.563 | 171 | 6.4558 | 117.3869 | 228.3914 | 0
2469 | 890.8602 | 3.3427 | 43.0694 | 93.311 | 83.4728 | 6.2509 | 83.794 | 3.6362 | 9.2602 | 26.8541 | 95.2825 | 15.8037 | 240.1679 | 142.4355 | 247.3061 | 9.1245 | 65.6254 | 5.2029 | 167 | 6.4558 | 117.3869 | 228.1942 | 0
2470 | 851.6935 | 2.9094 | 43.0694 | 92.2452 | 83.6443 | 6.088 | 85.7264 | 3.5808 | 8.4313 | 29.8729 | 92.2433 | 14.3074 | 210.8874 | 131.8683 | 230.0857 | 9.1928 | 61.6361 | 5.248 | 156 | 6.4558 | 117.3869 | 232.2882 | 0
2471 | 823.634 | 1.8488 | 43.0694 | 91.5147 | 83.468 | 6.2555 | 85.8781 | 3.2109 | 8.6063 | 27.8866 | 86.2484 | 8.9411 | 193.293 | 126.3011 | 238.5107 | 9.2376 | 58.6898 | 5.1811 | 134 | 6.4558 | 117.3869 | 231.0622 | 0
2472 | 823.7778 | 1.4262 | 43.0694 | 92.0863 | 83.6735 | 6.0602 | 85.9585 | 2.9865 | 8.342 | 24.1297 | 83.7566 | 7.3241 | 177.2303 | 128.399 | 241.0769 | 9.1925 | 57.7948 | 5.0494 | 120 | 6.4558 | 117.3869 | 228.9075 | 0
2473 | 810.8301 | 1.4633 | 43.0694 | 91.521 | 84.0087 | 5.7418 | 85.9884 | 3.5129 | 7.3205 | 21.7504 | 84.7795 | 7.2919 | 173.383 | 128.7315 | 239.8914 | 9.1751 | 57.5859 | 5.6597 | 112 | 6.4558 | 117.3869 | 230.9197 | 0
2474 | 791.2002 | 1.3924 | 43.0694 | 90.6135 | 83.4276 | 6.2938 | 86.0912 | 3.7971 | 6.9258 | 21.169 | 84.4428 | 7.3118 | 173.8697 | 121.1807 | 228.9975 | 9.2266 | 57.2373 | 5.7208 | 126 | 6.4558 | 117.3869 | 237.7859 | 0
2475 | 793.0898 | 1.2774 | 41.0076 | 90.5075 | 83.641 | 6.0911 | 85.9101 | 3.8032 | 6.9343 | 23.5995 | 83.5386 | 7.3049 | 166.7162 | 114.8611 | 219.0378 | 9.1913 | 57.1782 | 4.569 | 106 | 6.4558 | 117.3869 | 242.3172 | 0
2476 | 802.496 | 1.7388 | 42.6051 | 90.2486 | 84.0521 | 5.7006 | 85.8629 | 3.8861 | 7.055 | 30.5415 | 83.4653 | 7.2784 | 161.7991 | 113.1587 | 217.8241 | 9.1176 | 58.074 | 3.7984 | 106 | 6.4558 | 117.3869 | 248.4328 | 0
2477 | 813.0699 | 2.9851 | 46.087 | 90.037 | 82.8395 | 6.8525 | 86.1587 | 3.9873 | 6.8515 | 38.1645 | 81.5317 | 8.9677 | 162.4976 | 114.6478 | 217.781 | 8.9446 | 59.9748 | 3.4481 | 114 | 6.4558 | 117.3869 | 263.8979 | 0
2478 | 842.2209 | 4.25 | 68.3102 | 91.5058 | 80.8304 | 8.7612 | 95.6033 | 3.8092 | 6.9313 | 49.1552 | 82.804 | 15.7266 | 180.3602 | 135.7257 | 228.5902 | 12.988 | 60.0606 | 2.9955 | 170 | 6.4558 | 117.3869 | 296.448 | 0.015326
2479 | 922.0216 | 4.5539 | 89.1245 | 97.6668 | 76.5564 | 12.8215 | 115.9745 | 4.4175 | 9.8807 | 69.2284 | 104.0241 | 27.7175 | 214.1399 | 190.6662 | 280.1275 | 25.177 | 61.0927 | 8.3049 | 244 | 6.4558 | 117.3869 | 351.1461 | 0.046805
2480 | 1030.4226 | 4.0724 | 99.3894 | 111.5989 | 75.104 | 14.2012 | 133.7116 | 5.0547 | 16.8152 | 84.1914 | 142.7438 | 34.504 | 266.4962 | 250.9974 | 370.0212 | 36.1976 | 68.2475 | 14.5505 | 301 | 6.4558 | 117.3869 | 412.8864 | 0.10126
2481 | 1122.6948 | 4.029 | 110.6941 | 126.3646 | 76.47 | 12.9036 | 153.4525 | 5.4924 | 21.7552 | 90.9898 | 175.7784 | 36.7808 | 319.8321 | 289.1311 | 471.9243 | 41.0327 | 78.4655 | 16.1017 | 345 | 6.4558 | 117.3869 | 480.9762 | 0.13955
2482 | 1164.6843 | 5.8663 | 111.4684 | 133.5835 | 74.5744 | 14.7044 | 163.2409 | 6.0204 | 22.4839 | 102.4239 | 190.6471 | 40.9353 | 370.4467 | 312.5695 | 540.6209 | 43.1596 | 86.1808 | 17.3525 | 353 | 6.4558 | 117.3869 | 534.7115 | 0.17222
2483 | 1174.0664 | 9.273 | 112.8483 | 139.0415 | 74.9101 | 14.3855 | 170.3897 | 6.0164 | 22.0762 | 110.1861 | 189.6728 | 41.5758 | 401.1528 | 332.2467 | 562.8774 | 42.1879 | 89.2604 | 17.8652 | 338 | 6.4558 | 117.3869 | 548.3685 | 0.20218
2484 | 1172.0121 | 9.7178 | 114.1332 | 140.7642 | 76.7443 | 12.643 | 174.6439 | 5.6542 | 20.5473 | 106.8524 | 183.6162 | 40.305 | 397.7844 | 341.7725 | 557.1918 | 42.6976 | 88.661 | 18.2144 | 355 | 6.4558 | 117.3869 | 548.7516 | 0.26848
2485 | 1176.4653 | 6.5054 | 114.1332 | 140.4657 | 75.228 | 14.0835 | 168.5846 | 4.0662 | 19.822 | 102.1521 | 182.9261 | 40.2592 | 403.0003 | 336.0461 | 541.4141 | 43.1276 | 87.3668 | 18.4077 | 339 | 6.4558 | 117.3869 | 549.7538 | 0.21684
2486 | 1191.9955 | 4.6832 | 112.3511 | 143.9368 | 70.83 | 18.2616 | 169.3716 | 4.5211 | 20.7067 | 102.2131 | 185.8113 | 39.8984 | 413.8793 | 330.3386 | 534.7911 | 39.6551 | 87.1259 | 17.9998 | 306 | 6.4558 | 117.3869 | 544.2253 | 0.1819
2487 | 1168.0676 | 6.6876 | 111.0981 | 141.5327 | 71.9155 | 17.2304 | 172.9662 | 4.7353 | 20.8422 | 103.9981 | 186.6521 | 39.0473 | 408.8825 | 328.4944 | 536.8706 | 37.2081 | 87.4337 | 17.9154 | 267 | 6.4558 | 117.3869 | 529.3073 | 0.1555
2488 | 1116.519 | 6.3205 | 105.934 | 131.2181 | 77.874 | 11.5698 | 167.5947 | 4.3649 | 19.477 | 102.2578 | 184.1689 | 35.0119 | 402.2061 | 317.4895 | 521.7623 | 30.9203 | 86.6997 | 18.0859 | 245 | 6.4558 | 117.3869 | 497.623 | 0.12596
2489 | 1069.0003 | 3.8135 | 101.2616 | 117.3237 | 81.9355 | 7.7113 | 148.6636 | 3.3168 | 17.9291 | 89.7926 | 171.4004 | 33.1475 | 379.1568 | 271.6044 | 463.8127 | 18.5289 | 82.3783 | 17.4204 | 215 | 6.4558 | 117.3869 | 446.4761 | 0.081637
2490 | 1005.8367 | 2.8928 | 101.2616 | 105.0505 | 83.7381 | 5.9989 | 127.4668 | 2.7097 | 17.5607 | 63.0406 | 140.4467 | 27.6181 | 351.3748 | 203.3636 | 387.0717 | 11.3354 | 75.7497 | 16.3679 | 225 | 6.4558 | 117.3869 | 389.5001 | 0.03868
2491 | 970.8151 | 2.4804 | 86.1428 | 96.5303 | 84.0725 | 5.6812 | 125.5816 | 3.3973 | 14.9158 | 36.6144 | 105.4686 | 13.2812 | 292.8934 | 161.6687 | 328.5117 | 9.6521 | 69.938 | 13.4377 | 193 | 6.4558 | 117.3869 | 346.5924 | 0.0044717
2492 | 939.0785 | 3.7197 | 57.5761 | 92.9338 | 82.6478 | 7.0347 | 110.5184 | 3.2853 | 9.6942 | 25.9734 | 89.6924 | 6.8462 | 262.1481 | 148.3195 | 297.3175 | 9.2955 | 64.9759 | 8.3105 | 176 | 6.4558 | 117.3869 | 327.0416 | 0
2493 | 888.7113 | 4.753 | 41.5292 | 92.7591 | 82.7724 | 6.9163 | 87.5847 | 2.9625 | 7.3364 | 26.2632 | 87.9997 | 8.1926 | 228.4726 | 139.2016 | 288.6798 | 9.4512 | 61.2064 | 5.407 | 173 | 6.4558 | 117.3869 | 322.9133 | 0
2494 | 854.2793 | 3.5573 | 39.4042 | 91.3689 | 83.7618 | 5.9763 | 84.5728 | 3.0093 | 7.3091 | 26.0551 | 83.165 | 8.5611 | 219.0754 | 126.9669 | 274.3767 | 9.489 | 59.4296 | 5.2439 | 149 | 6.4558 | 117.3869 | 319.8919 | 0
2495 | 828.1759 | 1.8195 | 39.5463 | 90.7767 | 84.0072 | 5.7433 | 84.4837 | 3.5115 | 7.2768 | 23.473 | 74.4384 | 8.3867 | 198.9054 | 115.6683 | 240.3396 | 9.5305 | 59.1079 | 9.7118 | 138 | 6.4558 | 117.3869 | 314.8105 | 0
2496 | 815.0071 | 1.1837 | 39.5466 | 90.4276 | 83.3778 | 6.3411 | 84.3762 | 3.6746 | 7.0953 | 22.3007 | 70.0412 | 8.2606 | 196.8563 | 109.5936 | 219.5857 | 9.4261 | 59.1483 | 13.0369 | 117 | 6.4558 | 117.3869 | 309.4692 | 0
2497 | 803.345 | 1.129 | 39.5665 | 89.8399 | 83.0191 | 6.6819 | 84.556 | 3.9255 | 6.7461 | 22.5521 | 70.1829 | 8.3046 | 180.0222 | 104.9094 | 223.4813 | 9.4694 | 59.2029 | 12.1049 | 108 | 6.4558 | 117.3869 | 305.5052 | 0
2498 | 790.8089 | 1.1108 | 39.5076 | 89.6816 | 83.7565 | 5.9814 | 84.4671 | 4.1034 | 6.7873 | 22.7761 | 70.8871 | 8.3344 | 167.3349 | 99.6759 | 232.1012 | 9.5641 | 59.2882 | 11.7501 | 123 | 6.4558 | 117.3869 | 301.1764 | 0
2499 | 797.7363 | 1.2167 | 39.4801 | 90.9326 | 84.0475 | 5.7049 | 84.4283 | 4.008 | 6.9384 | 24.6111 | 71.5489 | 8.6509 | 164.886 | 96.844 | 229.3785 | 9.5205 | 59.3722 | 12.0671 | 105 | 6.4558 | 117.3869 | 292.5968 | 0
2500 | 806.4683 | 1.8697 | 39.4761 | 90.8215 | 83.449 | 6.2736 | 84.0122 | 3.9757 | 6.8475 | 31.2622 | 71.5834 | 8.6167 | 157.8953 | 94.9742 | 219.3133 | 9.4435 | 60.5708 | 11.9187 | 101 | 6.4558 | 117.3869 | 293.4878 | 0
2501 | 821.1106 | 2.8121 | 52.4784 | 90.2974 | 82.5691 | 7.1095 | 84.0865 | 4.1347 | 6.7741 | 39.7861 | 72.3862 | 9.8236 | 158.2181 | 99.9908 | 219.9844 | 9.2246 | 62.4868 | 11.71 | 109 | 6.4558 | 117.3869 | 313.7832 | 0
2502 | 855.1238 | 3.7239 | 63.6973 | 91.5782 | 80.7095 | 8.876 | 92.4702 | 3.9626 | 6.7273 | 52.2413 | 79.5965 | 15.8073 | 174.2813 | 127.3002 | 237.1718 | 13.098 | 62.082 | 11.8728 | 194 | 6.4558 | 117.3869 | 346.1674 | 0.017141
2503 | 922.6284 | 7.9861 | 83.774 | 95.8323 | 78.0202 | 11.4309 | 113.9355 | 4.586 | 8.8402 | 74.9853 | 104.0127 | 29.4061 | 210.2267 | 172.7232 | 293.573 | 24.6657 | 62.5626 | 13.4998 | 260 | 6.4558 | 117.3869 | 404.2355 | 0.052612
2504 | 1013.4915 | 9.5345 | 100.9475 | 108.9086 | 76.6414 | 12.7408 | 132.1485 | 5.9246 | 16.2501 | 87.7194 | 144.6628 | 39.1612 | 280.3188 | 222.405 | 392.6355 | 34.1494 | 69.1101 | 15.3892 | 296 | 6.4558 | 117.3869 | 479.7405 | 0.099956
2505 | 1071.8117 | 7.2497 | 105.9311 | 121.1073 | 76.0736 | 13.2802 | 147.6555 | 6.3457 | 21.984 | 83.7781 | 177.0957 | 37.7916 | 328.6867 | 266.8726 | 479.5889 | 37.4873 | 78.5673 | 15.9128 | 361 | 6.4558 | 117.3869 | 529.538 | 0.157
2506 | 1125.6882 | 7.2237 | 110.4085 | 127.3698 | 72.9137 | 16.282 | 166.3949 | 5.9369 | 22.1499 | 86.5826 | 189.1162 | 32.6321 | 363.2843 | 296.6007 | 528.9246 | 40.3132 | 86.7894 | 16.6281 | 363 | 6.4558 | 117.3869 | 548.6892 | 0.11844
2507 | 1175.1487 | 7.3948 | 110.4085 | 130.4919 | 71.1681 | 17.9404 | 165.619 | 6.1136 | 19.4627 | 94.771 | 191.1543 | 31.6003 | 398.8817 | 312.1574 | 560.1426 | 42.261 | 91.1755 | 16.6017 | 357 | 6.4558 | 117.3869 | 554.4989 | 0.19095
2508 | 1194.0635 | 7.2592 | 110.4085 | 134.1541 | 74.2176 | 15.0434 | 169.5276 | 6.1016 | 19.2173 | 95.603 | 189.7949 | 35.6196 | 409.7074 | 316.1037 | 570.5464 | 42.507 | 91.242 | 16.4669 | 378 | 6.4558 | 117.3869 | 555.9437 | 0.26444
2509 | 1207.3816 | 6.1083 | 110.4085 | 138.8423 | 75.8664 | 13.477 | 183.1369 | 5.5993 | 20.4187 | 91.2641 | 191.9543 | 38.8806 | 405.2513 | 317.0031 | 563.6606 | 42.2112 | 90.2904 | 17.6496 | 357 | 6.4558 | 117.3869 | 554.8053 | 0.29521
2510 | 1205.6245 | 4.4824 | 111.0745 | 139.8581 | 75.4778 | 13.8462 | 174.3079 | 6.2838 | 19.2598 | 91.4847 | 196.0697 | 39.0149 | 405.6106 | 321.6433 | 573.3079 | 41.4576 | 90.5282 | 18.4701 | 313 | 6.4558 | 117.3869 | 542.5263 | 0.18021
2511 | 1176.7786 | 3.7639 | 102.035 | 138.0295 | 75.7186 | 13.6174 | 157.9087 | 5.4521 | 17.7275 | 96.6311 | 196.3687 | 35.796 | 424.4947 | 320.4899 | 577.743 | 38.9727 | 91.2609 | 18.5023 | 306 | 6.4558 | 117.3869 | 518.2401 | 0.12287
2512 | 1131.1276 | 3.7615 | 93.4034 | 133.6424 | 80.3815 | 9.1877 | 158.5356 | 5.083 | 16.36 | 96.6772 | 195.6018 | 30.769 | 408.0768 | 308.0095 | 532.2062 | 30.4837 | 89.8938 | 17.9717 | 290 | 6.4558 | 117.3869 | 475.2737 | 0.11565
2513 | 1068.4087 | 3.733 | 93.4034 | 117.7519 | 83.6452 | 6.0871 | 140.8174 | 4.2381 | 14.8533 | 84.9513 | 182.9676 | 30.1968 | 380.7844 | 263.7991 | 447.6394 | 16.1623 | 84.2576 | 16.4277 | 251 | 6.4558 | 117.3869 | 409.5162 | 0.13053
2514 | 1011.3823 | 2.9055 | 93.4034 | 100.3964 | 80.9646 | 8.6337 | 109.7614 | 2.8553 | 14.814 | 63.1503 | 149.1026 | 28.0821 | 334.962 | 195.1714 | 363.6674 | 8.3942 | 77.0788 | 15.0205 | 250 | 6.4558 | 117.3869 | 346.4784 | 0.16771
2515 | 967.0142 | 2.7898 | 93.4034 | 92.392 | 82.1472 | 7.5103 | 96.3953 | 3.4554 | 13.7273 | 44.283 | 113.2253 | 20.3203 | 292.5465 | 149.8723 | 302.4497 | 7.671 | 71.4536 | 14.4253 | 223 | 6.4558 | 117.3869 | 304.3573 | 0.048925
2516 | 914.3832 | 3.453 | 93.4034 | 89.9199 | 83.9744 | 5.7744 | 88.5348 | 3.8602 | 9.8 | 36.3665 | 97.5273 | 15.8661 | 250.5652 | 133.9927 | 263.7395 | 7.7395 | 66.2146 | 14.179 | 198 | 6.4558 | 117.3869 | 286.0591 | 0
2517 | 877.7307 | 3.5236 | 76.8024 | 90.4743 | 83.4718 | 6.2518 | 87.8854 | 4.0409 | 7.5199 | 35.4275 | 94.9165 | 14.476 | 225.2169 | 125.3642 | 242.7506 | 8.3364 | 62.5381 | 13.6769 | 178 | 6.4558 | 117.3869 | 287.1324 | 0
2518 | 856.6388 | 3.2353 | 63.1536 | 90.0994 | 83.7425 | 5.9947 | 87.3333 | 4.2741 | 7.5445 | 35.6361 | 90.6833 | 14.0356 | 221.6352 | 117.5231 | 239.7052 | 8.8426 | 61.654 | 12.9152 | 156 | 6.4558 | 117.3869 | 287.6345 | 0
2519 | 840.9638 | 2.2226 | 63.1422 | 88.8733 | 83.4398 | 6.2823 | 87.3078 | 4.4362 | 7.3089 | 34.636 | 84.239 | 14.1256 | 205.2459 | 110.0205 | 235.8725 | 8.8595 | 61.5701 | 12.3221 | 132 | 6.4558 | 117.3869 | 280.2763 | 0
2520 | 844.0151 | 1.2791 | 63.4503 | 88.4682 | 83.5872 | 6.1422 | 88.2599 | 4.3336 | 7.1347 | 34.4143 | 79.4362 | 13.9449 | 189.1369 | 104.1187 | 228.77 | 8.9551 | 61.2316 | 12.0901 | 122 | 6.4558 | 117.3869 | 272.5894 | 0
2521 | 837.6902 | 1.3822 | 63.6798 | 88.9615 | 84.0034 | 5.7469 | 88.0748 | 4.2667 | 7.162 | 35.8914 | 77.2132 | 13.7123 | 185.8368 | 101.0212 | 227.6068 | 8.9332 | 60.9483 | 12.725 | 111 | 6.4558 | 117.3869 | 268.6349 | 0
2522 | 819.4966 | 1.8981 | 63.2741 | 88.8688 | 83.428 | 6.2935 | 87.3019 | 4.2284 | 6.97 | 36.7675 | 76.654 | 12.0286 | 172.6104 | 97.5202 | 224.1496 | 8.7369 | 60.8406 | 13.4129 | 130 | 6.4558 | 117.3869 | 267.9249 | 0
2523 | 822.8135 | 1.9117 | 62.9661 | 88.5683 | 83.7002 | 6.0349 | 86.938 | 4.2759 | 6.9775 | 37.651 | 77.2837 | 10.7526 | 164.0212 | 94.1625 | 219.4108 | 8.2645 | 60.6171 | 12.966 | 119 | 6.4558 | 117.3869 | 267.4817 | 0
2524 | 828.3057 | 1.8813 | 64.2834 | 89.3336 | 84.0601 | 5.6929 | 86.509 | 4.1486 | 7.0955 | 43.1729 | 77.8697 | 10.8536 | 154.2725 | 92.4479 | 213.3268 | 8.0675 | 61.4763 | 12.5216 | 124 | 6.4558 | 117.3869 | 277.0797 | 0
2525 | 833.6837 | 2.7844 | 65.3955 | 90.2372 | 82.7585 | 6.9295 | 86.8036 | 4.0019 | 7.111 | 50.8191 | 77.6178 | 11.7042 | 154.8682 | 99.4978 | 212.9029 | 7.9761 | 63.3759 | 12.3456 | 124 | 6.4558 | 117.3869 | 301.5582 | 0
2526 | 881.0204 | 4.3217 | 72.2729 | 91.7763 | 80.9067 | 8.6887 | 95.8337 | 4.0951 | 7.4345 | 61.0037 | 82.673 | 16.3575 | 178.2562 | 129.7608 | 232.1452 | 12.2086 | 63.1678 | 11.9611 | 166 | 6.4558 | 117.3869 | 334.8778 | 0.0070562
2527 | 943.8945 | 5.204 | 95.1745 | 96.4789 | 77.4945 | 11.9303 | 114.9397 | 4.8505 | 8.9442 | 75.7036 | 106.5045 | 26.4948 | 209.3863 | 188.5003 | 279.0765 | 23.4614 | 64.9009 | 12.5952 | 243 | 6.4558 | 117.3869 | 384.9291 | 0.021434
2528 | 1033.0666 | 7.485 | 110.4825 | 109.533 | 75.4268 | 13.8946 | 132.9462 | 5.8926 | 14.4027 | 84.6042 | 145.1736 | 30.8665 | 264.9943 | 251.6521 | 367.6606 | 34.4524 | 73.942 | 14.0224 | 310 | 6.4558 | 117.3869 | 449.9345 | 0.041459
2529 | 1128.8762 | 8.5544 | 110.4825 | 124.0902 | 75.7713 | 13.5673 | 141.7558 | 5.9323 | 18.6377 | 84.6798 | 173.7427 | 31.973 | 314.0341 | 295.7833 | 477.0409 | 40.4479 | 84.1096 | 15.7488 | 362 | 6.4558 | 117.3869 | 506.6574 | 0.075293
2530 | 1170.9062 | 8.3809 | 110.4825 | 129.0246 | 75.6108 | 13.7199 | 143.3692 | 6.1069 | 19.6888 | 83.7639 | 183.8493 | 35.8862 | 354.3424 | 325.0162 | 549.4606 | 42.8586 | 91.4384 | 17.8255 | 358 | 6.4558 | 117.3869 | 554.086 | 0.11685
2531 | 1197.3971 | 9.6688 | 113.1441 | 129.0429 | 74.3005 | 14.9646 | 143.3371 | 6.8298 | 20.33 | 85.0415 | 185.8526 | 36.4608 | 390.7431 | 341.5559 | 575.8984 | 41.8663 | 95.1305 | 18.3355 | 320 | 6.4558 | 117.3869 | 596.4183 | 0.10511
2532 | 1195.9 | 8.6092 | 115.7357 | 131.5161 | 73.9196 | 15.3264 | 141.0116 | 6.9752 | 19.5465 | 85.5517 | 185.0392 | 37.3489 | 404.9007 | 345.5314 | 581.4716 | 41.6049 | 93.7288 | 17.743 | 358 | 6.4558 | 117.3869 | 616.2183 | 0.12619
2533 | 1186.9899 | 6.5439 | 115.7357 | 139.4143 | 73.5529 | 15.6749 | 135.9379 | 6.5065 | 18.7263 | 91.9614 | 184.822 | 38.6755 | 405.1437 | 343.9562 | 583.62 | 41.7627 | 92.5716 | 17.6238 | 313 | 6.4558 | 117.3869 | 615.0451 | 0.069392
2534 | 1173.6171 | 4.9748 | 112.7806 | 142.3135 | 74.3066 | 14.9588 | 132.9796 | 5.7826 | 19.9453 | 103.0198 | 186.1325 | 37.9985 | 408.2698 | 341.6148 | 582.5608 | 40.3825 | 92.7907 | 17.8293 | 291 | 6.4558 | 117.3869 | 610.5734 | 0.080684
2535 | 1151.4641 | 4.9493 | 110.1326 | 137.4774 | 76.1984 | 13.1616 | 129.9135 | 5.6229 | 19.9084 | 100.1262 | 185.2758 | 37.0566 | 406.2317 | 331.9152 | 568.5353 | 37.6609 | 91.3547 | 18.1076 | 277 | 6.4558 | 117.3869 | 591.6013 | 0.056398
2536 | 1112.1189 | 4.4536 | 81.6149 | 130.6818 | 80.1336 | 9.4232 | 118.6509 | 5.7043 | 16.865 | 85.2968 | 181.5197 | 35.4446 | 397.5064 | 306.8317 | 517.3442 | 25.0587 | 88.0095 | 18.0777 | 255 | 6.4558 | 117.3869 | 532.9672 | 0.033167
2537 | 1028.777 | 3.1243 | 56.2138 | 113.0916 | 83.2895 | 6.425 | 103.9194 | 4.7493 | 15.2293 | 68.7425 | 171.1692 | 33.7643 | 363.6851 | 255.7173 | 415.0753 | 11.9717 | 82.1621 | 16.9081 | 233 | 6.4558 | 117.3869 | 454.3254 | 0.029145
2538 | 964.8688 | 2.8001 | 56.2138 | 95.8919 | 84.0785 | 5.6755 | 95.1681 | 3.7364 | 16.2767 | 51.9136 | 143.897 | 25.4845 | 323.5144 | 190.055 | 323.0335 | 9.3055 | 75.2382 | 15.2509 | 222 | 6.4558 | 117.3869 | 388.1065 | 0.0065594
2539 | 922.2836 | 3.086 | 56.2138 | 91.281 | 84.7073 | 5.0781 | 89.3023 | 3.6266 | 14.7027 | 40.0723 | 109.046 | 13.0649 | 278.2265 | 152.2472 | 280.1256 | 8.092 | 68.6678 | 14.4785 | 218 | 6.4558 | 117.3869 | 336.8885 | 0.0021531
2540 | 899.5907 | 3.4904 | 56.2138 | 95.3044 | 83.7299 | 6.0066 | 86.5795 | 3.3668 | 9.7433 | 36.9228 | 89.229 | 8.9922 | 235.6164 | 147.097 | 260.6028 | 7.8483 | 63.1023 | 13.7525 | 210 | 6.4558 | 117.3869 | 312.9312 | 0
2541 | 870.8391 | 3.3065 | 56.2138 | 94.7929 | 82.4206 | 7.2505 | 85.7965 | 3.1651 | 7.5039 | 38.0418 | 82.239 | 9.9047 | 213.7392 | 147.3976 | 246.1919 | 7.9397 | 59.9733 | 12.8115 | 201 | 6.4558 | 117.3869 | 319.4128 | 0
2542 | 842.9532 | 3.0176 | 56.2138 | 90.8318 | 82.0927 | 7.562 | 84.8021 | 3.3058 | 7.2473 | 38.136 | 77.8444 | 10.0491 | 198.9901 | 139.7252 | 238.3194 | 7.9759 | 58.6644 | 12.445 | 182 | 6.4558 | 117.3869 | 326.5121 | 0
2543 | 828.2094 | 2.0802 | 48.4081 | 89.9183 | 83.3042 | 6.4111 | 83.902 | 3.6129 | 6.6999 | 37.1395 | 75.4889 | 10.1487 | 187.3843 | 125.9467 | 241.4888 | 8.0872 | 57.9729 | 12.3223 | 159 | 6.4558 | 117.3869 | 321.3171 | 0
2544 | 837.8538 | 1.448 | 41.7504 | 90.3532 | 84.0796 | 5.6745 | 83.4741 | 3.8662 | 6.8203 | 35.8823 | 74.8802 | 10.0084 | 199.1645 | 115.0186 | 242.2557 | 8.0801 | 57.7311 | 11.9644 | 149 | 6.4558 | 117.3869 | 313.7292 | 0
2545 | 840.6246 | 1.3641 | 41.3184 | 90.2258 | 84.0962 | 5.6586 | 83.543 | 3.866 | 6.8014 | 35.0411 | 75.0512 | 9.0232 | 197.5409 | 108.9059 | 235.9911 | 7.9843 | 57.85 | 11.6743 | 138 | 6.4558 | 117.3869 | 302.6086 | 0
2546 | 823.6499 | 1.24 | 40.7458 | 90.13 | 84.0527 | 5.7 | 83.1691 | 4.0567 | 6.696 | 34.6652 | 74.976 | 8.2268 | 180.3573 | 105.8877 | 230.6714 | 7.9432 | 57.9243 | 11.7421 | 156 | 6.4558 | 117.3869 | 284.7921 | 0
2547 | 818.9881 | 1.3232 | 41.5247 | 89.7205 | 84.0732 | 5.6806 | 82.9824 | 4.1277 | 6.7533 | 35.3464 | 74.7685 | 8.3844 | 167.6437 | 102.6569 | 229.4231 | 8.0113 | 57.673 | 11.9231 | 131 | 6.4558 | 117.3869 | 271.364 | 0
2548 | 821.1578 | 1.7105 | 42.3856 | 89.414 | 84.0154 | 5.7354 | 83.2942 | 3.9857 | 6.8495 | 38.805 | 74.8006 | 8.6309 | 170.1061 | 96.2056 | 223.7999 | 8.0774 | 58.2475 | 11.7867 | 128 | 6.4558 | 117.3869 | 269.69 | 0
2549 | 820.3402 | 2.5269 | 42.3856 | 89.1639 | 83.4049 | 6.3154 | 83.6732 | 3.9484 | 6.8342 | 43.485 | 74.2623 | 8.1812 | 164.6355 | 91.5277 | 212.4986 | 7.874 | 59.8623 | 11.5876 | 119 | 6.4558 | 117.3869 | 267.1725 | 0
2550 | 832.4656 | 3.1109 | 54.076 | 87.1552 | 83.6937 | 6.0411 | 84.7746 | 3.7135 | 6.7871 | 45.9953 | 72.9204 | 6.4782 | 166.6376 | 91.8637 | 200.2492 | 7.6492 | 59.7409 | 11.4162 | 125 | 6.4558 | 117.3869 | 261.2404 | 0.0042617
2551 | 848.0228 | 2.4333 | 64.0676 | 85.9361 | 83.9912 | 5.7585 | 93.8764 | 3.3084 | 7.8567 | 44.5617 | 76.1689 | 7.6857 | 163.5975 | 94.0546 | 195.0537 | 7.4326 | 57.6769 | 11.6277 | 128 | 6.4558 | 117.3869 | 260.3715 | 0.019504
2552 | 852.0614 | 1.5173 | 64.0676 | 85.9731 | 84.066 | 5.6874 | 98.7071 | 2.7662 | 10.7243 | 44.963 | 95.7235 | 12.7043 | 181.9033 | 98.1208 | 201.0433 | 7.4282 | 56.4129 | 12.2481 | 137 | 6.4558 | 117.3869 | 262.2423 | 0.03855
2553 | 879.097 | 1.472 | 75.435 | 86.3033 | 84.0711 | 5.6825 | 94.102 | 2.9104 | 10.4688 | 53.2632 | 126.4415 | 15.2709 | 195.173 | 107.9301 | 205.854 | 7.4828 | 56.3856 | 12.4687 | 160 | 6.4558 | 117.3869 | 270.1618 | 0.033386
2554 | 901.8578 | 1.8439 | 83.1927 | 86.5359 | 84.0334 | 5.7183 | 99.4887 | 3.4016 | 10.769 | 61.5547 | 141.9168 | 15.2222 | 206.5551 | 120.6178 | 212.7607 | 7.4287 | 56.5385 | 12.6329 | 172 | 6.4558 | 117.3869 | 281.3612 | 0.054741
2555 | 904.4585 | 5.5417 | 80.5262 | 86.3234 | 84.0565 | 5.6964 | 104.6356 | 3.2831 | 12.303 | 64.3588 | 130.3218 | 15.1771 | 219.0884 | 130.9194 | 222.8471 | 7.3273 | 57.2959 | 12.7781 | 196 | 6.4558 | 117.3869 | 278.7633 | 0.08387
2556 | 905.6925 | 8.3737 | 79.4676 | 86.6569 | 84.7197 | 5.0664 | 102.5762 | 3.009 | 13.7201 | 65.4528 | 108.1421 | 15.1997 | 222.5535 | 135.0656 | 222.0565 | 7.3466 | 59.9641 | 12.7496 | 199 | 6.4558 | 117.3869 | 267.5558 | 0.080966
2557 | 899.5747 | 8.1908 | 79.4676 | 87.1089 | 84.4387 | 5.3333 | 120.2999 | 2.3072 | 15.1812 | 67.508 | 96.8742 | 15.4167 | 224.23 | 138.9692 | 209.4965 | 7.4115 | 62.1502 | 12.7605 | 202 | 6.4558 | 117.3869 | 258.8972 | 0.080748
2558 | 882.9918 | 7.3788 | 65.0794 | 88.6212 | 84.0262 | 5.7252 | 135.2225 | 2.5104 | 15.608 | 68.0548 | 95.3815 | 16.4531 | 231.8644 | 144.4677 | 196.0745 | 7.4284 | 60.8548 | 12.805 | 200 | 6.4558 | 117.3869 | 251.0452 | 0.1465
2559 | 889.2771 | 3.9927 | 52.4994 | 90.2848 | 84.0178 | 5.7332 | 123.6555 | 3.0976 | 15.8622 | 58.4251 | 94.4285 | 15.0131 | 238.2098 | 139.4965 | 198.2624 | 7.345 | 59.8332 | 12.7385 | 212 | 6.4558 | 117.3869 | 247.6851 | 0.081856
2560 | 898.1396 | 2.0098 | 52.1825 | 89.7133 | 84.0402 | 5.7119 | 112.2914 | 2.4098 | 15.2163 | 39.9788 | 96.5788 | 8.9355 | 233.8065 | 130.1474 | 204.2302 | 7.3707 | 61.1467 | 12.8225 | 208 | 6.4558 | 117.3869 | 243.0851 | 0.053989
2561 | 900.3663 | 2.7222 | 52.9607 | 89.9024 | 84.0628 | 5.6905 | 96.9556 | 2.4869 | 14.2498 | 28.034 | 102.2156 | 5.3081 | 230.6144 | 129.9938 | 209.9089 | 7.4048 | 60.7858 | 13.2346 | 213 | 6.4558 | 117.3869 | 239.4668 | 0.044061
2562 | 906.2227 | 3.3713 | 52.4155 | 90.5626 | 84.1039 | 5.6514 | 82.9988 | 3.1443 | 13.2673 | 26.8852 | 99.1341 | 5.3122 | 222.3838 | 132.846 | 219.4456 | 7.3929 | 58.8136 | 13.2786 | 207 | 6.4558 | 117.3869 | 243.5139 | 0.007908
2563 | 894.6226 | 3.3818 | 51.8295 | 89.1326 | 84.0006 | 5.7495 | 80.8964 | 3.4421 | 10.8507 | 27.9694 | 84.5844 | 5.3095 | 212.4382 | 128.4465 | 222.3145 | 7.4886 | 57.3972 | 13.2373 | 218 | 6.4558 | 117.3869 | 249.0234 | 0.0021547
2564 | 872.7453 | 3.2329 | 51.8498 | 88.9849 | 84.085 | 5.6693 | 81.5604 | 4.0405 | 7.8081 | 29.1906 | 75.8966 | 6.571 | 210.668 | 118.6677 | 223.4611 | 7.6518 | 56.522 | 13.1233 | 210 | 6.4558 | 117.3869 | 254.5323 | 0
2565 | 857.6676 | 4.7809 | 51.6649 | 89.6168 | 84.0722 | 5.6815 | 82.8975 | 4.3105 | 6.8301 | 31.556 | 77.4383 | 8.0558 | 195.8745 | 113.7782 | 217.928 | 7.9172 | 56.4802 | 12.6328 | 205 | 6.4558 | 117.3869 | 260.0413 | 0
2566 | 849.4011 | 7.9883 | 51.7909 | 88.7926 | 83.9812 | 5.7679 | 82.5558 | 4.1139 | 6.9643 | 31.8945 | 78.3721 | 8.5492 | 193.5727 | 113.8836 | 213.6937 | 7.9133 | 56.5665 | 12.8248 | 183 | 6.4558 | 117.3869 | 261.8316 | 0
2567 | 835.5943 | 9.178 | 51.5723 | 88.5344 | 83.4156 | 6.3053 | 81.7103 | 4.1381 | 6.7153 | 28.6432 | 75.9061 | 8.4825 | 203.3661 | 114.8062 | 219.9291 | 7.9389 | 56.1508 | 12.801 | 155 | 6.4558 | 117.3869 | 256.4477 | 0
2568 | 836.9554 | 8.5323 | 51.2764 | 88.9542 | 82.4199 | 7.2512 | 81.9182 | 4.1548 | 6.4945 | 25.2984 | 73.1152 | 8.2969 | 206.7729 | 114.0754 | 229.5365 | 8.135 | 55.8714 | 12.1975 | 149 | 6.4558 | 117.3869 | 249.8242 | 0
2569 | 829.3338 | 8.3552 | 51.2214 | 89.592 | 81.3852 | 8.2341 | 82.1505 | 4.2877 | 6.4072 | 24.2293 | 71.7999 | 8.2358 | 205.235 | 108.7806 | 234.7376 | 8.7256 | 55.6889 | 12.0137 | 153 | 6.4558 | 117.3869 | 247.158 | 0
2570 | 811.923 | 5.016 | 51.2214 | 88.8164 | 79.878 | 9.666 | 82.4747 | 4.4009 | 6.6809 | 24.1943 | 72.0443 | 8.2195 | 192.8594 | 104.3582 | 226.414 | 9.0903 | 55.83 | 12.0007 | 171 | 6.4558 | 117.3869 | 248.6702 | 0
2571 | 800.075 | 1.7022 | 51.2214 | 87.7904 | 79.1292 | 10.3774 | 82.4515 | 4.6152 | 6.9907 | 24.1894 | 73.2425 | 8.2192 | 187.2084 | 101.5708 | 213.3125 | 9.049 | 56.4676 | 11.6439 | 146 | 6.4558 | 117.3869 | 252.437 | 0
2572 | 786.6906 | 2.0744 | 51.1744 | 87.6969 | 80.9725 | 8.6262 | 81.9601 | 4.7114 | 6.9338 | 24.0783 | 74.0743 | 8.1991 | 191.9863 | 96.1186 | 210.5077 | 9.0868 | 57.6955 | 11.3137 | 143 | 6.4558 | 117.3869 | 256.3064 | 0
2573 | 780.1682 | 2.8543 | 50.6732 | 87.4773 | 83.2396 | 6.4725 | 81.7967 | 4.4966 | 6.7913 | 24.3213 | 73.3753 | 8.179 | 196.399 | 90.8874 | 211.5146 | 9.0356 | 59.3845 | 11.3062 | 123 | 6.4558 | 117.3869 | 258.6555 | 0
2574 | 785.2618 | 2.7146 | 50.773 | 85.6775 | 83.3549 | 6.3629 | 81.1271 | 4.3118 | 6.5905 | 24.0354 | 71.107 | 6.7042 | 195.6812 | 88.9368 | 205.5146 | 8.7809 | 59.0124 | 11.3055 | 123 | 6.4558 | 117.3869 | 251.7041 | 0.0054793
2575 | 807.1438 | 2.0661 | 51.0734 | 84.8834 | 83.7158 | 6.0201 | 80.4695 | 4.0627 | 6.047 | 21.9982 | 69.0015 | 5.4611 | 187.0497 | 90.3461 | 201.9233 | 8.5609 | 56.7732 | 11.6125 | 127 | 6.4558 | 117.3869 | 239.4377 | 0.027157
2576 | 809.8607 | 1.4314 | 50.9694 | 86.1387 | 84.0967 | 5.6582 | 88.7149 | 3.8956 | 5.7108 | 25.8485 | 69.6874 | 5.4258 | 191.217 | 92.1798 | 202.5894 | 8.5568 | 55.7428 | 12.2323 | 131 | 6.4558 | 117.3869 | 236.2974 | 0.037563
2577 | 827.0723 | 0.98806 | 50.9694 | 86.6068 | 84.0456 | 5.7068 | 103.3168 | 3.5579 | 5.9644 | 40.1675 | 71.8489 | 5.4146 | 191.5259 | 93.8161 | 211.6169 | 7.9586 | 55.8652 | 12.6129 | 186 | 6.4558 | 117.3869 | 241.296 | 0.074754
2578 | 863.6287 | 1.3409 | 50.9694 | 86.2953 | 83.4546 | 6.2682 | 101.2481 | 4.9122 | 9.5813 | 54.1271 | 77.2156 | 5.5312 | 194.4065 | 101.3703 | 224.514 | 7.5509 | 56.1997 | 12.6744 | 173 | 6.4558 | 117.3869 | 245.9551 | 0.10134
2579 | 880.0403 | 1.4279 | 50.9694 | 86.7766 | 83.0366 | 6.6654 | 86.3255 | 5.4969 | 13.1213 | 61.4088 | 86.21 | 5.8277 | 220.4528 | 113.6982 | 230.2543 | 7.8753 | 56.9582 | 13.038 | 173 | 6.4558 | 117.3869 | 250.727 | 0.10041
2580 | 878.4783 | 1.3916 | 51.1851 | 87.6905 | 83.0498 | 6.6528 | 79.6095 | 3.8564 | 14.302 | 59.2225 | 90.7894 | 8.5821 | 236.3609 | 130.0991 | 228.1058 | 7.6671 | 57.7121 | 13.2211 | 195 | 6.4558 | 117.3869 | 250.1488 | 0.1516
2581 | 873.8438 | 1.4996 | 51.3936 | 87.9272 | 83.0665 | 6.6369 | 84.8942 | 3.5869 | 14.57 | 50.1365 | 95.7544 | 10.4382 | 246.4155 | 142.8187 | 224.1888 | 7.2873 | 57.9394 | 12.9462 | 183 | 6.4558 | 117.3869 | 242.7551 | 0.19184
2582 | 878.7468 | 1.4163 | 51.4171 | 88.6419 | 82.9823 | 6.7169 | 91.9518 | 3.5445 | 13.7567 | 46.2062 | 115.0539 | 10.224 | 258.1623 | 141.0716 | 221.634 | 7.3183 | 59.2612 | 12.8945 | 178 | 6.4558 | 117.3869 | 239.7661 | 0.19997
2583 | 875.3861 | 1.6932 | 51.5237 | 89.5404 | 82.4427 | 7.2295 | 94.4924 | 3.3257 | 12.858 | 43.6067 | 131.6599 | 10.3833 | 250.0678 | 134.708 | 220.0309 | 7.3076 | 61.5784 | 12.9323 | 171 | 6.4558 | 117.3869 | 243.7575 | 0.16028
2584 | 878.4753 | 1.9391 | 51.641 | 89.7775 | 83.3601 | 6.358 | 93.8711 | 3.5851 | 9.4347 | 34.2121 | 119.565 | 10.469 | 251.0584 | 136.8958 | 223.739 | 7.2855 | 61.0538 | 12.8055 | 163 | 6.4558 | 117.3869 | 247.195 | 0.099631
2585 | 875.6141 | 2.0769 | 52.2942 | 88.6906 | 82.1243 | 7.532 | 86.5107 | 3.8282 | 9.858 | 25.003 | 98.8092 | 9.5524 | 247.192 | 141.87 | 230.7836 | 7.334 | 58.3235 | 12.7632 | 155 | 6.4558 | 117.3869 | 245.3948 | 0.069905
2586 | 855.1018 | 2.0951 | 52.7829 | 87.5411 | 82.9107 | 6.7849 | 80.0231 | 3.5074 | 12.816 | 21.4355 | 91.537 | 6.9326 | 245.6231 | 134.6432 | 235.8727 | 7.3174 | 57.2437 | 12.7971 | 140 | 6.4558 | 117.3869 | 241.4925 | 0.042107
2587 | 836.8784 | 3.1742 | 51.9958 | 86.6399 | 84.0552 | 5.6977 | 79.9191 | 3.6026 | 10.4026 | 20.6076 | 88.0987 | 5.4605 | 226.4834 | 118.8615 | 238.5836 | 7.3005 | 57.3292 | 12.7942 | 137 | 6.4558 | 117.3869 | 236.3131 | 0.028668
2588 | 828.5882 | 7.857 | 51.4443 | 87.0075 | 84.0277 | 5.7238 | 80.5059 | 4.2873 | 7.2348 | 20.9621 | 82.3747 | 6.2615 | 220.6864 | 110.111 | 242.9603 | 7.4419 | 57.4512 | 12.6081 | 131 | 6.4558 | 117.3869 | 232.9473 | 0
2589 | 832.9039 | 10.9441 | 51.3796 | 88.5041 | 84.0794 | 5.6746 | 81.7391 | 4.6779 | 6.5028 | 22.6562 | 78.7851 | 7.6536 | 201.5521 | 108.2918 | 242.2441 | 7.7306 | 58.0914 | 12.1147 | 121 | 6.4558 | 117.3869 | 236.2374 | 0
2590 | 828.7731 | 9.9117 | 51.3509 | 88.9616 | 83.4638 | 6.2595 | 82.3918 | 4.6533 | 6.5397 | 23.9931 | 78.4002 | 8.2582 | 186.1102 | 105.8266 | 227.6507 | 8.0542 | 58.695 | 12.0339 | 117 | 6.4558 | 117.3869 | 242.2899 | 0
2591 | 803.2923 | 8.4572 | 51.3509 | 88.4955 | 83.6556 | 6.0773 | 81.9493 | 4.4344 | 6.6713 | 24.1066 | 77.4274 | 8.2368 | 179.2421 | 102.4045 | 205.2501 | 8.539 | 58.778 | 12.2266 | 116 | 6.4558 | 117.3869 | 245.9387 | 0
2592 | 794.1291 | 4.7397 | 51.2499 | 89.0244 | 84.0224 | 5.7288 | 82.1236 | 4.4782 | 6.7961 | 23.9196 | 75.0255 | 8.2546 | 174.1739 | 97.8135 | 202.4508 | 8.8308 | 58.6381 | 12.0835 | 110 | 6.4558 | 117.3869 | 245.0315 | 0
2593 | 791.7151 | 1.5959 | 51.1908 | 89.1758 | 84.0811 | 5.673 | 82.3075 | 4.5512 | 6.8919 | 23.937 | 72.9468 | 8.2661 | 163.0108 | 95.6501 | 215.3459 | 8.8309 | 58.6753 | 11.8564 | 106 | 6.4558 | 117.3869 | 241.6966 | 0
2594 | 777.5705 | 1.2462 | 50.6449 | 88.8178 | 84.0691 | 5.6845 | 81.8391 | 4.6359 | 7.0334 | 23.9926 | 72.402 | 8.5661 | 153.0682 | 98.0377 | 217.5252 | 8.7475 | 58.8676 | 11.7464 | 124 | 6.4558 | 117.3869 | 240.7178 | 0
2595 | 779.8269 | 1.1982 | 50.2431 | 88.9858 | 84.0382 | 5.7138 | 81.7167 | 4.7083 | 7.2169 | 25.8681 | 73.0682 | 8.7994 | 153.9977 | 99.7816 | 213.6625 | 8.3605 | 58.7625 | 11.7251 | 106 | 6.4558 | 117.3869 | 244.3855 | 0
2596 | 780.9213 | 1.6709 | 51.552 | 90.1794 | 84.0015 | 5.7487 | 82.5389 | 4.562 | 7.1592 | 32.5092 | 73.8095 | 8.7641 | 148.5254 | 97.0356 | 210.1042 | 7.9276 | 59.4987 | 11.7415 | 104 | 6.4558 | 117.3869 | 262.0685 | 0
2597 | 792.6149 | 2.8287 | 52.0799 | 89.6082 | 83.4705 | 6.2531 | 83.2241 | 4.3337 | 7.1212 | 39.8933 | 74.3403 | 9.0615 | 152.3745 | 98.3627 | 205.5107 | 7.6715 | 61.0515 | 12.4947 | 111 | 6.4558 | 117.3869 | 285.6755 | 0
2598 | 830.733 | 3.5601 | 58.2675 | 91.7439 | 81.7891 | 7.8504 | 96.878 | 4.3663 | 6.8647 | 50.6659 | 87.2125 | 15.3509 | 161.5474 | 125.2236 | 228.4063 | 11.5411 | 60.6515 | 12.6885 | 184 | 6.4558 | 117.3869 | 324.1977 | 0.014425
2599 | 891.0582 | 5.1202 | 89.1886 | 101.2829 | 77.4055 | 12.0148 | 117.4944 | 5.4885 | 8.4022 | 70.4717 | 119.8588 | 27.8274 | 223.554 | 181.8471 | 301.3273 | 22.6831 | 62.2825 | 13.0969 | 306 | 6.4558 | 117.3869 | 393.8678 | 0.02892
2600 | 990.453 | 10.316 | 110.3499 | 113.466 | 74.3576 | 14.9103 | 129.9907 | 6.8766 | 16.1404 | 81.483 | 152.8263 | 34.5661 | 280.3631 | 245.5456 | 393.1323 | 31.8008 | 69.7012 | 16.148 | 329 | 6.4558 | 117.3869 | 459.6937 | 0.047409
2601 | 1073.1408 | 10.7063 | 110.3499 | 125.0484 | 74.6167 | 14.6642 | 142.9372 | 7.5062 | 22.8114 | 80.2066 | 175.3024 | 37.3341 | 326.0745 | 294.7969 | 472.2516 | 35.4013 | 77.0976 | 17.6582 | 334 | 6.4558 | 117.3869 | 505.942 | 0.074978
2602 | 1116.8508 | 7.0941 | 110.3499 | 129.2149 | 73.8355 | 15.4064 | 149.6303 | 7.3207 | 25.6207 | 80.4521 | 187.7668 | 39.2088 | 380.4622 | 320.872 | 528.3193 | 37.3455 | 81.9204 | 17.8144 | 362 | 6.4558 | 117.3869 | 534.4595 | 0.19554
2603 | 1164.0518 | 5.731 | 110.3499 | 130.6798 | 74.9338 | 14.3629 | 148.3713 | 6.6196 | 26.5853 | 83.182 | 190.1676 | 39.127 | 393.7401 | 333.6919 | 553.6944 | 38.1907 | 84.9528 | 18.5681 | 343 | 6.4558 | 117.3869 | 540.6044 | 0.16728
2604 | 1176.6219 | 5.9426 | 110.3499 | 133.9734 | 73.6217 | 15.6095 | 149.4378 | 6.876 | 23.9427 | 89.6832 | 188.6815 | 39.465 | 399.0775 | 340.2208 | 559.2399 | 40.4506 | 86.1449 | 18.5741 | 375 | 6.4558 | 117.3869 | 543.5769 | 0.17834
2605 | 1179.2391 | 9.0841 | 111.0309 | 136.423 | 73.3124 | 15.9033 | 153.8603 | 7.4687 | 20.9059 | 96.3902 | 189.3949 | 39.9976 | 409.5818 | 336.5953 | 569.504 | 43.7744 | 87.8287 | 19.1535 | 294 | 6.4558 | 117.3869 | 546.0936 | 0.14518
2606 | 1175.8573 | 9.7049 | 111.5536 | 139.1584 | 74.731 | 14.5557 | 155.6636 | 7.3781 | 21.8699 | 98.8761 | 192.5068 | 38.9909 | 409.4284 | 332.461 | 575.1803 | 42.4667 | 89.8167 | 20.3022 | 304 | 6.4558 | 117.3869 | 539.1663 | 0.10813
2607 | 1143.0694 | 7.1585 | 108.0496 | 136.7778 | 74.9538 | 14.344 | 150.0467 | 7.1467 | 22.2735 | 96.3331 | 193.3831 | 35.8989 | 415.0032 | 330.7705 | 564.0281 | 39.229 | 90.1747 | 20.7498 | 284 | 6.4558 | 117.3869 | 529.5224 | 0.074558
2608 | 1104.7658 | 4.6043 | 104.9897 | 130.1745 | 79.4299 | 10.0916 | 136.8286 | 6.8492 | 17.8833 | 88.8777 | 190.5542 | 33.026 | 418.4407 | 316.5529 | 522.9598 | 31.1645 | 88.4205 | 19.2639 | 241 | 6.4558 | 117.3869 | 495.4211 | 0.068971
2609 | 1047.7045 | 3.5485 | 104.9897 | 119.4014 | 81.9382 | 7.7088 | 119.9058 | 4.8927 | 14.558 | 78.5275 | 179.0304 | 30.6333 | 386.2488 | 274.4157 | 434.8911 | 17.1406 | 83.7164 | 17.5801 | 223 | 6.4558 | 117.3869 | 427.7731 | 0.091314
2610 | 978.4136 | 2.9859 | 104.9897 | 104.9703 | 82.6894 | 6.9951 | 107.7466 | 3.3738 | 14.5631 | 61.7049 | 150.6938 | 24.4543 | 344.3164 | 218.7802 | 349.0244 | 9.666 | 76.8764 | 16.7892 | 210 | 6.4558 | 117.3869 | 363.5508 | 0.071841
2611 | 921.8007 | 3.3388 | 88.8103 | 95.3852 | 83.774 | 5.9648 | 99.6127 | 3.8901 | 13.4637 | 40.9804 | 117.2096 | 15.2276 | 300.2531 | 180.7256 | 310.9603 | 8.6285 | 69.1997 | 16.1546 | 194 | 6.4558 | 117.3869 | 320.4085 | 0.025524
2612 | 882.8757 | 3.9742 | 60.3629 | 90.5842 | 84.0383 | 5.7137 | 90.4869 | 4.029 | 9.6203 | 28.2825 | 101.1405 | 10.4871 | 278.2429 | 161.3641 | 285.1458 | 8.3586 | 61.8038 | 15.2856 | 171 | 6.4558 | 117.3869 | 296.5175 | 0
2613 | 856.5745 | 3.5638 | 44.4463 | 90.4383 | 83.4293 | 6.2922 | 85.619 | 4.2161 | 7.3698 | 27.1883 | 98.1353 | 9.6058 | 270.3939 | 149.5906 | 249.6642 | 8.508 | 57.4445 | 14.1113 | 162 | 6.4558 | 117.3869 | 290.7701 | 0
2614 | 824.5096 | 2.8705 | 42.2956 | 90.6478 | 83.6949 | 6.0399 | 85.5661 | 4.3728 | 7.1097 | 28.0286 | 91.2184 | 8.9249 | 246.6887 | 136.0108 | 219.6298 | 8.6991 | 56.4971 | 13.4223 | 155 | 6.4558 | 117.3869 | 288.9193 | 0
2615 | 798.4734 | 1.9625 | 41.7369 | 89.8238 | 83.3924 | 6.3273 | 85.7671 | 4.4499 | 6.942 | 24.9032 | 81.7348 | 8.6591 | 223.8568 | 120.1603 | 215.1569 | 9.135 | 56.4775 | 13.1085 | 133 | 6.4558 | 117.3869 | 283.5984 | 0
2616 | 797.6737 | 2.1661 | 41.2664 | 89.8418 | 83.68 | 6.0541 | 85.7546 | 4.4318 | 6.8013 | 22.6031 | 77.5248 | 8.6886 | 211.4653 | 113.4721 | 226.1341 | 9.3447 | 56.3606 | 12.3837 | 119 | 6.4558 | 117.3869 | 277.3692 | 0
2617 | 787.0989 | 5.6969 | 41.2664 | 89.8968 | 84.0752 | 5.6787 | 85.5339 | 4.5416 | 6.7512 | 22.3273 | 78.7648 | 8.0206 | 207.3193 | 109.819 | 232.9867 | 8.9969 | 56.4708 | 11.8506 | 119 | 6.4558 | 117.3869 | 272.5963 | 0
2618 | 770.3769 | 8.4058 | 41.2664 | 89.3847 | 84.0728 | 5.681 | 85.8454 | 4.5548 | 6.7718 | 22.1807 | 82.3963 | 7.1381 | 199.9686 | 103.0632 | 229.9372 | 8.5851 | 56.5701 | 13.0836 | 135 | 6.4558 | 117.3869 | 269.3014 | 0
2619 | 778.281 | 8.3093 | 41.2664 | 89.2902 | 83.4346 | 6.2872 | 86.2032 | 4.4465 | 6.9043 | 23.9966 | 85.2407 | 6.8774 | 191.3964 | 98.8939 | 224.4911 | 8.5632 | 56.4955 | 14.0333 | 114 | 6.4558 | 117.3869 | 267.0586 | 0
2620 | 786.3903 | 6.0463 | 41.3821 | 89.589 | 83.6887 | 6.0458 | 85.734 | 4.4 | 6.8793 | 30.6937 | 85.098 | 6.8593 | 188.1602 | 96.1115 | 221.9869 | 8.6092 | 57.3732 | 13.5731 | 112 | 6.4558 | 117.3869 | 280.0708 | 0
2621 | 797.9353 | 3.6598 | 51.9467 | 90.116 | 83.4203 | 6.3008 | 85.3121 | 4.1921 | 6.922 | 38.2588 | 81.1242 | 7.101 | 184.504 | 101.2547 | 220.5088 | 8.3483 | 59.168 | 13.269 | 111 | 6.4558 | 117.3869 | 309.6265 | 0
2622 | 828.2356 | 3.6267 | 76.7959 | 91.1175 | 81.2185 | 8.3925 | 95.264 | 4.2762 | 7.0687 | 49.2818 | 82.5412 | 12.8951 | 187.5036 | 127.8318 | 231.9108 | 12.31 | 58.9983 | 13.0853 | 193 | 6.4558 | 117.3869 | 345.1494 | 0.028879
2623 | 887.5116 | 4.1678 | 90.3629 | 96.6061 | 78.1669 | 11.2915 | 116.7042 | 4.8838 | 9.1025 | 71.5324 | 105.8152 | 24.1647 | 229.8125 | 179.4374 | 277.082 | 23.6249 | 60.1814 | 13.7759 | 276 | 6.4558 | 117.3869 | 401.6685 | 0.1255
2624 | 987.0791 | 7.1213 | 101.1948 | 111.3337 | 72.7936 | 16.3962 | 134.9903 | 5.9991 | 15.445 | 90.3638 | 145.9908 | 29.6237 | 310.8944 | 241.0187 | 378.8396 | 33.6058 | 68.6884 | 15.5708 | 295 | 6.4558 | 117.3869 | 471.2859 | 0.21346
2625 | 1076.6292 | 10.3937 | 110.6879 | 128.2299 | 72.373 | 16.7957 | 143.1643 | 6.5185 | 21.2634 | 96.2815 | 178.6438 | 32.5959 | 365.0819 | 288.1373 | 498.8558 | 36.305 | 81.2708 | 16.7275 | 302 | 6.4558 | 117.3869 | 517.2487 | 0.29673
2626 | 1125.1803 | 10.4125 | 110.6879 | 133.5076 | 72.1698 | 16.9888 | 144.8065 | 5.962 | 23.8416 | 96.8163 | 194.6302 | 38.6764 | 402.1188 | 314.0707 | 563.3683 | 37.644 | 96.0104 | 17.5203 | 347 | 6.4558 | 117.3869 | 525.588 | 0.30794
2627 | 1144.4663 | 7.1424 | 113.0859 | 129.2139 | 73.5816 | 15.6476 | 147.4747 | 6.1483 | 25.3897 | 94.0384 | 198.9119 | 40.5203 | 436.8024 | 328.9256 | 574.043 | 38.4508 | 108.5178 | 18.3894 | 320 | 6.4558 | 117.3869 | 508.366 | 0.29134
2628 | 1150.5106 | 4.6333 | 113.939 | 129.0385 | 74.6067 | 14.6737 | 155.9317 | 6.3766 | 23.9812 | 87.0715 | 194.4417 | 39.2317 | 437.2697 | 331.1909 | 564.924 | 39.9604 | 112.1507 | 18.6622 | 359 | 6.4558 | 117.3869 | 491.5924 | 0.27618
2629 | 1150.3339 | 7.7119 | 115.5701 | 136.9982 | 75.1853 | 14.124 | 155.9479 | 5.4769 | 20.7219 | 81.9531 | 191.8044 | 38.6384 | 434.5792 | 324.5079 | 554.0624 | 41.5957 | 112.3758 | 18.4391 | 314 | 6.4558 | 117.3869 | 484.1491 | 0.24801
2630 | 1158.4862 | 11.9198 | 115.498 | 140.7197 | 72.7447 | 16.4427 | 145.3129 | 5.9695 | 20.0813 | 86.0215 | 199.1716 | 38.4905 | 428.0668 | 323.5584 | 563.6618 | 40.6719 | 113.4613 | 18.3679 | 285 | 6.4558 | 117.3869 | 479.593 | 0.18318
2631 | 1145.2138 | 10.6523 | 113.3137 | 134.657 | 72.2975 | 16.8674 | 137.3842 | 7.0993 | 20.4557 | 87.5277 | 205.1022 | 37.2052 | 429.3912 | 321.5292 | 572.5815 | 38.1081 | 112.818 | 18.752 | 280 | 6.4558 | 117.3869 | 471.966 | 0.18797
2632 | 1115.372 | 6.0671 | 108.1813 | 125.9436 | 77.465 | 11.9583 | 129.2984 | 5.7108 | 18.0924 | 79.685 | 198.2721 | 34.0935 | 428.0725 | 307.6834 | 549.1441 | 30.3734 | 106.3497 | 18.4888 | 261 | 6.4558 | 117.3869 | 444.5292 | 0.16807
2633 | 1063.1746 | 3.6858 | 101.034 | 114.36 | 80.6559 | 8.927 | 117.9143 | 3.6344 | 15.9347 | 67.8889 | 180.1694 | 30.9331 | 395.5806 | 270.6935 | 487.3521 | 17.149 | 90.469 | 16.951 | 217 | 6.4558 | 117.3869 | 395.3501 | 0.17805
2634 | 1001.3958 | 2.8926 | 98.6428 | 107.0243 | 82.9861 | 6.7133 | 98.5894 | 3.2335 | 15.3466 | 50.3113 | 148.6461 | 24.0307 | 352.564 | 219.3256 | 415.0506 | 10.2274 | 73.595 | 15.1194 | 216 | 6.4558 | 117.3869 | 343.287 | 0.17404
2635 | 957.6008 | 2.2076 | 75.4311 | 93.6643 | 84.6732 | 5.1106 | 80.6365 | 3.7283 | 13.2842 | 32.7842 | 114.4839 | 12.9213 | 305.891 | 186.2416 | 357.6138 | 8.9083 | 65.6911 | 13.9796 | 191 | 6.4558 | 117.3869 | 297.1813 | 0.063944
2636 | 914.3165 | 3.265 | 55.753 | 86.0509 | 84.4383 | 5.3337 | 84.0258 | 3.7238 | 9.8125 | 25.0641 | 99.5044 | 8.1315 | 264.319 | 169.1067 | 306.122 | 8.2145 | 61.7577 | 13.3265 | 179 | 6.4558 | 117.3869 | 266.6023 | 0
2637 | 885.3911 | 3.8866 | 55.753 | 89.7819 | 84.0177 | 5.7333 | 93.7792 | 4.1171 | 7.802 | 25.6685 | 98.1843 | 9.2719 | 243.2348 | 149.804 | 264.2253 | 8.4371 | 57.9678 | 12.6714 | 170 | 6.4558 | 117.3869 | 259.5372 | 0
2638 | 860.2761 | 3.3421 | 48.5351 | 89.9175 | 82.7717 | 6.917 | 94.7007 | 4.2037 | 7.7558 | 26.245 | 93.4148 | 9.1657 | 227.3665 | 135.1389 | 241.1185 | 8.5766 | 56.5666 | 12.7874 | 145 | 6.4558 | 117.3869 | 261.9936 | 0
2639 | 833.6471 | 2.3727 | 42.6046 | 89.2857 | 82.7181 | 6.9679 | 94.8487 | 4.4114 | 7.5735 | 23.8298 | 83.9216 | 7.827 | 212.2019 | 129.3123 | 234.5891 | 8.6053 | 56.2871 | 13.3207 | 128 | 6.4558 | 117.3869 | 261.9404 | 0
2640 | 829.3409 | 1.4758 | 42.6046 | 90.1081 | 83.1302 | 6.5764 | 94.8272 | 4.4093 | 7.2195 | 21.8311 | 77.8337 | 7.1995 | 199.1025 | 127.0264 | 234.0562 | 8.675 | 55.7595 | 13.1575 | 115 | 6.4558 | 117.3869 | 265.0109 | 0
2641 | 822.3756 | 1.441 | 56.33 | 90.1074 | 83.6345 | 6.0973 | 94.812 | 4.1947 | 7.1486 | 21.6503 | 76.4021 | 7.2054 | 193.6299 | 124.7289 | 228.5081 | 8.9269 | 55.4555 | 12.7491 | 116 | 6.4558 | 117.3869 | 267.1058 | 0
2642 | 812.9431 | 1.3953 | 68.6331 | 89.4673 | 83.3434 | 6.3739 | 94.67 | 4.3915 | 7.0594 | 22.1631 | 76.115 | 7.1749 | 191.7417 | 120.4147 | 220.7988 | 9.3818 | 55.3051 | 12.7045 | 132 | 6.4558 | 117.3869 | 262.8336 | 0
2643 | 807.2573 | 1.3749 | 68.6331 | 89.095 | 83.6955 | 6.0394 | 94.4059 | 4.8791 | 7.268 | 24.1609 | 76.458 | 7.1814 | 179.5861 | 116.2029 | 216.3241 | 9.5113 | 55.0544 | 12.8569 | 110 | 6.4558 | 117.3869 | 259.4894 | 0
2644 | 814.7517 | 4.7832 | 68.6331 | 88.991 | 84.104 | 5.6513 | 94.2994 | 4.9239 | 7.589 | 30.4211 | 76.8308 | 7.2069 | 170.0145 | 112.3688 | 217.2346 | 9.5224 | 55.8449 | 12.5364 | 108 | 6.4558 | 117.3869 | 266.3276 | 0
2645 | 840.3567 | 9.3307 | 68.6331 | 88.3838 | 83.4457 | 6.2766 | 93.9007 | 4.6351 | 7.6225 | 37.2078 | 75.4638 | 7.2681 | 170.4194 | 111.407 | 217.4661 | 9.2626 | 57.5517 | 11.8051 | 114 | 6.4558 | 117.3869 | 281.9436 | 0
2646 | 872.9562 | 10.8146 | 68.6331 | 90.4286 | 81.1909 | 8.4187 | 94.8591 | 4.5756 | 7.011 | 47.9407 | 79.8273 | 13.0003 | 174.858 | 130.6768 | 232.0949 | 13.4275 | 57.4737 | 11.4213 | 208 | 6.4558 | 117.3869 | 312.8595 | 0.12734
2647 | 935.352 | 11.0489 | 68.6331 | 96.5818 | 76.3259 | 13.0405 | 110.4173 | 5.265 | 7.95 | 68.257 | 105.9206 | 27.1135 | 232.6754 | 180.2905 | 288.5739 | 24.5383 | 59.1376 | 12.3029 | 257 | 6.4558 | 117.3869 | 383.5179 | 0.23034
2648 | 1041.8352 | 10.2114 | 68.6331 | 109.1854 | 75.269 | 14.0445 | 134.0512 | 5.8356 | 12.714 | 77.5489 | 146.388 | 37.4018 | 295.5037 | 236.8428 | 390.3037 | 35.6029 | 67.1137 | 14.4535 | 308 | 6.4558 | 117.3869 | 470.1506 | 0.29313
2649 | 1135.4595 | 10.1216 | 68.6331 | 122.6502 | 75.3905 | 13.9291 | 147.5964 | 5.3855 | 18.196 | 74.1415 | 175.2811 | 39.4755 | 321.372 | 278.8396 | 481.3226 | 41.4377 | 76.1215 | 16.0421 | 358 | 6.4558 | 117.3869 | 525.3588 | 0.32357
2650 | 1177.6418 | 10.5913 | 93.7565 | 127.0527 | 73.586 | 15.6434 | 139.0687 | 6.0606 | 22.0936 | 74.3927 | 186.454 | 39.1436 | 381.8975 | 307.9644 | 517.0836 | 42.3825 | 81.5609 | 17.0571 | 355 | 6.4558 | 117.3869 | 535.4687 | 0.31555
2651 | 1187.8698 | 8.6223 | 115.1453 | 128.8703 | 72.9691 | 16.2294 | 128.2015 | 6.9452 | 24.3339 | 74.732 | 189.5865 | 37.1856 | 423.1889 | 325.8891 | 535.2578 | 40.4681 | 83.3503 | 17.7011 | 354 | 6.4558 | 117.3869 | 519.4897 | 0.29826
2652 | 1182.6256 | 7.2207 | 114.5856 | 128.3909 | 74.0964 | 15.1585 | 129.1775 | 5.744 | 23.108 | 75.0036 | 188.7195 | 34.5211 | 427.9651 | 327.9536 | 545.7766 | 39.8616 | 82.4914 | 17.7356 | 343 | 6.4558 | 117.3869 | 510.4942 | 0.29552
2653 | 1181.8476 | 7.1379 | 114.1953 | 133.5099 | 73.9966 | 15.2533 | 130.0497 | 5.6005 | 21.7647 | 77.5915 | 190.4124 | 35.7936 | 436.5477 | 324.7601 | 541.7249 | 39.4677 | 81.7081 | 18.1234 | 303 | 6.4558 | 117.3869 | 508.1787 | 0.31773
2654 | 1201.4771 | 6.8843 | 114.1953 | 137.8859 | 73.2228 | 15.9885 | 132.9016 | 6.0887 | 21.6005 | 86.1981 | 196.0377 | 37.4029 | 440.0121 | 322.7229 | 538.0364 | 37.5967 | 81.4697 | 18.0869 | 283 | 6.4558 | 117.3869 | 503.6222 | 0.31925
2655 | 1187.0278 | 7.2757 | 114.1953 | 135.8681 | 73.6225 | 15.6087 | 129.541 | 4.8423 | 21.1598 | 95.8657 | 195.0073 | 37.2844 | 434.3738 | 314.5096 | 525.6368 | 35.6972 | 79.7162 | 17.4506 | 312 | 6.4558 | 117.3869 | 499.0507 | 0.28115
2656 | 1128.3923 | 6.3431 | 107.0646 | 127.6442 | 79.1574 | 10.3506 | 118.618 | 4.3634 | 18.97 | 92.9994 | 188.3536 | 34.2689 | 420.0704 | 294.9434 | 495.683 | 29.0109 | 75.9056 | 16.4683 | 277 | 6.4558 | 117.3869 | 468.0923 | 0.21529
2657 | 1078.589 | 4.4525 | 101.0894 | 113.2578 | 81.4476 | 8.1749 | 110.0669 | 3.6172 | 16.5525 | 76.2196 | 177.5369 | 30.4653 | 384.8632 | 243.5402 | 435.8428 | 17.0191 | 70.9218 | 15.769 | 236 | 6.4558 | 117.3869 | 403.004 | 0.24054
2658 | 1024.3675 | 3.4931 | 101.0894 | 100.8454 | 81.7906 | 7.8491 | 100.6816 | 2.7352 | 15.9189 | 52.5532 | 149.9716 | 25.8727 | 346.0917 | 174.6991 | 357.7674 | 10.7702 | 66.595 | 15.464 | 222 | 6.4558 | 117.3869 | 345.4216 | 0.17462
2659 | 965.2394 | 3.3649 | 78.6753 | 94.9109 | 82.0203 | 7.6308 | 90.5948 | 3.9551 | 13.2547 | 33.6697 | 115.7606 | 16.7213 | 295.5982 | 134.9447 | 297.7795 | 9.3481 | 63.0475 | 15.0485 | 204 | 6.4558 | 117.3869 | 314.1441 | 0.059755
2660 | 928.0411 | 4.0155 | 59.1593 | 94.1918 | 82.6278 | 7.0537 | 90.3089 | 4.2724 | 8.4087 | 26.9161 | 101.358 | 10.0286 | 259.2591 | 124.4738 | 266.0721 | 8.5638 | 58.5283 | 14.625 | 207 | 6.4558 | 117.3869 | 299.2098 | 0
2661 | 903.3716 | 4.3448 | 48.5269 | 95.7695 | 82.4043 | 7.266 | 99.1154 | 4.0793 | 6.4282 | 28.6022 | 99.4522 | 8.8851 | 237.946 | 120.3591 | 252.6794 | 8.9214 | 54.9654 | 14.0007 | 202 | 6.4558 | 117.3869 | 296.4708 | 0
2662 | 873.1529 | 3.5081 | 40.1456 | 93.4799 | 82.7829 | 6.9063 | 102.8791 | 4.3039 | 7.1117 | 29.9364 | 92.8858 | 8.1256 | 221.5397 | 111.8277 | 236.9876 | 9.4213 | 54.0307 | 13.3976 | 164 | 6.4558 | 117.3869 | 295.1103 | 0
2663 | 842.3435 | 2.2459 | 40.1456 | 90.9749 | 82.4269 | 7.2446 | 96.4057 | 4.4327 | 7.4765 | 28.2315 | 83.9238 | 7.804 | 219.1983 | 101.3036 | 223.2878 | 9.7121 | 54.0305 | 13.2484 | 146 | 6.4558 | 117.3869 | 287.46 | 0
2664 | 836.4397 | 1.5672 | 40.9227 | 91.2776 | 82.0797 | 7.5744 | 91.2544 | 4.3825 | 8.0585 | 27.0638 | 78.6159 | 7.6991 | 216.2073 | 97.3479 | 229.5511 | 9.7365 | 54.0756 | 13.3139 | 138 | 6.4558 | 117.3869 | 278.2203 | 0
2665 | 830.9524 | 1.2929 | 41.5994 | 91.245 | 82.6411 | 7.041 | 88.5389 | 4.4952 | 7.9708 | 27.1131 | 76.7752 | 7.3858 | 214.5862 | 96.515 | 237.2994 | 9.768 | 54.2146 | 13.2566 | 131 | 6.4558 | 117.3869 | 272.9736 | 0
2666 | 812.2021 | 1.4298 | 41.5994 | 90.7441 | 82.4074 | 7.2631 | 81.947 | 4.6705 | 7.3543 | 27.1726 | 76.1853 | 7.3856 | 211.8714 | 95.1516 | 233.2024 | 9.8472 | 54.346 | 13.2923 | 150 | 6.4558 | 117.3869 | 272.7033 | 0
2667 | 802.7102 | 1.4766 | 41.5994 | 90.6252 | 82.0876 | 7.5669 | 84.135 | 4.617 | 7.0162 | 28.9815 | 76.9871 | 7.3473 | 195.3047 | 95.6782 | 228.5758 | 9.7945 | 54.4966 | 12.8174 | 117 | 6.4558 | 117.3869 | 273.1469 | 0
2668 | 806.9324 | 1.8875 | 41.5994 | 90.3542 | 82.0008 | 7.6494 | 87.9975 | 4.5213 | 6.7444 | 35.6823 | 77.7655 | 7.3328 | 185.6628 | 94.7922 | 226.3331 | 9.7971 | 55.522 | 11.9215 | 120 | 6.4558 | 117.3869 | 281.6444 | 0
2669 | 823.3555 | 2.9138 | 41.5994 | 90.7179 | 82.1175 | 7.5384 | 80.0605 | 4.2351 | 6.6687 | 43.2088 | 75.928 | 7.2714 | 186.7791 | 98.4969 | 221.7034 | 9.5863 | 57.2244 | 11.4879 | 121 | 6.4558 | 117.3869 | 306.1935 | 0
2670 | 853.3808 | 3.4923 | 70.6809 | 92.9401 | 79.5045 | 10.0208 | 90.8225 | 4.4908 | 6.762 | 53.3268 | 78.6717 | 11.9974 | 186.9496 | 121.5525 | 234.0917 | 13.2155 | 57.4976 | 12.0168 | 190 | 6.4558 | 117.3869 | 344.1267 | 0.072893
2671 | 904.7612 | 8.5556 | 96.5785 | 101.8786 | 74.2147 | 15.0461 | 119.7419 | 5.0505 | 9.2705 | 71.3244 | 104.8154 | 26.7873 | 227.9515 | 170.4899 | 303.342 | 24.7865 | 59.7147 | 13.3934 | 268 | 6.4558 | 117.3869 | 391.4703 | 0.22082
2672 | 988.6367 | 13.5904 | 96.5785 | 116.9417 | 72.6372 | 16.5447 | 136.5813 | 4.8316 | 14.891 | 82.7632 | 147.9071 | 36.9705 | 288.3131 | 228.9787 | 415.6966 | 34.1207 | 67.9086 | 16.7132 | 291 | 6.4558 | 117.3869 | 439.66 | 0.16161
2673 | 1085.7478 | 9.3335 | 96.5785 | 124.649 | 72.4645 | 16.7088 | 147.3795 | 5.2026 | 19.0234 | 85.0524 | 179.4295 | 37.7781 | 347.4373 | 276.9331 | 514.4027 | 37.346 | 77.1569 | 18.3984 | 337 | 1.5085 | 84.5863 | 483.0927 | 0.13489
2674 | 1132.7952 | 5.9144 | 102.8683 | 126.1931 | 71.4272 | 17.6942 | 150.3985 | 6.1304 | 19.6563 | 89.5288 | 192.9053 | 37.1013 | 388.2353 | 308.6389 | 560.9929 | 38.3248 | 83.2193 | 18.0407 | 376 | 6.0819 | 152.3219 | 507.9199 | 0.15202
2675 | 1159.0284 | 6.2307 | 111.8055 | 127.0918 | 73.4253 | 15.7961 | 150.5075 | 6.7015 | 19.0668 | 91.8168 | 196.7613 | 38.0831 | 399.7519 | 323.9846 | 577.5369 | 38.2276 | 86.2921 | 17.8376 | 341 | 8.6807 | 196.0557 | 515.4798 | 0.19814
2676 | 1166.3914 | 4.875 | 115.369 | 125.1839 | 74.5776 | 14.7013 | 137.0324 | 6.1109 | 18.1342 | 86.318 | 195.6697 | 37.3757 | 416.2963 | 324.7076 | 581.7489 | 38.9292 | 86.0549 | 17.4968 | 356 | 7.9767 | 188.1877 | 522.4245 | 0.15036
2677 | 1165.7866 | 4.0603 | 114.7016 | 127.4554 | 73.579 | 15.6501 | 123.4285 | 5.5697 | 16.1279 | 83.4462 | 195.8196 | 38.6083 | 414.3112 | 324.3906 | 580.7096 | 39.6274 | 85.252 | 17.9714 | 300 | 8.8572 | 190.013 | 521.1849 | 0.20427
2678 | 1177.1609 | 5.9356 | 113.9674 | 127.7601 | 72.3651 | 16.8033 | 124.42 | 6.2006 | 16.08 | 87.8462 | 198.2962 | 39.8698 | 408.2432 | 332.0102 | 585.2677 | 38.6914 | 85.955 | 18.4631 | 269 | 8.0177 | 192.0382 | 520.5786 | 0.22165
2679 | 1156.3617 | 7.2163 | 110.9831 | 123.8727 | 70.811 | 18.2796 | 134.4113 | 5.7643 | 16.219 | 88.0583 | 196.9449 | 38.5453 | 418.1879 | 331.9217 | 569.7912 | 36.9747 | 86.2304 | 18.7305 | 278 | 4.5961 | 185.1951 | 524.0286 | 0.24677
2680 | 1103.7537 | 5.136 | 103.4419 | 116.4963 | 73.747 | 15.4904 | 130.8948 | 4.8562 | 15.0193 | 82.8638 | 191.3127 | 35.9384 | 414.0508 | 312.5294 | 511.6431 | 34.4874 | 84.2615 | 18.5543 | 267 | 2.4544 | 168.4094 | 498.8293 | 0.21963
2681 | 1050.4128 | 3.1787 | 99.5024 | 103.6945 | 78.5962 | 10.8837 | 115.2279 | 4.1306 | 14.9489 | 70.4938 | 179.4935 | 31.0388 | 381.7081 | 259.4395 | 423.221 | 27.9787 | 78.7439 | 17.4789 | 246 | 2.0558 | 144.0495 | 438.6331 | 0.2162
2682 | 994.1016 | 2.6972 | 95.9826 | 93.1946 | 81.9284 | 7.7181 | 103.2735 | 4.2817 | 15.7695 | 50.0822 | 151.0122 | 24.2161 | 348.8277 | 190.5551 | 348.3045 | 24.5887 | 72.1628 | 16.592 | 221 | 2.0454 | 125.6582 | 376.4351 | 0.19601
2683 | 950.0689 | 2.2873 | 76.53 | 87.9992 | 82.4446 | 7.2277 | 104.8333 | 4.176 | 15.43 | 35.5494 | 115.7036 | 15.1832 | 304.3245 | 150.4534 | 303.2375 | 17.8047 | 66.7643 | 15.9911 | 213 | 2.0128 | 111.5979 | 330.8071 | 0.083174
2684 | 931.6425 | 2.9489 | 49.5713 | 87.3774 | 82.6682 | 7.0153 | 99.7777 | 3.6956 | 12.0598 | 33.0554 | 98.7122 | 10.0477 | 263.1036 | 134.0142 | 267.2044 | 10.3037 | 61.3037 | 15.6458 | 198 | 2.0306 | 102.305 | 306.3075 | 0
2685 | 900.5347 | 3.6089 | 38.3181 | 92.1231 | 83.1111 | 6.5945 | 91.3786 | 4.0772 | 8.8931 | 36.1995 | 95.7593 | 9.308 | 236.0801 | 119.1275 | 248.9248 | 9.3912 | 57.6225 | 15.247 | 196 | 2.066 | 99.1079 | 303.9096 | 0
2686 | 866.7327 | 3.0045 | 38.6985 | 90.3424 | 82.3959 | 7.2739 | 91.7537 | 4.0118 | 7.7869 | 38.1405 | 89.6916 | 8.921 | 207.9419 | 108.9567 | 243.2427 | 9.4561 | 56.9755 | 14.1065 | 174 | 2.0967 | 93.7299 | 305.8276 | 0
2687 | 846.399 | 2.1141 | 39.0096 | 86.8509 | 82.0953 | 7.5596 | 91.8195 | 3.6981 | 7.2653 | 37.3582 | 81.6192 | 8.6756 | 199.723 | 105.6866 | 229.0212 | 9.5132 | 56.535 | 13.4046 | 145 | 2.1237 | 79.4926 | 299.019 | 0
2688 | 835.5052 | 1.511 | 31.096 | 86.6869 | 82.6832 | 7.001 | 91.6616 | 3.8982 | 7.1826 | 36.7193 | 78.4005 | 8.7157 | 194.022 | 102.9899 | 224.2723 | 9.518 | 55.6843 | 13.3603 | 143 | 2.1617 | 71.0598 | 291.8776 | 0
2689 | 825.8503 | 1.5274 | 24.5858 | 86.9127 | 82.3723 | 7.2964 | 91.2047 | 4.1077 | 7.2809 | 36.8946 | 78.0877 | 8.7701 | 184.2342 | 98.9336 | 235.545 | 9.48 | 55.4618 | 12.7375 | 134 | 2.165 | 68.5206 | 291.3222 | 0
2690 | 818.5409 | 1.6616 | 24.2145 | 86.6769 | 82.7149 | 6.971 | 91.303 | 4.1482 | 7.1467 | 36.9716 | 77.7474 | 8.7319 | 177.552 | 96.9171 | 235.2247 | 9.7034 | 55.2489 | 11.9576 | 169 | 2.1536 | 66.6318 | 289.6101 | 0
2691 | 817.5239 | 1.7934 | 24.1895 | 87.2461 | 82.397 | 7.2729 | 92.119 | 4.2774 | 7.043 | 38.7734 | 78.1813 | 8.6771 | 163.461 | 95.96 | 220.701 | 10.1275 | 54.9642 | 11.6877 | 136 | 2.1378 | 68.0603 | 288.516 | 0
2692 | 826.6536 | 2.0786 | 28.6779 | 87.5982 | 81.9833 | 7.666 | 92.5826 | 4.5839 | 6.9131 | 45.3901 | 78.7436 | 8.6901 | 158.921 | 92.8395 | 215.7297 | 10.4089 | 55.8805 | 11.6965 | 135 | 2.1331 | 69.5156 | 303.5438 | 0
2693 | 848.0628 | 2.6498 | 31.9673 | 86.1614 | 81.4637 | 8.1596 | 92.0328 | 4.7041 | 6.9324 | 52.7166 | 77.1528 | 8.6405 | 160.4645 | 96.2799 | 214.9046 | 10.0879 | 57.2649 | 11.5833 | 126 | 2.1335 | 72.5023 | 330.0327 | 0
2694 | 888.1056 | 3.1504 | 47.51 | 87.3209 | 79.8274 | 9.7141 | 102.0052 | 4.8123 | 6.5142 | 62.0106 | 80.6686 | 14.3815 | 167.0403 | 121.1212 | 234.9836 | 13.5379 | 56.9533 | 11.4503 | 186 | 2.2234 | 91.7942 | 366.1904 | 0.13905
2695 | 938.9223 | 3.7469 | 81.1753 | 93.4194 | 77.0633 | 12.34 | 123.2375 | 4.9493 | 5.8085 | 78.3823 | 104.8391 | 25.4726 | 217.311 | 172.8616 | 313.5842 | 24.4899 | 58.658 | 12.1574 | 243 | 5.1105 | 125.122 | 419.8092 | 0.24151
2696 | 1023.0877 | 4.1457 | 104.3974 | 108.5171 | 74.1676 | 15.0908 | 137.2903 | 5.7566 | 11.7092 | 92.9821 | 143.9519 | 29.7474 | 289.532 | 231.538 | 413.0145 | 34.3145 | 66.1525 | 13.8554 | 277 | 6.8984 | 149.4044 | 481.0049 | 0.29766
2697 | 1102.4595 | 4.0821 | 110.2112 | 122.5332 | 73.7225 | 15.5137 | 142.5818 | 6.1953 | 16.1914 | 94.6934 | 172.953 | 31.9651 | 327.7704 | 272.4152 | 484.6181 | 39.2941 | 75.6245 | 15.3337 | 318 | 7.4826 | 166.0286 | 523.345 | 0.32202
2698 | 1137.8924 | 3.7315 | 110.9868 | 127.4552 | 73.3479 | 15.8696 | 142.4638 | 6.5756 | 17.3204 | 88.124 | 184.2769 | 36.9473 | 366.976 | 295.2005 | 534.066 | 41.8723 | 82.3707 | 16.48 | 368 | 8.0507 | 179.1432 | 535.3521 | 0.3549
2699 | 1156.9275 | 3.9039 | 110.7901 | 131.4761 | 73.8073 | 15.4332 | 133.7751 | 6.3563 | 18.1855 | 81.2144 | 188.665 | 38.152 | 399.9404 | 309.3142 | 557.745 | 39.8104 | 84.5483 | 16.6607 | 336 | 6.9284 | 206.3362 | 543.4229 | 0.30307
2700 | 1137.2218 | 4.1271 | 110.7041 | 130.8217 | 74.6925 | 14.5922 | 129.0493 | 5.0461 | 17.3245 | 73.6624 | 189.8729 | 37.5142 | 408.7519 | 313.2644 | 564.4277 | 38.5243 | 83.3135 | 16.9217 | 361 | 6.7848 | 213.0648 | 548.8651 | 0.28894
2701 | 1126.4935 | 3.9209 | 110.7041 | 130.8532 | 74.9378 | 14.3592 | 129.7665 | 5.4247 | 17.4502 | 75.4504 | 190.2258 | 36.5678 | 411.6087 | 309.648 | 564.7206 | 39.1122 | 82.5105 | 18.0158 | 311 | 8.3256 | 210.9611 | 543.2015 | 0.32583
2702 | 1124.0735 | 3.8204 | 110.7041 | 131.6103 | 74.551 | 14.7266 | 125.9324 | 6.2058 | 19.2778 | 86.4889 | 193.8227 | 33.6891 | 419.0919 | 303.3109 | 545.256 | 38.7682 | 84.0045 | 18.72 | 302 | 9.1712 | 208.7544 | 541.6859 | 0.32268
2703 | 1096.8915 | 3.64 | 110.7041 | 127.5175 | 74.6992 | 14.5858 | 117.1732 | 6.0508 | 19.2819 | 91.3429 | 195.1336 | 30.9704 | 425.8476 | 289.835 | 525.023 | 37.5965 | 85.3668 | 18.2299 | 304 | 8.5629 | 201.4368 | 541.0795 | 0.27958
2704 | 1052.694 | 3.5479 | 110.7041 | 122.466 | 80.7192 | 8.8669 | 105.0072 | 4.7291 | 16.1732 | 86.6596 | 192.2819 | 28.9552 | 413.6569 | 264.8209 | 482.4753 | 24.7477 | 83.5561 | 17.0134 | 295 | 7.8475 | 181.3035 | 503.2456 | 0.2629
2705 | 1004.4197 | 3.1805 | 90.3638 | 112.8232 | 84.0184 | 5.7326 | 97.0582 | 2.9999 | 14.391 | 70.4378 | 180.5422 | 25.8461 | 402.5285 | 215.6294 | 397.6418 | 11.4904 | 77.8705 | 16.2393 | 256 | 7.6338 | 154.8109 | 428.3494 | 0.2483
2706 | 961.6363 | 2.336 | 53.1736 | 98.6112 | 83.3965 | 6.3234 | 93.4192 | 3.1089 | 14.0847 | 46.9093 | 145.0468 | 19.3721 | 357.3784 | 158.8991 | 319.0253 | 8.8079 | 71.1916 | 15.7305 | 224 | 7.7355 | 134.2107 | 359.4649 | 0.18799
2707 | 908.9784 | 2.3196 | 38.4192 | 90.1597 | 83.7364 | 6.0005 | 86.4938 | 3.7614 | 12.5217 | 32.3043 | 104.0352 | 10.2426 | 308.1003 | 126.7967 | 275.3267 | 7.9353 | 65.2079 | 15.3268 | 201 | 7.8061 | 119.0769 | 313.4827 | 0.085548
2708 | 863.5785 | 3.2489 | 30.9383 | 87.4261 | 84.0697 | 5.6839 | 82.3077 | 3.8708 | 8.6262 | 29.131 | 82.9427 | 6.3263 | 277.2198 | 113.7023 | 257.1477 | 7.6528 | 59.5113 | 15.1814 | 191 | 7.8546 | 108.9031 | 294.015 | 0
2709 | 838.7389 | 3.6801 | 25.4009 | 89.4894 | 83.9751 | 5.7737 | 83.4688 | 4.0563 | 6.5743 | 30.5216 | 75.6043 | 7.8548 | 243.2197 | 108.2363 | 243.5331 | 8.2796 | 56.053 | 14.8111 | 194 | 7.9129 | 105.9519 | 294.0276 | 0
2710 | 829.9233 | 2.9852 | 25.3832 | 89.9674 | 84.0199 | 5.7312 | 84.2825 | 4.4239 | 7.0121 | 32.5152 | 74.1256 | 8.7948 | 230.8767 | 106.6706 | 226.5216 | 8.7616 | 54.9865 | 13.7276 | 176 | 7.9782 | 94.3482 | 297.1862 | 0
2711 | 817.0902 | 2.177 | 25.5877 | 89.1139 | 83.5021 | 6.2231 | 84.7902 | 4.4632 | 7.1522 | 32.6067 | 74.0721 | 8.7962 | 227.0089 | 103.955 | 217.8854 | 8.7452 | 55.0596 | 12.9384 | 175 | 8.0345 | 69.8583 | 300.4101 | 0
2712 | 806.2679 | 1.9139 | 25.7883 | 89.2673 | 83.7159 | 6.02 | 84.8123 | 4.4198 | 7.0097 | 32.3652 | 73.5495 | 8.765 | 216.6128 | 100.9794 | 220.5589 | 8.7512 | 55.5652 | 13.1484 | 170 | 8.0528 | 60.2463 | 301.1687 | 0
2713 | 801.1444 | 1.676 | 24.6361 | 89.2541 | 84.0127 | 5.738 | 84.3737 | 4.6361 | 6.949 | 32.8721 | 73.6135 | 8.9325 | 210.2645 | 98.325 | 234.63 | 8.7177 | 55.5782 | 13.2094 | 165 | 8.0595 | 59.8205 | 299.5118 | 0
2714 | 799.259 | 1.5275 | 24.4684 | 89.591 | 83.3813 | 6.3378 | 78.8352 | 5.0354 | 6.962 | 33.2516 | 73.9645 | 8.8638 | 207.9175 | 94.4379 | 243.4801 | 8.7459 | 55.4539 | 13.1728 | 172 | 8.0496 | 58.9544 | 298.4559 | 0
2715 | 800.0322 | 1.5706 | 24.9349 | 89.4208 | 83.0234 | 6.6778 | 69.5908 | 5.1642 | 6.9069 | 34.0207 | 74.6564 | 8.7146 | 205.6785 | 91.5096 | 235.3243 | 8.7364 | 55.3825 | 12.8909 | 138 | 8.0771 | 57.4854 | 296.7533 | 0
2716 | 794.4879 | 1.8687 | 36.5445 | 90.3106 | 83.6684 | 6.0651 | 71.7832 | 5.1424 | 6.9142 | 37.3177 | 75.1278 | 8.7367 | 196.196 | 90.2131 | 219.8812 | 8.7715 | 56.1089 | 12.4041 | 138 | 8.0319 | 58.1319 | 294.6578 | 0
2717 | 801.5622 | 2.758 | 44.8907 | 89.3986 | 84.0895 | 5.665 | 80.2699 | 5.0067 | 6.8783 | 41.2489 | 74.3181 | 7.4626 | 182.2552 | 87.8359 | 208.0683 | 8.4724 | 57.4732 | 12.0711 | 129 | 8.0207 | 57.773 | 287.5682 | 0
2718 | 816.6107 | 2.2698 | 44.8907 | 87.1448 | 82.8321 | 6.8596 | 82.6443 | 4.7967 | 6.4392 | 43.2316 | 72.6831 | 5.9535 | 178.9085 | 86.1943 | 206.3837 | 8.2072 | 57.0078 | 11.7474 | 130 | 8.0519 | 58.0013 | 272.7498 | 0.10115
2719 | 829.1835 | 1.4783 | 44.8907 | 86.429 | 81.5124 | 8.1133 | 87.6713 | 4.7475 | 6.9225 | 42.8912 | 75.938 | 7.2459 | 176.7496 | 92.6609 | 212.8569 | 8.1721 | 56.9521 | 11.8935 | 125 | 8.0514 | 59.8916 | 260.6692 | 0.25374
2720 | 841.7323 | 1.6978 | 59.9146 | 87.76 | 80.9568 | 8.6411 | 104.568 | 4.4268 | 9.251 | 44.248 | 96.6911 | 14.0745 | 186.489 | 104.0851 | 225.1088 | 7.8155 | 59.9552 | 13.0275 | 131 | 8.0441 | 71.315 | 260.0192 | 0.31141
2721 | 854.3859 | 2.0478 | 71.768 | 89.4941 | 82.2879 | 7.3765 | 115.092 | 3.9318 | 9.1992 | 51.6617 | 128.6951 | 18.9166 | 200.6094 | 112.7493 | 234.6203 | 7.3615 | 61.2828 | 13.7431 | 149 | 7.9805 | 98.9953 | 262.6115 | 0.34806
2722 | 865.4891 | 2.534 | 75.8808 | 90.0143 | 82.4459 | 7.2265 | 115.6402 | 3.6534 | 11.1832 | 57.9718 | 141.6624 | 16.5007 | 220.7012 | 118.866 | 240.8557 | 7.2768 | 59.8209 | 13.7003 | 161 | 7.9394 | 113.3638 | 263.0856 | 0.36023
2723 | 885.9009 | 2.6972 | 78.9589 | 90.4439 | 82.0535 | 7.5992 | 113.7322 | 3.4997 | 13.4675 | 59.6531 | 125.9197 | 15.0856 | 240.3901 | 123.01 | 247.2582 | 7.2802 | 60.4456 | 13.3164 | 163 | 7.9703 | 112.5115 | 259.2451 | 0.29224
2724 | 884.5221 | 2.5059 | 79.2284 | 92.5547 | 83.3288 | 6.3877 | 111.4439 | 2.8783 | 13.5163 | 58.5814 | 103.3596 | 15.8065 | 246.4039 | 128.1097 | 250.6741 | 7.2984 | 62.176 | 13.0297 | 189 | 7.9304 | 111.0348 | 246.6929 | 0.28973
2725 | 871.0492 | 2.1694 | 65.5245 | 95.6746 | 84.0287 | 5.7228 | 112.6822 | 3.5632 | 13.772 | 54.6003 | 93.8125 | 15.8356 | 245.9658 | 132.8494 | 250.3624 | 7.3424 | 60.5249 | 13.2748 | 225 | 7.8401 | 110.4575 | 233.1966 | 0.32198
2726 | 871.1469 | 3.5622 | 37.7966 | 92.6648 | 83.4338 | 6.288 | 106.7449 | 4.1128 | 14.4133 | 49.8884 | 92.9916 | 17.1669 | 243.0798 | 133.3823 | 246.9857 | 7.2701 | 56.7788 | 13.2615 | 271 | 7.8164 | 110.9478 | 227.4527 | 0.25167
2727 | 865.2555 | 3.4415 | 25.0368 | 90.1797 | 83.6957 | 6.0391 | 99.047 | 4.0204 | 15.0217 | 41.0289 | 92.157 | 17.326 | 235.2545 | 135.4551 | 259.0014 | 7.2828 | 54.8343 | 12.9444 | 252 | 7.8006 | 103.3547 | 220.3998 | 0.21956
2728 | 875.8182 | 1.7617 | 24.479 | 90.3613 | 84.0296 | 5.722 | 97.0418 | 3.8754 | 15.0155 | 27.6368 | 91.317 | 11.534 | 231.0932 | 138.8225 | 273.1272 | 7.2565 | 55.3809 | 12.8929 | 261 | 7.761 | 81.1249 | 213.1199 | 0.23405
2729 | 874.4917 | 1.9905 | 24.1647 | 90.8795 | 84.0358 | 5.7161 | 97.2004 | 2.5154 | 15.0959 | 19.889 | 91.0368 | 6.0856 | 234.8884 | 138.938 | 271.049 | 7.2598 | 56.8866 | 13.5923 | 304 | 7.7998 | 70.8217 | 213.1006 | 0.18207
2730 | 852.7167 | 1.8181 | 24.1224 | 89.807 | 83.4571 | 6.2659 | 89.6892 | 3.0808 | 15.0036 | 19.8447 | 90.4043 | 6.7186 | 235.9841 | 128.7761 | 247.433 | 7.2966 | 59.1397 | 13.6763 | 270 | 7.8117 | 71.3975 | 216.9786 | 0.11257
2731 | 832.2445 | 1.5367 | 24.078 | 88.0578 | 83.6859 | 6.0485 | 82.887 | 4.1617 | 13.1651 | 20.8172 | 86.7626 | 8.7406 | 232.5708 | 112.189 | 218.1962 | 7.3161 | 61.597 | 13.4195 | 260 | 7.868 | 71.2131 | 221.76 | 0.050966
2732 | 819.6828 | 2.7042 | 24.4552 | 87.2098 | 84.0211 | 5.7301 | 81.7837 | 4.1946 | 9.2814 | 21.5053 | 80.9806 | 7.6453 | 222.8013 | 108.0919 | 206.602 | 7.8806 | 61.3733 | 13.0887 | 280 | 7.8972 | 72.377 | 227.8289 | 0
2733 | 804.3603 | 4.9062 | 24.7473 | 88.5725 | 83.4242 | 6.2971 | 81.3644 | 4.5397 | 7.0513 | 22.8602 | 78.3995 | 7.2315 | 211.7741 | 112.239 | 208.3743 | 8.4548 | 58.7484 | 13.0101 | 251 | 7.964 | 71.0044 | 233.7901 | 0
2734 | 790.3122 | 8.0967 | 24.7473 | 89.8053 | 83.6957 | 6.0392 | 81.8378 | 4.6942 | 7.0263 | 23.296 | 78.3875 | 7.7078 | 201.7077 | 112.3526 | 221.7068 | 8.6668 | 56.5748 | 13.0012 | 225 | 8.0693 | 67.9607 | 237.7347 | 0
2735 | 782.4995 | 9.2021 | 24.7459 | 90.0143 | 84.0432 | 5.709 | 79.491 | 4.8258 | 7.1057 | 22.9602 | 76.405 | 7.8113 | 198.3754 | 109.4939 | 237.4297 | 8.6712 | 55.6115 | 12.6118 | 214 | 8.1078 | 66.1055 | 239.6343 | 0
2736 | 795.3656 | 8.6848 | 24.7569 | 90.0978 | 83.4181 | 6.3029 | 70.0716 | 5.2281 | 7.161 | 22.825 | 74.3805 | 7.8182 | 202.94 | 104.4097 | 241.5244 | 8.6514 | 55.315 | 11.9224 | 217 | 8.0923 | 64.9938 | 236.7544 | 0
2737 | 801.6082 | 4.9526 | 24.116 | 89.9149 | 81.7722 | 7.8665 | 69.8738 | 5.4246 | 7.0717 | 22.8203 | 73.9422 | 7.7289 | 199.4856 | 99.7852 | 233.8578 | 8.6804 | 55.2691 | 11.445 | 175 | 8.0926 | 63.6958 | 236.6268 | 0
2738 | 788.0837 | 1.5582 | 23.3028 | 89.1973 | 80.4731 | 9.1006 | 77.041 | 5.4797 | 6.9508 | 23.3101 | 74.1708 | 7.7504 | 193.5102 | 99.7723 | 226.5643 | 8.6664 | 55.4255 | 11.5101 | 181 | 8.0475 | 62.0441 | 241.9901 | 0
2739 | 772.8148 | 1.3974 | 23.0802 | 88.7898 | 80.7032 | 8.8821 | 70.3638 | 5.6707 | 6.6801 | 23.6452 | 74.8977 | 7.7432 | 184.9386 | 102.2734 | 224.3194 | 8.6782 | 55.7348 | 11.5827 | 146 | 8.0034 | 61.8636 | 245.6213 | 0
2740 | 757.1682 | 3.239 | 23.6505 | 88.9758 | 81.0428 | 8.5595 | 63.1345 | 5.6808 | 6.834 | 23.0325 | 75.7485 | 7.7386 | 178.4396 | 100.3775 | 222.6079 | 8.6842 | 56.7174 | 11.3301 | 144 | 7.9978 | 61.6407 | 245.8413 | 0
2741 | 753.8881 | 7.7744 | 23.9111 | 87.1065 | 82.9302 | 6.7664 | 69.991 | 5.6761 | 6.9009 | 21.8307 | 75.7506 | 6.5986 | 186.9176 | 93.1035 | 223.9433 | 8.434 | 58.0022 | 11.4704 | 138 | 8.0576 | 59.738 | 238.2445 | 0
2742 | 760.0186 | 9.2199 | 24.0306 | 85.3407 | 83.424 | 6.2973 | 74.4636 | 5.3143 | 6.7518 | 20.903 | 74.3851 | 5.3701 | 194.8131 | 87.1715 | 225.0313 | 8.2064 | 57.1654 | 11.7421 | 133 | 8.0984 | 59.3097 | 227.719 | 0.04183
2743 | 769.4018 | 8.3674 | 24.005 | 85.8833 | 83.6781 | 6.0559 | 67.2925 | 4.8942 | 6.961 | 19.9114 | 73.6578 | 5.05 | 193.7883 | 86.6249 | 225.0317 | 8.3246 | 54.985 | 11.9478 | 129 | 8.0767 | 61.6252 | 223.2851 | 0.048108
2744 | 782.036 | 5.6741 | 23.8814 | 86.5949 | 83.4247 | 6.2966 | 63.0727 | 4.5269 | 8.5183 | 24.3176 | 74.7822 | 5.0655 | 189.3157 | 90.3861 | 227.5978 | 8.3281 | 54.3932 | 12.2051 | 117 | 7.9559 | 64.5349 | 229.3207 | 0.12115
2745 | 804.0107 | 2.3951 | 23.9346 | 86.9075 | 83.0156 | 6.6853 | 72.5479 | 4.2252 | 7.6647 | 37.8931 | 83.3485 | 6.8609 | 201.2675 | 94.1487 | 221.7402 | 7.9436 | 54.8743 | 12.2539 | 137 | 7.8732 | 65.4187 | 239.8618 | 0.12974
2746 | 836.0282 | 2.218 | 23.9666 | 87.0698 | 83.0429 | 6.6593 | 78.7468 | 4.2058 | 7.5619 | 50.1344 | 102.6418 | 9.2028 | 223.5097 | 99.1785 | 211.6267 | 7.4094 | 55.1878 | 12.211 | 158 | 7.8197 | 65.1365 | 240.0326 | 0.20345
2747 | 864.5574 | 2.2343 | 24.1595 | 87.429 | 83.7083 | 6.0272 | 68.9245 | 3.9846 | 11.5122 | 56.9844 | 112.1063 | 8.3304 | 236.4238 | 107.6445 | 207.0095 | 7.2768 | 55.5527 | 12.3551 | 179 | 7.7756 | 65.4772 | 234.9229 | 0.21504
2748 | 868.1078 | 1.9132 | 23.5279 | 89.3772 | 83.4331 | 6.2886 | 69.4508 | 3.8263 | 13.52 | 59.6028 | 103.9512 | 8.9474 | 239.8748 | 115.4285 | 208.7187 | 7.2489 | 56.017 | 12.708 | 176 | 7.7704 | 67.2719 | 237.532 | 0.22438
2749 | 874.9717 | 2.0045 | 22.8641 | 91.5023 | 83.6652 | 6.0682 | 78.5533 | 3.4144 | 13.4043 | 56.7587 | 97.6076 | 10.6177 | 248.729 | 122.3187 | 217.5588 | 7.2604 | 56.3443 | 12.8217 | 182 | 7.8218 | 69.9175 | 242.1664 | 0.20732
2750 | 883.1429 | 1.9142 | 22.8051 | 90.6562 | 82.775 | 6.9138 | 80.4248 | 3.0949 | 13.5102 | 52.191 | 97.8592 | 11.039 | 257.8186 | 134.4922 | 219.5373 | 7.3366 | 57.0613 | 12.8785 | 198 | 7.8273 | 71.8523 | 240.6701 | 0.18871
2751 | 873.8634 | 1.5782 | 22.8051 | 88.7709 | 82.6681 | 7.0154 | 81.3171 | 3.0126 | 13.7165 | 45.122 | 106.1745 | 10.6547 | 259.8108 | 142.2033 | 217.7047 | 7.2365 | 58.7777 | 12.8898 | 184 | 7.8247 | 74.367 | 239.402 | 0.18364
2752 | 866.0676 | 1.6241 | 22.9335 | 89.2248 | 83.7384 | 5.9986 | 90.8702 | 3.3717 | 13.8261 | 33.6016 | 116.2001 | 9.0482 | 256.966 | 136.8159 | 227.8552 | 7.2409 | 59.9901 | 12.859 | 171 | 7.8247 | 75.2625 | 240.0913 | 0.18866
2753 | 866.5737 | 1.8895 | 23.8894 | 90.039 | 84.0355 | 5.7164 | 94.178 | 4.1574 | 13.6361 | 24.1734 | 110.2876 | 9.2567 | 254.2803 | 131.6 | 242.2587 | 7.4829 | 60.1029 | 12.9472 | 166 | 7.7951 | 73.743 | 241.0129 | 0.15854
2754 | 857.9891 | 3.6541 | 24.7215 | 88.8107 | 84.069 | 5.6845 | 86.0183 | 4.6661 | 10.9509 | 21.5317 | 97.7347 | 9.9649 | 249.076 | 126.4406 | 266.3378 | 8.1129 | 60.3812 | 12.8856 | 159 | 7.7806 | 82.9042 | 239.3387 | 0.048743
2755 | 848.2167 | 3.721 | 24.8489 | 87.1816 | 83.4133 | 6.3075 | 73.0913 | 4.751 | 7.5224 | 21.3654 | 91.5915 | 7.9757 | 239.9443 | 115.7458 | 284.4654 | 8.3915 | 59.546 | 12.7287 | 148 | 7.7694 | 89.0854 | 235.4771 | 0.026169
2756 | 833.1304 | 3.185 | 24.8124 | 86.7571 | 83.6632 | 6.07 | 64.9637 | 4.8336 | 6.83 | 20.9289 | 85.3973 | 9.0793 | 231.4133 | 107.8812 | 258.7488 | 8.4226 | 57.123 | 12.4691 | 149 | 7.8018 | 86.6734 | 237.3959 | 0
2757 | 812.3834 | 3.53 | 24.7978 | 87.7595 | 83.4991 | 6.2259 | 72.3824 | 5.2103 | 7.3061 | 21.8934 | 79.7766 | 11.8378 | 220.7267 | 105.0797 | 225.7451 | 8.7176 | 55.7052 | 12.2563 | 142 | 7.8684 | 81.9025 | 245.8866 | 0
2758 | 798.8829 | 3.2427 | 24.752 | 88.5963 | 83.0626 | 6.6407 | 79.5414 | 5.46 | 7.6328 | 23.2337 | 78.4933 | 10.0632 | 206.7549 | 103.5718 | 216.6909 | 8.7625 | 56.0628 | 12.1643 | 140 | 7.9607 | 74.9282 | 253.4314 | 0
2759 | 779.4046 | 6.0768 | 24.668 | 88.7426 | 83.6205 | 6.1106 | 71.7985 | 5.848 | 8.2462 | 23.1708 | 77.1687 | 7.9663 | 197.1306 | 102.2566 | 215.499 | 8.7946 | 56.7244 | 11.9167 | 137 | 7.9854 | 69.5671 | 251.0385 | 0
2760 | 778.0386 | 6.8946 | 24.4454 | 88.7685 | 83.4009 | 6.3192 | 65.28 | 5.8215 | 7.8456 | 22.7219 | 75.3808 | 7.8368 | 194.219 | 99.5128 | 218.6566 | 8.8169 | 56.7825 | 11.5798 | 130 | 8.0149 | 68.1433 | 244.2549 | 0
2761 | 772.5839 | 3.1781 | 23.9764 | 88.5418 | 83.7092 | 6.0263 | 73.1406 | 5.6758 | 6.973 | 22.7901 | 74.3111 | 7.8515 | 185.3215 | 96.687 | 217.1968 | 8.7416 | 56.5155 | 11.4528 | 125 | 8.0096 | 66.5762 | 244.3507 | 0
2762 | 760.9225 | 1.3275 | 23.7365 | 89.4769 | 83.4255 | 6.2959 | 78.1268 | 5.8611 | 6.9445 | 23.3234 | 73.617 | 8.1448 | 175.7026 | 97.6366 | 212.6452 | 8.7537 | 56.2949 | 11.4289 | 138 | 7.9599 | 66.7639 | 250.0752 | 0
2763 | 764.21 | 1.4767 | 23.7365 | 89.8374 | 83.6326 | 6.0991 | 70.7787 | 5.9932 | 7.0155 | 25.6478 | 73.8957 | 8.4148 | 172.7262 | 101.7082 | 211.8367 | 8.8025 | 56.2035 | 11.4173 | 132 | 7.973 | 67.2029 | 256.1313 | 0
2764 | 770.9944 | 1.9775 | 23.7365 | 91.7879 | 83.4195 | 6.3016 | 65.514 | 6.185 | 6.91 | 32.701 | 74.2323 | 8.3775 | 173.2526 | 100.9751 | 213.0713 | 8.7184 | 57.1778 | 11.435 | 120 | 7.9887 | 66.2292 | 275.4197 | 0
2765 | 781.4811 | 2.7605 | 30.687 | 90.3483 | 83.0798 | 6.6242 | 73.2903 | 6.2089 | 6.9133 | 39.9087 | 72.8852 | 7.638 | 193.4855 | 100.8036 | 212.3165 | 8.4538 | 58.5451 | 11.3561 | 132 | 7.9481 | 77.6531 | 301.7982 | 0
2766 | 834.5348 | 3.6999 | 58.6116 | 47.0283 | 79.2713 | 10.2423 | 92.3756 | 6.5806 | 6.8058 | 54.065 | 86.1451 | 18.2097 | 216.7241 | 134.8613 | 239.0902 | 15.9039 | 59.8996 | 12.1604 | 181 | 9.9367 | 130.3271 | 341.912 | 0.043735
2767 | 879.7084 | 4.2282 | 75.3849 | 109.8473 | 77.0707 | 12.3329 | 103.0188 | 6.9888 | 11.3033 | 76.1003 | 115.9081 | 26.5147 | 240.6498 | 182.5491 | 281.9637 | 23.15 | 62.0987 | 12.8458 | 338 | 11.162 | 159.0883 | 391.6894 | 0.1171
2768 | 966.6689 | 9.3559 | 93.4411 | 122.4139 | 75.143 | 14.1643 | 121.6617 | 7.2763 | 14.8235 | 86.8073 | 143.4126 | 32.5917 | 254.9468 | 222.5801 | 342.4571 | 29.7477 | 68.8949 | 14.1903 | 336 | 12.6088 | 189.1068 | 434.7146 | 0.14698
2769 | 1070.5011 | 10.8029 | 106.9148 | 140.2764 | 74.0251 | 15.2262 | 147.4791 | 7.5978 | 20.1648 | 91.6825 | 168.2882 | 34.9994 | 346.9625 | 267.0927 | 450.303 | 37.982 | 84.1274 | 17.8351 | 384 | 12.4782 | 223.3504 | 488.3715 | 0.18657
2770 | 1107.0728 | 7.4962 | 106.9148 | 132.9556 | 72.8604 | 16.3327 | 148.7684 | 6.4282 | 24.7675 | 96.2082 | 183.1219 | 34.0212 | 420.0476 | 299.4359 | 535.6903 | 39.6121 | 99.8634 | 18.3882 | 425 | 12.8871 | 231.4341 | 532.9626 | 0.11308
2771 | 1139.6441 | 7.5762 | 112.4206 | 124.5162 | 74.017 | 15.2339 | 146.6132 | 5.4609 | 25.4033 | 96.8356 | 184.5931 | 35.2264 | 421.4195 | 316.4777 | 560.9891 | 38.7722 | 107.3542 | 17.5126 | 358 | 12.798 | 227.5248 | 554.7512 | 0.23842
2772 | 1162.411 | 9.4832 | 113.9798 | 129.3787 | 73.7622 | 15.476 | 151.0069 | 6.0491 | 23.2255 | 98.6999 | 185.4917 | 38.6246 | 434.8082 | 327.4852 | 562.9122 | 40.0477 | 107.505 | 17.6772 | 366 | 11.3006 | 225.7037 | 565.9922 | 0.23196
2773 | 1167.245 | 10.5269 | 112.0088 | 132.3666 | 72.9403 | 16.2568 | 151.7695 | 6.4316 | 22.6917 | 100.3291 | 190.8424 | 40.7698 | 447.257 | 332.9542 | 559.9379 | 41.9581 | 105.282 | 17.6823 | 302 | 10.6405 | 225.8867 | 570.3469 | 0.21097
2774 | 1167.245 | 10.5269 | 112.0088 | 132.3666 | 72.9403 | 16.2568 | 151.7695 | 6.4316 | 23.5877 | 100.3386 | 194.5231 | 40.7698 | 449.7657 | 334.2337 | 557.7564 | 41.9581 | 104.3424 | 17.6823 | 282 | 10.6405 | 225.8867 | 570.7957 | 0.20353
2775 | 1143.273 | 10.9028 | 107.5245 | 133.3886 | 73.8129 | 15.4278 | 149.0143 | 6.8344 | 23.5877 | 96.7585 | 197.1388 | 39.5705 | 449.7657 | 329.3452 | 551.1047 | 41.8331 | 104.7864 | 18.2612 | 280 | 10.0257 | 229.0566 | 568.8751 | 0.12408
2776 | 1097.1356 | 8.4413 | 104.3857 | 129.4793 | 77.7289 | 11.7076 | 128.531 | 6.8687 | 22.5831 | 87.946 | 199.3778 | 37.1249 | 444.6513 | 312.501 | 510.7088 | 33.2906 | 104.1211 | 18.3653 | 273 | 8.9949 | 214.3205 | 539.0188 | 0.16705
2777 | 1051.8318 | 5.101 | 99.8292 | 114.4809 | 80.7411 | 8.8461 | 117.3708 | 4.2654 | 20.8065 | 74.658 | 189.5728 | 31.4631 | 437.5097 | 267.8555 | 425.0973 | 17.0091 | 94.3291 | 17.217 | 233 | 8.6297 | 180.31 | 473.3622 | 0.15612
2778 | 990.1621 | 4.0401 | 95.6585 | 100.3049 | 82.9504 | 6.7472 | 116.1576 | 3.3145 | 18.6535 | 59.3648 | 157.3991 | 24.0418 | 424.5359 | 209.5351 | 348.7312 | 10.0923 | 78.5647 | 15.4974 | 216 | 8.7318 | 154.5222 | 410.0524 | 0.11018
2779 | 926.5963 | 3.1624 | 74.5131 | 92.7437 | 84.0015 | 5.7486 | 108.8895 | 4.2757 | 15.8493 | 46.5119 | 116.6158 | 12.3204 | 400.2215 | 171.5478 | 312.2257 | 9.6258 | 68.9381 | 13.9352 | 197 | 8.8073 | 136.4855 | 364.5471 | 0.058856
2780 | 898.0436 | 3.4954 | 60.44 | 87.6057 | 84.0731 | 5.6806 | 100.2384 | 4.5301 | 11.2639 | 37.9874 | 96.1064 | 6.1547 | 426.7328 | 148.8334 | 286.5653 | 9.3086 | 64.0097 | 13.2239 | 188 | 8.7878 | 123.7533 | 331.4405 | 0
2781 | 879.2679 | 4.0002 | 47.0369 | 88.0392 | 84.1178 | 5.6382 | 92.1059 | 4.8945 | 7.809 | 34.4773 | 92.0014 | 6.5886 | 401.2604 | 129.5566 | 270.9766 | 9.5847 | 60.7994 | 12.8984 | 167 | 8.8631 | 119.0001 | 317.4398 | 0
2782 | 840.3992 | 3.3754 | 37.7328 | 88.7162 | 82.833 | 6.8588 | 80.0914 | 5.0891 | 7.3588 | 32.8556 | 86.1769 | 6.9733 | 351.0744 | 115.8195 | 254.1038 | 9.8508 | 59.6469 | 12.7088 | 158 | 8.9585 | 109.4293 | 322.5696 | 0
2783 | 814.3488 | 2.1906 | 37.3975 | 88.5533 | 82.6325 | 7.0493 | 71.9191 | 5.2578 | 7.0599 | 30.6189 | 78.086 | 6.9457 | 332.8704 | 109.5121 | 238.6449 | 9.8177 | 58.669 | 12.1696 | 140 | 9.0134 | 89.7849 | 332.4564 | 0
2784 | 799.5989 | 1.4906 | 37.1589 | 88.2281 | 83.0762 | 6.6277 | 81.3717 | 5.4581 | 7.071 | 28.5773 | 73.6386 | 6.9671 | 316.7884 | 110.615 | 244.2188 | 9.7903 | 57.7571 | 12.13 | 135 | 9.0533 | 80.0815 | 332.6351 | 0
2785 | 786.7661 | 1.5428 | 37.0483 | 87.8289 | 83.6907 | 6.0439 | 87.1288 | 5.5644 | 6.9082 | 27.4439 | 74.5093 | 6.98 | 311.9563 | 110.8962 | 250.4358 | 9.6959 | 57.5465 | 11.9591 | 129 | 9.0713 | 78.2701 | 325.9611 | 0
2786 | 781.769 | 1.5067 | 37.2256 | 88.96 | 83.9787 | 5.7704 | 77.7923 | 5.5589 | 6.6975 | 26.9836 | 77.9774 | 6.9712 | 311.8548 | 106.6228 | 242.8863 | 9.5935 | 57.8027 | 11.5275 | 144 | 9.0566 | 75.1801 | 324.4434 | 0
2787 | 778.5964 | 1.3608 | 37.0016 | 91.0824 | 83.4389 | 6.2831 | 71.3351 | 5.5573 | 6.7646 | 28.7493 | 80.7399 | 6.9395 | 307.6582 | 102.8654 | 230.6322 | 9.567 | 57.9398 | 11.9726 | 125 | 9.0032 | 70.818 | 326.6564 | 0
2788 | 775.0419 | 1.6915 | 36.729 | 92.1907 | 83.693 | 6.0418 | 81.0268 | 5.7384 | 6.4463 | 35.7391 | 80.5846 | 6.9139 | 300.6729 | 99.7764 | 223.5295 | 9.6334 | 58.6067 | 12.0056 | 119 | 8.9726 | 67.7566 | 340.3772 | 0
2789 | 794.9073 | 2.9318 | 37.8605 | 92.424 | 83.3852 | 6.3342 | 84.9499 | 5.4427 | 6.2874 | 43.2252 | 77.3733 | 6.7677 | 292.4184 | 104.2504 | 222.0273 | 9.5115 | 60.0758 | 11.4504 | 128 | 8.9694 | 73.7912 | 368.0018 | 0
2790 | 836.7415 | 3.7711 | 60.8394 | 92.8382 | 81.0738 | 8.5299 | 86.7611 | 4.9564 | 6.3742 | 53.8164 | 80.8623 | 13.5325 | 296.316 | 133.8161 | 225.7584 | 13.2776 | 59.8359 | 11.1472 | 198 | 9.1535 | 107.5207 | 402.4132 | 0.019883
2791 | 902.1685 | 4.0649 | 76.3867 | 95.7646 | 77.5659 | 11.8625 | 106.3793 | 5.2216 | 8.6191 | 75.2158 | 104.8239 | 26.7378 | 420.556 | 190.6264 | 269.8992 | 25.7582 | 60.7506 | 12.0371 | 273 | 9.9767 | 152.8524 | 461.3206 | 0.050441
2792 | 1002.1988 | 4.1715 | 93.0478 | 106.7561 | 76.75 | 12.6375 | 132.3339 | 5.9604 | 15.1356 | 94.6399 | 142.6264 | 31.1995 | 443.3829 | 249.6115 | 371.4663 | 36.7 | 72.0548 | 13.8409 | 332 | 10.0448 | 184.6796 | 536.5441 | 0.08116
2793 | 1088.8532 | 4.0217 | 112.6578 | 122.3805 | 76.5069 | 12.8686 | 148.5678 | 6.6334 | 20.6712 | 102.4038 | 169.8072 | 33.3995 | 424.4991 | 294.4435 | 479.6402 | 40.3263 | 89.8861 | 15.2868 | 352 | 10.901 | 206.075 | 594.3745 | 0.15632
2794 | 1117.6486 | 3.8853 | 112.9787 | 131.0475 | 76.0603 | 13.2928 | 151.4253 | 6.8417 | 22.0915 | 105.6998 | 180.7423 | 40.0274 | 538.768 | 323.2751 | 542.0419 | 41.7958 | 101.995 | 16.3978 | 322 | 12.3971 | 212.865 | 616.8712 | 0.23681
2795 | 1149.6057 | 3.8408 | 111.4335 | 130.8662 | 74.717 | 14.5689 | 150.2662 | 5.9911 | 21.7974 | 106.6849 | 188.6414 | 42.4178 | 501.5618 | 339.9772 | 566.0171 | 41.1873 | 107.7885 | 16.8688 | 318 | 12.1965 | 217.4416 | 610.7381 | 0.20842
2796 | 1171.1105 | 3.9425 | 113.2192 | 127.9752 | 74.0312 | 15.2205 | 144.7059 | 5.3957 | 21.2212 | 100.0055 | 195.2311 | 41.6082 | 576.4511 | 345.0071 | 575.6655 | 41.009 | 108.7824 | 16.6075 | 311 | 12.0886 | 217.2864 | 592.1077 | 0.21332
2797 | 1165.9594 | 3.8615 | 113.2192 | 134.3946 | 74.0203 | 15.2308 | 138.3989 | 5.6922 | 20.0683 | 93.3922 | 202.6407 | 41.6788 | 501.7775 | 341.7677 | 573.541 | 42.8865 | 107.2448 | 16.4543 | 347 | 12.5358 | 219.5192 | 566.8163 | 0.25361
2798 | 1181.9087 | 3.9176 | 112.9765 | 138.8037 | 73.4217 | 15.7995 | 138.7552 | 5.3585 | 21.0475 | 98.6958 | 208.6323 | 41.2326 | 523.8773 | 339.0488 | 572.0879 | 42.1251 | 107.5154 | 16.2438 | 335 | 12.886 | 220.6462 | 556.2836 | 0.28192
2799 | 1164.033 | 4.1654 | 110.7708 | 135.6638 | 77.5765 | 11.8524 | 137.0306 | 5.1165 | 21.4833 | 100.9301 | 203.9769 | 40.2017 | 592.1795 | 332.4315 | 579.1648 | 39.0461 | 107.1914 | 16.5846 | 305 | 11.0583 | 212.9195 | 566.1233 | 0.21742
2800 | 1115.7314 | 4.086 | 105.8868 | 123.4041 | 82.5465 | 7.1309 | 131.4129 | 5.5888 | 18.2057 | 92.4805 | 194.4152 | 37.7241 | 499.3843 | 313.723 | 545.9273 | 31.4466 | 101.1779 | 16.3397 | 288 | 9.306 | 192.588 | 543.9753 | 0.17492
2801 | 1060.0335 | 3.6492 | 99.3021 | 108.738 | 84.6917 | 5.093 | 118.9748 | 4.6273 | 15.8988 | 81.2318 | 181.9952 | 35.2885 | 504.3546 | 263.7414 | 472.54 | 18.1215 | 88.1969 | 15.4359 | 238 | 8.9563 | 163.3262 | 471.7299 | 0.14449
2802 | 999.2791 | 2.6618 | 95.5321 | 99.4638 | 84.4199 | 5.3511 | 103.4249 | 3.3623 | 15.0574 | 62.1232 | 153.8804 | 28.5456 | 518.6159 | 198.6103 | 414.7023 | 11.3226 | 76.1076 | 14.7756 | 218 | 9.2505 | 142.9128 | 404.8433 | 0.085747
2803 | 951.5329 | 2.055 | 80.9989 | 96.182 | 84.0457 | 5.7067 | 93.3117 | 3.2725 | 12.7865 | 40.8548 | 118.0655 | 14.3934 | 417.7236 | 159.089 | 377.3342 | 9.8286 | 69.2635 | 14.1921 | 197 | 9.1525 | 124.8368 | 364.6911 | 0.01478
2804 | 914.776 | 3.1558 | 54.8461 | 92.1359 | 84.1093 | 5.6463 | 91.165 | 3.545 | 8.679 | 29.8137 | 98.8631 | 7.0337 | 403.6439 | 143.4103 | 332.7022 | 9.0488 | 63.4099 | 13.7308 | 189 | 9.047 | 114.4211 | 336.6211 | 0
2805 | 881.3318 | 4.1156 | 40.273 | 90.2625 | 84.029 | 5.7226 | 92.3052 | 3.9845 | 6.7314 | 28.3495 | 93.8844 | 7.8097 | 359.3393 | 136.52 | 280.7467 | 9.3541 | 59.5507 | 13.285 | 180 | 9.1324 | 108.9762 | 319.0691 | 0
2806 | 852.6908 | 3.7766 | 37.7544 | 91.0165 | 84.1004 | 5.6547 | 92.1833 | 4.2982 | 7.2159 | 29.2345 | 88.3864 | 8.7205 | 356.0504 | 130.9219 | 237.3891 | 9.923 | 59.1232 | 12.8006 | 164 | 9.1953 | 102.1141 | 311.8737 | 0
2807 | 831.1062 | 2.4026 | 36.8114 | 89.779 | 83.4059 | 6.3145 | 91.1441 | 4.3981 | 7.2693 | 27.6544 | 81.5116 | 8.8252 | 331.4193 | 123.8487 | 220.579 | 10.1958 | 59.5645 | 12.5128 | 141 | 9.2139 | 81.4688 | 309.4919 | 0
2808 | 827.9941 | 1.5386 | 36.2888 | 88.8251 | 83.6274 | 6.104 | 91.0119 | 4.4776 | 6.9894 | 24.5624 | 78.3577 | 8.6865 | 298.6373 | 121.1576 | 230.4144 | 10.0622 | 59.4533 | 12.4422 | 132 | 9.1988 | 66.8636 | 304.7943 | 0
2809 | 825.399 | 1.5712 | 36.8181 | 88.786 | 84.0494 | 5.7032 | 90.5057 | 4.8536 | 6.7349 | 22.4619 | 77.8576 | 8.4868 | 295.4237 | 118.5042 | 240.2453 | 10.0727 | 58.9355 | 12.5251 | 127 | 9.1966 | 66.7286 | 302.5033 | 0
2810 | 807.5289 | 1.3825 | 36.9484 | 88.3629 | 83.4727 | 6.251 | 83.0979 | 4.9532 | 6.5742 | 21.7185 | 77.1037 | 8.4499 | 299.9569 | 113.8368 | 238.4605 | 10.1164 | 58.7108 | 12.7611 | 144 | 9.2249 | 64.5874 | 306.1272 | 0
2811 | 805.8273 | 1.4325 | 36.6955 | 88.3303 | 83.6833 | 6.051 | 76.3932 | 4.8651 | 6.5244 | 23.2273 | 77.0466 | 8.4493 | 295.3255 | 111.9935 | 228.3145 | 10.1074 | 58.8615 | 12.7196 | 125 | 9.2329 | 60.7176 | 308.7634 | 0
2812 | 814.2483 | 2.0621 | 36.5106 | 88.1022 | 84.0247 | 5.7266 | 83.0448 | 4.8896 | 6.409 | 29.3575 | 77.0999 | 8.4132 | 284.8707 | 111.1264 | 217.6912 | 9.9845 | 59.7407 | 11.8698 | 129 | 9.2014 | 58.8486 | 317.9349 | 0
2813 | 825.9201 | 2.8471 | 37.4629 | 86.8027 | 83.4858 | 6.2385 | 85.3725 | 4.6517 | 6.3249 | 36.2316 | 75.4006 | 7.8672 | 274.6738 | 111.805 | 211.4002 | 9.7103 | 60.977 | 11.168 | 133 | 9.1495 | 65.1005 | 340.324 | 0
2814 | 867.2562 | 3.6138 | 49.2476 | 91.0723 | 81.2674 | 8.346 | 86.8996 | 4.8866 | 6.5882 | 48.171 | 80.8739 | 12.7435 | 357.1723 | 130.2129 | 219.5954 | 13.7568 | 60.4957 | 11.0041 | 203 | 9.607 | 100.3169 | 377.8209 | 0.042769
2815 | 923.6361 | 3.9684 | 80.209 | 95.9952 | 77.5613 | 11.8669 | 107.2976 | 5.4296 | 8.1883 | 68.9648 | 108.2751 | 27.8336 | 312.554 | 181.9767 | 270.9058 | 24.7892 | 61.2577 | 11.969 | 260 | 10.8675 | 151.8666 | 434.7147 | 0.077948
2816 | 992.9175 | 4.1616 | 104.9502 | 110.2823 | 75.1701 | 14.1385 | 136.3864 | 5.8962 | 14.122 | 80.6497 | 149.3263 | 36.8901 | 358.2138 | 247.6725 | 349.4046 | 35.1639 | 68.1172 | 13.5638 | 287 | 11.8351 | 193.2457 | 502.9187 | 0.1122
2817 | 1063.3844 | 6.5885 | 110.6347 | 127.4085 | 73.6715 | 15.5622 | 153.6006 | 6.3569 | 18.5588 | 79.4703 | 181.7916 | 37.653 | 496.9384 | 292.5965 | 427.7357 | 40.2129 | 78.1634 | 15.0273 | 330 | 11.9783 | 218.6819 | 562.1923 | 0.21307
2818 | 1106.5719 | 9.7064 | 110.837 | 132.6008 | 75.0184 | 14.2826 | 156.7858 | 7.0724 | 18.6952 | 80.4703 | 198.1203 | 39.9236 | 466.3636 | 310.4847 | 486.83 | 42.8129 | 85.5288 | 16.2586 | 372 | 13.8487 | 230.3334 | 589.3318 | 0.15498
2819 | 1128.1407 | 9.0888 | 110.837 | 131.2299 | 75.5401 | 13.787 | 157.8254 | 6.8956 | 17.9917 | 83.5583 | 202.4168 | 40.6402 | 492.6633 | 317.7342 | 521.5218 | 43.2321 | 88.7694 | 18.608 | 335 | 14.8484 | 227.6058 | 593.5888 | 0.19701
2820 | 1127.1664 | 5.989 | 110.2179 | 129.2937 | 75.6019 | 13.7283 | 159.4094 | 6.5611 | 18.357 | 85.6117 | 200.5892 | 39.346 | 518.6402 | 320.8292 | 535.5038 | 42.3359 | 88.6249 | 18.7026 | 355 | 15.1635 | 219.5538 | 597.5833 | 0.20664
2821 | 1119.666 | 4.1897 | 112.3219 | 133.1995 | 72.9006 | 16.2945 | 156.1081 | 7.254 | 19.5913 | 90.8859 | 202.1425 | 39.291 | 527.1916 | 321.0948 | 531.6553 | 42.1869 | 87.0722 | 17.7763 | 303 | 14.7028 | 226.1439 | 598.433 | 0.18335
2822 | 1141.5156 | 4.0179 | 115.1673 | 136.8649 | 72.4987 | 16.6763 | 150.9318 | 7.4045 | 21.1526 | 97.5291 | 210.2973 | 39.826 | 525.7864 | 326.2991 | 532.6867 | 41.4276 | 87.3941 | 18.1524 | 311 | 12.5264 | 230.8471 | 593.3341 | 0.20083
2823 | 1142.9325 | 5.0395 | 112.8515 | 136.8647 | 74.8774 | 14.4165 | 149.2157 | 7.0957 | 21.6755 | 101.6187 | 213.8091 | 37.8745 | 534.2711 | 329.6637 | 536.3082 | 39.3318 | 89.0609 | 18.5315 | 302 | 10.3173 | 229.3169 | 585.4749 | 0.14686
2824 | 1103.3102 | 4.8736 | 107.5376 | 130.6261 | 77.2657 | 12.1476 | 142.6214 | 5.4418 | 19.5727 | 99.7092 | 207.0547 | 33.1964 | 539.8402 | 315.4124 | 500.1224 | 31.9284 | 88.1348 | 18.9174 | 304 | 8.8527 | 205.8503 | 554.0579 | 0.14414
2825 | 1044.2932 | 3.565 | 100.1577 | 115.1881 | 81.1959 | 8.4139 | 125.5633 | 3.5945 | 17.1193 | 86.7429 | 190.2172 | 30.2691 | 503.6222 | 269.5015 | 420.2644 | 18.7792 | 82.7516 | 18.674 | 243 | 8.2569 | 169.7748 | 486.5468 | 0.069417
2826 | 979.4565 | 2.9084 | 96.2896 | 102.0894 | 83.671 | 6.0626 | 106.7856 | 3.4759 | 16.5921 | 64.8348 | 156.357 | 28.6378 | 450.8357 | 205.8875 | 346.1506 | 11.3417 | 75.2283 | 17.5361 | 229 | 8.3082 | 151.616 | 417.688 | 0.061073
2827 | 944.6294 | 2.7741 | 79.1667 | 95.3327 | 83.4242 | 6.2971 | 93.7691 | 3.8029 | 14.9604 | 43.9952 | 119.3991 | 19.5883 | 396.5608 | 156.4943 | 305.9495 | 9.6521 | 67.897 | 16.0931 | 204 | 8.4691 | 141.5598 | 370.2671 | 0.023467
2828 | 929.2817 | 3.1946 | 51.4184 | 90.8996 | 83.7091 | 6.0264 | 89.2941 | 4.0111 | 10.8608 | 31.2726 | 102.8373 | 13.5245 | 413.2793 | 130.3676 | 286.5343 | 9.2527 | 61.1602 | 14.7184 | 195 | 8.5788 | 133.1021 | 347.3678 | 0
2829 | 894.3565 | 3.7633 | 37.1478 | 90.2926 | 84.0898 | 5.6648 | 92.0472 | 4.9869 | 9.0538 | 27.2252 | 98.8279 | 12.6684 | 319.0405 | 118.3559 | 279.4938 | 9.841 | 56.987 | 13.899 | 182 | 8.4433 | 129.8195 | 340.9161 | 0
2830 | 845.471 | 3.5722 | 35.2108 | 90.0265 | 83.4158 | 6.3051 | 91.6947 | 5.3045 | 8.6135 | 26.1823 | 90.8275 | 11.9762 | 330.7939 | 111.1322 | 262.3012 | 9.8681 | 55.8489 | 13.4076 | 166 | 8.3981 | 123.0336 | 335.7056 | 0
2831 | 825.1404 | 2.3389 | 35.1891 | 89.2073 | 83.6562 | 6.0767 | 81.7985 | 4.6966 | 7.4007 | 24.4573 | 80.5061 | 11.69 | 341.3556 | 105.0044 | 234.5724 | 9.9154 | 55.357 | 12.9725 | 146 | 8.4904 | 96.801 | 331.2421 | 0
2832 | 819.8313 | 1.6692 | 34.7146 | 89.2794 | 83.4569 | 6.266 | 82.8936 | 4.6638 | 6.8009 | 23.6113 | 76.1333 | 11.6873 | 320.0987 | 100.2776 | 225.2731 | 9.9537 | 54.8777 | 12.6744 | 147 | 8.5533 | 78.9478 | 329.5857 | 0
2833 | 815.1594 | 1.5044 | 34.4266 | 89.4394 | 83.6377 | 6.0943 | 91.1203 | 4.8442 | 6.9067 | 23.7229 | 75.9663 | 11.6665 | 341.9373 | 100.3851 | 227.478 | 9.9502 | 54.9024 | 12.078 | 143 | 8.5688 | 74.5174 | 329.0625 | 0
2834 | 803.3289 | 1.4652 | 34.8996 | 89.9966 | 83.4183 | 6.3027 | 85.42 | 5.2277 | 6.7966 | 24.0393 | 75.7316 | 11.5664 | 252.0636 | 99.8862 | 225.0978 | 9.9848 | 55.2351 | 11.662 | 157 | 8.5827 | 70.912 | 326.4197 | 0
2835 | 802.1722 | 1.4405 | 35.291 | 89.3645 | 83.6699 | 6.0637 | 76.0251 | 5.39 | 6.7359 | 25.9842 | 75.9887 | 11.7821 | 316.022 | 95.0171 | 219.8346 | 9.9648 | 55.3377 | 11.6492 | 123 | 8.5959 | 68.3448 | 326.28 | 0
2836 | 806.3504 | 1.7536 | 35.291 | 89.7168 | 83.4602 | 6.2629 | 81.8721 | 5.3599 | 6.7136 | 32.0543 | 76.2217 | 11.7189 | 239.2919 | 90.8943 | 216.868 | 9.9097 | 55.9098 | 11.6656 | 119 | 8.616 | 67.3542 | 339.4779 | 0
2837 | 822.5622 | 2.9628 | 35.291 | 89.574 | 83.0634 | 6.6398 | 87.9594 | 5.1849 | 6.4913 | 38.484 | 74.6791 | 11.4887 | 251.337 | 96.0943 | 215.3009 | 9.6066 | 57.0502 | 11.5192 | 117 | 8.4985 | 76.2101 | 364.6685 | 0
2838 | 867.2609 | 5.8172 | 49.4687 | 90.7331 | 81.1439 | 8.4634 | 87.8267 | 4.7218 | 6.1773 | 50.1257 | 79.1534 | 15.713 | 273.3048 | 123.4042 | 230.3584 | 13.4314 | 56.2454 | 11.339 | 193 | 8.5624 | 110.7906 | 403.9728 | 0.055459
2839 | 934.6766 | 9.3873 | 81.5865 | 92.5627 | 76.7803 | 12.6088 | 104.8322 | 5.0976 | 8.3066 | 72.9625 | 105.4786 | 26.3764 | 379.5096 | 177.4577 | 288.3347 | 25.3853 | 56.8061 | 11.8529 | 258 | 12.1438 | 157.8002 | 459.4253 | 0.060462
2840 | 1015.7985 | 10.2508 | 104.6754 | 111.1525 | 73.812 | 15.4287 | 134.7904 | 6.1579 | 14.3773 | 87.225 | 148.1431 | 32.2281 | 345.4265 | 235.7801 | 382.2614 | 36.8101 | 63.497 | 13.3169 | 313 | 13.3521 | 191.8433 | 512.1773 | 0.12256
2841 | 1080.2168 | 6.7555 | 112.2074 | 127.1407 | 74.3293 | 14.9372 | 151.3771 | 6.2562 | 19.2433 | 91.3526 | 181.7575 | 31.0428 | 418.1233 | 276.6022 | 476.8639 | 41.5383 | 72.8067 | 15.0202 | 314 | 12.3578 | 215.1742 | 561.1911 | 0.20447
2842 | 1126.5178 | 4.2738 | 112.5111 | 132.3414 | 74.1257 | 15.1307 | 169.2337 | 6.3643 | 19.6175 | 99.5552 | 195.0804 | 29.5012 | 470.105 | 301.4169 | 534.9899 | 41.6587 | 81.2609 | 16.4018 | 384 | 12.4082 | 227.6412 | 597.9511 | 0.19588
2843 | 1136.8165 | 3.954 | 111.8401 | 135.5054 | 73.4607 | 15.7624 | 162.5244 | 6.1187 | 18.3178 | 103.53 | 198.1522 | 31.6723 | 496.4145 | 312.1496 | 550.7722 | 40.5404 | 86.751 | 17.0104 | 356 | 12.86 | 231.3601 | 617.4712 | 0.20169
2844 | 1152.4623 | 3.9138 | 112.6056 | 131.8074 | 74.351 | 14.9166 | 142.8928 | 6.0605 | 17.9899 | 97.8477 | 197.2875 | 35.1145 | 511.5875 | 314.3989 | 559.5591 | 41.4571 | 86.8102 | 17.1027 | 368 | 13.0694 | 218.2488 | 626.1653 | 0.22695
2845 | 1181.5217 | 4.3546 | 115.8195 | 136.5555 | 74.2576 | 15.0053 | 137.4984 | 7.3704 | 17.3756 | 96.4665 | 192.6339 | 37.3374 | 560.0687 | 320.878 | 566.2186 | 43.0315 | 86.1966 | 17.4802 | 309 | 13.5156 | 220.1807 | 622.4497 | 0.24096
2846 | 1171.6658 | 4.0552 | 117.0186 | 144.581 | 72.7302 | 16.4564 | 142.4117 | 8.0659 | 16.9344 | 102.8385 | 191.1853 | 38.8529 | 477.0087 | 331.3263 | 576.8243 | 41.9961 | 89.1602 | 18.2944 | 299 | 12.6704 | 229.8745 | 610.9138 | 0.24034
2847 | 1158.0965 | 5.1505 | 113.1732 | 139.9889 | 74.6507 | 14.6319 | 145.873 | 7.6226 | 16.8264 | 106.1841 | 192.1231 | 38.468 | 501.0413 | 333.4191 | 581.1289 | 38.3594 | 91.0923 | 19.0943 | 287 | 11.1856 | 229.2497 | 593.3997 | 0.17042
2848 | 1114.858 | 4.7123 | 107.3715 | 128.2867 | 77.3359 | 12.081 | 140.4487 | 6.7479 | 17.7727 | 100.0367 | 189.3409 | 38.7087 | 518.3773 | 316.2384 | 533.0314 | 33.2435 | 89.0041 | 19.0073 | 278 | 9.9458 | 205.5917 | 549.0359 | 0.036091
2849 | 1041.0525 | 3.5683 | 99.6116 | 111.948 | 81.3839 | 8.2353 | 125.7606 | 5.8164 | 19.9414 | 82.7695 | 178.194 | 36.1217 | 496.0643 | 265.4702 | 446.5371 | 19.9002 | 82.9478 | 17.8618 | 228 | 9.0297 | 172.9494 | 474.594 | 0.023195
2850 | 975.7391 | 2.8688 | 96.163 | 98.8493 | 83.0849 | 6.6194 | 109.5119 | 4.5235 | 19.8278 | 61.7684 | 149.2672 | 28.1883 | 371.2332 | 200.7707 | 363.8114 | 11.2973 | 74.6566 | 16.7509 | 213 | 8.8034 | 157.8545 | 412.2511 | 0.015701
2851 | 931.2014 | 2.6307 | 71.891 | 93.8007 | 83.7612 | 5.9769 | 92.3768 | 3.8899 | 17.1482 | 45.3847 | 114.2802 | 14.0749 | 281.5687 | 159.8015 | 307.3615 | 10.1123 | 67.1511 | 16.0596 | 192 | 8.8983 | 148.4249 | 370.7428 | 0.010362
2852 | 908.5081 | 3.1047 | 55.9404 | 89.9306 | 84.0288 | 5.7228 | 84.7039 | 4.1258 | 14.5741 | 37.7029 | 96.1854 | 7.1372 | 266.2624 | 139.5815 | 274.2346 | 9.3643 | 61.2308 | 15.1941 | 175 | 8.9429 | 134.6275 | 347.0122 | 0
2853 | 879.3833 | 3.2637 | 43.3405 | 90.4715 | 84.0722 | 5.6815 | 89.7316 | 4.2228 | 13.424 | 38.02 | 91.7541 | 8.3507 | 256.8657 | 126.33 | 255.8447 | 9.5067 | 57.7148 | 14.226 | 174 | 8.9948 | 123.7069 | 342.0591 | 0
2854 | 851.0984 | 2.8182 | 35.1016 | 89.8677 | 83.3394 | 6.3776 | 89.8357 | 4.2417 | 10.288 | 39.5304 | 85.7354 | 9.0187 | 227.2488 | 116.0026 | 240.9593 | 9.7089 | 56.5298 | 13.7845 | 176 | 9.0163 | 111.6626 | 338.6321 | 0
2855 | 833.8698 | 1.8382 | 34.935 | 88.8317 | 83.7581 | 5.9799 | 79.9491 | 4.4631 | 7.4466 | 37.8624 | 75.9874 | 8.6232 | 203.5564 | 106.4861 | 221.727 | 9.6322 | 56.6519 | 13.3768 | 151 | 8.991 | 93.1681 | 331.7859 | 0
2856 | 825.9855 | 1.3493 | 34.7034 | 89.2729 | 84.0298 | 5.7218 | 80.6849 | 4.4485 | 6.7372 | 35.9825 | 70.9623 | 8.4545 | 196.2109 | 99.453 | 214.1896 | 9.6453 | 56.8842 | 12.9607 | 140 | 8.9929 | 79.3736 | 324.6983 | 0
2857 | 818.0382 | 1.3426 | 34.6138 | 89.3366 | 82.7555 | 6.9324 | 88.9021 | 4.2735 | 7.0869 | 35.5515 | 70.7625 | 8.4449 | 179.8716 | 97.2389 | 217.445 | 9.6485 | 56.7992 | 12.7671 | 136 | 9.0182 | 73.193 | 319.726 | 0
2858 | 801.6986 | 1.3182 | 34.6687 | 88.8025 | 82.0864 | 7.568 | 87.8597 | 4.3858 | 7.1813 | 35.5012 | 71.0908 | 8.4874 | 165.427 | 96.3636 | 218.7596 | 9.6494 | 56.7782 | 12.4222 | 148 | 9.0914 | 71.6055 | 319.0454 | 0
2859 | 800.1961 | 1.2052 | 34.5438 | 88.4487 | 83.3406 | 6.3765 | 78.6754 | 4.4648 | 7.058 | 37.1261 | 71.7855 | 8.5035 | 160.613 | 93.7743 | 225.2295 | 9.6836 | 56.5374 | 11.7238 | 124 | 9.0991 | 67.1593 | 320.2425 | 0
2860 | 800.7782 | 2.0535 | 34.4374 | 88.2779 | 84.1233 | 5.633 | 83.2293 | 4.5646 | 6.944 | 43.0684 | 71.8997 | 8.3632 | 165.8029 | 90.6685 | 226.1926 | 9.6004 | 57.1398 | 11.4273 | 127 | 9.0457 | 63.1569 | 332.4221 | 0
2861 | 819.8204 | 3.1238 | 35.1948 | 87.2766 | 83.3816 | 6.3376 | 90.782 | 4.358 | 6.8692 | 48.9964 | 70.1592 | 7.9973 | 169.8658 | 94.6124 | 224.1203 | 9.3173 | 58.459 | 11.2589 | 121 | 9.0017 | 66.8759 | 357.3365 | 0
2862 | 865.8435 | 3.2297 | 48.858 | 89.2565 | 81.7497 | 7.8879 | 98.3168 | 4.2596 | 6.7088 | 57.8956 | 75.6266 | 13.7273 | 186.8094 | 126.818 | 243.7943 | 12.9431 | 58.0668 | 11.0616 | 209 | 9.2764 | 92.0714 | 392.988 | 0.035963
2863 | 929.1796 | 3.5064 | 85.4893 | 94.557 | 76.4716 | 12.902 | 111.3489 | 5.0028 | 8.6539 | 76.4807 | 102.3085 | 30.0912 | 213.1097 | 185.7022 | 302.3599 | 24.4894 | 59.1922 | 11.7132 | 254 | 11.4208 | 126.6023 | 452.259 | 0.14919
2864 | 1017.0442 | 3.9705 | 104.1158 | 109.9691 | 75.4189 | 13.9021 | 129.8489 | 6.0287 | 13.888 | 91.693 | 142.2364 | 39.3233 | 264.8261 | 244.2328 | 396.6509 | 34.5403 | 66.0603 | 13.0461 | 274 | 13.4011 | 148.1572 | 522.391 | 0.20626
2865 | 1097.2959 | 4.115 | 108.444 | 124.9092 | 75.464 | 13.8592 | 144.9428 | 6.5168 | 16.982 | 93.9703 | 172.131 | 39.9678 | 332.3948 | 285.3143 | 489.5713 | 39.5546 | 75.5104 | 16.0982 | 359 | 12.766 | 173.0463 | 570.3694 | 0.22669
2866 | 1146.1628 | 4.0986 | 111.4904 | 127.8726 | 71.6457 | 17.4866 | 148.0155 | 5.9243 | 18.3399 | 91.1191 | 184.4441 | 40.5669 | 367.8771 | 309.6649 | 547.0231 | 42.4697 | 83.9865 | 16.8755 | 346 | 10.9833 | 196.2405 | 584.2044 | 0.18346
2867 | 1152.1024 | 3.9192 | 109.6563 | 127.3457 | 71.2474 | 17.865 | 147.5921 | 6.3665 | 19.917 | 90.4524 | 186.9918 | 39.9618 | 373.4465 | 325.7005 | 553.877 | 41.0565 | 88.8406 | 16.2713 | 317 | 10.4918 | 196.6893 | 590.4527 | 0.21004
2868 | 1129.4108 | 3.9351 | 108.2886 | 127.0964 | 72.0045 | 17.1458 | 146.4457 | 6.8842 | 19.5291 | 86.4704 | 187.7997 | 38.8856 | 382.7439 | 327.5932 | 538.1568 | 40.6384 | 87.1727 | 16.8133 | 330 | 12.4287 | 185.1489 | 601.485 | 0.2793
2869 | 1132.6827 | 3.9817 | 110.9103 | 127.101 | 73.4804 | 15.7437 | 127.5663 | 6.8899 | 19.362 | 81.9547 | 192.7926 | 35.3977 | 394.3234 | 319.2614 | 541.7437 | 41.0431 | 84.0779 | 17.5076 | 304 | 13.9083 | 190.9145 | 598.2858 | 0.29517
2870 | 1133.3133 | 3.841 | 111.5022 | 132.7197 | 75.2483 | 14.0642 | 119.472 | 6.3109 | 23.22 | 86.5306 | 197.6541 | 35.4114 | 398.5291 | 315.3812 | 546.3548 | 40.4683 | 84.7435 | 17.9579 | 304 | 14.2428 | 190.5092 | 590.9618 | 0.28726
2871 | 1114.1098 | 4.0588 | 107.0702 | 129.4972 | 76.1443 | 13.213 | 121.0459 | 5.2765 | 24.3799 | 89.5956 | 193.818 | 37.1528 | 397.4691 | 309.233 | 529.6493 | 37.746 | 86.0485 | 17.9748 | 301 | 13.5076 | 178.8792 | 569.1307 | 0.22429
2872 | 1074.7958 | 3.7368 | 104.7866 | 127.5342 | 81.3086 | 8.3069 | 107.8741 | 4.0281 | 20.4959 | 84.3083 | 185.247 | 36.3546 | 376.2466 | 288.3262 | 482.6081 | 23.8056 | 83.8775 | 17.4527 | 277 | 12.7213 | 156.439 | 504.4027 | 0.13013
2873 | 1003.7369 | 2.9424 | 84.8745 | 114.981 | 84.0136 | 5.7372 | 89.1134 | 3.354 | 17.8142 | 74.0733 | 172.3545 | 34.8757 | 346.6463 | 235.8551 | 393.6245 | 12.2112 | 77.1136 | 16.4391 | 238 | 12.5506 | 127.3349 | 424.7793 | 0.072865
2874 | 941.805 | 2.4251 | 54.406 | 99.3128 | 84.0638 | 5.6895 | 78.3675 | 3.4031 | 16.518 | 59.4518 | 141.3553 | 27.4155 | 291.7586 | 170.9214 | 311.8136 | 10.5235 | 68.7245 | 15.77 | 204 | 12.6496 | 112.7797 | 367.9242 | 0.044683
2875 | 889.1043 | 3.3487 | 38.9306 | 91.2753 | 84.0783 | 5.6757 | 79.7428 | 3.4669 | 14.298 | 46.6502 | 103.0361 | 16.6712 | 257.1254 | 134.7607 | 267.1048 | 9.3974 | 61.5445 | 15.5233 | 200 | 12.696 | 103.4522 | 334.5721 | 0.014457
2876 | 856.8566 | 3.8594 | 32.6721 | 87.8924 | 84.0023 | 5.7479 | 85.0524 | 3.8377 | 10.608 | 41.5893 | 80.8631 | 11.9451 | 234.3384 | 124.3913 | 240.5676 | 8.8706 | 56.5186 | 14.9641 | 196 | 12.7711 | 94.8263 | 312.1858 | 0
2877 | 837.1436 | 3.4933 | 35.97 | 89.2921 | 84.0706 | 5.683 | 86.136 | 3.9994 | 9.32 | 41.8742 | 72.1058 | 10.9381 | 215.0798 | 121.1101 | 239.3627 | 8.5044 | 54.2993 | 14.0197 | 183 | 12.7858 | 90.0046 | 301.5385 | 0
2878 | 812.1011 | 2.9966 | 39.649 | 89.1504 | 83.4428 | 6.2794 | 85.3391 | 3.7674 | 8.9772 | 41.8014 | 69.053 | 10.3534 | 203.7517 | 116.9811 | 236.6325 | 8.4281 | 54.0337 | 13.5274 | 163 | 12.8085 | 83.6071 | 301.4887 | 0
2879 | 796.261 | 1.9144 | 39.8609 | 88.478 | 83.0085 | 6.692 | 85.284 | 3.5532 | 7.8541 | 40.1543 | 68.3535 | 10.2785 | 192.0119 | 109.5743 | 233.6573 | 8.7834 | 54.1386 | 13.1215 | 152 | 12.8952 | 68.8337 | 301.0828 | 0
2880 | 790.9174 | 1.2558 | 34.11 | 88.3184 | 83.6685 | 6.065 | 85.7461 | 3.6523 | 7.297 | 39.2994 | 68.3438 | 9.2418 | 182.6852 | 101.3776 | 238.2467 | 9.3547 | 54.1432 | 12.7959 | 149 | 13.0023 | 59.2916 | 298.3406 | 0
2881 | 787.0087 | 1.3651 | 26.9157 | 88.3507 | 83.5095 | 6.2161 | 85.5101 | 3.7895 | 7.3289 | 39.51 | 68.5721 | 8.5686 | 179.489 | 95.6131 | 233.8541 | 9.6571 | 54.0564 | 12.4093 | 135 | 13.0641 | 54.9191 | 299.0731 | 0
2882 | 787.4311 | 1.3831 | 25.1694 | 88.3522 | 84.3381 | 5.4289 | 84.9354 | 3.8959 | 6.9506 | 39.6319 | 68.2148 | 8.5475 | 182.042 | 92.3836 | 218.1711 | 9.5399 | 53.6543 | 11.8814 | 156 | 13.0702 | 53.1883 | 298.1664 | 0
2883 | 783.2357 | 1.2097 | 25.3893 | 88.2945 | 83.7147 | 6.0211 | 84.2373 | 4.0474 | 6.9229 | 40.145 | 68.3923 | 8.5156 | 179.282 | 90.9757 | 205.8352 | 9.5121 | 53.2511 | 11.6977 | 128 | 13.004 | 52.9946 | 291.2936 | 0
2884 | 783.3515 | 1.5403 | 25.3502 | 89.3466 | 83.6583 | 6.0747 | 84.1367 | 4.2673 | 7.0273 | 43.1405 | 68.7131 | 8.5435 | 170.6371 | 89.8915 | 205.8015 | 9.4832 | 54.1729 | 11.7291 | 125 | 13.0099 | 51.1729 | 285.4835 | 0
2885 | 784.7862 | 2.1649 | 27.9052 | 86.6686 | 84.1001 | 5.655 | 83.6962 | 4.2174 | 6.8313 | 46.7491 | 67.0083 | 7.5538 | 164.0576 | 87.2725 | 200.3068 | 9.1994 | 55.8735 | 11.5713 | 128 | 13.0759 | 50.2692 | 278.6646 | 0
2886 | 796.4717 | 1.5798 | 42.9034 | 85.1282 | 84.0313 | 5.7203 | 83.575 | 3.9257 | 6.2928 | 48.8082 | 67.205 | 7.0443 | 159.2397 | 86.3747 | 197.1858 | 8.5259 | 55.5299 | 11.3753 | 126 | 13.031 | 51.1113 | 269.9417 | 0.046171
2887 | 814.9421 | 1.2084 | 52.1539 | 85.303 | 84.0014 | 5.7487 | 83.666 | 3.6897 | 6.4106 | 48.4262 | 77.8771 | 9.3183 | 149.5803 | 89.957 | 201.2588 | 7.9225 | 53.4663 | 12.0049 | 139 | 12.9084 | 53.4139 | 268.4233 | 0.064583
2888 | 818.9347 | 1.3869 | 52.1539 | 85.8776 | 84.1064 | 5.649 | 81.6416 | 3.3091 | 11.166 | 49.1597 | 103.1982 | 14.5767 | 157.1061 | 95.992 | 211.689 | 7.9291 | 52.3106 | 12.7616 | 154 | 12.8285 | 62.205 | 271.7924 | 0.090262
2889 | 842.5945 | 1.6344 | 69.6261 | 87.6368 | 84.1234 | 5.6328 | 61.5162 | 2.2206 | 15.9358 | 56.459 | 132.1415 | 17.6087 | 178.1124 | 102.0138 | 225.9418 | 7.9188 | 52.7723 | 12.6452 | 160 | 12.6587 | 80.6164 | 274.123 | 0.10698
2890 | 870.7226 | 2.1391 | 79.4705 | 88.3276 | 84.0321 | 5.7196 | 48.9527 | 2.3826 | 16.1548 | 62.859 | 141.6096 | 17.9454 | 199.4703 | 106.4004 | 232.323 | 7.9155 | 54.8345 | 12.7014 | 163 | 12.6253 | 89.6852 | 277.5162 | 0.22191
2891 | 881.635 | 2.4415 | 78.4936 | 91.0404 | 84.6746 | 5.1092 | 57.8139 | 2.2418 | 15.7703 | 62.8739 | 123.3706 | 17.7288 | 215.6743 | 110.8896 | 226.4471 | 7.8966 | 57.0986 | 13.1452 | 177 | 12.659 | 91.1969 | 281.6427 | 0.15569
2892 | 884.3448 | 2.3618 | 78.8982 | 93.1984 | 84.4023 | 5.3679 | 62.861 | 2.1244 | 15.3425 | 60.9554 | 98.8295 | 20.3521 | 220.0324 | 120.1969 | 221.8087 | 7.8994 | 56.7669 | 13.339 | 174 | 12.6196 | 90.6422 | 282.367 | 0.17057
2893 | 881.6586 | 2.0687 | 72.3041 | 92.4323 | 84.0238 | 5.7274 | 59.2508 | 2.8329 | 15.148 | 59.2057 | 90.2186 | 22.7162 | 220.9464 | 130.7564 | 220.4714 | 7.9139 | 55.2216 | 13.4458 | 171 | 12.553 | 91.8266 | 281.9684 | 0.24895
2894 | 866.0992 | 1.7475 | 49.6212 | 90.8603 | 84.7537 | 5.0341 | 55.8824 | 2.2498 | 16.398 | 57.1081 | 95.3978 | 21.1355 | 220.1433 | 140.7194 | 224.7755 | 7.9412 | 54.611 | 13.2246 | 176 | 12.5348 | 95.2331 | 284.607 | 0.16837
2895 | 848.5619 | 1.5895 | 37.5408 | 89.2799 | 84.4088 | 5.3617 | 59.6116 | 3.2047 | 16.698 | 52.0388 | 107.938 | 18.4647 | 216.9223 | 143.5971 | 230.7405 | 7.921 | 54.0962 | 13.0878 | 185 | 12.5662 | 91.8961 | 286.2959 | 0.13988
2896 | 845.6973 | 2.3548 | 37.2329 | 88.2252 | 84.0024 | 5.7478 | 59.6576 | 4.2281 | 16.086 | 42.3619 | 112.4603 | 12.7134 | 211.1683 | 133.9116 | 233.844 | 7.9058 | 53.9497 | 13.2048 | 186 | 12.5652 | 80.6034 | 283.7943 | 0.13655
2897 | 838.334 | 3.6784 | 37.107 | 88.3068 | 84.0433 | 5.7089 | 71.1705 | 3.6462 | 16.524 | 31.3638 | 100.0576 | 12.9773 | 208.7031 | 122.0545 | 241.7544 | 7.8806 | 54.1643 | 13.2298 | 179 | 12.5588 | 75.4842 | 281.9414 | 0.097256
2898 | 810.3782 | 3.6804 | 37.3355 | 88.3849 | 84.7621 | 5.0261 | 82.1757 | 3.1578 | 18.448 | 23.3088 | 84.3189 | 11.5927 | 204.8144 | 110.1054 | 251.3474 | 7.9141 | 53.8165 | 13.161 | 184 | 12.6767 | 72.6304 | 279.9871 | 0.053238
2899 | 803.8717 | 3.467 | 37.5038 | 88.2505 | 83.7128 | 6.0229 | 82.758 | 2.7909 | 15.9026 | 19.7066 | 73.3699 | 8.0576 | 190.6649 | 100.6627 | 250.5087 | 8.0223 | 53.4472 | 13.9963 | 210 | 12.7738 | 71.283 | 277.7754 | 0.019606
2900 | 811.9791 | 4.5156 | 37.8432 | 88.9676 | 83.7445 | 5.9929 | 83.9324 | 3.0238 | 11.368 | 20.9832 | 69.5098 | 10.767 | 188.0143 | 98.8085 | 248.2184 | 8.0091 | 53.1795 | 14.5674 | 234 | 12.6999 | 71.3374 | 285.7575 | 0
2901 | 807.9074 | 4.9208 | 38.499 | 90.2436 | 84.035 | 5.7168 | 85.1526 | 3.5106 | 10.1221 | 26.2286 | 70.0389 | 14.7751 | 195.1825 | 100.387 | 247.0682 | 8.2641 | 52.96 | 13.829 | 237 | 12.6872 | 72.2857 | 304.5109 | 0
2902 | 794.694 | 3.8083 | 38.8111 | 90.5004 | 84.0205 | 5.7306 | 85.4073 | 4.0966 | 9.8973 | 29.2922 | 69.6376 | 13.4412 | 191.0611 | 106.8402 | 230.862 | 8.3214 | 53.3675 | 13.2897 | 248 | 12.8402 | 71.3837 | 312.3375 | 0
2903 | 785.4283 | 2.2115 | 38.6808 | 90.2349 | 84.0772 | 5.6768 | 85.3829 | 4.2515 | 8.1259 | 27.9306 | 68.2877 | 11.6411 | 257.798 | 113.8819 | 221.1403 | 8.4491 | 53.2716 | 13.5852 | 248 | 12.971 | 67.8495 | 305.1171 | 0
2904 | 776.8248 | 1.6948 | 38.3178 | 89.4478 | 84.0403 | 5.7118 | 85.5622 | 4.1376 | 7.342 | 26.6094 | 67.5624 | 11.5118 | 200.9219 | 113.2873 | 229.4512 | 8.4729 | 51.8068 | 13.6298 | 234 | 12.9497 | 63.6765 | 299.3305 | 0
2905 | 763.6452 | 1.8991 | 38.1335 | 89.928 | 82.1035 | 7.5518 | 85.6433 | 4.2105 | 7.134 | 26.541 | 67.4637 | 11.5347 | 154.1294 | 105.1942 | 228.2479 | 8.4667 | 50.4868 | 12.8883 | 218 | 12.8993 | 63.2577 | 295.5744 | 0
2906 | 758.0885 | 1.8984 | 38.1096 | 91.3545 | 79.7487 | 9.7889 | 85.6131 | 4.2691 | 7.042 | 27.0165 | 67.6073 | 11.6576 | 235.6368 | 100.3944 | 224.9848 | 8.4457 | 50.2296 | 12.4088 | 235 | 12.91 | 62.4459 | 292.545 | 0
2907 | 757.7604 | 1.7956 | 38.2244 | 90.487 | 80.3574 | 9.2105 | 84.9819 | 4.3528 | 7.124 | 28.279 | 68.2482 | 11.7282 | 151.0782 | 100.5293 | 226.8559 | 8.7893 | 50.2636 | 11.8816 | 201 | 12.9639 | 61.8741 | 299.0083 | 0
2908 | 760.6586 | 2.0327 | 38.0249 | 89.0098 | 81.6616 | 7.9716 | 84.6357 | 4.6789 | 7.3 | 29.7686 | 68.1945 | 11.4628 | 176.5373 | 95.5706 | 226.6866 | 9.2354 | 50.9673 | 11.3231 | 173 | 12.9695 | 60.2774 | 310.7123 | 0
2909 | 771.782 | 2.5236 | 37.6142 | 86.9848 | 82.6985 | 6.9865 | 84.3511 | 4.6018 | 6.8975 | 31.0312 | 66.0883 | 9.8322 | 256.1253 | 88.635 | 232.4179 | 9.0577 | 52.5066 | 11.1912 | 162 | 13.058 | 59.6143 | 313.5791 | 0
2910 | 780.1068 | 2.0019 | 37.6361 | 86.2252 | 83.7355 | 6.0013 | 86.7776 | 4.2542 | 6.2287 | 32.3744 | 67.0328 | 8.1841 | 195.6129 | 86.3533 | 230.95 | 8.9142 | 52.4574 | 11.1491 | 154 | 13.0217 | 59.0063 | 305.6879 | 0.11015
2911 | 782.9224 | 1.3713 | 37.6187 | 86.3666 | 84.0879 | 5.6666 | 81.5009 | 4.022 | 8.1718 | 31.9145 | 74.2974 | 7.5713 | 148.9428 | 89.4147 | 226.2467 | 8.576 | 51.0141 | 11.3986 | 147 | 13.0233 | 56.4677 | 290.9991 | 0.23758
2912 | 787.6428 | 1.4906 | 37.5464 | 87.425 | 84.0195 | 5.7316 | 79.7824 | 3.803 | 9.66 | 34.7987 | 80.4353 | 8.8995 | 238.9474 | 92.5116 | 228.0826 | 7.9928 | 50.1241 | 11.9738 | 142 | 12.9683 | 55.877 | 278.1799 | 0.2445
2913 | 790.6911 | 1.8576 | 37.0765 | 87.6954 | 84.0502 | 5.7024 | 88.7624 | 2.5534 | 10.3783 | 45.4602 | 81.2025 | 10.9652 | 160.5049 | 93.6136 | 223.1842 | 7.8588 | 49.357 | 12.2013 | 181 | 12.8079 | 58.0516 | 271.0697 | 0.27634
2914 | 816.1548 | 1.9428 | 36.9527 | 87.4906 | 84.0232 | 5.728 | 92.855 | 2.5812 | 8.012 | 50.7837 | 81.0502 | 11.2215 | 194.2284 | 97.2473 | 213.6168 | 7.9305 | 48.8053 | 12.1952 | 170 | 12.7298 | 61.6612 | 270.5023 | 0.30415
2915 | 835.2643 | 2.0413 | 37.1015 | 87.8889 | 84.0868 | 5.6677 | 91.2356 | 3.5286 | 9.9847 | 47.5732 | 83.438 | 11.4686 | 216.7203 | 107.7764 | 204.9544 | 7.9401 | 49.2237 | 12.3367 | 197 | 12.7805 | 63.68 | 277.0387 | 0.30151
2916 | 834.9617 | 2.1082 | 37.4949 | 88.9817 | 84.0791 | 5.675 | 86.0689 | 3.291 | 12.582 | 47.4898 | 86.7009 | 10.924 | 275.777 | 122.5803 | 201.6861 | 7.9209 | 50.0732 | 12.8007 | 175 | 12.8305 | 63.3863 | 281.7958 | 0.29882
2917 | 823.8757 | 2.3121 | 37.4501 | 89.9297 | 84.084 | 5.6703 | 85.5333 | 2.4326 | 10.629 | 47.9673 | 88.3483 | 8.9281 | 167.7976 | 129.2513 | 209.7462 | 7.8609 | 50.2707 | 13.1689 | 168 | 12.8702 | 63.1525 | 280.2467 | 0.31644
2918 | 823.5643 | 2.161 | 36.8963 | 91.0284 | 83.3872 | 6.3323 | 89.989 | 2.8841 | 11.7456 | 45.1542 | 88.4075 | 9.8518 | 185.0361 | 131.0483 | 228.9391 | 7.8952 | 50.1574 | 13.3383 | 190 | 12.8597 | 66.0689 | 276.5392 | 0.32814
2919 | 843.3825 | 2.046 | 36.9175 | 92.9516 | 83.7032 | 6.032 | 95.2071 | 3.4142 | 12.2246 | 42.5724 | 88.0988 | 11.5844 | 263.3065 | 137.4221 | 251.0058 | 7.9764 | 49.9833 | 13.4167 | 183 | 12.8515 | 68.1131 | 281.8155 | 0.29251
2920 | 841.7913 | 2.426 | 36.8593 | 93.7152 | 84.0227 | 5.7285 | 102.0184 | 2.2565 | 12.6317 | 37.5455 | 87.1776 | 11.8531 | 166.3983 | 137.4863 | 253.6088 | 7.9061 | 49.8192 | 13.6024 | 175 | 12.7764 | 67.882 | 281.3106 | 0.26569
2921 | 834.9479 | 2.4311 | 36.1608 | 92.0438 | 84.0905 | 5.6641 | 98.2872 | 1.6965 | 13.846 | 29.6965 | 85.644 | 10.0544 | 193.7923 | 127.2095 | 236.4563 | 7.884 | 50.2255 | 13.5421 | 156 | 12.6824 | 69.667 | 265.7619 | 0.23037
2922 | 827.4525 | 1.9654 | 35.3316 | 92.0194 | 84.6894 | 5.0951 | 85.8749 | 2.5112 | 14.1285 | 25.2552 | 85.5241 | 7.9993 | 267.3159 | 114.6148 | 225.828 | 7.8006 | 50.7267 | 13.2885 | 140 | 12.6548 | 70.2076 | 257.4239 | 0.13408
2923 | 815.7519 | 1.7436 | 39.1277 | 90.913 | 84.3792 | 5.3899 | 81.6932 | 3.3115 | 12.7374 | 25.7878 | 84.365 | 7.8507 | 206.3508 | 106.1361 | 225.4669 | 7.902 | 50.7671 | 13.0369 | 132 | 12.7296 | 70.2418 | 262.365 | 0.029313
2924 | 806.5853 | 2.7567 | 46.6198 | 88.6489 | 84.0544 | 5.6984 | 83.8338 | 3.5954 | 9.4002 | 26.4877 | 77.466 | 8.4366 | 169.4951 | 103.4252 | 224.7393 | 8.0333 | 50.3462 | 12.5277 | 132 | 12.7989 | 70.3889 | 268.3272 | 0.0056381
2925 | 788.0984 | 3.6008 | 49.9833 | 88.3805 | 84.0418 | 5.7104 | 84.8054 | 3.7044 | 7.022 | 27.0648 | 71.1706 | 11.7753 | 198.7663 | 104.0965 | 227.0623 | 8.1685 | 50.3491 | 12.337 | 123 | 12.7497 | 68.1847 | 272.7403 | 0
2926 | 781.3266 | 2.8843 | 64.5199 | 89.0907 | 84.0568 | 5.6961 | 86.2796 | 3.7628 | 6.74 | 28.0684 | 70.351 | 13.4241 | 266.5076 | 103.632 | 220.9787 | 8.3736 | 50.7288 | 12.0519 | 123 | 12.9125 | 65.3079 | 279.7716 | 0
2927 | 764.2649 | 2.0165 | 44.7633 | 89.156 | 84.0915 | 5.6632 | 86.1933 | 4.1836 | 6.74 | 27.4301 | 69.7689 | 10.3768 | 196.5789 | 100.3676 | 212.3222 | 8.6427 | 50.8197 | 11.6006 | 123 | 12.9508 | 63.1433 | 283.0806 | 0
2928 | 750.2272 | 1.5584 | 31.7533 | 89.1694 | 72.9237 | 6.2997 | 85.5739 | 4.5718 | 6.7024 | 26.3826 | 68.5805 | 8.4256 | 145.904 | 97.8428 | 217.5109 | 9.0872 | 51.6215 | 11.4768 | 109 | 12.9224 | 64.424 | 285.4977 | 0
2929 | 752.6685 | 1.4368 | 34.4347 | 89.9063 | 73.115 | 6.118 | 85.6225 | 4.6099 | 6.9981 | 25.8801 | 68.0333 | 8.3848 | 121.1649 | 96.6496 | 223.4928 | 9.2361 | 52.7182 | 11.5054 | 108 | 12.9594 | 64.2959 | 286.5301 | 0
2930 | 747.8873 | 1.2958 | 36.3695 | 89.5746 | 73.542 | 5.7123 | 81.4922 | 4.7166 | 7.1573 | 25.797 | 67.8595 | 8.7193 | 141.204 | 96.9539 | 221.1287 | 9.2211 | 52.9041 | 11.5217 | 122 | 12.9978 | 65.4869 | 286.1623 | 0
2931 | 741.1775 | 1.3701 | 36.6148 | 88.9664 | 73.554 | 5.7009 | 72.3605 | 4.941 | 6.8951 | 27.727 | 68.3991 | 8.9669 | 141.1497 | 98.3021 | 215.2899 | 9.2659 | 52.8485 | 11.5094 | 108 | 12.9904 | 65.03 | 291.9821 | 0
2932 | 749.5687 | 1.7542 | 37.4547 | 90.3027 | 73.5948 | 5.6622 | 76.8464 | 4.954 | 6.8991 | 34.1075 | 68.3032 | 8.6816 | 199.3305 | 95.2827 | 209.8281 | 9.1561 | 53.6957 | 11.4986 | 104 | 12.9675 | 60.697 | 313.2021 | 0
2933 | 765.6668 | 1.7619 | 37.1318 | 89.7815 | 72.8897 | 6.332 | 85.4444 | 4.4849 | 6.95 | 44.351 | 66.2748 | 7.6776 | 141.2232 | 95.5721 | 203.44 | 8.8943 | 55.2883 | 11.4357 | 108 | 12.9465 | 63.0902 | 336.8464 | 0
2934 | 802.2538 | 2.4753 | 106.4051 | 91.8925 | 70.5865 | 8.52 | 88.8303 | 4.0205 | 6.7859 | 53.9122 | 75.9144 | 13.1359 | 114.2014 | 125.5538 | 223.386 | 12.5264 | 56.0523 | 11.9764 | 156 | 12.9808 | 88.9544 | 375.8824 | 0.037294
2935 | 883.3517 | 3.5787 | 65.4386 | 99.664 | 66.9946 | 11.9323 | 107.7631 | 3.992 | 9.402 | 67.7872 | 107.6907 | 29.2283 | 160.2981 | 181.8628 | 284.6152 | 23.5567 | 58.4706 | 13.8611 | 245 | 14.3713 | 119.3987 | 442.7865 | 0.088901
2936 | 986.98 | 4.1774 | 118.1795 | 113.7814 | 64.9147 | 13.9083 | 135.2272 | 4.5974 | 15.8146 | 81.1449 | 145.0206 | 38.599 | 204.036 | 237.4967 | 380.595 | 33.1712 | 66.1521 | 15.442 | 291 | 15.1771 | 150.3189 | 505.9449 | 0.11255
2937 | 1048.9519 | 4.1054 | 91.814 | 126.679 | 66.4656 | 12.4349 | 142.7743 | 5.4563 | 21.9234 | 86.7897 | 169.4887 | 40.0431 | 286.1753 | 280.5191 | 474.8074 | 37.079 | 77.0247 | 18.344 | 317 | 15.3266 | 179.4496 | 548.9742 | 0.14585
2938 | 1091.17 | 3.7929 | 69.5122 | 134.3868 | 66.1645 | 12.7209 | 143.793 | 5.0555 | 23.422 | 90.8688 | 178.5496 | 41.0995 | 234.1884 | 307.1971 | 527.7153 | 37.8997 | 86.5615 | 18.7204 | 339 | 15.261 | 191.8484 | 569.4292 | 0.16405
2939 | 1123.8097 | 3.7995 | 96.0713 | 138.2085 | 65.4434 | 13.4059 | 168.7501 | 4.6902 | 23.3538 | 94.4628 | 183.9726 | 40.6149 | 200.4954 | 320.9091 | 548.0609 | 36.6759 | 92.289 | 17.4273 | 344 | 14.5446 | 192.3566 | 569.4832 | 0.24288
2940 | 1141.9231 | 7.0723 | 138.0704 | 142.8509 | 65.621 | 13.2372 | 195.2707 | 4.3816 | 22.201 | 93.3937 | 189.4415 | 39.2831 | 230.0707 | 324.1646 | 542.1055 | 38.5785 | 93.3265 | 17.0977 | 371 | 14.1351 | 192.3763 | 562.8485 | 0.21102
2941 | 1163.598 | 12.3025 | 79.0987 | 145.9547 | 63.9742 | 14.8017 | 202.3451 | 4.9609 | 20.8447 | 89.3003 | 191.5663 | 40.7423 | 291.6593 | 327.0063 | 547.9816 | 40.2735 | 92.2302 | 17.762 | 281 | 13.9969 | 189.3622 | 554.0701 | 0.30785
2942 | 1177.3129 | 13.7147 | 96.268 | 149.8467 | 61.9703 | 16.7054 | 198.5606 | 4.8807 | 22.8065 | 89.9446 | 191.6521 | 41.3355 | 206.9953 | 331.5646 | 568.8549 | 39.9699 | 91.5359 | 17.5403 | 269 | 13.8918 | 182.1182 | 533.38 | 0.33222
2943 | 1151.0531 | 10.6179 | 103.5469 | 143.8234 | 63.8319 | 14.9369 | 199.5691 | 3.6813 | 22.9127 | 89.7717 | 191.8954 | 36.6814 | 280.9939 | 322.5333 | 567.993 | 38.9473 | 88.755 | 17.5737 | 256 | 13.12 | 178.5822 | 512.3954 | 0.23896
2944 | 1106.9821 | 6.0311 | 103.1377 | 136.305 | 68.3349 | 10.659 | 195.1741 | 2.9326 | 17.9829 | 79.8816 | 192.9707 | 33.4916 | 254.8083 | 299.9801 | 529.3194 | 30.4746 | 83.6778 | 17.3315 | 249 | 12.2367 | 165.3701 | 481.4412 | 0.12581
2945 | 1048.5858 | 3.9727 | 136.478 | 125.659 | 71.7841 | 7.3823 | 177.6212 | 2.0165 | 16.3751 | 64.5149 | 183.6853 | 32.3216 | 227.8735 | 251.1016 | 445.3918 | 15.7688 | 78.2564 | 16.9293 | 221 | 11.4644 | 141.1294 | 420.4996 | 0.11615
2946 | 1001.5648 | 3.517 | 79.0317 | 109.0157 | 73.2793 | 5.9618 | 169.9232 | 2.4837 | 14.921 | 50.5921 | 151.2562 | 28.4273 | 266.0321 | 189.5276 | 376.3155 | 9.8786 | 73.3107 | 16.0736 | 209 | 11.1711 | 125.8686 | 360.6837 | 0.052872
2947 | 942.4528 | 2.2469 | 72.8628 | 101.6639 | 74.3226 | 4.9707 | 148.0434 | 2.9368 | 12.6903 | 35.8806 | 114.2809 | 20.7957 | 179.2714 | 157.3645 | 334.7606 | 9.2521 | 68.2321 | 15.2109 | 193 | 10.964 | 114.8071 | 321.656 | 0.021559
2948 | 896.9504 | 3.2014 | 47.9028 | 94.066 | 73.8041 | 5.4633 | 137.8321 | 2.9298 | 8.1098 | 23.9352 | 96.8008 | 9.6937 | 184.3369 | 146.2309 | 286.3599 | 8.4976 | 62.4176 | 14.2424 | 179 | 10.9472 | 107.641 | 295.1291 | 0.0013243
2949 | 862.2186 | 3.8912 | 45.9551 | 92.1737 | 73.5574 | 5.6977 | 127.2388 | 2.4279 | 5.9762 | 21.7246 | 91.8792 | 7.0648 | 176.5991 | 135.9335 | 254.0206 | 8.3007 | 58.5792 | 13.5544 | 168 | 10.9606 | 100.0043 | 286.1097 | 0
2950 | 832.2868 | 2.9762 | 49.5556 | 95.0661 | 73.5128 | 5.7401 | 98.4458 | 3.1736 | 6.4228 | 23.8237 | 85.8794 | 7.5849 | 170.6514 | 126.941 | 230.7591 | 8.4197 | 57.7112 | 13.3035 | 142 | 11.0853 | 91.6553 | 287.6506 | 0
2951 | 817.4355 | 1.8753 | 49.2843 | 95.9739 | 73.5642 | 5.6912 | 88.4767 | 3.614 | 6.4605 | 23.5613 | 77.8237 | 7.4993 | 201.6724 | 114.4615 | 214.1839 | 8.3315 | 57.5172 | 12.7678 | 122 | 11.0919 | 78.0084 | 285.7188 | 0
2952 | 815.7808 | 1.1974 | 48.6838 | 96.3248 | 68.3804 | 5.6281 | 91.8434 | 3.2726 | 6.3807 | 22.0302 | 73.6289 | 7.4101 | 107.1101 | 104.1675 | 212.672 | 8.3224 | 57.4012 | 12.4152 | 111 | 11.0874 | 70.5457 | 278.6873 | 0
2953 | 801.3419 | 1.1848 | 48.9939 | 95.3913 | 68.9731 | 5.0651 | 103.6684 | 2.5908 | 6.3232 | 21.1168 | 74.3025 | 7.4296 | 204.9058 | 99.7294 | 210.7052 | 8.3418 | 57.504 | 12.3828 | 112 | 11.1255 | 66.0541 | 272.7845 | 0
2954 | 788.553 | 1.2491 | 49.6755 | 95.238 | 67.8175 | 6.1629 | 99.6533 | 3.2495 | 6.212 | 20.7414 | 77.5407 | 7.4551 | 126.0059 | 95.7468 | 205.8496 | 8.3901 | 57.5126 | 12.1231 | 127 | 11.1283 | 60.5572 | 271.0274 | 0
2955 | 802.1331 | 1.1727 | 49.5829 | 96.7799 | 68.0268 | 5.964 | 91.5543 | 3.6467 | 6.3417 | 22.3173 | 80.1668 | 7.4565 | 217.798 | 94.5983 | 206.0127 | 8.3488 | 57.4609 | 11.731 | 107 | 11.1516 | 57.9979 | 271.7481 | 0
2956 | 814.2974 | 1.6778 | 49.3456 | 91.4818 | 68.3162 | 5.689 | 88.3973 | 3.6662 | 6.3927 | 29.1196 | 80.3357 | 7.2053 | 144.5155 | 96.0211 | 215.9179 | 8.1907 | 58.2084 | 11.6076 | 104 | 11.1189 | 56.5836 | 281.5986 | 0
2957 | 829.034 | 2.3583 | 57.148 | 87.002 | 68.2902 | 5.7138 | 85.6032 | 3.0148 | 6.4122 | 36.3385 | 78.8774 | 6.7062 | 188.3442 | 101.1597 | 217.764 | 7.9468 | 59.7036 | 11.4022 | 108 | 11.0484 | 57.672 | 300.5372 | 0
2958 | 876.2476 | 2.7065 | 60.662 | 71.8336 | 66.1702 | 7.7278 | 89.825 | 2.2659 | 6.2681 | 47.3378 | 84.7748 | 15.7182 | 273.7995 | 126.5712 | 228.2777 | 11.6701 | 59.5816 | 11.2819 | 164 | 11.067 | 83.8456 | 340.2916 | 0.060016
2959 | 950.2379 | 3.6678 | 87.8923 | 94.1005 | 62.9746 | 10.7636 | 117.2403 | 3.4417 | 7.9879 | 70.605 | 113.4176 | 29.2761 | 189.8639 | 176.5116 | 302.0513 | 26.0269 | 61.4344 | 11.9782 | 261 | 13.028 | 120.5962 | 404.3518 | 0.19026
2960 | 1031.3754 | 4.2003 | 100.9287 | 136.5742 | 58.6458 | 14.8759 | 168.3912 | 5.0559 | 14.0506 | 89.9547 | 156.7245 | 35.6744 | 244.0772 | 232.3355 | 421.1461 | 39.015 | 69.7131 | 14.4281 | 314 | 13.2343 | 151.9148 | 468.6779 | 0.2464
2961 | 1110.4528 | 3.9985 | 104.1242 | 140.7146 | 58.1063 | 15.3885 | 186.3988 | 5.0287 | 18.3915 | 94.1898 | 187.7966 | 37.9534 | 265.499 | 274.9525 | 516.4094 | 41.9373 | 78.8386 | 16.7896 | 328 | 12.1834 | 176.6091 | 515.1899 | 0.29857
2962 | 1166.0446 | 3.8464 | 109.4245 | 137.4655 | 57.5054 | 15.9593 | 184.582 | 4.7343 | 20.5013 | 94.2058 | 202.0393 | 41.9024 | 240.8734 | 301.265 | 564.6427 | 41.3782 | 85.0575 | 18.0116 | 335 | 12.283 | 188.1266 | 538.633 | 0.25841
2963 | 1188.7913 | 3.7251 | 111.2071 | 141.3643 | 58.1376 | 15.3587 | 194.4555 | 4.3536 | 23.3814 | 93.5757 | 209.8608 | 39.9746 | 291.0987 | 320.8878 | 585.0299 | 40.4964 | 88.4541 | 17.8607 | 333 | 11.2363 | 184.2248 | 554.6432 | 0.19251
2964 | 1174.8186 | 4.3196 | 111.2071 | 138.5889 | 60.0877 | 13.5061 | 202.1912 | 4.955 | 22.237 | 86.282 | 211.8119 | 37.7232 | 179.4215 | 333.8448 | 597.1832 | 41.1548 | 89.1537 | 17.741 | 357 | 8.1334 | 184.0003 | 570.0335 | 0.20101
2965 | 1177.371 | 8.4091 | 109.6248 | 142.8863 | 60.0706 | 13.5224 | 204.5015 | 5.658 | 18.1608 | 84.428 | 211.1522 | 38.7157 | 233.5673 | 342.042 | 599.9975 | 42.1727 | 90.8166 | 17.6868 | 307 | 6.2961 | 187.5413 | 573.8322 | 0.20409
2966 | 1194.2559 | 9.7596 | 110.7231 | 152.9854 | 59.4411 | 14.1204 | 201.3743 | 6.3986 | 16.8368 | 89.7577 | 213.6945 | 38.1384 | 338.6547 | 343.4892 | 604.9613 | 41.7146 | 93.1905 | 17.7069 | 268 | 5.4807 | 213.5437 | 573.8357 | 0.15324
2967 | 1176.9076 | 6.7682 | 106.9938 | 148.3323 | 61.56 | 12.1075 | 170.1503 | 6.5743 | 15.8009 | 88.6048 | 213.6381 | 34.5828 | 228.9912 | 340.1273 | 617.7554 | 39.5856 | 94.1844 | 17.5169 | 285 | 4.6844 | 217.9335 | 565.7514 | 0.13054
2968 | 1126.5624 | 4.0155 | 102.1447 | 132.6161 | 65.2299 | 8.6211 | 144.9755 | 6.6024 | 16.438 | 84.3036 | 206.5979 | 32.2823 | 261.5953 | 327.4134 | 590.2468 | 31.9875 | 91.8413 | 17.1695 | 261 | 3.6943 | 203.4177 | 527.8671 | 0.11243
2969 | 1053.2797 | 3.1166 | 97.1585 | 113.8938 | 67.8143 | 6.1659 | 134.4651 | 4.8513 | 17.9403 | 76.9381 | 191.9682 | 28.9841 | 268.9524 | 283.1422 | 508.5984 | 17.9393 | 84.5813 | 16.5695 | 214 | 3.2463 | 175.7455 | 461.6846 | 0.078465
2970 | 1005.8464 | 2.5826 | 95.4387 | 99.3013 | 68.322 | 5.6835 | 115.4511 | 3.3941 | 18.636 | 61.8679 | 159.9005 | 23.6935 | 314.9441 | 227.3064 | 420.5172 | 10.6014 | 76.3014 | 15.874 | 231 | 3.2165 | 156.4429 | 390.7587 | 0.091357
2971 | 963.5623 | 2.2788 | 82.891 | 92.9442 | 68.2963 | 5.708 | 97.3415 | 3.6352 | 18.4288 | 42.3595 | 123.0944 | 11.4659 | 188.3143 | 194.5947 | 354.5492 | 9.0625 | 69.4165 | 15.1605 | 209 | 3.0461 | 136.3106 | 336.6867 | 0.048756
2972 | 920.782 | 3.2892 | 50.5419 | 88.4062 | 68.3133 | 5.6918 | 90.8309 | 3.576 | 17.2755 | 28.2095 | 105.5171 | 6.3922 | 192.7862 | 175.9269 | 295.516 | 8.5069 | 63.0495 | 14.2352 | 180 | 2.9943 | 120.9533 | 306.4305 | 0.004324
2973 | 898.9208 | 4.193 | 38.2813 | 90.5296 | 68.271 | 5.732 | 90.9798 | 3.5811 | 15.5261 | 24.5694 | 102.1432 | 8.1878 | 182.8566 | 155.2675 | 247.1075 | 8.7961 | 58.9931 | 13.7202 | 161 | 3.0356 | 114.799 | 298.3087 | 0
2974 | 871.9332 | 3.3445 | 36.7812 | 89.9737 | 68.323 | 5.6826 | 91.6208 | 3.8403 | 15.2115 | 24.3244 | 96.1475 | 9.2124 | 172.2527 | 137.6856 | 223.4547 | 9.048 | 58.5554 | 13.6939 | 144 | 3.185 | 99.1143 | 297.7784 | 0
2975 | 849.0312 | 2.0255 | 36.1148 | 89.2356 | 68.2879 | 5.7159 | 92.1811 | 4.1624 | 14.2862 | 22.9225 | 85.6379 | 9.2817 | 129.4155 | 127.8723 | 219.9596 | 8.9882 | 58.9028 | 13.6746 | 126 | 3.1386 | 73.2477 | 295.932 | 0
2976 | 849.924 | 1.497 | 29.2614 | 88.5239 | 68.3301 | 5.6759 | 92.1754 | 4.0238 | 13.372 | 21.7005 | 80.4604 | 9.1278 | 102.8125 | 123.5656 | 226.2552 | 9.084 | 58.4951 | 13.15 | 118 | 3.0821 | 65.6278 | 293.6159 | 0
2977 | 847.3554 | 1.3816 | 26.4576 | 89.3474 | 67.491 | 6.473 | 91.7365 | 3.5794 | 13.3377 | 20.9783 | 79.8388 | 9.1365 | 106.4197 | 119.0051 | 229.8476 | 8.9222 | 58.2291 | 12.6277 | 117 | 3.1587 | 64.3916 | 292.8781 | 0
2978 | 827.8309 | 1.3836 | 26.3224 | 89.5621 | 68.0634 | 5.9293 | 91.6513 | 3.5575 | 13.0681 | 21.1002 | 80.0509 | 9.1426 | 110.9197 | 114.2868 | 230.2723 | 8.9824 | 58.318 | 12.2254 | 133 | 3.2299 | 61.9026 | 290.8369 | 0
2979 | 831.7605 | 1.2362 | 26.1945 | 90.2541 | 68.3044 | 5.7002 | 91.7239 | 3.8303 | 12.8705 | 22.8556 | 80.2839 | 9.1395 | 106.9095 | 111.6548 | 228.0571 | 8.9942 | 58.429 | 12.1153 | 114 | 3.1617 | 58.5653 | 289.1985 | 0
2980 | 842.6504 | 1.8193 | 26.1157 | 84.5337 | 68.3144 | 5.6908 | 91.1994 | 3.8174 | 12.8382 | 28.867 | 77.2402 | 8.5706 | 97.2111 | 110.9015 | 220.4201 | 8.8426 | 59.0104 | 12.0619 | 106 | 3.1211 | 54.1566 | 299.9967 | 0
2981 | 849.7548 | 2.2788 | 39.4639 | 89.5504 | 68.2988 | 5.7056 | 91.8712 | 3.5624 | 12.8573 | 35.6612 | 71.1435 | 7.8171 | 93.0536 | 110.3035 | 209.0548 | 8.5503 | 60.143 | 11.863 | 112 | 3.2748 | 58.3192 | 324.9157 | 0
2982 | 890.4891 | 2.5853 | 45.68 | 92.413 | 66.092 | 7.802 | 87.3743 | 3.4629 | 12.788 | 48.3905 | 72.6965 | 13.3545 | 103.5646 | 119.0244 | 225.8942 | 12.1635 | 59.8808 | 11.8162 | 188 | 3.2406 | 98.3514 | 360.2951 | 0.1655
2983 | 939.7308 | 3.6582 | 82.1103 | 94.3878 | 62.2609 | 11.4416 | 120.9773 | 4.063 | 14.0278 | 70.3363 | 101.0061 | 27.01 | 154.4366 | 163.1561 | 293.2458 | 24.665 | 62.0936 | 12.546 | 287 | 6.1912 | 141.9794 | 417.4093 | 0.25986
2984 | 1032.1562 | 5.0187 | 99.0764 | 108.8601 | 60.5564 | 13.0608 | 146.6393 | 5.0808 | 16.9783 | 81.9861 | 146.2805 | 33.1548 | 201.5917 | 229.9419 | 392.4494 | 36.8095 | 68.9766 | 14.3209 | 285 | 7.4646 | 176.2152 | 482.3121 | 0.30029
2985 | 1100.6447 | 10.9029 | 102.9977 | 123.3572 | 61.1839 | 12.4647 | 143.9899 | 5.2776 | 19.4328 | 76.7662 | 174.157 | 36.061 | 261.2219 | 278.3733 | 476.1572 | 41.0954 | 77.7669 | 15.8811 | 328 | 7.9076 | 213.5586 | 519.6959 | 0.33687
2986 | 1126.8123 | 12.1572 | 105.4516 | 131.7127 | 60.5737 | 13.0445 | 153.2658 | 4.5685 | 19.0075 | 69.3273 | 186.0024 | 39.1211 | 324.4449 | 301.6718 | 520.4505 | 41.8658 | 86.2508 | 18.3076 | 379 | 8.2128 | 218.6444 | 543.3632 | 0.31921
2987 | 1133.9271 | 11.2387 | 105.7788 | 133.7091 | 60.2442 | 13.3575 | 159.8161 | 4.2077 | 16.8624 | 67.1882 | 194.6146 | 40.0244 | 346.4783 | 310.6229 | 535.3958 | 41.9515 | 90.4563 | 19.2719 | 347 | 8.2822 | 216.3543 | 564.6711 | 0.30715
2988 | 1124.1521 | 8.8752 | 105.7788 | 130.5532 | 59.5949 | 13.9743 | 180.9027 | 4.2973 | 16.085 | 71.5191 | 193.661 | 36.8538 | 347.3158 | 308.0356 | 530.0503 | 42.8241 | 90.3309 | 18.9847 | 314 | 7.8906 | 208.5704 | 566.4498 | 0.31541
2989 | 1131.5933 | 7.4111 | 110.5344 | 132.2691 | 57.8745 | 15.6086 | 188.8353 | 4.9465 | 16.1288 | 80.8008 | 189.604 | 36.7755 | 344.5166 | 308.8692 | 538.2167 | 42.5199 | 89.8285 | 19.4294 | 281 | 6.997 | 221.5442 | 558.7381 | 0.289
2990 | 1153.3457 | 6.6313 | 109.0944 | 137.5362 | 59.5309 | 14.0351 | 186.1126 | 4.2068 | 17.0247 | 89.1612 | 190.8705 | 36.3879 | 347.2486 | 312.1598 | 564.661 | 39.1157 | 90.3414 | 18.7475 | 284 | 6.4645 | 221.0701 | 552.6659 | 0.3295
2991 | 1123.3054 | 5.8918 | 105.046 | 139.023 | 60.9625 | 12.6751 | 183.72 | 3.2 | 17.4764 | 92.5495 | 191.7322 | 34.5571 | 357.1563 | 307.334 | 570.5764 | 35.6191 | 89.7792 | 17.7575 | 262 | 5.9526 | 214.6626 | 540.1685 | 0.29777
2992 | 1065.417 | 4.3221 | 99.9142 | 128.0101 | 65.7695 | 8.1084 | 177.5863 | 2.2178 | 16.2011 | 86.8186 | 188.4513 | 30.9046 | 343.5159 | 294.7726 | 547.496 | 31.237 | 86.8521 | 17.1675 | 258 | 5.1219 | 195.5284 | 498.7934 | 0.28243
2993 | 1018.8625 | 3.4906 | 98.0747 | 112.7261 | 67.2831 | 6.6705 | 175.8527 | 1.6462 | 14.8471 | 73.4578 | 176.4486 | 27.7923 | 322.6045 | 253.1071 | 462.6895 | 24.1687 | 80.7119 | 16.5088 | 209 | 4.8864 | 166.0089 | 424.6206 | 0.26464
2994 | 968.8438 | 2.9778 | 94.5817 | 106.4208 | 68.0346 | 5.9566 | 140.0796 | 1.518 | 14.275 | 55.3182 | 145.4546 | 23.0775 | 276.9433 | 195.2631 | 366.9313 | 14.2021 | 73.6361 | 15.7471 | 212 | 4.8408 | 145.9434 | 355.6917 | 0.22665
2995 | 930.9201 | 1.891 | 81.2688 | 91.405 | 67.5482 | 6.4187 | 116.1162 | 2.6937 | 13.8793 | 34.8988 | 108.9172 | 10.7979 | 240.1264 | 158.1468 | 312.9888 | 8.4784 | 67.9754 | 15.3372 | 192 | 4.7779 | 128.5446 | 311.8582 | 0.12446
2996 | 906.9474 | 2.6109 | 49.4572 | 85.8966 | 68.0729 | 5.9202 | 100.4347 | 3.4615 | 13.2181 | 22.2354 | 91.0175 | 5.9487 | 229.7873 | 134.4824 | 275.736 | 7.6699 | 62.6323 | 15.2968 | 175 | 4.7712 | 119.5174 | 287.1114 | 0.015828
2997 | 878.973 | 3.5731 | 44.8081 | 88.0236 | 68.2452 | 5.7565 | 89.8628 | 3.6525 | 12.6027 | 21.2312 | 87.1251 | 7.119 | 190.8397 | 115.7604 | 266.451 | 7.8055 | 57.9462 | 14.3822 | 165 | 4.879 | 115.6761 | 280.6812 | 0
2998 | 850.1086 | 3.1897 | 42.9294 | 88.7887 | 67.5443 | 6.4223 | 88.4877 | 3.8532 | 13.9678 | 24.8744 | 81.8169 | 8.38 | 157.3221 | 107.1996 | 251.8043 | 8.1363 | 55.7008 | 13.5898 | 147 | 4.9553 | 106.1967 | 284.6851 | 0
2999 | 831.504 | 2.217 | 38.9182 | 88.8643 | 68.1118 | 5.8832 | 89.0347 | 3.8358 | 14.2164 | 25.7148 | 74.4078 | 8.7355 | 150.5089 | 105.1333 | 242.7947 | 8.2571 | 55.1596 | 12.6969 | 136 | 4.8957 | 81.7791 | 285.419 | 0
3000 | 830.9475 | 1.4987 | 30.5184 | 90.2599 | 68.3521 | 5.6549 | 89.2853 | 4.0139 | 13.384 | 24.2887 | 71.5323 | 8.7146 | 148.8674 | 101.6181 | 238.2301 | 8.8111 | 53.9209 | 12.5606 | 130 | 4.9185 | 71.8923 | 280.692 | 0
3001 | 816.8841 | 1.3441 | 26.9521 | 89.2359 | 68.246 | 5.7558 | 89.7585 | 4.1814 | 13.1036 | 25.4313 | 71.6392 | 8.7331 | 146.207 | 95.4025 | 237.1714 | 8.9985 | 52.3884 | 13.0067 | 124 | 5.0738 | 67.5154 | 277.8228 | 0
3002 | 804.8248 | 1.3976 | 24.9869 | 89.2071 | 67.6123 | 6.3578 | 89.0767 | 4.3989 | 12.939 | 27.232 | 72.0487 | 8.5055 | 136.3611 | 91.1502 | 237.6654 | 9.0727 | 51.8852 | 12.8115 | 142 | 5.002 | 58.8883 | 276.3603 | 0
3003 | 800.1461 | 1.3329 | 24.3219 | 88.6853 | 68.0427 | 5.9489 | 81.7895 | 4.6696 | 12.9203 | 26.9007 | 72.5255 | 9.8922 | 131.561 | 89.6477 | 238.4298 | 9.0541 | 51.8345 | 12.4466 | 117 | 4.9209 | 51.2016 | 275.3412 | 0
3004 | 800.4524 | 1.5712 | 24.1147 | 87.4387 | 68.3127 | 5.6924 | 75.4827 | 4.6269 | 12.6817 | 25.4558 | 71.6594 | 8.5294 | 127.5866 | 88.374 | 231.7202 | 8.9792 | 52.505 | 12.1737 | 111 | 5.0188 | 49.246 | 281.1857 | 0
3005 | 809.323 | 1.9297 | 23.9847 | 85.7238 | 68.2846 | 5.7191 | 82.6583 | 4.3169 | 12.3482 | 25.2836 | 68.8565 | 6.2218 | 121.8139 | 91.2591 | 218.0314 | 8.6681 | 54.0422 | 11.6426 | 109 | 5.0249 | 49.7164 | 294.6134 | 0
3006 | 828.9996 | 1.9345 | 23.8312 | 85.008 | 68.2582 | 5.7441 | 88.8362 | 3.7028 | 12.496 | 32.8609 | 68.7236 | 4.8192 | 110.8064 | 103.0982 | 218.1584 | 8.477 | 53.7169 | 11.3549 | 110 | 5.0033 | 52.3731 | 305.1914 | 0.16282
3007 | 844.7427 | 1.6544 | 23.8119 | 85.2611 | 64.6474 | 9.1744 | 91.4661 | 3.0298 | 12.4711 | 46.6504 | 79.6613 | 4.048 | 109.6718 | 118.4335 | 235.5275 | 8.011 | 51.8692 | 11.9176 | 121 | 5.743 | 56.3262 | 306.5016 | 0.25176
3008 | 856.8769 | 1.7536 | 23.3531 | 86.5408 | 64.057 | 9.7353 | 106.4453 | 3.2342 | 12.5353 | 52.5853 | 94.7847 | 5.4933 | 121.5685 | 137.5837 | 275.3753 | 8.1075 | 51.5176 | 13.5831 | 152 | 5.7962 | 64.0585 | 305.8955 | 0.29837
3009 | 890.8859 | 2.3875 | 23.066 | 88.3375 | 64.2762 | 9.527 | 109.9843 | 3.3367 | 13.4442 | 50.0563 | 101.2613 | 8.1604 | 149.0133 | 159.5655 | 305.3515 | 7.9742 | 52.2669 | 15.2032 | 174 | 5.632 | 73.2719 | 305.7056 | 0.32502
3010 | 915.3549 | 2.5062 | 22.9671 | 89.5588 | 64.2988 | 9.5056 | 115.585 | 2.3471 | 15.1498 | 45.2242 | 104.3093 | 7.8403 | 185.7495 | 177.4211 | 322.6354 | 7.6842 | 53.3715 | 16.1068 | 173 | 5.9373 | 77.6628 | 300.0606 | 0.31031
3011 | 918.7191 | 2.7228 | 23.0274 | 93.6273 | 64.3013 | 9.5032 | 141.4389 | 2.5982 | 16.1247 | 41.6814 | 111.5445 | 5.3703 | 200.479 | 188.9246 | 330.7418 | 7.6259 | 54.8377 | 16.4609 | 198 | 5.8979 | 82.7032 | 302.101 | 0.29026
3012 | 931.6252 | 2.9297 | 22.8798 | 94.6803 | 64.334 | 9.4721 | 139.8277 | 2.5216 | 15.9137 | 42.8556 | 121.5536 | 5.3445 | 206.77 | 190.2667 | 331.4924 | 7.508 | 56.4122 | 17.0727 | 185 | 5.7935 | 82.8995 | 311.9383 | 0.25147
3013 | 942.3321 | 2.9801 | 22.6369 | 93.974 | 64.9481 | 8.8887 | 136.9357 | 2.6999 | 15.6238 | 47.1088 | 128.4322 | 11.1962 | 206.3505 | 187.7616 | 338.6043 | 7.6169 | 58.8262 | 17.8774 | 192 | 5.8039 | 81.2714 | 313.7913 | 0.28085
3014 | 951.9428 | 2.5026 | 22.6883 | 95.5296 | 63.832 | 9.949 | 141.655 | 2.482 | 15.931 | 49.775 | 130.8575 | 14.8347 | 201.9754 | 191.2171 | 353.1614 | 7.6463 | 61.0569 | 17.6471 | 182 | 5.1992 | 81.9223 | 312.5877 | 0.32259
3015 | 942.3429 | 2.0072 | 22.3777 | 96.2781 | 66.3382 | 7.5682 | 145.3321 | 2.2503 | 16.6385 | 46.6598 | 133.4223 | 12.7125 | 200.6143 | 193.3242 | 365.5458 | 7.7172 | 60.1447 | 17.1806 | 180 | 4.7227 | 82.827 | 306.9319 | 0.29277
3016 | 929.3368 | 1.8637 | 23.2292 | 95.1346 | 68.0083 | 5.9815 | 144.5934 | 2.3436 | 16.6489 | 42.9601 | 134.0079 | 13.2313 | 196.5929 | 189.7011 | 366.4841 | 7.6391 | 57.6992 | 16.4127 | 171 | 4.7627 | 77.8135 | 296.7083 | 0.2448
3017 | 915.7612 | 1.6791 | 24.0194 | 95.998 | 69.0575 | 4.9848 | 119.0027 | 2.2503 | 15.8396 | 39.1255 | 125.9043 | 11.9608 | 187.2688 | 175.1494 | 346.2345 | 7.6236 | 56.9522 | 15.4753 | 165 | 4.7017 | 72.0669 | 289.5374 | 0.22955
3018 | 891.3979 | 1.5373 | 23.9655 | 94.1921 | 68.558 | 5.4594 | 110.8737 | 2.1537 | 15.2076 | 32.4537 | 110.3671 | 7.7959 | 178.6663 | 151.8279 | 316.8059 | 7.6347 | 57.7788 | 14.7687 | 155 | 4.6204 | 67.6327 | 285.0439 | 0.21876
3019 | 871.1338 | 1.2768 | 25.3069 | 92.7703 | 69.0677 | 4.9752 | 106.1922 | 3.0529 | 14.7106 | 30.8898 | 96.511 | 5.698 | 169.5682 | 135.6398 | 301.6551 | 7.757 | 60.4592 | 15.1207 | 133 | 4.6639 | 68.163 | 276.5079 | 0.12048
3020 | 866.4498 | 2.4717 | 28.897 | 89.248 | 68.5901 | 5.4289 | 95.187 | 3.2453 | 13.7703 | 30.6151 | 84.0057 | 4.6055 | 159.7302 | 123.8876 | 287.5212 | 7.6638 | 61.9094 | 15.0731 | 129 | 4.8033 | 67.028 | 265.6127 | 0.0070844
3021 | 862.385 | 3.7157 | 41.0867 | 88.1522 | 68.3332 | 5.6729 | 93.5932 | 3.351 | 13.2503 | 26.5861 | 74.4129 | 5.615 | 134.1643 | 113.0688 | 267.4351 | 7.8912 | 58.8307 | 14.8448 | 128 | 4.6937 | 64.865 | 261.1575 | 0
3022 | 849.224 | 3.086 | 48.0833 | 93.1113 | 66.7849 | 7.1438 | 88.8171 | 3.234 | 13.1596 | 24.7396 | 73.7596 | 6.6497 | 110.5751 | 108.6254 | 252.2071 | 8.0998 | 55.3673 | 14.3789 | 129 | 4.7182 | 63.069 | 262.2685 | 0
3023 | 834.9313 | 1.7961 | 41.8069 | 89.0105 | 67.7695 | 6.2084 | 86.6699 | 3.3696 | 13.2328 | 24.3775 | 76.3984 | 6.6674 | 109.0427 | 106.3565 | 253.7139 | 8.2717 | 54.0319 | 13.5534 | 123 | 4.8828 | 62.0903 | 262.7044 | 0
3024 | 834.0989 | 1.3496 | 38.6095 | 88.7975 | 68.333 | 5.6731 | 86.4923 | 3.871 | 13.2984 | 23.8049 | 78.0176 | 6.6003 | 98.9803 | 105.3598 | 251.3294 | 8.7088 | 53.7952 | 12.3869 | 124 | 4.8577 | 65.9653 | 261.2049 | 0
3025 | 824.0564 | 1.3431 | 38.6095 | 92.2034 | 68.3253 | 5.6804 | 86.048 | 3.9838 | 12.8887 | 23.5831 | 78.4055 | 6.8133 | 88.6466 | 101.2299 | 242.4886 | 8.9792 | 53.6818 | 11.8724 | 123 | 4.8107 | 66.549 | 260.3389 | 0
3026 | 810.4071 | 1.5163 | 30.8471 | 86.6293 | 67.5944 | 6.3747 | 86.342 | 4.097 | 12.6821 | 23.4654 | 78.4447 | 6.6657 | 85.567 | 92.9537 | 235.2365 | 8.9371 | 53.1293 | 11.8817 | 128 | 4.8412 | 63.7782 | 260.4707 | 0
3027 | 811.1383 | 1.8398 | 25.0936 | 86.8222 | 68.0223 | 5.9683 | 82.4636 | 4.4307 | 12.5538 | 25.1317 | 79.0436 | 6.5309 | 84.6388 | 87.9949 | 233.5995 | 8.9676 | 52.885 | 11.7334 | 109 | 4.8639 | 60.0492 | 262.7585 | 0
3028 | 816.8665 | 2.0529 | 24.117 | 87.6203 | 68.2486 | 5.7533 | 71.9082 | 4.7694 | 12.4932 | 31.5628 | 77.2249 | 5.8676 | 81.6725 | 86.0376 | 225.5889 | 8.8026 | 53.6296 | 11.6501 | 104 | 4.8134 | 57.3955 | 275.6085 | 0
3029 | 818.5531 | 2.0961 | 23.8012 | 87.8377 | 68.3256 | 5.6801 | 78.3638 | 4.5547 | 12.7736 | 38.3307 | 71.6962 | 5.4184 | 78.9597 | 89.8837 | 211.7268 | 8.6129 | 55.058 | 11.4558 | 106 | 4.8616 | 62.4492 | 295.6766 | 0
3030 | 848.6625 | 1.8895 | 24.1956 | 86.4356 | 66.8303 | 7.1007 | 90.6205 | 4.2425 | 12.2853 | 46.0164 | 72.1225 | 10.208 | 85.3082 | 101.5216 | 208.4035 | 8.5788 | 55.0014 | 11.3225 | 138 | 4.89 | 91.6362 | 320.3254 | 0.17162
3031 | 871.371 | 1.9438 | 29.975 | 87.5662 | 64.1102 | 9.6847 | 101.5213 | 3.2372 | 12.1452 | 57.7636 | 95.5026 | 19.0779 | 112.2953 | 121.6212 | 217.1799 | 8.8827 | 56.0095 | 11.9472 | 186 | 4.883 | 124.5739 | 357.5855 | 0.26161
3032 | 881.2791 | 2.4928 | 32.2 | 88.8181 | 62.6133 | 11.1068 | 110.2145 | 3.4126 | 12.4259 | 60.5588 | 133.9305 | 21.9641 | 144.311 | 148.1526 | 242.1483 | 9.6718 | 60.3257 | 13.4238 | 223 | 5.0281 | 138.0611 | 391.2395 | 0.3034
3033 | 907.3303 | 2.5631 | 32.5258 | 94.242 | 62.2731 | 11.43 | 124.2082 | 2.7141 | 12.9441 | 53.5523 | 160.4411 | 21.9738 | 189.9814 | 170.1151 | 285.494 | 10.2976 | 64.2608 | 14.7153 | 251 | 4.9653 | 143.2819 | 404.4328 | 0.33433
3034 | 942.1453 | 2.4174 | 35.0197 | 99.0459 | 63.0898 | 10.6541 | 144.5546 | 2.2395 | 13.4798 | 48.7399 | 167.4998 | 23.6691 | 210.3641 | 185.6605 | 328.3443 | 10.6482 | 66.962 | 15.6502 | 233 | 4.9047 | 144.8453 | 406.9326 | 0.31827
3035 | 953.2288 | 3.654 | 36.7113 | 104.2861 | 63.1928 | 10.5563 | 164.4505 | 2.1779 | 13.7582 | 47.8722 | 166.1905 | 25.9726 | 211.7088 | 199.5992 | 351.0883 | 10.4785 | 68.8308 | 15.8843 | 221 | 5.0699 | 149.6348 | 409.2438 | 0.29121
3036 | 988.8834 | 5.2826 | 35.3251 | 103.5149 | 63.2798 | 10.4736 | 182.7047 | 2.066 | 13.908 | 48.6004 | 165.6163 | 23.644 | 225.9072 | 205.8732 | 338.2033 | 10.4472 | 68.8737 | 16.2142 | 224 | 5.0433 | 151.1339 | 407.8628 | 0.26963
3037 | 1000.8671 | 5.5864 | 35.7032 | 100.8932 | 63.2578 | 10.4946 | 189.3786 | 1.9975 | 13.9276 | 56.7839 | 165.4114 | 26.63 | 236.773 | 210.6736 | 324.9485 | 10.8398 | 69.5295 | 16.648 | 211 | 4.9737 | 154.2472 | 403.2372 | 0.28094
3038 | 997.472 | 4.8519 | 36.2303 | 99.2879 | 63.3226 | 10.433 | 191.0169 | 1.929 | 14.3655 | 69.1346 | 165.0475 | 28.0724 | 234.8983 | 220.1967 | 327.4224 | 11.0867 | 72.2733 | 16.1817 | 230 | 5.0673 | 154.4425 | 395.5223 | 0.32369
3039 | 995.3433 | 3.0296 | 35.5814 | 97.846 | 65.5203 | 8.3451 | 189.7726 | 2.1791 | 13.7771 | 73.6123 | 165.3818 | 28.4437 | 241.9118 | 223.704 | 327.1472 | 11.2303 | 73.4453 | 15.8634 | 218 | 4.8339 | 153.7737 | 394.1999 | 0.29617
3040 | 984.6996 | 2.0668 | 33.8432 | 98.7317 | 67.8219 | 6.1586 | 167.1591 | 1.961 | 13.5249 | 66.7688 | 167.2763 | 29.4271 | 236.6298 | 217.3215 | 324.7274 | 10.1718 | 71.9617 | 15.7033 | 203 | 4.3247 | 150.0456 | 379.8572 | 0.276
3041 | 959.2922 | 2.0387 | 26.4283 | 98.9259 | 68.3513 | 5.6557 | 157.0951 | 1.3872 | 14.1848 | 51.9317 | 162.1835 | 26.0087 | 225.1927 | 194.618 | 308.3053 | 9.2795 | 69.8583 | 15.055 | 183 | 4.0909 | 138.3677 | 340.2538 | 0.25487
3042 | 945.2102 | 1.7657 | 25.5348 | 94.6119 | 69.0164 | 5.0238 | 149.3128 | 1.1722 | 13.6989 | 38.959 | 137.9897 | 19.9695 | 206.439 | 160.8797 | 288.4252 | 9.0182 | 68.0217 | 14.6055 | 183 | 4.2331 | 130.5373 | 311.8493 | 0.23022
3043 | 910.0947 | 1.2015 | 26.54 | 92.6481 | 69.3219 | 4.7337 | 116.8106 | 1.8776 | 13.131 | 32.9234 | 109.6237 | 11.2694 | 185.513 | 134.3437 | 271.7694 | 8.9359 | 64.8294 | 14.1712 | 167 | 4.2009 | 116.3721 | 296.3513 | 0.11695
3044 | 886.1699 | 2.369 | 26.54 | 91.727 | 69.2926 | 4.7615 | 100.6484 | 1.8474 | 12.6831 | 31.8413 | 93.0191 | 8.2503 | 162.891 | 118.6144 | 263.8327 | 8.8941 | 61.2847 | 13.2909 | 168 | 4.1071 | 108.9898 | 282.9585 | 0.017395
3045 | 874.0823 | 3.5282 | 40.8216 | 92.5835 | 68.6488 | 5.3731 | 91.9655 | 2.6092 | 12.3272 | 34.052 | 84.2587 | 8.3376 | 139.0202 | 113.4338 | 259.6139 | 8.7718 | 58.2817 | 12.2628 | 166 | 4.1891 | 110.2387 | 276.6407 | 0
3046 | 863.3078 | 2.9639 | 46.9404 | 97.0108 | 69.004 | 5.0356 | 105.1014 | 3.2685 | 12.9216 | 36.2586 | 81.1237 | 7.5163 | 136.9767 | 111.6451 | 267.778 | 9.1371 | 55.3126 | 12.03 | 133 | 4.219 | 102.5354 | 280.5973 | 0
3047 | 842.4216 | 1.7721 | 47.2434 | 98.9322 | 68.5475 | 5.4693 | 94.0376 | 2.9571 | 13.1792 | 37.2764 | 80.2688 | 7.0747 | 136.5415 | 104.2107 | 279.5154 | 9.258 | 54.8801 | 11.9532 | 119 | 4.2021 | 75.831 | 284.0407 | 0
3048 | 830.8962 | 1.5399 | 46.2915 | 96.1556 | 68.2936 | 5.7105 | 91.0088 | 2.5007 | 13.1019 | 39.2173 | 79.5048 | 7.1335 | 120.1521 | 99.3419 | 279.1233 | 8.8256 | 56.3639 | 11.7484 | 132 | 4.222 | 66.5638 | 277.3775 | 0
3049 | 826.3599 | 1.6735 | 45.5504 | 94.5138 | 68.2971 | 5.7072 | 104.3135 | 3.0273 | 13.2918 | 38.6371 | 79.2572 | 6.7439 | 108.0702 | 97.6601 | 281.7325 | 8.8874 | 57.2417 | 11.8745 | 133 | 4.3939 | 65.1096 | 273.4385 | 0
3050 | 814.0223 | 1.3963 | 45.4742 | 91.9582 | 69.0441 | 4.9976 | 91.8709 | 3.5245 | 13.0893 | 35.9111 | 79.4593 | 6.5043 | 108.2228 | 94.0503 | 283.6464 | 9.0473 | 57.4066 | 12.4086 | 149 | 4.3399 | 62.8251 | 274.2357 | 0
3051 | 817.0455 | 1.2385 | 45.6919 | 90.0306 | 67.862 | 6.1206 | 84.3313 | 3.8074 | 12.704 | 35.3277 | 80.2577 | 6.5312 | 104.5462 | 90.505 | 274.6577 | 9.2665 | 56.6741 | 12.5994 | 128 | 4.3163 | 61.4616 | 272.4632 | 0
3052 | 811.9377 | 1.8463 | 44.7642 | 87.4921 | 68.7424 | 5.2842 | 85.1691 | 3.6519 | 12.7813 | 37.6913 | 79.6172 | 5.8061 | 93.9035 | 87.3231 | 256.0723 | 8.7959 | 55.9501 | 11.9417 | 127 | 4.4585 | 59.042 | 267.6108 | 0
3053 | 803.8797 | 1.7227 | 44.2836 | 86.4962 | 68.5461 | 5.4706 | 83.0345 | 2.6327 | 12.4805 | 40.9844 | 76.1556 | 4.333 | 81.5239 | 84.0716 | 233.66 | 7.9351 | 55.8685 | 11.3897 | 126 | 4.358 | 54.9559 | 257.9683 | 0.079289
3054 | 817.7629 | 1.1376 | 56.0079 | 85.3821 | 68.3533 | 5.6538 | 77.035 | 2.3661 | 11.9977 | 44.0929 | 73.5843 | 3.8635 | 79.2753 | 82.1929 | 221.7273 | 7.708 | 54.9296 | 11.2976 | 130 | 4.3496 | 55.2256 | 250.0672 | 0.16112
3055 | 824.8935 | 1.1827 | 61.2863 | 85.6083 | 69.0042 | 5.0354 | 78.4846 | 2.6999 | 11.5786 | 44.611 | 76.9486 | 6.0181 | 77.8562 | 84.4602 | 230.4514 | 7.6296 | 53.7149 | 11.5213 | 129 | 4.4087 | 56.8573 | 250.247 | 0.267
3056 | 844.3635 | 1.5193 | 61.2863 | 89.8852 | 68.5436 | 5.473 | 85.0472 | 2.0198 | 11.4802 | 41.3988 | 98.7012 | 11.6139 | 91.242 | 89.0067 | 241.0245 | 7.6581 | 53.3354 | 12.0872 | 132 | 4.2535 | 63.7988 | 257.2428 | 0.31047
3057 | 869.4499 | 1.8423 | 79.885 | 90.5595 | 68.3339 | 5.6722 | 115.2225 | 1.4835 | 11.9683 | 40.4598 | 130.6786 | 13.4952 | 110.8805 | 93.6483 | 245.7237 | 7.5876 | 53.3043 | 12.3205 | 168 | 4.2209 | 91.4136 | 263.5105 | 0.34447
3058 | 882.9028 | 2.3016 | 93.901 | 90.152 | 69.0629 | 4.9797 | 126.2546 | 1.6204 | 12.067 | 42.1397 | 144.2323 | 13.3898 | 126.4146 | 100.3243 | 244.5204 | 7.7577 | 53.3289 | 12.4226 | 183 | 4.2703 | 109.5463 | 262.7778 | 0.32257
3059 | 897.8419 | 1.6632 | 92.5194 | 91.2893 | 69.2895 | 4.7645 | 121.6836 | 1.5031 | 12.1283 | 44.5507 | 130.5111 | 13.1469 | 146.714 | 112.2364 | 240.6557 | 7.7618 | 52.6364 | 12.5444 | 207 | 4.1895 | 116.5431 | 266.0883 | 0.30491
3060 | 921.2434 | 1.516 | 88.7724 | 91.2779 | 69.3013 | 4.7532 | 115.8136 | 1.3553 | 11.7609 | 44.8578 | 109.4097 | 15.746 | 161.1181 | 122.7048 | 245.062 | 8.8937 | 54.7375 | 12.5836 | 185 | 4.1444 | 118.3207 | 271.534 | 0.26691
3061 | 910.2978 | 1.7632 | 75.8245 | 94.3895 | 67.8685 | 6.1144 | 125.2687 | 1.3228 | 11.531 | 39.5418 | 101.5583 | 18.4957 | 160.2395 | 130.8405 | 257.8712 | 8.7259 | 59.2318 | 12.8653 | 192 | 4.2448 | 117.5301 | 267.4062 | 0.26942
3062 | 900.2078 | 1.869 | 46.3694 | 95.9873 | 68.7272 | 5.2987 | 161.5329 | 1.2835 | 11.6533 | 33.9168 | 103.2604 | 16.2969 | 161.8186 | 133.3977 | 254.2371 | 8.1508 | 59.7976 | 13.2082 | 186 | 4.2143 | 113.6994 | 257.3332 | 0.30968
3063 | 906.2317 | 2.4003 | 34.5987 | 93.7756 | 69.2806 | 4.7729 | 153.5152 | 1.2818 | 11.7115 | 27.4668 | 105.2209 | 13.9782 | 156.308 | 129.3274 | 256.6235 | 8.0982 | 57.5205 | 13.6267 | 182 | 4.1497 | 104.3961 | 250.4366 | 0.2392
3064 | 901.0988 | 2.4961 | 34.0214 | 92.4252 | 68.5855 | 5.4333 | 115.3086 | 1.2272 | 12.2362 | 20.6611 | 104.8598 | 6.5174 | 153.9868 | 127.1324 | 269.6105 | 8.3482 | 55.7177 | 13.4801 | 188 | 4.1961 | 79.7653 | 246.7899 | 0.24787
3065 | 893.5058 | 1.7585 | 33.9202 | 92.362 | 69.0849 | 4.9588 | 107.2988 | 1.358 | 12.767 | 18.4022 | 103.5523 | 3.4841 | 152.2823 | 129.8165 | 288.8388 | 8.2107 | 55.235 | 13.3188 | 176 | 4.2774 | 70.7528 | 243.3995 | 0.23194
3066 | 885.2253 | 1.319 | 34.6239 | 90.8452 | 69.3013 | 4.7533 | 113.8707 | 1.1856 | 12.9478 | 18.4488 | 97.2349 | 3.6497 | 155.1022 | 131.7369 | 296.3718 | 8.2968 | 55.8143 | 13.2603 | 164 | 4.1594 | 66.9981 | 241.6498 | 0.18274
3067 | 878.9136 | 1.1086 | 34.938 | 88.5728 | 69.2679 | 4.785 | 113.3888 | 1.0552 | 12.2662 | 18.4088 | 88.3471 | 3.8852 | 148.3832 | 132.0339 | 280.9865 | 8.2701 | 56.185 | 13.2084 | 165 | 4.0737 | 65.0033 | 241.0189 | 0.09212
3068 | 873.7237 | 1.8834 | 35.4978 | 88.1965 | 69.3174 | 4.7379 | 105.0326 | 1.2286 | 11.8003 | 17.759 | 85.0376 | 3.7827 | 141.3504 | 131.5733 | 266.2973 | 8.1626 | 55.3986 | 12.9139 | 161 | 4.0739 | 63.9723 | 241.2828 | 0.01818
3069 | 857.5689 | 2.9443 | 35.0348 | 90.6215 | 69.3273 | 4.7285 | 111.4458 | 2.0952 | 11.4181 | 17.1831 | 86.0894 | 4.7879 | 130.8182 | 128.6697 | 263.7366 | 8.5448 | 54.4414 | 12.6537 | 184 | 4.1746 | 60.5782 | 243.3666 | 0
3070 | 855.7211 | 2.8212 | 34.7197 | 91.7219 | 68.5575 | 5.4599 | 97.13 | 2.0543 | 11.8615 | 18.5954 | 87.5364 | 6.2664 | 130.6164 | 128.0711 | 273.7687 | 8.9271 | 54.4722 | 12.9593 | 166 | 4.2151 | 57.422 | 246.9367 | 0
3071 | 846.7736 | 1.7033 | 34.1191 | 92.6235 | 69.0543 | 4.9879 | 100.924 | 2.5092 | 12.6698 | 20.6396 | 86.9138 | 6.8962 | 131.7338 | 123.9893 | 285.6956 | 9.2057 | 54.781 | 12.2104 | 155 | 4.1813 | 54.5389 | 246.5072 | 0
3072 | 851.4532 | 1.3187 | 33.3607 | 94.5952 | 68.583 | 5.4356 | 109.0317 | 2.4712 | 13.1045 | 21.265 | 84.7662 | 6.4415 | 129.994 | 112.8012 | 284.3399 | 9.2901 | 54.7735 | 11.8597 | 155 | 4.1721 | 52.0879 | 244.4358 | 0
3073 | 840.3126 | 1.307 | 32.9634 | 94.9021 | 66.7859 | 7.1429 | 105.8131 | 2.6974 | 12.534 | 21.5513 | 83.1518 | 6.2919 | 121.0257 | 105.2486 | 281.5595 | 9.3717 | 54.8255 | 12.2011 | 146 | 4.2849 | 50.8597 | 246.5001 | 0
3074 | 822.9694 | 1.3557 | 32.8907 | 93.1773 | 64.8162 | 9.0141 | 99.8208 | 3.1138 | 12.3598 | 21.4728 | 82.1843 | 6.2572 | 111.2534 | 104.4353 | 274.1068 | 9.1932 | 55.0401 | 11.9454 | 164 | 4.3779 | 49.1669 | 249.1093 | 0
3075 | 823.6862 | 1.4976 | 32.8385 | 91.7907 | 64.3207 | 9.4848 | 102.0802 | 2.3305 | 12.7207 | 21.0597 | 82.5063 | 6.1883 | 101.4254 | 104.4568 | 271.0113 | 9.1141 | 55.3706 | 11.7682 | 156 | 4.2644 | 48.1802 | 248.7115 | 0
3076 | 805.0974 | 1.5973 | 32.7416 | 88.6295 | 65.8051 | 8.0746 | 106.867 | 2.5897 | 12.7101 | 20.0351 | 81.881 | 5.2763 | 94.9409 | 101.3958 | 258.8279 | 8.65 | 55.0748 | 11.7865 | 156 | 4.2243 | 47.1134 | 244.3284 | 0
3077 | 794.346 | 1.2419 | 32.6102 | 86.1591 | 67.764 | 6.2136 | 90.3748 | 2.9149 | 12.6879 | 18.3959 | 78.4257 | 3.7765 | 93.0288 | 93.3614 | 242.9051 | 7.9185 | 54.8572 | 11.4309 | 150 | 4.4307 | 47.1178 | 237.7454 | 0.093657
3078 | 797.7369 | 1.0108 | 32.5846 | 85.9249 | 69.0323 | 5.0087 | 91.5891 | 1.934 | 12.3146 | 18.7971 | 76.3152 | 3.259 | 83.6667 | 84.7384 | 234.8703 | 7.6886 | 55.2561 | 11.1847 | 138 | 4.3291 | 48.1352 | 232.502 | 0.18423
3079 | 813.0184 | 0.97172 | 32.3395 | 89.2141 | 68.5589 | 5.4585 | 103.2158 | 1.5214 | 11.6747 | 19.293 | 77.0399 | 3.2102 | 80.7104 | 83.024 | 229.4459 | 7.7608 | 55.1847 | 11.1441 | 138 | 4.225 | 48.9071 | 230.2125 | 0.27872
3080 | 810.648 | 1.2018 | 32.2874 | 89.614 | 69.0766 | 4.9666 | 122.8735 | 1.573 | 11.6125 | 19.5889 | 76.9428 | 3.099 | 85.7878 | 87.1147 | 240.6356 | 7.6669 | 54.6629 | 11.2568 | 151 | 4.2319 | 51.3789 | 230.5153 | 0.32003
3081 | 825.7738 | 1.4024 | 32.3246 | 89.4049 | 69.3051 | 4.7496 | 142.0984 | 2.104 | 12.0057 | 22.2231 | 75.8201 | 3.0096 | 94.0059 | 95.7506 | 255.0887 | 7.4444 | 54.1815 | 11.2686 | 197 | 4.2095 | 53.7603 | 235.9356 | 0.3559
3082 | 852.8946 | 1.465 | 32.3874 | 89.8806 | 68.5513 | 5.4657 | 128.6896 | 1.9918 | 11.9169 | 26.6748 | 78.0709 | 3.5175 | 116.3652 | 108.4975 | 273.7684 | 7.9448 | 53.8834 | 11.5923 | 171 | 4.1164 | 57.2471 | 241.3911 | 0.32099
3083 | 861.2669 | 1.7736 | 32.6321 | 92.9522 | 69.7534 | 4.3238 | 146.7501 | 1.6973 | 11.6619 | 32.2456 | 86.379 | 4.4462 | 141.5357 | 119.0924 | 291.6996 | 8.6005 | 54.2011 | 12.1995 | 202 | 4.0954 | 63.2236 | 242.5916 | 0.30128
3084 | 859.7836 | 2.2386 | 32.4004 | 93.6536 | 69.5657 | 4.502 | 193.6319 | 1.6517 | 11.332 | 33.3324 | 97.0893 | 8.803 | 156.2025 | 124.9667 | 296.577 | 8.4715 | 55.443 | 12.3934 | 204 | 4.1631 | 63.4147 | 239.936 | 0.25428
3085 | 862.838 | 2.2771 | 33.4558 | 93.2732 | 68.5895 | 5.4294 | 165.1963 | 1.5037 | 11.8349 | 30.139 | 103.7458 | 9.2331 | 159.1965 | 128.9851 | 293.7815 | 8.3026 | 56.0957 | 12.703 | 223 | 4.172 | 64.9567 | 240.7877 | 0.27896
3086 | 867.6642 | 2.2812 | 34.0269 | 93.6282 | 68.3001 | 5.7043 | 126.6232 | 1.3891 | 12.7076 | 28.4585 | 107.2832 | 6.4577 | 159.1248 | 133.6514 | 295.1464 | 8.2687 | 57.4873 | 12.6726 | 207 | 4.1619 | 65.091 | 244.3112 | 0.31243
3087 | 867.6543 | 2.3434 | 34.0269 | 92.652 | 68.3029 | 5.7018 | 125.9936 | 1.6199 | 13.2428 | 27.8507 | 110.3776 | 7.91 | 161.3071 | 133.7048 | 299.8037 | 8.3502 | 59.8437 | 12.252 | 193 | 4.0796 | 65.1629 | 241.9139 | 0.28132
3088 | 872.0156 | 2.2967 | 34.0466 | 93.4993 | 69.0355 | 5.0057 | 129.8432 | 1.4478 | 13.7788 | 28.9464 | 110.3675 | 9.7237 | 152.7463 | 130.8061 | 293.3391 | 8.2787 | 59.1665 | 12.0663 | 174 | 4.0475 | 62.715 | 238.0205 | 0.26903
3089 | 860.5471 | 2.1182 | 34.4 | 95.6341 | 68.5552 | 5.4621 | 115.375 | 1.2505 | 13.7142 | 31.0227 | 107.6701 | 9.9348 | 147.6577 | 130.516 | 287.0665 | 8.2979 | 56.6512 | 12.5976 | 165 | 4.0613 | 61.286 | 235.2118 | 0.2553
3090 | 862.4224 | 1.7904 | 34.0444 | 94.5351 | 69.1279 | 4.918 | 113.496 | 1.2925 | 13.5464 | 32.1472 | 107.5498 | 6.155 | 149.0474 | 128.2393 | 291.4722 | 8.2036 | 55.382 | 12.6279 | 148 | 4.0158 | 60.4796 | 233.4337 | 0.22574
3091 | 853.2974 | 1.3667 | 35.26 | 92.2921 | 69.2435 | 4.8081 | 117.9535 | 1.2989 | 12.9182 | 32.9418 | 106.2126 | 6.2157 | 143.6103 | 122.1922 | 306.6391 | 8.1328 | 54.6577 | 12.6092 | 138 | 3.9971 | 59.6454 | 230.709 | 0.13648
3092 | 825.7958 | 1.6401 | 34.4593 | 90.2604 | 69.3383 | 4.718 | 116.9641 | 1.8241 | 11.786 | 31.7678 | 97.5401 | 8.8365 | 131.3931 | 116.1246 | 299.0284 | 8.3255 | 53.8054 | 12.7584 | 135 | 4.0289 | 60.4296 | 228.901 | 0.024185
3093 | 826.7899 | 1.6673 | 34.0653 | 90.7753 | 69.2811 | 4.7724 | 100.3113 | 1.9825 | 11.4965 | 28.633 | 90.3181 | 8.6457 | 122.0818 | 111.8536 | 267.2902 | 8.5812 | 53.6787 | 12.9104 | 132 | 4.1532 | 59.9154 | 230.1667 | 0
3094 | 819.1033 | 1.6371 | 34.216 | 97.9042 | 68.5861 | 5.4327 | 105.5091 | 2.0884 | 11.7308 | 26.8091 | 89.119 | 7.4151 | 109.866 | 111.1346 | 244.9325 | 8.7957 | 54.6749 | 13.0968 | 124 | 4.1421 | 56.7631 | 236.092 | 0
3095 | 814.2335 | 1.5211 | 33.738 | 100.2936 | 68.2971 | 5.7072 | 111.5594 | 2.6069 | 12.1312 | 26.1519 | 87.2008 | 6.5693 | 102.3199 | 111.4742 | 236.8213 | 9.6984 | 55.4535 | 12.7316 | 122 | 4.1582 | 54.9813 | 240.6593 | 0
3096 | 822.3809 | 1.2844 | 33.5191 | 98.9847 | 69.034 | 5.0071 | 108.2782 | 2.5968 | 12.157 | 25.2624 | 83.8677 | 6.2093 | 98.9797 | 107.9012 | 249.8442 | 11.7204 | 55.2386 | 12.2674 | 118 | 4.1183 | 58.7219 | 239.1077 | 0
3097 | 806.4604 | 1.3655 | 33.3722 | 98.5603 | 69.2909 | 4.7631 | 105.4932 | 2.131 | 12.2503 | 24.9544 | 81.6367 | 6.1979 | 98.1023 | 102.9912 | 252.2629 | 12.6342 | 54.5677 | 12.0356 | 112 | 4.2395 | 92.9142 | 239.3684 | 0
3098 | 790.5062 | 1.615 | 33.3653 | 98.5412 | 67.0736 | 6.8696 | 105.1114 | 2.7155 | 12.3542 | 24.6999 | 80.7131 | 8.2282 | 101.2124 | 101.4603 | 238.0648 | 12.9496 | 54.0706 | 11.8511 | 134 | 4.2242 | 106.5921 | 241.8219 | 0
3099 | 801.4028 | 1.5728 | 36.1036 | 97.4819 | 67.7753 | 6.2029 | 105.3652 | 2.4535 | 12.5203 | 25.6396 | 80.9129 | 14.0163 | 102.5183 | 100.955 | 228.5396 | 13.0267 | 54.0533 | 11.7668 | 120 | 4.1608 | 107.465 | 243.4307 | 0
3100 | 806.0926 | 1.2661 | 37.3635 | 97.4527 | 69.0223 | 5.0183 | 105.1471 | 2.7055 | 12.5482 | 31.4119 | 79.2928 | 13.341 | 106.6115 | 98.2439 | 226.6651 | 11.9909 | 54.0632 | 11.6957 | 114 | 4.1718 | 101.8683 | 249.0087 | 0
3101 | 812.105 | 1.2493 | 37.3635 | 96.5729 | 67.8565 | 6.1258 | 104.8607 | 2.1252 | 12.3756 | 37.5498 | 76.2829 | 7.9007 | 103.6838 | 102.9697 | 227.9568 | 9.2543 | 54.3422 | 11.6832 | 134 | 4.2763 | 101.6642 | 257.1719 | 0.069826
3102 | 842.7854 | 2.0137 | 50.0143 | 94.1014 | 66.6098 | 7.3102 | 117.3473 | 2.6637 | 12.4097 | 43.7836 | 87.4809 | 14.4598 | 128.9076 | 133.83 | 252.0701 | 11.2218 | 55.527 | 12.1009 | 168 | 4.3728 | 114.64 | 299.9291 | 0.11871
3103 | 917.3457 | 3.6712 | 79.8873 | 103.8453 | 63.3979 | 10.3615 | 159.0316 | 2.924 | 12.2172 | 52.4018 | 118.0119 | 29.3894 | 167.7863 | 187.6593 | 322.329 | 22.7743 | 59.3972 | 12.7485 | 296 | 5.154 | 144.2283 | 376.6658 | 0.1434
3104 | 1004.0943 | 8.1708 | 102.9357 | 125.1364 | 61.5502 | 12.1168 | 183.0154 | 2.9107 | 15.2971 | 52.8365 | 152.4509 | 38.3481 | 297.3963 | 247.606 | 423.004 | 31.5214 | 66.7286 | 14.207 | 312 | 6.6219 | 168.9473 | 438.2933 | 0.21067
3105 | 1072.3626 | 10.382 | 108.4801 | 138.509 | 62.0216 | 11.6689 | 201.2026 | 4.2383 | 19.4735 | 50.5102 | 177.119 | 39.3295 | 371.1491 | 296.4643 | 529.3072 | 36.6967 | 75.9701 | 18.0582 | 349 | 6.5181 | 198.3072 | 469.0939 | 0.18064
3106 | 1123.7612 | 8.5684 | 112.8066 | 139.5798 | 62.2203 | 11.4802 | 228.0278 | 4.507 | 20.4103 | 48.8404 | 187.5323 | 39.4942 | 400.1479 | 325.1697 | 611.7664 | 38.9339 | 90.4285 | 18.4464 | 371 | 6.1521 | 200.7302 | 488.468 | 0.21681
3107 | 1152.7591 | 7.3755 | 114.879 | 142.3927 | 61.5415 | 12.1251 | 244.4657 | 3.7786 | 19.3089 | 43.6374 | 189.827 | 36.7455 | 319.3433 | 338.4632 | 642.4576 | 37.7791 | 105.4009 | 17.2227 | 343 | 5.389 | 201.8827 | 505.2573 | 0.22151
3108 | 1176.7419 | 7.3438 | 112.2239 | 144.9184 | 61.3379 | 12.3185 | 234.9904 | 3.4979 | 17.5058 | 44.0021 | 191.8986 | 38.2702 | 280.5911 | 344.8788 | 640.2558 | 39.1572 | 110.7945 | 16.579 | 369 | 4.9374 | 197.9198 | 508.2428 | 0.29032
3109 | 1178.6463 | 7.1842 | 111.4599 | 145.4927 | 59.954 | 13.6332 | 194.6123 | 3.3301 | 15.9795 | 54.437 | 196.9519 | 40.7782 | 368.2271 | 352.5593 | 644.3993 | 40.0853 | 110.9865 | 16.3181 | 335 | 4.7596 | 195.2917 | 504.0289 | 0.26754
3110 | 1178.3026 | 6.9213 | 111.6897 | 150.8095 | 59.2818 | 14.2718 | 169.7081 | 3.3061 | 18.9567 | 67.5983 | 201.3359 | 40.2302 | 409.9134 | 357.2731 | 662.6768 | 40.233 | 111.5634 | 16.6558 | 358 | 5.001 | 193.6357 | 506.4192 | 0.29172
3111 | 1169.1762 | 5.5749 | 111.0196 | 147.571 | 59.2896 | 14.2643 | 171.0944 | 2.966 | 19.5628 | 74.0619 | 200.6635 | 38.0635 | 435.2409 | 349.8435 | 659.6322 | 40.0902 | 105.1498 | 16.5312 | 282 | 4.3052 | 194.9945 | 515.0053 | 0.2294
3112 | 1149.3887 | 4.4114 | 106.0428 | 137.2297 | 62.1532 | 11.5439 | 181.4974 | 2.6202 | 16.24 | 72.6945 | 194.5158 | 32.3969 | 411.2794 | 333.0543 | 604.8196 | 33.1372 | 93.1066 | 15.8565 | 254 | 3.0846 | 175.0665 | 483.8793 | 0.15686
3113 | 1084.004 | 3.9822 | 99.53 | 119.568 | 67.0234 | 6.9173 | 199.9838 | 1.9315 | 14.0612 | 62.2993 | 181.2488 | 28.8467 | 371.6983 | 282.2305 | 521.8877 | 17.897 | 83.7632 | 14.8099 | 219 | 2.799 | 147.6723 | 407.6967 | 0.15526
3114 | 995.1004 | 3.5009 | 96.4509 | 105.6628 | 67.5748 | 6.3934 | 185.9798 | 1.5026 | 13.1023 | 49.3925 | 151.3367 | 23.2587 | 314.4816 | 208.081 | 447.0149 | 10.62 | 75.5352 | 13.329 | 221 | 2.8171 | 133.3827 | 340.2817 | 0.08197
3115 | 946.3892 | 2.4164 | 80.189 | 100.5417 | 68.8018 | 5.2277 | 137.607 | 1.2303 | 12.93 | 39.1245 | 116.3379 | 10.2748 | 262.6404 | 165.2049 | 398.0855 | 9.1815 | 69.1077 | 13.0098 | 191 | 2.7824 | 120.6455 | 289.6999 | 0.043423
3116 | 922.0318 | 1.9854 | 49.2541 | 96.0107 | 69.2858 | 4.7679 | 121.7284 | 1.1384 | 12.3155 | 31.342 | 99.4194 | 5.4933 | 229.1591 | 148.7213 | 355.9184 | 8.6995 | 64.114 | 12.6016 | 173 | 2.6879 | 110.545 | 250.159 | 0.0032359
3117 | 897.4974 | 1.7538 | 45.5462 | 95.3505 | 68.5928 | 5.4263 | 114.7659 | 1.6512 | 11.8874 | 28.7551 | 95.4934 | 6.1358 | 188.4963 | 133.5145 | 327.7383 | 8.5897 | 59.1575 | 12.5314 | 169 | 2.6732 | 102.854 | 231.6667 | 0
3118 | 864.0323 | 1.7583 | 48.7691 | 99.1383 | 69.0326 | 5.0084 | 101.7643 | 2.1611 | 11.8961 | 28.9383 | 90.9617 | 7.5934 | 178.5357 | 124.0631 | 302.4597 | 8.9439 | 56.2642 | 12.4987 | 140 | 2.798 | 90.6793 | 226.1351 | 0
3119 | 828.104 | 1.5201 | 48.9007 | 100.587 | 68.5778 | 5.4405 | 119.6443 | 1.9709 | 12.112 | 28.4561 | 85.0874 | 7.033 | 178.5115 | 118.5566 | 272.277 | 10.3239 | 55.5067 | 12.0561 | 134 | 2.7383 | 64.9018 | 221.1229 | 0
3120 | 815.9985 | 1.3792 | 47.7388 | 100.0063 | 68.3122 | 5.6929 | 132.7138 | 1.6924 | 12.3186 | 26.5459 | 82.3021 | 6.3865 | 175.4084 | 111.0867 | 258.8476 | 12.3489 | 54.9712 | 11.4831 | 121 | 2.7003 | 56.0325 | 213.2703 | 0
3121 | 798.6173 | 1.432 | 47.0621 | 99.5342 | 69.0278 | 5.013 | 130.6048 | 1.6073 | 12.4172 | 24.9321 | 81.8949 | 6.3133 | 142.1407 | 103.0991 | 251.7037 | 13.0704 | 54.3719 | 11.284 | 115 | 2.7511 | 54.8317 | 207.4148 | 0
3122 | 794.5329 | 1.2975 | 48.3337 | 98.9307 | 68.6006 | 5.4188 | 117.626 | 1.6014 | 12.0472 | 24.4501 | 82.2717 | 8.3054 | 158.9789 | 100.065 | 254.3165 | 13.3768 | 54.1048 | 11.1155 | 134 | 2.8299 | 67.0384 | 205.0388 | 0
3123 | 806.3269 | 1.1636 | 49.7334 | 98.8249 | 68.2882 | 5.7157 | 112.9432 | 2.3517 | 11.8263 | 25.88 | 82.1871 | 14.2811 | 138.2494 | 99.4469 | 259.7711 | 13.0644 | 53.9396 | 11.0503 | 115 | 2.7632 | 84.9323 | 205.0188 | 0
3124 | 813.1507 | 1.5456 | 50.112 | 98.2848 | 69.0265 | 5.0143 | 104.433 | 2.2582 | 12.1085 | 31.2086 | 79.6985 | 13.785 | 154.1317 | 96.147 | 252.6636 | 10.7917 | 53.693 | 11.0437 | 112 | 2.7286 | 98.0337 | 210.6338 | 0
3125 | 825.6835 | 1.7268 | 51.934 | 97.2166 | 68.5689 | 5.449 | 102.4812 | 1.4637 | 12.332 | 36.3067 | 76.7923 | 7.2896 | 132.9413 | 100.1989 | 244.8301 | 9.1472 | 52.9691 | 10.8301 | 107 | 2.7881 | 96.7007 | 217.8078 | 0.021316
3126 | 853.5335 | 2.6488 | 50.92 | 98.702 | 66.0632 | 7.8294 | 117.8185 | 1.2009 | 12.042 | 39.7597 | 82.4763 | 10.5142 | 148.7557 | 129.5007 | 240.5214 | 11.4644 | 52.6134 | 10.7421 | 192 | 2.9818 | 104.2508 | 250.9945 | 0.077223
3127 | 917.5477 | 8.224 | 79.498 | 107.0733 | 62.3574 | 11.3499 | 164.0823 | 2.0088 | 14.0152 | 46.5251 | 108.7693 | 21.0544 | 145.7733 | 192.7162 | 287.5602 | 23.9873 | 56.3164 | 11.4805 | 296 | 4.9812 | 135.9117 | 315.4112 | 0.2196
3128 | 1007.5927 | 10.319 | 105.3558 | 120.626 | 60.6373 | 12.984 | 207.7172 | 2.5428 | 15.8877 | 53.4534 | 146.3206 | 25.0834 | 220.2463 | 263.0972 | 401.7935 | 34.2629 | 64.5081 | 13.0393 | 295 | 5.3847 | 167.8038 | 384.8535 | 0.24085
3129 | 1079.5162 | 6.248 | 115.278 | 138.3833 | 62.3956 | 11.3137 | 245.654 | 2.5081 | 17.9343 | 55.7904 | 174.0232 | 31.5479 | 304.2585 | 310.7605 | 525.7461 | 39.2304 | 74.4455 | 14.5508 | 353 | 5.254 | 193.147 | 445.3776 | 0.32722
3130 | 1130.8614 | 4.1065 | 116.9113 | 147.44 | 59.6711 | 13.9019 | 223.3926 | 2.4556 | 18.7952 | 55.0147 | 188.2657 | 39.5331 | 357.9912 | 336.7601 | 595.512 | 40.5962 | 91.6483 | 16.1852 | 341 | 6.9573 | 199.3803 | 486.9384 | 0.32231
3131 | 1163.2189 | 4.2225 | 116.4149 | 147.0315 | 53.4116 | 19.8484 | 247.3631 | 3.4302 | 18.9855 | 54.8615 | 192.9892 | 39.0208 | 428.323 | 353.6805 | 617.9104 | 40.4368 | 107.6283 | 17.0886 | 333 | 6.5022 | 203.7505 | 496.3397 | 0.31589
3132 | 1180.2532 | 4.2757 | 114.0416 | 140.5304 | 53.3826 | 19.876 | 256.126 | 2.9751 | 19.2928 | 56.4059 | 191.9742 | 35.0607 | 575.6766 | 361.7706 | 611.236 | 41.7753 | 109.8175 | 16.8054 | 340 | 6.2188 | 196.5979 | 487.6184 | 0.29494
3133 | 1202.1897 | 4.2116 | 112.9929 | 143.6581 | 55.0129 | 18.3272 | 247.2006 | 2.3835 | 19.3188 | 59.7859 | 193.8019 | 37.4494 | 608.6016 | 363.24 | 606.5482 | 42.6264 | 109.4039 | 17.1173 | 283 | 6.4887 | 200.5953 | 487.9661 | 0.27583
3134 | 1210.4094 | 4.1138 | 114.1336 | 147.6918 | 53.704 | 19.5707 | 250.0681 | 2.5879 | 16.7926 | 63.4256 | 199.1733 | 38.4903 | 581.3137 | 363.8652 | 605.9509 | 41.5602 | 111.6298 | 17.4501 | 270 | 7.3238 | 202.0673 | 493.38 | 0.29501
3135 | 1244.7921 | 4.2254 | 119.4237 | 141.0157 | 55.6644 | 17.7083 | 250.1056 | 2.3307 | 15.0436 | 63.4551 | 200.1739 | 37.9614 | 572.4214 | 351.6309 | 591.757 | 39.6049 | 111.6826 | 17.2024 | 320 | 5.6517 | 197.7791 | 506.4653 | 0.26327
3136 | 1213.8782 | 4.2387 | 112.5084 | 133.7801 | 61.3558 | 12.3015 | 234.7198 | 2.0405 | 14.9673 | 57.6864 | 194.4155 | 36.5944 | 561.4215 | 326.7771 | 553.4832 | 31.5497 | 108.1599 | 17.005 | 288 | 3.3047 | 178.2707 | 490.7958 | 0.26549
3137 | 1135.4626 | 4.0352 | 108.2741 | 117.7148 | 61.8434 | 11.8382 | 206.66 | 1.4756 | 15.5156 | 51.4961 | 178.899 | 34.5789 | 546.2284 | 277.3996 | 501.3945 | 17.8665 | 101.8303 | 16.3695 | 258 | 2.6196 | 147.8279 | 412.6905 | 0.23834
3138 | 1058.1741 | 3.7278 | 108.2741 | 105.2566 | 61.2829 | 12.3707 | 211.2287 | 1.0706 | 16.1599 | 48.7046 | 147.7126 | 26.9962 | 488.5226 | 212.3806 | 464.4844 | 11.6697 | 91.5027 | 15.0743 | 269 | 2.6555 | 129.9559 | 321.5783 | 0.14573
3139 | 1015.9367 | 2.8224 | 87.8079 | 99.7443 | 62.739 | 10.9874 | 146.7197 | 0.98243 | 15.8299 | 44.5366 | 116.1272 | 11.5104 | 433.956 | 171.6764 | 430.2208 | 9.859 | 77.3475 | 14.8192 | 283 | 2.6758 | 114.9607 | 258.2295 | 0.092686
3140 | 961.407 | 2.6401 | 50.4018 | 96.3199 | 64.8151 | 9.0151 | 120.2675 | 1.2204 | 13.6997 | 36.1297 | 104.0992 | 4.7539 | 397.3413 | 153.0214 | 373.924 | 9.2016 | 66.5001 | 14.3221 | 237 | 2.8141 | 107.429 | 219.7416 | 0.0074156
3141 | 931.3753 | 3.6427 | 46.2552 | 93.0951 | 66.0477 | 7.8442 | 113.9363 | 1.465 | 12.2191 | 27.1416 | 105.0001 | 4.9269 | 344.2162 | 141.7525 | 317.8693 | 9.6502 | 61.6199 | 13.3431 | 202 | 2.7061 | 103.2164 | 208.9683 | 0
3142 | 912.6988 | 3.3433 | 49.9576 | 97.1135 | 66.3362 | 7.57 | 116.7318 | 1.5716 | 11.8159 | 22.4178 | 103.2298 | 6.1697 | 294.9998 | 137.5654 | 300.3163 | 9.6147 | 59.863 | 12.9261 | 185 | 2.6674 | 92.7812 | 211.9474 | 0
3143 | 887.7498 | 1.9651 | 49.9576 | 99.3815 | 64.1007 | 9.6938 | 103.9874 | 2.2279 | 12.0451 | 19.8965 | 93.9984 | 6.5174 | 292.407 | 134.2523 | 298.1629 | 10.5377 | 59.3722 | 12.6245 | 155 | 2.6365 | 65.09 | 209.73 | 0
3144 | 884.9058 | 1.2515 | 49.2087 | 98.9937 | 65.4758 | 8.3874 | 110.8313 | 2.2225 | 11.7234 | 17.7842 | 86.4462 | 6.6884 | 289.9565 | 128.864 | 277.4261 | 12.9492 | 59.1733 | 12.4407 | 147 | 2.6402 | 55.8477 | 204.3136 | 0
3145 | 862.3795 | 1.3142 | 48.7819 | 98.9815 | 66.2738 | 7.6293 | 120.3691 | 1.7705 | 11.8536 | 17.1398 | 84.5302 | 6.5251 | 277.2133 | 124.9587 | 258.0564 | 13.6992 | 59.0048 | 11.8791 | 140 | 2.7466 | 86.6526 | 201.6376 | 0
3146 | 842.4039 | 1.3701 | 50.0663 | 99.3741 | 65.6116 | 8.2585 | 104.3914 | 2.3407 | 11.9793 | 17.3961 | 84.0189 | 9.6231 | 261.6334 | 125.9278 | 246.7117 | 13.6275 | 58.9776 | 11.2379 | 148 | 2.7133 | 100.0931 | 201.1087 | 0
3147 | 847.983 | 1.5127 | 50.3127 | 98.5062 | 66.0463 | 7.8455 | 109.1153 | 2.0513 | 11.8677 | 18.7603 | 83.496 | 17.9696 | 221.5962 | 132.3553 | 236.7436 | 13.5553 | 58.9934 | 11.0501 | 123 | 2.6443 | 102.5288 | 202.8849 | 0
3148 | 848.3423 | 1.9753 | 50.0262 | 96.6718 | 63.2846 | 10.4691 | 113.8347 | 2.3293 | 11.9291 | 23.4848 | 82.0828 | 17.2114 | 209.8121 | 140.2922 | 237.5784 | 12.4867 | 58.5526 | 10.9841 | 121 | 2.6774 | 101.9449 | 206.0259 | 0
3149 | 863.0517 | 2.1961 | 53.9508 | 93.4348 | 64.5722 | 9.2458 | 112.6446 | 1.7787 | 11.6159 | 28.5183 | 79.7722 | 8.9942 | 206.6271 | 141.5154 | 240.8628 | 9.891 | 57.6049 | 10.7962 | 118 | 2.6659 | 97.4132 | 213.9412 | 0.041417
3150 | 891.7906 | 2.8266 | 76.9265 | 94.7715 | 64.5227 | 9.2929 | 122.9777 | 2.2259 | 11.2734 | 32.9388 | 85.9889 | 14.227 | 205.2181 | 146.7668 | 247.7083 | 12.4526 | 57.2899 | 10.7555 | 198 | 2.5596 | 107.8576 | 248.8544 | 0.13134
3151 | 951.7904 | 3.7011 | 86.8398 | 100.3229 | 60.6332 | 12.988 | 159.6921 | 2.3205 | 11.7793 | 40.1777 | 112.6438 | 27.8561 | 275.5984 | 181.4219 | 309.2444 | 25.1877 | 61.5598 | 12.2314 | 301 | 3.8739 | 149.4197 | 313.1194 | 0.2145
3152 | 1064.9166 | 7.0925 | 86.8398 | 119.0156 | 58.5879 | 14.931 | 174.6975 | 2.5491 | 13.8743 | 45.4097 | 152.4011 | 32.7339 | 351.9347 | 236.5936 | 412.1231 | 34.297 | 71.2391 | 14.9585 | 342 | 4.1277 | 177.0958 | 381.8259 | 0.27143
3153 | 1143.272 | 5.7182 | 109.2292 | 133.5447 | 58.9208 | 14.6147 | 182.4284 | 3.0103 | 16.162 | 48.6438 | 177.7153 | 34.6334 | 418.2293 | 279.2125 | 516.1473 | 37.9057 | 82.2677 | 15.8919 | 361 | 4.6538 | 199.3362 | 438.7283 | 0.31145
3154 | 1185.9812 | 4.0868 | 120.8525 | 138.9223 | 58.0022 | 15.4873 | 190.915 | 3.2329 | 17.2637 | 50.6217 | 183.1107 | 37.4981 | 451.7249 | 306.2633 | 583.7056 | 41.2427 | 98.3789 | 16.649 | 369 | 5.6067 | 216.5244 | 474.9327 | 0.28815
3155 | 1209.0053 | 4.0802 | 121.5533 | 138.4877 | 57.1797 | 16.2687 | 217.9196 | 3.3807 | 17.8284 | 54.8136 | 187.9464 | 38.3231 | 484.8665 | 324.6089 | 602.2367 | 41.5436 | 111.5694 | 17.4748 | 333 | 6.1104 | 218.5697 | 493.111 | 0.28747
3156 | 1219.5009 | 4.1058 | 121.5533 | 138.9233 | 58.7969 | 14.7324 | 229.4259 | 3.4295 | 18.1131 | 57.5635 | 193.7217 | 37.2765 | 517.9842 | 329.9469 | 600.372 | 41.1921 | 112.7305 | 17.872 | 335 | 5.6247 | 211.5309 | 501.8271 | 0.25597
3157 | 1229.4166 | 8.3754 | 120.5688 | 141.0681 | 59.4686 | 14.0943 | 221.4902 | 3.4747 | 16.8238 | 54.705 | 199.9102 | 37.1212 | 550.6663 | 341.2598 | 607.6632 | 41.1635 | 111.2295 | 18.6578 | 318 | 5.3253 | 213.1073 | 502.0739 | 0.27501
3158 | 1231.6866 | 10.0756 | 122.2616 | 144.0567 | 56.1956 | 17.2037 | 233.0406 | 3.6386 | 16.228 | 56.0956 | 205.1016 | 36.5309 | 577.475 | 355.1152 | 614.357 | 42.1189 | 110.9972 | 19.1493 | 307 | 4.9615 | 214.1589 | 499.1668 | 0.31431
3159 | 1194.591 | 6.0462 | 121.4677 | 140.8595 | 58.2717 | 15.2314 | 217.356 | 3.4511 | 16.786 | 65.4184 | 202.8543 | 36.1987 | 596.9234 | 348.1259 | 605.8956 | 40.3093 | 110.1648 | 18.6711 | 282 | 4.5738 | 204.7371 | 489.8229 | 0.28903
3160 | 1173.3381 | 3.9718 | 117.1457 | 135.1281 | 63.7458 | 10.031 | 232.8293 | 2.8113 | 17.1896 | 74.2382 | 198.2529 | 32.1088 | 592.5427 | 326.0096 | 580.5976 | 34.1512 | 108.2415 | 18.5437 | 275 | 3.742 | 185.0319 | 461.7434 | 0.27514
3161 | 1162.5901 | 3.9792 | 106.1229 | 124.6414 | 65.2827 | 8.5709 | 205.3438 | 1.7502 | 16.0708 | 73.6939 | 187.4528 | 27.5235 | 557.494 | 281.2222 | 501.0229 | 20.1689 | 103.4388 | 17.9603 | 233 | 2.6737 | 160.1605 | 403.8511 | 0.26502
3162 | 1110.5826 | 3.0712 | 102.0659 | 109.8475 | 66.0634 | 7.8292 | 160.2898 | 1.2922 | 15.1346 | 65.7833 | 158.0632 | 21.218 | 506.3982 | 226.677 | 416.4458 | 11.6869 | 90.4805 | 17.2491 | 211 | 2.3222 | 139.206 | 328.0816 | 0.21012
3163 | 1019.7734 | 2.1479 | 92.1686 | 99.8828 | 65.6942 | 8.1799 | 113.8618 | 1.0843 | 14.487 | 51.0258 | 125.1481 | 9.4723 | 446.751 | 187.1582 | 389.5016 | 9.5305 | 75.1337 | 15.4885 | 184 | 2.3454 | 120.9388 | 264.478 | 0.14021
3164 | 954.806 | 2.592 | 65.2431 | 94.9131 | 65.9715 | 7.9165 | 112.3159 | 1.1024 | 13.0627 | 41.194 | 109.2686 | 4.8559 | 376.3701 | 154.1805 | 365.0748 | 9.1407 | 65.7208 | 14.0673 | 181 | 2.389 | 110.8618 | 222.9885 | 0.032033
3165 | 926.745 | 3.814 | 60.7904 | 97.9076 | 65.5215 | 8.344 | 105.4072 | 1.5199 | 12.484 | 40.9483 | 103.8699 | 5.4527 | 350.5115 | 133.3409 | 333.4256 | 9.4264 | 60.4077 | 13.3269 | 169 | 2.4086 | 102.7973 | 208.1739 | 0
3166 | 911.7694 | 3.3101 | 63.2435 | 104.1911 | 63.8089 | 9.971 | 115.2932 | 2.3053 | 11.7861 | 41.9778 | 96.1069 | 6.9263 | 340.4425 | 132.6123 | 310.2852 | 9.2252 | 58.4546 | 12.9253 | 155 | 2.5295 | 91.3185 | 210.1836 | 0
3167 | 890.1371 | 1.8883 | 62.4803 | 103.5336 | 65.5854 | 8.2833 | 138.7806 | 2.0338 | 11.8689 | 42.1021 | 85.8935 | 8.1923 | 317.2202 | 134.4302 | 295.6659 | 10.2932 | 57.9655 | 12.6768 | 136 | 2.4541 | 63.3379 | 210.9454 | 0
3168 | 883.133 | 1.4496 | 62.2339 | 99.9271 | 64.1321 | 9.664 | 125.4359 | 2.4289 | 11.8676 | 37.0168 | 80.2918 | 8.5733 | 290.6629 | 126.524 | 276.0452 | 12.5764 | 57.2712 | 12.6603 | 122 | 2.4676 | 54.8562 | 208.7198 | 0
3169 | 868.1946 | 1.2981 | 63.2398 | 98.5263 | 66.2298 | 7.6712 | 109.2814 | 2.0908 | 11.6681 | 30.012 | 78.747 | 7.4399 | 278.1474 | 118.1208 | 254.1356 | 13.7871 | 57.1235 | 12.5452 | 117 | 2.5474 | 84.3265 | 204.0079 | 0
3170 | 847.7929 | 1.1635 | 63.5639 | 98.4606 | 66.4998 | 7.4146 | 106.8954 | 2.7041 | 11.6988 | 26.5362 | 79.1281 | 9.9071 | 238.779 | 113.1901 | 245.2254 | 13.9719 | 57.0695 | 11.8896 | 142 | 2.6416 | 96.3525 | 199.1279 | 0
3171 | 855.1453 | 1.1398 | 63.6024 | 98.7877 | 65.534 | 8.3321 | 101.8225 | 2.3086 | 12.14 | 25.9188 | 79.8437 | 14.2943 | 209.8574 | 110.3267 | 239.3612 | 13.8133 | 56.9002 | 11.4852 | 107 | 2.7801 | 96.3944 | 199.8051 | 0
3172 | 868.4294 | 1.642 | 63.2581 | 96.3102 | 66.1296 | 7.7664 | 106.3778 | 2.4361 | 11.7671 | 29.0504 | 77.9337 | 8.7474 | 221.865 | 106.3217 | 237.0584 | 10.4813 | 56.4533 | 11.3416 | 105 | 2.8736 | 94.4739 | 201.6836 | 0
3173 | 868.0647 | 1.8672 | 61.0143 | 91.2698 | 65.5493 | 8.3176 | 94.2734 | 2.7555 | 11.7822 | 32.9264 | 74.5637 | 5.64 | 230.696 | 107.4909 | 236.3585 | 8.6912 | 55.6799 | 11.2576 | 109 | 2.874 | 89.955 | 206.2817 | 0.080976
3174 | 903.3044 | 2.3067 | 57.0282 | 92.6792 | 63.0861 | 10.6576 | 94.9399 | 1.7669 | 12.023 | 39.971 | 78.554 | 11.4386 | 236.2696 | 132.9196 | 245.8063 | 12.6879 | 55.6778 | 11.4782 | 204 | 3.2427 | 102.3073 | 239.3407 | 0.18676
3175 | 985.687 | 4.194 | 80.1492 | 100.4762 | 57.7092 | 15.7657 | 122.3815 | 2.5595 | 13.0572 | 51.3647 | 106.2113 | 24.695 | 295.9961 | 186.3627 | 316.614 | 25.7914 | 59.9855 | 12.1862 | 302 | 4.82 | 143.5119 | 308.4096 | 0.2651
3176 | 1073.7552 | 7.522 | 106.6872 | 121.0159 | 57.1315 | 16.3145 | 159.9874 | 3.1166 | 15.237 | 60.3219 | 152.5826 | 31.3501 | 345.5673 | 245.9109 | 427.4428 | 35.1422 | 68.4975 | 13.6646 | 371 | 5.5713 | 170.8308 | 388.387 | 0.30359
3177 | 1164.6915 | 15.3062 | 113.3409 | 134.4536 | 57.3472 | 16.1096 | 182.5478 | 2.6999 | 18.1754 | 68.6536 | 185.5794 | 33.0902 | 403.6168 | 289.8463 | 524.5083 | 39.2877 | 76.7608 | 15.7183 | 355 | 6.311 | 192.0201 | 448.6561 | 0.33602
3178 | 1210.3551 | 16.3908 | 114.4593 | 138.9273 | 57.4007 | 16.0588 | 184.7921 | 2.492 | 19.3707 | 69.9741 | 197.8487 | 35.2239 | 466.6606 | 316.5212 | 583.7896 | 41.1441 | 91.933 | 17.1744 | 389 | 6.607 | 210.4559 | 477.3338 | 0.30986
3179 | 1228.5924 | 10.916 | 116.4708 | 139.4696 | 56.4881 | 16.9258 | 197.4021 | 2.594 | 20.525 | 63.2478 | 204.1864 | 35.1382 | 509.9556 | 330.8665 | 612.7018 | 40.7353 | 109.1725 | 17.5531 | 339 | 6.912 | 209.7466 | 480.5812 | 0.30269
3180 | 1227.3965 | 5.5182 | 117.2268 | 139.3932 | 58.474 | 15.0391 | 234.5259 | 2.6681 | 19.5893 | 58.4863 | 204.4135 | 33.8679 | 543.1419 | 338.5703 | 629.6701 | 42.1246 | 116.1751 | 18.1424 | 330 | 6.7115 | 194.4642 | 480.2893 | 0.26015
3181 | 1238.0368 | 3.6048 | 117.2144 | 142.0025 | 57.1132 | 16.3319 | 212.4021 | 3.5046 | 16.5377 | 58.8909 | 201.5737 | 33.8624 | 555.8903 | 344.2306 | 635.5287 | 42.281 | 120.2792 | 19.014 | 310 | 6.072 | 201.2968 | 484.473 | 0.26058
3182 | 1242.1994 | 3.848 | 118.413 | 142.1162 | 57.0569 | 16.3854 | 204.5435 | 3.437 | 14.74 | 62.4541 | 206.2352 | 36.5736 | 563.2612 | 347.0141 | 637.2375 | 42.2324 | 124.9123 | 19.0716 | 301 | 6.2705 | 203.9636 | 487.7364 | 0.33242
3183 | 1219.7495 | 4.1841 | 114.2351 | 137.5453 | 56.4094 | 17.0005 | 225.599 | 2.9684 | 15.1604 | 66.1907 | 209.7576 | 37.0797 | 559.6904 | 346.4858 | 629.8479 | 39.4931 | 126.1201 | 18.5421 | 298 | 4.5264 | 201.8707 | 484.3657 | 0.29261
3184 | 1201.4859 | 4.0106 | 107.5351 | 136.2371 | 61.6252 | 12.0455 | 197.2657 | 2.7649 | 15.3958 | 68.9702 | 203.86 | 33.6524 | 547.4845 | 334.2122 | 594.5012 | 29.7425 | 122.7608 | 17.8619 | 279 | 2.6012 | 188.4484 | 444.2577 | 0.23889
3185 | 1118.0378 | 3.6765 | 95.3221 | 118.197 | 64.7787 | 9.0497 | 185.0447 | 1.7337 | 15.8366 | 68.268 | 187.3247 | 30.8017 | 550.0134 | 281.6189 | 524.7498 | 16.0655 | 115.9075 | 16.75 | 240 | 2.0627 | 153.4658 | 369.6336 | 0.25475
3186 | 1042.1085 | 2.4195 | 90.6327 | 101.7786 | 65.298 | 8.5564 | 177.394 | 1.2953 | 17.3871 | 64.2711 | 152.8552 | 25.3986 | 493.5405 | 219.8204 | 453.6082 | 9.5783 | 107.4457 | 16.006 | 208 | 2.0575 | 133.7039 | 301.9131 | 0.21746
3187 | 997.2331 | 1.854 | 71.2539 | 95.1909 | 65.4025 | 8.457 | 136.5319 | 1.8543 | 15.9381 | 56.4619 | 118.3639 | 14.5709 | 421.1231 | 184.1228 | 412.6807 | 8.5747 | 93.5548 | 13.4349 | 199 | 2.1728 | 119.0458 | 247.6337 | 0.14665
3188 | 959.4009 | 3.004 | 43.6415 | 91.4201 | 64.5035 | 9.3112 | 116.1498 | 1.5988 | 13.0389 | 49.0548 | 103.4859 | 14.9334 | 354.5282 | 156.7607 | 369.1953 | 8.423 | 74.3591 | 7.882 | 170 | 2.0873 | 111.6459 | 208.3706 | 0.034164
3189 | 932.586 | 3.4603 | 46.0507 | 90.849 | 64.3387 | 9.4677 | 122.6833 | 2.3791 | 13.18 | 44.623 | 98.5249 | 16.2804 | 320.5785 | 132.8987 | 319.3915 | 9.0918 | 61.0049 | 5.1903 | 157 | 1.9765 | 107.0198 | 194.0725 | 0
3190 | 896.0902 | 2.8281 | 50.7342 | 97.4229 | 64.3303 | 9.4757 | 126.5383 | 2.1807 | 12.6949 | 41.0449 | 92.0365 | 14.8366 | 273.9338 | 122.5783 | 278.7293 | 9.2588 | 57.8058 | 4.4825 | 148 | 2.0339 | 98.1978 | 197.7929 | 0
3191 | 875.9378 | 1.6735 | 50.7342 | 98.5245 | 65.7313 | 8.1448 | 117.3594 | 2.4824 | 12.3676 | 39.0798 | 83.4841 | 14.0117 | 230.7449 | 120.4341 | 256.7331 | 8.7652 | 58.6806 | 4.0172 | 130 | 2.1589 | 68.7279 | 204.4022 | 0
3192 | 878.85 | 1.1853 | 50.7342 | 98.818 | 67.7581 | 6.2193 | 113.7034 | 2.5834 | 12.308 | 37.5456 | 79.3303 | 11.1721 | 220.2054 | 115.6688 | 254.2419 | 8.8392 | 59.273 | 3.9674 | 121 | 2.0614 | 59.7021 | 202.4892 | 0
3193 | 859.9521 | 1.1553 | 51.0458 | 99.2066 | 66.0889 | 7.805 | 99.9019 | 2.5696 | 12.2662 | 34.6196 | 78.8147 | 8.2406 | 234.7928 | 111.175 | 258.3927 | 8.7263 | 59.4045 | 3.7889 | 118 | 2.0261 | 88.826 | 198.6889 | 0
3194 | 842.0947 | 1.1455 | 51.0482 | 98.1164 | 65.3321 | 8.524 | 104.2202 | 2.9654 | 12.1143 | 30.9214 | 77.8976 | 9.2855 | 245.3538 | 106.2614 | 257.2382 | 9.0064 | 59.7036 | 3.0753 | 145 | 2.1192 | 98.4291 | 196.3724 | 0
3195 | 853.2926 | 1.7327 | 51.0374 | 98.2155 | 65.3174 | 8.5379 | 107.5041 | 3.131 | 12.1596 | 30.2707 | 77.5805 | 9.5598 | 239.2868 | 102.375 | 246.1439 | 9.1228 | 59.6963 | 2.5958 | 113 | 2.141 | 98.9644 | 198.6035 | 0
3196 | 849.7977 | 2.0096 | 51.0751 | 96.4762 | 66.055 | 7.8372 | 92.3233 | 2.0607 | 12.0859 | 34.1211 | 76.2832 | 6.6947 | 216.51 | 101.0281 | 235.739 | 8.8477 | 58.6326 | 2.4398 | 110 | 2.0653 | 98.0646 | 210.8675 | 0
3197 | 858.364 | 1.3692 | 55.6001 | 91.8229 | 66.2826 | 7.621 | 81.4848 | 2.3463 | 11.9548 | 38.5891 | 73.4657 | 6.1135 | 211.2439 | 106.6215 | 230.2108 | 8.3827 | 57.6434 | 2.292 | 122 | 2.0761 | 93.3808 | 225.8149 | 0.079435
3198 | 908.5886 | 1.7582 | 69.3261 | 91.9101 | 63.3082 | 10.4466 | 92.3892 | 2.2055 | 11.6689 | 44.1486 | 82.8935 | 13.7159 | 220.9935 | 131.0313 | 240.5457 | 12.4678 | 57.7693 | 2.2771 | 202 | 2.4581 | 101.647 | 250.8475 | 0.175
3199 | 971.6592 | 3.1226 | 74.5277 | 100.2084 | 57.901 | 15.5835 | 120.4185 | 2.7261 | 12.0861 | 48.5054 | 119.2202 | 25.108 | 276.6577 | 184.085 | 319.2547 | 24.9224 | 61.2553 | 8.2286 | 255 | 4.2467 | 137.3725 | 302.8157 | 0.27481
3200 | 1037.3343 | 6.8057 | 100.1009 | 118.5013 | 56.4366 | 16.9746 | 165.0207 | 3.0177 | 14.1155 | 45.8121 | 162.5603 | 29.7527 | 335.8812 | 248.1121 | 432.0679 | 34.3647 | 69.812 | 13.7877 | 328 | 5.0275 | 168.3656 | 382.1163 | 0.31001
3201 | 1109.8723 | 5.6757 | 112.0685 | 133.1196 | 56.1824 | 17.2162 | 199.344 | 3.1805 | 16.9863 | 42.6651 | 186.2536 | 30.6646 | 394.7621 | 295.3251 | 526.8859 | 39.4827 | 86.1687 | 16.0905 | 377 | 5.5164 | 190.1857 | 460.5733 | 0.33513
3202 | 1193.9775 | 4.0394 | 110.7217 | 137.7824 | 56.9926 | 16.4465 | 225.2253 | 3.3352 | 17.6026 | 42.9914 | 193.3398 | 32.8491 | 442.9498 | 326.3395 | 592.2582 | 39.2883 | 102.5468 | 17.0863 | 369 | 5.4885 | 205.1843 | 511.1888 | 0.30792
3203 | 1221.8301 | 6.9546 | 111.7129 | 138.5205 | 57.3408 | 16.1157 | 220.7204 | 3.3952 | 16.0923 | 45.5407 | 194.1333 | 33.4467 | 484.8119 | 344.0781 | 628.8129 | 36.3614 | 107.3041 | 17.3616 | 347 | 4.8669 | 208.9565 | 523.7912 | 0.2236
3204 | 1218.8796 | 10.2589 | 113.375 | 136.3824 | 57.9997 | 15.4897 | 210.2876 | 3.359 | 16.2271 | 50.7661 | 193.2305 | 34.6028 | 500.9777 | 343.2601 | 631.183 | 34.3199 | 104.9105 | 17.4512 | 376 | 4.1726 | 196.8331 | 513.4023 | 0.21255
3205 | 1229.123 | 8.2231 | 113.273 | 139.7296 | 59.0812 | 14.4623 | 196.6734 | 3.066 | 18.2807 | 54.9771 | 195.6133 | 37.6578 | 510.9539 | 340.716 | 619.2662 | 32.3796 | 104.4612 | 18.2285 | 306 | 4.3137 | 202.8292 | 515.4894 | 0.3002
3206 | 1228.6095 | 4.5735 | 114.3047 | 142.0607 | 55.5713 | 17.7967 | 186.963 | 2.7888 | 19.8392 | 60.6005 | 201.6716 | 34.2317 | 517.2171 | 347.1831 | 619.7827 | 31.9427 | 107.2013 | 18.4856 | 325 | 3.366 | 204.0134 | 522.052 | 0.27383
3207 | 1190.9263 | 6.2907 | 91.8298 | 142.6585 | 52.1321 | 21.064 | 180.2987 | 2.7875 | 17.5009 | 73.1107 | 205.1031 | 30.9904 | 516.9494 | 343.1674 | 613.2523 | 31.7373 | 107.4709 | 18.148 | 314 | 1.4985 | 196.319 | 507.9523 | 0.20456
3208 | 1141.9669 | 9.3387 | 81.5912 | 134.2999 | 58.6792 | 14.8443 | 174.8095 | 2.3758 | 14.6958 | 82.5556 | 200.9446 | 29.5545 | 502.2864 | 313.5254 | 566.8352 | 21.3635 | 104.0746 | 17.6982 | 315 | 0.62288 | 178.1566 | 459.3335 | 0.1929
3209 | 1092.6585 | 6.7011 | 81.5912 | 116.8248 | 64.2637 | 9.5389 | 174.8323 | 2.6874 | 14.522 | 74.3505 | 184.0077 | 28.5132 | 489.6617 | 250.1761 | 486.0695 | 13.7645 | 95.3165 | 17.0636 | 263 | 0.6363 | 147.9499 | 384.1814 | 0.22245
3210 | 1018.9241 | 3.0897 | 81.5912 | 102.4252 | 65.3684 | 8.4895 | 156.8125 | 1.9226 | 13.5512 | 59.5476 | 147.6606 | 22.5424 | 472.3808 | 184.8739 | 403.2661 | 12.474 | 82.0309 | 16.3823 | 232 | 0.59862 | 126.6131 | 323.8836 | 0.096107
3211 | 958.6819 | 2.1439 | 47.9639 | 94.3759 | 65.98 | 7.9084 | 116.4457 | 2.1011 | 12.4887 | 47.4902 | 109.6418 | 9.6016 | 411.4623 | 152.9027 | 355.9393 | 12.0224 | 70.3251 | 13.0109 | 218 | 0.57374 | 111.1525 | 288.8747 | 0.067857
3212 | 919.3298 | 2.4963 | 32.958 | 92.2197 | 65.6093 | 8.2606 | 96.3559 | 2.9015 | 11.9621 | 38.1691 | 88.8693 | 4.6696 | 354.0131 | 136.8896 | 329.9823 | 16.8491 | 62.1433 | 6.793 | 188 | 0.55365 | 105.6647 | 262.898 | 0.012308
3213 | 899.2612 | 3.905 | 39.8482 | 94.6179 | 65.3506 | 8.5064 | 92.195 | 2.3921 | 11.6077 | 37.4559 | 80.5946 | 5.8685 | 312.8973 | 123.5948 | 306.8828 | 17.7902 | 57.8192 | 4.1245 | 198 | 0.63183 | 98.1998 | 259.8778 | 0
3214 | 902.1496 | 3.877 | 44.4428 | 93.4519 | 65.2131 | 8.637 | 90.5927 | 2.5218 | 11.9294 | 40.1715 | 79.8902 | 7.0626 | 275.8438 | 116.023 | 292.5743 | 13.9981 | 56.2107 | 4.0474 | 174 | 0.57371 | 86.9859 | 276.7577 | 0
3215 | 888.1611 | 3.1145 | 45.12 | 92.2763 | 63.9029 | 9.8817 | 89.7642 | 3.146 | 12.0172 | 39.9583 | 80.3898 | 7.281 | 254.2352 | 112.7437 | 291.8438 | 10.7312 | 54.8783 | 3.6081 | 165 | 0.56011 | 64.109 | 287.736 | 0
3216 | 876.6628 | 2.7866 | 45.12 | 92.2233 | 65.4975 | 8.3669 | 89.9817 | 3.3427 | 12.1079 | 34.5808 | 79.0304 | 7.1451 | 240.3122 | 111.4607 | 292.0715 | 9.1925 | 51.9598 | 2.9831 | 155 | 0.60997 | 51.4414 | 289.3383 | 0
3217 | 849.3018 | 2.3309 | 48.4422 | 92.0494 | 64.7443 | 9.0824 | 89.8262 | 3.6303 | 11.9348 | 28.3419 | 77.7928 | 7.119 | 231.2373 | 103.9795 | 281.8912 | 8.8965 | 49.0303 | 2.9019 | 148 | 0.4718 | 47.5183 | 285.981 | 0
3218 | 822.5447 | 2.1209 | 49.9744 | 92.464 | 65.1268 | 8.719 | 89.6758 | 2.677 | 11.9341 | 25.375 | 77.6595 | 7.249 | 224.9473 | 95.0272 | 270.5766 | 9.595 | 48.1013 | 2.6181 | 171 | 0.50118 | 46.1941 | 274.5231 | 0
3219 | 845.455 | 2.0489 | 49.9744 | 92.6332 | 65.3073 | 8.5476 | 89.5122 | 2.6359 | 12.0835 | 23.8736 | 78.1167 | 7.214 | 211.5948 | 91.1694 | 260.1303 | 9.2445 | 48.1248 | 2.5773 | 138 | 0.55559 | 45.7681 | 265.6552 | 0
3220 | 856.9586 | 2.6108 | 39.8101 | 91.2098 | 65.2836 | 8.5701 | 89.2834 | 3.3386 | 12.266 | 24.5878 | 77.9229 | 7.1837 | 151.8983 | 88.8798 | 258.8957 | 8.8287 | 48.9535 | 2.8869 | 128 | 0.50886 | 45.5778 | 262.9609 | 0
3221 | 851.9513 | 3.5933 | 34.8848 | 89.0564 | 65.9867 | 7.9021 | 88.6843 | 3.3259 | 12.248 | 26.3802 | 75.8081 | 5.3995 | 117.5702 | 87.192 | 255.5359 | 8.7387 | 50.4443 | 2.666 | 125 | 0.61791 | 45.8796 | 253.678 | 0.0090681
3222 | 853.7949 | 2.9925 | 48.7362 | 88.6008 | 64.1399 | 9.6566 | 89.0835 | 3.162 | 12.0943 | 28.186 | 75.0089 | 4.5276 | 115.031 | 87.0095 | 256.2381 | 8.7115 | 49.6773 | 2.2737 | 123 | 0.53138 | 47.4996 | 239.6849 | 0.037748
3223 | 865.9992 | 2.1428 | 54.9556 | 88.1192 | 65.5917 | 8.2773 | 89.922 | 3.159 | 11.6473 | 29.406 | 75.3926 | 4.4711 | 108.3104 | 90.9043 | 250.2348 | 8.8113 | 47.4762 | 2.3222 | 128 | 0.47842 | 49.4047 | 229.2428 | 0.075956
3224 | 876.6458 | 2.2574 | 67.8821 | 89.21 | 65.5267 | 8.3391 | 89.572 | 3.5424 | 11.5069 | 30.6928 | 73.6685 | 4.4326 | 118.59 | 98.3301 | 237.4763 | 8.502 | 47.2105 | 2.8882 | 129 | 0.53614 | 51.7734 | 226.719 | 0.10413
3225 | 877.1829 | 2.071 | 73.9102 | 89.2362 | 63.7844 | 9.9942 | 89.8015 | 2.5732 | 11.6977 | 36.8819 | 84.1237 | 4.3867 | 160.5529 | 108.4473 | 242.2694 | 9.1028 | 48.297 | 5.1357 | 144 | 0.4194 | 57.2833 | 229.3651 | 0.089332
3226 | 858.0764 | 1.7494 | 76.0862 | 90.3919 | 65.5264 | 8.3394 | 94.7921 | 2.1645 | 12.3264 | 43.7505 | 107.977 | 4.7065 | 180.0225 | 118.683 | 256.4498 | 10.0182 | 48.7307 | 11.1619 | 169 | 0.48191 | 63.4618 | 237.499 | 0.1266
3227 | 866.2779 | 2.1067 | 77.0796 | 93.7446 | 65.4675 | 8.3953 | 101.0519 | 2.8904 | 12.7199 | 45.7021 | 113.9091 | 4.7536 | 178.2566 | 126.0519 | 269.9142 | 9.5271 | 48.2875 | 14.579 | 177 | 0.40469 | 66.883 | 250.1241 | 0.15604
3228 | 861.6659 | 2.301 | 78.3459 | 93.9141 | 64.5671 | 9.2508 | 101.4847 | 3.6797 | 12.983 | 46.0884 | 102.8638 | 4.7745 | 178.6852 | 132.7536 | 262.6165 | 9.2282 | 48.539 | 14.9666 | 208 | 0.47884 | 70.0247 | 252.8271 | 0.15345
3229 | 847.8144 | 2.0931 | 73.4276 | 92.9708 | 65.1897 | 8.6593 | 103.7592 | 3.0899 | 12.496 | 45.3166 | 99.5266 | 4.7818 | 179.44 | 143.6692 | 263.3552 | 9.285 | 49.4637 | 15.2205 | 246 | 0.39334 | 72.4007 | 246.7365 | 0.15749
3230 | 840.8581 | 2.2772 | 55.9939 | 94.4726 | 65.2824 | 8.5712 | 104.7633 | 1.9914 | 12.1094 | 40.3231 | 102.1501 | 4.8706 | 170.0669 | 154.3543 | 275.1019 | 9.0432 | 50.3707 | 15.5071 | 243 | 0.46829 | 75.208 | 241.0437 | 0.16334
3231 | 846.9829 | 1.9419 | 48.6117 | 94.1033 | 65.2363 | 8.615 | 103.5531 | 2.6564 | 12.1796 | 34.3426 | 102.125 | 5.8813 | 171.6899 | 157.5113 | 289.0077 | 8.6899 | 51.7417 | 15.655 | 234 | 0.4395 | 72.7787 | 237.5631 | 0.21763
3232 | 842.6143 | 1.6503 | 48.0632 | 93.5189 | 65.3975 | 8.4618 | 102.3755 | 3.2044 | 12.6978 | 34.8475 | 99.5245 | 6.1222 | 175.3036 | 148.7726 | 306.6417 | 8.2123 | 53.1323 | 15.5262 | 242 | 0.37671 | 69.2786 | 237.1769 | 0.10986
3233 | 835.7998 | 1.5463 | 48.4591 | 92.4377 | 65.3549 | 8.5023 | 102.0679 | 2.9172 | 13.0813 | 37.4233 | 97.8173 | 6.0433 | 170.4155 | 136.0486 | 306.9023 | 8.2564 | 53.8552 | 15.1281 | 247 | 0.45969 | 66.6613 | 242.7889 | 0.10275
3234 | 822.4515 | 2.8601 | 48.6031 | 91.6249 | 65.9526 | 7.9345 | 95.3277 | 2.1923 | 13.1136 | 33.3606 | 91.3314 | 6.4631 | 162.1298 | 130.5052 | 290.3409 | 8.3664 | 54.018 | 12.2989 | 258 | 0.40674 | 68.3291 | 245.5208 | 0.11469
3235 | 811.8843 | 6.3352 | 48.5571 | 90.757 | 66.3127 | 7.5924 | 89.5531 | 2.5436 | 13.0752 | 27.1556 | 80.1752 | 7.1302 | 163.2389 | 128.8401 | 276.3886 | 8.2387 | 53.2635 | 6.5989 | 259 | 0.50176 | 68.9303 | 234.1494 | 0.046869
3236 | 810.8944 | 4.6863 | 48.2718 | 90.5402 | 65.5829 | 8.2857 | 91.1531 | 3.1437 | 12.8711 | 23.2578 | 73.3378 | 11.3621 | 162.6755 | 129.7178 | 267.0219 | 8.1328 | 51.7896 | 4.3427 | 311 | 0.44164 | 67.868 | 228.2328 | 0.013086
3237 | 808.7496 | 3.245 | 48.7472 | 90.789 | 64.5919 | 9.2272 | 99.3514 | 3.5047 | 13.0397 | 22.1222 | 71.3801 | 12.9977 | 137.3927 | 129.1713 | 263.6726 | 8.4663 | 51.1479 | 4.1162 | 263 | 0.52569 | 67.1253 | 238.092 | 0
3238 | 800.8168 | 2.8012 | 48.3879 | 91.8125 | 65.7543 | 8.1229 | 96.9237 | 4.0096 | 13.1463 | 22.9526 | 72.0362 | 10.9381 | 118.222 | 128.5638 | 262.0055 | 8.7133 | 51.5478 | 3.9147 | 240 | 0.46614 | 65.8427 | 247.5369 | 0
3239 | 784.5109 | 1.7715 | 48.0889 | 91.9438 | 66.2833 | 7.6203 | 90.6323 | 3.8612 | 13.1393 | 22.6116 | 72.6574 | 10.1066 | 119.3481 | 125.7344 | 261.6634 | 8.6433 | 51.8949 | 3.6942 | 207 | 0.51424 | 60.7581 | 252.4995 | 0
3240 | 792.2191 | 1.686 | 48.2278 | 92.3365 | 65.5893 | 8.2796 | 89.8496 | 3.793 | 12.8317 | 22.1142 | 72.4446 | 10.0894 | 133.7066 | 121.3441 | 260.8159 | 8.5721 | 51.8775 | 3.131 | 219 | 0.53749 | 58.743 | 261.0077 | 0
3241 | 787.5756 | 1.7827 | 48.31 | 92.9792 | 65.2647 | 8.588 | 90.4272 | 3.8324 | 12.568 | 21.8529 | 72.1307 | 11.3804 | 141.8859 | 120.4965 | 262.2468 | 10.095 | 51.9182 | 2.6906 | 186 | 0.4909 | 55.9487 | 270.4644 | 0
3242 | 780.2519 | 1.5294 | 48.1203 | 92.1984 | 65.3056 | 8.5491 | 89.5495 | 3.8032 | 12.0185 | 20.7527 | 72.139 | 10.3227 | 136.8304 | 117.0442 | 255.4879 | 9.0223 | 51.7535 | 2.5124 | 180 | 0.57181 | 51.2098 | 268.3282 | 0
3243 | 779.3041 | 1.5797 | 48.0994 | 91.3999 | 66.0648 | 7.8279 | 88.8267 | 3.5513 | 11.9404 | 20.8349 | 72.8996 | 9.4867 | 129.8397 | 108.7694 | 245.0688 | 8.3072 | 51.0977 | 2.108 | 146 | 0.51914 | 48.4484 | 255.045 | 0
3244 | 778.8844 | 1.9479 | 48.1382 | 91.4696 | 64.7546 | 9.0726 | 88.451 | 3.3738 | 12.2371 | 22.4285 | 72.3927 | 10.7266 | 125.9285 | 99.7454 | 251.6171 | 7.9983 | 50.9362 | 1.9257 | 138 | 0.63507 | 47.2847 | 242.9484 | 0
3245 | 783.7727 | 2.5213 | 47.8221 | 90.1629 | 64.2346 | 9.5666 | 87.681 | 3.4298 | 12.1267 | 24.2902 | 69.6423 | 10.7679 | 112.5935 | 92.6858 | 252.7266 | 7.8824 | 51.8408 | 1.9442 | 128 | 0.53906 | 46.1353 | 233.0948 | 0.02237
3246 | 800.6251 | 1.515 | 47.703 | 89.1914 | 65.9262 | 7.9595 | 87.5407 | 3.2184 | 11.7292 | 26.2905 | 67.5044 | 9.9297 | 102.2024 | 88.8477 | 234.3741 | 8.0999 | 51.4263 | 1.9446 | 123 | 0.64546 | 46.932 | 224.1248 | 0.083804
3247 | 810.3366 | 1.1739 | 47.8901 | 88.6805 | 65.6454 | 8.2264 | 87.5245 | 3.0386 | 11.3911 | 26.1171 | 66.8741 | 8.8081 | 95.9677 | 89.9191 | 221.1342 | 7.9871 | 49.5427 | 2.1872 | 120 | 0.56788 | 47.4402 | 223.9181 | 0.079776
3248 | 808.2558 | 1.2973 | 47.995 | 88.3583 | 65.2425 | 8.6091 | 87.1442 | 3.2516 | 11.4099 | 29.2121 | 68.2188 | 8.7257 | 95.1431 | 96.3833 | 216.9254 | 8.2275 | 48.7119 | 2.8231 | 127 | 0.62013 | 49.7641 | 228.8749 | 0.073962
3249 | 814.585 | 1.3171 | 47.5886 | 89.228 | 64.6079 | 9.2119 | 87.1045 | 3.2747 | 11.3912 | 43.8043 | 72.212 | 8.9713 | 108.8852 | 106.1752 | 219.9173 | 8.3966 | 48.7008 | 3.6771 | 161 | 0.50931 | 55.834 | 232.6091 | 0.21432
3250 | 844.3555 | 1.2205 | 47.4454 | 91.043 | 65.7429 | 8.1337 | 87.0516 | 3.2148 | 11.6632 | 53.4995 | 79.7461 | 9.5182 | 137.7625 | 115.3455 | 231.2478 | 8.3814 | 48.7643 | 6.4814 | 172 | 0.50265 | 59.0627 | 240.5012 | 0.14018
3251 | 842.4614 | 1.0987 | 47.4739 | 90.9116 | 64.879 | 8.9544 | 87.456 | 3.0694 | 12.1806 | 53.2001 | 88.8112 | 9.5323 | 149.5907 | 122.327 | 230.5917 | 8.1902 | 50.0911 | 12.0524 | 191 | 0.47702 | 60.8434 | 247.7936 | 0.20353
3252 | 826.0333 | 1.3701 | 47.4739 | 91.438 | 65.7344 | 8.1418 | 89.3998 | 2.2459 | 12.196 | 55.8483 | 94.8692 | 10.041 | 157.6174 | 128.35 | 226.2396 | 7.9974 | 53.2118 | 14.2895 | 202 | 0.47797 | 62.2805 | 246.2012 | 0.19206
3253 | 818.5655 | 1.3503 | 47.5877 | 94.2164 | 65.6291 | 8.2418 | 79.6747 | 2.4155 | 12.899 | 57.8293 | 106.681 | 10.1517 | 167.7384 | 134.9152 | 259.3783 | 8.1794 | 55.4419 | 14.4404 | 176 | 0.54354 | 62.548 | 239.1187 | 0.19684
3254 | 824.9445 | 1.763 | 47.4006 | 99.2971 | 65.2422 | 8.6094 | 76.6233 | 2.7951 | 14.1757 | 57.1087 | 120.4914 | 10.0904 | 179.659 | 144.8296 | 299.6763 | 8.6067 | 55.689 | 14.7808 | 166 | 0.5397 | 65.3562 | 232.8927 | 0.17939
3255 | 834.1238 | 2.1515 | 47.4406 | 98.8473 | 64.486 | 9.3277 | 80.7009 | 1.9167 | 14.2378 | 53.4566 | 119.0078 | 10.6986 | 184.1165 | 151.3564 | 314.1138 | 8.0925 | 56.2075 | 13.0276 | 191 | 0.66546 | 66.6305 | 229.6755 | 0.21672
3256 | 842.0133 | 2.1901 | 47.4113 | 99.5435 | 65.873 | 8.0101 | 91.3982 | 2.3051 | 14.0632 | 42.4525 | 110.6778 | 10.8154 | 183.1151 | 153.0983 | 311.0688 | 8.2092 | 57.3074 | 8.1834 | 188 | 0.55389 | 66.7934 | 224.8141 | 0.15132
3257 | 840.5736 | 1.6479 | 47.4896 | 99.4692 | 65.5382 | 8.3282 | 106.1008 | 2.8331 | 13.6568 | 29.59 | 107.5312 | 16.3106 | 181.7377 | 148.9495 | 310.3273 | 8.1496 | 55.8101 | 6.0029 | 161 | 0.61927 | 66.3641 | 218.9071 | 0.11701
3258 | 841.3409 | 1.6824 | 47.5604 | 96.3194 | 66.0872 | 7.8066 | 116.855 | 2.1114 | 13.6816 | 23.5682 | 106.561 | 19.6591 | 174.4936 | 136.5605 | 298.2967 | 8.5891 | 52.1653 | 5.6644 | 149 | 0.5471 | 66.5716 | 215.094 | 0.10065
3259 | 833.7913 | 1.5263 | 54.0679 | 93.9591 | 66.1983 | 7.7011 | 100.8741 | 2.4704 | 14.1529 | 21.7451 | 103.2031 | 14.0758 | 164.1934 | 124.2432 | 288.0172 | 8.7149 | 50.0635 | 5.0795 | 131 | 0.60604 | 64.2855 | 212.3513 | 0.029262
3260 | 805.7151 | 2.0817 | 57.1497 | 91.5267 | 66.3574 | 7.5499 | 96.4547 | 2.9615 | 14.833 | 20.0733 | 93.1976 | 9.4729 | 160.002 | 116.2504 | 273.4844 | 8.4823 | 49.4487 | 4.5253 | 141 | 0.62449 | 62.5474 | 208.8436 | 0.0067905
3261 | 794.7003 | 3.1938 | 60.9951 | 91.7853 | 66.2639 | 7.6388 | 105.554 | 2.8755 | 14.9728 | 19.705 | 83.2233 | 9.3808 | 136.8979 | 113.6829 | 256.9085 | 8.7283 | 49.374 | 3.9147 | 135 | 0.57821 | 61.6903 | 206.2895 | 0
3262 | 788.9498 | 3.1108 | 63.2511 | 95.8205 | 65.6066 | 8.2632 | 102.5368 | 2.4572 | 14.0867 | 20.8476 | 80.8528 | 10.67 | 120.6682 | 114.9946 | 243.5685 | 8.1907 | 49.8241 | 3.5547 | 126 | 0.66447 | 60.6322 | 209.6315 | 0
3263 | 773.3799 | 1.8505 | 63.2415 | 97.4529 | 66.049 | 7.8429 | 109.0854 | 2.9607 | 13.2968 | 21.5598 | 80.5282 | 11.0864 | 112.8453 | 114.2479 | 245.0225 | 8.3907 | 51.4376 | 3.476 | 117 | 0.54832 | 58.8026 | 214.2605 | 0
3264 | 760.876 | 1.2258 | 63.4331 | 94.8137 | 66.2593 | 7.6432 | 83.9732 | 3.4769 | 13.028 | 21.084 | 79.512 | 11.1131 | 99.4659 | 109.3772 | 250.0906 | 8.8925 | 55.8132 | 3.4592 | 121 | 0.626 | 59.3389 | 216.4055 | 0
3265 | 743.6427 | 1.3522 | 63.5871 | 93.6272 | 65.5988 | 8.2706 | 75.8836 | 3.785 | 12.8277 | 20.5384 | 78.9632 | 11.0944 | 90.6024 | 102.6548 | 244.4252 | 8.8677 | 60.1807 | 3.3068 | 110 | 0.52467 | 57.9813 | 219.3797 | 0
3266 | 733.4141 | 1.3343 | 63.6307 | 93.206 | 65.3304 | 8.5256 | 85.4873 | 4.0087 | 12.4805 | 20.7302 | 78.9088 | 11.0193 | 89.7764 | 97.8799 | 234.2207 | 9.1475 | 61.3593 | 3.2242 | 125 | 0.58683 | 55.4362 | 219.7827 | 0
3267 | 735.726 | 1.2289 | 63.3496 | 92.4425 | 65.2981 | 8.5562 | 88.942 | 4.0047 | 12.3407 | 22.3791 | 79.391 | 11.0194 | 92.9758 | 95.1493 | 224.2921 | 9.0105 | 61.0034 | 3.1589 | 103 | 0.49033 | 58.4367 | 220.5312 | 0
3268 | 737.3545 | 1.8685 | 55.158 | 89.5839 | 65.9732 | 7.9149 | 88.1328 | 3.6123 | 12.5623 | 23.3918 | 77.9796 | 9.7305 | 92.437 | 90.855 | 224.8217 | 8.0265 | 59.6723 | 2.5892 | 102 | 0.58527 | 57.15 | 237.5156 | 0
3269 | 756.8154 | 1.8622 | 51.3502 | 89.3651 | 65.5577 | 8.3096 | 87.8719 | 3.1068 | 12.3442 | 24.0682 | 74.4493 | 9.3198 | 89.374 | 95.2068 | 220.4971 | 7.9836 | 57.8641 | 2.3171 | 97 | 0.50989 | 56.6372 | 258.632 | 0.035678
3270 | 809.6706 | 2.19 | 79.6188 | 91.7649 | 62.2966 | 11.4077 | 84.9653 | 2.5694 | 12.0786 | 33.5948 | 84.8037 | 14.9124 | 98.5426 | 130.8363 | 231.3725 | 11.7414 | 57.6509 | 2.6808 | 156 | 0.80386 | 100.3719 | 296.1156 | 0.088337
3271 | 887.8017 | 4.3995 | 92.4392 | 101.5168 | 59.1361 | 14.4101 | 98.5454 | 3.6622 | 13.8022 | 55.22 | 116.9269 | 27.9637 | 164.677 | 193.6543 | 303.7634 | 24.0932 | 61.3887 | 8.8273 | 271 | 2.4443 | 144.9125 | 361.6696 | 0.19675
3272 | 972.465 | 4.5958 | 92.4392 | 119.5768 | 58.2794 | 15.224 | 98.7005 | 5.0048 | 18.9563 | 68.5126 | 154.4008 | 34.4038 | 249.6416 | 255.1983 | 405.3099 | 33.1902 | 68.9259 | 15.7546 | 276 | 4.4418 | 171.9036 | 442.4206 | 0.28032
3273 | 1041.62 | 4.3456 | 112.257 | 134.163 | 60.5558 | 13.0614 | 106.6439 | 4.0943 | 23.6857 | 68.0937 | 182.578 | 33.4318 | 374.4616 | 299.9046 | 494.7255 | 37.4358 | 79.012 | 17.9152 | 338 | 4.59 | 199.6492 | 509.1338 | 0.33932
3274 | 1070.7077 | 4.3311 | 119.9593 | 142.0938 | 61.3541 | 12.303 | 111.942 | 5.7062 | 23.3951 | 69.0719 | 197.3371 | 34.0955 | 446.3376 | 328.4959 | 554.7622 | 40.2802 | 99.4713 | 18.109 | 337 | 4.3814 | 206.9694 | 543.4842 | 0.30203
3275 | 1111.1862 | 4.314 | 119.2959 | 144.5082 | 61.3019 | 12.3527 | 136.9898 | 5.5991 | 20.3051 | 67.2421 | 200.5561 | 37.9993 | 456.814 | 342.4549 | 587.6217 | 38.9476 | 118.7056 | 18.0213 | 350 | 5.0179 | 207.0851 | 559.2602 | 0.281
3276 | 1118.6476 | 4.8827 | 115.2608 | 139.7904 | 59.912 | 13.6731 | 156.01 | 4.6587 | 20.0519 | 63.6206 | 199.2314 | 40.2682 | 467.3018 | 345.7097 | 598.6232 | 39.5703 | 118.7615 | 18.7839 | 364 | 6.4714 | 204.2233 | 569.2295 | 0.25153
3277 | 1119.5077 | 10.3088 | 113.415 | 141.9464 | 59.3593 | 14.1981 | 150.0075 | 4.2329 | 20.6234 | 63.3131 | 203.9721 | 41.9914 | 482.8963 | 353.985 | 604.8413 | 40.9254 | 114.1127 | 19.578 | 325 | 5.8925 | 213.4804 | 572.9756 | 0.2626
3278 | 1120.5253 | 13.1083 | 113.403 | 147.2569 | 59.1366 | 14.4097 | 152.8815 | 4.7549 | 23.2808 | 63.9381 | 211.6023 | 41.2656 | 484.2192 | 362.8506 | 611.3669 | 41.3519 | 115.604 | 19.6003 | 302 | 7.2447 | 218.4756 | 568.11 | 0.24013
3279 | 1098.8563 | 8.3797 | 113.403 | 147.9041 | 56.3299 | 17.076 | 150.856 | 3.9489 | 23.8482 | 62.6465 | 212.8382 | 36.3234 | 475.5802 | 359.4021 | 598.1655 | 40.0307 | 116.8302 | 19.9621 | 336 | 5.424 | 208.0571 | 564.176 | 0.1942
3280 | 1088.9774 | 4.322 | 113.6929 | 144.4689 | 60.497 | 13.1173 | 131.6463 | 4.0258 | 21.1644 | 59.2711 | 208.9709 | 31.065 | 475.7931 | 340.9634 | 551.4729 | 31.6683 | 112.3009 | 20.1003 | 288 | 3.5752 | 195.9277 | 533.2126 | 0.15016
3281 | 1043.0424 | 3.5199 | 106.3438 | 122.6899 | 66.0668 | 7.826 | 112.9041 | 3.5239 | 20.5413 | 52.4483 | 194.0531 | 25.6849 | 452.0274 | 291.1762 | 475.2747 | 16.8531 | 101.938 | 19.2648 | 233 | 2.5153 | 174.6011 | 466.3066 | 0.10889
3282 | 992.3896 | 2.9872 | 93.2664 | 102.211 | 66.5368 | 7.3795 | 110.1632 | 2.2061 | 19.4171 | 43.4166 | 158.5559 | 20.3883 | 399.5995 | 229.668 | 403.4689 | 9.7366 | 91.17 | 18.4385 | 249 | 2.2648 | 155.3712 | 399.3619 | 0.065562
3283 | 955.4783 | 2.0712 | 88.7311 | 95.7943 | 66.3001 | 7.6044 | 98.2871 | 2.3609 | 18.3089 | 40.1148 | 122.936 | 10.6043 | 371.888 | 192.1017 | 355.3402 | 8.3657 | 81.6993 | 15.6859 | 220 | 2.0985 | 136.5929 | 349.6899 | 0.079611
3284 | 928.676 | 2.2355 | 52.9868 | 89.161 | 67.0148 | 6.9254 | 73.2869 | 2.9186 | 17.6705 | 34.8452 | 109.3784 | 6.7528 | 316.4838 | 173.611 | 318.5268 | 7.8091 | 69.6667 | 10.1428 | 197 | 2.1843 | 124.718 | 318.6349 | 0.0080918
3285 | 892.3658 | 3.4759 | 36.1807 | 86.7067 | 66.5493 | 7.3676 | 72.1257 | 3.2752 | 16.3861 | 27.5841 | 107.9272 | 7.0603 | 289.7785 | 154.3412 | 294.0752 | 7.7815 | 59.0657 | 7.2133 | 197 | 2.0985 | 119.8852 | 304.9919 | 0
3286 | 848.6878 | 3.2049 | 36.4145 | 88.2627 | 67.0787 | 6.8647 | 85.7216 | 3.3369 | 13.8134 | 26.2338 | 102.2015 | 8.1722 | 278.5561 | 135.8997 | 273.2811 | 8.1308 | 55.3083 | 6.137 | 163 | 2.1165 | 108.7742 | 301.6539 | 0
3287 | 827.6523 | 2.0038 | 36.5319 | 89.4402 | 66.579 | 7.3394 | 90.1877 | 2.6983 | 13.1397 | 25.5683 | 92.5122 | 8.3074 | 255.51 | 125.3113 | 243.2214 | 8.0663 | 55.1173 | 5.4128 | 143 | 2.0469 | 79.8207 | 301.692 | 0
3288 | 827.3497 | 1.4494 | 36.4197 | 88.9813 | 67.053 | 6.8891 | 90.0238 | 3.1272 | 12.7857 | 22.8282 | 87.2727 | 8.2391 | 240.1273 | 120.7022 | 220.9067 | 8.1374 | 55.679 | 4.8663 | 123 | 2.0867 | 64.6509 | 297.9259 | 0
3289 | 820.1124 | 1.6098 | 36.6939 | 89.1722 | 66.5512 | 7.3658 | 90.0814 | 3.6265 | 12.8123 | 20.9999 | 85.962 | 8.3196 | 220.7682 | 114.4277 | 220.3044 | 8.243 | 56.4777 | 4.1316 | 116 | 2.1689 | 62.7007 | 293.7743 | 0
3290 | 808.8031 | 1.5716 | 36.6775 | 88.4258 | 66.9974 | 6.9419 | 90.6624 | 3.6477 | 13.2712 | 21.1474 | 84.902 | 8.3531 | 207.8187 | 107.0169 | 222.4612 | 8.1891 | 56.5274 | 3.0662 | 132 | 2.0694 | 61.7414 | 291.0153 | 0
3291 | 807.2466 | 1.27 | 36.5207 | 88.6499 | 66.5889 | 7.33 | 90.6479 | 3.6439 | 12.8639 | 22.2653 | 83.9594 | 8.3654 | 207.6891 | 104.7023 | 220.3798 | 8.3636 | 56.0231 | 2.516 | 112 | 2.1521 | 59.506 | 288.7451 | 0
3292 | 810.7712 | 1.6241 | 30.8769 | 86.9503 | 67.0292 | 6.9117 | 90.1046 | 3.3888 | 12.7907 | 27.0339 | 81.637 | 7.1622 | 197.8618 | 99.3284 | 223.1299 | 8.15 | 56.1393 | 2.3505 | 108 | 2.0576 | 58.3145 | 295.1653 | 0
3293 | 828.6159 | 1.7271 | 38.4965 | 87.3789 | 66.5424 | 7.3742 | 90.0386 | 2.4565 | 12.4562 | 33.7762 | 78.053 | 6.9863 | 201.2953 | 96.9115 | 225.1263 | 8.0028 | 57.0989 | 2.1411 | 109 | 2.1044 | 64.7194 | 312.9803 | 0.028317
3294 | 865.9057 | 4.039 | 66.2384 | 90.261 | 63.4952 | 10.2691 | 84.3113 | 2.6334 | 12.0931 | 45.8797 | 83.2069 | 15.1598 | 218.2708 | 119.4133 | 227.8529 | 11.5112 | 56.8779 | 2.0732 | 193 | 2.2629 | 96.6232 | 350.399 | 0.077116
3295 | 960.392 | 9.1773 | 76.7625 | 95.651 | 60.7135 | 12.9117 | 86.8196 | 3.3454 | 12.8126 | 66.1338 | 114.2342 | 27.3501 | 247.588 | 173.8761 | 284.7043 | 25.3215 | 58.7401 | 8.3994 | 279 | 6.1132 | 139.9961 | 411.2003 | 0.17292
3296 | 1006.5793 | 9.7647 | 99.1338 | 115.8441 | 61.1689 | 12.479 | 102.2397 | 3.2412 | 15.6884 | 78.4961 | 158.9923 | 29.8975 | 311.4464 | 246.6418 | 397.6108 | 33.5603 | 67.0617 | 14.4128 | 306 | 7.499 | 180.9789 | 478.7916 | 0.2591
3297 | 1063.9106 | 5.9193 | 113.2891 | 129.303 | 61.1766 | 12.4717 | 124.1493 | 4.9432 | 17.4969 | 83.0889 | 185.5414 | 30.5521 | 385.2988 | 309.7948 | 501.1154 | 36.569 | 82.7652 | 17.0256 | 338 | 7.7319 | 212.7279 | 531.4069 | 0.34255
3298 | 1123.4707 | 4.4013 | 117.1929 | 137.5068 | 60.7024 | 12.9222 | 139.034 | 4.8588 | 18.1812 | 88.2604 | 195.4131 | 32.0012 | 441.8539 | 342.2591 | 551.5277 | 39.5407 | 99.9472 | 18.6793 | 380 | 7.7067 | 217.4056 | 559.2682 | 0.33169
3299 | 1134.1163 | 4.5011 | 121.9531 | 138.2913 | 57.3085 | 16.1464 | 146.5243 | 4.4757 | 19.2037 | 90.8348 | 198.663 | 32.5866 | 459.5908 | 352.1658 | 574.3419 | 39.4304 | 107.8729 | 18.8717 | 346 | 8.629 | 213.061 | 569.2467 | 0.32087
3300 | 1118.8751 | 4.4936 | 122.574 | 136.9769 | 58.4055 | 15.1042 | 146.2401 | 5.2388 | 19.221 | 85.8337 | 196.8945 | 32.3089 | 478.7901 | 350.6019 | 579.976 | 39.9799 | 108.2304 | 18.8463 | 334 | 7.6031 | 207.7362 | 575.4505 | 0.27579
3301 | 1110.5993 | 8.1836 | 122.2027 | 139.2879 | 59.3327 | 14.2234 | 140.5512 | 4.4571 | 18.5922 | 83.0529 | 200.2849 | 35.6041 | 490.9268 | 353.5499 | 565.5372 | 42.0957 | 109.1391 | 19.2417 | 293 | 6.1064 | 212.6743 | 570.4607 | 0.29122
3302 | 1119.6159 | 7.3613 | 122.5267 | 143.6308 | 59.2027 | 14.3469 | 136.5381 | 3.6208 | 20.184 | 88.2023 | 205.3381 | 36.6428 | 502.5434 | 362.5091 | 556.3355 | 40.7274 | 110.8646 | 19.3933 | 276 | 7.3707 | 214.958 | 546.9095 | 0.28617
3303 | 1117.5364 | 4.9666 | 120.7973 | 143.2768 | 62.3133 | 11.3918 | 139.9279 | 4.3432 | 20.2906 | 89.5628 | 204.6934 | 37.0755 | 507.8698 | 359.0493 | 555.5016 | 38.8259 | 110.2882 | 19.3716 | 298 | 5.8361 | 209.9385 | 527.8107 | 0.27435
3304 | 1099.5236 | 4.2011 | 114.6499 | 134.0388 | 65.5706 | 8.2974 | 142.9926 | 3.6105 | 17.9454 | 86.407 | 202.4955 | 36.0337 | 502.6944 | 336.9344 | 519.8151 | 31.1178 | 108.3633 | 19.0692 | 274 | 4.4348 | 193.5512 | 497.0447 | 0.17067
3305 | 1047.8189 | 3.711 | 105.529 | 116.4963 | 67.8226 | 6.158 | 133.2472 | 2.5127 | 16.8417 | 77.8937 | 190.0801 | 32.4573 | 462.597 | 287.0552 | 437.0211 | 16.2355 | 102.6011 | 17.7609 | 245 | 4.0321 | 162.9738 | 435.0699 | 0.20954
3306 | 1002.9746 | 2.6613 | 102.3375 | 101.2738 | 68.2487 | 5.7532 | 121.9117 | 1.6993 | 16.6065 | 64.1074 | 158.3722 | 24.7106 | 433.0345 | 224.6676 | 363.0869 | 9.7093 | 91.7317 | 15.6237 | 221 | 3.0903 | 146.8554 | 369.9263 | 0.10566
3307 | 962.7112 | 2.0757 | 86.3761 | 95.9809 | 67.6582 | 6.3142 | 113.4653 | 2.2109 | 16.9654 | 47.4846 | 126.7091 | 12.1655 | 406.0954 | 185.7611 | 336.5212 | 8.912 | 78.8948 | 12.5163 | 185 | 2.8199 | 131.1131 | 326.1254 | 0.055318
3308 | 917.3552 | 3.1495 | 53.8695 | 91.2369 | 67.9736 | 6.0145 | 105.3059 | 2.8056 | 16.4394 | 33.327 | 114.0868 | 7.2402 | 356.9366 | 166.7188 | 316.8942 | 8.4751 | 67.0178 | 7.3491 | 178 | 2.7878 | 121.2598 | 302.0668 | 0.0080923
3309 | 884.6258 | 3.5087 | 49.9643 | 88.9766 | 68.2643 | 5.7384 | 92.6197 | 3.0181 | 15.1809 | 27.2103 | 111.7867 | 7.6146 | 319.6298 | 154.2749 | 280.2985 | 8.6268 | 59.7153 | 4.4701 | 175 | 2.9336 | 116.6102 | 293.5872 | 0
3310 | 867.5759 | 2.6862 | 53.3812 | 93.2531 | 68.3802 | 5.6283 | 91.4739 | 2.344 | 13.9155 | 26.4577 | 104.5018 | 8.8772 | 286.5964 | 144.7291 | 259.5512 | 8.8553 | 56.7166 | 4.0523 | 169 | 2.8407 | 107.1864 | 293.6463 | 0
3311 | 834.4973 | 1.7709 | 52.0759 | 94.8611 | 68.2795 | 5.7239 | 86.4638 | 2.8298 | 13.4587 | 26.3619 | 92.9274 | 9.2768 | 269.6428 | 133.3803 | 250.0427 | 8.8368 | 55.4074 | 3.9398 | 144 | 2.8904 | 79.7029 | 289.7521 | 0
3312 | 825.3751 | 1.2876 | 51.1248 | 93.5137 | 67.5894 | 6.3796 | 103.2348 | 3.3517 | 13.481 | 25.2925 | 87.0734 | 8.8424 | 252.1074 | 125.0637 | 244.5426 | 8.9242 | 54.8488 | 3.8616 | 124 | 2.8391 | 63.0247 | 281.6251 | 0
3313 | 814.2676 | 1.1971 | 51.5335 | 90.2396 | 68.0632 | 5.9294 | 103.7337 | 2.9953 | 13.3917 | 24.9723 | 85.8622 | 8.6379 | 221.1906 | 122.6516 | 240.6757 | 8.9639 | 54.8146 | 3.7972 | 115 | 2.9146 | 58.6662 | 278.5232 | 0
3314 | 792.3746 | 1.3855 | 51.8392 | 89.3097 | 68.3042 | 5.7005 | 93.5586 | 2.4795 | 12.6888 | 25.1405 | 85.1105 | 8.6039 | 212.7255 | 119.1135 | 231.7698 | 8.9119 | 54.7972 | 3.0651 | 131 | 2.8199 | 56.5584 | 280.3936 | 0
3315 | 803.2633 | 1.332 | 51.628 | 90.1523 | 68.2763 | 5.7269 | 90.044 | 3.1385 | 12.3115 | 26.9213 | 84.7465 | 8.5876 | 210.7561 | 113.6265 | 221.5269 | 8.9016 | 54.6962 | 2.6817 | 111 | 2.8467 | 54.065 | 281.4717 | 0
3316 | 804.2139 | 2.0228 | 51.43 | 88.4433 | 68.2678 | 5.735 | 89.5405 | 3.4064 | 12.2721 | 33.3308 | 83.1422 | 7.905 | 204.6099 | 108.98 | 210.2039 | 8.6318 | 55.1649 | 2.6347 | 110 | 2.7946 | 52.9429 | 284.3789 | 0
3317 | 809.3521 | 2.5072 | 56.3397 | 85.978 | 68.3395 | 5.6669 | 88.3506 | 3.0423 | 12.2375 | 39.6828 | 79.5761 | 7.3716 | 199.0839 | 108.1468 | 206.703 | 8.3524 | 56.0977 | 2.4493 | 111 | 2.7934 | 57.4945 | 300.1942 | 0.017588
3318 | 850.2691 | 2.8221 | 71.8673 | 86.4738 | 64.6021 | 9.2175 | 81.6233 | 1.8974 | 12.1809 | 47.8716 | 82.5964 | 12.1005 | 208.0919 | 135.1649 | 234.0685 | 11.5986 | 55.6703 | 2.3671 | 233 | 3.0495 | 93.5884 | 344.1618 | 0.046065
3319 | 897.7646 | 9.407 | 77.9202 | 93.0674 | 62.5878 | 11.131 | 95.8339 | 2.8041 | 13.3718 | 59.8602 | 111.1452 | 24.6317 | 253.669 | 194.8388 | 292.7969 | 24.7461 | 57.2757 | 8.1311 | 266 | 5.7834 | 140.7268 | 402.2617 | 0.086338
3320 | 976.254 | 11.4069 | 106.9241 | 114.1131 | 60.8329 | 12.7982 | 126.1645 | 3.7595 | 16.3539 | 66.0956 | 157.9 | 33.9355 | 312.5428 | 257.1618 | 379.8821 | 34.0144 | 64.8442 | 13.902 | 325 | 8.2412 | 172.4795 | 456.6495 | 0.1931
3321 | 1081.7364 | 10.2314 | 122.9393 | 130.5394 | 59.4664 | 14.0964 | 136.3438 | 4.5094 | 19.5214 | 70.9754 | 189.4655 | 37.1029 | 380.693 | 299.7179 | 474.6087 | 39.2118 | 77.9716 | 16.6056 | 374 | 7.3325 | 207.676 | 505.6729 | 0.22673
3322 | 1139.8897 | 7.5306 | 123.9161 | 133.6934 | 59.361 | 14.1965 | 139.724 | 4.3017 | 18.8737 | 73.143 | 203.0794 | 38.1109 | 414.7285 | 324.6408 | 544.4427 | 41.8916 | 95.9678 | 17.5623 | 372 | 7.9345 | 223.849 | 536.5983 | 0.25351
3323 | 1150.9422 | 4.8027 | 124.4493 | 135.2207 | 59.2867 | 14.2671 | 140.174 | 4.1583 | 19.2817 | 67.8854 | 205.3125 | 37.5293 | 443.7 | 340.2253 | 563.5075 | 40.784 | 107.495 | 17.6723 | 350 | 8.3686 | 219.8451 | 546.9763 | 0.22406
3324 | 1132.6232 | 4.105 | 122.6774 | 136.8147 | 59.2284 | 14.3225 | 139.099 | 4.5174 | 19.6396 | 64.5318 | 200.0535 | 36.4069 | 465.9388 | 346.8673 | 554.2697 | 40.2515 | 107.1951 | 17.804 | 373 | 7.9508 | 209.1142 | 549.7067 | 0.18888
3325 | 1130.522 | 3.8838 | 121.9975 | 135.4327 | 59.365 | 14.1927 | 143.2714 | 3.9455 | 18.5298 | 70.1797 | 200.8659 | 36.6219 | 475.1216 | 349.6802 | 556.5186 | 41.1469 | 105.3648 | 18.4387 | 316 | 7.9113 | 214.9553 | 547.9731 | 0.21559
3326 | 1127.6235 | 3.8906 | 124.5088 | 142.3179 | 58.028 | 15.4629 | 140.901 | 3.7445 | 19.532 | 75.6852 | 206.1729 | 37.746 | 494.9506 | 351.4502 | 570.8015 | 40.547 | 105.1186 | 18.7899 | 283 | 8.6448 | 220.59 | 541.4646 | 0.20086
3327 | 1118.2233 | 4.8484 | 118.5047 | 143.2877 | 59.4567 | 14.1056 | 141.6994 | 4.4135 | 19.127 | 75.5849 | 204.3958 | 39.3994 | 512.9502 | 343.0187 | 568.3869 | 39.1079 | 103.8313 | 18.5231 | 301 | 6.9538 | 220.9944 | 536.069 | 0.18576
3328 | 1095.3157 | 4.4443 | 115.2507 | 137.4851 | 64.7488 | 9.0781 | 131.3096 | 4.299 | 17.357 | 72.7043 | 195.0512 | 38.92 | 494.2491 | 325.0311 | 543.2474 | 32.3195 | 100.727 | 17.7468 | 273 | 4.793 | 201.9461 | 506.5824 | 0.1498
3329 | 1028.1907 | 3.2526 | 115.2507 | 120.0161 | 67.7329 | 6.2432 | 130.2261 | 3.5424 | 16.2275 | 57.5629 | 180.4592 | 36.6957 | 458.853 | 279.8618 | 473.9227 | 18.1534 | 94.6029 | 16.544 | 239 | 4.0478 | 167.4703 | 438.657 | 0.12723
3330 | 972.8176 | 2.1706 | 110.4103 | 101.6579 | 67.5453 | 6.4215 | 123.4275 | 3.466 | 14.924 | 37.6764 | 150.3277 | 31.0266 | 432.0124 | 212.587 | 386.6566 | 10.4222 | 87.5228 | 14.9131 | 228 | 3.3548 | 150.4128 | 372.1939 | 0.13221
3331 | 949.6103 | 1.6442 | 89.6764 | 95.0081 | 66.6097 | 7.3103 | 103.0862 | 2.592 | 13.7603 | 26.184 | 120.3626 | 20.4365 | 383.0387 | 165.8788 | 316.0605 | 9.1718 | 78.1651 | 11.8284 | 200 | 2.8239 | 135.9556 | 326.7039 | 0.095284
3332 | 903.6791 | 2.1855 | 58.7138 | 90.0563 | 67.7605 | 6.217 | 84.0673 | 2.3831 | 12.6778 | 21.1427 | 107.4055 | 15.6085 | 338.3974 | 147.6489 | 278.3359 | 8.5029 | 66.2554 | 6.2992 | 188 | 2.6381 | 126.6144 | 301.7259 | 0.046665
3333 | 872.4197 | 3.5807 | 48.3247 | 88.0451 | 67.586 | 6.3828 | 69.8204 | 3.0259 | 12.4772 | 19.6217 | 97.6311 | 10.3498 | 302.7297 | 135.2535 | 265.0898 | 8.4562 | 58.6597 | 3.6852 | 180 | 2.5225 | 122.8637 | 288.8068 | 0
3334 | 838.7396 | 2.9806 | 53.2825 | 90.0366 | 68.0222 | 5.9684 | 82.2812 | 3.4038 | 12.6388 | 19.9334 | 86.1639 | 8.2858 | 268.2935 | 122.8259 | 261.0844 | 8.7144 | 56.0163 | 3.4667 | 152 | 2.5439 | 118.4503 | 281.8811 | 0
3335 | 809.637 | 1.7183 | 54.6437 | 89.867 | 68.2491 | 5.7528 | 92.4781 | 2.8906 | 12.7073 | 20.6003 | 78.1613 | 7.9263 | 242.5058 | 115.72 | 240.9519 | 8.901 | 54.7688 | 3.6089 | 164 | 2.5995 | 92.6135 | 288.9231 | 0
3336 | 803.4057 | 1.2567 | 53.791 | 89.298 | 68.3412 | 5.6654 | 91.8545 | 2.5458 | 12.8117 | 21.4699 | 75.4199 | 7.5125 | 231.5117 | 109.6559 | 228.0269 | 8.8466 | 53.8577 | 3.5902 | 138 | 2.5265 | 78.17 | 292.3636 | 0
3337 | 790.4809 | 1.3832 | 53.8038 | 89.4185 | 68.3532 | 5.6539 | 91.8273 | 3.0305 | 12.7658 | 21.9125 | 75.7735 | 7.5514 | 219.8495 | 103.7035 | 228.6561 | 8.7783 | 53.6216 | 3.5186 | 126 | 2.6305 | 70.7186 | 283.9734 | 0
3338 | 778.2609 | 1.3562 | 53.9746 | 89.1386 | 68.2914 | 5.7126 | 91.7476 | 3.3355 | 12.7749 | 21.4827 | 76.6203 | 7.4367 | 207.4167 | 100.2495 | 228.0401 | 8.8611 | 53.5412 | 3.5538 | 137 | 2.5582 | 63.2195 | 277.2321 | 0
3339 | 789.1503 | 1.2759 | 53.8822 | 89.169 | 67.552 | 6.415 | 71.0272 | 3.4382 | 12.7989 | 22.9372 | 76.9221 | 7.4115 | 203.4794 | 98.6368 | 226.5659 | 8.8594 | 53.3879 | 3.5587 | 112 | 2.6697 | 59.8047 | 276.9505 | 0
3340 | 790.5779 | 1.6514 | 53.8342 | 88.5863 | 68.7143 | 5.3109 | 60.1574 | 2.4908 | 12.8565 | 28.9755 | 75.2756 | 6.9164 | 204.6095 | 95.2095 | 222.034 | 8.6888 | 54.1623 | 3.4157 | 114 | 2.6028 | 58.0414 | 282.838 | 0
3341 | 806.2768 | 2.8115 | 54.6994 | 87.9543 | 67.8311 | 6.1499 | 58.9924 | 2.5466 | 12.5877 | 35.4892 | 72.1014 | 6.8385 | 204.2577 | 99.872 | 217.4169 | 8.4352 | 55.6734 | 2.7774 | 119 | 2.6807 | 61.6834 | 292.5916 | 0.041832
3342 | 846.9234 | 2.6393 | 57.1741 | 92.4727 | 64.3548 | 9.4524 | 70.9276 | 2.8844 | 12.205 | 45.9222 | 78.1258 | 15.1951 | 212.0319 | 135.3584 | 229.3251 | 12.2189 | 55.4943 | 3.3063 | 245 | 2.6387 | 100.1403 | 326.6028 | 0.058562
3343 | 900.176 | 2.8513 | 81.658 | 98.0089 | 60.5375 | 13.0788 | 100.3704 | 2.9755 | 12.3924 | 60.5444 | 108.4411 | 26.7482 | 274.9258 | 192.8084 | 292.636 | 25.1036 | 56.9728 | 9.7415 | 271 | 6.5205 | 147.423 | 396.7037 | 0.098129
3344 | 989.5522 | 3.5325 | 107.1983 | 112.2401 | 60.0202 | 13.5703 | 126.1581 | 4.6763 | 15.3221 | 69.8489 | 153.1421 | 33.4979 | 308.5837 | 249.514 | 397.8788 | 33.4295 | 64.2113 | 15.5457 | 340 | 8.0082 | 179.2955 | 471.5452 | 0.21947
3345 | 1100.9802 | 5.094 | 113.1927 | 127.6091 | 60.9915 | 12.6476 | 139.3999 | 4.8267 | 18.3762 | 74.6128 | 183.3153 | 37.4615 | 361.9999 | 297.0353 | 484.9146 | 37.8084 | 73.117 | 16.6982 | 368 | 8.2776 | 208.4927 | 519.5527 | 0.18302
3346 | 1150.4782 | 8.6169 | 112.3685 | 142.7102 | 59.8621 | 13.7205 | 143.7192 | 4.3542 | 18.7243 | 81.6483 | 196.2574 | 39.2734 | 433.0828 | 330.6974 | 531.8105 | 39.7086 | 85.3222 | 16.9547 | 372 | 8.3467 | 223.3993 | 532.9808 | 0.21224
3347 | 1151.8775 | 9.9645 | 112.8372 | 143.7212 | 59.3711 | 14.1869 | 146.467 | 4.7184 | 16.3899 | 87.6897 | 202.2835 | 37.6837 | 484.7672 | 344.6397 | 562.761 | 39.9582 | 99.3329 | 16.9615 | 357 | 7.8601 | 217.9514 | 532.1324 | 0.20307
3348 | 1128.4002 | 6.4073 | 113.3285 | 141.9392 | 60.7735 | 12.8546 | 149.7809 | 4.6051 | 15.9043 | 83.6037 | 204.7927 | 35.2479 | 517.5775 | 342.7888 | 577.803 | 40.437 | 107.7452 | 17.0483 | 360 | 7.6322 | 209.3281 | 535.6376 | 0.25953
3349 | 1140.4612 | 4.0595 | 114.5819 | 146.2733 | 58.8878 | 14.6461 | 145.0005 | 4.3032 | 15.9062 | 83.7699 | 206.0798 | 38.534 | 534.4387 | 343.6057 | 575.8102 | 41.4138 | 110.9095 | 17.8787 | 328 | 7.4644 | 212.1668 | 538.408 | 0.26543
3350 | 1132.9526 | 3.7077 | 115.014 | 150.0311 | 59.169 | 14.3789 | 136.1824 | 4.1397 | 17.2925 | 90.0647 | 205.1813 | 40.6702 | 543.2148 | 351.2553 | 571.7344 | 39.2388 | 111.2883 | 18.8165 | 305 | 7.3432 | 211.9456 | 542.274 | 0.24291
3351 | 1110.7954 | 4.7405 | 113.3097 | 148.8872 | 60.0782 | 13.5151 | 143.102 | 4.1199 | 19.4173 | 87.4363 | 204.2081 | 39.4761 | 536.8939 | 350.4445 | 568.3608 | 36.7364 | 110.529 | 18.5808 | 292 | 6.7403 | 210.6688 | 540.3473 | 0.26241
3352 | 1099.1747 | 4.5499 | 103.9562 | 136.2873 | 62.3546 | 11.3526 | 136.5491 | 3.835 | 18.1877 | 77.3147 | 202.4755 | 35.5501 | 531.6421 | 334.9377 | 535.9234 | 30.5773 | 107.4602 | 17.8858 | 289 | 6.2056 | 198.043 | 500.3378 | 0.2298
3353 | 1066.4309 | 3.5989 | 100.0027 | 120.2556 | 65.5358 | 8.3304 | 123.243 | 2.7708 | 16.4157 | 62.7209 | 187.0987 | 31.986 | 502.7718 | 286.0039 | 463.6012 | 17.8643 | 100.5715 | 16.1341 | 253 | 5.3885 | 172.347 | 429.9741 | 0.26071
3354 | 1011.0226 | 2.8776 | 96.9226 | 106.1026 | 67.8302 | 6.1508 | 108.2489 | 2.6601 | 16.9446 | 46.8743 | 150.2549 | 27.131 | 458.5089 | 213.5508 | 375.9663 | 10.662 | 92.807 | 14.8758 | 266 | 4.7064 | 157.5768 | 359.2607 | 0.17502
3355 | 966.1038 | 2.2633 | 66.5743 | 100.8941 | 68.2746 | 5.7286 | 99.3096 | 2.1257 | 17.7534 | 37.344 | 115.8348 | 22.1488 | 400.9765 | 158.1179 | 322.5231 | 9.5851 | 87.0316 | 12.2712 | 246 | 4.5988 | 138.0436 | 304.5855 | 0.14166
3356 | 930.3311 | 2.8087 | 52.9963 | 97.5415 | 69.0303 | 5.0107 | 85.5223 | 2.1835 | 17.0151 | 37.319 | 103.4276 | 21.1901 | 360.337 | 128.8233 | 283.6629 | 9.3568 | 79.0555 | 7.1711 | 219 | 4.7382 | 122.2911 | 274.4821 | 0.013692
3357 | 907.5799 | 3.5019 | 48.4482 | 98.7294 | 68.5476 | 5.4692 | 72.8687 | 2.0834 | 15.6963 | 40.6162 | 101.3368 | 14.7614 | 329.7465 | 117.7616 | 264.2407 | 9.1392 | 66.6601 | 4.7118 | 209 | 4.5971 | 116.8715 | 265.7432 | 0
3358 | 882.1884 | 7.4816 | 47.0326 | 103.7898 | 68.2919 | 5.7121 | 65.4183 | 2.6037 | 14.6077 | 42.0324 | 94.4218 | 12.3157 | 302.5114 | 115.5351 | 259.4046 | 9.1089 | 57.7167 | 4.1847 | 156 | 4.5409 | 108.3037 | 265.6438 | 0
3359 | 862.9177 | 9.1843 | 47.3452 | 105.6162 | 67.5821 | 6.3865 | 66.8869 | 2.2653 | 13.4668 | 42.2911 | 83.8449 | 9.7282 | 281.3087 | 114.865 | 250.0205 | 9.3906 | 55.5371 | 3.7636 | 134 | 4.666 | 83.2555 | 261.5776 | 0
3360 | 846.2555 | 8.3191 | 47.396 | 105.469 | 68.037 | 5.9543 | 61.7437 | 2.5712 | 12.3383 | 41.9226 | 79.0796 | 8.0783 | 261.0715 | 108.9287 | 253.6092 | 9.2679 | 55.5663 | 3.4259 | 130 | 4.6038 | 70.6971 | 253.3463 | 0
3361 | 834.7437 | 3.747 | 47.0517 | 105.0962 | 69.032 | 5.0091 | 65.2744 | 2.2383 | 12.359 | 39.2885 | 78.9962 | 7.4281 | 244.1356 | 105.8161 | 254.3571 | 9.2819 | 55.7543 | 2.8537 | 127 | 4.5892 | 70.0342 | 250.2563 | 0
3362 | 823.1218 | 1.4261 | 46.7499 | 104.8619 | 67.8569 | 6.1254 | 63.0315 | 2.8137 | 12.2703 | 35.1604 | 79.3172 | 7.2786 | 236.6114 | 110.2794 | 244.6121 | 9.0363 | 55.9093 | 2.2985 | 141 | 4.7162 | 61.3166 | 254.5721 | 0
3363 | 829.4571 | 1.6288 | 46.6931 | 104.986 | 68.7991 | 5.2303 | 65.558 | 3.0513 | 12.0202 | 34.5251 | 79.6145 | 7.4967 | 227.8755 | 106.8464 | 236.3478 | 9.4193 | 55.749 | 2.1411 | 120 | 4.6328 | 57.8595 | 257.1573 | 0
3364 | 843.6722 | 1.7877 | 46.6005 | 102.8981 | 68.5987 | 5.4207 | 60.8664 | 2.1644 | 11.9395 | 39.8636 | 78.2396 | 6.182 | 231.8734 | 97.1233 | 241.2901 | 9.265 | 55.112 | 1.9985 | 116 | 4.663 | 55.3121 | 260.7233 | 0
3365 | 844.3396 | 2.3575 | 65.2727 | 101.6375 | 67.586 | 6.3827 | 64.5807 | 2.3793 | 11.5883 | 45.6807 | 75.6201 | 5.6907 | 229.7102 | 99.5314 | 240.5251 | 8.9089 | 54.2423 | 1.8513 | 115 | 4.6643 | 58.2317 | 272.317 | 0.031225
3366 | 898.9022 | 3.0672 | 74.0488 | 101.2344 | 64.3108 | 9.4942 | 70.2651 | 1.9818 | 11.5257 | 51.7902 | 80.5494 | 11.7689 | 239.3286 | 124.2103 | 247.7077 | 12.326 | 53.929 | 1.8225 | 195 | 4.7642 | 88.957 | 308.6137 | 0.054605
3367 | 952.2134 | 3.3993 | 74.0488 | 106.2243 | 60.2982 | 13.3062 | 100.5581 | 3.295 | 13.3945 | 59.3478 | 110.5538 | 24.0949 | 295.6153 | 182.3293 | 314.0358 | 24.7269 | 56.9977 | 7.8179 | 278 | 9.0231 | 140.2122 | 376.0569 | 0.11058
3368 | 1050.738 | 6.1027 | 74.0488 | 122.4539 | 54.8763 | 18.4569 | 125.8713 | 4.4237 | 15.4837 | 65.4343 | 151.934 | 30.8503 | 332.4166 | 255.4697 | 418.75 | 35.5572 | 65.067 | 13.9834 | 333 | 10.0056 | 176.7365 | 468.1942 | 0.21896
3369 | 1134.7531 | 7.2769 | 96.0204 | 138.3517 | 55.4545 | 17.9077 | 138.9505 | 4.0491 | 17.3993 | 69.6659 | 174.3993 | 35.61 | 385.6688 | 306.1418 | 507.0186 | 40.4764 | 74.8705 | 15.7152 | 356 | 9.2953 | 198.3525 | 528.3665 | 0.23247
3370 | 1186.6408 | 5.6466 | 107.8484 | 144.6966 | 57.7743 | 15.7038 | 146.1224 | 3.7379 | 17.6715 | 63.2716 | 182.5364 | 39.599 | 439.301 | 334.4667 | 568.4331 | 42.0503 | 82.704 | 17.3209 | 413 | 8.8186 | 207.0504 | 545.2642 | 0.14531
3371 | 1239.4394 | 4.0565 | 108.6099 | 149.8416 | 56.3072 | 17.0976 | 153.4212 | 4.6294 | 17.0727 | 51.8421 | 186.8076 | 39.9368 | 458.6214 | 347.371 | 600.9793 | 41.6736 | 86.3805 | 17.6102 | 351 | 7.5059 | 215.6757 | 547.4674 | 0.13274
3372 | 1223.5004 | 4.0191 | 109.3304 | 150.7489 | 55.9325 | 17.4536 | 151.1307 | 4.1616 | 18.2259 | 48.1226 | 189.3803 | 41.8045 | 478.5751 | 341.6179 | 603.9599 | 43.5511 | 86.1781 | 17.2513 | 374 | 9.1612 | 212.5626 | 538.7753 | 0.15193
3373 | 1213.2482 | 8.3999 | 110.9073 | 153.7778 | 54.4324 | 18.8787 | 139.0025 | 3.4891 | 19.9573 | 56.2929 | 195.5467 | 37.6772 | 494.6399 | 334.4696 | 597.6291 | 45.5027 | 86.7601 | 17.7092 | 318 | 8.8562 | 211.8977 | 541.8957 | 0.16039
3374 | 1197.4263 | 9.575 | 109.8369 | 152.6093 | 55.3405 | 18.016 | 132.0598 | 3.3796 | 19.9064 | 68.6471 | 200.2151 | 37.2843 | 506.081 | 333.9383 | 592.7489 | 43.2464 | 89.8174 | 17.8757 | 301 | 7.7168 | 212.3861 | 535.2432 | 0.1759
3375 | 1180.3982 | 6.0826 | 109.0771 | 150.0622 | 55.429 | 17.9319 | 134.3422 | 4.1879 | 19.1066 | 70.6429 | 195.8453 | 34.5404 | 515.8697 | 328.8926 | 589.1685 | 39.6206 | 92.6725 | 17.9234 | 297 | 6.3162 | 209.8322 | 506.3497 | 0.15857
3376 | 1142.6424 | 4.789 | 109.0771 | 139.7857 | 62.6173 | 11.103 | 126.5364 | 3.4936 | 18.4915 | 65.2215 | 188.543 | 32.0664 | 507.9879 | 309.2238 | 564.0514 | 24.9385 | 96.2946 | 18.196 | 276 | 4.5197 | 197.7239 | 447.0493 | 0.12262
3377 | 1077.0641 | 3.3018 | 90.709 | 128.7106 | 65.3182 | 8.5372 | 115.0842 | 3.2046 | 17.1 | 58.3185 | 177.6468 | 30.9932 | 478.0368 | 260.8198 | 496.8262 | 12.6188 | 100.6071 | 17.7385 | 247 | 4.1097 | 171.1975 | 362.413 | 0.058476
3378 | 1015.7959 | 2.295 | 82.1538 | 115.4572 | 65.2736 | 8.5796 | 107.8244 | 2.1612 | 15.3273 | 46.4781 | 149.878 | 25.7927 | 422.9962 | 208.7267 | 415.9839 | 10.1845 | 100.1579 | 16.5626 | 240 | 4.2299 | 150.9713 | 309.0949 | 0.10078
3379 | 953.6385 | 1.6921 | 82.1538 | 106.1617 | 65.377 | 8.4813 | 84.085 | 2.0671 | 13.6152 | 34.7244 | 116.6796 | 14.6473 | 376.7839 | 185.5485 | 355.125 | 9.7006 | 90.519 | 15.7897 | 208 | 4.1454 | 133.3634 | 293.2759 | 0.042733
3380 | 911.9358 | 1.9214 | 50.0053 | 101.7885 | 66.0563 | 7.836 | 67.1554 | 2.0438 | 12.5088 | 31.8493 | 96.5592 | 8.6573 | 327.9476 | 170.2172 | 305.6961 | 9.1467 | 73.9188 | 15.2451 | 183 | 4.03 | 118.5199 | 280.4868 | 0.024403
3381 | 886.0627 | 3.3731 | 45.1278 | 99.9514 | 66.2645 | 7.6382 | 66.7827 | 2.353 | 12.1283 | 33.5235 | 85.3049 | 7.0367 | 298.3566 | 146.6864 | 280.0753 | 9.1895 | 60.3092 | 14.4442 | 181 | 4.1652 | 110.0165 | 271.7897 | 0
3382 | 882.9786 | 3.2044 | 49.3722 | 100.8179 | 65.5649 | 8.3028 | 64.6599 | 3.04 | 12.1709 | 35.2576 | 81.7597 | 8.4692 | 277.3958 | 132.5193 | 285.5463 | 9.4907 | 55.5634 | 14.2658 | 164 | 4.0672 | 101.072 | 271.0638 | 0
3383 | 868.3856 | 1.8705 | 48.5156 | 100.9054 | 65.3441 | 8.5125 | 68.6502 | 3.3333 | 12.3532 | 36.3851 | 83.41 | 9.2206 | 265.3347 | 127.0597 | 286.6386 | 10.106 | 55.6097 | 14.1297 | 137 | 4.0775 | 78.569 | 270.7209 | 0
3384 | 873.6424 | 1.4139 | 48.17 | 101.1258 | 65.3118 | 8.5432 | 66.1632 | 2.8347 | 12.3905 | 35.166 | 84.0815 | 8.9958 | 261.9678 | 121.3908 | 282.5805 | 9.8273 | 55.6843 | 14.2361 | 139 | 4.1239 | 66.4693 | 268.0821 | 0
3385 | 861.6723 | 1.3849 | 48.17 | 100.0577 | 63.8468 | 9.935 | 71.4581 | 2.704 | 12.2707 | 31.3009 | 83.8973 | 8.9436 | 254.8255 | 118.821 | 280.3129 | 9.385 | 55.1272 | 14.6035 | 141 | 4.0742 | 58.809 | 266.2131 | 0
3386 | 836.9987 | 1.4844 | 47.7422 | 99.8359 | 65.4856 | 8.3781 | 74.4982 | 3.1494 | 12.1585 | 28.4451 | 84.0889 | 9.015 | 175.4078 | 114.8823 | 269.3703 | 9.3818 | 54.8053 | 14.4513 | 168 | 4.1538 | 55.0673 | 261.789 | 0
3387 | 850.8365 | 1.4475 | 47.3125 | 99.6487 | 66.2631 | 7.6395 | 73.2159 | 3.3605 | 12.376 | 28.2738 | 84.5123 | 9.0848 | 122.0283 | 109.0875 | 264.0745 | 9.2586 | 54.7459 | 13.5689 | 134 | 4.1181 | 58.4323 | 255.6242 | 0
3388 | 860.0437 | 1.546 | 47.1647 | 97.7444 | 66.3448 | 7.5619 | 67.4038 | 2.5052 | 12.0732 | 30.4591 | 83.146 | 7.6459 | 113.8132 | 101.413 | 262.8749 | 9.2696 | 54.4045 | 12.6004 | 124 | 4.056 | 59.4634 | 250.6753 | 0
3389 | 863.9425 | 1.2521 | 44.6857 | 95.9242 | 65.558 | 8.3094 | 68.4288 | 2.1461 | 11.9203 | 33.7806 | 80.2581 | 6.6314 | 114.5761 | 93.1734 | 252.0202 | 9.6388 | 53.737 | 11.7676 | 118 | 4.1675 | 57.0003 | 244.0824 | 0.029788
3390 | 884.0411 | 0.92132 | 47.7452 | 97.1786 | 66.0515 | 7.8406 | 62.7864 | 2.8319 | 11.5827 | 37.0285 | 79.0645 | 6.3776 | 115.0324 | 89.633 | 236.3285 | 9.1229 | 53.2922 | 11.0862 | 128 | 4.0552 | 56.6548 | 241.7755 | 0.06755
3391 | 893.1606 | 1.1694 | 49.6378 | 96.7233 | 66.2481 | 7.6538 | 69.5357 | 2.0018 | 11.168 | 37.6959 | 83.2399 | 7.4798 | 115.6942 | 89.9158 | 230.6395 | 9.413 | 53.0972 | 11.1959 | 125 | 4.1469 | 56.0218 | 247.5814 | 0.13724
3392 | 906.0356 | 1.269 | 60.2754 | 95.8189 | 65.5784 | 8.29 | 81.5676 | 2.1365 | 11.2978 | 37.2481 | 102.7928 | 12.6287 | 115.63 | 94.5368 | 231.8153 | 12.2008 | 53.1474 | 12.0868 | 144 | 4.2951 | 64.5227 | 259.2196 | 0.1144
3393 | 929.1081 | 1.4447 | 81.3924 | 96.8306 | 65.3594 | 8.4981 | 97.4784 | 1.8419 | 11.695 | 39.0582 | 130.4885 | 16.8935 | 129.7214 | 105.7816 | 240.6887 | 12.5872 | 53.3419 | 12.6327 | 157 | 4.1584 | 95.2508 | 272.0677 | 0.14137
3394 | 965.7368 | 1.7003 | 88.5311 | 97.7446 | 65.3193 | 8.5361 | 103.6303 | 1.3253 | 12.0239 | 41.4985 | 143.5149 | 23.3532 | 151.3713 | 120.43 | 255.3589 | 11.7176 | 53.5658 | 12.823 | 169 | 4.2105 | 108.0091 | 277.572 | 0.14867
3395 | 974.9365 | 2.1257 | 88.5311 | 99.8991 | 65.2605 | 8.592 | 100.4592 | 1.2562 | 11.3919 | 43.8289 | 131.7093 | 24.4316 | 172.5727 | 131.9431 | 263.0922 | 11.7233 | 54.064 | 13.1208 | 188 | 4.0583 | 112.048 | 276.3683 | 0.13836
3396 | 959.9939 | 2.0825 | 88.0014 | 98.8377 | 63.822 | 9.9585 | 93.6804 | 1.247 | 11.4563 | 46.0417 | 111.1967 | 19.9519 | 184.6753 | 139.437 | 262.7606 | 12.3276 | 54.8507 | 13.0035 | 194 | 4.0391 | 113.949 | 272.8385 | 0.15511
3397 | 952.4666 | 1.6108 | 84.2403 | 99.9676 | 65.5054 | 8.3594 | 89.2537 | 1.5485 | 12.3917 | 45.8033 | 102.7272 | 20.0659 | 185.3368 | 151.8229 | 271.7759 | 11.9519 | 56.6275 | 12.7204 | 197 | 4.166 | 115.0234 | 269.7343 | 0.27451
3398 | 947.5947 | 1.6617 | 76.5377 | 99.5723 | 65.5621 | 8.3054 | 108.965 | 1.4258 | 12.7555 | 44.6518 | 102.2836 | 21.5768 | 191.4657 | 157.9474 | 286.1411 | 11.904 | 58.4095 | 12.9975 | 203 | 4.0372 | 115.0315 | 269.2814 | 0.22228
3399 | 936.2261 | 1.866 | 55.5938 | 100.9656 | 66.0476 | 7.8443 | 96.8222 | 1.232 | 12.6213 | 40.8432 | 101.9898 | 18.5655 | 190.351 | 150.5782 | 294.0354 | 11.3716 | 57.1922 | 13.5174 | 213 | 3.986 | 108.866 | 268.4268 | 0.22664
3400 | 926.0084 | 2.0282 | 47.2672 | 98.9582 | 66.3347 | 7.5715 | 79.2838 | 1.9433 | 12.8814 | 32.1879 | 100.9452 | 12.9518 | 180.3432 | 142.1718 | 300.4061 | 9.5077 | 54.8498 | 13.8198 | 213 | 4.0016 | 85.021 | 267.2305 | 0.13171
3401 | 923.2546 | 2.2329 | 39.2913 | 98.8879 | 66.3654 | 7.5423 | 77.0357 | 1.6744 | 13.071 | 24.6354 | 99.8092 | 10.6812 | 176.483 | 136.7764 | 292.4181 | 8.3159 | 54.3986 | 13.2226 | 208 | 3.9294 | 76.4372 | 262.0863 | 0.095421
3402 | 921.9111 | 2.2415 | 35.7037 | 98.7692 | 66.3202 | 7.5853 | 67.8403 | 2.0102 | 14.402 | 19.7356 | 94.3084 | 7.1341 | 176.8441 | 130.3869 | 260.6402 | 8.0584 | 54.5281 | 13.688 | 211 | 4.0366 | 76.0762 | 257.5646 | 0.069424
3403 | 915.4323 | 2.3738 | 35.7037 | 100.5945 | 66.2726 | 7.6305 | 67.8757 | 1.7218 | 14.3472 | 16.7869 | 87.2213 | 6.171 | 160.223 | 124.3845 | 243.2422 | 8.1906 | 54.0354 | 14.0562 | 199 | 4.0628 | 79.3336 | 256.0853 | 0.017672
3404 | 896.105 | 2.8803 | 35.7806 | 100.0763 | 66.2786 | 7.6248 | 70.5866 | 2.3772 | 13.712 | 15.9358 | 88.2466 | 6.115 | 150.2933 | 121.3896 | 252.1584 | 8.2708 | 53.3671 | 13.3608 | 212 | 3.9826 | 76.069 | 250.0907 | 0.0032047
3405 | 874.0726 | 3.1924 | 35.4252 | 98.6273 | 66.25 | 7.652 | 65.1211 | 2.768 | 13.1842 | 16.4542 | 89.3209 | 9.2871 | 137.6548 | 118.0091 | 261.8685 | 8.534 | 52.8919 | 12.9587 | 200 | 4.0403 | 70.3553 | 245.1256 | 0
3406 | 868.9885 | 2.6413 | 35.7711 | 100.6888 | 65.6579 | 8.2145 | 68.9716 | 2.1989 | 12.887 | 18.5658 | 84.4448 | 13.4412 | 121.243 | 112.9985 | 259.5605 | 8.7687 | 53.2219 | 12.6593 | 185 | 4.0002 | 65.8212 | 249.1573 | 0
3407 | 873.268 | 1.6427 | 35.7502 | 100.4444 | 65.3192 | 8.5362 | 67.4513 | 2.6139 | 12.7938 | 20.1141 | 80.4423 | 12.7848 | 124.2659 | 108.5918 | 264.4039 | 8.5363 | 54.0953 | 11.7696 | 187 | 4.0402 | 63.7457 | 255.4169 | 0
3408 | 872.0381 | 1.2028 | 35.705 | 101.5166 | 65.2615 | 8.591 | 68.4692 | 2.2029 | 13.0387 | 19.7072 | 78.746 | 10.0557 | 129.4309 | 105.0934 | 274.445 | 8.3831 | 54.5345 | 11.3324 | 156 | 4.1688 | 62.253 | 262.4904 | 0
3409 | 857.6408 | 1.3697 | 35.0941 | 101.6643 | 65.9713 | 7.9167 | 70.3681 | 2.5226 | 13.0263 | 19.089 | 78.2515 | 9.1813 | 130.742 | 102.5075 | 262.8615 | 8.824 | 54.4362 | 11.0038 | 154 | 4.0964 | 60.2215 | 264.0368 | 0
3410 | 836.0664 | 1.2594 | 35.1532 | 100.566 | 65.5149 | 8.3503 | 67.2281 | 2.1732 | 12.9258 | 18.8129 | 78.4775 | 9.2559 | 120.5557 | 100.2358 | 246.0505 | 8.7179 | 54.3766 | 10.8808 | 185 | 4.1276 | 57.1099 | 255.2578 | 0
3411 | 847.1534 | 1.1369 | 35.2027 | 100.103 | 65.408 | 8.4519 | 69.415 | 2.7372 | 12.951 | 18.8362 | 79.1292 | 9.1671 | 110.4123 | 95.9873 | 237.7083 | 8.4991 | 54.7745 | 10.9653 | 155 | 4.152 | 52.8818 | 250.692 | 0
3412 | 853.834 | 1.5656 | 35.1622 | 99.2446 | 66.7511 | 7.176 | 65.0458 | 3.0921 | 12.5532 | 17.8905 | 77.769 | 8.1303 | 108.2933 | 91.6059 | 238.7359 | 8.4407 | 54.6211 | 11.0611 | 146 | 4.0934 | 50.3854 | 246.5204 | 0
3413 | 842.5751 | 1.6217 | 37.0257 | 97.6421 | 65.8782 | 8.0052 | 67.8813 | 1.8904 | 12.3016 | 16.3679 | 74.1318 | 6.8121 | 107.8265 | 90.4156 | 241.1845 | 8.1673 | 53.5983 | 10.9497 | 136 | 4.1633 | 48.9329 | 239.9229 | 0.026567
3414 | 833.5433 | 1.0394 | 47.6228 | 97.3717 | 66.0515 | 7.8405 | 65.6088 | 2.1206 | 11.9034 | 16.354 | 72.1095 | 6.4055 | 108.2702 | 90.0069 | 228.3751 | 8.0412 | 52.8136 | 10.8467 | 130 | 4.0743 | 49.0276 | 236.5667 | 0.1111
3415 | 837.5147 | 1.0545 | 60.0722 | 97.5927 | 65.5793 | 8.2891 | 72.5695 | 1.7797 | 11.796 | 17.9192 | 72.1197 | 5.684 | 103.0558 | 90.177 | 223.3197 | 8.9108 | 52.8492 | 11.0615 | 128 | 4.1703 | 49.5381 | 232.7785 | 0.070226
3416 | 831.7486 | 0.92349 | 68.9475 | 101.1258 | 65.9785 | 7.9099 | 77.2722 | 1.2983 | 11.6218 | 23.0196 | 73.8063 | 6.7791 | 102.5351 | 96.4533 | 222.5851 | 14.7365 | 53.1358 | 11.691 | 127 | 4.2462 | 52.2881 | 231.4724 | 0.14353
3417 | 837.5298 | 0.99595 | 74.5208 | 101.8535 | 65.5516 | 8.3154 | 91.3726 | 1.4621 | 11.9763 | 29.258 | 76.2477 | 9.16 | 117.7466 | 106.9638 | 221.8249 | 17.1074 | 53.3132 | 11.9202 | 180 | 4.1857 | 56.7975 | 234.3364 | 0.24795
3418 | 855.1233 | 1.215 | 73.439 | 103.0652 | 66.0292 | 7.8617 | 111.8303 | 2.3285 | 11.3802 | 35.6426 | 83.2721 | 9.6011 | 148.9046 | 118.3895 | 238.279 | 12.9894 | 53.6733 | 11.9371 | 174 | 4.1398 | 59.0616 | 237.689 | 0.18217
3419 | 863.0144 | 1.1924 | 72.3432 | 103.561 | 64.9212 | 8.9143 | 108.4728 | 2.4871 | 11.6948 | 40.6762 | 94.4531 | 10.0716 | 175.6962 | 129.9844 | 252.9572 | 11.4721 | 54.0423 | 12.2038 | 174 | 3.9852 | 64.1482 | 241.5589 | 0.24348
3420 | 867.2323 | 1.7735 | 72.8405 | 104.0015 | 64.223 | 9.5777 | 120.6703 | 1.6691 | 11.938 | 37.5536 | 100.443 | 17.1562 | 226.1893 | 137.4362 | 260.1278 | 11.9249 | 53.7618 | 12.659 | 225 | 3.9519 | 68.4814 | 247.473 | 0.22459
3421 | 873.6739 | 2.0769 | 74.4106 | 107.1396 | 65.7403 | 8.1362 | 139.4801 | 1.209 | 12.1248 | 30.5832 | 102.4374 | 20.0022 | 214.2077 | 141.1652 | 273.5026 | 12.0097 | 52.7462 | 13.0978 | 214 | 4.0885 | 71.136 | 250.9595 | 0.23361
3422 | 878.5458 | 2.004 | 74.9512 | 107.1295 | 65.6147 | 8.2555 | 150.598 | 1.0933 | 12.7741 | 24.7879 | 104.9709 | 16.4727 | 203.3095 | 145.8496 | 287.7787 | 11.831 | 52.2485 | 13.2799 | 198 | 4.0913 | 73.6263 | 250.4582 | 0.21668
3423 | 871.8225 | 2.076 | 57.0271 | 106.8198 | 65.3256 | 8.5302 | 144.8533 | 1.1103 | 13.7627 | 21.251 | 106.5232 | 19.2727 | 245.6027 | 148.9866 | 296.5664 | 11.1857 | 52.6789 | 14.0366 | 191 | 3.9945 | 75.9612 | 252.3035 | 0.2024
3424 | 866.5397 | 2.2115 | 48.9516 | 106.2613 | 66.8055 | 7.1242 | 148.2822 | 1.0355 | 14.071 | 20.6304 | 106.181 | 18.2353 | 259.7574 | 147.4605 | 303.0052 | 9.5129 | 53.4064 | 14.1545 | 191 | 4.0494 | 75.2512 | 250.751 | 0.15821
3425 | 861.4646 | 2.2405 | 39.5817 | 104.0909 | 65.8109 | 8.0691 | 146.9792 | 1.0769 | 14.4301 | 22.4779 | 104.6536 | 13.0697 | 228.9928 | 148.7737 | 305.5487 | 8.3669 | 54.092 | 13.5942 | 177 | 4.014 | 74.4763 | 246.1473 | 0.099089
3426 | 849.4022 | 2.2108 | 35.2647 | 102.6703 | 66.787 | 7.1418 | 107.9642 | 1.1089 | 15.2313 | 23.4404 | 102.6192 | 11.2145 | 212.8646 | 151.828 | 302.3327 | 8.6214 | 54.0841 | 13.1233 | 162 | 4.0129 | 73.0846 | 244.5273 | 0.066196
3427 | 843.2269 | 2.0075 | 36.7937 | 101.4491 | 65.88 | 8.0034 | 73.9252 | 1.0077 | 14.9385 | 21.8046 | 100.7127 | 10.8347 | 203.102 | 146.917 | 281.0726 | 8.2494 | 53.9511 | 13.1392 | 143 | 4.1485 | 73.9747 | 246.7856 | 0.051229
3428 | 820.5453 | 1.6345 | 35.934 | 101.3909 | 66.7398 | 7.1866 | 71.8022 | 1.5601 | 14.9751 | 20.8961 | 94.3346 | 9.4535 | 190.3229 | 132.6186 | 266.3327 | 8.0268 | 54.1204 | 13.011 | 132 | 4.3051 | 69.8066 | 238.8697 | 0.012156
3429 | 793.3717 | 2.9173 | 35.2216 | 99.955 | 67.2505 | 6.7015 | 87.1107 | 1.663 | 15.7859 | 21.4032 | 85.2184 | 8.5051 | 177.3458 | 120.4504 | 254.5495 | 8.399 | 54.2237 | 12.6204 | 129 | 4.0854 | 65.1851 | 221.8102 | 0
3430 | 786.955 | 2.8344 | 35.7131 | 100.6416 | 65.7985 | 8.0808 | 89.4766 | 1.7284 | 15.8198 | 22.7216 | 82.3221 | 8.5871 | 149.7342 | 117.0754 | 254.9245 | 8.5793 | 54.7412 | 12.7327 | 120 | 4.0468 | 63.1311 | 218.0181 | 0
3431 | 779.1023 | 1.7756 | 35.9502 | 100.8354 | 66.099 | 7.7954 | 78.9273 | 1.7194 | 14.6718 | 23.1823 | 83.0412 | 8.3506 | 143.7065 | 112.8128 | 251.2452 | 9.937 | 54.9776 | 11.9505 | 120 | 4.2217 | 61.3434 | 220.2536 | 0
3432 | 771.2965 | 1.3058 | 35.8711 | 100.7382 | 66.2872 | 7.6166 | 70.234 | 1.6746 | 14.4392 | 21.2469 | 82.1538 | 7.802 | 131.9324 | 106.0587 | 248.331 | 11.8235 | 54.7358 | 11.0857 | 125 | 4.1798 | 59.655 | 216.9144 | 0
3433 | 766.8194 | 1.3071 | 35.9498 | 99.9622 | 64.8058 | 9.024 | 70.0252 | 2.3342 | 13.0229 | 18.7453 | 80.9945 | 7.5505 | 125.678 | 102.5816 | 248.1861 | 12.6999 | 54.5782 | 10.8919 | 116 | 4.1233 | 58.9218 | 213.4659 | 0
3434 | 762.1225 | 1.2617 | 35.6412 | 100.1119 | 65.7232 | 8.1525 | 73.9232 | 2.0334 | 12.2461 | 17.7393 | 80.533 | 7.7151 | 124.2649 | 99.8817 | 235.0997 | 12.907 | 54.1153 | 10.8763 | 145 | 4.1173 | 60.4657 | 211.8047 | 0
3435 | 767.6715 | 1.1361 | 35.4576 | 99.9148 | 66.387 | 7.5218 | 66.4927 | 1.8593 | 12.1102 | 19.1768 | 80.3259 | 7.8496 | 121.4121 | 96.4724 | 224.739 | 12.7197 | 53.6199 | 10.8679 | 120 | 4.2734 | 66.6762 | 211.918 | 0
3436 | 788.0767 | 1.494 | 35.4597 | 98.9639 | 65.623 | 8.2476 | 68.5959 | 2.3484 | 11.9563 | 25.8977 | 78.5531 | 6.7522 | 117.4247 | 93.5855 | 226.4281 | 10.0982 | 53.387 | 10.8112 | 118 | 4.17 | 63.5745 | 217.3644 | 0
3437 | 794.1631 | 1.3939 | 48.4829 | 97.8564 | 63.8172 | 9.9631 | 67.4887 | 1.7579 | 12.0881 | 33.0849 | 75.8972 | 6.7817 | 121.8832 | 98.8796 | 225.9933 | 8.3481 | 53.1909 | 11.225 | 112 | 4.0625 | 66.0788 | 228.1763 | 0.029273
3438 | 818.6008 | 2.2902 | 54.7678 | 103.8667 | 61.804 | 11.8757 | 80.7284 | 1.2029 | 11.5413 | 39.3867 | 87.6597 | 14.3898 | 142.4761 | 134.8252 | 246.1335 | 11.6947 | 53.4436 | 11.5892 | 180 | 4.2174 | 103.0217 | 263.8271 | 0.067996
3439 | 901.1204 | 3.4472 | 82.1368 | 114.0033 | 59.0124 | 14.5277 | 109.2813 | 2.2705 | 13.7083 | 47.8479 | 122.2517 | 28.4133 | 210.9811 | 198.8582 | 308.4244 | 24.1573 | 57.0483 | 12.3749 | 316 | 5.1445 | 144.2748 | 326.8451 | 0.091638
3440 | 980.4831 | 4.7057 | 107.1166 | 129.9996 | 59.158 | 14.3893 | 143.1574 | 4.26 | 17.9572 | 51.1976 | 157.7501 | 32.2878 | 277.3504 | 262.3615 | 392.8136 | 32.7568 | 65.2054 | 14.8406 | 299 | 6.5911 | 171.8602 | 395.9358 | 0.10854
3441 | 1072.1564 | 7.686 | 112.7049 | 144.5954 | 59.9319 | 13.6542 | 160.5819 | 4.1751 | 20.7486 | 55.2451 | 175.2935 | 33.6621 | 377.9529 | 306.4653 | 489.0596 | 35.6925 | 75.5168 | 17.2846 | 368 | 7.5061 | 200.7591 | 463.5719 | 0.1407
3442 | 1160.7348 | 5.5679 | 114.5757 | 151.3774 | 58.159 | 15.3384 | 165.4545 | 3.965 | 20.3394 | 65.0973 | 181.777 | 38.8363 | 466.9941 | 333.6263 | 565.1897 | 38.8283 | 86.6831 | 17.3144 | 374 | 7.0923 | 211.263 | 513.0871 | 0.15454
3443 | 1198.0645 | 3.5812 | 117.4996 | 150.5916 | 63.2155 | 10.5347 | 165.8146 | 4.3888 | 18.9712 | 74.8168 | 184.8748 | 41.1864 | 498.3267 | 354.0841 | 601.3395 | 40.8199 | 101.7639 | 17.0226 | 381 | 6.4894 | 211.0436 | 533.8099 | 0.1629
3444 | 1206.5338 | 3.364 | 118.463 | 154.2993 | 57.2191 | 16.2313 | 159.7733 | 4.2586 | 17.2176 | 77.5258 | 185.7229 | 40.4666 | 501.8033 | 361.5116 | 613.2739 | 42.0068 | 118.8384 | 17.6779 | 361 | 5.253 | 206.9182 | 539.2637 | 0.12176
3445 | 1218.8678 | 3.232 | 118.463 | 161.2333 | 55.1173 | 18.228 | 160.0461 | 3.903 | 17.459 | 74.9997 | 190.0821 | 40.2987 | 508.6686 | 361.0151 | 613.6053 | 42.649 | 129.8644 | 18.3092 | 305 | 5.2419 | 208.9541 | 548.4196 | 0.17334
3446 | 1226.7432 | 3.4336 | 118.463 | 165.4339 | 53.043 | 20.1986 | 171.4089 | 4.2026 | 20.8774 | 75.664 | 194.5177 | 39.7122 | 512.4158 | 361.9911 | 614.7157 | 42.204 | 132.537 | 18.287 | 294 | 6.3244 | 204.2885 | 543.369 | 0.16516
3447 | 1205.1785 | 3.5827 | 118.463 | 155.302 | 56.6459 | 16.7759 | 171.4504 | 4.3784 | 21.1346 | 78.0203 | 192.6711 | 35.7942 | 523.6969 | 358.1469 | 608.2422 | 42.1085 | 130.1355 | 18.091 | 280 | 3.3739 | 196.7837 | 527.7483 | 0.20212
3448 | 1157.7552 | 3.6615 | 113.004 | 144.292 | 62.1139 | 11.5812 | 153.4724 | 3.4673 | 18.5248 | 77.3416 | 188.7737 | 34.4057 | 516.8076 | 343.2933 | 580.359 | 33.4613 | 126.9191 | 17.6219 | 250 | 0.25748 | 182.4996 | 499.8576 | 0.16735
3449 | 1085.9842 | 3.2948 | 104.031 | 128.1551 | 65.4853 | 8.3784 | 130.7729 | 2.2227 | 18.4488 | 63.9041 | 179.7789 | 34.8097 | 475.6928 | 293.3175 | 525.2346 | 18.9724 | 119.9368 | 16.3983 | 226 | -0.25598 | 160.8196 | 435.3434 | 0.16269
3450 | 1023.329 | 2.6778 | 101.004 | 113.4974 | 65.4515 | 8.4106 | 111.598 | 1.6685 | 17.1275 | 43.7149 | 152.6638 | 31.4785 | 433.1788 | 229.3194 | 441.4671 | 12.0168 | 106.8921 | 15.2067 | 223 | -0.070506 | 147.7567 | 343.187 | 0.1051
3451 | 984.8172 | 1.6331 | 84.5088 | 106.6027 | 65.2935 | 8.5607 | 108.9299 | 1.4438 | 13.983 | 31.2115 | 121.3972 | 15.1549 | 382.2822 | 189.031 | 382.3394 | 10.6594 | 91.503 | 14.2574 | 212 | -0.38961 | 131.4854 | 262.6197 | 0.055495
3452 | 947.9939 | 2.1745 | 57.9889 | 100.0996 | 66.052 | 7.8401 | 109.6276 | 1.9988 | 12.2235 | 26.3073 | 107.8843 | 6.9922 | 350.5402 | 157.4234 | 337.9433 | 10.1292 | 74.0809 | 13.6628 | 190 | -0.76532 | 119.2514 | 220.6331 | 0.0073588
3453 | 902.9235 | 3.3011 | 54.8792 | 99.0595 | 65.6452 | 8.2265 | 97.1577 | 2.0065 | 11.6777 | 24.7549 | 102.7484 | 6.6303 | 320.5948 | 131.3764 | 307.3415 | 10.3696 | 60.6045 | 13.0046 | 164 | -0.87784 | 116.5779 | 206.3921 | 0
3454 | 863.5586 | 3.0393 | 57.782 | 104.7596 | 65.3084 | 8.5465 | 82.5166 | 1.6926 | 11.3704 | 22.6886 | 95.2037 | 7.9158 | 245.7426 | 121.1565 | 283.1307 | 11.0801 | 56.554 | 12.8739 | 142 | -0.88719 | 105.6619 | 207.703 | 0
3455 | 845.0777 | 1.7375 | 58.2701 | 107.0898 | 66.1311 | 7.7649 | 80.0291 | 2.3389 | 11.446 | 20.1775 | 87.6313 | 9.1112 | 235.7381 | 118.5351 | 255.3005 | 10.8144 | 56.4215 | 12.7597 | 128 | -0.88143 | 79.5332 | 209.1556 | 0
3456 | 842.2433 | 1.1442 | 58.4403 | 106.2843 | 65.6187 | 8.2517 | 81.0885 | 2.0955 | 11.9616 | 18.5598 | 83.3704 | 8.652 | 250.9353 | 113.7161 | 241.7493 | 10.5121 | 56.3887 | 12.6799 | 122 | -0.85723 | 67.1307 | 207.8133 | 0
3457 | 824.9069 | 1.1324 | 58.3533 | 105.7348 | 66.0191 | 7.8713 | 81.8035 | 2.4569 | 12.0757 | 17.5901 | 81.8673 | 8.161 | 254.0783 | 108.9341 | 242.2161 | 10.6621 | 56.3783 | 12.5001 | 120 | -0.84789 | 62.8881 | 206.996 | 0
3458 | 800.4971 | 1.2495 | 58.3018 | 105.5359 | 65.6172 | 8.2531 | 70.7735 | 2.3594 | 11.7833 | 17.384 | 81.687 | 8.1939 | 252.5965 | 102.1248 | 239.1473 | 10.627 | 56.3868 | 12.3737 | 149 | -0.81948 | 59.3953 | 207.3299 | 0
3459 | 803.6448 | 1.3034 | 58.2478 | 105.3284 | 65.9868 | 7.902 | 66.4979 | 2.558 | 11.8867 | 19.1799 | 82.0767 | 8.1384 | 246.4703 | 95.7503 | 237.5317 | 10.9796 | 56.255 | 12.6493 | 123 | -0.81565 | 58.9424 | 207.7718 | 0
3460 | 812.1856 | 1.5492 | 57.6633 | 102.894 | 65.5618 | 8.3058 | 62.4324 | 1.9494 | 11.8252 | 25.2345 | 80.5899 | 6.6166 | 239.5374 | 91.9773 | 235.6044 | 10.5376 | 55.6416 | 12.3154 | 113 | -0.82169 | 58.8708 | 206.3371 | 0
3461 | 825.6559 | 1.5454 | 57.0263 | 101.8908 | 65.9918 | 7.8972 | 64.0982 | 1.998 | 11.3792 | 32.5327 | 77.7383 | 8.5853 | 236.4062 | 96.2936 | 233.777 | 10.0432 | 55.1424 | 11.994 | 140 | -0.49618 | 62.663 | 211.2744 | 0.038504
3462 | 865.8863 | 2.6039 | 58.2318 | 101.6502 | 63.4487 | 10.3132 | 71.0027 | 1.8243 | 11.0418 | 41.8349 | 83.4236 | 16.185 | 251.6976 | 122.5959 | 239.6544 | 13.1855 | 55.1383 | 11.9677 | 190 | 0.42824 | 96.8512 | 249.3042 | 0.063929
3463 | 932.2548 | 3.6361 | 83.9355 | 107.2834 | 60.6532 | 12.9689 | 104.1727 | 2.575 | 11.0555 | 51.673 | 110.0329 | 32.7807 | 287.9993 | 181.7033 | 280.6637 | 25.1016 | 57.6196 | 12.7795 | 288 | 4.4888 | 145.2771 | 314.7613 | 0.10736
3464 | 1042.6823 | 7.4018 | 107.7258 | 126.4203 | 57.9936 | 15.4955 | 145.9286 | 3.8844 | 12.5594 | 51.29 | 145.9887 | 37.2617 | 360.4703 | 253.5949 | 388.6196 | 33.2958 | 64.669 | 16.6268 | 320 | 4.232 | 179.1383 | 380.815 | 0.22681
3465 | 1169.5615 | 11.7169 | 113.0861 | 141.9541 | 55.8707 | 17.5123 | 159.2884 | 3.7015 | 14.0212 | 51.6581 | 163.8461 | 35.6251 | 427.0544 | 301.216 | 500.0542 | 35.8588 | 74.5143 | 16.9612 | 340 | 3.6379 | 203.7493 | 445.6484 | 0.26162
3466 | 1193.7271 | 8.6326 | 114.2242 | 147.9766 | 56.9291 | 16.5068 | 174.1346 | 3.3911 | 16.4598 | 62.9558 | 165.6708 | 40.5796 | 522.2559 | 322.3739 | 570.0152 | 38.3128 | 84.3803 | 17.0779 | 339 | 3.0439 | 218.2768 | 488.9897 | 0.2284
3467 | 1196.2874 | 4.7913 | 116.2747 | 149.0783 | 57.3447 | 16.112 | 184.1751 | 3.6922 | 19.0613 | 73.6383 | 168.6861 | 42.1194 | 579.5645 | 337.0571 | 600.2678 | 39.0876 | 90.0866 | 17.3503 | 350 | 2.3096 | 222.6349 | 506.6496 | 0.26297
3468 | 1182.269 | 4.0852 | 117.0983 | 149.4426 | 55.7459 | 17.6309 | 192.1123 | 3.4521 | 19.3677 | 75.9842 | 174.6273 | 41.8363 | 601.5792 | 349.8555 | 594.3229 | 39.2531 | 90.6971 | 17.3978 | 333 | 1.7246 | 216.5653 | 521.5791 | 0.25574
3469 | 1177.1583 | 4.211 | 115.7283 | 156.3353 | 54.6669 | 18.6559 | 199.4836 | 3.4 | 19.2328 | 75.2618 | 182.1305 | 41.4902 | 616.059 | 360.9924 | 581.4342 | 39.3941 | 91.3125 | 18.2787 | 294 | 1.9977 | 218.1571 | 538.1115 | 0.29631
3470 | 1175.0299 | 4.1718 | 115.3866 | 161.2477 | 54.1535 | 19.1437 | 207.9964 | 3.5491 | 19.9232 | 75.2723 | 186.6091 | 41.5542 | 624.2559 | 368.9301 | 586.5538 | 38.0321 | 95.0881 | 18.678 | 274 | 3.5753 | 218.1832 | 542.606 | 0.25324
3471 | 1188.7242 | 4.0717 | 115.3789 | 154.0709 | 55.8219 | 17.5587 | 187.8583 | 3.6994 | 20.1971 | 72.5914 | 185.4652 | 39.8699 | 610.7029 | 353.3236 | 582.9169 | 36.2797 | 101.4765 | 18.4429 | 283 | 1.5449 | 210.1904 | 528.4516 | 0.17626
3472 | 1144.5466 | 3.5319 | 112.7517 | 145.1399 | 60.7459 | 12.8809 | 116.5912 | 3.2934 | 18.9727 | 66.4013 | 184.21 | 37.4475 | 535.4653 | 315.4671 | 558.3718 | 30.2969 | 104.416 | 17.7456 | 261 | -0.46813 | 197.0245 | 483.9816 | 0.06211
3473 | 1084.8924 | 2.948 | 106.4695 | 120.5899 | 62.3089 | 11.396 | 81.2563 | 2.131 | 17.4067 | 54.497 | 175.3883 | 32.1403 | 525.1152 | 263.8558 | 504.4236 | 17.1853 | 100.7079 | 16.4909 | 246 | -1.5585 | 175.1097 | 415.8797 | 0.14452
3474 | 1032.8879 | 2.2621 | 102.3021 | 106.5057 | 63.7739 | 10.0042 | 83.1722 | 1.4176 | 16.4096 | 40.5856 | 147.119 | 23.8402 | 486.7701 | 203.6175 | 429.6126 | 10.694 | 94.1509 | 15.4355 | 216 | -2.0573 | 156.4673 | 352.5055 | 0.098469
3475 | 966.5412 | 1.555 | 87.0989 | 103.1681 | 64.2612 | 9.5413 | 88.4037 | 1.8274 | 14.5514 | 30.6579 | 117.8967 | 10.0879 | 437.5801 | 161.9005 | 363.8059 | 9.6278 | 87.323 | 14.987 | 186 | -2.1025 | 139.1955 | 301.9235 | 0.053076
3476 | 946.1046 | 2.3981 | 60.1408 | 73.674 | 64.9554 | 8.8818 | 83.8809 | 1.6264 | 9.9547 | 25.3764 | 106.393 | 4.7771 | 383.3577 | 146.1291 | 322.349 | 9.4736 | 81.7505 | 14.4315 | 168 | -2.1534 | 123.1608 | 266.8421 | 0.028673
3477 | 919.5854 | 3.3798 | 56.4146 | 43.4916 | 66.1189 | 7.7765 | 76.97 | 1.5214 | 7.8483 | 21.839 | 104.2431 | 5.8167 | 329.3784 | 136.8227 | 287.6954 | 9.6378 | 78.2897 | 14.071 | 158 | -2.1821 | 113.0402 | 252.8939 | 0
3478 | 877.9081 | 3.2127 | 59.3119 | 77.629 | 64.877 | 8.9563 | 71.5644 | 2.3814 | 7.683 | 18.4775 | 101.4781 | 6.61 | 259.1442 | 129.1924 | 273.7834 | 10.0506 | 77.1368 | 13.4532 | 136 | -2.1836 | 106.6976 | 252.3183 | 0
3479 | 850.0502 | 2.1622 | 59.1553 | 79.318 | 65.818 | 8.0623 | 67.4826 | 2.0982 | 7.8483 | 16.9499 | 94.1144 | 6.5759 | 225.0751 | 125.1264 | 268.4345 | 10.7811 | 77.2816 | 13.5559 | 128 | -2.1534 | 83.7819 | 249.792 | 0
3480 | 838.1453 | 1.9341 | 58.5085 | 100.2664 | 64.1963 | 9.603 | 70.716 | 2.3833 | 7.9915 | 16.6513 | 87.0485 | 6.4865 | 237.1638 | 119.7613 | 257.2763 | 13.1751 | 77.5173 | 13.1804 | 118 | -2.1342 | 72.4331 | 247.294 | 0
3481 | 824.0528 | 1.5907 | 58.2272 | 58.035 | 66.1478 | 7.7491 | 66.4186 | 2.2046 | 7.1112 | 16.8116 | 84.2484 | 6.5834 | 257.8452 | 114.3144 | 248.5234 | 14.4043 | 77.4813 | 12.8913 | 117 | -2.1423 | 67.4786 | 245.7063 | 0
3482 | 802.5396 | 1.2763 | 57.9867 | 78.2893 | 67.2046 | 6.7451 | 69.3526 | 2.645 | 6.6353 | 17.2398 | 82.8672 | 8.4527 | 251.6685 | 113.0408 | 247.3072 | 13.8899 | 77.4283 | 13.0937 | 147 | -2.1457 | 62.8832 | 244.7476 | 0
3483 | 815.9009 | 1.6045 | 57.7639 | 77.8755 | 66.5586 | 7.3588 | 65.518 | 2.202 | 6.3183 | 19.1282 | 82.4306 | 14.4575 | 240.8 | 113.1829 | 243.9687 | 13.3368 | 77.5046 | 13.1573 | 121 | -2.1238 | 60.4055 | 246.7698 | 0
3484 | 834.5492 | 2.1534 | 57.9382 | 96.4895 | 65.5767 | 8.2916 | 68.3571 | 2.4145 | 6.3097 | 25.4297 | 81.3657 | 9.9169 | 236.4602 | 110.4725 | 231.8654 | 10.9647 | 77.472 | 13.7619 | 113 | -2.1022 | 58.5432 | 249.1847 | 0
3485 | 840.5285 | 2.3579 | 60.9763 | 54.0237 | 65.3219 | 8.5336 | 67.0615 | 2.3366 | 5.9307 | 32.0388 | 79.1896 | 6.6232 | 228.5269 | 107.7233 | 220.0981 | 9.7628 | 76.9095 | 13.5828 | 133 | -2.1306 | 61.2249 | 256.0923 | 0.017215
3486 | 889.6494 | 2.61 | 62.3437 | 103.3219 | 62.3919 | 11.3172 | 76.9428 | 1.8604 | 5.6343 | 38.2578 | 87.8849 | 12.1196 | 241.124 | 117.0264 | 233.0909 | 13.1545 | 76.3375 | 12.6657 | 181 | -1.6635 | 102.9044 | 295.253 | 0.023905
3487 | 961.0004 | 4.3888 | 85.9158 | 89.5974 | 59.7579 | 13.8195 | 104.5121 | 3.5361 | 8.9862 | 45.3749 | 119.7146 | 27.5194 | 277.6974 | 164.2244 | 299.8476 | 25.8774 | 79.8743 | 13.5106 | 314 | 2.1795 | 147.7531 | 359.6453 | 0.044135
3488 | 1053.6109 | 6.2673 | 107.0455 | 145.8719 | 58.5547 | 14.9625 | 125.2696 | 3.9102 | 14.8309 | 51.4938 | 155.3139 | 37.8548 | 364.0529 | 239.9075 | 431.6067 | 35.6773 | 88.5931 | 17.2919 | 352 | 2.5866 | 184.1444 | 421.6672 | 0.044193
3489 | 1150.7329 | 4.8083 | 116.114 | 192.6034 | 56.1016 | 17.2929 | 138.8997 | 4.9512 | 17.2988 | 58.3711 | 170.7497 | 40.0945 | 402.9971 | 302.8403 | 561.0707 | 40.1516 | 98.171 | 18.1372 | 368 | 2.3388 | 215.7363 | 480.8249 | 0.054157
3490 | 1190.9197 | 3.7628 | 117.0479 | 186.1969 | 55.4656 | 17.8972 | 148.0187 | 4.6513 | 18.2133 | 70.0043 | 176.3878 | 41.6821 | 451.6748 | 339.7134 | 624.842 | 42.2869 | 106.2375 | 18.3301 | 389 | 3.5482 | 219.2653 | 514.6899 | 0.097941
3491 | 1201.621 | 3.8097 | 119.4509 | 184.4741 | 56.1197 | 17.2757 | 149.6889 | 5.0645 | 19.729 | 83.5569 | 183.5445 | 38.8142 | 497.9687 | 361.4554 | 630.252 | 42.8738 | 111.8951 | 18.279 | 361 | 3.9175 | 219.1475 | 522.5503 | 0.092509
3492 | 1188.6863 | 6.0002 | 121.1672 | 158.7037 | 54.8848 | 18.4489 | 148.7749 | 4.8692 | 20.157 | 84.843 | 189.514 | 35.8001 | 521.7807 | 367.0801 | 631.1077 | 43.0402 | 114.6608 | 18.422 | 411 | 4.3903 | 222.1784 | 530.4314 | 0.1335
3493 | 1213.48 | 6.8206 | 123.1535 | 210.8289 | 52.7707 | 20.4573 | 152.2711 | 4.9122 | 20.6672 | 80.6363 | 195.3597 | 40.0263 | 521.0793 | 365.9391 | 640.501 | 43.0154 | 113.9477 | 18.937 | 320 | 2.392 | 221.2236 | 543.9277 | 0.12808
3494 | 1217.9536 | 6.8301 | 123.6051 | 171.6942 | 53.6399 | 19.6315 | 148.1098 | 4.5967 | 21.7005 | 82.5661 | 199.4363 | 41.4296 | 510.037 | 368.3083 | 650.0909 | 40.5928 | 112.3142 | 19.1443 | 312 | 3.0644 | 221.3627 | 552.5718 | 0.11996
3495 | 1191.9035 | 6.9478 | 121.3035 | 208.9562 | 55.7956 | 17.5836 | 138.8945 | 3.9538 | 21.5553 | 85.1918 | 198.4098 | 41.1457 | 479.5283 | 358.2178 | 660.8021 | 38.0441 | 112.4918 | 18.9719 | 312 | 0.59452 | 215.5636 | 541.5718 | 0.13244
3496 | 1163.6525 | 4.9066 | 115.7133 | 180.6961 | 59.0929 | 14.4512 | 137.7096 | 4.2174 | 20.6682 | 81.0201 | 192.5537 | 38.933 | 434.8547 | 340.1043 | 632.755 | 31.0731 | 111.3677 | 18.5806 | 319 | -1.8541 | 201.6994 | 502.5916 | 0.13029
3497 | 1110.114 | 3.2184 | 109.5262 | 132.274 | 62.5466 | 11.1702 | 130.5696 | 2.6536 | 20.0324 | 65.4792 | 177.9981 | 37.3667 | 385.0947 | 305.1548 | 543.3291 | 17.0279 | 105.5884 | 18.4048 | 273 | -2.5385 | 182.1029 | 431.6187 | 0.15805
3498 | 1046.8523 | 2.8265 | 104.031 | 107.6907 | 64.8438 | 8.9879 | 121.1107 | 1.574 | 19.3874 | 43.9344 | 147.4514 | 30.6534 | 328.4124 | 244.1889 | 456.0036 | 10.2547 | 97.392 | 18.229 | 237 | -3.4794 | 164.6504 | 358.1248 | 0.087506
3499 | 1012.2013 | 2.1598 | 87.9718 | 99.7008 | 64.6624 | 9.1602 | 111.2557 | 2.4799 | 17.2179 | 26.8876 | 116.1329 | 16.4612 | 265.7601 | 191.3183 | 404.731 | 9.8435 | 89.8105 | 16.9375 | 205 | -3.8554 | 142.6201 | 306.6712 | 0.043258
3500 | 994.4342 | 2.2216 | 53.5822 | 93.392 | 65.7272 | 8.1486 | 82.1773 | 3.174 | 11.2882 | 19.3854 | 103.0658 | 11.0781 | 234.4019 | 159.3639 | 356.6335 | 10.754 | 83.5396 | 15.489 | 195 | -3.877 | 127.913 | 273.1481 | 0.044045
3501 | 955.8021 | 3.8258 | 45.7902 | 97.1991 | 65.5891 | 8.2798 | 69.3161 | 2.0988 | 7.1192 | 18.4852 | 97.7684 | 10.9437 | 220.4772 | 139.0594 | 306.3359 | 9.6722 | 79.0883 | 13.6812 | 180 | -3.8645 | 115.7276 | 255.3811 | 0
3502 | 910.4836 | 3.9405 | 48.1081 | 99.025 | 64.5239 | 9.2918 | 66.528 | 2.5243 | 6.0272 | 19.0433 | 89.6428 | 12.6501 | 172.7278 | 128.6018 | 270.1058 | 9.1446 | 77.0031 | 13.163 | 166 | -3.6382 | 111.8671 | 251.0949 | 0
3503 | 886.9558 | 2.1388 | 48.2068 | 98.2906 | 65.7672 | 8.1107 | 81.0898 | 3.4957 | 6.173 | 19.3616 | 83.0075 | 13.5403 | 140.0342 | 122.7595 | 250.5364 | 9.7481 | 76.9863 | 13.4657 | 143 | -3.5594 | 84.0976 | 252.6058 | 0
3504 | 866.2294 | 1.376 | 47.7954 | 53.4113 | 65.5434 | 8.3232 | 89.898 | 3.509 | 6.1711 | 19.2584 | 81.3243 | 13.6436 | 124.741 | 116.8208 | 247.1561 | 9.8068 | 76.9713 | 13.7184 | 133 | -3.6489 | 70.344 | 250.0369 | 0
3505 | 839.496 | 1.4056 | 41.3985 | 81.6194 | 65.354 | 8.5032 | 89.7019 | 3.5394 | 6.2082 | 18.9705 | 80.3196 | 13.6414 | 122.8046 | 111.9902 | 243.7304 | 10.3972 | 76.345 | 13.5179 | 129 | -3.6956 | 67.3801 | 244.6814 | 0
3506 | 851.9567 | 1.3183 | 36.9126 | 63.9599 | 64.5558 | 9.2615 | 88.6952 | 3.5817 | 6.2432 | 19.0109 | 78.484 | 13.6011 | 123.4749 | 106.7481 | 237.4095 | 10.7002 | 75.8139 | 13.6017 | 157 | -3.7137 | 65.0476 | 242.5963 | 0
3507 | 882.8559 | 1.238 | 36.18 | 54.9309 | 64.9961 | 8.8431 | 88.2759 | 3.5513 | 6.2914 | 19.3285 | 77.0262 | 13.3551 | 120.4326 | 100.4706 | 228.749 | 10.2637 | 75.4869 | 13.017 | 120 | -3.7193 | 62.1566 | 240.567 | 0
3508 | 874.465 | 1.4234 | 30.4602 | 46.8314 | 63.7843 | 9.9943 | 87.5908 | 2.9536 | 5.7446 | 24.1414 | 74.4465 | 11.8023 | 120.4799 | 94.9015 | 224.8465 | 10.6616 | 75.0309 | 12.3963 | 109 | -3.7057 | 61.3222 | 242.5899 | 0
3509 | 877.1816 | 1.1924 | 42.4387 | 59.145 | 62.6898 | 11.0342 | 88.5922 | 2.6778 | 5.346 | 32.3147 | 74.4006 | 12.2031 | 120.0777 | 98.8817 | 221.1153 | 10.2801 | 74.6707 | 11.5879 | 121 | -3.6835 | 66.0087 | 261.7957 | 0.11496
3510 | 912.486 | 2.0009 | 60.3233 | 62.9209 | 63.0388 | 10.7026 | 86.552 | 3.1032 | 5.123 | 43.4919 | 86.8699 | 18.3012 | 128.6185 | 127.2736 | 244.6412 | 12.8735 | 74.9386 | 13.2079 | 160 | -3.2947 | 102.2726 | 304.3742 | 0.20366
3511 | 972.0371 | 3.2506 | 82.4218 | 112.0369 | 58.9044 | 14.6303 | 99.8388 | 3.61 | 5.8956 | 63.5769 | 118.5368 | 31.438 | 170.9763 | 175.4526 | 310.1151 | 26.5383 | 78.2957 | 13.2109 | 271 | 0.10781 | 150.2281 | 371.0889 | 0.28027
3512 | 1060.2039 | 3.7917 | 99.8433 | 145.295 | 57.9015 | 15.583 | 127.8058 | 4.2513 | 12.5324 | 80.3726 | 152.0807 | 37.9872 | 247.6733 | 229.9144 | 410.5828 | 34.7057 | 87.0713 | 16.0446 | 284 | 1.4497 | 181.2516 | 446.9568 | 0.31492
3513 | 1138.5176 | 7.1695 | 108.9063 | 171.4702 | 55.32 | 18.0354 | 152.2189 | 4.3264 | 16.652 | 86.1271 | 168.3782 | 41.5228 | 318.2954 | 275.2062 | 520.9881 | 36.4213 | 97.4176 | 17.0643 | 394 | 2.7473 | 201.349 | 499.2721 | 0.28685
3514 | 1165.2312 | 10.6067 | 109.5504 | 195.123 | 53.8287 | 19.4522 | 146.9277 | 3.9568 | 19.664 | 87.6264 | 175.1581 | 42.6108 | 389.5704 | 302.2134 | 584.7616 | 38.5916 | 103.8047 | 17.6884 | 378 | 2.8473 | 214.4991 | 521.4288 | 0.32744
3515 | 1213.3619 | 10.7392 | 111.5329 | 182.6167 | 55.4445 | 17.9172 | 138.3006 | 3.884 | 21.2857 | 86.9622 | 181.7016 | 40.9745 | 435.5474 | 317.2476 | 596.4667 | 39.5211 | 106.1452 | 18.35 | 363 | 2.8742 | 215.3292 | 527.5282 | 0.25195
3516 | 1202.4608 | 5.9383 | 112.9021 | 180.5766 | 57.1025 | 16.3421 | 147.2179 | 4.1232 | 19.9622 | 80.3206 | 184.577 | 36.5691 | 469.1315 | 322.7858 | 592.3109 | 39.9634 | 105.6833 | 18.8233 | 405 | 2.9091 | 209.0357 | 534.7446 | 0.27124
3517 | 1208.3436 | 3.9439 | 114.136 | 180.3042 | 55.7354 | 17.6408 | 158.6255 | 4.5587 | 17.116 | 79.336 | 186.0636 | 38.3152 | 487.6299 | 328.68 | 583.2653 | 39.9688 | 103.9743 | 19.2099 | 313 | 1.729 | 216.997 | 543.8613 | 0.27386
3518 | 1179.673 | 3.9728 | 115.393 | 184.1135 | 53.7943 | 19.4848 | 181.0425 | 4.1954 | 17.1899 | 85.5042 | 188.5072 | 39.787 | 497.45 | 336.2728 | 575.5292 | 39.6223 | 103.3331 | 18.8895 | 301 | 2.3287 | 217.2636 | 534.4484 | 0.29296
3519 | 1141.1951 | 4.0149 | 112.2446 | 158.4101 | 56.3314 | 17.0746 | 171.3195 | 3.7615 | 17.6272 | 82 | 185.7545 | 39.7021 | 493.1576 | 335.1244 | 563.688 | 37.8234 | 102.8074 | 18.5126 | 285 | 0.34307 | 206.5388 | 515.349 | 0.28562
3520 | 1124.1813 | 4.1293 | 110.4487 | 186.738 | 58.8524 | 14.6797 | 161.7935 | 3.3519 | 16.8463 | 68.2097 | 180.8181 | 39.0284 | 481.9884 | 323.5491 | 533.1814 | 28.975 | 100.4269 | 18.8661 | 297 | -2.277 | 187.3527 | 481.1858 | 0.21524
3521 | 1081.6158 | 3.5553 | 103.486 | 124.6245 | 63.621 | 10.1495 | 149.4479 | 2.354 | 15.8897 | 55.1537 | 170.9105 | 36.5111 | 470.6208 | 269.0617 | 482.4971 | 15.3971 | 95.6176 | 17.9528 | 270 | -3.267 | 157.0463 | 416.9038 | 0.22775
3522 | 1014.0513 | 2.7399 | 98.8699 | 142.2507 | 63.8709 | 9.9121 | 130.7905 | 1.5312 | 15.4838 | 49.642 | 142.865 | 29.5556 | 446.3925 | 191.7496 | 422.2572 | 9.346 | 90.0481 | 16.7491 | 251 | -3.3378 | 140.7134 | 353.7954 | 0.12547
3523 | 961.9491 | 1.9518 | 90.8533 | 94.2865 | 66.1603 | 7.7372 | 103.193 | 1.4832 | 14.6783 | 46.612 | 112.8413 | 15.4686 | 412.4548 | 155.1422 | 365.8865 | 8.959 | 85.2912 | 16.2523 | 228 | -3.3406 | 125.2353 | 305.8293 | 0.036266
3524 | 927.8474 | 1.3549 | 78.4168 | 96.6716 | 66.5572 | 7.3601 | 89.4325 | 2.0541 | 10.3195 | 41.2298 | 101.0196 | 10.0942 | 368.0774 | 147.1768 | 323.6293 | 8.5807 | 80.6519 | 16.0074 | 221 | -3.3469 | 114.9276 | 272.3594 | 0.0072991
3525 | 899.6034 | 2.5347 | 79.3996 | 96.0332 | 66.3376 | 7.5687 | 92.8432 | 1.7873 | 7.3167 | 33.5491 | 98.0389 | 10.5333 | 332.0186 | 136.076 | 287.5304 | 8.6999 | 76.8031 | 15.0101 | 197 | -3.3524 | 107.5554 | 261.6584 | 0
3526 | 862.3542 | 2.8186 | 66.825 | 102.5302 | 65.5263 | 8.3395 | 85.4613 | 2.4082 | 6.1113 | 29.0993 | 92.3871 | 12.1088 | 294.2509 | 119.0549 | 269.3373 | 9.195 | 75.4085 | 14.2585 | 171 | -3.348 | 96.7724 | 263.6894 | 0
3527 | 828.2982 | 1.9751 | 51.9121 | 76.8361 | 66.1118 | 7.7833 | 84.5056 | 3.0526 | 5.9373 | 28.7146 | 84.0127 | 13.2388 | 257.4305 | 106.5241 | 253.8927 | 9.0858 | 75.5532 | 13.9093 | 157 | -3.3194 | 70.1171 | 267.6926 | 0
3528 | 820.3601 | 1.3347 | 48.8929 | 44.8038 | 66.3404 | 7.566 | 76.857 | 2.4631 | 5.9489 | 29.2033 | 79.5124 | 13.4802 | 244.0759 | 100.6101 | 247.183 | 8.8027 | 75.6757 | 13.497 | 137 | -3.296 | 59.9373 | 264.4409 | 0
3529 | 815.2502 | 1.2657 | 48.7626 | 85.412 | 65.441 | 8.4206 | 63.6603 | 2.8097 | 6.1233 | 29.3837 | 77.6581 | 12.8333 | 236.0075 | 96.4477 | 244.2845 | 9.1119 | 75.5784 | 13.9303 | 129 | -3.3052 | 58.6923 | 259.509 | 0
3530 | 808.0157 | 1.2786 | 48.6805 | 50.3779 | 66.0631 | 7.8295 | 63.0293 | 3.2355 | 6.3488 | 29.4128 | 75.0672 | 9.9711 | 221.6953 | 93.2613 | 238.5023 | 8.8649 | 75.3849 | 13.754 | 125 | -3.3342 | 57.8291 | 259.527 | 0
3531 | 810.4192 | 1.676 | 48.5615 | 87.5177 | 66.335 | 7.5712 | 61.6548 | 2.3279 | 6.1289 | 31.0949 | 73.8337 | 8.7463 | 213.5801 | 91.5978 | 234.875 | 8.9505 | 75.2262 | 13.6447 | 118 | -3.3271 | 56.4633 | 261.3502 | 0
3532 | 813.9889 | 1.8539 | 48.0137 | 71.0981 | 66.2467 | 7.6551 | 64.2522 | 2.6518 | 6.0168 | 36.6085 | 72.2883 | 7.4707 | 208.4525 | 89.9848 | 228.9525 | 8.9166 | 74.7708 | 13.311 | 116 | -3.3094 | 54.7882 | 266.7576 | 0
3533 | 839.7309 | 1.6391 | 62.7351 | 58.2887 | 64.7999 | 9.0295 | 63.9421 | 3.1207 | 5.5824 | 43.2144 | 69.3831 | 7.5563 | 203.4497 | 95.0483 | 224.0186 | 8.6033 | 74.0042 | 12.2611 | 119 | -3.3028 | 58.9606 | 275.6575 | 0.021137
3534 | 896.4799 | 2.0002 | 75.5357 | 98.826 | 63.6349 | 10.1363 | 76.4022 | 1.9647 | 5.1559 | 51.217 | 72.8428 | 13.594 | 222.2462 | 114.4432 | 231.6462 | 11.9681 | 73.6629 | 11.6712 | 193 | -3.1696 | 94.892 | 311.9675 | 0.03583
3535 | 963.6578 | 2.99 | 89.9636 | 134.5422 | 59.6291 | 13.9418 | 108.7942 | 2.974 | 7.639 | 54.779 | 101.6722 | 25.7568 | 260.1149 | 163.6638 | 279.9675 | 23.736 | 77.1448 | 12.4258 | 262 | -0.73869 | 141.7845 | 378.4176 | 0.054023
3536 | 1040.5377 | 3.4665 | 106.0911 | 152.9592 | 58.2745 | 15.2287 | 129.8596 | 3.9168 | 14.4505 | 49.3504 | 142.819 | 32.8791 | 285.7709 | 235.4995 | 391.1708 | 34.4063 | 86.6599 | 14.7851 | 313 | -0.56415 | 169.2066 | 446.5132 | 0.11081
3537 | 1112.9995 | 3.4765 | 113.379 | 147.2729 | 56.1016 | 17.293 | 138.9396 | 4.6955 | 18.8695 | 47.4781 | 164.5247 | 34.4786 | 365.7031 | 294.3901 | 504.4587 | 38.6003 | 96.8167 | 16.2223 | 349 | -1.1695 | 196.7689 | 500.6903 | 0.10677
3538 | 1169.0144 | 3.4433 | 114.5527 | 197.9713 | 55.3388 | 18.0176 | 141.4803 | 4.9757 | 19.687 | 53.3852 | 172.6667 | 35.5543 | 410.5553 | 337.0444 | 577.882 | 40.8431 | 104.2041 | 17.2851 | 396 | 0.15745 | 214.3638 | 528.5984 | 0.10102
3539 | 1193.2845 | 3.4683 | 115.5298 | 163.989 | 56.0863 | 17.3075 | 139.9531 | 4.815 | 19.8067 | 61.096 | 178.6743 | 37.0412 | 442.362 | 362.4816 | 611.2722 | 38.5574 | 109.2924 | 17.4734 | 361 | 1.0327 | 214.2378 | 541.8532 | 0.11619
3540 | 1180.5442 | 3.5436 | 113.0566 | 198.4115 | 57.1124 | 16.3327 | 141.0483 | 4.9335 | 19.4641 | 63.3413 | 181.8082 | 40.0559 | 467.1961 | 361.0335 | 608.762 | 38.0173 | 110.2411 | 17.381 | 382 | -0.10256 | 209.9481 | 558.9389 | 0.13968
3541 | 1176.6808 | 3.4633 | 111.7118 | 168.1589 | 56.4532 | 16.9589 | 134.0742 | 4.4688 | 18.5205 | 68.1121 | 181.7031 | 41.2537 | 475.0905 | 356.7764 | 601.2968 | 38.963 | 108.5467 | 17.6434 | 336 | -1.0017 | 210.5294 | 560.7321 | 0.19431
3542 | 1160.1144 | 3.3885 | 114.9716 | 207.6159 | 53.9713 | 19.3167 | 130.8869 | 4.3351 | 17.3537 | 76.3029 | 181.2729 | 40.2429 | 476.0369 | 358.1598 | 610.752 | 38.8207 | 106.2243 | 17.6036 | 312 | -1.3134 | 210.3971 | 550.7183 | 0.17482
3543 | 1126.7587 | 3.1491 | 115.9533 | 190.0089 | 59.3586 | 14.1988 | 131.3463 | 4.3878 | 17.135 | 73.0342 | 180.6833 | 39.5342 | 459.6176 | 352.8778 | 595.3591 | 37.9646 | 103.0888 | 17.7077 | 324 | -2.5019 | 202.8776 | 538.2922 | 0.15014
3544 | 1073.1483 | 3.3421 | 110.0871 | 168.7965 | 62.0606 | 11.6319 | 121.9769 | 4.3178 | 16.7086 | 63.3633 | 176.9689 | 37.6167 | 442.0192 | 326.3064 | 534.192 | 24.379 | 98.941 | 17.5946 | 304 | -3.121 | 181.4292 | 480.893 | 0.15175
3545 | 1014.9824 | 2.5637 | 94.1801 | 140.4902 | 65.1881 | 8.6608 | 119.2241 | 2.9185 | 16.4672 | 50.734 | 166.0076 | 36.4931 | 425.8886 | 258.7964 | 458.2312 | 13.0175 | 93.0549 | 17.4253 | 288 | -3.2598 | 157.8122 | 393.9128 | 0.19103
3546 | 968.6566 | 1.9497 | 78.3766 | 93.7203 | 66.2699 | 7.633 | 97.4529 | 1.9543 | 16.8293 | 36.1574 | 137.9674 | 30.6736 | 385.9765 | 183.5802 | 393.0495 | 10.0411 | 85.9075 | 17.1098 | 266 | -3.2729 | 135.525 | 333.3986 | 0.18227
3547 | 932.8278 | 1.7201 | 74.0035 | 91.3993 | 64.9509 | 8.8861 | 67.3148 | 1.5308 | 15.9895 | 28.8462 | 105.1401 | 16.5766 | 352.951 | 146.7482 | 340.9056 | 8.9904 | 79.2617 | 16.4573 | 276 | -3.2432 | 115.7884 | 299.0564 | 0.13318
3548 | 884.4756 | 1.3868 | 51.4164 | 78.2045 | 65.6914 | 8.1826 | 63.0259 | 2.0451 | 11.8975 | 27.5906 | 85.4173 | 11.0444 | 320.6398 | 140.3342 | 297.187 | 8.6115 | 75.0761 | 15.4228 | 290 | -3.2397 | 105.4665 | 277.1759 | 0.066555
3549 | 857.1466 | 2.7536 | 40.4196 | 66.3869 | 66.2823 | 7.6213 | 58.2801 | 2.0208 | 11.7427 | 26.8722 | 74.8185 | 10.4472 | 286.7146 | 136.6591 | 272.5016 | 8.829 | 72.9857 | 14.6303 | 249 | -3.2417 | 99.8059 | 266.9817 | 0
3550 | 840.1691 | 2.9597 | 45.6568 | 67.5667 | 66.2559 | 7.6463 | 60.6442 | 2.5997 | 8.0073 | 27.1591 | 71.9479 | 11.6282 | 266.4791 | 130.1251 | 249.4624 | 9.0425 | 72.2133 | 14.7893 | 217 | -3.2374 | 92.9771 | 268.6098 | 0
3551 | 816.0362 | 1.7316 | 47.4828 | 69.8981 | 66.2909 | 7.6131 | 57.5558 | 3.1742 | 7.031 | 29.0014 | 74.1302 | 11.8137 | 258.2486 | 121.4642 | 249.0076 | 9.5 | 72.5182 | 14.3823 | 197 | -3.2211 | 69.8884 | 265.0627 | 0
3552 | 817.424 | 1.5761 | 47.0441 | 68.887 | 65.6634 | 8.2092 | 59.5491 | 2.4588 | 7.01 | 29.414 | 75.7225 | 9.6833 | 242.059 | 112.4322 | 247.0034 | 9.1309 | 72.6671 | 13.7865 | 187 | -3.222 | 60.4873 | 248.8868 | 0
3553 | 811.6016 | 1.3804 | 46.6353 | 67.9555 | 65.2941 | 8.5601 | 59.5598 | 2.8942 | 6.3316 | 27.9795 | 75.8752 | 8.7685 | 232.8871 | 107.0651 | 250.0031 | 9.4573 | 72.5574 | 13.5477 | 164 | -3.2189 | 56.7562 | 239.1497 | 0
3554 | 812.1702 | 1.2308 | 46.4903 | 69.5079 | 65.3712 | 8.4868 | 59.9761 | 3.321 | 6.133 | 27.4049 | 75.7427 | 8.8147 | 225.1558 | 105.7094 | 256.488 | 9.5929 | 72.6162 | 13.623 | 159 | -3.2076 | 53.6669 | 241.5268 | 0
3555 | 817.1881 | 1.1889 | 46.2291 | 43.3602 | 65.3214 | 8.5341 | 59.9654 | 2.9582 | 5.853 | 27.5882 | 76.3213 | 8.5623 | 218.519 | 105.3764 | 256.472 | 9.0077 | 72.479 | 13.0849 | 148 | -3.1915 | 50.7515 | 243.7938 | 0
3556 | 818.6982 | 1.2523 | 46.3274 | 64.3603 | 66.7059 | 7.2189 | 57.8206 | 2.273 | 5.6828 | 29.1568 | 75.7015 | 6.9114 | 205.7472 | 101.709 | 245.1168 | 8.5438 | 72.1383 | 12.5845 | 135 | -3.1807 | 48.9443 | 232.1194 | 0
3557 | 812.5812 | 1.0192 | 45.7431 | 63.6105 | 65.8155 | 8.0647 | 61.2753 | 2.5634 | 5.4953 | 32.6369 | 72.3876 | 5.9174 | 198.167 | 95.3108 | 229.1697 | 8.7876 | 71.7113 | 11.9927 | 135 | -3.2061 | 48.7719 | 219.8235 | 0.058443
3558 | 831.8736 | 0.80424 | 49.4733 | 85.7747 | 66.026 | 7.8648 | 62.3533 | 3.0535 | 5.0821 | 36.4659 | 69.417 | 5.0862 | 195.2536 | 92.0787 | 226.1856 | 8.5768 | 71.4366 | 11.7769 | 136 | -3.2007 | 49.6944 | 219.4126 | 0.068919
3559 | 849.5683 | 1.0618 | 55.2778 | 78.1239 | 65.5182 | 8.3472 | 88.3307 | 2.112 | 5.001 | 38.5877 | 71.48 | 6.4936 | 191.7548 | 96.9434 | 222.9242 | 8.4228 | 71.294 | 12.0632 | 136 | -3.2148 | 51.4642 | 225.3355 | 0.18017
3560 | 864.455 | 1.0564 | 67.1229 | 86.6341 | 65.4196 | 8.4408 | 112.1682 | 2.312 | 5.2132 | 41.5653 | 89.2277 | 15.2987 | 200.6959 | 108.3588 | 221.862 | 8.4737 | 71.1382 | 13.0202 | 157 | -3.229 | 59.0367 | 229.1706 | 0.18985
3561 | 885.6132 | 1.0862 | 85.9129 | 104.9141 | 66.0158 | 7.8744 | 106.6913 | 1.9632 | 5.3739 | 45.9192 | 117.4589 | 20.2926 | 227.2668 | 121.8372 | 231.0283 | 8.7135 | 71.7811 | 13.9941 | 170 | -3.2463 | 83.5621 | 233.2814 | 0.13994
3562 | 927.2749 | 1.3522 | 96.7642 | 116.7043 | 65.4795 | 8.3839 | 105.947 | 1.5952 | 5.2254 | 46.9334 | 132.5187 | 21.2762 | 250.0403 | 133.5388 | 246.8316 | 8.4878 | 73.9992 | 15.086 | 205 | -3.1476 | 95.9109 | 238.9061 | 0.20902
3563 | 938.0404 | 1.8537 | 96.3271 | 95.4665 | 66.0554 | 7.8368 | 115.9897 | 1.656 | 5.2412 | 44.9219 | 121.9589 | 19.4345 | 267.5304 | 144.1395 | 264.9849 | 8.3944 | 76.0159 | 15.9102 | 210 | -2.8994 | 98.6124 | 241.059 | 0.21264
3564 | 938.7432 | 1.4944 | 95.2185 | 121.2608 | 65.5771 | 8.2912 | 123.8106 | 2.3394 | 5.3524 | 40.5294 | 101.8475 | 18.4405 | 277.8918 | 153.0721 | 270.361 | 8.3994 | 75.5168 | 16.3554 | 222 | -3.1361 | 103.7569 | 239.0672 | 0.21203
3565 | 918.8813 | 1.4606 | 95.2261 | 120.6252 | 65.3465 | 8.5103 | 130.7856 | 2.7109 | 7.508 | 37.8694 | 93.9769 | 22.2153 | 280.9974 | 155.5795 | 266.1246 | 8.8457 | 73.618 | 16.3395 | 214 | -3.2625 | 104.8871 | 235.988 | 0.23113
3566 | 909.171 | 1.171 | 85.6118 | 126.4451 | 65.3082 | 8.5467 | 137.6795 | 2.197 | 10.9811 | 37.217 | 94.8246 | 24.6375 | 279.6708 | 155.2698 | 270.1254 | 8.4597 | 72.4207 | 16.3313 | 210 | -3.2839 | 105.4215 | 235.2355 | 0.22179
3567 | 902.0051 | 1.0263 | 78.8122 | 107.3909 | 66.7426 | 7.184 | 142.0253 | 1.6834 | 12.1778 | 31.3463 | 97.1567 | 21.1432 | 272.3775 | 156.8345 | 293.8725 | 8.271 | 72.5872 | 16.6683 | 199 | -3.301 | 99.772 | 234.4548 | 0.23731
3568 | 878.7709 | 0.97229 | 61.8951 | 85.5981 | 66.5817 | 7.3368 | 140.2068 | 1.5673 | 11.5771 | 23.9958 | 99.53 | 20.1632 | 274.5932 | 155.3197 | 320.6937 | 8.7047 | 73.9198 | 16.8317 | 187 | -3.3006 | 77.1997 | 236.0609 | 0.1518
3569 | 866.0452 | 1.2686 | 54.032 | 52.8494 | 65.6674 | 8.2055 | 135.8237 | 1.6866 | 7.3834 | 21.3931 | 97.7774 | 18.5033 | 283.0346 | 148.5305 | 322.4967 | 8.6522 | 74.1957 | 16.413 | 194 | -3.2865 | 66.2089 | 240.5217 | 0.16794
3570 | 861.7546 | 1.2738 | 53.5952 | 94.1306 | 66.7818 | 7.1467 | 125.4643 | 1.6166 | 6.3502 | 21.7768 | 89.1956 | 10.3973 | 299.2676 | 143.2345 | 292.8912 | 8.6504 | 72.6992 | 15.6191 | 186 | -3.283 | 65.5378 | 237.4003 | 0.085935
3571 | 840.5257 | 1.3211 | 53.5324 | 80.6025 | 66.5295 | 7.3864 | 99.9283 | 1.5434 | 6.9283 | 21.0769 | 80.1563 | 5.976 | 302.0246 | 140.8959 | 267.779 | 8.4024 | 71.4581 | 14.7657 | 186 | -3.2601 | 66.9592 | 228.8845 | 0.081706
3572 | 829.6898 | 1.4205 | 53.2645 | 51.7662 | 66.3281 | 7.5777 | 64.7967 | 2.2039 | 6.2015 | 18.4821 | 76.2659 | 5.4113 | 276.0127 | 144.1642 | 271.8423 | 8.5719 | 71.0559 | 14.1876 | 182 | -3.2144 | 64.5061 | 222.7693 | 0.019938
3573 | 819.6463 | 2.7874 | 53.28 | 92.612 | 66.252 | 7.6501 | 55.4402 | 2.0894 | 5.7385 | 17.4283 | 74.8038 | 5.4075 | 259.9988 | 146.7155 | 273.5384 | 8.9443 | 70.833 | 13.5719 | 170 | -3.2268 | 60.1165 | 222.4048 | 0
3574 | 812.2456 | 2.7771 | 53.5553 | 55.9631 | 65.5668 | 8.301 | 53.9333 | 2.5889 | 5.9628 | 19.7357 | 74.7549 | 7.0201 | 251.1399 | 140.6215 | 265.1941 | 8.762 | 70.9202 | 13.3313 | 155 | -3.2437 | 56.4929 | 236.1228 | 0
3575 | 791.8158 | 1.8856 | 53.7743 | 77.2043 | 65.3097 | 8.5453 | 54.9632 | 2.6172 | 6.6198 | 22.2169 | 75.1843 | 7.9614 | 242.9633 | 129.0146 | 264.369 | 8.8935 | 71.4827 | 13.3485 | 161 | -3.2336 | 52.364 | 249.8692 | 0
3576 | 784.7756 | 1.5282 | 53.8469 | 76.361 | 66.0126 | 7.8775 | 54.1807 | 2.9421 | 6.4737 | 22.3882 | 74.3624 | 8.0951 | 227.946 | 113.8014 | 262.5518 | 9.1675 | 71.9008 | 13.0284 | 156 | -3.2303 | 50.8155 | 250.714 | 0
3577 | 787.1511 | 1.2638 | 53.9192 | 94.9612 | 66.3074 | 7.5974 | 56.5278 | 2.4973 | 9.3992 | 21.2868 | 73.346 | 7.4028 | 216.4743 | 102.4733 | 260.5645 | 9.1291 | 72.2126 | 12.5523 | 154 | -3.2008 | 50.9175 | 243.9699 | 0
3578 | 764.2141 | 1.2369 | 53.3824 | 82.8399 | 66.3251 | 7.5806 | 56.2106 | 2.7782 | 9.0545 | 20.5912 | 72.5095 | 7.1291 | 208.7625 | 97.9487 | 254.001 | 9.0168 | 72.4296 | 11.9894 | 143 | -3.1845 | 48.5169 | 233.7036 | 0
3579 | 770.5794 | 1.2111 | 54.2427 | 54.0474 | 66.3382 | 7.5682 | 54.3471 | 2.4806 | 11.0431 | 20.3023 | 72.3677 | 6.9298 | 206.7041 | 95.4374 | 249.4768 | 9.0625 | 72.4072 | 11.5826 | 134 | -3.1844 | 46.733 | 226.0698 | 0
3580 | 779.4449 | 1.5681 | 53.6038 | 75.1735 | 66.2741 | 7.629 | 54.1616 | 2.5655 | 12.736 | 18.1277 | 70.9983 | 5.322 | 207.2123 | 91.525 | 237.5882 | 8.7356 | 71.7122 | 11.5298 | 149 | -3.2156 | 47.3435 | 218.4835 | 0
3581 | 785.7783 | 1.456 | 53.0834 | 73.5776 | 65.5618 | 8.3058 | 53.9274 | 2.0956 | 11.4653 | 15.9579 | 68.0902 | 4.1895 | 210.9818 | 89.6923 | 224.1436 | 8.6904 | 71.0823 | 11.3989 | 131 | -3.2548 | 46.4358 | 208.9231 | 0.035284
3582 | 802.7165 | 0.94286 | 54.3801 | 91.4491 | 65.276 | 8.5773 | 55.3481 | 2.6502 | 6.803 | 16.5452 | 66.8366 | 4.0037 | 212.5189 | 93.5985 | 224.0847 | 8.4366 | 70.9106 | 11.3239 | 133 | -3.2588 | 46.4346 | 203.7187 | 0.078388
3583 | 819.9627 | 0.82457 | 62.652 | 88.0574 | 65.3285 | 8.5274 | 52.5289 | 2.2142 | 7.6373 | 16.4273 | 67.2392 | 4.0668 | 209.0898 | 98.6314 | 228.0168 | 8.4236 | 70.4851 | 11.547 | 135 | -3.2433 | 46.9301 | 203.9095 | 0.23754
3584 | 839.6518 | 0.78525 | 73.705 | 69.0756 | 66.0754 | 7.8178 | 74.9429 | 1.6295 | 6.1774 | 18.776 | 67.9223 | 5.9733 | 203.0479 | 108.267 | 237.841 | 8.9883 | 70.2379 | 12.6708 | 150 | -3.2635 | 51.3417 | 201.4316 | 0.26706
3585 | 855.3969 | 0.91407 | 77.2151 | 116.7883 | 66.2431 | 7.6585 | 96.9398 | 1.6558 | 6.7181 | 23.4021 | 68.7116 | 15.748 | 214.019 | 127.959 | 248.498 | 8.6638 | 70.5553 | 13.4204 | 200 | -3.2601 | 55.107 | 194.7637 | 0.27278
3586 | 873.5125 | 3.699 | 77.2151 | 107.1394 | 65.6313 | 8.2397 | 115.9053 | 1.5978 | 11.0652 | 27.4029 | 73.9284 | 18.0513 | 244.3565 | 143.1083 | 254.3157 | 8.2237 | 70.843 | 14.2876 | 212 | -3.2263 | 58.1278 | 192.0734 | 0.27553
3587 | 879.2128 | 5.0531 | 79.2349 | 103.0421 | 66.0142 | 7.876 | 116.0777 | 1.5493 | 12.5807 | 33.6302 | 83.8302 | 15.0767 | 283.1779 | 146.9457 | 272.8273 | 8.6897 | 70.9096 | 15.1845 | 234 | -3.2124 | 60.8487 | 190.8802 | 0.23657
3588 | 881.0925 | 3.0253 | 79.8296 | 104.7053 | 64.8172 | 9.0131 | 124.8813 | 1.5341 | 10.7026 | 33.6455 | 91.4459 | 19.0785 | 308.0238 | 150.3475 | 303.6594 | 8.5374 | 71.2712 | 15.2183 | 252 | -3.2242 | 61.9368 | 189.0639 | 0.24139
3589 | 891.4461 | 1.355 | 79.2658 | 105.5087 | 65.0749 | 8.7683 | 133.5084 | 1.75 | 12.1787 | 28.5853 | 96.2182 | 23.4899 | 324.6246 | 159.0932 | 319.0954 | 8.8014 | 72.306 | 15.3275 | 251 | -3.222 | 64.1808 | 190.819 | 0.20297
3590 | 921.9562 | 1.1413 | 79.4199 | 104.6517 | 65.3783 | 8.4801 | 121.886 | 1.6768 | 13.9013 | 26.7828 | 99.4772 | 22.736 | 351.4083 | 176.2999 | 322.3151 | 9.0096 | 74.6268 | 15.7036 | 241 | -3.2362 | 65.1667 | 193.3637 | 0.23794
3591 | 927.9083 | 1.4921 | 77.9822 | 101.6488 | 65.9384 | 7.948 | 130.3829 | 1.3674 | 14.117 | 26.1854 | 99.5568 | 19.9956 | 361.7817 | 191.2287 | 314.3954 | 9.026 | 76.1947 | 15.7182 | 209 | -3.2239 | 68.806 | 193.5634 | 0.22308
3592 | 910.1282 | 2.3099 | 61.8863 | 85.0983 | 65.5704 | 8.2976 | 146.4573 | 1.2652 | 14.6745 | 24.4885 | 97.6266 | 21.201 | 354.3443 | 190.296 | 308.9035 | 8.7863 | 75.0551 | 15.8151 | 224 | -3.2388 | 70.4683 | 192.9383 | 0.2436
3593 | 905.8155 | 2.2979 | 53.9203 | 76.5375 | 67.5137 | 6.4515 | 140.6503 | 1.2759 | 13.776 | 24.1444 | 95.8724 | 23.7268 | 325.2529 | 186.9755 | 311.889 | 8.4776 | 73.3459 | 16.2347 | 207 | -3.2629 | 68.6149 | 188.7969 | 0.13214
3594 | 899.9296 | 2.0207 | 53.4059 | 75.3001 | 66.8059 | 7.1238 | 139.093 | 1.2629 | 13.2286 | 25.4667 | 95.3328 | 18.7848 | 303.4253 | 183.8753 | 308.3253 | 8.3883 | 72.5834 | 16.473 | 189 | -3.2547 | 66.9442 | 185.6952 | 0.07589
3595 | 862.8885 | 1.8733 | 57.7824 | 54.5377 | 66.3183 | 7.5871 | 105.3077 | 1.2651 | 13.0086 | 24.2405 | 94.9198 | 10.8694 | 296.7873 | 163.5224 | 300.231 | 8.7274 | 72.0122 | 15.98 | 188 | -3.2276 | 62.5555 | 189.3966 | 0.025477
3596 | 842.0432 | 1.2446 | 59.7098 | 82.7474 | 66.3599 | 7.5475 | 89.8392 | 1.4545 | 8.6942 | 21.6493 | 89.1796 | 15.0547 | 294.6898 | 139.3494 | 284.1563 | 8.8258 | 71.457 | 15.1319 | 156 | -3.2157 | 59.7369 | 193.1259 | 0.0063387
3597 | 823.3794 | 2.4614 | 62.0284 | 102.3767 | 66.2518 | 7.6503 | 89.0216 | 2.2049 | 6.1778 | 19.9277 | 81.0631 | 17.3065 | 285.098 | 131.4794 | 270.0949 | 8.6409 | 71.3272 | 14.2223 | 148 | -3.2228 | 57.6363 | 190.5336 | 0
3598 | 797.4693 | 2.838 | 63.2607 | 70.587 | 66.317 | 7.5883 | 76.9265 | 2.4677 | 5.7718 | 18.776 | 79.69 | 11.7741 | 241.8403 | 129.432 | 258.6768 | 8.9132 | 71.5269 | 14.2861 | 142 | -3.2064 | 53.6774 | 190.9157 | 0
3599 | 788.2569 | 1.6427 | 62.7243 | 105.284 | 66.2822 | 7.6214 | 61.9614 | 2.1059 | 6.4646 | 18.185 | 80.302 | 9.3851 | 208.2725 | 121.4524 | 246.5081 | 9.7568 | 71.3234 | 13.9406 | 132 | -3.2471 | 53.3206 | 196.577 | 0
3600 | 784.4936 | 1.1219 | 63.3366 | 95.3726 | 66.2422 | 7.6594 | 62.3565 | 1.9573 | 6.1835 | 18.4309 | 78.1303 | 9.2825 | 195.0187 | 110.6044 | 234.1603 | 12.3817 | 70.7338 | 13.8534 | 125 | -3.2569 | 51.9843 | 198.6232 | 0
3601 | 769.0747 | 1.2237 | 64.0099 | 71.1623 | 65.5701 | 8.2979 | 58.2651 | 1.9535 | 6.3435 | 18.128 | 75.799 | 9.1563 | 188.8208 | 102.3165 | 231.2854 | 13.1137 | 70.4314 | 13.8607 | 128 | -3.2471 | 49.5098 | 198.1712 | 0
3602 | 751.6592 | 1.1863 | 63.9742 | 112.1349 | 66.1103 | 7.7847 | 61.9536 | 2.5908 | 6.327 | 17.0866 | 74.0371 | 10.6805 | 196.9707 | 98.1124 | 236.7629 | 12.8856 | 70.4333 | 13.5783 | 127 | -3.2343 | 47.9073 | 198.1215 | 0
3603 | 762.5665 | 1.1314 | 64.4417 | 99.7152 | 66.3462 | 7.5606 | 60.8483 | 2.3358 | 5.8172 | 18.1731 | 73.5899 | 16.1072 | 213.4807 | 95.1549 | 239.6495 | 13.5061 | 70.6109 | 13.4685 | 128 | -3.2423 | 67.701 | 199.2811 | 0
3604 | 772.6073 | 1.1115 | 63.1846 | 90.5142 | 66.2853 | 7.6184 | 59.3608 | 2.1819 | 5.6319 | 23.8936 | 71.107 | 14.3364 | 240.3045 | 90.7282 | 229.4731 | 11.9531 | 70.5684 | 13.3072 | 124 | -3.2409 | 92.9542 | 201.4877 | 0
3605 | 781.0022 | 0.92835 | 61.2595 | 62.8191 | 65.5872 | 8.2817 | 60.51 | 2.3388 | 5.5412 | 30.9257 | 67.0752 | 10.4051 | 278.523 | 95.8877 | 224.8516 | 9.3745 | 70.0854 | 12.9264 | 124 | -3.2597 | 96.5587 | 208.2673 | 0.019468
3606 | 824.9648 | 1.8149 | 63.796 | 105.6154 | 63.7743 | 10.0039 | 67.2769 | 1.8261 | 5.4248 | 39.7922 | 77.1242 | 15.0387 | 296.8394 | 130.9297 | 248.0501 | 11.8776 | 70.0998 | 13.2694 | 189 | -3.2016 | 102.0737 | 242.7342 | 0.093539
3607 | 892.9045 | 3.3366 | 87.5822 | 124.5645 | 58.9275 | 14.6084 | 104.1619 | 2.2892 | 7.2897 | 55.5194 | 109.948 | 24.6171 | 320.4096 | 184.5704 | 307.8857 | 23.4371 | 73.4767 | 13.8467 | 320 | -1.5617 | 131.6805 | 307.5634 | 0.1893
3608 | 978.4544 | 4.0433 | 109.0405 | 155.7202 | 66.1024 | 7.7922 | 133.6002 | 3.2389 | 15.728 | 68.1081 | 146.1532 | 30.9639 | 371.7952 | 233.758 | 403.2584 | 31.7202 | 82.1325 | 14.9141 | 337 | -0.70474 | 158.7157 | 377.9065 | 0.25623
3609 | 1046.6308 | 4.0993 | 115.921 | 177.8761 | 73.0014 | 1.2381 | 158.6096 | 3.7312 | 20.5252 | 71.482 | 166.2948 | 36.9743 | 428.1435 | 268.5687 | 495.8087 | 35.2359 | 92.0902 | 17.9564 | 362 | -1.4709 | 172.7335 | 445.8869 | 0.26002
3610 | 1089.7884 | 4.0215 | 116.938 | 159.1255 | 71.3871 | 2.7717 | 174.0159 | 3.9379 | 21.122 | 73.2036 | 176.3736 | 40.2246 | 507.0134 | 295.0306 | 563.0451 | 35.7121 | 100.697 | 17.666 | 369 | -0.26327 | 181.6407 | 502.4581 | 0.25994
3611 | 1124.0879 | 4.0232 | 124.1067 | 207.7832 | 60.0789 | 13.5145 | 180.3232 | 4.0888 | 21.0145 | 79.4642 | 181.8671 | 39.1369 | 557.3241 | 316.7745 | 589.816 | 35.09 | 106.9282 | 17.8224 | 337 | -0.78165 | 193.3058 | 533.2989 | 0.2339
3612 | 1134.5279 | 3.9629 | 122.9697 | 197.837 | 55.5106 | 17.8544 | 175.3774 | 4.4133 | 20.6957 | 83.6322 | 182.3637 | 39.0865 | 577.1857 | 329.0978 | 591.3466 | 35.1207 | 107.7393 | 18.9275 | 365 | -0.55537 | 194.0988 | 536.7592 | 0.25794
3613 | 1195.2291 | 3.4665 | 121.4324 | 195.862 | 58.1404 | 15.3561 | 186.9878 | 4.5561 | 18.7443 | 82.804 | 185.3674 | 39.2693 | 590.0954 | 334.9619 | 607.1997 | 34.774 | 106.1264 | 19.6853 | 374 | -0.15775 | 193.8571 | 539.9219 | 0.28768
3614 | 1227.0218 | 3.502 | 121.7047 | 175.6579 | 58.5454 | 14.9713 | 201.5566 | 4.1387 | 17.3862 | 84.2528 | 189.5863 | 38.4008 | 608.1806 | 334.9164 | 610.0585 | 34.7191 | 106.0446 | 19.9085 | 303 | 1.8518 | 188.3682 | 547.1025 | 0.27887
3615 | 1223.7893 | 3.9004 | 119.4288 | 216.6352 | 56.9009 | 16.5336 | 198.4549 | 3.5721 | 17.3865 | 86.6293 | 189.2351 | 38.3261 | 606.9989 | 328.6119 | 584.4099 | 34.5108 | 105.5274 | 19.922 | 302 | 0.36343 | 180.9654 | 534.2349 | 0.2258
3616 | 1176.1346 | 3.7134 | 118.4263 | 168.5454 | 59.3693 | 14.1887 | 188.4945 | 2.9032 | 17.5647 | 85.806 | 186.5703 | 37.4318 | 587.8815 | 313.7691 | 543.2681 | 28.5257 | 103.1633 | 19.7907 | 308 | -1.5554 | 168.7629 | 493.0195 | 0.23692
3617 | 1107.5609 | 3.3715 | 115.051 | 131.8412 | 63.9324 | 9.8537 | 170.833 | 2.0039 | 17.2854 | 79.2909 | 176.9511 | 35.7587 | 542.3072 | 259.8115 | 481.9719 | 16.0892 | 97.1063 | 19.4034 | 256 | -2.2664 | 150.4589 | 429.3323 | 0.21119
3618 | 1044.1464 | 2.9654 | 115.0175 | 116.4456 | 66.7543 | 7.1729 | 132.9796 | 1.2461 | 15.7487 | 63.885 | 147.1664 | 30.7079 | 493.0623 | 191.3586 | 418.0543 | 9.8591 | 83.4056 | 19.0494 | 234 | -2.8477 | 137.2222 | 362.122 | 0.21906
3619 | 990.9564 | 2.1032 | 97.735 | 110.2187 | 66.634 | 7.2872 | 85.8246 | 1.1346 | 12.704 | 41.3111 | 112.4246 | 22.0666 | 458.7548 | 162.1345 | 366.7714 | 9.7274 | 68.7741 | 17.7959 | 223 | -3.0249 | 121.7683 | 304.8021 | 0.16828
3620 | 966.5435 | 1.5441 | 53.1359 | 104.6268 | 66.2893 | 7.6147 | 62.9313 | 1.056 | 7.5521 | 25.5781 | 98.2004 | 11.1882 | 408.9341 | 158.4928 | 324.6819 | 9.6915 | 60.7496 | 16.7371 | 207 | -2.9752 | 108.6545 | 271.0306 | 0.077104
3621 | 940.5431 | 2.4334 | 35.299 | 100.7508 | 66.2014 | 7.6981 | 48.8185 | 0.97994 | 5.6908 | 21.3552 | 96.3822 | 6.3537 | 372.8858 | 152.5568 | 300.6298 | 9.6604 | 56.4567 | 15.2903 | 205 | -2.981 | 105.8262 | 255.9034 | 0
3622 | 873.109 | 2.5481 | 35.5352 | 101.3772 | 64.0806 | 9.7129 | 46.8791 | 1.2056 | 5.8813 | 21.1959 | 91.7628 | 6.6445 | 339.7366 | 139.6135 | 274.6522 | 9.9435 | 54.5505 | 14.3207 | 181 | -2.9992 | 100.2986 | 252.728 | 0
3623 | 827.3829 | 1.7175 | 38.6748 | 102.3839 | 64.0621 | 9.7305 | 50.0609 | 1.7074 | 6.0257 | 21.4645 | 86.2566 | 7.6318 | 310.6334 | 127.3403 | 262.8391 | 10.0736 | 54.7391 | 14.0741 | 149 | -2.9967 | 76.1685 | 257.8122 | 0
3624 | 820.0047 | 1.4446 | 39.8469 | 102.1261 | 65.0813 | 8.7623 | 43.9331 | 1.7354 | 6.111 | 20.6463 | 85.4647 | 7.9148 | 286.5443 | 117.0874 | 261.6502 | 10.779 | 54.858 | 13.6573 | 134 | -3.022 | 66.7294 | 259.5685 | 0
3625 | 815.1818 | 1.2401 | 39.9976 | 101.0191 | 66.7937 | 7.1355 | 45.5049 | 1.6163 | 6.2052 | 19.3742 | 85.9273 | 7.9787 | 289.0453 | 110.9974 | 259.7494 | 13.0058 | 54.6306 | 13.0347 | 131 | -3.0227 | 62.436 | 258.6764 | 0
3626 | 800.8911 | 1.119 | 39.98 | 99.737 | 67.2573 | 6.695 | 45.6257 | 1.6129 | 6.199 | 18.1012 | 84.8177 | 11.0024 | 295.5897 | 106.7643 | 258.435 | 13.9494 | 54.8131 | 12.6738 | 134 | -3.029 | 73.3595 | 257.0395 | 0
3627 | 806.2155 | 1.1186 | 39.698 | 102.9149 | 65.8083 | 8.0716 | 45.7701 | 1.5418 | 5.9736 | 18.0974 | 83.3723 | 19.0734 | 292.4133 | 100.2251 | 255.8903 | 14.0687 | 54.1564 | 12.6407 | 131 | -3.022 | 81.858 | 256.3447 | 0
3628 | 828.7754 | 1.0333 | 38.7083 | 104.1259 | 65.3494 | 8.5075 | 47.9076 | 1.862 | 5.5916 | 22.0534 | 80.9539 | 17.3709 | 275.9819 | 92.5321 | 246.5724 | 12.7861 | 52.5096 | 12.5179 | 126 | -3.0098 | 96.6497 | 258.4733 | 0
3629 | 847.424 | 1.0337 | 48.0106 | 103.2338 | 66.7951 | 7.1341 | 41.7748 | 1.7893 | 5.456 | 27.247 | 77.6542 | 9.8434 | 283.5931 | 97.426 | 241.4882 | 10.5962 | 51.4416 | 12.375 | 122 | -3.0365 | 105.6151 | 265.9667 | 0.11609
3630 | 865.8922 | 2.2021 | 60.2829 | 104.6059 | 62.9594 | 10.778 | 56.1252 | 1.3531 | 5.2313 | 32.2236 | 81.229 | 12.5825 | 286.0982 | 124.4953 | 244.6043 | 12.8871 | 51.3153 | 12.2476 | 211 | -2.792 | 107.9974 | 295.7754 | 0.153
3631 | 934.4987 | 3.7689 | 90.7332 | 108.9473 | 58.2684 | 15.2345 | 103.4957 | 1.8801 | 7.2483 | 43.3233 | 104.9205 | 23.0411 | 319.6626 | 174.3243 | 296.9716 | 24.3808 | 54.558 | 14.5439 | 256 | -1.0647 | 135.6079 | 357.1319 | 0.22535
3632 | 1031.8207 | 6.3006 | 113.3437 | 127.5921 | 58.8643 | 14.6683 | 121.8354 | 2.9965 | 10.8548 | 55.8304 | 138.2553 | 26.7643 | 375.6965 | 238.8065 | 394.6662 | 32.8032 | 61.9781 | 15.3135 | 305 | 0.024487 | 158.7671 | 433.8637 | 0.14428
3633 | 1103.6606 | 11.2525 | 121.6755 | 141.4672 | 57.8014 | 15.6782 | 132.5054 | 3.5826 | 11.7097 | 59.6082 | 161.3617 | 30.1181 | 448.7435 | 286.5835 | 491.0424 | 36.0686 | 69.3767 | 15.9732 | 357 | 0.31498 | 175.7164 | 495.3705 | 0.17617
3634 | 1141.1452 | 14.0066 | 122.7727 | 146.4506 | 57.9466 | 15.5401 | 145.0811 | 4.4421 | 9.3974 | 59.0122 | 175.0054 | 33.4499 | 479.4223 | 307.3995 | 559.3319 | 37.5768 | 78.1125 | 17.1559 | 366 | 0.58232 | 182.9869 | 524.0891 | 0.30489
3635 | 1149.0124 | 11.519 | 126.8063 | 119.0762 | 56.0637 | 17.3289 | 155.6642 | 4.2943 | 10.6702 | 62.4954 | 184.5047 | 36.1379 | 526.6044 | 319.3754 | 586.1729 | 38.0075 | 91.013 | 17.9515 | 348 | 0.86938 | 187.6625 | 536.2644 | 0.25372
3636 | 1189.088 | 6.1776 | 122.3327 | 184.4233 | 57.5411 | 15.9254 | 166.6018 | 3.6049 | 12.7232 | 65.2948 | 189.9775 | 38.4874 | 571.1795 | 330.3149 | 587.9227 | 38.3777 | 100.2677 | 18.6482 | 382 | 0.4766 | 189.201 | 546.8802 | 0.25477
3637 | 1243.783 | 3.5878 | 119.0028 | 162.7053 | 56.84 | 16.5915 | 169.5871 | 3.6866 | 13.659 | 67.315 | 190.8464 | 39.4235 | 590.5596 | 335.1316 | 588.2873 | 39.3361 | 102.3227 | 19.2351 | 327 | 0.31371 | 186.5895 | 566.0951 | 0.2971
3638 | 1257.111 | 3.4544 | 116.3804 | 114.5897 | 55.8133 | 17.5668 | 182.4318 | 3.4877 | 14.5803 | 73.4515 | 189.9123 | 39.3977 | 589.751 | 336.6599 | 599.7706 | 37.8359 | 101.303 | 19.4988 | 309 | 0.91893 | 194.4922 | 579.5159 | 0.27698
3639 | 1225.3867 | 3.7606 | 114.6484 | 174.9171 | 58.9368 | 14.5995 | 184.3352 | 3.1569 | 14.6287 | 76.9119 | 189.5597 | 38.6025 | 582.6421 | 337.445 | 615.7394 | 35.5563 | 99.5962 | 19.3461 | 296 | 0.89406 | 190.8345 | 565.2689 | 0.31583
3640 | 1194.4463 | 3.9508 | 113.5886 | 143.6284 | 63.8213 | 9.9592 | 178.1645 | 2.8116 | 14.1128 | 74.6372 | 187.8644 | 37.2641 | 564.9533 | 325.5027 | 584.8837 | 28.5021 | 97.3324 | 18.6894 | 291 | 0.20619 | 174.8825 | 499.4898 | 0.19691
3641 | 1117.3422 | 3.1443 | 110.2181 | 117.4196 | 65.3496 | 8.5073 | 172.6934 | 1.9928 | 12.3779 | 67.086 | 177.0869 | 35.7676 | 529.7774 | 284.0541 | 508.435 | 16.1042 | 92.8006 | 18.6079 | 225 | 0.21191 | 154.1428 | 400.3889 | 0.12732
3642 | 996.1489 | 3.7061 | 106.7146 | 111.163 | 65.2502 | 8.6018 | 134.552 | 1.4106 | 12.3709 | 54.535 | 149.0477 | 32.5535 | 496.8226 | 226.7411 | 431.8268 | 9.4095 | 87.2028 | 18.54 | 222 | 0.24435 | 144.9584 | 320.1896 | 0.066459
3643 | 911.3124 | 3.1582 | 94.6781 | 106.2979 | 66.0376 | 7.8537 | 74.4503 | 1.0819 | 12.5339 | 39.204 | 119.3556 | 19.8024 | 448.9355 | 192.3041 | 373.8758 | 8.3815 | 82.59 | 17.6406 | 214 | -0.66115 | 130.5226 | 261.0384 | 0.017893
3644 | 900.1422 | 2.8665 | 57.679 | 100.8678 | 64.0558 | 9.7364 | 46.2733 | 0.95686 | 9.6724 | 27.3666 | 106.841 | 17.3836 | 410.8254 | 180.9876 | 326.3704 | 8.2673 | 79.1287 | 16.7902 | 202 | -1.0624 | 113.0216 | 221.399 | 0.014247
3645 | 905.4994 | 3.0908 | 42.705 | 74.6364 | 65.5063 | 8.3585 | 48.0872 | 1.0204 | 7.4659 | 22.8445 | 101.1183 | 15.3991 | 384.7416 | 167.4203 | 286.1688 | 8.1183 | 75.9317 | 15.7509 | 204 | -1.0905 | 101.6659 | 205.9664 | 0.00049641
3646 | 880.4389 | 2.762 | 44.4266 | 102.7468 | 64.9162 | 8.9191 | 51.9671 | 1.4271 | 6.4436 | 23.1352 | 92.9957 | 18.863 | 360.5189 | 152.0474 | 254.1391 | 8.4092 | 73.722 | 14.5814 | 177 | -1.0871 | 90.9337 | 210.3987 | 0
3647 | 846.6495 | 1.8251 | 45.3721 | 76.7316 | 65.8014 | 8.0781 | 45.4472 | 1.4552 | 6.2362 | 23.9947 | 86.3993 | 23.3157 | 355.9567 | 142.694 | 241.705 | 9.5266 | 73.5815 | 13.5565 | 149 | -1.0698 | 66.1376 | 218.5149 | 0
3648 | 846.2692 | 1.3561 | 44.9143 | 89.5596 | 59.0237 | 8.3603 | 58.4277 | 1.3281 | 6.1475 | 22.2696 | 83.6626 | 24.0769 | 358.1029 | 134.597 | 244.251 | 11.7385 | 73.8898 | 12.9328 | 138 | 10.569 | 58.034 | 217.4559 | 0
3649 | 828.3421 | 1.2637 | 44.7981 | 93.7705 | 59.6179 | 7.7959 | 70.9913 | 1.3603 | 6.0112 | 20.0021 | 83.3136 | 24.0031 | 278.0514 | 126.0653 | 243.0317 | 12.8068 | 73.6307 | 12.6801 | 133 | 10.6045 | 91.6466 | 208.022 | 0
3650 | 824.9841 | 1.17 | 44.7302 | 109.3033 | 59.8046 | 7.6185 | 72.7554 | 1.3775 | 6.093 | 19.3932 | 83.6358 | 26.4199 | 297.4552 | 120.2159 | 240.1548 | 12.665 | 73.0293 | 12.1491 | 128 | 10.612 | 104.0272 | 199.33 | 0
3651 | 819.905 | 1.1168 | 44.6827 | 100.6139 | 59.8079 | 7.6154 | 72.693 | 1.5805 | 6.1295 | 20.9035 | 83.1459 | 32.004 | 274.2975 | 115.6605 | 233.3403 | 12.2882 | 72.1627 | 11.6618 | 127 | 10.5934 | 102.8777 | 195.2788 | 0
3652 | 830.372 | 1.225 | 44.2035 | 76.3207 | 59.8001 | 7.6228 | 73.0712 | 1.2161 | 6.0653 | 25.0111 | 81.3753 | 25.7583 | 246.0652 | 112.0225 | 223.9339 | 11.1296 | 71.3194 | 11.3794 | 124 | 10.5982 | 103.6147 | 190.7447 | 0
3653 | 856.707 | 1.3789 | 48.5652 | 109.9644 | 58.3587 | 8.9921 | 72.836 | 0.91159 | 5.6166 | 29.7493 | 80.1501 | 13.3031 | 258.0625 | 113.4095 | 219.1083 | 9.1216 | 70.6261 | 11.3059 | 144 | 10.5767 | 97.733 | 196.8345 | 0.052064
3654 | 898.4929 | 2.1538 | 56.3946 | 107.9551 | 57.0618 | 10.2242 | 84.0847 | 0.94549 | 5.1891 | 33.7538 | 85.4798 | 14.3159 | 240.1867 | 132.1698 | 241.1435 | 11.5495 | 70.4484 | 11.2545 | 195 | 10.2802 | 94.6677 | 233.7233 | 0.058633
3655 | 953.9022 | 3.2455 | 82.2783 | 117.6585 | 53.9683 | 13.163 | 118.9893 | 1.8421 | 7.498 | 36.4452 | 109.3276 | 26.7074 | 313.0696 | 180.2669 | 308.2975 | 21.354 | 73.4959 | 11.6584 | 260 | 12.2466 | 119.4831 | 302.7629 | 0.12875
3656 | 1009.1804 | 3.7774 | 103.6994 | 188.7073 | 52.0324 | 15.002 | 145.7371 | 3.0714 | 13.8095 | 36.6467 | 143.4085 | 28.8595 | 340.2433 | 236.3713 | 396.0466 | 28.4133 | 81.6944 | 13.5045 | 304 | 11.5361 | 146.9804 | 383.3577 | 0.17321
3657 | 1104.6328 | 3.7125 | 111.1838 | 162.6852 | 51.9387 | 15.0911 | 159.3766 | 4.2164 | 16.6807 | 40.3438 | 168.1554 | 30.3501 | 441.5401 | 277.4084 | 482.5551 | 29.5084 | 93.2406 | 15.8169 | 330 | 11.6954 | 168.2188 | 447.6167 | 0.19502
3658 | 1145.0669 | 3.7118 | 112.1998 | 146.8406 | 50.9819 | 16.0001 | 180.5444 | 3.9734 | 16.9659 | 50.3496 | 180.5257 | 33.1141 | 465.7022 | 308.7167 | 536.6951 | 28.9583 | 103.4173 | 16.9505 | 371 | 11.9142 | 177.7662 | 473.3097 | 0.13484
3659 | 1163.8639 | 3.8121 | 112.1998 | 148.9181 | 51.3172 | 15.6815 | 181.9362 | 3.7846 | 16.9641 | 55.531 | 182.9979 | 33.7334 | 498.9508 | 334.1878 | 549.1302 | 29.0113 | 107.9513 | 17.6845 | 349 | 11.7193 | 184.72 | 477.9207 | 0.23459
3660 | 1179.1561 | 3.9205 | 111.3641 | 152.8026 | 50.3331 | 16.6164 | 193.607 | 3.9468 | 16.8488 | 53.2287 | 182.4245 | 32.4843 | 524.9728 | 345.8288 | 554.7467 | 29.5052 | 106.9633 | 17.6458 | 389 | 12.0348 | 188.0425 | 476.8887 | 0.20288
3661 | 1234.9573 | 3.5027 | 110.2973 | 166.535 | 49.1136 | 17.7749 | 197.669 | 3.7629 | 15.701 | 54.3061 | 186.0728 | 29.8448 | 548.079 | 350.8797 | 556.4415 | 30.1597 | 104.9348 | 17.9226 | 341 | 11.8763 | 186.3174 | 476.1945 | 0.2628
3662 | 1238.0927 | 6.3557 | 110.5522 | 161.8646 | 49.0533 | 17.8322 | 192.8373 | 3.6801 | 15.657 | 57.9884 | 187.967 | 31.592 | 559.8126 | 352.8089 | 565.1482 | 30.32 | 104.7017 | 18.4194 | 311 | 13.4891 | 184.2463 | 492.8586 | 0.21927
3663 | 1209.1033 | 9.8296 | 109.1783 | 153.3415 | 50.998 | 15.9847 | 200.3619 | 3.3254 | 15.4654 | 57.4284 | 184.8034 | 33.2353 | 551.6415 | 349.8908 | 570.0823 | 29.7277 | 103.7851 | 17.8315 | 295 | 13.0089 | 176.7627 | 505.0695 | 0.19666
3664 | 1175.0181 | 8.5193 | 106.9933 | 109.4637 | 54.6313 | 12.5331 | 238.0858 | 2.8611 | 14.7005 | 54.9568 | 182.3816 | 32.0807 | 547.1364 | 337.1985 | 543.2592 | 25.5639 | 100.701 | 16.9903 | 283 | 11.959 | 162.5855 | 480.046 | 0.16865
3665 | 1115.5491 | 4.5032 | 108.8942 | 151.9995 | 57.2873 | 10.01 | 255.2671 | 2.0105 | 13.9721 | 52.8015 | 174.1609 | 30.3641 | 532.0589 | 290.4774 | 488.476 | 15.0251 | 95.3046 | 16.6133 | 242 | 11.2068 | 144.8391 | 420.9627 | 0.12217
3666 | 1057.868 | 3.4986 | 108.7188 | 118.6378 | 59.3835 | 8.0186 | 222.9206 | 1.4828 | 13.689 | 45.4399 | 148.4795 | 25.3162 | 495.1942 | 220.0006 | 425.9196 | 9.4449 | 89.4303 | 16.0341 | 231 | 10.8891 | 129.9526 | 358.6339 | 0.096345
3667 | 980.6364 | 7.3024 | 70.4255 | 105.702 | 59.8154 | 7.6082 | 131.5327 | 1.3232 | 11.326 | 32.7338 | 119.9697 | 17.0506 | 456.925 | 172.3871 | 368.4487 | 8.8985 | 84.7176 | 15.4352 | 213 | 10.7746 | 113.6908 | 305.6517 | 0.046515
3668 | 932.2697 | 8.6252 | 53.6478 | 104.2166 | 59.8532 | 7.5723 | 84.7271 | 1.1397 | 6.704 | 23.9245 | 107.9957 | 12.2266 | 411.965 | 152.818 | 319.3128 | 9.0959 | 79.6751 | 14.7492 | 191 | 10.7688 | 104.1844 | 262.9255 | 0.018905
3669 | 905.6437 | 9.1157 | 53.6478 | 103.6337 | 59.8944 | 7.5332 | 76.0515 | 1.3764 | 5.234 | 21.8652 | 103.3578 | 10.9813 | 365.4448 | 140.3433 | 295.9313 | 9.0824 | 75.0742 | 13.6997 | 180 | 10.7999 | 101.1106 | 240.7125 | 0.001048
3670 | 886.3569 | 9.3488 | 53.6478 | 104.2196 | 59.7704 | 7.651 | 73.5895 | 1.4445 | 5.2164 | 22.1979 | 96.4058 | 12.2098 | 328.0805 | 129.0233 | 282.7671 | 8.8759 | 73.0854 | 13.1256 | 160 | 10.8149 | 92.5569 | 239.9083 | 0
3671 | 843.38 | 6.0963 | 49.5385 | 105.5059 | 59.7616 | 7.6593 | 72.2859 | 1.3699 | 5.7307 | 22.3873 | 91.0772 | 13.0866 | 294.0316 | 120.0392 | 273.186 | 9.2605 | 72.8294 | 13.0442 | 160 | 10.8416 | 66.6487 | 251.2291 | 0
3672 | 798.3628 | 2.1984 | 48.9539 | 105.2973 | 56.6528 | 7.5333 | 71.1077 | 1.5896 | 6.0779 | 21.6272 | 89.5578 | 13.1248 | 279.6076 | 116.8136 | 271.9449 | 9.2987 | 72.766 | 13.0676 | 160 | 10.8496 | 58.164 | 257.254 | 0
3673 | 775.2319 | 1.0625 | 49.5194 | 105.6333 | 56.5667 | 7.6151 | 70.8579 | 1.5321 | 6.2288 | 20.3579 | 89.2698 | 13.0054 | 241.4478 | 113.5448 | 278.5526 | 9.2003 | 74.013 | 13.0412 | 156 | 10.808 | 58.3214 | 256.5266 | 0
3674 | 769.3509 | 1.069 | 49.3113 | 106.8614 | 55.1154 | 8.9939 | 70.9097 | 1.4186 | 6.1692 | 20.0679 | 89.383 | 16.846 | 229.3033 | 107.5073 | 278.4767 | 9.1447 | 78.2413 | 12.8528 | 153 | 10.8215 | 56.1065 | 258.007 | 0
3675 | 778.0749 | 1.2172 | 48.9031 | 103.3616 | 56.8183 | 7.3761 | 70.7987 | 1.3914 | 6.1337 | 20.7005 | 88.8422 | 27.1255 | 221.5844 | 100.9706 | 265.5291 | 9.6078 | 82.2081 | 12.5509 | 144 | 10.7938 | 54.3259 | 256.269 | 0
3676 | 787.24 | 1.2441 | 48.7647 | 99.5941 | 56.2052 | 7.9585 | 69.1274 | 1.1082 | 6.1673 | 24.4805 | 86.45 | 25.564 | 236.3347 | 91.6631 | 237.0636 | 10.5443 | 82.4538 | 12.089 | 149 | 10.7848 | 67.2339 | 248.7171 | 0
3677 | 791.4433 | 0.93903 | 49.0889 | 99.5283 | 56.2451 | 7.9206 | 69.3094 | 0.93339 | 5.9613 | 29.9056 | 83.1921 | 15.692 | 240.3523 | 95.1494 | 226.9646 | 9.5618 | 81.4242 | 11.6333 | 153 | 10.7263 | 72.3161 | 252.5745 | 0.10867
3678 | 820.5498 | 2.2677 | 70.3621 | 103.5567 | 55.0436 | 9.062 | 81.5811 | 1.3069 | 5.3302 | 34.1049 | 84.8981 | 16.3719 | 255.5684 | 121.4785 | 241.8278 | 12.0326 | 80.1502 | 11.019 | 187 | 10.7887 | 90.0859 | 291.0487 | 0.17738
3679 | 869.2747 | 5.1376 | 79.9259 | 109.3677 | 51.5759 | 12.3564 | 122.6198 | 1.8486 | 7.5174 | 41.3971 | 106.5984 | 27.3885 | 304.3905 | 171.6042 | 291.4047 | 23.1789 | 79.0431 | 11.1935 | 250 | 11.9487 | 123.9696 | 354.3984 | 0.061334
3680 | 943.4998 | 6.8412 | 101.3177 | 129.91 | 51.3559 | 12.5653 | 147.469 | 2.7469 | 10.919 | 51.6312 | 143.0154 | 32.9337 | 395.0246 | 233.0405 | 387.4006 | 31.4361 | 83.6062 | 12.0067 | 306 | 13.6331 | 147.7262 | 414.5733 | 0.19439
3681 | 1031.255 | 6.666 | 110.8116 | 146.6308 | 50.8288 | 13.0661 | 181.7665 | 3.3475 | 12.287 | 57.7395 | 169.6417 | 34.3464 | 482.0869 | 278.6384 | 486.2919 | 33.9674 | 92.9529 | 14.9838 | 352 | 13.6954 | 166.3509 | 462.9728 | 0.21664
3682 | 1086.8547 | 8.4653 | 109.6621 | 149.9326 | 48.3609 | 15.4106 | 192.6669 | 3.3888 | 12.328 | 61.5749 | 182.8711 | 35.6729 | 532.9527 | 305.0468 | 534.2579 | 32.6806 | 100.1346 | 14.9085 | 367 | 14.24 | 177.2867 | 495.7602 | 0.27159
3683 | 1114.9225 | 5.8742 | 110.893 | 149.3227 | 48.3955 | 15.3777 | 229.0399 | 3.7551 | 12.42 | 62.7211 | 188.4079 | 36.0302 | 577.3329 | 319.6015 | 553.2076 | 30.7406 | 102.4716 | 13.9756 | 341 | 13.913 | 178.3885 | 512.9213 | 0.17321
3684 | 1155.769 | 6.5471 | 109.0398 | 143.7385 | 50.8952 | 13.003 | 252.7273 | 3.5424 | 11.514 | 61.383 | 188.3608 | 38.335 | 599.9828 | 328.6641 | 559.2321 | 29.1462 | 102.083 | 14.0596 | 371 | 13.4505 | 172.8405 | 520.8204 | 0.23344
3685 | 1173.6064 | 9.5093 | 107.7445 | 147.2972 | 50.7251 | 13.1646 | 254.4652 | 3.3714 | 13.713 | 68.1809 | 188.1845 | 38.3641 | 602.6124 | 339.6056 | 556.3043 | 27.9437 | 100.9644 | 14.267 | 332 | 14.3788 | 175.9629 | 519.2989 | 0.18096
3686 | 1178.0717 | 6.0392 | 107.72 | 154.4735 | 47.7104 | 16.0286 | 252.6195 | 3.539 | 17.7893 | 77.8608 | 188.2397 | 33.5202 | 598.1744 | 344.8858 | 565.6256 | 27.8633 | 99.7178 | 14.3311 | 291 | 14.7416 | 176.1125 | 505.0558 | 0.19957
3687 | 1175.9302 | 4.082 | 103.1143 | 150.8838 | 50.1564 | 13.7049 | 250.5955 | 3.3765 | 19.1809 | 83.1021 | 187.264 | 30.923 | 601.6962 | 336.777 | 573.4913 | 27.9378 | 99.3292 | 14.1683 | 282 | 12.6831 | 171.9164 | 488.209 | 0.14747
3688 | 1147.8847 | 3.6895 | 101.0018 | 142.7334 | 52.2922 | 11.6759 | 239.4068 | 3.2598 | 19.5443 | 81.6408 | 186.6025 | 30.3302 | 556.5831 | 317.8004 | 551.4563 | 23.8132 | 94.6947 | 14.3423 | 274 | 11.5574 | 155.0793 | 454.9604 | 0.162
3689 | 1089.3818 | 2.8256 | 98.8633 | 125.7896 | 55.593 | 8.5401 | 167.4104 | 2.3923 | 19.5485 | 73.0205 | 180.04 | 26.1542 | 550.9865 | 268.5558 | 500.479 | 13.1792 | 81.5601 | 15.1417 | 255 | 11.4194 | 140.7696 | 402.4891 | 0.16883
3690 | 1034.0044 | 2.5996 | 82.2195 | 109.9083 | 55.7994 | 8.3441 | 137.6149 | 1.6762 | 18.773 | 60.4784 | 154.0947 | 21.0644 | 481.9289 | 207.8592 | 446.3119 | 8.5241 | 68.6002 | 15.2427 | 240 | 11.4383 | 127.9087 | 354.4284 | 0.078658
3691 | 985.6969 | 1.9268 | 75.2403 | 104.1882 | 56.3798 | 7.7927 | 111.529 | 1.6078 | 13.885 | 47.1971 | 121.4293 | 13.356 | 422.0408 | 175.2547 | 400.6399 | 8.6703 | 62.5142 | 14.607 | 198 | 11.443 | 109.4068 | 304.75 | 0.06982
3692 | 964.1139 | 1.5632 | 75.2403 | 102.4357 | 56.679 | 7.5084 | 86.2341 | 1.4296 | 7.5144 | 38.8515 | 105.9347 | 9.423 | 408.8649 | 158.1742 | 354.6401 | 8.5902 | 58.4184 | 13.9435 | 193 | 11.4906 | 98.3321 | 268.9268 | 0.043617
3693 | 941.4091 | 2.5272 | 63.1188 | 101.8574 | 56.5564 | 7.6249 | 76.8376 | 1.1687 | 5.8953 | 35.1903 | 100.5949 | 6.7345 | 361.783 | 136.5958 | 324.1694 | 8.7765 | 54.2266 | 13.2069 | 198 | 11.5175 | 93.9704 | 259.8202 | 0.0055336
3694 | 882.2262 | 2.8315 | 58.9335 | 102.2079 | 56.5516 | 7.6295 | 74.5149 | 1.3204 | 6.9357 | 33.7776 | 93.0123 | 6.7656 | 295.2043 | 116.2676 | 304.3272 | 8.6992 | 52.0265 | 13.1892 | 177 | 11.5232 | 85.1309 | 261.5392 | 0
3695 | 828.7241 | 2.0125 | 60.7938 | 87.6872 | 55.053 | 9.0531 | 74.4882 | 1.4551 | 6.521 | 33.748 | 86.9337 | 7.8952 | 261.8766 | 106.7746 | 292.3367 | 9.064 | 51.4714 | 13.2718 | 169 | 11.5437 | 60.0012 | 263.1264 | 0
3696 | 833.4866 | 1.663 | 59.7392 | 118.9853 | 56.0696 | 8.0873 | 75.3698 | 1.4123 | 5.8717 | 33.358 | 86.0827 | 12.6727 | 248.7245 | 102.211 | 276.9799 | 8.9667 | 51.5762 | 12.7834 | 160 | 11.4589 | 50.7128 | 259.3233 | 0
3697 | 826.2848 | 1.4517 | 60.8668 | 106.8817 | 55.853 | 8.2931 | 76.3216 | 1.6497 | 5.795 | 31.4979 | 86.2293 | 18.7024 | 243.1737 | 97.652 | 272.2573 | 9.4582 | 51.6853 | 12.3621 | 151 | 11.4521 | 63.0672 | 255.0443 | 0
3698 | 809.6201 | 1.5876 | 60.2446 | 102.092 | 55.561 | 8.5705 | 76.2206 | 1.5848 | 5.8466 | 28.902 | 85.7721 | 24.6972 | 259.4913 | 98.6615 | 266.2872 | 11.9794 | 51.3415 | 12.3282 | 144 | 11.4428 | 70.7988 | 253.8279 | 0
3699 | 812.7307 | 1.7905 | 57.1394 | 103.8052 | 54.8151 | 9.2791 | 72.421 | 1.3979 | 6.005 | 27.4461 | 85.9044 | 31.3133 | 284.1911 | 105.6474 | 247.2801 | 13.1699 | 50.8473 | 12.2118 | 130 | 11.4981 | 71.5462 | 249.6563 | 0
3700 | 807.8511 | 1.9318 | 52.7114 | 104.6822 | 56.1446 | 8.0161 | 69.9299 | 1.1489 | 5.6714 | 30.2263 | 85.2715 | 26.4558 | 288.2978 | 109.2678 | 228.4231 | 11.868 | 50.0579 | 11.4898 | 123 | 11.4817 | 71.2553 | 245.1027 | 0
3701 | 803.5978 | 1.224 | 52.6669 | 103.7604 | 56.5529 | 7.6282 | 69.874 | 0.99126 | 4.9343 | 35.0254 | 83.6525 | 13.2914 | 284.8069 | 111.1398 | 222.1509 | 9.3579 | 49.3561 | 10.9445 | 123 | 11.4269 | 72.1985 | 250.1821 | 0.12049
3702 | 846.8585 | 2.3335 | 72.6695 | 104.6379 | 54.9691 | 9.1328 | 81.2676 | 1.0296 | 4.8005 | 39.08 | 87.5614 | 17.239 | 289.6357 | 129.0073 | 241.5338 | 42.9738 | 49.4249 | 10.8177 | 212 | 11.4552 | 94.2473 | 279.893 | 0.18939
3703 | 932.199 | 3.8012 | 81.1266 | 105.2269 | 49.5067 | 14.3221 | 119.3089 | 1.8998 | 6.1464 | 51.1295 | 112.3112 | 33.8107 | 266.6525 | 173.8759 | 315.2139 | 56.8125 | 52.7717 | 11.0377 | 265 | 12.7215 | 132.7603 | 341.1491 | 0.25669
3704 | 1001.9088 | 4.0562 | 97.9988 | 125.1187 | 49.0734 | 14.7337 | 144.7619 | 2.3874 | 13.7238 | 68.4427 | 148.5623 | 39.9016 | 206.9692 | 228.2827 | 411.0751 | 48.9174 | 63.4382 | 11.7899 | 287 | 12.9589 | 143.747 | 417.4139 | 0.3063
3705 | 1061.1778 | 5.6218 | 106.0328 | 143.0081 | 50.3464 | 13.5244 | 170.7255 | 2.4144 | 17.7265 | 78.0014 | 170.5857 | 40.2679 | 239.7389 | 266.5761 | 485.692 | 38.5024 | 81.2436 | 12.2784 | 319 | 13.5522 | 158.4196 | 479.3972 | 0.31056
3706 | 1137.3991 | 8.5654 | 106.8873 | 114.6869 | 49.471 | 14.356 | 191.2111 | 2.5484 | 18.0196 | 79.0434 | 180.5142 | 40.4762 | 303.6975 | 284.0459 | 533.5763 | 7.2353 | 95.3803 | 12.3771 | 355 | 14.0242 | 166.4568 | 505.2114 | 0.31539
3707 | 1170.8353 | 9.7253 | 107.3232 | 149.1415 | 49.0524 | 14.7537 | 196.3809 | 2.6262 | 18.9358 | 77.2138 | 186.2994 | 40.5782 | 333.7438 | 289.347 | 545.5048 | -8.9328 | 99.3199 | 12.3921 | 328 | 14.1132 | 167.4302 | 507.0479 | 0.23986
3708 | 1196.0193 | 6.1452 | 107.3232 | 175.4192 | 48.8481 | 14.9477 | 204.8312 | 3.3141 | 19.415 | 71.2222 | 187.2575 | 37.7421 | 340.1136 | 290.6452 | 541.6357 | 19.0706 | 99.2086 | 12.5339 | 317 | 14.2844 | 169.4497 | 512.8229 | 0.2532
3709 | 1206.1717 | 3.9368 | 110.3981 | 159.784 | 48.4868 | 15.291 | 205.7825 | 3.0155 | 19.5705 | 72.4034 | 189.633 | 35.7244 | 341.2327 | 289.5527 | 537.0624 | 35.3205 | 99.3313 | 12.8534 | 289 | 13.4718 | 170.3107 | 518.1106 | 0.29412
3710 | 1192.0744 | 3.9085 | 108.136 | 149.8175 | 50.0014 | 13.8521 | 203.8665 | 2.783 | 20.8255 | 84.6062 | 193.4992 | 33.5484 | 450.8215 | 286.0957 | 531.9861 | 33.7958 | 99.4746 | 13.2052 | 303 | 12.6682 | 161.218 | 504.5295 | 0.26688
3711 | 1152.3688 | 4.116 | 103.6941 | 149.0394 | 51.4016 | 12.5219 | 202.1172 | 2.6293 | 21.681 | 89.6606 | 193.2447 | 31.2094 | 488.0186 | 282.1832 | 528.547 | 31.4431 | 98.4992 | 13.59 | 284 | 11.4735 | 151.5365 | 487.9219 | 0.29254
3712 | 1123.2042 | 3.7395 | 98.7601 | 137.7873 | 53.7936 | 10.2495 | 195.1449 | 2.1904 | 21.4545 | 81.7223 | 189.7236 | 27.3197 | 468.7344 | 272.2626 | 495.0745 | 19.3808 | 95.5018 | 13.6105 | 277 | 10.5622 | 147.6141 | 454.0177 | 0.24874
3713 | 1078.9318 | 3.036 | 73.433 | 119.8266 | 56.0157 | 8.1385 | 178.1359 | 1.6182 | 20.8984 | 63.3484 | 177.0996 | 27.7101 | 465.4551 | 228.7088 | 436.9947 | 10.9891 | 90.2514 | 13.3712 | 234 | 10.3876 | 134.6917 | 400.1402 | 0.25857
3714 | 1023.941 | 2.5556 | 62.5683 | 106.7959 | 54.3276 | 9.7422 | 147.1099 | 1.3972 | 19.977 | 49.5951 | 144.8415 | 23.489 | 401.487 | 168.924 | 379.1684 | 8.7188 | 84.24 | 13.2238 | 210 | 10.381 | 123.1053 | 350.3717 | 0.237
3715 | 960.4266 | 1.7201 | 44.1046 | 96.3693 | 56.5323 | 7.6478 | 96.6906 | 1.2071 | 15.2642 | 46.2943 | 110.5044 | 10.2045 | 336.9366 | 133.7157 | 337.8896 | 7.9375 | 78.3471 | 13.1031 | 195 | 10.3337 | 110.4359 | 304.4421 | 0.173
3716 | 922.9265 | 1.1149 | 31.7948 | 109.402 | 57.644 | 6.5916 | 74.6805 | 1.055 | 8.091 | 43.7686 | 90.9768 | 4.4009 | 293.5628 | 118.2201 | 307.0039 | 7.8977 | 73.5051 | 12.8636 | 200 | 10.3852 | 98.9414 | 275.7206 | 0.076044
3717 | 902.0982 | 2.2012 | 33.6834 | 94.2839 | 56.8711 | 7.3259 | 72.4628 | 1.058 | 5.8978 | 41.4146 | 79.1949 | 4.0473 | 263.8294 | 108.048 | 263.1906 | 7.6957 | 70.9967 | 12.2282 | 215 | 10.4222 | 92.8501 | 266.4925 | 0.0071232
3718 | 861.7547 | 2.7481 | 37.6292 | 93.5293 | 55.8507 | 8.2953 | 71.7067 | 1.3029 | 6.1241 | 40.3584 | 75.1038 | 5.2688 | 236.9409 | 107.8345 | 247.8423 | 8.0108 | 70.1756 | 11.9396 | 188 | 10.3491 | 87.4727 | 265.0665 | 0
3719 | 801.6131 | 1.9109 | 38.6831 | 95.0041 | 56.2655 | 7.9013 | 71.3776 | 1.4429 | 6.2293 | 39.9508 | 76.6098 | 6.2782 | 217.2737 | 112.447 | 274.7238 | 8.4818 | 70.1909 | 12.0808 | 170 | 10.3437 | 69.512 | 259.0578 | 0
3720 | 798.9008 | 1.6389 | 37.6977 | 95.3324 | 56.5265 | 7.6532 | 69.2528 | 1.6703 | 6.1929 | 42.6145 | 78.5888 | 6.6787 | 211.2786 | 114.433 | 287.3482 | 11.1764 | 70.667 | 12.215 | 174 | 10.4478 | 60.6693 | 251.5745 | 0
3721 | 790.2504 | 1.4801 | 37.5181 | 94.893 | 56.6643 | 7.5224 | 69.6433 | 1.6302 | 6.3459 | 45.3254 | 79.2598 | 6.4898 | 214.7682 | 111.9114 | 283.6526 | 12.2646 | 71.024 | 12.0023 | 174 | 10.4619 | 59.932 | 249.1228 | 0
3722 | 776.049 | 1.5704 | 37.2583 | 97.1158 | 57.3437 | 6.877 | 71.0912 | 1.4903 | 6.3119 | 44.6431 | 78.6826 | 6.6092 | 229.8081 | 109.096 | 275.5737 | 12.0928 | 71.0442 | 11.8377 | 173 | 10.4334 | 60.893 | 249.594 | 0
3723 | 762.9387 | 1.502 | 37.1855 | 82.5711 | 56.0447 | 8.111 | 68.9037 | 1.4332 | 6.2071 | 41.3903 | 77.2413 | 6.0323 | 243.3727 | 115.2447 | 269.1536 | 12.3091 | 70.8096 | 11.5905 | 165 | 10.4437 | 53.7552 | 247.8167 | 0
3724 | 755.9109 | 1.3321 | 37.2427 | 106.2135 | 55.6294 | 8.5055 | 67.9963 | 1.1544 | 5.8972 | 37.2275 | 74.9755 | 4.287 | 248.2716 | 119.5456 | 264.4359 | 11.1702 | 70.2139 | 11.3243 | 162 | 10.4873 | 49.9375 | 238.6138 | 0
3725 | 763.2741 | 0.98517 | 41.7332 | 96.2113 | 55.5465 | 8.5843 | 66.7107 | 1.0036 | 5.3698 | 36.2779 | 73.0796 | 3.7129 | 244.6414 | 116.1375 | 253.154 | 8.7703 | 69.56 | 11.179 | 162 | 10.4764 | 49.9493 | 229.8502 | 0.048149
3726 | 774.5672 | 1.2289 | 43.7841 | 98.3127 | 55.5695 | 8.5624 | 64.1659 | 1.0277 | 5.263 | 39.0655 | 73.7646 | 3.8743 | 230.8384 | 105.6334 | 247.5091 | 7.7771 | 69.1379 | 11.1522 | 154 | 10.4518 | 51.6925 | 226.4598 | 0.086001
3727 | 798.6521 | 1.3803 | 56.9205 | 109.5755 | 55.5608 | 8.5707 | 64.2445 | 1.0469 | 7.11 | 40.2833 | 82.5298 | 5.858 | 225.0161 | 96.7059 | 245.2156 | 7.792 | 68.9492 | 11.4308 | 153 | 10.5372 | 53.28 | 228.7095 | 0.24454
3728 | 805.7517 | 1.4618 | 70.7823 | 108.0026 | 57.129 | 7.0809 | 66.3224 | 1.385 | 8.009 | 36.8132 | 106.0925 | 11.7647 | 231.1415 | 101.6635 | 244.0746 | 7.71 | 69.4072 | 12.0629 | 141 | 10.5864 | 58.9674 | 234.7309 | 0.29789
3729 | 830.1749 | 1.6637 | 83.5335 | 147.9678 | 57.6228 | 6.6118 | 66.3759 | 1.2627 | 12.8285 | 33.2772 | 135.8987 | 13.7821 | 253.0182 | 112.3907 | 248.039 | 7.8294 | 70.2074 | 12.4092 | 153 | 10.6163 | 85.185 | 240.6946 | 0.31121
3730 | 833.3438 | 1.4155 | 92.6037 | 116.4075 | 56.8774 | 7.3199 | 66.1464 | 1.064 | 14.9868 | 32.6747 | 148.2022 | 13.5997 | 272.2062 | 120.1821 | 245.6572 | 7.8238 | 70.3765 | 12.6214 | 160 | 10.5736 | 97.2399 | 246.5209 | 0.30758
3731 | 847.7461 | 1.7071 | 94.9436 | 100.6287 | 56.5314 | 7.6486 | 67.7344 | 1.2003 | 14.4455 | 34.6453 | 130.9164 | 13.7824 | 279.4263 | 124.1951 | 249.6347 | 7.7432 | 70.0136 | 12.534 | 164 | 10.4669 | 99.0185 | 248.1023 | 0.19761
3732 | 905.805 | 2.4525 | 79.556 | 100.0638 | 56.5681 | 7.6137 | 69.3297 | 1.3934 | 13.7668 | 36.5257 | 107.191 | 14.1991 | 294.6969 | 125.9558 | 242.0518 | 7.8707 | 70.2866 | 12.3146 | 162 | 10.4372 | 98.7923 | 245.2035 | 0.22857
3733 | 924.1191 | 2.5133 | 72.4497 | 99.827 | 57.3035 | 6.9151 | 70.4846 | 1.3615 | 13.4775 | 35.8119 | 99.7028 | 16.9343 | 299.3938 | 129.2896 | 235.9 | 7.7108 | 71.8492 | 12.5003 | 172 | 10.4569 | 98.4532 | 244.5984 | 0.24793
3734 | 926.9398 | 2.256 | 72.4497 | 99.6265 | 56.882 | 7.3156 | 71.0781 | 1.5023 | 13.4327 | 33.6567 | 100.1859 | 18.4852 | 280.0311 | 134.9803 | 269.9337 | 7.6045 | 72.9372 | 12.743 | 158 | 10.4482 | 99.0428 | 248.5435 | 0.2471
3735 | 921.1444 | 2.356 | 48.6091 | 101.2502 | 55.8547 | 8.2914 | 72.9732 | 1.2214 | 11.5626 | 28.6827 | 99.8787 | 15.6854 | 283.6039 | 138.9717 | 300.9169 | 7.9613 | 71.8211 | 12.6665 | 162 | 10.4829 | 93.5304 | 251.7413 | 0.26912
3736 | 903.9717 | 2.4395 | 37.4625 | 100.7378 | 56.2199 | 7.9445 | 73.2017 | 0.95002 | 12.3045 | 23.2094 | 99.0957 | 7.2076 | 294.5104 | 136.1789 | 299.9796 | 7.8951 | 70.2891 | 12.7462 | 160 | 10.4223 | 68.4616 | 250.2769 | 0.2119
3737 | 883.6714 | 2.3069 | 36.9171 | 99.8228 | 57.4253 | 6.7994 | 71.5489 | 0.97161 | 10.5996 | 20.652 | 96.8471 | 3.9707 | 276.7266 | 128.5046 | 285.4403 | 7.7005 | 69.7939 | 13.4032 | 170 | 10.404 | 58.4355 | 244.7995 | 0.18941
3738 | 866.5353 | 1.7273 | 36.9252 | 99.8878 | 56.7886 | 7.4043 | 69.0177 | 1.0202 | 8.3929 | 19.6828 | 90.4478 | 3.8967 | 265.2961 | 123.0256 | 287.4378 | 7.5831 | 69.7201 | 13.3663 | 164 | 10.4475 | 57.933 | 239.6109 | 0.18306
3739 | 851.4447 | 1.2231 | 36.6233 | 98.9867 | 56.5358 | 7.6444 | 68.6383 | 1.0413 | 9.5847 | 19.6422 | 82.2564 | 3.8393 | 274.6529 | 120.7176 | 303.3246 | 7.7424 | 69.6232 | 13.0892 | 167 | 10.4767 | 58.4773 | 240.0815 | 0.1597
3740 | 827.8016 | 0.89741 | 36.5748 | 98.9799 | 55.9476 | 8.2033 | 68.0212 | 1.0349 | 7.0608 | 21.5247 | 77.3455 | 4.0009 | 263.5457 | 116.9005 | 294.5127 | 7.5614 | 69.4575 | 12.837 | 170 | 10.4608 | 57.0689 | 239.8734 | 0.083932
3741 | 785.9246 | 1.9793 | 36.6574 | 98.6376 | 56.2741 | 7.893 | 68.0101 | 1.3034 | 6.2255 | 24.1231 | 75.4947 | 3.7919 | 241.267 | 112.1238 | 267.8681 | 7.8126 | 69.274 | 12.251 | 159 | 10.5243 | 55.8422 | 238.9696 | 0.0079971
3742 | 757.4148 | 2.5046 | 36.6797 | 94.9034 | 56.5856 | 7.5971 | 70.494 | 1.4541 | 6.0105 | 23.5973 | 74.6412 | 4.4776 | 232.2248 | 109.5468 | 261.6907 | 7.8049 | 69.1674 | 12.0535 | 148 | 10.5538 | 54.7977 | 241.6407 | 0
3743 | 753.708 | 1.8538 | 36.8831 | 93.7035 | 56.5556 | 7.6257 | 71.6053 | 1.4497 | 6.1662 | 21.5542 | 75.1662 | 5.8831 | 259.2863 | 108.1517 | 263.5023 | 9.1488 | 69.5223 | 12.3543 | 158 | 10.5377 | 54.1733 | 246.7933 | 0
3744 | 775.2686 | 1.6721 | 36.7792 | 98.7214 | 55.0997 | 9.0087 | 69.461 | 1.4298 | 6.5948 | 21.625 | 76.3804 | 6.5492 | 282.2733 | 105.2735 | 259.7643 | 11.3772 | 70.0399 | 11.8881 | 154 | 10.5587 | 52.7754 | 250.844 | 0
3745 | 756.3458 | 1.403 | 49.2261 | 101.3051 | 55.3819 | 8.7407 | 69.3646 | 1.4345 | 6.77 | 22.286 | 76.6384 | 6.4595 | 275.4085 | 105.0943 | 254.2751 | 12.3319 | 70.2177 | 11.8414 | 156 | 10.5052 | 51.6636 | 249.0857 | 0
3746 | 738.7693 | 1.4587 | 29.0862 | 102.2418 | 57.0328 | 7.1723 | 68.5113 | 1.461 | 10.0386 | 21.923 | 75.7951 | 6.6699 | 256.9326 | 112.7024 | 260.0573 | 12.3944 | 70.2097 | 12.1447 | 149 | 10.4758 | 51.4421 | 247.2669 | 0
3747 | 734.8445 | 1.505 | 35.1585 | 100.1292 | 56.8617 | 7.3348 | 68.9855 | 1.4075 | 11.7985 | 20.4403 | 73.8546 | 5.8875 | 247.5864 | 124.227 | 262.5622 | 11.9659 | 69.9787 | 11.9761 | 150 | 10.4954 | 50.8219 | 244.9427 | 0
3748 | 742.8722 | 1.1997 | 37.8164 | 99.1003 | 56.5751 | 7.6071 | 69.8896 | 1.1768 | 10.3866 | 18.4645 | 71.5215 | 4.2387 | 240.1277 | 128.2731 | 255.6968 | 10.724 | 69.6911 | 11.6973 | 146 | 10.5204 | 49.56 | 238.6463 | 0
3749 | 746.2821 | 0.86478 | 37.868 | 96.9629 | 55.8873 | 8.2605 | 68.5955 | 1.2981 | 9.1901 | 17.7798 | 69.9235 | 3.7255 | 218.2258 | 122.2017 | 234.9316 | 8.8594 | 69.354 | 11.2337 | 135 | 10.5163 | 48.3808 | 232.4645 | 0.12562
3750 | 757.303 | 0.80896 | 50.2598 | 95.7984 | 56.264 | 7.9027 | 68.5388 | 1.1819 | 9.1687 | 18.1826 | 69.3994 | 3.6217 | 196.0596 | 107.9053 | 226.0492 | 7.8918 | 68.8965 | 11.0291 | 133 | 10.5012 | 48.7807 | 228.8095 | 0.2008
3751 | 770.4051 | 1.0551 | 29.043 | 96.3312 | 57.299 | 6.9194 | 67.6276 | 1.0388 | 9.5302 | 18.2427 | 71.1397 | 3.9023 | 167.068 | 97.3814 | 228.2331 | 7.9474 | 68.6381 | 11.173 | 145 | 10.4777 | 50.4444 | 226.1917 | 0.26869
3752 | 773.8432 | 1.0112 | 47.0313 | 97.0856 | 55.341 | 8.7795 | 67.6739 | 1.105 | 7.6623 | 19.011 | 73.4391 | 3.9591 | 161.8167 | 97.9715 | 232.5472 | 7.6624 | 68.6681 | 11.7211 | 136 | 10.4674 | 50.8753 | 227.924 | 0.31861
3753 | 778.7369 | 1.0927 | 29.1171 | 96.9208 | 56.0834 | 8.0742 | 70.1797 | 1.0947 | 10.289 | 21.1159 | 74.9788 | 3.7595 | 182.3285 | 100.8266 | 244.0419 | 7.5514 | 69.2614 | 12.0464 | 140 | 10.4741 | 52.6622 | 231.9929 | 0.31994
3754 | 786.3311 | 1.2287 | 34.9928 | 96.1622 | 57.3301 | 6.8898 | 71.6595 | 1.0349 | 13.215 | 25.2312 | 77.6302 | 3.91 | 219.657 | 105.2624 | 251.0374 | 7.7499 | 69.894 | 12.1651 | 154 | 10.455 | 54.0792 | 232.991 | 0.31982
3755 | 806.4116 | 2.0355 | 38.0766 | 96.3391 | 56.8462 | 7.3496 | 68.7343 | 1.0267 | 14.0087 | 30.1792 | 82.8088 | 6.1464 | 246.16 | 111.8585 | 251.6341 | 7.8378 | 69.8793 | 12.1638 | 153 | 10.4326 | 56.8799 | 231.512 | 0.24958
3756 | 812.9871 | 2.3823 | 38.1357 | 96.1948 | 56.5931 | 7.59 | 68.0956 | 1.0273 | 13.8015 | 29.1804 | 90.424 | 8.3759 | 253.4894 | 119.9448 | 235.041 | 7.9083 | 69.6692 | 12.2785 | 160 | 10.4387 | 57.5919 | 230.8553 | 0.26007
3757 | 807.6051 | 2.1068 | 37.8211 | 98.4156 | 56.6682 | 7.5187 | 69.1742 | 1.3028 | 14.1758 | 24.0209 | 96.1283 | 7.3603 | 258.6474 | 125.5573 | 226.3464 | 7.4732 | 69.7898 | 12.5874 | 162 | 10.44 | 57.8094 | 233.5881 | 0.31007
3758 | 812.4158 | 1.9612 | 50.084 | 100.0887 | 55.8134 | 8.3307 | 70.4489 | 1.1969 | 11.0912 | 21.5803 | 97.6354 | 5.7754 | 265.7127 | 123.8346 | 238.4321 | 7.6416 | 70.0421 | 12.7024 | 164 | 10.4359 | 59.3032 | 235.9908 | 0.2823
3759 | 841.8099 | 1.6534 | 29.2477 | 96.3747 | 54.7063 | 9.3825 | 70.7901 | 1.0111 | 11.1115 | 21.3395 | 97.1201 | 6.742 | 272.8786 | 120.4374 | 266.6854 | 7.8147 | 69.6847 | 12.6925 | 142 | 10.44 | 58.5766 | 237.4846 | 0.28654
3760 | 879.0228 | 2.0729 | 35.1829 | 93.3846 | 57.5746 | 6.6576 | 71.5645 | 0.98277 | 13.2437 | 21.3224 | 95.7019 | 6.6801 | 276.9521 | 118.7524 | 279.1062 | 7.7998 | 68.961 | 12.8478 | 143 | 10.4442 | 55.4978 | 234.99 | 0.24903
3761 | 886.6143 | 2.0924 | 49.682 | 93.0221 | 57.0716 | 7.1354 | 71.3977 | 0.97291 | 14.4106 | 21.8822 | 94.1367 | 8.0632 | 275.0643 | 118.7959 | 272.3771 | 7.6015 | 69.1167 | 12.9152 | 141 | 10.4575 | 54.902 | 227.4252 | 0.26673
3762 | 874.6387 | 2.0427 | 29.0245 | 93.0592 | 56.6267 | 7.5581 | 69.4336 | 0.99265 | 14.431 | 23.5529 | 93.1672 | 8.6614 | 260.6399 | 118.3697 | 276.5328 | 7.8859 | 69.6624 | 12.9546 | 133 | 10.4513 | 54.1096 | 222.9093 | 0.23479
3763 | 846.9018 | 1.4504 | 35.1728 | 93.0159 | 56.6034 | 7.5802 | 66.9008 | 1.0059 | 12.677 | 23.3694 | 93.0365 | 8.5355 | 241.5144 | 117.1097 | 269.5283 | 7.7447 | 69.3873 | 12.584 | 130 | 10.441 | 53.2279 | 220.6462 | 0.18039
3764 | 801.0449 | 0.97129 | 38.1986 | 93.9487 | 57.3146 | 6.9046 | 67.2941 | 1.0164 | 7.9739 | 20.8643 | 89.8509 | 6.6128 | 226.822 | 111.4179 | 260.0852 | 7.8061 | 68.9111 | 12.3568 | 145 | 10.4683 | 54.0678 | 218.1776 | 0.086181
3765 | 784.3098 | 2.0543 | 37.7613 | 93.0735 | 56.1392 | 8.0212 | 67.0745 | 1.2272 | 5.9312 | 18.8516 | 81.7333 | 8.2381 | 223.2829 | 100.7456 | 256.8712 | 7.7286 | 68.7996 | 12.505 | 147 | 10.4756 | 53.5281 | 218.3207 | 0.0083221
3766 | 772.3587 | 2.5034 | 38.1623 | 96.1893 | 56.2878 | 7.8801 | 67.41 | 1.4915 | 5.6162 | 19.0436 | 76.4365 | 21.5746 | 234.5517 | 96.4745 | 248.9665 | 7.9096 | 69.0661 | 12.3101 | 142 | 10.4779 | 51.7863 | 221.8508 | 0
3767 | 745.679 | 3.0015 | 49.9078 | 89.2403 | 56.6066 | 7.5772 | 69.618 | 1.5083 | 5.5579 | 21.6148 | 76.8364 | 23.5534 | 238.851 | 100.3573 | 236.8203 | 9.0776 | 69.0767 | 12.1195 | 141 | 10.4753 | 51.9138 | 228.1635 | 0
3768 | 736.0346 | 6.9541 | 38.0383 | 111.4015 | 55.0349 | 9.0703 | 69.7142 | 1.4377 | 5.738 | 22.6464 | 78.8564 | 11.2645 | 225.552 | 106.6186 | 227.4976 | 11.2719 | 66.8133 | 12.1051 | 138 | 10.4793 | 82.6917 | 231.2797 | 0
3769 | 717.5775 | 7.3744 | 28.957 | 105.0889 | 55.3724 | 8.7497 | 70.8504 | 1.4265 | 5.8922 | 21.3492 | 79.4624 | 6.3713 | 213.8061 | 109.7704 | 227.314 | 12.4168 | 63.9441 | 12.0653 | 124 | 10.4866 | 120.3729 | 231.619 | 0
3770 | 729.8986 | 3.4065 | 35.2476 | 100.9226 | 54.8234 | 9.2713 | 68.8498 | 1.4507 | 6.0888 | 20.2256 | 78.4251 | 8.351 | 200.378 | 119.5594 | 235.2278 | 12.3658 | 63.5293 | 11.9384 | 120 | 10.4902 | 73.3085 | 233.9324 | 0
3771 | 741.721 | 1.6959 | 38.1449 | 98.1192 | 56.0948 | 8.0634 | 70.8705 | 1.3888 | 6.1797 | 19.874 | 75.833 | 14.0314 | 198.6884 | 134.9362 | 238.8124 | 12.157 | 63.9507 | 11.8667 | 122 | 10.5001 | 88.2852 | 235.1743 | 0
3772 | 728.7471 | 1.4237 | 49.8012 | 96.6282 | 57.3375 | 6.8828 | 67.2742 | 1.1726 | 5.8934 | 23.0915 | 72.2883 | 12.4535 | 200.1367 | 138.399 | 241.3576 | 10.7487 | 64.4144 | 11.421 | 127 | 10.5063 | 94.5457 | 232.5437 | 0
3773 | 742.2605 | 1.4022 | 29.1047 | 82.1064 | 56.0688 | 8.0881 | 68.2336 | 1.3367 | 5.6748 | 27.9092 | 71.3001 | 5.832 | 189.1396 | 134.5398 | 238.2321 | 8.6865 | 65.9128 | 11.1069 | 121 | 10.5008 | 92.5537 | 225.5094 | 0.11369
3774 | 757.4495 | 1.3095 | 32.9065 | 98.9208 | 54.9011 | 9.1974 | 73.2194 | 1.1986 | 5.661 | 31.0016 | 76.2056 | 3.4127 | 175.6378 | 129.1329 | 239.1632 | 7.8814 | 67.1754 | 11.006 | 126 | 10.5023 | 63.7014 | 221.3228 | 0.13891
3775 | 768.7195 | 1.0543 | 36.8079 | 92.6688 | 53.05 | 10.956 | 106.7751 | 1.0785 | 6.8099 | 32.9185 | 88.54 | 3.5916 | 153.4775 | 129.3278 | 260.2151 | 7.757 | 67.5789 | 11.2666 | 145 | 10.5066 | 54.1477 | 223.8897 | 0.19616
3776 | 777.5468 | 1.3318 | 38.2598 | 90.4489 | 53.2769 | 10.7404 | 117.8084 | 1.1472 | 10.6136 | 30.4783 | 100.9331 | 4.0209 | 184.833 | 139.5777 | 285.7301 | 8.0817 | 67.8944 | 12.1245 | 135 | 10.4831 | 54.9056 | 228.3281 | 0.25466
3777 | 804.4077 | 1.3462 | 51.188 | 80.3621 | 52.2004 | 11.7631 | 129.5671 | 1.1426 | 12.2907 | 27.6709 | 106.5276 | 3.5742 | 226.7886 | 153.0032 | 310.7211 | 8.1969 | 68.2871 | 12.4561 | 142 | 10.4461 | 54.913 | 232.6893 | 0.27364
3778 | 830.4556 | 1.2557 | 39.4911 | 104.499 | 53.093 | 10.9151 | 142.7877 | 1.0633 | 14.8471 | 29.6268 | 112.5644 | 3.3558 | 251.8954 | 169.1551 | 324.8887 | 8.0304 | 68.4258 | 12.599 | 142 | 10.4279 | 56.4679 | 238.4954 | 0.31323
3779 | 844.6199 | 1.6089 | 30.2099 | 102.1733 | 52.7965 | 11.1968 | 149.352 | 1.0166 | 15.8295 | 32.6619 | 122.6056 | 3.2972 | 280.3001 | 178.411 | 327.9613 | 7.7748 | 68.3879 | 12.8224 | 156 | 10.4034 | 57.2988 | 243.3299 | 0.24614
3780 | 845.4192 | 2.016 | 48.77 | 96.3202 | 53.2292 | 10.7857 | 151.7065 | 1.0258 | 15.4586 | 35.1983 | 129.7152 | 3.6056 | 298.5525 | 181.7571 | 334.8823 | 7.6833 | 68.5678 | 13.6578 | 162 | 10.4103 | 57.4605 | 244.9715 | 0.26614
3781 | 837.7662 | 1.8231 | 30.0821 | 100.6162 | 52.8549 | 11.1413 | 158.0145 | 1.1997 | 13.9645 | 41.2135 | 132.1671 | 3.4772 | 281.9577 | 184.6076 | 350.0026 | 7.5921 | 69.024 | 14.1807 | 178 | 10.4364 | 58.1241 | 241.2685 | 0.3186
3782 | 836.9454 | 1.6136 | 36.5927 | 89.2482 | 52.7065 | 11.2823 | 161.6997 | 1.2594 | 13.0918 | 49.0116 | 134.2789 | 3.4685 | 288.2962 | 183.3819 | 364.1971 | 7.3763 | 69.1739 | 14.0406 | 150 | 10.4354 | 59.7224 | 236.6919 | 0.29402
3783 | 830.6709 | 1.9286 | 51.7962 | 109.7526 | 55.5473 | 8.5835 | 160.844 | 1.097 | 11.0961 | 50.5276 | 136.2997 | 3.4941 | 288.0933 | 183.434 | 363.4685 | 7.8084 | 68.148 | 13.3053 | 155 | 10.3977 | 59.6349 | 236.9254 | 0.24576
3784 | 817.4096 | 2.0443 | 39.4911 | 101.7276 | 56.4827 | 7.6949 | 154.0623 | 1.008 | 8.3914 | 44.7203 | 135.1574 | 3.5102 | 279.204 | 184.7028 | 353.1982 | 7.986 | 67.2142 | 12.996 | 144 | 10.4268 | 58.7388 | 236.9986 | 0.20065
3785 | 811.362 | 2.0173 | 30.3195 | 96.2485 | 56.5535 | 7.6276 | 137.4866 | 0.98247 | 11.4555 | 37.592 | 130.9675 | 3.394 | 274.0868 | 168.1218 | 326.0139 | 7.4691 | 67.2652 | 12.7052 | 136 | 10.4474 | 57.2889 | 236.7883 | 0.2314
3786 | 804.1649 | 6.748 | 36.3517 | 95.352 | 53.7322 | 10.3078 | 119.5047 | 0.98539 | 12.4352 | 32.7537 | 122.4748 | 4.231 | 261.0384 | 140.8599 | 298.3499 | 7.4602 | 67.0048 | 12.6206 | 134 | 10.4411 | 55.6135 | 234.7619 | 0.188
3787 | 787.9094 | 4.3784 | 38.0123 | 93.7432 | 50.3656 | 13.5061 | 93.6931 | 1.036 | 11.5244 | 27.4241 | 109.3068 | 6.9928 | 244.3209 | 123.5597 | 283.3519 | 7.3481 | 66.1921 | 12.7025 | 145 | 10.4457 | 54.8764 | 230.6276 | 0.16383
3788 | 764.2041 | 1.5303 | 37.73 | 94.7278 | 53.9064 | 10.1424 | 65.1941 | 1.0564 | 8.0211 | 22.4577 | 98.4379 | 7.4197 | 237.934 | 111.9217 | 268.3415 | 7.4376 | 64.7887 | 12.4278 | 168 | 10.4371 | 54.9243 | 231.252 | 0.053633
3789 | 764.5253 | 2.4125 | 40.6792 | 99.7285 | 56.4218 | 7.7528 | 58.9419 | 1.3163 | 5.8627 | 19.34 | 93.1169 | 6.0165 | 222.4005 | 101.8894 | 257.5465 | 7.834 | 63.1289 | 11.9067 | 163 | 10.4481 | 52.3306 | 234.0499 | 0.0061576
3790 | 760.7152 | 2.9938 | 41.7981 | 106.0036 | 55.8546 | 8.2916 | 61.374 | 1.4239 | 5.5865 | 17.1579 | 87.2404 | 5.4845 | 233.3352 | 96.0388 | 254.9884 | 7.7209 | 62.3599 | 11.8571 | 164 | 10.4799 | 50.6882 | 236.3695 | 0
3791 | 748.5917 | 2.1292 | 42.061 | 109.7689 | 54.801 | 9.2925 | 67.1485 | 1.4048 | 5.6741 | 17.622 | 80.8678 | 8.6503 | 239.3131 | 95.6878 | 244.9606 | 8.4744 | 63.9088 | 12.2487 | 153 | 10.4863 | 51.9997 | 242.3869 | 0
3792 | 763.8824 | 1.3103 | 41.6874 | 100.131 | 56.1254 | 8.0343 | 66.7428 | 1.4668 | 6.284 | 19.1541 | 78.4796 | 18.0951 | 222.8737 | 98.8176 | 225.8669 | 10.8161 | 68.0547 | 12.426 | 156 | 10.4995 | 58.6601 | 244.6848 | 0
3793 | 782.9862 | 1.1538 | 41.3077 | 123.3016 | 56.5877 | 7.5952 | 66.4403 | 1.4736 | 6.1742 | 19.1392 | 76.2453 | 21.3225 | 216.0644 | 102.3784 | 224.2079 | 12.2061 | 71.3905 | 12.4629 | 144 | 10.4939 | 93.1238 | 242.5142 | 0
3794 | 764.5827 | 1.2278 | 40.7393 | 116.2423 | 56.4755 | 7.7017 | 67.9661 | 1.4436 | 6.1503 | 18.2834 | 73.9909 | 23.3232 | 211.6102 | 109.5573 | 226.5302 | 12.2007 | 71.9703 | 11.864 | 139 | 10.4877 | 104.7467 | 243.7027 | 0
3795 | 757.3637 | 1.2947 | 40.7833 | 111.5224 | 55.8126 | 8.3315 | 66.5587 | 1.3428 | 5.8681 | 18.7131 | 73.429 | 29.4053 | 184.5503 | 116.8402 | 231.1216 | 11.9429 | 71.3931 | 11.2142 | 126 | 10.5143 | 103.9954 | 244.1638 | 0
3796 | 750.6004 | 1.0506 | 43.8721 | 108.9265 | 55.6554 | 8.4808 | 67.9521 | 1.1307 | 5.5965 | 23.1668 | 71.8456 | 24.5373 | 170.8294 | 114.1083 | 223.4901 | 10.7127 | 70.6829 | 10.9191 | 126 | 10.5078 | 103.043 | 245.0714 | 0
3797 | 769.1377 | 0.94833 | 45.2065 | 104.9425 | 55.5416 | 8.589 | 65.8084 | 1.3307 | 5.3555 | 28.81 | 71.4866 | 9.8023 | 168.7962 | 111.0289 | 217.4855 | 8.5855 | 69.976 | 10.7872 | 129 | 10.4866 | 97.3657 | 250.5055 | 0.038772
3798 | 812.2643 | 1.931 | 86.1149 | 102.5221 | 50.5714 | 13.3106 | 78.5464 | 1.2104 | 5.0815 | 32.3125 | 79.2659 | 11.3383 | 170.5482 | 130.4757 | 230.572 | 10.8051 | 69.7027 | 10.8348 | 180 | 10.7218 | 95.3332 | 281.0616 | 0.089507
3799 | 851.9551 | 6.5484 | 106.3905 | 105.6853 | 49.1799 | 14.6326 | 116.8257 | 1.152 | 7.6327 | 34.5235 | 108.3083 | 22.3306 | 211.0771 | 175.4355 | 284.1451 | 22.0506 | 72.5427 | 11.1562 | 321 | 12.4056 | 122.6527 | 335.1687 | 0.14873
3800 | 930.9098 | 6.2925 | 70.1836 | 122.8824 | 47.3696 | 16.3523 | 130.3688 | 2.1576 | 14.3456 | 32.6763 | 147.8325 | 24.4757 | 283.255 | 225.757 | 385.8137 | 30.4009 | 79.9376 | 11.8309 | 291 | 12.4439 | 143.0896 | 400.998 | 0.14032
3801 | 1028.461 | 6.9252 | 53.2712 | 127.7884 | 47.2363 | 16.479 | 139.1282 | 2.7012 | 17.4869 | 29.0232 | 170.3045 | 27.3411 | 342.2828 | 264.9242 | 475.9176 | 34.6123 | 89.8768 | 12.3032 | 309 | 13.3995 | 148.6821 | 461.4957 | 0.23266
3802 | 1088.2237 | 9.8859 | 76.7602 | 176.7717 | 47.6433 | 16.0924 | 142.1848 | 2.6074 | 16.9955 | 31.5599 | 177.4409 | 28.4798 | 370.6719 | 288.4855 | 519.0532 | 36.0124 | 97.3246 | 12.3944 | 328 | 15.3221 | 154.3518 | 494.0413 | 0.29596
3803 | 1122.1385 | 6.7358 | 89.9019 | 165.6574 | 47.7219 | 16.0177 | 148.0081 | 2.7233 | 16.4819 | 35.2912 | 182.0757 | 30.2878 | 400.9012 | 299.5311 | 528.9094 | 37.3795 | 99.9291 | 12.41 | 341 | 13.8067 | 154.4874 | 507.5762 | 0.23811
3804 | 1129.2811 | 7.0491 | 91.2268 | 141.4752 | 48.2599 | 15.5065 | 154.7733 | 2.6836 | 17.2972 | 36.0985 | 184.2019 | 30.7437 | 441.6611 | 299.2183 | 525.9274 | 37.3931 | 99.2735 | 12.4553 | 319 | 12.6426 | 151.5693 | 514.1222 | 0.27659
3805 | 1128.1734 | 7.5506 | 90.1885 | 170.0887 | 44.8025 | 18.7911 | 159.5219 | 2.6324 | 17.6163 | 41.7316 | 183.2766 | 29.6543 | 446.2941 | 296.3638 | 519.3373 | 37.2023 | 97.5475 | 14.7511 | 297 | 14.0854 | 150.8154 | 522.477 | 0.27614
3806 | 1123.5461 | 7.1102 | 89.7382 | 197.6218 | 44.3152 | 19.254 | 161.0914 | 2.788 | 17.6549 | 50.9169 | 183.069 | 29.0785 | 461.7001 | 296.5172 | 524.4576 | 35.8177 | 97.8958 | 13.973 | 252 | 17.561 | 153.1573 | 524.9382 | 0.27733
3807 | 1103.1374 | 6.5798 | 89.7382 | 159.2234 | 48.3164 | 15.4529 | 158.598 | 2.998 | 17.8519 | 54.7543 | 181.7784 | 29.7782 | 469.745 | 288.5448 | 534.1227 | 33.4838 | 97.8256 | 13.0693 | 265 | 14.4123 | 150.0765 | 521.1399 | 0.28574
3808 | 1085.5396 | 4.7624 | 89.7382 | 171.9693 | 53.2422 | 10.7734 | 149.6696 | 2.3786 | 16.9022 | 49.4871 | 177.7591 | 28.7983 | 451.3195 | 279.0953 | 511.2865 | 27.8743 | 94.3166 | 12.7096 | 224 | 11.6524 | 137.4043 | 493.9571 | 0.24926
3809 | 1024.4476 | 3.1746 | 80.8962 | 131.2566 | 55.4046 | 8.7191 | 130.9607 | 1.4568 | 16.0018 | 40.4518 | 165.9714 | 26.7278 | 435.0191 | 252.2739 | 452.1366 | 15.0366 | 88.3183 | 12.5959 | 188 | 11.2945 | 125.2429 | 427.462 | 0.2608
3810 | 963.9291 | 2.7022 | 74.7239 | 108.7623 | 55.6338 | 8.5013 | 114.1503 | 1.2997 | 15.42 | 33.048 | 136.4403 | 19.9425 | 395.9612 | 198.9208 | 388.0944 | 9.0512 | 82.763 | 12.57 | 170 | 10.7007 | 115.8496 | 357.9015 | 0.20208
3811 | 931.4215 | 4.3974 | 68.7757 | 98.1961 | 55.442 | 8.6836 | 81.4813 | 1.1703 | 12.5117 | 25.4732 | 104.2193 | 7.6698 | 353.3442 | 156.3794 | 348.0711 | 8.1594 | 78.9778 | 12.3845 | 154 | 10.3259 | 102.5312 | 302.6295 | 0.16346
3812 | 909.6609 | 6.8978 | 49.2197 | 77.9638 | 56.3321 | 7.838 | 66.551 | 1.0483 | 7.3883 | 19.3226 | 92.6924 | 3.2778 | 288.5064 | 136.0687 | 320.9463 | 7.9113 | 74.7548 | 12.0325 | 138 | 10.1446 | 95.2495 | 257.8402 | 0.048304
3813 | 891.9848 | 8.8337 | 44.2861 | 74.5092 | 55.7935 | 8.3496 | 69.3021 | 1.0575 | 5.678 | 16.849 | 93.0991 | 4.0286 | 258.9451 | 126.8483 | 292.1433 | 8.032 | 71.3264 | 11.426 | 134 | 10.1173 | 91.9706 | 234.88 | 0.0064164
3814 | 880.0706 | 9.2236 | 43.2075 | 79.7708 | 55.6585 | 8.4779 | 63.0707 | 1.3514 | 5.598 | 15.9727 | 88.5932 | 7.8479 | 256.1998 | 125.6916 | 256.5643 | 8.297 | 70.1625 | 11.2105 | 133 | 10.1275 | 86.7083 | 229.7465 | 0
3815 | 856.4165 | 5.1576 | 43.3001 | 82.2015 | 55.6565 | 8.4798 | 62.4545 | 1.6218 | 5.803 | 16.0093 | 81.0543 | 10.1623 | 231.2171 | 131.5212 | 230.0584 | 9.4327 | 70.0138 | 11.2746 | 128 | 10.1283 | 63.9419 | 231.4478 | 0
3816 | 843.4973 | 2.3883 | 42.5416 | 61.379 | 54.7807 | 9.3118 | 61.6365 | 1.5495 | 5.9446 | 16.0881 | 75.7012 | 10.507 | 210.0945 | 133.1576 | 230.7976 | 11.6543 | 70.8891 | 11.3432 | 125 | 10.1362 | 55.9241 | 237.1628 | 0
3817 | 841.0349 | 1.8548 | 41.9607 | 100.9062 | 56.8224 | 7.3722 | 63.3956 | 1.4786 | 5.7755 | 16.0544 | 72.1976 | 10.5578 | 176.0088 | 127.2288 | 236.8433 | 12.6385 | 71.7707 | 11.1846 | 134 | 10.1374 | 87.5608 | 242.5172 | 0
3818 | 825.8806 | 1.8373 | 42.5029 | 108.1062 | 56.8324 | 7.3627 | 61.9199 | 1.4642 | 5.6422 | 16.5207 | 71.9772 | 13.8019 | 164.2157 | 134.7789 | 235.0969 | 12.3284 | 71.626 | 11.1009 | 121 | 10.1397 | 99.8757 | 245.554 | 0
3819 | 822.2623 | 1.6961 | 42.3034 | 110.7522 | 56.5793 | 7.6031 | 63.9788 | 1.4403 | 5.7157 | 18.0961 | 73.7935 | 22.3146 | 160.3961 | 147.0801 | 232.1642 | 12.3133 | 71.3197 | 11.1312 | 122 | 10.1521 | 95.278 | 248.4708 | 0
3820 | 819.2289 | 2.044 | 41.7685 | 107.5653 | 55.0225 | 9.0821 | 61.9956 | 1.2992 | 5.8059 | 22.4846 | 72.5976 | 19.8921 | 180.0668 | 145.301 | 225.417 | 11.2293 | 70.7248 | 10.9964 | 133 | 10.1333 | 96.4565 | 246.1725 | 0
3821 | 840.2961 | 2.1519 | 42.2803 | 101.8357 | 55.3501 | 8.7709 | 63.8995 | 1.3861 | 5.2481 | 27.9088 | 68.82 | 8.4095 | 204.082 | 138.6716 | 216.9398 | 8.9973 | 69.8161 | 10.8229 | 135 | 10.1123 | 94.1888 | 248.5342 | 0.01663
3822 | 880.7164 | 2.1803 | 49.3419 | 100.5784 | 54.0891 | 9.9688 | 69.2642 | 1.2118 | 5.07 | 31.7702 | 75.2794 | 10.6922 | 215.6233 | 137.5474 | 230.4402 | 10.9767 | 69.6976 | 10.7724 | 167 | 10.5266 | 94.8478 | 281.8958 | 0.051289
3823 | 942.8026 | 3.1909 | 71.9713 | 70.1461 | 47.7278 | 16.012 | 95.1657 | 1.674 | 7.851 | 33.4607 | 107.1034 | 20.2553 | 243.697 | 165.6755 | 277.6057 | 22.1854 | 72.2277 | 11.0551 | 254 | 14.2686 | 122.4297 | 341.8791 | 0.082376
3824 | 1033.0359 | 3.4477 | 84.9908 | 136.0527 | 48.4341 | 15.3411 | 95.625 | 2.8951 | 13.9182 | 29.6235 | 149.0208 | 27.3206 | 308.4236 | 210.0231 | 373.1799 | 29.7108 | 79.5012 | 11.7647 | 289 | 15.5377 | 139.7044 | 409.7238 | 0.11818
3825 | 1109.2229 | 3.5461 | 89.114 | 142.7586 | 45.3529 | 18.2682 | 109.0217 | 3.7885 | 13.2025 | 26.2784 | 173.0362 | 28.0808 | 356.0315 | 239.215 | 458.8421 | 30.7284 | 90.2936 | 12.0964 | 330 | 16.3087 | 143.2588 | 470.9257 | 0.096922
3826 | 1142.4002 | 3.4436 | 89.6065 | 142.6139 | 45.002 | 18.6016 | 129.0162 | 3.9572 | 12.3647 | 30.0535 | 181.5437 | 28.2468 | 402.5941 | 258.1324 | 498.4252 | 30.1069 | 100.8725 | 12.1892 | 344 | 16.6387 | 146.1025 | 500.6712 | 0.16571
3827 | 1157.9421 | 3.7509 | 89.9779 | 140.192 | 49.2166 | 14.5977 | 121.8958 | 3.7844 | 13.933 | 33.5401 | 186.1609 | 30.0993 | 438.417 | 274.5808 | 517.388 | 31.6529 | 106.1783 | 13.7744 | 334 | 15.2661 | 150.0696 | 503.068 | 0.22045
3828 | 1149.1949 | 4.0959 | 93.1947 | 115.5046 | 49.8106 | 14.0334 | 121.1856 | 3.3592 | 15.1408 | 35.6104 | 189.4808 | 30.1103 | 448.4572 | 285.42 | 509.2648 | 32.8095 | 105.1266 | 12.8407 | 323 | 14.203 | 150.8112 | 501.4614 | 0.23778
3829 | 1135.3435 | 4.3594 | 91.7307 | 164.7161 | 47.3595 | 16.3619 | 120.2155 | 3.13 | 15.0547 | 43.0904 | 193.3539 | 28.5706 | 444.2441 | 287.5626 | 498.8015 | 33.0927 | 104.5426 | 12.2103 | 313 | 13.2384 | 146.8229 | 509.5102 | 0.27172
3830 | 1140.2937 | 4.2603 | 90.7966 | 150.9058 | 47.3425 | 16.3781 | 113.4065 | 3.2285 | 13.3798 | 53.3661 | 196.2689 | 25.3185 | 466.9607 | 281.5693 | 498.0693 | 31.9541 | 106.9684 | 12.7616 | 292 | 14.4652 | 148.5327 | 516.1038 | 0.27999
3831 | 1127.18 | 3.8125 | 87.7993 | 137.4995 | 50.4901 | 13.3879 | 121.0732 | 2.9944 | 14.3405 | 54.8091 | 194.2464 | 23.7919 | 494.7697 | 274.7087 | 498.9943 | 30.8218 | 108.8768 | 12.959 | 282 | 13.9959 | 145.2245 | 505.4181 | 0.29225
3832 | 1080.1225 | 3.7779 | 86.3456 | 128.4794 | 48.6322 | 15.1528 | 121.9442 | 2.401 | 15.3287 | 46.7399 | 188.2963 | 22.068 | 468.2607 | 265.2829 | 480.514 | 25.7308 | 107.6459 | 12.7575 | 295 | 12.496 | 133.5058 | 466.5366 | 0.2304
3833 | 1018.144 | 7.4767 | 80.456 | 112.8539 | 54.3611 | 9.7104 | 109.1656 | 1.7936 | 15.5184 | 40.1237 | 175.1722 | 21.16 | 437.9817 | 218.335 | 421.6497 | 14.4935 | 102.4501 | 12.7145 | 230 | 12.4101 | 122.147 | 401.3585 | 0.25492
3834 | 962.3111 | 9.6795 | 73.6958 | 99.7001 | 55.8099 | 8.334 | 92.2153 | 1.2365 | 16.2108 | 34.4869 | 144.9956 | 17.2673 | 400.9581 | 154.0347 | 360.1725 | 9.194 | 95.3655 | 12.7776 | 263 | 12.5424 | 114.8631 | 335.3477 | 0.24256
3835 | 924.5527 | 5.203 | 71.85 | 95.4228 | 54.8183 | 9.2761 | 55.2229 | 1.2453 | 14.1667 | 26.1833 | 113.6503 | 7.387 | 338.372 | 126.5049 | 322.8969 | 8.634 | 81.9967 | 12.7428 | 203 | 12.3062 | 101.9248 | 283.5191 | 0.16308
3836 | 885.2938 | 2.2176 | 47.8813 | 93.5564 | 54.5515 | 9.5295 | 51.9402 | 1.1525 | 8.492 | 20.7662 | 100.734 | 3.319 | 296.9593 | 120.3499 | 289.0162 | 8.6884 | 65.3994 | 12.352 | 219 | 11.7177 | 92.7597 | 254.1657 | 0.040205
3837 | 867.0712 | 2.5184 | 49.114 | 92.6773 | 56.1801 | 7.9824 | 55.6944 | 1.0293 | 6.2012 | 19.4111 | 96.2123 | 3.3015 | 242.97 | 106.6059 | 264.1797 | 8.5496 | 56.6667 | 11.3812 | 194 | 11.5581 | 89.6854 | 244.6765 | 0.010828
3838 | 836.2065 | 2.7987 | 56.9908 | 95.1601 | 56.5063 | 7.6725 | 57.931 | 1.4291 | 6.253 | 19.0056 | 88.4795 | 4.0221 | 177.3659 | 96.1042 | 254.0923 | 9.0537 | 54.368 | 11.1221 | 164 | 11.5172 | 87.4318 | 246.1436 | 0
3839 | 816.8056 | 1.8373 | 59.9201 | 98.6999 | 55.8685 | 8.2784 | 47.9462 | 1.5201 | 6.2686 | 19.9586 | 82.0814 | 5.595 | 145.4691 | 94.4726 | 243.1993 | 9.2214 | 54.5017 | 11.0833 | 159 | 11.4456 | 68.2984 | 251.0998 | 0
3840 | 819.929 | 1.3218 | 58.7097 | 102.4413 | 55.5344 | 8.5958 | 45.9252 | 1.4641 | 6.2563 | 21.4084 | 81.667 | 6.024 | 142.0334 | 94.3209 | 233.4284 | 9.0943 | 55.2689 | 11.1396 | 124 | 11.4093 | 62.4473 | 252.9012 | 0
3841 | 814.0245 | 1.3917 | 58.329 | 103.2272 | 55.5439 | 8.5868 | 59.8564 | 1.488 | 6.4961 | 21.4006 | 82.673 | 6.0428 | 150.8203 | 95.739 | 231.9027 | 9.4784 | 55.3786 | 11.3559 | 120 | 11.4208 | 78.5749 | 252.5937 | 0
3842 | 807.691 | 1.6607 | 57.1564 | 99.5718 | 56.4152 | 7.759 | 65.6802 | 1.672 | 6.6031 | 21.0345 | 82.3233 | 6.1317 | 157.4745 | 102.2058 | 238.5622 | 9.4874 | 55.0378 | 11.3498 | 113 | 11.4133 | 83.1056 | 254.2305 | 0
3843 | 798.3281 | 1.4604 | 56.2047 | 92.5419 | 54.3479 | 9.7229 | 65.0668 | 1.5031 | 6.4003 | 21.3066 | 80.1628 | 5.3924 | 153.436 | 107.7172 | 237.1258 | 8.9255 | 54.4798 | 11.2459 | 114 | 11.4218 | 81.8902 | 255.6756 | 0
3844 | 807.721 | 1.2424 | 56.051 | 49.989 | 54.3421 | 9.7285 | 64.1718 | 1.1942 | 5.8673 | 25.7039 | 76.3706 | 3.865 | 146.7316 | 106.3892 | 222.8019 | 8.5053 | 53.7152 | 10.9525 | 117 | 11.4226 | 80.4634 | 257.7702 | 0
3845 | 823.9316 | 1.4409 | 56.4788 | 69.8232 | 55.2475 | 8.8684 | 57.4174 | 1.0967 | 5.6258 | 32.2708 | 74.8798 | 4.2974 | 154.8584 | 111.0899 | 216.1929 | 8.7248 | 53.4787 | 10.7759 | 117 | 11.3892 | 81.4186 | 270.7049 | 0.1236
3846 | 851.9794 | 2.7469 | 59.1483 | 93.4871 | 53.5213 | 10.5082 | 59.6376 | 1.0756 | 5.3345 | 37.8114 | 84.8315 | 11.8401 | 168.7307 | 130.0523 | 227.4503 | 12.2876 | 54.3353 | 10.7492 | 178 | 11.5299 | 89.9184 | 306.8067 | 0.067649
3847 | 913.0435 | 7.2961 | 73.4592 | 99.4791 | 50.4002 | 13.4733 | 80.3579 | 1.5658 | 7.9907 | 42.0294 | 112.5967 | 21.759 | 200.517 | 165.7374 | 281.597 | 22.4459 | 58.3171 | 11.0243 | 246 | 12.5653 | 120.3962 | 364.3528 | 0.10937
3848 | 972.9403 | 9.5341 | 83.1977 | 117.1738 | 47.2233 | 16.4913 | 95.8614 | 2.6248 | 13.5833 | 43.1347 | 144.0986 | 24.8733 | 204.6956 | 205.3262 | 372.3123 | 29.9908 | 65.6216 | 11.5941 | 277 | 13.7522 | 139.236 | 431.4839 | 0.16042
3849 | 1041.5108 | 8.9156 | 86.2434 | 136.2219 | 46.6766 | 17.0107 | 108.7749 | 2.8555 | 15.7263 | 40.7017 | 164.3116 | 24.3207 | 272.3064 | 230.9059 | 454.078 | 31.2313 | 80.8459 | 11.9007 | 350 | 13.8016 | 142.3167 | 475.5452 | 0.23246
3850 | 1077.2293 | 8.6354 | 86.717 | 142.4861 | 45.2547 | 18.3615 | 125.1459 | 2.6253 | 15.2012 | 35.9749 | 175.8394 | 24.9159 | 330.146 | 248.7451 | 504.5926 | 30.9436 | 98.7322 | 12.3662 | 338 | 13.9728 | 144.4289 | 490.1194 | 0.27535
3851 | 1106.1806 | 7.5229 | 85.689 | 140.2946 | 45.8219 | 17.8226 | 137.4617 | 2.875 | 12.9268 | 34.2809 | 181.2375 | 25.2236 | 353.7961 | 262.9399 | 522.7067 | 30.7777 | 105.2147 | 12.6338 | 311 | 13.8295 | 146.2576 | 491.7043 | 0.22606
3852 | 1111.9361 | 4.9397 | 82.9888 | 137.9647 | 50.1138 | 13.7453 | 138.769 | 3.1573 | 13.9617 | 34.0819 | 185.1834 | 24.9447 | 401.0454 | 273.0432 | 518.9248 | 30.6071 | 103.7119 | 12.5882 | 329 | 14.2012 | 144.7845 | 488.3306 | 0.28955
3853 | 1104.3912 | 3.5687 | 83.793 | 118.5832 | 48.4978 | 15.2806 | 131.0153 | 3.1677 | 15.0732 | 37.6582 | 191.4252 | 23.5416 | 433.8697 | 281.9444 | 509.9971 | 31.5373 | 103.5171 | 12.4641 | 307 | 14.9283 | 145.3664 | 496.8956 | 0.29397
3854 | 1097.1522 | 3.8682 | 83.3125 | 159.7111 | 48.4063 | 15.3675 | 128.4967 | 2.9594 | 15.2028 | 44.3862 | 195.6461 | 23.3923 | 460.4248 | 287.1907 | 503.6934 | 32.2545 | 105.2689 | 12.5281 | 275 | 15.637 | 147.7989 | 506.0783 | 0.28484
3855 | 1081.1748 | 4.0561 | 76.6397 | 144.3503 | 47.889 | 15.8589 | 127.9985 | 2.6647 | 15.619 | 45.6662 | 191.2966 | 22.7863 | 477.2277 | 284.3893 | 498.9289 | 32.0793 | 105.7079 | 12.3166 | 266 | 14.4951 | 141.747 | 501.9983 | 0.22216
3856 | 1053.1837 | 3.2834 | 51.0972 | 136.2173 | 49.8293 | 14.0156 | 121.1603 | 2.2158 | 15.6708 | 42.3989 | 181.989 | 21.6557 | 460.2523 | 273.4531 | 471.3313 | 26.44 | 104.3198 | 12.178 | 257 | 13.6178 | 128.9684 | 472.1912 | 0.22027
3857 | 1009.2622 | 2.704 | 51.0972 | 114.4368 | 56.6267 | 7.5581 | 103.6573 | 1.636 | 15.6336 | 36.1804 | 167.9339 | 21.0602 | 414.3304 | 225.9524 | 418.6114 | 14.5065 | 95.6183 | 12.1876 | 219 | 12.98 | 115.4191 | 410.4756 | 0.12328
3858 | 952.359 | 2.5133 | 38.5963 | 99.9357 | 57.1263 | 7.0835 | 84.7601 | 1.1917 | 15.845 | 30.4498 | 137.3434 | 17.6224 | 354.762 | 158.8304 | 370.2408 | 9.0662 | 80.1995 | 12.2534 | 199 | 12.5323 | 106.4584 | 346.7836 | 0.10897
3859 | 910.6384 | 2.7248 | 47.1627 | 97.0343 | 56.5573 | 7.624 | 60.0977 | 1.0666 | 12.824 | 26.9905 | 105.9118 | 9.3771 | 302.6221 | 130.1764 | 329.2629 | 8.7167 | 69.1031 | 12.3875 | 183 | 11.7461 | 95.0104 | 295.7373 | 0.059018
3860 | 879.5443 | 2.2862 | 51.4339 | 97.2035 | 55.8492 | 8.2967 | 51.9914 | 1.0425 | 7.731 | 23.7334 | 94.137 | 7.366 | 276.4129 | 128.5938 | 287.7456 | 8.7401 | 63.0733 | 12.1611 | 169 | 11.6018 | 87.2973 | 254.7875 | 0.041094
3861 | 850.1837 | 2.7861 | 50.8792 | 86.1985 | 56.2776 | 7.8897 | 46.4736 | 1.1388 | 5.8213 | 21.7898 | 90.6278 | 7.982 | 226.3734 | 116.6659 | 260.3751 | 8.3237 | 58.8266 | 11.7021 | 146 | 11.6153 | 84.662 | 231.388 | 0.0051668
3862 | 832.227 | 3.3271 | 51.2053 | 108.6231 | 55.8482 | 8.2977 | 48.3783 | 1.3757 | 5.9933 | 22.135 | 82.9963 | 6.2942 | 194.7031 | 101.6826 | 253.1869 | 8.4521 | 57.1793 | 11.6969 | 131 | 11.5697 | 78.1117 | 226.8403 | 0
3863 | 812.2179 | 1.9367 | 50.8767 | 107.5171 | 55.6298 | 8.5052 | 52.9303 | 1.4683 | 6.0038 | 23.5433 | 75.8699 | 5.9669 | 158.9145 | 97.6026 | 248.3096 | 8.9696 | 56.6658 | 11.8196 | 129 | 11.5862 | 54.3925 | 232.9112 | 0
3864 | 812.9072 | 1.4696 | 51.4879 | 107.7721 | 54.021 | 10.0335 | 50.6032 | 1.4607 | 6.3258 | 23.8268 | 74.1554 | 6.1599 | 142.9583 | 95.948 | 235.5636 | 8.7479 | 56.0551 | 11.7412 | 130 | 11.549 | 46.4276 | 237.9621 | 0
3865 | 800.5226 | 1.3083 | 51.1658 | 109.4864 | 55.8231 | 8.3215 | 51.3605 | 1.4268 | 6.2973 | 23.0922 | 74.4032 | 6.2871 | 154.5141 | 93.5637 | 230.6487 | 8.8772 | 55.4395 | 11.6184 | 131 | 11.6285 | 65.8719 | 240.5975 | 0
3866 | 793.9827 | 1.2484 | 50.2885 | 108.0277 | 57.4052 | 6.8186 | 50.8081 | 1.4135 | 6.1436 | 22.6972 | 74.555 | 9.3812 | 169.7657 | 95.7145 | 224.9491 | 8.9062 | 54.9895 | 11.5642 | 119 | 11.636 | 73.9231 | 242.0398 | 0
3867 | 794.5563 | 1.8983 | 67.8723 | 107.1337 | 56.0155 | 8.1388 | 50.6126 | 1.6935 | 6.4205 | 23.7408 | 74.6465 | 17.4211 | 171.0694 | 99.4946 | 224.0607 | 8.8436 | 54.6489 | 11.5598 | 121 | 11.6191 | 72.9966 | 243.3261 | 0
3868 | 798.9216 | 2.1027 | 38.71 | 83.6433 | 55.5779 | 8.5544 | 45.3824 | 1.3975 | 6.3699 | 28.2808 | 72.9172 | 9.0633 | 168.2262 | 99.2941 | 217.7649 | 8.6595 | 54.0792 | 11.43 | 123 | 11.6441 | 72.5175 | 246.7026 | 0
3869 | 815.0625 | 1.6265 | 63.4812 | 74.6306 | 55.5735 | 8.5587 | 44.4742 | 1.0587 | 5.6701 | 34.0107 | 70.403 | 4.3788 | 167.573 | 104.4661 | 214.0741 | 8.318 | 53.4023 | 11.1017 | 123 | 11.6707 | 73.18 | 255.0207 | 0.04401
3870 | 850.504 | 2.1765 | 39.2552 | 87.1255 | 51.7899 | 12.1531 | 49.6694 | 1.0393 | 5.3621 | 40.104 | 78.4264 | 10.3748 | 169.1446 | 128.6236 | 224.8834 | 11.6022 | 53.3912 | 10.7637 | 170 | 12.0729 | 85.5626 | 286.6608 | 0.11429
3871 | 914.0989 | 4.1235 | 62.9364 | 114.4454 | 47.8022 | 15.9414 | 70.8738 | 1.8645 | 7.7297 | 43.7802 | 111.5873 | 19.8494 | 198.309 | 171.0291 | 266.1271 | 24.6661 | 56.9959 | 10.9764 | 227 | 15.1924 | 112.6936 | 342.7224 | 0.12902
3872 | 981.0126 | 6.4537 | 38.6775 | 117.0501 | 46.5801 | 17.1024 | 101.384 | 2.7894 | 13.2558 | 40.5609 | 150.0386 | 23.9831 | 250.9261 | 214.2393 | 350.4344 | 31.837 | 65.9447 | 11.5868 | 255 | 16.2759 | 129.5743 | 409.2464 | 0.2236
3873 | 1050.5944 | 6.891 | 68.4589 | 165.6361 | 47.306 | 16.4127 | 106.2036 | 3.2372 | 14.6287 | 33.0047 | 167.8472 | 24.0266 | 297.9368 | 240.9228 | 436.4399 | 33.069 | 82.3316 | 11.7893 | 319 | 14.9675 | 132.1702 | 474.9614 | 0.28312
3874 | 1099.7631 | 7.0438 | 83.1084 | 163.1256 | 46.9287 | 16.7712 | 114.6932 | 3.408 | 17.7388 | 27.2762 | 174.5457 | 24.8308 | 348.3355 | 259.7141 | 492.3228 | 32.8818 | 99.354 | 11.9004 | 316 | 15.0976 | 130.7036 | 513.4503 | 0.32076
3875 | 1110.8782 | 6.2956 | 86.1403 | 163.4635 | 45.6938 | 17.9443 | 112.1808 | 3.3679 | 19.8057 | 25.3621 | 178.6694 | 25.0867 | 371.6221 | 272.4978 | 513.5959 | 33.338 | 106.9558 | 12.2732 | 292 | 15.2164 | 130.8675 | 519.2729 | 0.2677
3876 | 1093.2031 | 4.4285 | 82.3242 | 144.8938 | 47.8672 | 15.8796 | 108.4185 | 3.3237 | 18.4862 | 27.8286 | 178.5331 | 25.7923 | 382.215 | 274.5181 | 509.3814 | 34.4231 | 106.5387 | 12.3352 | 287 | 14.6776 | 130.9322 | 513.6246 | 0.28448
3877 | 1091.0378 | 3.6651 | 80.8959 | 175.6153 | 47.1163 | 16.5929 | 108.677 | 3.1146 | 16.6079 | 37.7841 | 178.033 | 28.4467 | 398.0311 | 273.4662 | 497.6447 | 33.0263 | 104.6419 | 12.0938 | 277 | 13.9844 | 129.0978 | 506.6172 | 0.26353
3878 | 1081.5034 | 3.6135 | 79.8974 | 165.6124 | 45.1297 | 18.4802 | 113.2803 | 3.1548 | 15.147 | 47.4448 | 180.2168 | 28.9777 | 399.4036 | 273.0514 | 495.3772 | 32.5283 | 104.86 | 12.0009 | 255 | 14.0632 | 128.222 | 499.2187 | 0.29355
3879 | 1061.7291 | 3.6089 | 79.2836 | 154.1956 | 47.395 | 16.3282 | 114.2511 | 3.0694 | 15.0827 | 49.5048 | 181.0043 | 28.221 | 394.8297 | 265.2177 | 486.5454 | 33.0318 | 104.1762 | 12.1976 | 241 | 12.4155 | 121.5282 | 483.4287 | 0.30559
3880 | 1025.2397 | 3.7604 | 84.3999 | 133.095 | 53.0609 | 10.9456 | 106.6367 | 2.4863 | 13.2617 | 44.7114 | 177.9963 | 27.4468 | 387.7968 | 242.1857 | 443.1107 | 21.1237 | 100.2554 | 12.4198 | 218 | 10.746 | 118.8998 | 431.1676 | 0.24232
3881 | 970.1983 | 3.2253 | 69.2987 | 139.248 | 54.564 | 9.5176 | 94.4016 | 1.9149 | 14.2847 | 34.1653 | 165.39 | 25.8692 | 362.4771 | 189.3145 | 376.0611 | 10.6956 | 93.1672 | 12.6965 | 176 | 10.3683 | 108.2851 | 358.0507 | 0.21506
3882 | 926.0216 | 2.4274 | 39.5344 | 69.3731 | 56.8557 | 7.3406 | 83.7481 | 1.3369 | 15.113 | 24.4199 | 135.2583 | 18.6558 | 358.755 | 132.9025 | 325.958 | 8.8218 | 86.3838 | 13.0372 | 164 | 10.4322 | 99.5895 | 302.5442 | 0.19895
3883 | 879.9079 | 2.0011 | 28.4902 | 77.1225 | 55.3416 | 8.779 | 61.2047 | 1.11 | 13.1051 | 20.6638 | 104.7833 | 7.3777 | 320.1367 | 114.294 | 295.5176 | 8.5705 | 78 | 12.8592 | 137 | 10.4126 | 85.5027 | 266.7384 | 0.15501
3884 | 847.5626 | 1.3072 | 27.9978 | 63.7556 | 55.9923 | 8.1607 | 63.3346 | 1.2895 | 7.8822 | 19.6072 | 88.302 | 3.475 | 260.0375 | 116.4855 | 263.6756 | 8.2783 | 66.0935 | 12.6646 | 128 | 10.4477 | 77.4736 | 244.8062 | 0.098131
3885 | 838.9252 | 1.9768 | 35.2024 | 67.9965 | 57.3608 | 6.8607 | 49.3325 | 1.2002 | 5.6569 | 18.5482 | 79.1717 | 3.4891 | 219.6629 | 105.9015 | 241.7971 | 8.399 | 57.4709 | 12.6364 | 128 | 10.4932 | 74.8245 | 233.2012 | 0.013732
3886 | 815.5246 | 2.637 | 38.2246 | 75.2367 | 56.1585 | 8.0029 | 49.6382 | 1.2787 | 5.5818 | 18.4304 | 74.9686 | 4.0171 | 205.0032 | 91.2052 | 232.5297 | 8.4805 | 54.0891 | 12.6284 | 126 | 10.4824 | 67.7419 | 235.2056 | 0
3887 | 804.5552 | 1.9549 | 38.2124 | 77.79 | 52.5544 | 11.4268 | 45.413 | 1.4541 | 5.8426 | 20.2421 | 75.0971 | 5.5926 | 179.1252 | 89.8369 | 233.7404 | 8.5783 | 53.322 | 12.4886 | 120 | 10.5142 | 45.23 | 245.3122 | 0
3888 | 808.2499 | 1.4986 | 37.0051 | 78.6182 | 53.1545 | 10.8567 | 51.907 | 1.5358 | 6.1582 | 22.4548 | 76.2817 | 6.1212 | 166.3981 | 90.8446 | 239.6647 | 8.9899 | 53.734 | 12.2172 | 129 | 10.5242 | 36.3685 | 249.9147 | 0
3889 | 808.477 | 1.4569 | 36.4269 | 74.3284 | 54.4022 | 9.6713 | 62.7119 | 1.7842 | 6.1727 | 23.3971 | 75.9306 | 6.2957 | 155.9782 | 95.433 | 240.1175 | 8.9257 | 54.1941 | 11.6537 | 137 | 10.5049 | 36.0249 | 252.2995 | 0
3890 | 805.8807 | 1.2574 | 36.4113 | 52.4308 | 56.7475 | 7.4433 | 64.5914 | 1.7006 | 6.1734 | 23.5324 | 75.6105 | 6.302 | 150.0571 | 109.3857 | 241.3802 | 8.7909 | 54.2476 | 11.2111 | 133 | 10.502 | 35.2636 | 253.0024 | 0
3891 | 808.2385 | 5.0434 | 36.2788 | 82.0081 | 56.8175 | 7.3768 | 63.5431 | 1.4609 | 6.518 | 22.9953 | 74.7159 | 5.3739 | 149.9257 | 113.1728 | 235.997 | 8.618 | 53.6522 | 11.0212 | 129 | 10.5192 | 34.746 | 245.0913 | 0
3892 | 810.6042 | 8.0406 | 36.3365 | 71.5523 | 55.8473 | 8.2985 | 62.7249 | 1.2782 | 6.2608 | 24.7589 | 72.2169 | 3.9098 | 136.9368 | 104.0398 | 228.2147 | 8.2811 | 52.8914 | 10.8669 | 123 | 10.5503 | 34.4554 | 231.3999 | 0
3893 | 812.0809 | 8.3302 | 36.3134 | 68.1952 | 55.6061 | 8.5276 | 62.7194 | 1.1948 | 5.6564 | 29.6045 | 70.4934 | 3.8648 | 129.59 | 97.3448 | 226.4946 | 8.1442 | 52.5094 | 10.8422 | 121 | 10.5424 | 33.9355 | 221.8626 | 0.14047
3894 | 838.4866 | 4.8913 | 39.8281 | 70.8582 | 54.1301 | 9.9299 | 56.667 | 1.1943 | 5.5548 | 34.0664 | 70.6259 | 4.056 | 126.6047 | 91.2144 | 221.464 | 8.3832 | 52.5462 | 10.8297 | 114 | 10.5591 | 34.1382 | 223.4398 | 0.20955
3895 | 856.6158 | 1.8544 | 53.0434 | 85.3869 | 55.7411 | 8.3994 | 44.3999 | 1.4502 | 7.394 | 35.4363 | 75.2939 | 5.8318 | 125.957 | 88.0633 | 223.9929 | 8.2595 | 52.7718 | 11.073 | 113 | 10.5309 | 36.2648 | 230.9321 | 0.26093
3896 | 864.9408 | 1.4109 | 69.4517 | 102.5189 | 56.5911 | 7.5919 | 54.7007 | 1.4745 | 12.0293 | 33.6277 | 94.8065 | 11.5043 | 123.0565 | 91.2814 | 228.6972 | 8.1094 | 52.8167 | 11.6991 | 116 | 10.4642 | 45.7009 | 236.4985 | 0.31665
3897 | 879.3407 | 1.7834 | 77.5592 | 92.5614 | 56.5388 | 7.6416 | 54.2414 | 1.2943 | 10.8995 | 32.617 | 123.0457 | 13.9864 | 129.7472 | 102.2706 | 237.3242 | 8.1919 | 53.0296 | 11.8954 | 128 | 10.4496 | 72.1986 | 241.011 | 0.31248
3898 | 882.3707 | 1.9382 | 76.6487 | 109.2146 | 56.5844 | 7.5983 | 50.0274 | 1.2186 | 7.8848 | 31.1668 | 138.7722 | 13.9189 | 151.0098 | 110.8778 | 250.0782 | 8.232 | 53.1764 | 11.8681 | 140 | 10.3964 | 82.1312 | 244.6054 | 0.32295
3899 | 888.7845 | 1.8893 | 74.9413 | 120.8522 | 55.8707 | 8.2763 | 59.5887 | 1.4226 | 12.3778 | 29.9937 | 131.7236 | 14.1769 | 163.05 | 110.8374 | 251.9862 | 8.5645 | 54.3261 | 11.9618 | 150 | 10.3925 | 82.3905 | 247.0997 | 0.26786
3900 | 904.9277 | 1.8718 | 74.5175 | 98.4199 | 54.8282 | 9.2667 | 53.5108 | 1.4667 | 14.3381 | 29.1451 | 112.916 | 14.0708 | 164.3194 | 119.019 | 243.2 | 8.4511 | 56.5511 | 12.0752 | 144 | 10.424 | 81.7505 | 247.2178 | 0.2743
3901 | 893.9733 | 1.9885 | 74.6964 | 90.2007 | 55.3921 | 8.7309 | 57.0358 | 1.667 | 14.2547 | 27.38 | 101.2759 | 13.8075 | 165.9349 | 123.0418 | 224.889 | 7.9674 | 56.0528 | 12.098 | 149 | 10.4785 | 81.9648 | 244.3111 | 0.28618
3902 | 886.8579 | 2.9256 | 65.473 | 89.6184 | 54.7626 | 9.3289 | 52.6784 | 1.3769 | 14.5533 | 25.9212 | 98.0921 | 14.743 | 166.3121 | 112.9415 | 227.018 | 7.9412 | 53.172 | 12.0826 | 149 | 10.4701 | 81.103 | 243.8792 | 0.25791
3903 | 866.3901 | 6.9149 | 57.3903 | 89.6247 | 56.1101 | 8.0489 | 45.1296 | 1.1545 | 13.2726 | 20.5066 | 98.6348 | 14.4977 | 166.704 | 108.1102 | 246.3467 | 8.5517 | 51.6666 | 12.0876 | 154 | 10.482 | 73.7823 | 241.7094 | 0.26203
3904 | 862.0655 | 8.7348 | 55.9055 | 89.3384 | 56.6674 | 7.5194 | 55.4301 | 1.1763 | 10.4235 | 14.3173 | 100.281 | 7.0731 | 167.1457 | 113.4033 | 249.907 | 8.3047 | 53.141 | 12.0692 | 146 | 10.475 | 50.4921 | 233.8473 | 0.23289
3905 | 861.0062 | 8.6426 | 56.0172 | 89.4127 | 56.5148 | 7.6644 | 56.7007 | 1.1378 | 10.2596 | 12.5001 | 98.5035 | 3.5788 | 171.8292 | 114.0348 | 245.6084 | 8.3951 | 55.4027 | 12.0753 | 141 | 10.4125 | 42.252 | 232.0171 | 0.25914
3906 | 828.1444 | 7.5616 | 55.952 | 89.0346 | 55.8444 | 8.3013 | 51.7205 | 1.3068 | 12.916 | 12.2811 | 95.1286 | 3.4237 | 177.8519 | 102.1084 | 233.1289 | 8.3708 | 54.2401 | 12.3595 | 136 | 10.4393 | 42.7329 | 238.0873 | 0.12693
3907 | 813.4096 | 3.287 | 55.0198 | 88.1431 | 56.278 | 7.8893 | 51.0361 | 1.3024 | 12.5108 | 12.2709 | 94.2066 | 3.498 | 171.4436 | 91.3212 | 223.6537 | 8.158 | 50.9088 | 12.5567 | 138 | 10.5389 | 42.0028 | 242.4582 | 0.097401
3908 | 826.4372 | 1.0142 | 54.3897 | 87.0822 | 56.633 | 7.5521 | 57.8702 | 1.1953 | 7.6412 | 12.6811 | 93.5681 | 3.4584 | 163.5035 | 89.0003 | 220.0128 | 8.259 | 49.4545 | 12.1606 | 146 | 10.5125 | 42.2977 | 244.3284 | 0.043683
3909 | 832.2254 | 2.0101 | 54.3031 | 87.2697 | 55.9197 | 8.2297 | 60.2506 | 1.1317 | 5.5428 | 12.1706 | 87.8895 | 3.4715 | 161.4901 | 88.8448 | 217.3248 | 8.1447 | 49.4754 | 11.6329 | 149 | 10.51 | 38.8314 | 249.3259 | 0.0063263
3910 | 819.0451 | 2.4799 | 54.5132 | 69.1446 | 56.2571 | 7.9092 | 50.0296 | 1.3165 | 5.2923 | 11.8874 | 79.3597 | 4.0717 | 152.9144 | 87.641 | 218.1677 | 8.2319 | 49.4975 | 11.7292 | 135 | 10.5193 | 36.0187 | 255.1332 | 0
3911 | 811.5222 | 1.6118 | 55.1646 | 102.6558 | 56.5463 | 7.6345 | 42.4864 | 1.5586 | 5.3672 | 14.079 | 75.9267 | 5.6124 | 149.5945 | 86.8825 | 219.3486 | 9.6928 | 49.8166 | 11.6083 | 141 | 10.4849 | 35.4668 | 258.0454 | 0
3912 | 818.329 | 1.1475 | 55.3903 | 95.2239 | 54.3889 | 9.684 | 45.0434 | 1.5988 | 6.0823 | 16.4995 | 76.4201 | 6.2626 | 148.0597 | 88.2066 | 218.7282 | 11.9707 | 50.3494 | 11.1052 | 138 | 10.5242 | 34.4833 | 258.0323 | 0
3913 | 816.8722 | 1.2158 | 55.2684 | 74.0474 | 55.043 | 9.0626 | 49.2056 | 1.8618 | 6.4005 | 17.0551 | 76.705 | 6.263 | 144.348 | 90.3521 | 223.6978 | 12.8404 | 50.6819 | 10.8726 | 133 | 10.528 | 33.8755 | 249.9945 | 0
3914 | 802.1536 | 1.3344 | 55.4149 | 104.8016 | 54.1854 | 9.8774 | 56.5427 | 1.7712 | 8.788 | 17.0397 | 76.8324 | 6.2073 | 141.4262 | 96.0318 | 223.0545 | 12.8263 | 50.7591 | 10.8496 | 118 | 10.5147 | 34.3055 | 242.3713 | 0
3915 | 793.8875 | 1.2818 | 55.0036 | 93.7428 | 54.239 | 9.8264 | 58.4742 | 1.5345 | 7.4505 | 15.9577 | 75.91 | 5.3886 | 136.1374 | 101.6493 | 219.6689 | 10.6984 | 50.4949 | 10.8186 | 116 | 10.5185 | 33.2669 | 241.3233 | 0
3916 | 783.2806 | 1.2752 | 54.7472 | 87.9406 | 56.0469 | 8.1089 | 61.6527 | 1.3345 | 6.0596 | 13.7698 | 73.3867 | 4.0151 | 130.7302 | 100.6785 | 212.141 | 8.7284 | 49.9318 | 10.8281 | 111 | 10.537 | 33.1756 | 235.9061 | 0
3917 | 786.4563 | 0.95673 | 54.7356 | 87.6918 | 56.6389 | 7.5465 | 55.118 | 1.2045 | 5.5342 | 13.0702 | 71.6468 | 3.5992 | 129.2672 | 96.1665 | 207.2961 | 8.2414 | 49.5076 | 10.8438 | 112 | 10.5386 | 32.5868 | 225.8202 | 0.052852
3918 | 809.0519 | 0.88708 | 54.6046 | 87.4243 | 56.5699 | 7.612 | 48.5366 | 1.2009 | 8.0799 | 14.1895 | 71.5905 | 3.6311 | 128.976 | 89.0996 | 210.492 | 8.2658 | 49.3714 | 10.7985 | 120 | 10.5521 | 32.2185 | 218.5216 | 0.085498
3919 | 825.3583 | 0.8324 | 54.5852 | 88.1635 | 56.6361 | 7.5491 | 46.3989 | 1.2601 | 6.5383 | 13.8806 | 72.1255 | 3.9544 | 114.3499 | 84.19 | 209.0616 | 8.1437 | 49.3448 | 11.0045 | 133 | 10.5517 | 33.1831 | 216.2077 | 0.16899
3920 | 831.4512 | 0.90517 | 54.3646 | 87.3902 | 55.7896 | 8.3533 | 44.5065 | 1.5429 | 5.3357 | 13.1348 | 73.0652 | 3.6662 | 108.3255 | 84.5541 | 212.4384 | 8.4204 | 49.2575 | 11.5894 | 120 | 10.4918 | 35.85 | 218.6436 | 0.29271
3921 | 826.695 | 1.0567 | 54.0416 | 88.9621 | 55.5458 | 8.5849 | 61.9019 | 1.4392 | 6.692 | 14.3603 | 74.2596 | 3.6147 | 110.1116 | 85.9371 | 218.4815 | 8.0812 | 49.2745 | 11.8168 | 121 | 10.3935 | 37.6042 | 219.9695 | 0.29249
3922 | 835.737 | 0.92139 | 54.5926 | 90.2705 | 56.2895 | 7.8784 | 69.575 | 1.2198 | 11.6118 | 20.1471 | 76.469 | 3.5511 | 113.6954 | 88.7665 | 227.7822 | 8.0184 | 49.664 | 11.7885 | 124 | 10.4412 | 39.5799 | 225.8775 | 0.21221
3923 | 847.9368 | 1.2849 | 54.5886 | 89.0541 | 55.1597 | 8.9517 | 57.0838 | 1.1977 | 13.7537 | 25.4709 | 81.695 | 3.5403 | 138.493 | 92.1431 | 237.5908 | 8.1285 | 50.0841 | 11.784 | 139 | 10.4488 | 39.5806 | 237.1914 | 0.23829
3924 | 845.3929 | 1.5732 | 54.426 | 87.5984 | 55.2836 | 8.8341 | 57.0185 | 1.1666 | 13.6959 | 23.2872 | 89.6014 | 3.481 | 152.4975 | 93.986 | 234.7341 | 8.2809 | 51.2228 | 11.8639 | 144 | 10.3966 | 39.0738 | 240.2978 | 0.23989
3925 | 848.942 | 1.5744 | 54.4748 | 87.6787 | 54.9236 | 9.1761 | 65.7192 | 1.1108 | 11.3858 | 21.7562 | 96.7937 | 3.6969 | 161.1866 | 95.0743 | 231.4048 | 8.2082 | 53.107 | 11.9664 | 143 | 10.4026 | 37.8954 | 242.1065 | 0.2562
3926 | 849.7916 | 1.5683 | 54.9089 | 89.0118 | 54.5413 | 9.5392 | 98.9146 | 1.18 | 12.5608 | 23.2171 | 101.2546 | 4.5249 | 172.9365 | 96.0108 | 230.4169 | 8.1497 | 53.8676 | 12.3041 | 142 | 10.3968 | 36.6854 | 243.1799 | 0.26839
3927 | 837.4724 | 1.7365 | 55.7313 | 91.6079 | 56.034 | 8.1212 | 120.1633 | 1.4455 | 13.59 | 23.0071 | 102.3575 | 6.107 | 175.0982 | 97.0411 | 230.6564 | 8.274 | 53.7007 | 12.4695 | 129 | 10.3622 | 38.4779 | 235.698 | 0.2683
3928 | 834.3592 | 1.6186 | 55.6758 | 91.6472 | 57.3283 | 6.8916 | 94.4791 | 1.2931 | 13.4192 | 21.1091 | 100.7583 | 4.5099 | 178.5694 | 97.0276 | 237.4772 | 8.115 | 52.6541 | 12.4508 | 131 | 10.5016 | 39.3314 | 228.8317 | 0.18415
3929 | 840.2668 | 1.2596 | 55.7739 | 89.7861 | 56.1291 | 8.0308 | 72.8663 | 1.1392 | 13.2785 | 19.2909 | 97.7407 | 3.5518 | 191.3006 | 95.6945 | 255.4969 | 8.4277 | 50.6603 | 12.4491 | 126 | 10.7037 | 39.519 | 228.1935 | 0.15659
3930 | 854.7175 | 0.98741 | 55.9572 | 73.072 | 55.5293 | 8.6007 | 66.5906 | 1.1413 | 7.8927 | 18.486 | 94.6814 | 3.5202 | 191.2762 | 93.899 | 277.8748 | 8.2214 | 49.4664 | 12.5314 | 128 | 10.3598 | 40.385 | 230.7583 | 0.11706
3931 | 853.1747 | 0.86239 | 56.3929 | 103.4163 | 56.2777 | 7.8896 | 68.5152 | 1.1467 | 8.0545 | 17.6223 | 93.0524 | 3.465 | 192.042 | 91.8188 | 276.327 | 7.9644 | 49.2104 | 12.5174 | 134 | 10.1863 | 39.5938 | 234.7716 | 0.078348
3932 | 829.692 | 1.3136 | 55.453 | 93.4725 | 57.3586 | 6.8628 | 72.0429 | 1.1084 | 6.5592 | 16.4129 | 87.8242 | 3.4573 | 188.7558 | 90.0992 | 255.2791 | 8.1125 | 49.1296 | 12.1892 | 128 | 10.1865 | 38.5573 | 234.0319 | 0.030599
3933 | 813.7637 | 2.5369 | 54.7843 | 71.2299 | 56.0634 | 8.0932 | 66.122 | 1.1262 | 5.3695 | 14.8365 | 79.7603 | 3.4904 | 183.886 | 89.0018 | 238.8273 | 8.2214 | 49.4348 | 11.5681 | 124 | 10.2714 | 38.0614 | 227.0969 | 0.0068353
3934 | 814.2449 | 2.9205 | 54.7254 | 105.428 | 55.661 | 8.4755 | 60.4168 | 1.641 | 5.4347 | 13.7093 | 74.7122 | 4.1258 | 176.9675 | 88.3527 | 234.9115 | 8.4323 | 50.2509 | 11.3153 | 114 | 10.2919 | 36.8321 | 223.9724 | 0
3935 | 795.3343 | 3.2349 | 54.9514 | 99.8949 | 56.3884 | 7.7845 | 59.6975 | 1.6908 | 5.7664 | 14.8515 | 72.7877 | 5.6654 | 168.5358 | 88.6354 | 235.7188 | 9.5311 | 51.1224 | 11.318 | 122 | 10.2442 | 36.2873 | 228.8132 | 0
3936 | 798.5895 | 6.4989 | 55.0548 | 79.2831 | 55.7469 | 8.3939 | 58.3561 | 1.5673 | 6.0577 | 16.5764 | 72.9218 | 6.4578 | 152.3779 | 89.6656 | 234.2354 | 11.6845 | 51.592 | 11.3392 | 116 | 10.2003 | 40.6479 | 230.6115 | 0
3937 | 793.3235 | 3.7343 | 55.1332 | 109.8711 | 54.1639 | 9.8977 | 60.3156 | 1.6075 | 6.1107 | 16.8077 | 73.3521 | 6.216 | 148.3226 | 90.9575 | 238.0854 | 12.8626 | 51.6814 | 11.1494 | 107 | 10.2201 | 74.1362 | 220.9734 | 0
3938 | 780.0384 | 1.266 | 55.249 | 100.9376 | 55.8153 | 8.329 | 60.8686 | 1.6118 | 5.9823 | 16.847 | 73.622 | 6.1202 | 151.6819 | 96.0701 | 240.7247 | 12.8569 | 51.6803 | 11.0548 | 110 | 10.256 | 87.2757 | 214.0108 | 0
3939 | 784.1149 | 1.2064 | 54.8903 | 94.8276 | 55.8485 | 8.2974 | 62.4809 | 1.5131 | 6.1149 | 17.6213 | 72.6235 | 5.4117 | 145.2917 | 101.2114 | 236.4042 | 11.2289 | 51.3812 | 10.9618 | 107 | 10.2048 | 83.0424 | 214.028 | 0
3940 | 792.4204 | 1.0562 | 54.6978 | 94.2377 | 56.3051 | 7.8636 | 63.704 | 1.281 | 6.0087 | 22.3552 | 70.0686 | 3.9438 | 135.1801 | 100.7827 | 224.148 | 8.7463 | 50.7863 | 10.8046 | 114 | 10.261 | 71.2273 | 220.4577 | 0
3941 | 794.6684 | 1.0424 | 55.5089 | 93.4995 | 55.1162 | 8.9931 | 59.9985 | 1.4889 | 5.8722 | 29.1298 | 68.9007 | 4.3121 | 147.2259 | 107.9034 | 210.7105 | 8.0086 | 50.2932 | 10.754 | 113 | 10.2074 | 68.1275 | 233.2492 | 0.13136
3942 | 819.8942 | 6.6912 | 57.7362 | 94.7957 | 53.0334 | 10.9718 | 71.5557 | 1.3772 | 5.4605 | 35.2648 | 80.054 | 12.1194 | 158.7579 | 129.6516 | 224.9462 | 11.4322 | 50.1703 | 10.7046 | 166 | 10.4071 | 80.5885 | 262.9695 | 0.18182
3943 | 885.8452 | 10.4187 | 76.7333 | 105.035 | 49.635 | 14.2002 | 97.2212 | 2.0061 | 6.2162 | 37.8189 | 112.5189 | 24.0795 | 166.4057 | 167.5986 | 281.0529 | 23.3425 | 53.0982 | 10.9409 | 209 | 12.3275 | 110.2494 | 319.231 | 0.20662
3944 | 976.2258 | 6.6545 | 86.7723 | 118.0597 | 48.4154 | 15.3588 | 108.0409 | 4.5146 | 12.4242 | 34.6914 | 150.0744 | 26.8138 | 222.7282 | 208.4801 | 377.7578 | 28.6198 | 61.1651 | 11.7171 | 216 | 13.4121 | 130.284 | 399.2345 | 0.19936
3945 | 1042.0148 | 4.1236 | 86.126 | 129.7002 | 47.0868 | 16.621 | 113.1217 | 4.4652 | 14.434 | 29.3558 | 172.2402 | 25.2801 | 292.8522 | 237.173 | 459.149 | 28.06 | 71.068 | 11.9337 | 295 | 14.0067 | 134.4816 | 466.2775 | 0.30772
3946 | 1079.717 | 8.0195 | 86.8822 | 135.8128 | 48.3048 | 15.4639 | 123.5732 | 3.8419 | 13.7296 | 25.4339 | 177.7286 | 26.0675 | 332.499 | 254.925 | 498.3068 | 27.4765 | 78.89 | 11.859 | 294 | 14.6406 | 137.8493 | 478.6188 | 0.30605
3947 | 1094.6881 | 6.3912 | 89.0377 | 135.0018 | 47.0273 | 16.6775 | 128.2938 | 3.7096 | 14.2719 | 27.0285 | 178.0724 | 29.4692 | 351.5174 | 265.2571 | 520.5921 | 27.5338 | 82.0747 | 11.9907 | 265 | 14.7817 | 139.0944 | 481.8456 | 0.24955
3948 | 1100.3167 | 4.324 | 90.37 | 133.6186 | 48.1543 | 15.6069 | 127.1665 | 3.673 | 14.7909 | 28.9945 | 179.9143 | 30.2214 | 366.0698 | 271.9984 | 534.4383 | 28.3764 | 80.8867 | 12.0808 | 309 | 16.1319 | 138.4507 | 501.3703 | 0.27128
3949 | 1104.9708 | 4.0414 | 90.6638 | 139.0989 | 48.6038 | 15.1798 | 131.3024 | 3.7828 | 14.5955 | 36.1766 | 182.2746 | 30.238 | 372.3275 | 276.8765 | 535.5863 | 29.6038 | 81.458 | 11.979 | 257 | 15.8205 | 139.9518 | 508.8981 | 0.27182
3950 | 1103.8393 | 3.6887 | 92.2153 | 155.2103 | 47.0027 | 16.7009 | 135.0048 | 3.6982 | 14.4604 | 47.5534 | 183.0759 | 29.4598 | 402.9732 | 277.6452 | 531.4504 | 30.9371 | 83.6089 | 12.0341 | 254 | 15.9546 | 142.4432 | 503.0373 | 0.23417
3951 | 1075.5087 | 3.4002 | 80.9073 | 147.3454 | 50.3116 | 13.5575 | 133.1744 | 3.6398 | 15.4922 | 51.8604 | 179.8566 | 28.7423 | 410.5711 | 271.3717 | 514.0407 | 30.5578 | 82.9717 | 12.1074 | 241 | 15.0644 | 140.6254 | 494.7891 | 0.25753
3952 | 1032.5765 | 3.6367 | 54.2481 | 110.1824 | 50.7928 | 13.1003 | 122.843 | 3.2382 | 14.6512 | 46.7306 | 176.0639 | 26.3967 | 405.6513 | 257.8776 | 472.3116 | 24.4716 | 79.457 | 12.1328 | 201 | 12.5863 | 128.2594 | 466.0232 | 0.25454
3953 | 979.673 | 3.2045 | 41.5323 | 103.7568 | 50.6093 | 13.2747 | 108.5032 | 1.8393 | 13.2405 | 36.2805 | 165.4306 | 22.506 | 403.8829 | 216.5791 | 401.5486 | 13.4417 | 72.5078 | 12.3462 | 162 | 11.786 | 114.4008 | 404.0155 | 0.24761
3954 | 931.8969 | 2.5299 | 38.8079 | 99.5172 | 54.2694 | 9.7975 | 94.9114 | 1.1434 | 12.1525 | 28.7032 | 138.4093 | 18.5011 | 387.5659 | 163.4416 | 336.2227 | 8.6582 | 65.968 | 12.3434 | 146 | 11.6988 | 103.262 | 342.4675 | 0.14432
3955 | 896.0559 | 1.6822 | 37.0076 | 92.9471 | 55.6276 | 8.5073 | 75.4112 | 1.2004 | 11.6355 | 21.9262 | 111.1768 | 10.49 | 353.7668 | 130.809 | 298.8673 | 8.7921 | 62.5494 | 12.2858 | 135 | 11.6524 | 90.1956 | 300.9231 | 0.1511
3956 | 869.3159 | 1.0434 | 36.4857 | 91.2888 | 57.0441 | 7.1616 | 70.2195 | 1.1221 | 7.6345 | 15.8731 | 100.18 | 4.9771 | 332.0443 | 115.194 | 282.2277 | 8.1156 | 58.4322 | 11.9198 | 124 | 11.424 | 82.7008 | 270.9205 | 0.080184
3957 | 838.3961 | 1.8843 | 37.6014 | 90.9299 | 55.3044 | 8.8142 | 69.7235 | 1.1168 | 5.533 | 13.2916 | 95.7152 | 3.4663 | 322.2825 | 108.1177 | 272.4898 | 7.7002 | 53.9168 | 11.1542 | 116 | 11.2971 | 79.8914 | 252.4929 | 0.016121
3958 | 817.3052 | 2.4975 | 38.0664 | 91.5097 | 55.3406 | 8.7799 | 67.1397 | 1.3951 | 5.4683 | 13.4024 | 86.4182 | 3.8294 | 296.7138 | 102.7987 | 252.7816 | 7.8427 | 52.6202 | 10.8748 | 115 | 11.2761 | 73.5303 | 249.1043 | 0
3959 | 816.9117 | 1.6321 | 37.8962 | 94.8193 | 55.55 | 8.581 | 68.8228 | 1.4964 | 5.7722 | 15.9011 | 78.8994 | 5.4685 | 244.2211 | 98.9962 | 233.2143 | 8.3421 | 53.4947 | 10.9465 | 113 | 11.2791 | 50.2476 | 255.6041 | 0
3960 | 806.4233 | 1.2662 | 38.6955 | 95.6287 | 54.8552 | 9.241 | 68.76 | 1.4893 | 6.0315 | 17.8474 | 77.8927 | 6.0119 | 222.6662 | 96.5125 | 221.6895 | 8.3643 | 53.7971 | 10.9766 | 119 | 11.2318 | 42.34 | 262.8378 | 0
3961 | 790.1726 | 1.2028 | 38.4319 | 96.1476 | 53.8195 | 10.225 | 66.3939 | 1.4678 | 6.1392 | 17.7195 | 77.5837 | 6.0277 | 226.5397 | 96.4845 | 221.7164 | 8.5218 | 53.408 | 10.962 | 108 | 11.2631 | 61.749 | 266.6863 | 0
3962 | 791.0566 | 1.1957 | 37.8728 | 94.0469 | 53.6307 | 10.4043 | 61.2531 | 1.6638 | 6.1678 | 17.4447 | 77.0496 | 5.9616 | 253.5065 | 102.0963 | 228.5355 | 8.4179 | 53.0997 | 11.0179 | 113 | 11.2787 | 69.9889 | 267.3754 | 0
3963 | 786.5075 | 1.2379 | 37.2814 | 92.6655 | 54.3656 | 9.7062 | 60.5966 | 1.5154 | 6.198 | 18.0013 | 75.265 | 5.0941 | 259.0676 | 106.7562 | 223.5753 | 8.3473 | 52.5789 | 10.9504 | 107 | 11.2739 | 69.8339 | 265.4248 | 0
3964 | 785.0189 | 1.0741 | 36.7608 | 42.1916 | 56.8055 | 7.3882 | 62.7028 | 1.1987 | 5.7945 | 23.3424 | 71.8352 | 3.7169 | 246.2346 | 104.3204 | 218.952 | 8.1167 | 51.834 | 10.7667 | 115 | 11.2634 | 68.6784 | 267.0174 | 0
3965 | 784.2288 | 0.96915 | 41.6321 | 78.1179 | 57.6055 | 6.6282 | 65.3854 | 1.4991 | 5.5095 | 31.1046 | 69.9499 | 4.1496 | 254.7347 | 108.5842 | 216.5279 | 8.1587 | 51.3951 | 10.7016 | 114 | 11.2179 | 66.4497 | 276.6977 | 0.109
3966 | 823.0796 | 2.2187 | 48.8538 | 75.5457 | 54.5884 | 9.4945 | 74.9121 | 1.9557 | 5.2072 | 39.8491 | 76.9017 | 10.2961 | 257.8602 | 131.5122 | 228.9387 | 11.3179 | 51.6022 | 10.6953 | 150 | 11.6197 | 76.7666 | 310.8743 | 0.15365
3967 | 884.7922 | 3.6922 | 68.5768 | 95.311 | 47.6513 | 16.0847 | 103.349 | 2.1868 | 6.1913 | 48.5943 | 103.456 | 19.973 | 278.6974 | 166.6803 | 279.0007 | 23.5444 | 55.1311 | 10.9069 | 221 | 14.3971 | 105.2431 | 372.3249 | 0.17759
3968 | 968.1611 | 6.0935 | 82.8907 | 123.3027 | 49.2934 | 14.5247 | 118.9808 | 3.0553 | 11.2574 | 46.905 | 136.0797 | 23.6183 | 323.9491 | 205.5602 | 366.3038 | 30.993 | 63.5331 | 11.5128 | 197 | 14.7954 | 127.3771 | 443.9497 | 0.24794
3969 | 1051.4751 | 7.8974 | 88.3069 | 138.2493 | 46.6445 | 17.0411 | 122.6077 | 3.4966 | 14.3716 | 38.4232 | 155.6399 | 23.5011 | 374.1117 | 238.6852 | 441.4469 | 32.2571 | 74.4974 | 11.7794 | 299 | 14.5562 | 135.5553 | 498.5415 | 0.19495
3970 | 1074.0116 | 8.0501 | 88.5269 | 127.2588 | 46.5315 | 17.1485 | 125.2644 | 3.6113 | 14.307 | 32.2111 | 164.9878 | 25 | 427.5499 | 260.6837 | 485.1154 | 32.0418 | 84.7406 | 11.3847 | 287 | 15.9227 | 140.0535 | 516.9295 | 0.21124
3971 | 1072.0404 | 8.1752 | 93.0851 | 170.0212 | 45.8689 | 17.778 | 126.7379 | 3.97 | 13.5316 | 30.9188 | 169.914 | 24.6186 | 447.7198 | 269.796 | 519.2702 | 32.4176 | 90.9227 | 11.6426 | 266 | 15.51 | 141.5556 | 519.2093 | 0.26513
3972 | 1074.5712 | 9.3276 | 94.1483 | 160.5311 | 46.3892 | 17.2837 | 131.7431 | 4.2003 | 13.0584 | 34.3192 | 172.601 | 24.5787 | 448.1608 | 272.6453 | 536.1899 | 33.1933 | 90.9304 | 11.876 | 274 | 15.1403 | 140.514 | 523.04 | 0.19974
3973 | 1081.4943 | 10.3612 | 93.7064 | 155.3899 | 47.9513 | 15.7997 | 131.7477 | 4.1976 | 9.3288 | 42.8475 | 168.825 | 25.0827 | 450.8698 | 275.98 | 530.5646 | 33.5307 | 90.1717 | 11.8854 | 251 | 15.2767 | 139.3652 | 535.584 | 0.20875
3974 | 1072.3322 | 9.6171 | 93.9137 | 135.8595 | 47.8234 | 15.9212 | 135.234 | 4.1243 | 11.1587 | 50.5225 | 165.1873 | 24.5146 | 446.4651 | 278.6347 | 512.638 | 32.6595 | 98.1854 | 11.8105 | 223 | 14.9361 | 139.8828 | 546.7927 | 0.20293
3975 | 1059.8589 | 6.0294 | 81.9382 | 162.2435 | 46.089 | 17.5689 | 133.5558 | 3.7839 | 13.6957 | 50.8758 | 167.7756 | 24.4338 | 436.5136 | 273.5846 | 500.2264 | 31.6738 | 108.2206 | 11.7817 | 240 | 13.9355 | 136.5767 | 535.4237 | 0.15898
3976 | 1040.8289 | 3.4902 | 58.3285 | 118.385 | 50.1686 | 13.6933 | 117.753 | 3.5329 | 14.4617 | 42.8048 | 169.4594 | 23.6315 | 403.8588 | 256.2187 | 467.7962 | 26.1783 | 108.0735 | 11.8219 | 189 | 12.9656 | 123.5654 | 481.4691 | 0.19574
3977 | 993.5058 | 2.6535 | 48.1748 | 87.2976 | 55.253 | 8.8631 | 102.3615 | 3.0045 | 14.5369 | 32.0445 | 162.7084 | 25.7628 | 375.7661 | 219.0051 | 405.4249 | 15.0898 | 100.1976 | 11.8025 | 160 | 12.946 | 113.7133 | 402.2113 | 0.11044
3978 | 948.9202 | 3.1585 | 45.8435 | 91.4047 | 56.5298 | 7.6502 | 94.1402 | 1.7489 | 12.9616 | 26.4158 | 140.5205 | 21.2575 | 340.4008 | 170.5394 | 335.5635 | 8.6479 | 87.5728 | 11.765 | 152 | 14.3057 | 104.6653 | 341.3844 | 0.056147
3979 | 908.8803 | 2.5222 | 43.5612 | 93.8004 | 56.5377 | 7.6426 | 79.4552 | 1.2706 | 9.649 | 21.626 | 117.3442 | 9.3143 | 312.8488 | 138.3367 | 296.9031 | 8.1601 | 71.0065 | 11.7349 | 129 | 14.4355 | 91.1343 | 293.118 | 0.0285
3980 | 872.7096 | 2.5934 | 39.2313 | 93.2836 | 55.9875 | 8.1653 | 72.9138 | 1.137 | 6.5389 | 17.8275 | 108.0051 | 4.0234 | 280.4634 | 125.4346 | 280.7602 | 7.971 | 57.532 | 11.5441 | 127 | 12.9721 | 82.2999 | 249.867 | 0.012556
3981 | 839.1377 | 3.0559 | 39.1273 | 92.1556 | 54.7709 | 9.3211 | 73.3637 | 1.1842 | 5.3716 | 17.1115 | 106.1907 | 3.7626 | 253.0257 | 119.9595 | 268.211 | 7.873 | 51.5694 | 11.4 | 126 | 12.2891 | 75.6373 | 229.0254 | 0.0015444
3982 | 820.7268 | 2.6756 | 42.1114 | 79.9166 | 55.9665 | 8.1853 | 74.8524 | 1.5573 | 5.4059 | 17.6852 | 100.0602 | 5.4304 | 221.3519 | 118.0673 | 249.0717 | 8.1234 | 50.3649 | 11.6216 | 121 | 12.2144 | 40.4451 | 229.888 | 0
3983 | 809.8766 | 1.5978 | 44.5832 | 106.6054 | 56.6535 | 7.5326 | 76.9251 | 1.5504 | 6.3153 | 18.0539 | 88.5077 | 6.3052 | 198.3954 | 117.0729 | 246.5656 | 8.3011 | 50.7061 | 11.7786 | 126 | 12.2536 | 47.9351 | 238.5529 | 0
3984 | 816.4669 | 1.2556 | 45.0511 | 100.2524 | 55.8065 | 8.3373 | 77.2154 | 1.4486 | 6.4033 | 17.8 | 81.2243 | 6.2789 | 173.8765 | 113.7952 | 253.731 | 8.3852 | 50.9853 | 11.7963 | 126 | 12.2446 | 51.69 | 247.0042 | 0
3985 | 807.5468 | 1.1989 | 44.4719 | 98.5609 | 55.5806 | 8.5519 | 75.5871 | 1.4814 | 6.1706 | 17.7073 | 79.5289 | 6.2877 | 168.0484 | 111.1324 | 255.1621 | 8.3975 | 51.2262 | 11.7729 | 116 | 12.255 | 51.6084 | 252.0978 | 0
3986 | 803.8042 | 1.1329 | 44.5993 | 98.7708 | 56.3368 | 7.8335 | 73.9878 | 1.4924 | 6.1123 | 18.0294 | 79.8889 | 6.2383 | 171.4956 | 116.7991 | 245.0944 | 8.2682 | 51.1464 | 11.7744 | 114 | 12.2801 | 51.4922 | 251.6538 | 0
3987 | 801.6318 | 1.1416 | 44.6378 | 97.9767 | 55.8466 | 8.2992 | 73.508 | 1.6801 | 6.4443 | 19.8094 | 79.9643 | 6.2749 | 183.7319 | 124.6943 | 230.9909 | 8.3648 | 50.4338 | 11.7887 | 117 | 12.2662 | 51.5472 | 251.5357 | 0
3988 | 799.9835 | 1.8061 | 43.6248 | 94.7041 | 54.0849 | 9.9728 | 72.9473 | 1.4718 | 6.5863 | 25.3618 | 76.7821 | 5.0798 | 185.5868 | 124.2526 | 219.6955 | 8.0903 | 49.6645 | 11.5922 | 139 | 12.2463 | 51.7973 | 251.6008 | 0
3989 | 820.41 | 3.232 | 45.6238 | 94.0096 | 55.8168 | 8.3275 | 73.9941 | 1.1515 | 6.0933 | 31.7442 | 72.8558 | 4.742 | 194.0275 | 121.622 | 226.8872 | 7.9298 | 49.0015 | 11.2289 | 135 | 12.1743 | 51.291 | 256.5057 | 0.034786
3990 | 877.9333 | 2.9628 | 63.2657 | 104.3887 | 53.6058 | 10.4279 | 78.9242 | 1.4601 | 5.8433 | 39.8165 | 78.4317 | 10.3698 | 197.562 | 136.0221 | 259.2479 | 11.3922 | 49.2388 | 10.9024 | 174 | 12.4958 | 51.7276 | 289.7962 | 0.066921
3991 | 923.1316 | 4.7737 | 71.0435 | 121.7652 | 48.8509 | 14.9451 | 95.5629 | 2.5601 | 7.4828 | 47.9711 | 105.5005 | 20.0097 | 222.132 | 174.2782 | 309.6187 | 23.4893 | 52.6697 | 11.0232 | 220 | 15.8937 | 63.0952 | 351.4821 | 0.12231
3992 | 986.8266 | 9.0319 | 87.4969 | 149.8277 | 45.9634 | 17.6883 | 111.3905 | 3.9203 | 10.9569 | 50.5806 | 141.6447 | 23.3787 | 252.6362 | 213.8989 | 371.3355 | 29.7405 | 61.2424 | 11.7868 | 203 | 15.7727 | 70.4925 | 420.6434 | 0.14162
3993 | 1055.9376 | 8.8224 | 94.8933 | 171.0361 | 49.3302 | 14.4897 | 120.4026 | 4.1516 | 13.1075 | 48.6121 | 162.411 | 24.2384 | 308.7325 | 240.2534 | 438.374 | 30.6819 | 73.1218 | 12.0331 | 264 | 15.5567 | 77.6677 | 470.3571 | 0.14662
3994 | 1093.5762 | 5.0676 | 95.1069 | 176.8677 | 47.7274 | 16.0125 | 129.6076 | 3.733 | 12.8967 | 43.7005 | 168.8862 | 25.0341 | 353.9422 | 257.2778 | 479.2356 | 31.6087 | 81.1973 | 11.978 | 282 | 16.0277 | 74.6452 | 497.2338 | 0.12576
3995 | 1095.8007 | 3.6474 | 94.8669 | 177.3864 | 48.1386 | 15.6218 | 137.4065 | 3.9233 | 10.7816 | 41.4145 | 172.1111 | 25.241 | 377.6476 | 267.7541 | 491.9628 | 32.5601 | 82.9728 | 11.9301 | 269 | 15.6649 | 71.2499 | 507.6136 | 0.15608
3996 | 1079.9643 | 3.4892 | 94.2763 | 155.5875 | 46.2632 | 17.4034 | 139.7818 | 4.0963 | 10.0984 | 42.8581 | 175.7788 | 24.7739 | 385.4855 | 272.5918 | 492.4596 | 32.2881 | 82.5155 | 11.8114 | 258 | 16.593 | 69.4388 | 499.9516 | 0.26983
3997 | 1071.2436 | 3.398 | 95.6131 | 176.6839 | 47.1996 | 16.5138 | 136.7121 | 3.7626 | 9.0165 | 47.4994 | 181.2278 | 23.646 | 393.4635 | 273.1885 | 490.1704 | 31.7665 | 83.591 | 12.0032 | 244 | 14.7201 | 68.4434 | 489.4045 | 0.23398
3998 | 1075.2469 | 3.505 | 95.8537 | 176.0707 | 46.0298 | 17.6251 | 137.7724 | 3.6545 | 6.9802 | 54.0598 | 185.9826 | 25.832 | 404.4545 | 273.6144 | 487.2902 | 31.233 | 86.7454 | 12.0218 | 239 | 15.871 | 52.0706 | 480.0354 | 0.11693
3999 | 1075.2991 | 4.1337 | 88.2829 | 182.9819 | 47.8414 | 15.9041 | 138.7355 | 3.5322 | 6.4344 | 58.5612 | 187.8684 | 27.3245 | 420.6981 | 269.2105 | 473.8651 | 30.2588 | 88.3486 | 11.9681 | 241 | 14.9674 | 57.3346 | 476.907 | 0.20354
4000 | 1053.0294 | 3.2028 | 59.9817 | 135.5535 | 49.4447 | 14.381 | 126.3428 | 3.6089 | 8.8795 | 54.8519 | 185.8361 | 27.4433 | 421.343 | 253.7819 | 443.2355 | 24.9076 | 86.7008 | 12.1593 | 228 | 12.3946 | 44.3142 | 451.4115 | 0.13772
4001 | 995.6873 | 2.7256 | 42.1328 | 77.531 | 52.3855 | 11.5872 | 108.999 | 3.0138 | 12.2625 | 43.9121 | 173.576 | 26.4806 | 390.5509 | 212.7678 | 399.5708 | 13.9329 | 81.2135 | 12.5398 | 173 | 11.7551 | 44.3142 | 394.8662 | 0.11815
4002 | 935.2746 | 2.2885 | 34.609 | 96.0817 | 55.8461 | 8.2996 | 92.592 | 2.0086 | 8.711 | 34.2788 | 150.7614 | 19.8374 | 346.0558 | 159.7295 | 360.5145 | 8.1816 | 73.998 | 12.819 | 172 | 11.6168 | 34.2489 | 343.8684 | 0.055478
4003 | 902.6221 | 1.7048 | 31.4356 | 75.8974 | 56.5242 | 7.6554 | 76.7212 | 1.3428 | 5.682 | 25.4304 | 129.128 | 8.3854 | 302.2191 | 129.5632 | 328.8899 | 7.9611 | 67.1382 | 12.8688 | 148 | 11.8995 | 41.4862 | 299.731 | 0.057318
4004 | 882.7465 | 1.8577 | 29.9642 | 64.5723 | 56.5974 | 7.5859 | 69.6891 | 1.6814 | 5.3649 | 18.5806 | 112.867 | 3.6483 | 276.6556 | 113.8462 | 300.1407 | 7.7285 | 60.1333 | 12.3748 | 132 | 10.7474 | 57.2053 | 260.5147 | 0.023037
4005 | 838.3858 | 2.7828 | 36.1795 | 71.3093 | 56.5882 | 7.5947 | 69.7205 | 2.1911 | 5.253 | 16.4291 | 97.9425 | 3.7016 | 253.5453 | 99.1709 | 269.6647 | 8.0143 | 55.0724 | 11.7742 | 134 | 10.1119 | 44.3142 | 239.3118 | 0.0031472
4006 | 830.3651 | 2.7272 | 40.2963 | 78.4506 | 56.6054 | 7.5784 | 69.6456 | 1.7458 | 5.519 | 18.3835 | 85.4034 | 5.4151 | 197.3454 | 94.3617 | 246.0045 | 8.1329 | 52.6604 | 11.6136 | 119 | 9.9139 | 44.3142 | 240.5398 | 0
4007 | 827.9522 | 1.897 | 42.9668 | 59.3986 | 54.3655 | 9.7062 | 67.3129 | 1.5861 | 6.2572 | 21.3961 | 77.6294 | 6.3794 | 159.784 | 97.5442 | 240.3132 | 8.5336 | 51.7979 | 11.2461 | 116 | 10.1485 | 34.3152 | 245.4154 | 0
4008 | 809.8581 | 1.319 | 44.3371 | 98.4789 | 54.2704 | 9.7966 | 51.4425 | 1.5443 | 6.2058 | 22.2188 | 74.6603 | 6.3352 | 160.289 | 97.053 | 234.1522 | 8.417 | 52.1947 | 11.0282 | 122 | 10.1218 | 41.6371 | 243.6272 | 0
4009 | 796.8435 | 1.2525 | 44.3866 | 67.5947 | 56.18 | 7.9825 | 47.4396 | 1.3918 | 6.1194 | 21.9914 | 73.5835 | 6.2636 | 165.3237 | 92.5135 | 228.3809 | 8.3052 | 52.522 | 10.9973 | 119 | 10.1667 | 43.6354 | 242.7436 | 0
4010 | 787.4423 | 1.3183 | 44.3916 | 98.1844 | 56.5484 | 7.6325 | 47.671 | 1.4101 | 6.0254 | 22.2145 | 73.2712 | 6.3099 | 162.747 | 88.9342 | 228.5167 | 8.5417 | 52.3372 | 10.9904 | 120 | 10.3251 | 44.2722 | 244.4026 | 0
4011 | 783.2931 | 1.2057 | 44.0177 | 86.9052 | 55.7604 | 8.3811 | 47.8726 | 1.3487 | 5.9694 | 23.6599 | 72.6363 | 5.9746 | 159.7553 | 87.1341 | 222.7361 | 8.1721 | 52.111 | 11.0139 | 122 | 10.2796 | 44.8691 | 245.4118 | 0
4012 | 786.6753 | 1.2078 | 42.6875 | 77.3062 | 57.1292 | 7.0807 | 46.9627 | 1.314 | 6.0057 | 28.8636 | 69.8081 | 4.4742 | 144.8521 | 85.3676 | 214.8054 | 7.8799 | 51.6084 | 10.845 | 119 | 10.1601 | 44.1499 | 242.1107 | 0
4013 | 798.1989 | 0.96471 | 50.0987 | 69.6231 | 56.0896 | 8.0684 | 48.0307 | 1.1256 | 5.7976 | 36.1382 | 67.443 | 4.5674 | 153.1644 | 95.0747 | 209.5453 | 7.7561 | 51.0825 | 10.6972 | 122 | 9.9293 | 57.3183 | 246.3924 | 0.03781
4014 | 823.3882 | 1.8892 | 64.2905 | 123.7635 | 52.6185 | 11.3658 | 58.0996 | 1.1196 | 5.3847 | 44.7431 | 70.1559 | 10.504 | 185.7491 | 126.1735 | 216.6283 | 11.7428 | 51.3774 | 10.6796 | 160 | 10.7638 | 34.1608 | 280.6763 | 0.063753
4015 | 893.1878 | 3.4708 | 79.7787 | 133.4539 | 49.2003 | 14.6131 | 82.7924 | 2.1294 | 5.4879 | 52.3346 | 82.2131 | 21.9882 | 232.0685 | 167.433 | 257.3168 | 22.7705 | 54.3867 | 10.9514 | 218 | 14.2679 | 41.8234 | 341.9839 | 0.06857
4016 | 986.0609 | 3.9468 | 89.0546 | 135.8082 | 46.5201 | 17.1594 | 102.6111 | 3.9399 | 11.0782 | 52.5249 | 112.701 | 25.6583 | 289.9023 | 206.1588 | 327.8297 | 28.7476 | 61.4607 | 11.5613 | 215 | 15.1951 | 43.9084 | 415.7484 | 0.088923
4017 | 1055.8278 | 7.8031 | 94.2968 | 171.602 | 47.7037 | 16.035 | 115.6891 | 4.503 | 11.4357 | 47.7941 | 148.5725 | 23.5772 | 346.057 | 236.5867 | 396.8019 | 30.9362 | 73.1545 | 11.899 | 318 | 15.4519 | 58.1697 | 473.6654 | 0.1215
4018 | 1079.3474 | 10.5897 | 98.5888 | 194.5975 | 48.5636 | 15.2181 | 112.338 | 3.8856 | 9.5148 | 44.0961 | 168.3889 | 23.6519 | 366.2164 | 252.3216 | 458.5852 | 31.3768 | 90.2582 | 11.9248 | 267 | 16.9234 | 67.8855 | 496.6201 | 0.12968
4019 | 1083.1834 | 8.8186 | 97.7922 | 166.2606 | 46.441 | 17.2345 | 117.5174 | 3.917 | 13.8658 | 39.2885 | 175.3471 | 23.9221 | 375.5192 | 255.6395 | 484.3264 | 31.6827 | 102.6853 | 11.9085 | 260 | 18.0447 | 67.1349 | 499.2156 | 0.16494
4020 | 1081.501 | 5.2786 | 94.99 | 176.143 | 47.798 | 15.9453 | 116.2541 | 4.1374 | 12.5028 | 34.1043 | 177.8645 | 22.2233 | 378.798 | 262.5433 | 475.4579 | 32.5308 | 103.507 | 11.8834 | 247 | 16.1798 | 66.6442 | 493.5634 | 0.15996
4021 | 1086.1221 | 3.7684 | 95.7818 | 194.2714 | 48.1029 | 15.6557 | 117.7222 | 4.0077 | 9.9997 | 36.4945 | 181.5148 | 21.9752 | 384.6129 | 267.2507 | 465.1606 | 31.8115 | 103.0928 | 11.8769 | 245 | 15.759 | 68.7465 | 486.6237 | 0.21501
4022 | 1089.3401 | 3.5278 | 97.8771 | 189.2363 | 48.2209 | 15.5436 | 124.0125 | 3.6765 | 12.7513 | 42.4678 | 187.7504 | 22.6461 | 401.381 | 260.0606 | 452.3898 | 31.3154 | 108.565 | 11.9375 | 228 | 16.5535 | 68.7916 | 478.7092 | 0.13213
4023 | 1080.8483 | 3.6348 | 90.2385 | 185.1588 | 47.8096 | 15.9343 | 102.445 | 3.6618 | 13.6842 | 43.6452 | 183.2391 | 22.6762 | 420.397 | 249.4081 | 434.1459 | 31.5007 | 112.9342 | 12.0715 | 227 | 14.605 | 63.2505 | 467.1149 | 0.15941
4024 | 1045.4748 | 3.6103 | 60.8902 | 153.5363 | 51.9244 | 12.0253 | 91.6515 | 3.7455 | 9.005 | 38.299 | 159.2682 | 22.2222 | 419.4025 | 237.2653 | 411.3342 | 26.0928 | 109.7596 | 12.2199 | 210 | 12.8039 | 55.599 | 431.2715 | 0.14438
4025 | 997.0209 | 2.8922 | 44.9232 | 120.0496 | 54.2584 | 9.808 | 80.4006 | 2.9296 | 6.9495 | 29.3156 | 131.6519 | 24.1102 | 370.2805 | 198.0765 | 387.5792 | 14.0213 | 104.0731 | 12.2615 | 177 | 11.6441 | 50.3108 | 370.3603 | 0.072615
4026 | 955.0519 | 2.1901 | 36.2049 | 71.857 | 53.9508 | 10.1002 | 68.7434 | 1.5657 | 7.8703 | 23.0062 | 113.595 | 21.6012 | 329.1694 | 148.5879 | 355.4261 | 7.7895 | 98.1439 | 12.3089 | 157 | 10.9166 | 48.853 | 320.2699 | 0.05853
4027 | 922.0233 | 1.5357 | 31.1038 | 76.9385 | 57.2344 | 6.9807 | 56.0151 | 1.0133 | 10.7862 | 21.5487 | 105.4402 | 10.4576 | 285.6187 | 124.7776 | 313.2449 | 7.7933 | 83.31 | 12.2923 | 139 | 10.7098 | 27.0248 | 286.1238 | 0.043457
4028 | 881.2633 | 1.8851 | 30.3759 | 71.66 | 57.128 | 7.0819 | 46.1515 | 1.199 | 8.2529 | 21.6505 | 102.41 | 5.2486 | 238.7309 | 114.4978 | 279.9508 | 7.7699 | 63.3339 | 11.9202 | 125 | 10.0613 | 32.4922 | 256.2504 | 0.011128
4029 | 863.3158 | 2.9709 | 36.4437 | 76.4596 | 56.5936 | 7.5895 | 48.808 | 1.1855 | 6.139 | 21.4326 | 99.0043 | 5.2522 | 199.5872 | 102.3938 | 264.5579 | 7.6098 | 52.8747 | 12.0051 | 131 | 10.3962 | 34.8548 | 237.8756 | 0.0018202
4030 | 850.6889 | 2.7674 | 40.2539 | 82.4659 | 56.5599 | 7.6215 | 46.8872 | 1.2399 | 6.2005 | 21.7375 | 92.5869 | 7.0332 | 179.9754 | 94.0991 | 255.6387 | 7.9017 | 50.9066 | 12.1867 | 120 | 10.2865 | 34.8787 | 236.7041 | 0
4031 | 826.7565 | 1.6671 | 40.7543 | 85.1315 | 56.6018 | 7.5817 | 49.2144 | 1.3998 | 6.6463 | 22.3862 | 85.1617 | 7.2418 | 171.5641 | 92.5692 | 248.3703 | 8.2735 | 50.8206 | 12.2417 | 123 | 10.2399 | 34.7517 | 239.0203 | 0
4032 | 813.0376 | 1.2203 | 40.8738 | 85.6139 | 55.7705 | 8.3715 | 45.9562 | 1.4022 | 6.4421 | 23.1761 | 81.3061 | 6.5194 | 162.3169 | 91.3087 | 242.0307 | 8.2027 | 51.3639 | 12.0018 | 121 | 10.0412 | 35.1136 | 236.3326 | 0
4033 | 820.1686 | 1.2186 | 41.2464 | 84.6045 | 55.5701 | 8.5619 | 47.7017 | 1.3733 | 6.4726 | 23.7568 | 80.2449 | 6.3178 | 161.9885 | 90.9478 | 238.9121 | 8.2888 | 51.9193 | 11.2742 | 120 | 10.2723 | 45.0214 | 236.6641 | 0
4034 | 816.9321 | 1.3937 | 40.6567 | 98.3356 | 54.155 | 9.9062 | 46.3942 | 1.6164 | 6.3967 | 23.2341 | 80.0297 | 6.2988 | 163.3719 | 91.0114 | 230.5061 | 8.2347 | 51.9191 | 10.9274 | 116 | 10.4787 | 34.877 | 237.9835 | 0
4035 | 813.1169 | 1.2768 | 40.1681 | 68.2264 | 55.7195 | 8.42 | 47.486 | 1.5755 | 6.6103 | 23.8844 | 79.8196 | 6.1645 | 139.3399 | 89.4746 | 220.3299 | 8.1074 | 51.4773 | 10.9214 | 116 | 10.3257 | 27.2299 | 237.4242 | 0
4036 | 810.1097 | 1.5569 | 49.3083 | 81.8813 | 56.6728 | 7.5143 | 43.5518 | 1.2042 | 6.3315 | 29.1371 | 77.771 | 4.4964 | 132.5239 | 85.8632 | 217.2743 | 7.8837 | 50.7608 | 10.7634 | 116 | 10.2252 | 27.7118 | 238.9127 | 0
4037 | 821.5677 | 1.156 | 54.2022 | 99.5102 | 56.5815 | 7.601 | 47.3118 | 0.99938 | 5.986 | 35.9676 | 75.4867 | 4.5222 | 159.0939 | 90.4717 | 213.3185 | 7.6347 | 50.1711 | 10.6323 | 120 | 10.0048 | 29.5239 | 246.4081 | 0.044994
4038 | 866.682 | 1.5285 | 70.6299 | 117.3438 | 52.8051 | 11.1887 | 50.7707 | 0.97581 | 5.683 | 43.7712 | 76.7922 | 10.8479 | 191.7761 | 116.6412 | 218.5838 | 11.0267 | 50.2398 | 10.5972 | 169 | 10.3626 | 37.9573 | 276.1986 | 0.14181
4039 | 934.0318 | 5.0628 | 85.6119 | 132.5181 | 47.0963 | 16.6119 | 70.82 | 1.9251 | 5.9075 | 48.3423 | 90.0645 | 20.3622 | 233.1848 | 157.6871 | 240.2534 | 21.0403 | 53.6053 | 11.0292 | 236 | 12.9906 | 52.7762 | 328.4633 | 0.16193
4040 | 989.8902 | 9.4897 | 92.0335 | 174.5455 | 47.1542 | 16.557 | 102.9413 | 2.8164 | 6.4316 | 46.1552 | 124.4263 | 24.703 | 304.3152 | 197.2973 | 307.6203 | 27.1113 | 61.2541 | 11.6643 | 234 | 13.8086 | 60.2041 | 387.0426 | 0.22286
4041 | 1023.6369 | 8.4317 | 95.4256 | 186.0863 | 48.3454 | 15.4254 | 107.9004 | 3.2524 | 11.187 | 40.2969 | 158.5124 | 28.2411 | 351.2152 | 219.2163 | 404.5462 | 27.8353 | 70.771 | 11.8392 | 323 | 14.3235 | 60.8084 | 439.9402 | 0.22567
4042 | 1064.1434 | 4.4989 | 95.3536 | 185.8115 | 47.7491 | 15.9918 | 111.6318 | 4.0464 | 13.6149 | 32.9852 | 171.6768 | 28.1815 | 361.1088 | 228.1328 | 466.1168 | 28.1156 | 78.3869 | 11.8432 | 297 | 15.9263 | 62.4531 | 467.9645 | 0.26131
4043 | 1093.3874 | 3.3576 | 96.1409 | 164.4156 | 48.4277 | 15.3472 | 117.8482 | 4.0545 | 14.3895 | 29.3691 | 175.5762 | 29.0168 | 374.4959 | 235.1428 | 482.1588 | 28.3128 | 82.3807 | 11.9712 | 259 | 14.7614 | 34.5166 | 481.6562 | 0.21677
4044 | 1087.0645 | 3.4727 | 97.0841 | 201.2743 | 48.4918 | 15.2863 | 112.8542 | 3.9399 | 11.682 | 29.7581 | 179.967 | 31.272 | 375.8668 | 242.8807 | 477.8593 | 29.0647 | 84.0181 | 11.9871 | 290 | 13.4849 | 42.1497 | 493.3144 | 0.20885
4045 | 1068.7335 | 3.4169 | 99.425 | 175.1355 | 45.6984 | 17.9399 | 117.9489 | 4.1445 | 7.2715 | 33.2867 | 184.038 | 31.1016 | 381.0011 | 246.3911 | 465.1098 | 29.2431 | 83.8582 | 11.9094 | 259 | 15.0218 | 44.2072 | 491.8712 | 0.20391
4046 | 1059.729 | 3.4252 | 93.2292 | 201.5448 | 46.7067 | 16.9821 | 117.1102 | 4.2576 | 11.2785 | 37.767 | 184.0885 | 29.5192 | 395.5425 | 247.7217 | 442.572 | 29.5671 | 82.6979 | 12.0235 | 240 | 15.631 | 44.6576 | 479.2288 | 0.23618
4047 | 1017.4231 | 3.6256 | 89.3839 | 171.8966 | 46.8772 | 16.8202 | 95.1727 | 3.817 | 15.3672 | 39.164 | 172.7338 | 28.4145 | 397.8938 | 248.6106 | 413.489 | 28.45 | 80.9935 | 12.1329 | 216 | 10.8414 | 44.7875 | 459.6112 | 0.14876
4048 | 979.0118 | 3.1944 | 61.8106 | 110.3122 | 51.0815 | 12.826 | 86.5878 | 3.2052 | 14.7484 | 34.7447 | 147.0899 | 27.5291 | 385.733 | 237.9242 | 389.7257 | 18.502 | 78.1109 | 12.1412 | 202 | 8.4517 | 57.6428 | 411.8879 | 0.12575
4049 | 947.2298 | 2.3102 | 42.3837 | 116.227 | 54.7256 | 9.3641 | 81.3307 | 2.6588 | 12.7711 | 26.5597 | 122.1072 | 26.4272 | 367.4837 | 194.9158 | 369.7313 | 11.3669 | 72.6999 | 12.0585 | 159 | 7.9024 | 34.9366 | 344.2619 | 0.12493
4050 | 900.3152 | 1.5595 | 32.3485 | 86.1642 | 57.1537 | 7.0574 | 70.0817 | 1.7178 | 13.3467 | 21.0461 | 110.2797 | 21.1281 | 314.3349 | 140.5602 | 337.755 | 8.7598 | 66.3156 | 12.0467 | 149 | 8.1429 | 41.4424 | 289.0736 | 0.12841
4051 | 867.5068 | 1.0496 | 28.8348 | 71.3838 | 57.622 | 6.6125 | 54.3428 | 1.1242 | 13.0204 | 19.2477 | 103.6673 | 9.501 | 260.8942 | 114.2292 | 306.8545 | 7.6297 | 61.3809 | 11.9971 | 128 | 8.1323 | 44.3561 | 248.2008 | 0.037934
4052 | 842.011 | 0.94748 | 29.2548 | 68.5745 | 57.5039 | 6.7247 | 42.6329 | 1.15 | 9.0697 | 17.9835 | 92.4473 | 4.4305 | 228.387 | 106.9294 | 285.0756 | 7.886 | 57.4674 | 11.7005 | 120 | 7.943 | 57.9051 | 222.2943 | 0.021836
4053 | 814.2114 | 1.9958 | 36.0261 | 55.752 | 56.7933 | 7.3998 | 43.8333 | 1.0852 | 6.6148 | 17.0421 | 79.7341 | 4.346 | 212.384 | 101.1423 | 279.48 | 7.8588 | 54.2979 | 11.0865 | 111 | 7.6338 | 34.7854 | 211.4588 | 0.0034199
4054 | 804.2707 | 2.4482 | 39.8418 | 84.2818 | 56.5937 | 7.5894 | 41.3579 | 1.2234 | 6.1284 | 18.3995 | 72.7238 | 5.361 | 183.9 | 95.2243 | 283.409 | 7.9547 | 53.2018 | 10.9839 | 110 | 7.8718 | 41.9187 | 213.5052 | 0
4055 | 806.6112 | 1.6846 | 39.8388 | 102.9852 | 56.6306 | 7.5544 | 43.3643 | 1.4942 | 6.54 | 20.5346 | 71.8423 | 6.7371 | 165.4479 | 93.1161 | 275.0609 | 8.3056 | 53.6704 | 10.9391 | 112 | 8.1224 | 44.3328 | 222.0927 | 0
4056 | 797.2923 | 1.3568 | 40.2208 | 94.9131 | 55.1131 | 8.996 | 45.6875 | 1.5404 | 6.55 | 21.5869 | 72.7894 | 7.0324 | 162.2078 | 94.1811 | 266.9496 | 8.4147 | 54.5102 | 10.901 | 134 | 7.9084 | 57.6033 | 225.8303 | 0
4057 | 792.3836 | 1.3653 | 40.3558 | 90.0872 | 54.5785 | 9.5039 | 42.1642 | 1.459 | 6.6089 | 22.3276 | 72.6308 | 6.9505 | 164.4117 | 93.8387 | 264.6037 | 8.4349 | 55.1941 | 10.9513 | 127 | 7.6279 | 34.5314 | 225.1635 | 0
4058 | 785.9643 | 1.2161 | 39.7516 | 88.4844 | 56.0814 | 8.0761 | 45.2723 | 1.4115 | 6.5954 | 22.6987 | 72.0119 | 7.1393 | 165.1796 | 92.9636 | 261.6716 | 8.2639 | 54.9236 | 10.9471 | 128 | 8.1327 | 30.5 | 226.5102 | 0
4059 | 769.4112 | 1.5615 | 39.8211 | 88.0269 | 57.2917 | 6.9263 | 41.2945 | 1.4156 | 6.46 | 23.0819 | 71.7195 | 6.8244 | 162.7875 | 91.9898 | 241.4937 | 8.2257 | 54.6967 | 10.9192 | 131 | 7.7469 | 28.5387 | 226.522 | 0
4060 | 770.4445 | 1.4564 | 39.8643 | 67.5928 | 54.7075 | 9.3813 | 42.7549 | 1.3573 | 6.279 | 25.1244 | 70.1337 | 5.0577 | 161.8216 | 88.5358 | 221.9507 | 8.1053 | 54.5091 | 10.7374 | 123 | 8.1222 | 27.9208 | 219.4105 | 0
4061 | 772.2248 | 0.94735 | 39.5682 | 98.5261 | 55.7099 | 8.429 | 41.2685 | 1.1193 | 5.9389 | 28.7105 | 68.1181 | 4.2021 | 141.2544 | 83.4661 | 212.5554 | 8.0176 | 53.7075 | 10.6494 | 120 | 7.6919 | 29.8116 | 210.8303 | 0.011991
4062 | 782.35 | 1.0967 | 38.1769 | 66.706 | 56.5757 | 7.6066 | 43.7526 | 0.99096 | 5.9642 | 32.5201 | 68.5001 | 4.2512 | 138.3842 | 79.8928 | 211.433 | 7.8163 | 52.9099 | 10.6129 | 124 | 7.8482 | 29.9841 | 212.9412 | 0.034315
4063 | 809.4113 | 1.0791 | 31.2216 | 89.376 | 56.5633 | 7.6183 | 41.0697 | 1.0212 | 5.9303 | 33.3229 | 74.5838 | 6.3559 | 149.445 | 80.1912 | 217.1779 | 7.844 | 52.5934 | 10.8892 | 125 | 8.1823 | 38.5208 | 220.3477 | 0.04984
4064 | 817.0507 | 0.97351 | 28.088 | 55.8556 | 56.6254 | 7.5593 | 41.8146 | 1.0351 | 11.7967 | 27.5971 | 92.8416 | 11.9407 | 159.7357 | 82.3054 | 229.6535 | 7.9577 | 52.7523 | 11.5209 | 122 | 7.8522 | 23.2272 | 225.0858 | 0.083462
4065 | 834.4327 | 1.0296 | 30.9859 | 74.6927 | 56.6271 | 7.5578 | 46.883 | 1.1843 | 14.1867 | 21.5634 | 116.9698 | 14.4026 | 182.498 | 84.2998 | 259.6635 | 7.8487 | 53.0668 | 11.7654 | 129 | 8.4045 | 33.5308 | 230.9816 | 0.088503
4066 | 878.7667 | 1.2637 | 31.9428 | 90.4677 | 55.7673 | 8.3745 | 43.5583 | 1.4982 | 11.6104 | 21.1107 | 133.2092 | 14.3449 | 206.0607 | 88.8709 | 279.8383 | 7.8525 | 53.758 | 11.756 | 133 | 8.5978 | 37.516 | 234.7306 | 0.11626
4067 | 895.3731 | 0.99273 | 31.5744 | 79.8436 | 56.3044 | 7.8643 | 45.2443 | 1.7297 | 7.1796 | 24.9229 | 139.9843 | 14.3599 | 217.0882 | 93.6151 | 287.2536 | 7.7768 | 54.2095 | 11.7239 | 132 | 8.7332 | 37.6905 | 234.9792 | 0.1851
4068 | 900.6417 | 1.1341 | 31.3597 | 54.6868 | 56.6766 | 7.5107 | 42.3376 | 2.2284 | 8.9967 | 28.263 | 141.3245 | 14.3731 | 224.3582 | 95.7416 | 278.2291 | 7.6716 | 53.5724 | 11.8845 | 137 | 8.5066 | 38.4226 | 236.04 | 0.17121
4069 | 887.1727 | 1.1061 | 31.4619 | 87.3161 | 56.5548 | 7.6264 | 45.7189 | 3.9867 | 12.93 | 27.5654 | 142.3048 | 14.5358 | 220.9389 | 97.5628 | 267.6225 | 7.7465 | 52.5969 | 12.1422 | 149 | 8.4577 | 38.1396 | 240.4178 | 0.14956
4070 | 879.0414 | 1.091 | 30.7035 | 95.2872 | 56.5547 | 7.6265 | 45.813 | 2.8968 | 14.44 | 24.3901 | 143.7903 | 15.6451 | 212.816 | 97.5197 | 283.1295 | 7.9838 | 52.3883 | 12.2606 | 138 | 8.2648 | 36.6752 | 249.4276 | 0.091726
4071 | 881.5092 | 1.1612 | 27.8353 | 93.0083 | 55.8183 | 8.3261 | 44.9324 | 1.2002 | 14.5333 | 19.0684 | 136.1508 | 14.8799 | 203.0246 | 97.8125 | 294.3406 | 8.1303 | 53.4521 | 12.2593 | 156 | 8.2203 | 35.8495 | 249.3281 | 0.051296
4072 | 875.3788 | 4.7592 | 26.6767 | 109.9276 | 56.3577 | 7.8137 | 48.1494 | 0.99275 | 11.0433 | 14.1246 | 115.1819 | 7.5166 | 195.6316 | 97.6509 | 286.7643 | 7.8271 | 54.9629 | 12.2111 | 153 | 8.1796 | 35.6296 | 233.8753 | 0.081922
4073 | 872.1338 | 7.6179 | 26.7346 | 84.5861 | 55.9034 | 8.2452 | 42.4769 | 1.1583 | 12.6313 | 12.402 | 95.8481 | 4.2254 | 192.6836 | 95.8859 | 266.3322 | 7.8976 | 56.4101 | 12.0833 | 152 | 8.4297 | 35.4468 | 218.9169 | 0.077
4074 | 841.1567 | 4.3085 | 26.5207 | 98.954 | 55.5211 | 8.6084 | 44.6665 | 1.1027 | 10.4587 | 12.746 | 83.7085 | 4.2137 | 171.8282 | 94.5661 | 244.0069 | 7.6503 | 57.9381 | 12.0758 | 151 | 8.0038 | 41.796 | 212.5861 | 0.050751
4075 | 820.3176 | 1.4995 | 26.5476 | 79.7091 | 56.3046 | 7.8641 | 43.7232 | 1.158 | 6.4695 | 13.6072 | 74.4382 | 4.1808 | 151.0993 | 91.718 | 238.0827 | 7.7898 | 57.5828 | 12.3284 | 157 | 8.3857 | 31.0732 | 211.548 | 0.038185
4076 | 819.6101 | 1.9274 | 31.5737 | 89.9767 | 56.6101 | 7.5738 | 45.3665 | 1.2909 | 5.5625 | 14.0026 | 70.7814 | 4.2468 | 153.3392 | 88.1875 | 235.7652 | 7.8939 | 55.2608 | 12.2265 | 147 | 8.0345 | 24.1293 | 212.8125 | 0.009206
4077 | 814.4225 | 2.6429 | 34.2105 | 97.9876 | 56.618 | 7.5664 | 44.471 | 1.5363 | 5.5913 | 14.4542 | 70.6379 | 5.161 | 175.7833 | 86.6444 | 231.7622 | 8.0665 | 53.862 | 12.1635 | 144 | 8.2454 | 29.0192 | 216.5947 | 0.0014023
4078 | 801.0999 | 2.5941 | 37.2738 | 112.058 | 56.5357 | 7.6445 | 45.9508 | 1.8268 | 5.9222 | 15.6407 | 71.4717 | 6.4847 | 186.2965 | 87.7125 | 232.3329 | 8.2041 | 53.9557 | 12.143 | 147 | 8.2308 | 31.1987 | 224.0614 | 0
4079 | 784.0366 | 1.6285 | 39.2453 | 94.6687 | 55.8355 | 8.3097 | 48.3329 | 1.6243 | 6.7417 | 16.0855 | 72.7589 | 7.0536 | 186.3231 | 92.1789 | 245.1109 | 8.4127 | 54.3114 | 12.164 | 125 | 8.2612 | 39.9441 | 229.6116 | 0
4080 | 777.238 | 1.1288 | 39.3853 | 112.7444 | 54.8122 | 9.2818 | 45.5625 | 1.4144 | 7.0512 | 15.7313 | 73.1894 | 6.9184 | 182.1139 | 94.3163 | 249.5733 | 8.2368 | 54.4107 | 11.8912 | 114 | 8.4136 | 24.2129 | 230.6994 | 0
4081 | 763.0892 | 1.1793 | 38.6384 | 106.6818 | 56.7875 | 7.4053 | 44.5399 | 1.4095 | 7.3861 | 15.8308 | 72.6173 | 6.8305 | 182.0226 | 92.9726 | 244.3937 | 8.113 | 54.3769 | 11.7999 | 112 | 8.2556 | 29.1723 | 230.5479 | 0
4082 | 754.2932 | 1.4664 | 38.4905 | 104.4407 | 56.1799 | 7.9826 | 44.738 | 1.4117 | 7.0454 | 15.9462 | 71.906 | 6.9101 | 183.3753 | 92.8545 | 236.8724 | 8.4417 | 54.3485 | 11.6408 | 112 | 7.9503 | 30.8085 | 231.8849 | 0
4083 | 749.703 | 1.3337 | 38.7122 | 103.5114 | 56.3305 | 7.8395 | 47.5509 | 1.4546 | 6.5503 | 15.6519 | 71.715 | 7.0136 | 177.1537 | 91.7742 | 225.05 | 8.4114 | 54.2919 | 11.2782 | 110 | 8.2472 | 30.9822 | 232.5654 | 0
4084 | 747.446 | 1.5309 | 38.3818 | 100.4925 | 56.5596 | 7.6219 | 43.4427 | 1.2971 | 6.9454 | 13.8876 | 69.9028 | 5.3924 | 173.0916 | 86.5669 | 215.4997 | 7.9404 | 53.8282 | 10.9098 | 111 | 8.3597 | 31.12 | 226.2803 | 0
4085 | 753.8292 | 1.2403 | 38.2543 | 88.274 | 55.8124 | 8.3317 | 45.5292 | 1.2616 | 6.3285 | 12.092 | 66.8886 | 4.3382 | 163.2401 | 81.3883 | 208.8587 | 7.9464 | 53.1622 | 10.7884 | 105 | 8.0377 | 40.1417 | 217.4862 | 0.020408
4086 | 762.6864 | 0.80861 | 36.7596 | 98.7126 | 55.5917 | 8.5413 | 42.0421 | 1.1733 | 6.0258 | 12.7409 | 66.5591 | 4.1958 | 161.067 | 80.3105 | 210.4167 | 7.9906 | 52.9142 | 10.7854 | 109 | 8.3831 | 31.0732 | 212.7026 | 0.039769
4087 | 779.903 | 1.2513 | 29.8219 | 99.4584 | 57.0664 | 7.1404 | 44.1151 | 1.052 | 7.9 | 12.9574 | 72.9269 | 4.2227 | 156.8952 | 81.2434 | 215.6638 | 7.8778 | 52.8746 | 11.0424 | 109 | 8.2767 | 31.0732 | 212.1105 | 0.059985
4088 | 791.3875 | 1.0643 | 26.6331 | 89.768 | 55.293 | 8.8251 | 44.1788 | 1.1059 | 12.9367 | 12.8974 | 93.0632 | 4.2194 | 150.5214 | 82.5355 | 227.5492 | 8.0116 | 52.8572 | 11.6475 | 110 | 8.2792 | 24.2181 | 214.133 | 0.10815
4089 | 805.837 | 0.87047 | 26.6299 | 74.7781 | 53.8849 | 10.1628 | 46.947 | 1.1308 | 14.6433 | 13.7299 | 115.0152 | 4.1861 | 150.9254 | 82.6121 | 253.7985 | 7.8212 | 53.1159 | 11.8909 | 119 | 8.555 | 28.9178 | 217.2578 | 0.13386
4090 | 820.2727 | 0.82583 | 26.5169 | 87.7401 | 56.5761 | 7.6061 | 46.1662 | 1.0994 | 12.08 | 16.5712 | 122.9744 | 4.1884 | 153.5374 | 82.2062 | 267.4614 | 7.6786 | 53.4442 | 11.9615 | 112 | 8.7022 | 31.0345 | 219.9155 | 0.129
4091 | 852.5803 | 0.75908 | 26.3936 | 87.8289 | 55.3417 | 8.7789 | 44.35 | 1.108 | 7.23 | 21.4747 | 127.0802 | 4.2405 | 170.3874 | 84.0779 | 270.3936 | 7.742 | 53.3291 | 12.25 | 119 | 8.1138 | 31.0933 | 222.6947 | 0.12392
4092 | 879.0637 | 0.83913 | 26.3757 | 86.6488 | 56.1279 | 8.0319 | 48.7765 | 1.2356 | 7.9836 | 23.3062 | 134.7422 | 4.2478 | 186.5033 | 88.865 | 265.9069 | 7.8032 | 53.4036 | 12.685 | 121 | 8.1732 | 30.9393 | 226.0522 | 0.14624
4093 | 871.6639 | 1.2838 | 26.4193 | 87.8644 | 57.3412 | 6.8793 | 45.9831 | 1.1685 | 12.6519 | 20.2193 | 141.1685 | 4.2411 | 194.445 | 94.7201 | 247.3255 | 7.8098 | 53.9378 | 12.904 | 129 | 8.3731 | 31.0293 | 228.3762 | 0.10745
4094 | 859.3209 | 1.4886 | 26.4816 | 97.3857 | 56.8301 | 7.3649 | 47.9096 | 1.0511 | 9.4845 | 16.1562 | 144.7216 | 5.2275 | 198.3156 | 99.309 | 247.1553 | 8.0962 | 54.1552 | 12.8155 | 125 | 8.1855 | 31.1576 | 229.5959 | 0.12132
4095 | 855.219 | 1.4785 | 26.4139 | 80.5089 | 56.4641 | 7.7125 | 46.5145 | 1.0258 | 5.929 | 14.8838 | 138.3712 | 6.7514 | 201.6103 | 105.6545 | 257.5 | 7.923 | 55.6216 | 12.5735 | 118 | 9.215 | 31.504 | 229.875 | 0.079733
4096 | 831.8083 | 1.7527 | 26.3831 | 98.3709 | 56.6041 | 7.5796 | 47.2806 | 1.0415 | 5.5598 | 14.6715 | 116.743 | 5.2173 | 199.2891 | 111.7787 | 258.2674 | 7.8076 | 57.3592 | 12.4751 | 119 | 9.3642 | 30.9862 | 226.111 | 0.092604
4097 | 824.4402 | 1.4275 | 26.9295 | 79.2842 | 56.6856 | 7.5022 | 50.3475 | 1.049 | 5.8579 | 13.1385 | 97.6995 | 4.1668 | 194.0385 | 111.4547 | 254.7241 | 7.8008 | 57.1414 | 12.4264 | 115 | 9.2755 | 39.8502 | 224.44 | 0.077385
4098 | 813.6911 | 1.0287 | 26.7101 | 97.1845 | 56.6026 | 7.581 | 45.4467 | 1.1149 | 10.5376 | 11.4021 | 92.3652 | 4.2497 | 192.2683 | 102.6366 | 246.8958 | 7.9428 | 56.3198 | 12.2234 | 108 | 8.319 | 23.969 | 224.6052 | 0.050409
4099 | 794.5322 | 1.5048 | 26.4664 | 77.798 | 55.7453 | 8.3954 | 47.4199 | 1.2779 | 11.6682 | 11.6864 | 90.7652 | 4.2332 | 182.7278 | 93.0963 | 246.2054 | 7.7336 | 55.7589 | 11.9853 | 112 | 7.483 | 30.6282 | 222.5474 | 0.043496
4100 | 792.8432 | 2.0417 | 27.6979 | 97.6145 | 56.3036 | 7.8651 | 43.6951 | 1.1946 | 7.5626 | 12.2511 | 83.7013 | 4.2116 | 173.8828 | 91.9995 | 255.0044 | 7.9509 | 55.2322 | 11.6043 | 117 | 7.6801 | 33.1274 | 223.475 | 0.014196
4101 | 798.1264 | 2.9446 | 34.8766 | 87.279 | 56.6387 | 7.5467 | 46.6297 | 1.0566 | 5.8282 | 11.5127 | 75.0973 | 6.4724 | 167.9762 | 91.2332 | 249.8311 | 7.7412 | 54.3569 | 10.9964 | 116 | 7.7529 | 31.3542 | 224.1296 | 0.001379
4102 | 787.5143 | 2.9746 | 38.422 | 100.2953 | 56.6048 | 7.5789 | 50.5353 | 1.2842 | 5.7634 | 12.3707 | 73.3196 | 13.222 | 157.9075 | 87.4695 | 231.3547 | 7.9967 | 53.9556 | 10.9418 | 113 | 7.7588 | 29.6255 | 223.6737 | 0
4103 | 768.7662 | 1.8384 | 38.2932 | 111.132 | 55.8905 | 8.2575 | 47.6083 | 1.5026 | 5.9193 | 15.2077 | 75.4426 | 17.1038 | 148.9071 | 86.7778 | 221.6631 | 8.3012 | 54.4955 | 11.336 | 108 | 7.9192 | 29.5649 | 226.2822 | 0
4104 | 762.252 | 1.1968 | 38.1226 | 105.2969 | 55.527 | 8.6028 | 51.3325 | 1.5163 | 6.5665 | 17.2072 | 76.2348 | 13.1887 | 142.2085 | 87.0871 | 225.621 | 8.2769 | 55.0383 | 11.2615 | 107 | 7.4969 | 30.1057 | 230.8734 | 0
4105 | 758.2124 | 1.138 | 38.1053 | 101.8346 | 56.3085 | 7.8604 | 45.6933 | 1.5071 | 6.9519 | 17.6972 | 75.415 | 8.3244 | 141.2737 | 85.5795 | 224.1665 | 8.3693 | 55.1334 | 11.1274 | 102 | 7.6987 | 29.8614 | 234.423 | 0
4106 | 748.186 | 1.1287 | 38.1965 | 89.8531 | 56.5406 | 7.6399 | 47.9176 | 1.7823 | 6.6438 | 17.7361 | 74.8034 | 6.9693 | 143.3963 | 83.8237 | 224.7337 | 8.3159 | 55.1112 | 11.173 | 105 | 7.688 | 29.1499 | 235.9443 | 0
4107 | 743.2307 | 1.1317 | 38.417 | 101.4758 | 56.5824 | 7.6002 | 47.9361 | 1.7091 | 6.7501 | 19.0532 | 74.469 | 6.9891 | 141.2471 | 83.2346 | 224.7546 | 8.2452 | 54.9894 | 11.1571 | 101 | 7.7677 | 40.9607 | 236.7454 | 0
4108 | 747.0026 | 1.5151 | 38.6911 | 109.1098 | 55.8634 | 8.2833 | 47.4653 | 1.3396 | 6.5246 | 24.1904 | 72.4075 | 5.2731 | 137.0212 | 82.254 | 223.616 | 8.0126 | 54.4238 | 10.9524 | 107 | 7.8768 | 59.5804 | 245.9207 | 0
4109 | 766.0078 | 1.1465 | 42.1027 | 89.5189 | 55.6254 | 8.5093 | 50.7717 | 1.164 | 6.1898 | 30.6789 | 70.5874 | 5.1334 | 137.5706 | 90.838 | 221.2808 | 8.0237 | 53.9523 | 10.8327 | 118 | 7.7299 | 46.2388 | 261.4741 | 0.023588
4110 | 806.5434 | 1.8907 | 43.8596 | 116.7287 | 53.3908 | 10.6322 | 49.6834 | 1.1713 | 5.7947 | 39.1995 | 72.517 | 10.8266 | 156.9281 | 118.216 | 223.7032 | 11.6986 | 54.2453 | 10.8518 | 160 | 7.8603 | 35.5911 | 295.1169 | 0.061073
4111 | 852.1339 | 3.0909 | 70.1688 | 146.5286 | 47.4861 | 16.2417 | 66.6253 | 1.9353 | 5.5996 | 50.0736 | 84.3451 | 23.1489 | 187.0808 | 152.4502 | 252.0153 | 22.3798 | 57.5663 | 11.1092 | 215 | 11.5055 | 43.1246 | 355.9066 | 0.10699
4112 | 922.2273 | 3.7873 | 90.0018 | 170.3017 | 45.522 | 18.1076 | 91.4395 | 3.3395 | 6.3275 | 50.3469 | 119.3634 | 29.4108 | 218.3865 | 188.6001 | 317.0788 | 29.2734 | 65.4551 | 11.6485 | 206 | 12.6287 | 59.9981 | 420.3105 | 0.14848
4113 | 986.0457 | 3.7419 | 98.3339 | 149.0838 | 46.292 | 17.3761 | 100.0984 | 4.3093 | 9.46 | 41.3774 | 160.1193 | 30.3899 | 251.0018 | 228.2588 | 384.3354 | 30.833 | 74.8157 | 11.9006 | 301 | 12.2488 | 35.8054 | 475.2073 | 0.16698
4114 | 1023.2721 | 5.182 | 97.9797 | 143.0313 | 46.5789 | 17.1035 | 100.7234 | 4.9878 | 14.0977 | 34.2071 | 179.163 | 30.5508 | 280.8084 | 258.8414 | 427.2459 | 30.9638 | 81.9612 | 12.0584 | 288 | 14.6524 | 42.9988 | 507.9152 | 0.12757
4115 | 1049.0287 | 6.0496 | 94.7791 | 140.1939 | 46.548 | 17.1329 | 103.436 | 5.3776 | 11.3399 | 33.1122 | 183.1353 | 30.0452 | 323.0982 | 272.9546 | 460.9306 | 31.2552 | 90.4324 | 12.1503 | 249 | 15.1357 | 56.5417 | 518.1898 | 0.15599
4116 | 1053.6381 | 6.9177 | 96.6294 | 193.9549 | 47.2099 | 16.5041 | 104.9734 | 5.2175 | 13.5294 | 35.065 | 186.8857 | 30.1287 | 345.3903 | 284.2142 | 475.2046 | 32.4374 | 100.506 | 12.0742 | 285 | 14.3353 | 59.6068 | 518.1299 | 0.16125
4117 | 1065.9092 | 10.2639 | 98.6006 | 181.1947 | 46.8657 | 16.831 | 102.1816 | 5.1379 | 15.53 | 40.2273 | 193.043 | 29.2303 | 355.0582 | 288.0118 | 459.062 | 32.3156 | 106.6607 | 11.894 | 284 | 15.3988 | 59.5891 | 510.8467 | 0.11624
4118 | 1050.933 | 10.3358 | 98.6792 | 148.0845 | 48.9764 | 14.8258 | 108.3764 | 4.8971 | 15.8691 | 48.4355 | 195.1325 | 28.1999 | 357.5263 | 279.2283 | 438.9597 | 30.717 | 109.0172 | 11.8817 | 223 | 17.4835 | 57.8212 | 503.5839 | 0.19087
4119 | 1015.3241 | 6.4353 | 90.9379 | 167.6815 | 50.2139 | 13.6502 | 96.7185 | 4.8405 | 17.7913 | 49.2419 | 180.7678 | 28.3073 | 366.4805 | 264.0041 | 427.3956 | 30.2745 | 108.9396 | 12.0272 | 201 | 15.0706 | 57.0167 | 497.8648 | 0.14416
4120 | 1008.0632 | 3.731 | 67.2872 | 143.3103 | 55.0431 | 9.0625 | 81.9412 | 4.6476 | 17.9715 | 42.9697 | 152.6076 | 27.9971 | 367.6705 | 241.951 | 407.712 | 26.013 | 106.6705 | 12.1011 | 172 | 11.9642 | 50.1337 | 464.5561 | 0.068063
4121 | 981.376 | 3.0542 | 54.652 | 115.6644 | 54.4182 | 9.6562 | 78.1265 | 3.0273 | 14.6325 | 35.5205 | 132.2773 | 26.8231 | 357.8684 | 198.4045 | 379.9245 | 14.4877 | 101.9777 | 12.1467 | 161 | 10.7571 | 42.7356 | 395.1423 | 0.025698
4122 | 938.67 | 2.6438 | 51.0322 | 95.5765 | 53.5285 | 10.5014 | 68.11 | 2.0991 | 8.6005 | 27.8917 | 119.3463 | 21.6553 | 317.9523 | 149.2649 | 342.6271 | 8.2381 | 96.077 | 12.1925 | 148 | 11.0214 | 44.5875 | 328.7276 | 0.016341
4123 | 885.4219 | 1.923 | 43.7711 | 98.3734 | 56.5163 | 7.663 | 56.5906 | 1.9756 | 5.6965 | 20.1084 | 105.4449 | 9.5119 | 276.2452 | 125.1299 | 302.5404 | 7.7213 | 90.3478 | 12.2634 | 127 | 10.5074 | 25.193 | 280.1029 | 0.009438
4124 | 847.5627 | 1.6311 | 40.0994 | 59.951 | 55.3436 | 8.7771 | 45.5446 | 1.8283 | 5.7441 | 15.4391 | 94.9665 | 4.4049 | 236.2299 | 116.4932 | 271.5359 | 7.9342 | 77.7815 | 12.349 | 132 | 9.4534 | 39.5934 | 248.547 | 0.0055337
4125 | 814.9827 | 2.7374 | 46.072 | 98.1112 | 56.1157 | 8.0435 | 47.4205 | 1.6537 | 5.6581 | 15.0055 | 85.817 | 4.4912 | 207.5711 | 106.0138 | 257.2253 | 8.1308 | 61.7435 | 12.2978 | 124 | 9.6933 | 25.0738 | 238.3089 | 0.00049726
4126 | 793.3862 | 3.2499 | 49.6962 | 69.8737 | 56.5964 | 7.5869 | 46.7116 | 1.5322 | 5.5943 | 16.5806 | 78.2697 | 6.07 | 182.6199 | 97.521 | 245.9334 | 8.1944 | 55.1069 | 12.4338 | 120 | 9.4994 | 30.1928 | 239.6939 | 0
4127 | 774.7415 | 2.0383 | 49.7208 | 105.0485 | 55.8582 | 8.2881 | 48.8743 | 1.538 | 6.3795 | 17.6001 | 76.67 | 7.0148 | 161.6216 | 96.6741 | 235.2111 | 8.4018 | 54.9601 | 12.266 | 120 | 9.4117 | 30.2283 | 242.4206 | 0
4128 | 768.2634 | 1.2763 | 49.6947 | 93.7474 | 55.5749 | 8.5573 | 45.1768 | 1.5596 | 6.4643 | 17.3654 | 77.1329 | 7.0238 | 157.9529 | 95.0976 | 230.222 | 8.3376 | 55.1152 | 12.0037 | 114 | 8.9596 | 27.0987 | 245.4294 | 0
4129 | 764.701 | 1.1668 | 49.6239 | 65.1823 | 57.0484 | 7.1574 | 48.2023 | 1.757 | 6.5552 | 17.0525 | 76.8211 | 7.0391 | 157.0494 | 91.5262 | 232.9858 | 8.339 | 55.0421 | 11.8489 | 113 | 9.6347 | 26.1805 | 245.5577 | 0
4130 | 757.2941 | 1.2096 | 49.7722 | 105.4434 | 56.1291 | 8.0308 | 46.6178 | 1.6802 | 6.378 | 16.9551 | 76.7263 | 6.9646 | 161.2089 | 89.2474 | 235.787 | 8.344 | 54.9023 | 11.7709 | 105 | 9.3497 | 26.2994 | 241.5096 | 0
4131 | 751.6914 | 1.2171 | 50.0651 | 71.4358 | 56.296 | 7.8723 | 48.236 | 1.5225 | 6.314 | 18.7064 | 77.2742 | 6.9873 | 163.4924 | 88.8351 | 227.9311 | 8.5582 | 54.713 | 11.784 | 112 | 9.616 | 26.0674 | 239.3145 | 0
4132 | 748.7854 | 1.1473 | 49.9064 | 102.0861 | 56.5956 | 7.5876 | 44.8334 | 1.4257 | 6.5 | 24.8663 | 76.6119 | 6.0902 | 165.217 | 89.1061 | 223.7753 | 8.5216 | 54.3885 | 11.7292 | 109 | 9.454 | 25.0457 | 242.2429 | 0
4133 | 761.6413 | 1.0864 | 49.7849 | 70.1715 | 55.8115 | 8.3325 | 47.3005 | 1.2177 | 6.037 | 31.7712 | 74.6142 | 5.7188 | 166.197 | 96.2225 | 217.4313 | 7.7245 | 53.9493 | 11.4599 | 114 | 9.4574 | 25.8246 | 252.2924 | 0.0085455
4134 | 788.9757 | 2.3787 | 54.8546 | 112.5043 | 54.0943 | 9.9639 | 50.9741 | 1.1393 | 5.5489 | 40.2044 | 75.5552 | 10.7987 | 176.5727 | 126.6039 | 229.3664 | 11.041 | 53.9918 | 11.0703 | 175 | 10.0104 | 34.6847 | 288.2163 | 0.040845
4135 | 835.5745 | 3.4959 | 78.2942 | 108.3393 | 47.6012 | 16.1323 | 71.5186 | 2.3407 | 5.5185 | 48.6633 | 89.5112 | 22.9898 | 194.5849 | 168.8025 | 265.3401 | 21.455 | 57.8224 | 10.9608 | 238 | 15.7812 | 66.7022 | 353.2331 | 0.046826
4136 | 929.3304 | 4.0683 | 92.6795 | 153.7773 | 47.0736 | 16.6335 | 94.0624 | 3.6984 | 11.2588 | 48.1526 | 126.4323 | 28.5739 | 224.0673 | 203.9912 | 315.0945 | 30.0224 | 66.7424 | 10.8961 | 230 | 20.2277 | 43.1154 | 423.9555 | 0.088521
4137 | 1019.4242 | 6.8202 | 95.7344 | 169.4188 | 46.8964 | 16.8019 | 103.6034 | 5.6497 | 15.5429 | 45.7693 | 163.1638 | 28.4607 | 291.4722 | 231.3645 | 371.4724 | 32.315 | 77.0641 | 10.9352 | 284 | 18.0174 | 51.9067 | 482.2663 | 0.15938
4138 | 1066.7423 | 9.6456 | 96.3667 | 177.5839 | 47.9648 | 15.7869 | 107.226 | 7.0154 | 15.7367 | 44.7004 | 171.7482 | 29.5339 | 346.722 | 250.6201 | 415.4338 | 31.0221 | 84.9826 | 10.9752 | 286 | 20.0163 | 71.616 | 507.6948 | 0.23287
4139 | 1069.4836 | 8.3791 | 97.2622 | 197.8963 | 47.8953 | 15.853 | 112.227 | 7.8199 | 9.73 | 40.9957 | 168.3717 | 30.5849 | 398.5386 | 265.7889 | 454.3553 | 28.6966 | 92.7772 | 11.0219 | 270 | 22.0146 | 42.8291 | 514.9059 | 0.23548
4140 | 1068.4398 | 6.9991 | 98.9872 | 168.4681 | 48.3727 | 15.3994 | 119.1592 | 6.4171 | 11.5488 | 38.9911 | 172.9192 | 30.2189 | 431.0495 | 275.6875 | 482.1919 | 30.6674 | 101.0221 | 11.0949 | 294 | 20.1504 | 68.2619 | 520.3023 | 0.24031
4141 | 1091.186 | 9.0442 | 99.7077 | 210.1128 | 47.769 | 15.9729 | 112.0379 | 5.7517 | 14.5055 | 42.7143 | 180.8076 | 29.4122 | 437.0459 | 271.9896 | 490.1732 | 33.6835 | 104.6431 | 11.1689 | 265 | 18.7917 | 43.2553 | 519.8467 | 0.27626
4142 | 1092.7258 | 7.8248 | 91.7255 | 196.3022 | 46.9277 | 16.7721 | 110.5918 | 5.678 | 9.8224 | 49.9167 | 185.5507 | 28.3191 | 435.5827 | 260.2428 | 487.2993 | 33.8086 | 105.141 | 11.1913 | 246 | 19.3413 | 67.836 | 522.7025 | 0.25745
4143 | 1064.5864 | 5.2423 | 87.5548 | 171.7781 | 51.8215 | 12.1231 | 97.5599 | 4.6819 | 7.86 | 51.8008 | 188.7398 | 27.4489 | 441.0269 | 250.052 | 470.6719 | 32.4799 | 105.7111 | 11.2203 | 230 | 17.3882 | 42.8475 | 521.4309 | 0.1793
4144 | 1012.1631 | 3.6876 | 61.6919 | 130.5625 | 54.3382 | 9.7322 | 84.112 | 4.5312 | 7.3874 | 43.6909 | 187.9189 | 26.4961 | 430.0959 | 236.3148 | 436.4544 | 26.8052 | 103.779 | 11.2081 | 198 | 14.5218 | 51.7169 | 480.4029 | 0.20046
4145 | 969.7984 | 2.9657 | 45.2254 | 100.5265 | 54.506 | 9.5727 | 86.5473 | 3.3889 | 6.3398 | 33.1388 | 172.6968 | 25.9248 | 381.6213 | 203.6703 | 394.8432 | 15.7556 | 96.9141 | 11.2867 | 166 | 13.3085 | 45.8513 | 400.8745 | 0.17639
4146 | 937.3965 | 2.8673 | 43.9607 | 66.0757 | 52.2834 | 11.6842 | 77.8966 | 1.7321 | 6.0221 | 26.9631 | 140.6634 | 21.0283 | 326.2585 | 166.0354 | 345.4092 | 10.9927 | 87.4122 | 11.5315 | 142 | 13.5883 | 38.3815 | 333.5714 | 0.24489
4147 | 906.31 | 1.8969 | 41.7018 | 97.5631 | 56.8411 | 7.3544 | 58.2965 | 1.1444 | 6.1859 | 21.1559 | 111.9341 | 8.8495 | 292.0896 | 150.479 | 300.0422 | 10.5646 | 75.9232 | 11.5063 | 124 | 13.0098 | 39.6926 | 288.3365 | 0.18308
4148 | 873.4414 | 1.3017 | 34.3696 | 53.4829 | 56.3527 | 7.8184 | 46.6113 | 1.226 | 6.2552 | 15.5013 | 98.9517 | 3.9414 | 258.7749 | 142.8372 | 264.9956 | 10.1213 | 64.8626 | 11.7103 | 126 | 12.2663 | 29.2257 | 253.7004 | 0.096947
4149 | 849.2484 | 1.3429 | 36.9536 | 87.717 | 57.0982 | 7.1101 | 48.953 | 1.1911 | 6.1675 | 13.2201 | 87.7036 | 3.9283 | 236.8368 | 129.311 | 235.8178 | 10.0212 | 59.404 | 11.7221 | 122 | 12.4124 | 22.5536 | 235.4606 | 0.015554
4150 | 817.2153 | 1.3516 | 39.4751 | 80.3442 | 57.5312 | 6.6988 | 47.5314 | 1.2837 | 5.977 | 12.8528 | 75.5534 | 4.3283 | 212.2347 | 120.7362 | 220.1983 | 9.9503 | 59.0802 | 11.6505 | 116 | 11.8476 | 27.3317 | 231.4983 | 0
4151 | 797.4623 | 1.2774 | 39.1245 | 53.8195 | 54.6632 | 9.4234 | 49.5853 | 1.6179 | 6.0105 | 14.1182 | 71.701 | 5.919 | 162.8779 | 120.345 | 218.6431 | 10.276 | 59.6475 | 11.3826 | 109 | 10.8175 | 37.7903 | 236.6848 | 0
4152 | 802.0602 | 1.1682 | 39.0622 | 91.8373 | 54.236 | 9.8293 | 47.8763 | 1.6159 | 6.343 | 16.1745 | 73.213 | 6.8718 | 133.3123 | 121.064 | 220.5255 | 10.2299 | 59.1927 | 11.1765 | 107 | 11.3698 | 29.2257 | 245.7539 | 0
4153 | 797.3347 | 1.1254 | 38.8807 | 98.1927 | 56.1328 | 8.0273 | 49.4969 | 1.5211 | 6.3169 | 16.9736 | 74.0819 | 7.1441 | 152.6499 | 118.021 | 224.6414 | 10.1599 | 58.8955 | 11.2011 | 101 | 11.1093 | 22.6215 | 251.0033 | 0
4154 | 789.0455 | 1.1229 | 38.9755 | 56.8199 | 57.3298 | 6.8902 | 52.578 | 1.502 | 6.3679 | 17.1334 | 74.3308 | 6.854 | 177.0861 | 115.0296 | 225.3794 | 10.3944 | 58.9163 | 11.2121 | 106 | 10.9835 | 24.5302 | 252.591 | 0
4155 | 783.5208 | 1.1259 | 38.676 | 67.3006 | 56.8572 | 7.3391 | 47.0121 | 1.4031 | 6.3631 | 17.7274 | 73.1147 | 5.8442 | 180.5059 | 113.8002 | 222.1996 | 10.1056 | 58.6508 | 11.1199 | 104 | 10.2983 | 25.5685 | 250.976 | 0
4156 | 795.3028 | 1.0155 | 38.448 | 83.6566 | 55.7938 | 8.3494 | 48.3978 | 1.4319 | 6.1526 | 22.581 | 70.4307 | 4.51 | 183.3349 | 112.4225 | 218.5114 | 9.7937 | 57.9937 | 10.9755 | 102 | 11.3768 | 24.8315 | 249.3317 | 0
4157 | 815.4011 | 1.024 | 38.4445 | 73.0286 | 56.3512 | 7.8198 | 45.8539 | 1.2422 | 5.878 | 30.2918 | 70.1869 | 5.0792 | 185.2567 | 113.9306 | 212.5145 | 9.6984 | 57.3825 | 10.9039 | 106 | 11.1202 | 25.0282 | 259.5554 | 0.13455
4158 | 842.7701 | 2.3448 | 46.7636 | 53.3555 | 54.3051 | 9.7637 | 53.3001 | 1.0588 | 5.7475 | 39.4781 | 78.4078 | 10.9147 | 190.1635 | 131.1818 | 222.7795 | 13.1613 | 57.3519 | 10.8679 | 150 | 11.0248 | 54.2845 | 292.4246 | 0.18089
4159 | 895.9744 | 7.4904 | 74.0246 | 127.7092 | 49.1272 | 14.6826 | 75.7309 | 1.6377 | 5.5816 | 48.5558 | 105.1109 | 22.5248 | 214.3997 | 165.6161 | 262.3242 | 22.7724 | 60.6307 | 10.9023 | 213 | 16.1311 | 36.3888 | 346.5866 | 0.22793
4160 | 965.2978 | 9.6754 | 89.3995 | 121.6338 | 49.8308 | 14.0142 | 108.1377 | 3.1411 | 5.9388 | 50.3926 | 145.7244 | 27.8756 | 270.9949 | 202.6606 | 319.9219 | 28.0089 | 68.2842 | 10.9314 | 228 | 18.1909 | 43.9479 | 411.4159 | 0.29824
4161 | 1041.1365 | 6.0968 | 91.4085 | 176.0566 | 48.465 | 15.3117 | 119.3359 | 3.8833 | 6.4451 | 46.9668 | 175.3489 | 28.5336 | 331.4662 | 230.8259 | 370.4873 | 29.1284 | 77.7752 | 10.8759 | 284 | 19.1957 | 46.781 | 468.4702 | 0.26125
4162 | 1072.9971 | 4.0885 | 93.0875 | 167.7679 | 47.5538 | 16.1774 | 124.9451 | 3.2476 | 6.7902 | 46.7633 | 184.6964 | 31.1002 | 373.5779 | 246.696 | 417.4765 | 30.8389 | 85.1811 | 10.969 | 265 | 21.2837 | 47.2202 | 493.22 | 0.27052
4163 | 1070.7755 | 3.8228 | 94.9395 | 138.9375 | 47.5719 | 16.1602 | 132.0103 | 3.2293 | 6.8386 | 45.1781 | 187.6045 | 32.9115 | 398.727 | 256.0885 | 451.7989 | 32.1644 | 87.4664 | 11.0551 | 268 | 22.9286 | 60.6204 | 500.4464 | 0.22964
4164 | 1064.7248 | 3.7404 | 96.2382 | 183.9402 | 45.3948 | 18.2284 | 125.1889 | 4.3151 | 6.6515 | 38.9372 | 190.6875 | 30.2644 | 388.149 | 262.7018 | 451.8867 | 33.2192 | 87.1134 | 11.0562 | 279 | 24.4456 | 36.4045 | 513.0609 | 0.20762
4165 | 1073.6211 | 3.6207 | 96.995 | 179.0959 | 46.8487 | 16.8472 | 124.7532 | 4.4697 | 6.8144 | 38.2093 | 194.7675 | 29.0982 | 373.1304 | 264.2066 | 440.3508 | 33.7766 | 86.7382 | 11.071 | 270 | 24.4446 | 43.6367 | 528.6376 | 0.19237
4166 | 1095.9408 | 3.6568 | 97.1439 | 159.4767 | 47.4445 | 16.2812 | 118.5848 | 4.2132 | 6.9316 | 46.2198 | 197.707 | 29.8484 | 358.3018 | 262.606 | 437.7786 | 34.1048 | 87.1196 | 11.1431 | 235 | 27.5271 | 47.4341 | 536.651 | 0.13475
4167 | 1074.3231 | 3.2679 | 84.1508 | 145.223 | 50.4944 | 13.3837 | 103.8559 | 4.0197 | 7.0243 | 49.7228 | 194.6243 | 29.5098 | 355.9385 | 253.4168 | 428.3751 | 34.6815 | 87.2641 | 11.0366 | 238 | 24.4087 | 47.3017 | 527.1967 | 0.12131
4168 | 1033.6683 | 3.4933 | 56.7454 | 136.6313 | 55.4287 | 8.6962 | 90.9113 | 3.385 | 7.4727 | 39.9813 | 188.5082 | 27.648 | 338.15 | 232.3826 | 398.8053 | 28.037 | 83.9979 | 10.8769 | 206 | 19.9016 | 46.3437 | 487.2547 | 0.074876
4169 | 996.6319 | 2.8311 | 44.3036 | 120.1336 | 55.7947 | 8.3485 | 85.7626 | 2.2281 | 6.5698 | 28.8114 | 171.7105 | 26.3591 | 310.7602 | 191.4291 | 346.5682 | 15.7984 | 77.5292 | 10.8814 | 160 | 20.9796 | 46.9374 | 416.5986 | 0.083299
4170 | 954.6824 | 1.9088 | 43.2439 | 92.643 | 56.3258 | 7.8439 | 80.4863 | 1.3101 | 5.8574 | 23.8528 | 137.9568 | 21.1008 | 283.6308 | 149.0396 | 298.8528 | 10.3082 | 70.7743 | 10.9906 | 147 | 19.4177 | 60.8845 | 343.1901 | 0.049909
4171 | 921.0171 | 1.3128 | 41.6992 | 80.9892 | 56.6338 | 7.5513 | 58.2807 | 1.5998 | 5.835 | 20.1356 | 107.5281 | 9.0115 | 255.9843 | 127.9415 | 264.2028 | 10.1159 | 65.9145 | 11.3534 | 122 | 16.4132 | 36.0554 | 284.8082 | 0.030326
4172 | 881.6109 | 1.1138 | 38.056 | 74.7878 | 54.2247 | 9.84 | 51.1059 | 1.4088 | 5.6988 | 16.0359 | 94.981 | 3.8891 | 234.996 | 112.6149 | 232.9902 | 10.0114 | 62.304 | 11.387 | 115 | 15.9788 | 34.3009 | 249.1346 | 0.017149
4173 | 859.1577 | 1.178 | 38.4686 | 75.7833 | 55.1919 | 8.9212 | 52.9149 | 0.98622 | 5.7444 | 13.1775 | 87.0234 | 3.974 | 215.7101 | 96.506 | 220.2674 | 10.0319 | 59.1648 | 11.5392 | 116 | 13.7533 | 42.8059 | 237.1256 | 0.009106
4174 | 838.5851 | 1.2696 | 39.861 | 54.7829 | 56.2577 | 7.9087 | 48.7769 | 1.1715 | 5.8833 | 11.0995 | 77.0498 | 3.8947 | 191.2814 | 87.6996 | 220.6314 | 9.9368 | 57.8091 | 11.7517 | 110 | 14.7906 | 33.3608 | 239.1556 | 0
4175 | 815.2983 | 1.5265 | 53.7048 | 76.9803 | 55.8429 | 8.3027 | 51.3952 | 1.564 | 5.8763 | 10.4828 | 71.8398 | 3.9806 | 169.3508 | 85.7801 | 221.2116 | 10.1523 | 57.205 | 11.7325 | 109 | 14.0373 | 25.9505 | 246.283 | 0
4176 | 817.8035 | 1.3834 | 30.0075 | 92.256 | 56.329 | 7.8409 | 50.3763 | 1.5406 | 5.9917 | 10.7315 | 70.6073 | 3.9706 | 139.9247 | 85.1739 | 222.2144 | 10.0396 | 56.2762 | 11.3811 | 108 | 14.4909 | 31.1125 | 251.7285 | 0
4177 | 820.6909 | 1.3489 | 36.7329 | 82.9576 | 56.5758 | 7.6064 | 51.3404 | 1.406 | 5.9467 | 10.6681 | 70.3838 | 3.9818 | 136.5844 | 83.4682 | 220.8411 | 10.0348 | 55.8859 | 10.9022 | 106 | 16.7362 | 33.2874 | 252.526 | 0
4178 | 804.0436 | 1.2359 | 40.161 | 76.1556 | 55.8704 | 8.2766 | 48.1178 | 1.428 | 5.8767 | 10.6655 | 70.3672 | 3.9778 | 152.0158 | 81.9177 | 213.3646 | 10.0393 | 56.0315 | 10.9389 | 105 | 14.5804 | 33.7123 | 252.2301 | 0
4179 | 794.9633 | 1.1141 | 40.1546 | 76.9099 | 54.8354 | 9.2598 | 50.7411 | 1.4176 | 5.97 | 12.4856 | 70.1455 | 3.9497 | 166.9068 | 82.3779 | 210.3608 | 9.8786 | 56.3778 | 10.8814 | 105 | 15.1778 | 33.1972 | 252.8874 | 0
4180 | 793.7883 | 1.3006 | 40.1267 | 77.4477 | 56.7997 | 7.3938 | 48.6004 | 1.3179 | 5.9739 | 19.572 | 70.2257 | 3.9096 | 166.7039 | 83.2788 | 215.6628 | 10.1496 | 56.7636 | 10.7983 | 103 | 13.7941 | 33.03 | 250.6501 | 0
4181 | 804.9514 | 1.2835 | 59.9533 | 57.248 | 56.8535 | 7.3426 | 50.3895 | 1.4244 | 6.0283 | 28.6005 | 71.0265 | 5.0868 | 187.6569 | 90.8512 | 217.8771 | 10.0864 | 56.7345 | 10.7942 | 108 | 12.7835 | 33.4762 | 252.739 | 0.054966
4182 | 828.2523 | 2.4027 | 33.8283 | 104.0842 | 54.3758 | 9.6965 | 55.1631 | 1.4151 | 5.8945 | 38.3788 | 78.1083 | 11.348 | 208.8079 | 112.9813 | 220.2582 | 13.5056 | 56.8601 | 10.7263 | 147 | 15.3223 | 33.262 | 282.4112 | 0.090362
4183 | 860.6126 | 3.4216 | 67.0596 | 127.4829 | 49.1684 | 14.6435 | 77.8684 | 1.8966 | 5.6245 | 48.1734 | 103.0511 | 23.9015 | 234.0736 | 147.7122 | 248.7319 | 23.6605 | 59.6066 | 10.9484 | 190 | 23.7162 | 33.3101 | 344.9692 | 0.079688
4184 | 920.7699 | 3.3781 | 89.6324 | 151.1416 | 47.5828 | 16.1498 | 105.0471 | 2.7596 | 5.699 | 51.5934 | 137.8561 | 30.4211 | 279.2213 | 187.5781 | 310.4116 | 31.3335 | 65.7368 | 11.5553 | 201 | 26.8956 | 43.2676 | 415.2785 | 0.18218
4185 | 991.8817 | 3.6 | 93.5552 | 166.6846 | 46.881 | 16.8166 | 119.9834 | 2.9436 | 6.0565 | 49.3245 | 165.5578 | 31.0693 | 320.093 | 219.98 | 361.0881 | 34.0704 | 72.9755 | 11.8104 | 279 | 22.4085 | 25.8166 | 472.2848 | 0.20259
4186 | 1036.9411 | 3.635 | 93.2616 | 168.5756 | 49.559 | 14.2725 | 126.7508 | 2.751 | 6.0505 | 45.3293 | 178.439 | 30.9358 | 332.2373 | 236.7423 | 392.0676 | 35.7215 | 79.8166 | 11.9045 | 257 | 24.2584 | 43.4342 | 500.9023 | 0.20509
4187 | 1056.1772 | 3.7651 | 92.4184 | 168.5752 | 50.5548 | 13.3264 | 125.6022 | 2.9366 | 6.1374 | 41.2573 | 179.1917 | 29.8875 | 335.2232 | 244.9647 | 414.2621 | 36.7531 | 84.1514 | 11.9671 | 231 | 24.8642 | 49.4669 | 515.3146 | 0.12757
4188 | 1067.9699 | 3.5467 | 91.7063 | 168.726 | 47.5681 | 16.1637 | 127.7873 | 2.9607 | 6.0516 | 37.1403 | 181.6843 | 29.908 | 338.8481 | 250.4756 | 423.3239 | 36.8162 | 84.0778 | 11.9522 | 274 | 22.3195 | 49.3882 | 517.2309 | 0.16175
4189 | 1073.1112 | 6.9745 | 93.0812 | 171.4961 | 48.0383 | 15.7171 | 130.3494 | 2.6518 | 5.7103 | 37.6129 | 185.9244 | 29.6732 | 342.8156 | 254.9339 | 417.0473 | 35.7079 | 86.3818 | 12.1294 | 241 | 23.0716 | 53.1499 | 501.2411 | 0.15848
4190 | 1065.2261 | 9.7559 | 114.6535 | 167.4685 | 48.6306 | 15.1544 | 119.302 | 1.8119 | 5.918 | 42.6991 | 186.6493 | 29.3304 | 348.2083 | 256.1135 | 414.1329 | 34.4408 | 96.8752 | 12.1938 | 235 | 24.2803 | 54.8334 | 485.0642 | 0.12506
4191 | 1032.3722 | 5.9174 | 64.4517 | 151.6658 | 51.445 | 12.4807 | 98.4621 | 1.1314 | 5.9948 | 44.6915 | 185.6086 | 29.2473 | 349.0971 | 247.5742 | 406.6453 | 32.6009 | 106.9967 | 12.1455 | 214 | 20.2597 | 53.0258 | 479.324 | 0.087056
4192 | 999.5227 | 2.7778 | 50.5899 | 129.8336 | 53.3275 | 10.6923 | 93.2228 | 0.97328 | 5.5637 | 39.6261 | 180.6406 | 27.9443 | 338.1187 | 234.9162 | 391.3156 | 26.5572 | 107.5299 | 12.159 | 207 | 14.217 | 45.2343 | 443.9412 | 0.076307
4193 | 942.888 | 1.9121 | 37.3484 | 112.9791 | 54.3265 | 9.7433 | 85.9418 | 1.1893 | 5.6508 | 30.2664 | 165.3251 | 27.3602 | 315.6366 | 195.4215 | 355.1211 | 14.3493 | 101.3247 | 12.4686 | 151 | 12.0827 | 39.9288 | 368.9065 | 0.04601
4194 | 893.145 | 1.376 | 33.8045 | 101.7728 | 55.3181 | 8.8013 | 80.8238 | 1.4087 | 5.5198 | 23.9499 | 136.8742 | 22.7268 | 278.7297 | 137.5675 | 312.4065 | 8.9368 | 94.3945 | 12.6351 | 135 | 11.8565 | 35.9593 | 308.9472 | 0.032484
4195 | 848.5046 | 2.0428 | 32.1869 | 97.9386 | 56.346 | 7.8248 | 56.8436 | 1.333 | 5.5671 | 22.5633 | 110.859 | 10.2893 | 250.6251 | 107.7923 | 270.4609 | 8.7073 | 87.5839 | 12.648 | 119 | 12.7729 | 34.8101 | 264.7585 | 0.014555
4196 | 818.6504 | 2.8643 | 30.0719 | 93.5385 | 57.3603 | 6.8612 | 46.0946 | 1.3313 | 5.8245 | 21.6693 | 99.695 | 5.5561 | 227.5794 | 103.0529 | 243.1531 | 8.6202 | 80.8788 | 12.3179 | 106 | 12.9177 | 30.3107 | 234.7145 | 0.0055057
4197 | 807.2078 | 3.1556 | 36.274 | 99.0639 | 56.0863 | 8.0715 | 49.8765 | 1.5163 | 5.8758 | 20.3797 | 91.8948 | 5.5378 | 209.8665 | 99.4463 | 234.6267 | 8.5036 | 76.0151 | 11.5634 | 116 | 12.7652 | 27.6665 | 223.2122 | 0.00044127
4198 | 793.4049 | 2.6308 | 39.522 | 98.9451 | 55.6151 | 8.5191 | 44.6503 | 1.6811 | 5.8792 | 20.0131 | 82.0159 | 5.5841 | 175.1348 | 94.3981 | 235.5437 | 8.359 | 74.3776 | 11.3142 | 116 | 12.8308 | 27.8216 | 220.5389 | 0
4199 | 776.3726 | 1.5996 | 39.6327 | 96.409 | 54.7892 | 9.3037 | 48.4119 | 2.027 | 5.9871 | 18.9533 | 75.6456 | 4.6949 | 161.3182 | 91.3729 | 234.5363 | 8.4839 | 73.451 | 11.3979 | 111 | 12.8576 | 27.5831 | 220.4136 | 0
4200 | 770.2501 | 1.211 | 39.694 | 83.531 | 56.7389 | 7.4515 | 46.4046 | 1.8135 | 5.9342 | 15.152 | 72.8418 | 4.0192 | 160.2646 | 87.0987 | 226.0903 | 8.4725 | 70.2574 | 11.0241 | 109 | 12.8305 | 26.1653 | 222.8715 | 0
4201 | 765.7875 | 1.3099 | 39.6125 | 107.0262 | 56.2355 | 7.9298 | 48.9568 | 1.4149 | 5.7319 | 11.8555 | 71.4923 | 3.9506 | 165.7196 | 84.2828 | 220.7188 | 8.6653 | 67.3219 | 10.7226 | 107 | 12.8162 | 24.4775 | 225.3679 | 0
4202 | 757.2756 | 1.2559 | 39.6089 | 99.7984 | 56.3098 | 7.8591 | 44.8932 | 1.365 | 5.7258 | 11.2477 | 70.4821 | 3.8944 | 177.1175 | 84.2007 | 216.2885 | 8.5056 | 66.5632 | 10.6867 | 99 | 12.8986 | 24.6448 | 224.1985 | 0
4203 | 749.1118 | 1.3076 | 39.7452 | 97.0545 | 56.4792 | 7.6982 | 46.6736 | 1.3736 | 5.7615 | 12.3865 | 69.4087 | 3.9419 | 176.5301 | 83.7006 | 208.2414 | 8.4097 | 66.6308 | 10.6954 | 102 | 12.9538 | 24.8345 | 223.4631 | 0
4204 | 748.8671 | 1.6041 | 51.577 | 96.7374 | 56.6431 | 7.5425 | 46.2866 | 1.1612 | 5.7522 | 16.8537 | 68.7709 | 3.8966 | 170.4243 | 82.7232 | 201.9824 | 8.4328 | 67.5607 | 10.6922 | 103 | 12.8329 | 24.2609 | 218.2984 | 0
4205 | 756.6677 | 1.0946 | 29.8804 | 96.534 | 56.6081 | 7.5757 | 45.5439 | 0.999 | 5.7447 | 21.9163 | 68.8071 | 3.9176 | 167.4945 | 89.555 | 198.4388 | 8.4454 | 69.5493 | 10.6635 | 101 | 12.8241 | 24.9395 | 209.1547 | 0.013598
4206 | 764.772 | 0.90719 | 36.7004 | 96.0483 | 55.7566 | 8.3847 | 48.9367 | 0.95495 | 5.796 | 24.6796 | 70.3876 | 3.9413 | 170.1107 | 103.3785 | 198.1124 | 8.4958 | 71.2784 | 10.6531 | 105 | 12.9162 | 29.1364 | 209.3221 | 0.026788
4207 | 773.6424 | 1.01 | 51.5689 | 96.4893 | 54.0308 | 10.0242 | 43.5796 | 1.2137 | 5.804 | 25.0234 | 74.9881 | 3.8416 | 176.903 | 111.7018 | 205.2867 | 8.278 | 71.6053 | 10.907 | 113 | 13.498 | 31.9449 | 215.2171 | 0.023297
4208 | 794.0817 | 1.04 | 29.8993 | 96.9058 | 52.2214 | 11.7431 | 46.5997 | 1.1846 | 5.778 | 20.6299 | 80.924 | 3.9412 | 180.7554 | 114.3179 | 220.8742 | 8.3406 | 71.1019 | 11.5217 | 113 | 13.5762 | 33.7924 | 216.5481 | 0.10465
4209 | 811.0572 | 1.0402 | 40.1965 | 96.7311 | 51.6861 | 12.2517 | 44.6413 | 1.0305 | 5.6418 | 15.9572 | 85.4124 | 4.1091 | 186.4479 | 118.3294 | 233.7708 | 8.3143 | 71.1837 | 11.7211 | 115 | 13.7792 | 34.7056 | 215.6059 | 0.11141
4210 | 830.3284 | 1.062 | 45.2278 | 99.1349 | 51.4803 | 12.4472 | 46.6215 | 0.94995 | 5.5207 | 14.9409 | 87.9297 | 3.8743 | 197.4243 | 127.6671 | 243.1224 | 8.2301 | 72.6158 | 11.6795 | 106 | 14.5087 | 34.417 | 217.3858 | 0.097157
4211 | 827.8181 | 1.4767 | 46.2486 | 99.7191 | 53.0418 | 10.9637 | 49.8986 | 0.93733 | 5.7087 | 14.7045 | 88.599 | 4.1845 | 209.1706 | 140.7279 | 249.5812 | 8.171 | 76.0176 | 11.8805 | 115 | 14.7807 | 33.8451 | 220.9617 | 0.24107
4212 | 810.5709 | 1.4517 | 47.1533 | 99.5396 | 52.8923 | 11.1058 | 44.6283 | 1.0713 | 5.9259 | 15.6453 | 88.4081 | 4.5748 | 212.9714 | 150.2233 | 245.8336 | 8.2106 | 79.1974 | 11.9668 | 103 | 14.5436 | 33.9615 | 220.1967 | 0.25648
4213 | 793.8964 | 1.5561 | 47.761 | 99.7209 | 53.2812 | 10.7363 | 48.1732 | 1.2067 | 6.0149 | 19.0574 | 88.2795 | 4.3412 | 223.6987 | 150.131 | 234.1459 | 8.2028 | 80.0631 | 11.9476 | 112 | 14.589 | 34.2402 | 223.5537 | 0.20865
4214 | 785.3774 | 1.1347 | 47.4309 | 100.1065 | 53.5766 | 10.4557 | 51.3279 | 1.322 | 5.9126 | 23.0732 | 88.4153 | 4.161 | 230.108 | 144.2994 | 239.0935 | 8.1383 | 81.3738 | 11.9137 | 113 | 14.6934 | 33.865 | 229.224 | 0.19258
4215 | 787.4573 | 1.4169 | 46.6031 | 99.8626 | 55.0886 | 9.0192 | 44.9312 | 1.5803 | 5.5327 | 23.9387 | 88.8931 | 4.1075 | 225.1577 | 140.3519 | 254.3271 | 8.2213 | 83.151 | 11.9345 | 115 | 14.5058 | 34.7406 | 230.9287 | 0.11662
4216 | 787.7055 | 1.1494 | 45.1171 | 99.6856 | 56.3403 | 7.8302 | 48.1454 | 1.4306 | 5.5098 | 19.5466 | 89.1009 | 4.1206 | 211.9712 | 137.9182 | 255.3495 | 8.3957 | 81.9406 | 11.9947 | 108 | 13.9649 | 33.3215 | 232.0673 | 0.13104
4217 | 779.0394 | 0.8945 | 43.6251 | 99.8519 | 57.2808 | 6.9367 | 49.3075 | 1.2871 | 5.529 | 14.472 | 86.7182 | 4.0904 | 207.4752 | 123.7393 | 249.2209 | 8.4099 | 79.3869 | 12.008 | 116 | 13.8223 | 32.0719 | 230.0735 | 0.13948
4218 | 781.1556 | 0.97015 | 40.2669 | 99.6623 | 56.0493 | 8.1066 | 46.3105 | 1.2528 | 5.8865 | 12.7981 | 82.4567 | 4.088 | 208.1822 | 104.318 | 242.0494 | 8.3619 | 77.1924 | 11.9831 | 115 | 13.7994 | 31.2339 | 226.2847 | 0.19208
4219 | 770.6287 | 0.87908 | 39.0133 | 100.248 | 56.4084 | 7.7654 | 49.6017 | 1.2223 | 5.7173 | 12.6241 | 79.0575 | 4.1193 | 201.671 | 94.6829 | 227.5035 | 8.3352 | 73.7047 | 11.9781 | 117 | 13.7135 | 31.7555 | 218.4639 | 0.071322
4220 | 757.8148 | 1.4278 | 38.8901 | 88.0861 | 55.1595 | 8.9519 | 51.0037 | 1.2658 | 5.5267 | 12.6511 | 77.2081 | 4.0472 | 195.6907 | 89.887 | 219.9195 | 8.296 | 69.6983 | 11.7552 | 110 | 13.8091 | 30.8016 | 211.9449 | 0.020326
4221 | 763.3837 | 2.4291 | 50.2321 | 106.25 | 54.5661 | 9.5156 | 43.9904 | 1.3505 | 5.8921 | 12.7553 | 77.0545 | 3.8989 | 188.6599 | 88.2022 | 208.5734 | 8.6203 | 67.3071 | 11.1759 | 110 | 13.6877 | 28.5336 | 213.2692 | 0.0014012
4222 | 764.4404 | 2.3599 | 28.6168 | 99.345 | 54.5491 | 9.5318 | 47.7253 | 1.5297 | 5.9265 | 12.7209 | 76.3962 | 3.9177 | 169.4045 | 87.9476 | 201.6673 | 8.4612 | 66.4867 | 10.9013 | 102 | 13.4368 | 25.2356 | 219.933 | 0
4223 | 751.0858 | 1.4543 | 34.6234 | 96.4465 | 56.8248 | 7.3699 | 52.3234 | 1.7469 | 5.7643 | 12.8242 | 75.0654 | 3.9221 | 161.1469 | 86.0029 | 200.8913 | 9.1914 | 66.1736 | 10.969 | 108 | 13.3429 | 24.6333 | 225.1124 | 0
4224 | 753.7785 | 1.0891 | 37.7432 | 94.3316 | 57.535 | 6.6952 | 45.3669 | 1.5306 | 5.9387 | 12.5158 | 74.4912 | 3.8292 | 165.6272 | 85.0331 | 198.8192 | 11.5839 | 66.0842 | 11.2413 | 101 | 13.4169 | 24.8577 | 228.2595 | 0
4225 | 765.2369 | 1.6736 | 49.3478 | 92.8412 | 56.8819 | 7.3156 | 48.8094 | 1.341 | 5.964 | 11.6353 | 73.5625 | 3.9331 | 167.6144 | 85.0787 | 203.7771 | 12.5712 | 66.0256 | 10.9318 | 103 | 13.4577 | 25.2854 | 235.0721 | 0
4226 | 763.0017 | 1.4755 | 28.7934 | 93.0976 | 56.518 | 7.6614 | 46.2895 | 1.36 | 5.9304 | 11.3581 | 71.7086 | 3.9383 | 171.2055 | 84.2877 | 203.0097 | 12.4556 | 66.1439 | 10.7424 | 109 | 13.4403 | 24.7804 | 237.3349 | 0
4227 | 756.8494 | 1.1341 | 34.7324 | 93.7262 | 55.897 | 8.2513 | 48.6362 | 1.2875 | 5.8601 | 12.7335 | 69.1764 | 3.897 | 170.4002 | 83.1485 | 196.945 | 12.7856 | 66.5662 | 10.7188 | 102 | 13.4015 | 24.252 | 231.0982 | 0
4228 | 751.9791 | 1.1384 | 37.5451 | 97.715 | 56.3319 | 7.8382 | 47.9334 | 1.0371 | 5.7485 | 15.2431 | 66.9487 | 3.8628 | 163.7633 | 83.1155 | 197.6086 | 11.1003 | 67.8723 | 10.7247 | 109 | 13.4657 | 25.226 | 221.123 | 0
4229 | 756.1779 | 0.91622 | 37.6209 | 99.4865 | 56.5359 | 7.6443 | 45.5598 | 0.95952 | 5.6432 | 19.0272 | 66.0189 | 3.9112 | 160.7486 | 83.3434 | 195.8118 | 9.0554 | 69.9393 | 10.7378 | 104 | 13.4706 | 24.6948 | 210.1492 | 0.015559
4230 | 770.5691 | 1.9669 | 37.6485 | 95.5366 | 56.6667 | 7.5201 | 55.1239 | 1.0349 | 5.6889 | 23.5044 | 66.1498 | 3.885 | 156.955 | 84.9106 | 197.9546 | 8.5051 | 69.6354 | 10.7483 | 104 | 13.3908 | 26.9235 | 204.46 | 0.041094
4231 | 786.8513 | 6.1079 | 37.9183 | 93.804 | 56.541 | 7.6395 | 77.8341 | 1.1924 | 5.8901 | 24.0066 | 66.7774 | 3.8808 | 155.1779 | 86.5321 | 204.05 | 8.2057 | 67.4398 | 10.9935 | 101 | 13.7613 | 28.4339 | 202.5566 | 0.10373
4232 | 782.5158 | 7.9391 | 38.5478 | 94.795 | 55.0586 | 9.0478 | 90.466 | 1.1469 | 5.6185 | 22.0704 | 72.6122 | 3.9386 | 156.8247 | 86.7448 | 211.5597 | 8.3776 | 66.5031 | 11.5875 | 99 | 14.2734 | 30.3743 | 201.3944 | 0.11787
4233 | 780.9514 | 7.8835 | 41.5178 | 85.6545 | 55.3388 | 8.7816 | 88.4753 | 1.4831 | 5.5302 | 22.0507 | 82.1932 | 4.1291 | 155.7698 | 87.5258 | 226.0719 | 8.1561 | 66.7946 | 11.7965 | 103 | 14.2838 | 32.962 | 203.1319 | 0.18616
4234 | 788.4186 | 7.0582 | 57.0012 | 108.6869 | 56.3592 | 7.8122 | 90.7143 | 2.2255 | 5.4832 | 20.1803 | 86.8449 | 3.9685 | 170.4715 | 89.8261 | 237.5713 | 8.0717 | 67.8356 | 11.8356 | 103 | 14.4195 | 34.4931 | 205.9577 | 0.21407
4235 | 791.2797 | 7.1451 | 33.1275 | 90.9643 | 56.5783 | 7.6041 | 98.3945 | 3.1511 | 5.7367 | 16.9105 | 82.7457 | 3.819 | 187.0454 | 92.9804 | 248.6737 | 8.5496 | 69.7995 | 11.9538 | 104 | 14.8737 | 33.769 | 206.0636 | 0.21379
4236 | 787.5747 | 7.9699 | 40.9758 | 111.3983 | 56.5773 | 7.605 | 110.585 | 2.051 | 6.0408 | 16.8373 | 79.7413 | 3.8802 | 193.6916 | 96.1474 | 245.7165 | 8.3802 | 72.124 | 12.0349 | 106 | 14.7792 | 34.0813 | 206.3452 | 0.22387
4237 | 787.2246 | 8.2671 | 44.3567 | 93.7354 | 56.5595 | 7.6219 | 108.8038 | 1.1409 | 6.161 | 17.8408 | 88.3784 | 4.0434 | 197.0135 | 99.6743 | 234.6212 | 8.2149 | 72.1975 | 12.1641 | 105 | 14.542 | 33.9835 | 209.094 | 0.20602
4238 | 778.8977 | 3.4083 | 43.5911 | 114.1609 | 55.9035 | 8.2451 | 111.664 | 1.0494 | 6.1048 | 17.5897 | 97.6353 | 3.846 | 192.4297 | 101.9072 | 224.26 | 8.2775 | 69.8483 | 12.1758 | 100 | 14.3882 | 32.8952 | 210.8436 | 0.22356
4239 | 783.7025 | 1.241 | 40.5022 | 104.1628 | 55.5717 | 8.5604 | 118.6852 | 0.96841 | 6.7602 | 17.6323 | 97.6111 | 3.9027 | 185.5095 | 103.412 | 213.0409 | 8.2869 | 67.8572 | 12.1863 | 104 | 14.3298 | 33.1329 | 209.8882 | 0.27501
4240 | 794.9515 | 6.0791 | 39.0385 | 97.7295 | 56.2854 | 7.8823 | 106.2899 | 1.1234 | 7.49 | 19.1904 | 90.8535 | 3.9703 | 178.8707 | 104.513 | 199.0245 | 8.1278 | 67.5211 | 12.151 | 117 | 13.9622 | 33.3588 | 203.9471 | 0.12631
4241 | 789.5544 | 4.064 | 38.7396 | 99.1886 | 56.5866 | 7.5962 | 94.4502 | 1.0196 | 7.3178 | 19.7477 | 84.0834 | 4.0118 | 175.8963 | 103.8584 | 198.2955 | 8.2389 | 67.8743 | 12.0433 | 117 | 13.8327 | 33.8241 | 199.0834 | 0.19137
4242 | 785.0721 | 1.3541 | 38.6891 | 99.6462 | 57.3171 | 6.9022 | 82.7261 | 0.92692 | 6.5828 | 17.2848 | 81.7289 | 4.1544 | 181.1597 | 99.0708 | 198.9432 | 8.1574 | 67.4316 | 11.9861 | 112 | 13.7546 | 32.9729 | 199.7955 | 0.12933
4243 | 789.6889 | 1.2492 | 38.5629 | 100.093 | 56.1821 | 7.9804 | 60.8555 | 0.95647 | 5.9578 | 14.4766 | 81.7145 | 4.3139 | 183.4624 | 92.646 | 201.9895 | 8.1443 | 66.7501 | 12.0049 | 106 | 13.6104 | 33.2601 | 199.722 | 0.11272
4244 | 784.0511 | 1.0474 | 38.5062 | 100.0005 | 57.0035 | 7.2002 | 52.1358 | 1.1311 | 5.9402 | 13.3723 | 81.4535 | 4.4551 | 186.0098 | 88.5414 | 197.7704 | 8.1744 | 66.4818 | 11.7392 | 105 | 13.5256 | 33.2165 | 197.4659 | 0.008268
4245 | 781.4545 | 2.211 | 38.5343 | 98.8984 | 56.7618 | 7.4297 | 50.501 | 1.1226 | 6.3151 | 13.3641 | 81.7714 | 4.4799 | 183.0785 | 85.9722 | 198.5689 | 8.4137 | 66.6384 | 11.1578 | 106 | 13.5139 | 31.4615 | 197.9614 | 0.0015445
4246 | 777.5475 | 2.4024 | 38.8559 | 98.5397 | 56.5983 | 7.585 | 47.2342 | 1.2518 | 6.4608 | 13.6561 | 82.2951 | 4.2911 | 187.8585 | 85.8565 | 201.5672 | 8.3848 | 66.7188 | 11.0481 | 100 | 13.669 | 27.3125 | 202.586 | 0
4247 | 768.7604 | 1.4307 | 50.6584 | 97.0048 | 56.5679 | 7.614 | 50.3106 | 1.3648 | 6.2773 | 13.657 | 80.968 | 4.2567 | 190.6398 | 86.8929 | 201.5181 | 8.1877 | 67.5307 | 10.9447 | 103 | 13.5951 | 25.223 | 210.6562 | 0
4248 | 773.6141 | 1.6016 | 29.1862 | 97.0618 | 56.675 | 7.5122 | 52.2385 | 1.327 | 5.843 | 13.425 | 79.1966 | 4.3289 | 188.3916 | 85.5573 | 199.4937 | 9.4633 | 71.431 | 10.8712 | 100 | 13.5665 | 25.425 | 216.5196 | 0
4249 | 773.5032 | 1.3887 | 34.8207 | 84.7967 | 56.6271 | 7.5578 | 46.9622 | 1.3531 | 6.1204 | 13.2831 | 78.296 | 4.284 | 187.3884 | 83.1802 | 199.5386 | 11.6022 | 75.6125 | 10.6742 | 99 | 13.4849 | 25.2657 | 218.1517 | 0
4250 | 764.225 | 1.0892 | 37.6118 | 104.7274 | 56.4882 | 7.6896 | 50.1824 | 1.6293 | 7.0942 | 13.371 | 78.141 | 4.2572 | 186.9605 | 82.036 | 200.7061 | 12.6278 | 76.3197 | 10.5638 | 102 | 13.5481 | 23.7249 | 218.2822 | 0
4251 | 762.8387 | 3.2104 | 37.481 | 88.3618 | 56.5654 | 7.6164 | 52.9374 | 1.4872 | 6.6569 | 13.4137 | 78.6397 | 4.2548 | 194.1169 | 81.7603 | 198.9399 | 11.3624 | 75.1599 | 10.5782 | 98 | 13.5624 | 23.7862 | 216.6606 | 0
4252 | 761.6836 | 7.1937 | 37.3808 | 104.9785 | 56.6423 | 7.5433 | 47.1167 | 1.2373 | 6.1061 | 13.3624 | 78.943 | 4.2811 | 197.3381 | 82.7027 | 197.9402 | 9.2153 | 74.0863 | 10.5817 | 102 | 13.5038 | 23.7203 | 210.3433 | 0
4253 | 767.2561 | 8.2288 | 37.3132 | 98.3772 | 55.8617 | 8.2848 | 49.8006 | 1.0595 | 5.9478 | 13.8393 | 78.9487 | 4.3182 | 199.3372 | 83.364 | 198.1047 | 8.0576 | 73.5478 | 10.5503 | 98 | 13.4777 | 23.1456 | 198.6474 | 0.051636
4254 | 778.2561 | 7.9515 | 37.3212 | 97.1954 | 55.6479 | 8.4879 | 50.184 | 0.94424 | 5.6982 | 15.5188 | 79.2264 | 4.3023 | 198.4831 | 82.409 | 202.1136 | 8.2581 | 73.5129 | 10.5148 | 101 | 13.6119 | 23.2449 | 192.4264 | 0.055624
4255 | 790.8984 | 4.1592 | 37.3292 | 95.8273 | 56.9501 | 7.2508 | 47.6866 | 0.93907 | 5.7845 | 15.7441 | 79.755 | 4.2905 | 205.7825 | 81.6305 | 206.4998 | 8.3333 | 73.4848 | 10.8175 | 101 | 14.2602 | 23.9908 | 193.3948 | 0.11152
4256 | 795.443 | 1.1221 | 37.4389 | 98.1751 | 56.8611 | 7.3354 | 50.2297 | 1.0228 | 5.5419 | 14.6169 | 81.4568 | 4.3985 | 200.0236 | 83.7302 | 215.3343 | 8.2852 | 73.5695 | 11.5113 | 106 | 14.3656 | 27.3028 | 197.277 | 0.094168
4257 | 796.5878 | 0.68548 | 37.3909 | 97.0418 | 56.6161 | 7.5682 | 47.3231 | 1.1754 | 5.4879 | 15.7487 | 83.007 | 4.3111 | 199.0465 | 88.0476 | 234.0264 | 8.4255 | 73.6932 | 11.8715 | 106 | 14.3238 | 30.2102 | 202.0142 | 0.096516
4258 | 797.8385 | 5.1912 | 37.2614 | 97.8978 | 56.5769 | 7.6054 | 49.7332 | 1.1664 | 5.4115 | 19.6818 | 82.9335 | 4.234 | 206.78 | 91.7511 | 241.0107 | 8.3908 | 73.6529 | 11.8414 | 100 | 14.4039 | 30.7585 | 202.5687 | 0.11038
4259 | 797.9125 | 7.7276 | 37.265 | 103.2151 | 55.8677 | 8.2792 | 53.7112 | 1.0224 | 5.408 | 23.7832 | 86.1115 | 4.0483 | 212.3761 | 94.3653 | 242.4746 | 8.0953 | 73.7821 | 11.8435 | 107 | 14.3433 | 31.7111 | 199.3318 | 0.12835
4260 | 808.6701 | 7.8371 | 37.2728 | 105.3666 | 54.0899 | 9.968 | 50.677 | 0.94384 | 5.6213 | 22.5427 | 94.2658 | 3.9394 | 210.9329 | 97.3569 | 244.5154 | 8.1558 | 73.9699 | 11.8853 | 119 | 14.1153 | 31.444 | 198.2847 | 0.10885
4261 | 811.0616 | 5.9793 | 37.0845 | 103.4786 | 55.7449 | 8.3958 | 48.7508 | 0.92096 | 5.8057 | 17.516 | 99.0474 | 3.9893 | 204.1514 | 99.679 | 243.7596 | 8.2931 | 74.4734 | 11.8434 | 123 | 13.9468 | 28.8524 | 198.5188 | 0.12052
4262 | 808.953 | 7.0435 | 48.9684 | 89.0968 | 55.8384 | 8.3069 | 54.0372 | 0.94062 | 5.5286 | 15.1478 | 104.8648 | 4.7974 | 201.803 | 99.9255 | 242.6311 | 8.212 | 75.4682 | 11.7511 | 127 | 14.17 | 26.0985 | 197.5543 | 0.10205
4263 | 805.2182 | 4.0949 | 37.5933 | 100.9259 | 55.5091 | 8.6199 | 51.5134 | 0.95426 | 5.5454 | 15.4066 | 115.635 | 6.4213 | 202.4041 | 101.3032 | 238.0948 | 8.1091 | 75.7236 | 11.7472 | 107 | 14.3344 | 26.0604 | 197.95 | 0.14898
4264 | 803.1926 | 4.4536 | 28.4021 | 108.8783 | 55.6422 | 8.4933 | 51.9417 | 0.92485 | 5.3455 | 15.416 | 113.9293 | 4.8971 | 204.8188 | 104.3209 | 231.6215 | 8.5091 | 75.715 | 11.8902 | 109 | 14.2278 | 26.3327 | 197.8103 | 0.1477
4265 | 801.7041 | 2.8419 | 34.3319 | 100.6857 | 57.0131 | 7.191 | 54.6176 | 1.2197 | 5.261 | 15.1969 | 103.5585 | 3.8994 | 203.7842 | 103.9237 | 224.3284 | 8.4576 | 76.393 | 11.9395 | 102 | 13.6311 | 27.1418 | 198.1802 | 0.20993
4266 | 798.4113 | 1.3633 | 38.0244 | 86.6405 | 56.9325 | 7.2676 | 54.0325 | 1.1306 | 5.3342 | 14.683 | 98.9703 | 3.8165 | 193.2586 | 101.1946 | 232.2853 | 8.1962 | 76.982 | 11.9379 | 104 | 13.3804 | 26.4107 | 202.589 | 0.15928
4267 | 793.8954 | 1.6995 | 38.3581 | 106.8164 | 55.8766 | 8.2707 | 48.4856 | 0.93635 | 5.4704 | 13.6201 | 94.0202 | 3.8901 | 179.8643 | 98.6907 | 231.7489 | 8.202 | 77.1588 | 11.9329 | 120 | 13.3043 | 26.4011 | 207.3741 | 0.13856
4268 | 798.6973 | 1.0825 | 38.0521 | 99.6711 | 56.2458 | 7.9199 | 51.8901 | 0.93089 | 5.4715 | 12.7504 | 87.3575 | 3.8292 | 189.7095 | 95.1261 | 221.9493 | 8.3252 | 76.6261 | 11.7045 | 111 | 13.3081 | 27.1475 | 205.7209 | 0.077935
4269 | 785.1342 | 1.7099 | 37.6717 | 99.5156 | 55.9137 | 8.2354 | 54.1542 | 0.95568 | 5.5457 | 11.605 | 83.8346 | 5.9252 | 196.9192 | 91.7908 | 213.9617 | 8.2395 | 75.71 | 11.1459 | 115 | 13.4149 | 28.0746 | 202.4583 | 0.01452
4270 | 787.5809 | 2.4238 | 37.4738 | 102.9581 | 56.2718 | 7.8952 | 47.7853 | 1.1357 | 5.6788 | 10.5813 | 79.7125 | 11.885 | 190.5795 | 89.7786 | 208.0038 | 8.4581 | 75.0213 | 10.8657 | 101 | 13.3831 | 26.9322 | 206.6796 | 0
4271 | 778.5273 | 1.856 | 37.7061 | 103.2846 | 56.5389 | 7.6415 | 51.5251 | 1.303 | 5.761 | 10.603 | 73.7132 | 14.3263 | 179.1921 | 86.6693 | 203.1868 | 9.4018 | 74.9476 | 10.9615 | 106 | 13.2699 | 24.8537 | 214.8519 | 0
4272 | 790.9714 | 1.2651 | 37.7631 | 102.9456 | 57.3866 | 6.8361 | 53.5386 | 1.3683 | 5.9651 | 10.7231 | 70.1956 | 14.2417 | 153.7604 | 83.5412 | 201.9498 | 11.1486 | 75.3858 | 10.8497 | 102 | 13.2615 | 24.2211 | 219.6074 | 0
4273 | 783.5979 | 1.1277 | 49.9475 | 102.5315 | 56.808 | 7.3859 | 47.9198 | 1.6436 | 5.9395 | 10.609 | 69.2498 | 14.2605 | 148.9693 | 84.2727 | 199.9141 | 12.1867 | 75.5964 | 10.7306 | 99 | 13.321 | 24.5313 | 220.6898 | 0
4274 | 768.986 | 1.2183 | 28.522 | 102.9477 | 55.8877 | 8.2601 | 50.7616 | 1.5266 | 5.8701 | 10.7026 | 69.0634 | 15.218 | 157.8289 | 90.0398 | 199.4594 | 12.9241 | 75.6749 | 10.7266 | 102 | 13.3455 | 24.1443 | 222.0962 | 0
4275 | 770.4352 | 1.1987 | 34.7329 | 90.4022 | 56.3391 | 7.8313 | 49.8803 | 1.3342 | 5.737 | 12.0989 | 69.0869 | 17.6649 | 154.9953 | 95.3651 | 202.322 | 13.176 | 75.8763 | 10.7188 | 100 | 13.2863 | 23.0848 | 222.0094 | 0
4276 | 781.0859 | 1.3193 | 37.9469 | 111.9805 | 56.522 | 7.6575 | 49.9567 | 1.0947 | 5.7249 | 19.5413 | 69.0139 | 15.4799 | 132.5727 | 96.4567 | 197.5933 | 11.1377 | 75.916 | 10.7049 | 101 | 13.3097 | 22.6293 | 223.5796 | 0
4277 | 789.0916 | 1.1544 | 37.226 | 106.8777 | 56.585 | 7.5977 | 52.8151 | 1.0387 | 5.9167 | 29.4496 | 69.337 | 7.8445 | 134.5441 | 103.9338 | 200.3362 | 9.295 | 75.2996 | 10.6809 | 99 | 13.293 | 23.8789 | 231.0401 | 0.077643
4278 | 807.5017 | 2.7142 | 47.687 | 105.2608 | 52.1633 | 11.7983 | 50.5543 | 1.2779 | 5.694 | 37.1504 | 80.2314 | 10.4442 | 163.4946 | 132.968 | 204.1661 | 12.1759 | 74.7623 | 10.6981 | 140 | 13.6348 | 28.4689 | 264.2744 | 0.10692
4279 | 860.6465 | 7.4739 | 73.2313 | 111.3694 | 46.8541 | 16.8421 | 69.4025 | 2.1104 | 5.5281 | 41.8907 | 107.6452 | 23.0959 | 204.2706 | 172.0761 | 224.4813 | 21.4976 | 79.0024 | 10.9594 | 162 | 17.7931 | 36.7247 | 330.3932 | 0.1679
4280 | 940.3308 | 9.9956 | 83.6219 | 119.3375 | 48.5395 | 15.2409 | 109.0493 | 2.819 | 5.428 | 41.5892 | 138.6713 | 29.4741 | 264.711 | 204.162 | 271.23 | 27.1347 | 89.074 | 11.5431 | 176 | 19.2146 | 44.1554 | 409.0767 | 0.23913
4281 | 1005.4984 | 8.8875 | 87.6411 | 127.5836 | 46.987 | 16.7158 | 115.3291 | 3.3347 | 5.6497 | 37.972 | 160.0146 | 30.5177 | 328.7973 | 229.6323 | 325.6275 | 27.6886 | 99.1186 | 11.7314 | 170 | 18.2442 | 44.1367 | 468.214 | 0.21514
4282 | 1042.0463 | 4.7393 | 89.829 | 133.1189 | 46.203 | 17.4607 | 110.6316 | 3.684 | 6.0145 | 38.2101 | 167.0321 | 31.1616 | 353.1073 | 246.8915 | 374.0256 | 28.4699 | 107.5625 | 11.798 | 130 | 20.9247 | 45.0181 | 491.4897 | 0.18727
4283 | 1067.7557 | 3.1569 | 92.9915 | 134.4854 | 48.7318 | 15.0583 | 116.3822 | 3.5771 | 6.1375 | 43.1158 | 166.7547 | 30.668 | 408.9291 | 255.5674 | 404.795 | 28.3912 | 113.5616 | 11.8048 | 131 | 22.6185 | 43.7262 | 484.7376 | 0.21813
4284 | 1071.0439 | 3.3494 | 93.6024 | 108.0834 | 48.7304 | 15.0596 | 115.9191 | 3.7235 | 5.9084 | 42.404 | 171.38 | 30.8708 | 442.943 | 260.4562 | 408.0428 | 28.7669 | 114.6132 | 11.916 | 135 | 22.7254 | 43.494 | 473.4879 | 0.23011
4285 | 1081.5036 | 3.589 | 92.0465 | 165.4832 | 46.3348 | 17.3354 | 117.396 | 3.8968 | 5.5745 | 40.5499 | 178.739 | 30.2338 | 406.6037 | 260.8654 | 394.3116 | 28.6241 | 113.4626 | 11.9802 | 146 | 22.3767 | 44.7671 | 479.1069 | 0.22492
4286 | 1082.8113 | 3.9028 | 91.6298 | 150.8442 | 49.3859 | 14.4368 | 114.4982 | 3.9388 | 5.4358 | 41.8635 | 181.913 | 30.2225 | 383.0843 | 261.651 | 391.9404 | 28.1447 | 112.6322 | 11.9734 | 138 | 23.7688 | 44.0303 | 487.7931 | 0.20734
4287 | 1073.4633 | 4.1321 | 89.1353 | 136.3893 | 50.5477 | 13.3332 | 94.6927 | 4.5181 | 5.6523 | 39.7402 | 182.5534 | 30.1351 | 428.2922 | 263.3795 | 389.8742 | 27.9973 | 111.3912 | 12.0066 | 128 | 24.2189 | 42.1768 | 486.8931 | 0.1986
4288 | 1036.1131 | 2.9463 | 62.4726 | 128.1677 | 54.1526 | 9.9085 | 88.6221 | 3.7279 | 5.637 | 30.9942 | 180.0307 | 28.9398 | 398.8422 | 254.1829 | 373.6346 | 23.5129 | 108.9878 | 12.0213 | 116 | 19.908 | 36.8227 | 443.9679 | 0.14014
4289 | 967.0061 | 2.1424 | 46.5802 | 115.6807 | 54.139 | 9.9214 | 82.6188 | 2.0741 | 5.3319 | 20.6618 | 166.1758 | 28.2035 | 342.975 | 208.6418 | 342.0183 | 12.7584 | 103.7092 | 11.995 | 110 | 19.5167 | 32.9644 | 368.8379 | 0.13735
4290 | 924.5688 | 2.5881 | 43.7832 | 106.8231 | 53.6411 | 10.3945 | 71.7766 | 1.2631 | 5.2143 | 15.8477 | 136.4603 | 23.3494 | 287.0928 | 145.4932 | 307.3389 | 8.2138 | 95.9431 | 12.0318 | 120 | 19.9893 | 31.0207 | 308.7693 | 0.052951
4291 | 910.4887 | 2.1221 | 41.5026 | 103.8725 | 56.4702 | 7.7068 | 56.787 | 1.0476 | 5.047 | 13.9227 | 108.1624 | 11.1726 | 260.1473 | 111.0328 | 278.0262 | 8.0375 | 89.7136 | 12.0683 | 115 | 19.7257 | 30.9517 | 267.3177 | 0.041782
4292 | 884.886 | 1.7702 | 37.7008 | 98.3199 | 56.8083 | 7.3856 | 50.6102 | 1.166 | 5.0345 | 11.9304 | 95.2517 | 6.3725 | 224.9179 | 99.3644 | 253.0643 | 7.8064 | 84.7525 | 11.6697 | 109 | 17.3391 | 27.3049 | 238.8968 | 0.016177
4293 | 862.6745 | 2.5093 | 37.1633 | 96.9987 | 56.6385 | 7.5468 | 44.1142 | 1.1373 | 5.0446 | 10.734 | 85.5067 | 6.3395 | 192.1648 | 91.9994 | 242.2427 | 7.917 | 79.7214 | 10.9433 | 100 | 16.3112 | 23.1339 | 225.6719 | 0.001048
4294 | 848.2649 | 2.4188 | 36.6569 | 96.6739 | 55.8158 | 8.3284 | 48.7294 | 1.2823 | 5.4488 | 12.0547 | 76.7882 | 8.08 | 175.2672 | 89.7298 | 237.1533 | 8.2312 | 77.2315 | 10.853 | 97 | 16.0106 | 21.4498 | 223.8003 | 0
4295 | 833.516 | 1.4938 | 36.3659 | 96.9879 | 57.0342 | 7.171 | 49.5677 | 1.3913 | 6.05 | 14.4792 | 75.5304 | 9.0179 | 165.9774 | 90.1261 | 229.6356 | 8.3457 | 76.8207 | 10.9585 | 95 | 15.4825 | 21.7364 | 227.0431 | 0
4296 | 837.8774 | 1.1941 | 36.3437 | 96.4469 | 56.1486 | 8.0123 | 48.0134 | 1.6001 | 5.8884 | 15.3594 | 76.1228 | 9.0839 | 147.1349 | 88.2134 | 214.2563 | 8.3657 | 76.353 | 11.0135 | 96 | 15.3821 | 21.5395 | 226.5631 | 0
4297 | 834.9379 | 1.1589 | 36.0346 | 96.3757 | 57.0649 | 7.1418 | 51.2546 | 1.5433 | 5.8266 | 15.4403 | 75.567 | 9.0162 | 141.8081 | 86.0003 | 208.7975 | 9.1259 | 76.0657 | 11.0153 | 95 | 15.3796 | 20.6371 | 224.8865 | 0
4298 | 822.3616 | 1.247 | 36.0671 | 95.9696 | 56.1711 | 7.9909 | 45.2001 | 1.3874 | 5.7682 | 15.3913 | 75.2201 | 9.0952 | 157.1626 | 85.9273 | 215.5981 | 8.7057 | 76.1774 | 10.9935 | 94 | 15.3092 | 20.8374 | 224.8619 | 0
4299 | 824.2754 | 1.5503 | 35.8897 | 68.4532 | 55.6052 | 8.5285 | 47.5501 | 1.3025 | 5.9401 | 15.7779 | 73.8486 | 8.1789 | 164.8964 | 86.0294 | 213.5938 | 8.1377 | 75.8308 | 10.9203 | 93 | 15.3365 | 20.7782 | 224.6844 | 0
4300 | 823.7264 | 1.3674 | 35.8158 | 92.9587 | 56.9744 | 7.2278 | 46.0099 | 1.1097 | 5.8487 | 20.0746 | 71.6271 | 6.709 | 165.4047 | 84.1789 | 206.9512 | 7.8908 | 74.8795 | 10.7857 | 92 | 15.3854 | 21.0763 | 232.683 | 0
4301 | 844.3596 | 0.98825 | 36.0586 | 85.6331 | 56.1106 | 8.0483 | 49.1628 | 1.0014 | 5.2847 | 26.3595 | 71.3357 | 7.0621 | 172.2955 | 90.8677 | 200.5117 | 7.7793 | 74.2452 | 10.7378 | 96 | 15.3634 | 20.7764 | 249.3125 | 0.099322
4302 | 862.0963 | 2.0522 | 40.7894 | 89.835 | 54.9177 | 9.1816 | 57.7886 | 1.4564 | 4.8311 | 33.8067 | 79.2925 | 11.4951 | 192.881 | 118.2058 | 205.3901 | 11.7469 | 74.4246 | 10.7179 | 112 | 16.1747 | 23.3607 | 280.1722 | 0.13322
4303 | 897.9046 | 3.9294 | 64.0827 | 102.2029 | 50.7582 | 13.1331 | 72.7676 | 2.068 | 5.0925 | 39.3968 | 107.2204 | 22.9482 | 217.8794 | 153.4232 | 228.7402 | 21.2961 | 77.9355 | 10.9622 | 138 | 22.8776 | 34.1844 | 334.1032 | 0.16686
4304 | 950.5584 | 7.0212 | 110.8803 | 161.6895 | 48.987 | 14.8158 | 89.0238 | 2.9277 | 5.0208 | 36.5179 | 144.5794 | 29.3227 | 267.7822 | 190.3259 | 276.4579 | 26.7988 | 87.172 | 11.5929 | 137 | 28.4024 | 41.8249 | 393.7641 | 0.24718
4305 | 1005.4163 | 12.0148 | 64.9144 | 143.17 | 49.2868 | 14.531 | 95.3286 | 3.4933 | 5.2316 | 30.9939 | 162.2686 | 30.6202 | 415.0476 | 225.3941 | 322.7629 | 27.9447 | 99.7555 | 12.4782 | 146 | 25.8485 | 43.7578 | 442.73 | 0.25226
4306 | 1042.246 | 14.787 | 83.5202 | 127.1954 | 48.7037 | 15.0849 | 100.9812 | 3.4769 | 5.4192 | 29.8543 | 161.2161 | 35.4064 | 503.7502 | 246.5951 | 351.781 | 28.1427 | 109.1181 | 12.3446 | 137 | 25.8087 | 57.2174 | 471.5983 | 0.27905
4307 | 1064.9561 | 12.8997 | 92.8506 | 131.437 | 49.4424 | 14.3831 | 104.9752 | 3.5114 | 5.414 | 30.4118 | 161.8769 | 36.5899 | 515.4071 | 258.5612 | 374.4262 | 28.7622 | 111.631 | 12.0646 | 141 | 27.8899 | 34.2412 | 485.0653 | 0.21877
4308 | 1066.4158 | 11.3487 | 91.4556 | 134.4143 | 49.717 | 14.1223 | 112.4169 | 3.5956 | 5.9246 | 28.1049 | 168.6668 | 34.6633 | 552.1162 | 264.7375 | 387.5419 | 28.3268 | 109.6516 | 12.1797 | 141 | 25.5773 | 41.4803 | 490.584 | 0.23133
4309 | 1066.4622 | 7.0675 | 92.2409 | 135.2749 | 49.6222 | 14.2124 | 107.4508 | 3.4361 | 6.2474 | 31.553 | 177.2044 | 31.5197 | 545.5663 | 265.5894 | 395.1454 | 28.8757 | 107.9551 | 12.4771 | 144 | 27.3159 | 44.1758 | 494.1899 | 0.24424
4310 | 1070.563 | 4.354 | 91.3766 | 134.8247 | 50.2034 | 13.6603 | 104.3855 | 3.3199 | 6.1428 | 38.3867 | 183.405 | 29.5311 | 467.1974 | 264.5961 | 395.331 | 29.8342 | 108.6004 | 12.2794 | 140 | 28.5375 | 45.6806 | 493.6244 | 0.26853
4311 | 1063.6129 | 4.3022 | 87.2443 | 131.3466 | 51.3219 | 12.5977 | 92.5287 | 3.266 | 5.7894 | 36.4191 | 186.1916 | 28.273 | 408.1741 | 253.6743 | 378.1025 | 28.6184 | 109.1324 | 12.0276 | 138 | 25.3447 | 24.753 | 478.2006 | 0.27197
4312 | 1042.2688 | 3.9806 | 62.7299 | 128.7777 | 53.763 | 10.2786 | 84.7785 | 3.0793 | 5.7841 | 27.9728 | 182.5704 | 27.1452 | 354.1048 | 229.3989 | 349.0207 | 22.7388 | 106.726 | 12.1226 | 134 | 16.0673 | 29.8783 | 440.296 | 0.19786
4313 | 989.6007 | 3.223 | 47.9458 | 116.6871 | 55.2706 | 8.8464 | 83.1271 | 2.2651 | 6.3093 | 20.2517 | 167.1191 | 27.1144 | 322.0566 | 191.4477 | 321.0036 | 12.1029 | 100.2895 | 12.1844 | 126 | 15.5775 | 32.2534 | 381.5724 | 0.17125
4314 | 932.833 | 2.4037 | 59.2381 | 104.3711 | 55.6156 | 8.5186 | 72.2322 | 1.8711 | 6.238 | 16.4786 | 138.391 | 21.7138 | 289.7724 | 151.7717 | 299.6197 | 7.7845 | 92.8528 | 12.2065 | 120 | 13.8187 | 32.1242 | 323.6995 | 0.16101
4315 | 893.1382 | 1.3751 | 42.6867 | 102.1171 | 56.286 | 7.8818 | 56.7976 | 1.6825 | 5.8295 | 14.401 | 109.9517 | 9.5036 | 255.5917 | 129.3695 | 280.6591 | 6.9262 | 87.5328 | 12.2019 | 128 | 11.538 | 32.3579 | 276.5601 | 0.14762
4316 | 864.411 | 1.3264 | 31.7504 | 99.794 | 56.5593 | 7.6222 | 50.9344 | 1.5008 | 5.9214 | 12.6981 | 96.5524 | 4.9929 | 231.0769 | 121.0414 | 253.0318 | 6.8147 | 83.9154 | 11.8906 | 110 | 11.3206 | 32.2037 | 244.7002 | 0.088454
4317 | 840.2738 | 2.6398 | 39.707 | 99.6899 | 55.8383 | 8.307 | 43.2516 | 1.5544 | 6.1336 | 11.7831 | 88.1781 | 4.813 | 205.2237 | 116.8712 | 224.3544 | 7.1632 | 81.0764 | 11.3427 | 107 | 11.6836 | 32.0058 | 232.5518 | 0.014001
4318 | 821.4406 | 2.6564 | 48.339 | 106.1452 | 55.5515 | 8.5796 | 44.9351 | 1.6221 | 5.9879 | 11.6628 | 78.867 | 4.9307 | 175.7932 | 113.6386 | 207.3907 | 7.4464 | 79.0877 | 11.4299 | 91 | 12.3205 | 32.2009 | 233.7134 | 0
4319 | 805.3647 | 1.5439 | 50.9722 | 108.117 | 56.485 | 7.6927 | 49.565 | 1.4799 | 6.1737 | 12.9791 | 76.3711 | 6.5221 | 164.4622 | 113.5617 | 210.8537 | 7.7825 | 78.6722 | 11.6648 | 101 | 12.3731 | 41.3357 | 234.4937 | 0
4320 | 811.7584 | 1.1277 | 51.1108 | 106.8236 | 57.2832 | 6.9344 | 45.2147 | 1.391 | 6.4891 | 14.8394 | 77.7081 | 7.1747 | 162.5623 | 114.7367 | 211.8837 | 7.4947 | 79.0379 | 11.5271 | 99 | 10.8305 | 32.1238 | 231.573 | 0
4321 | 808.5055 | 1.1248 | 69.3477 | 108.1763 | 56.0776 | 8.0797 | 47.2221 | 1.3962 | 6.628 | 15.5561 | 76.8961 | 7.2595 | 177.0763 | 112.5609 | 205.4714 | 7.5195 | 78.8945 | 11.29 | 95 | 11.413 | 32.1238 | 229.6791 | 0
4322 | 800.5245 | 1.1297 | 38.0568 | 75.9577 | 55.6451 | 8.4906 | 49.2424 | 1.3851 | 6.6147 | 15.7419 | 75.9075 | 7.1697 | 183.5668 | 110.189 | 203.3028 | 7.8381 | 78.5366 | 11.1468 | 93 | 12.056 | 24.6948 | 232.0536 | 0
4323 | 796.1138 | 1.1303 | 46.4362 | 91.7113 | 56.1906 | 7.9724 | 44.1737 | 1.3773 | 6.472 | 15.8221 | 74.794 | 6.791 | 178.4262 | 108.534 | 204.4441 | 7.787 | 78.1815 | 11.076 | 95 | 11.1021 | 24.011 | 234.2923 | 0
4324 | 801.7784 | 1.1014 | 50.8001 | 104.9984 | 56.6013 | 7.5822 | 46.3598 | 1.3938 | 6.2239 | 17.2234 | 72.024 | 5.2235 | 174.6302 | 105.712 | 197.3528 | 7.3127 | 77.5326 | 10.8549 | 95 | 11.4525 | 23.5782 | 234.4726 | 0
4325 | 812.0838 | 0.94364 | 50.68 | 94.7848 | 55.1586 | 8.9528 | 44.5396 | 1.1433 | 5.834 | 20.1379 | 69.973 | 5.3542 | 177.3241 | 104.0177 | 193.9332 | 7.1031 | 76.8967 | 10.7447 | 98 | 11.0705 | 24.1889 | 241.0777 | 0.056204
4326 | 840.3076 | 2.3414 | 56.7458 | 95.1285 | 53.1286 | 10.8813 | 52.9903 | 1.184 | 5.9833 | 25.7727 | 76.6344 | 10.7968 | 181.0699 | 118.7556 | 202.3091 | 10.9212 | 76.8183 | 10.7215 | 117 | 12.6751 | 27.5948 | 271.5733 | 0.086122
4327 | 883.2687 | 8.9404 | 66.1484 | 104.8838 | 48.8146 | 14.9795 | 73.0344 | 1.6141 | 5.7876 | 31.1899 | 104.1635 | 23.7621 | 180.2985 | 154.7955 | 225.867 | 21.5777 | 79.6265 | 10.9913 | 128 | 20.3753 | 38.4309 | 326.8778 | 0.1762
4328 | 948.0236 | 20.5677 | 76.5202 | 129.4317 | 49.7948 | 14.0484 | 97.6536 | 2.5744 | 5.912 | 31.7246 | 139.8063 | 29.862 | 205.6814 | 195.5193 | 263.9857 | 26.8141 | 87.086 | 11.7808 | 135 | 22.3028 | 43.4127 | 381.4908 | 0.20479
4329 | 1034.5793 | 19.2594 | 86.0767 | 154.4061 | 49.0829 | 14.7247 | 113.3509 | 3.1484 | 6.0837 | 31.1948 | 159.165 | 30.0105 | 280.5742 | 227.9359 | 303.8542 | 26.239 | 96.7182 | 11.9109 | 145 | 20.9713 | 42.2121 | 420.7239 | 0.21457
4330 | 1076.0192 | 11.2879 | 90.8759 | 163.0797 | 49.359 | 14.4624 | 118.6688 | 3.4267 | 6.15 | 31.6095 | 165.0158 | 30.2008 | 360.2815 | 247.7789 | 339.6259 | 27.4813 | 104.5019 | 12.9111 | 148 | 22.7578 | 41.736 | 449.2398 | 0.24026
4331 | 1079.3863 | 8.8091 | 91.558 | 139.8804 | 49.6498 | 14.1861 | 119.8284 | 3.5935 | 5.9867 | 32.859 | 166.9262 | 31.5517 | 396.4049 | 258.933 | 356.101 | 28.3958 | 108.1034 | 12.6499 | 143 | 23.8096 | 42.2547 | 465.0425 | 0.20031
4332 | 1077.0202 | 8.0215 | 92.0972 | 179.1483 | 48.085 | 15.6727 | 124.3353 | 3.6712 | 5.701 | 32.0876 | 171.0913 | 31.2359 | 403.5921 | 265.3478 | 361.8509 | 28.3392 | 107.7998 | 12.0474 | 156 | 23.2601 | 44.0616 | 472.8812 | 0.22011
4333 | 1083.3754 | 8.5008 | 124.3746 | 151.4947 | 48.2187 | 15.5457 | 115.2763 | 3.6095 | 6.1598 | 32.0027 | 177.7962 | 30.5207 | 409.589 | 262.378 | 373.7167 | 28.5429 | 107.741 | 12.3113 | 149 | 25.4184 | 41.6378 | 481.9458 | 0.21311
4334 | 1088.9068 | 9.1113 | 69.2455 | 170.8085 | 48.464 | 15.3127 | 108.2108 | 3.5296 | 6.9625 | 35.4447 | 180.7727 | 30.4301 | 378.8923 | 255.3991 | 384.7108 | 28.7029 | 109.7196 | 12.5014 | 157 | 27.4521 | 28.3111 | 486.5408 | 0.12937
4335 | 1062.0395 | 8.4869 | 75.7562 | 159.5779 | 50.8987 | 12.9997 | 91.0417 | 3.3947 | 7.215 | 36.4904 | 178.9289 | 30.4812 | 359.399 | 247.2014 | 371.5696 | 28.5294 | 110.887 | 12.6664 | 149 | 24.9672 | 21.8384 | 479.8425 | 0.086252
4336 | 1037.5978 | 7.7456 | 58.7233 | 144.9186 | 53.764 | 10.2777 | 81.4905 | 3.0505 | 6.6607 | 32.0634 | 174.9902 | 29.6094 | 333.1316 | 231.8581 | 347.6691 | 23.362 | 109.104 | 13.0916 | 132 | 20.4452 | 26.6499 | 442.8243 | 0.13922
4337 | 1013.0219 | 5.0713 | 46.1244 | 83.2956 | 55.4064 | 8.7174 | 78.3317 | 1.7865 | 6.3225 | 24.3634 | 164.4565 | 27.6421 | 294.8934 | 191.8813 | 327.1767 | 13.0351 | 103.9126 | 12.2564 | 120 | 17.3196 | 28.1318 | 379.8069 | 0.17115
4338 | 961.3419 | 3.1894 | 44.9018 | 84.7459 | 53.2655 | 10.7512 | 67 | 1.0922 | 5.8669 | 17.0614 | 137.5596 | 22.0052 | 268.4623 | 139.4783 | 290.2768 | 8.3013 | 97.7276 | 11.7462 | 115 | 18.4209 | 36.6227 | 321.6788 | 0.096115
4339 | 926.5448 | 2.4862 | 44.0109 | 97.6362 | 53.3573 | 10.664 | 53.1988 | 1.1602 | 5.7064 | 12.1273 | 108.0721 | 9.5508 | 222.6956 | 107.08 | 256.3609 | 7.9928 | 92.3091 | 11.7743 | 114 | 18.4596 | 28.3111 | 270.2575 | 0.044414
4340 | 904.1637 | 2.1565 | 42.4558 | 59.4649 | 54.3255 | 9.7442 | 43.4357 | 1.1695 | 5.8085 | 11.1303 | 94.2059 | 4.5355 | 199.8229 | 94.0234 | 242.884 | 8.0075 | 86.7004 | 11.5508 | 109 | 17.1471 | 21.9655 | 231.2356 | 0.014693
4341 | 879.5101 | 3.4889 | 48.2999 | 80.6696 | 56.8206 | 7.3738 | 46.4388 | 1.8697 | 5.9033 | 12.1858 | 85.3325 | 4.5156 | 192.4998 | 90.5963 | 231.887 | 7.9388 | 81.6618 | 11.0222 | 100 | 16.6617 | 26.6751 | 216.8394 | 0.0022404
4342 | 870.4312 | 2.9191 | 51.725 | 101.6085 | 54.6124 | 9.4717 | 42.5407 | 1.954 | 6.1258 | 14.1775 | 76.6964 | 6.1395 | 176.3511 | 92.2798 | 217.1021 | 8.481 | 79.7453 | 10.9467 | 100 | 14.7981 | 28.1147 | 218.0553 | 0
4343 | 857.3706 | 1.8246 | 51.4292 | 68.9196 | 54.3965 | 9.6768 | 45.6344 | 1.6891 | 6.4069 | 16.3044 | 74.3849 | 7.0549 | 177.1678 | 93.013 | 213.7637 | 8.395 | 79.9133 | 10.9945 | 96 | 15.9026 | 28.1498 | 223.7881 | 0
4344 | 848.7684 | 1.3232 | 51.6555 | 102.4901 | 55.356 | 8.7653 | 47.4267 | 1.5039 | 6.5573 | 16.3315 | 73.9353 | 7.1048 | 185.744 | 90.7902 | 211.4838 | 8.5142 | 79.9186 | 11.3538 | 95 | 15.9886 | 28.202 | 226.0925 | 0
4345 | 845.5173 | 1.1251 | 51.2367 | 67.8206 | 57.7447 | 6.496 | 44.3905 | 1.3833 | 6.5639 | 15.4618 | 73.2169 | 7.1335 | 187.1942 | 87.9785 | 206.1478 | 8.6429 | 79.796 | 11.2695 | 94 | 15.0292 | 28.6495 | 227.201 | 0
4346 | 840.6712 | 1.3073 | 51.1873 | 85.2174 | 57.8564 | 6.3899 | 44.4197 | 1.4062 | 6.3845 | 15.2078 | 73.2212 | 7.1639 | 184.1542 | 86.1054 | 204.2031 | 8.5823 | 79.8694 | 11.0494 | 91 | 14.8214 | 28.1613 | 229.9707 | 0
4347 | 840.333 | 1.2362 | 51.1464 | 84.8573 | 56.8349 | 7.3603 | 43.1741 | 1.3988 | 6.5049 | 15.4111 | 72.4826 | 6.8501 | 180.5117 | 85.2912 | 202.2135 | 8.7783 | 79.7473 | 11.0159 | 92 | 16.2876 | 28.265 | 231.5406 | 0
4348 | 837.4988 | 1.3582 | 51.1373 | 82.1673 | 56.6194 | 7.565 | 45.5727 | 1.3785 | 6.2069 | 16.9953 | 70.021 | 5.3439 | 183.3189 | 83.7557 | 198.2825 | 8.3518 | 79.1115 | 10.8379 | 95 | 14.6776 | 28.1724 | 232.2392 | 0
4349 | 848.1955 | 1.2514 | 51.3992 | 82.0478 | 56.5489 | 7.632 | 43.5576 | 1.1735 | 5.6455 | 19.757 | 68.1022 | 5.4601 | 193.7513 | 93.6174 | 194.3148 | 8.0159 | 78.497 | 10.7445 | 97 | 15.9583 | 36.7543 | 240.3775 | 0.02935
4350 | 874.5841 | 2.0665 | 57.3429 | 108.6745 | 52.1714 | 11.7906 | 51.5451 | 1.124 | 5.6259 | 28.2331 | 75.481 | 10.7769 | 193.4944 | 120.8229 | 200.2364 | 11.4196 | 78.7116 | 10.7265 | 110 | 17.0861 | 21.9513 | 278.6525 | 0.045321
4351 | 907.1121 | 2.782 | 72.2609 | 118.3521 | 49.78 | 14.0624 | 70.2971 | 1.582 | 5.4918 | 41.4627 | 103.1265 | 22.2135 | 217.9772 | 158.3645 | 215.652 | 21.5059 | 81.8475 | 10.9502 | 122 | 25.3865 | 33.7956 | 349.1987 | 0.050182
4352 | 966.0099 | 3.432 | 87.8138 | 143.6297 | 48.8163 | 14.978 | 86.1841 | 2.8168 | 6.5933 | 49.4692 | 135.5934 | 28.3496 | 254.9575 | 195.2835 | 258.9676 | 27.5058 | 89.6133 | 11.5196 | 126 | 29.334 | 41.7785 | 427.8352 | 0.069261
4353 | 1039.5027 | 7.3313 | 98.1418 | 141.4479 | 47.8451 | 15.9006 | 91.9478 | 3.8731 | 8.4918 | 48.7623 | 153.2901 | 28.7304 | 288.039 | 220.6917 | 311.7663 | 28.9334 | 99.2314 | 11.7811 | 138 | 28.4234 | 44.1339 | 491.4203 | 0.078579
4354 | 1075.6288 | 10.0234 | 96.5831 | 182.3498 | 48.3246 | 15.4451 | 99.2411 | 3.7988 | 8.7441 | 42.0766 | 160.1678 | 28.4226 | 329.7838 | 235.7449 | 347.1188 | 29.6163 | 107.4413 | 11.8371 | 132 | 31.4215 | 43.074 | 515.3025 | 0.14466
4355 | 1083.7266 | 6.5884 | 94.0978 | 151.6156 | 48.4645 | 15.3122 | 101.5446 | 3.6876 | 10.0441 | 38.8287 | 165.9453 | 28.4526 | 358.0592 | 244.6996 | 368.5531 | 29.8735 | 112.2748 | 11.8238 | 147 | 31.4117 | 36.1447 | 501.1114 | 0.064153
4356 | 1079.7797 | 3.6788 | 94.6659 | 137.9501 | 47.32 | 16.3994 | 101.1703 | 3.7294 | 9.4067 | 36.696 | 174.6297 | 28.4065 | 367.8265 | 250.1983 | 378.5905 | 30.1294 | 111.614 | 11.8489 | 136 | 27.0347 | 32.6444 | 486.8242 | 0.11939
4357 | 1087.4315 | 4.1919 | 96.5632 | 138.6328 | 45.869 | 17.778 | 99.3149 | 3.6573 | 7.723 | 33.4483 | 180.1606 | 28.3953 | 376.1512 | 253.8582 | 385.6617 | 30.6709 | 110.1699 | 12.1156 | 137 | 28.3977 | 33.1439 | 489.0343 | 0.20038
4358 | 1097.3007 | 5.998 | 92.9437 | 141.0192 | 44.162 | 19.3995 | 99.9639 | 3.5709 | 7.4152 | 34.8702 | 180.0256 | 28.2311 | 379.9812 | 259.4616 | 393.2444 | 30.8839 | 112.253 | 12.2219 | 132 | 31.1966 | 43.0928 | 485.0881 | 0.15012
4359 | 1086.6677 | 4.3928 | 86.0979 | 140.3261 | 47.3786 | 16.3438 | 96.7602 | 3.4347 | 8.0198 | 33.7702 | 178.6953 | 27.828 | 372.4128 | 258.1155 | 381.7305 | 30.6961 | 114.3113 | 12.2078 | 127 | 26.083 | 25.5205 | 466.9668 | 0.11911
4360 | 1053.5161 | 2.5484 | 92.4822 | 116.6227 | 53.5803 | 10.4522 | 84.8805 | 2.7927 | 7.8287 | 28.7919 | 177.8726 | 26.8422 | 365.8783 | 240.5848 | 355.7047 | 24.7711 | 112.9201 | 12.1321 | 118 | 18.6211 | 31.1908 | 426.2954 | 0.1728
4361 | 1006.6518 | 2.3362 | 47.3368 | 122.1327 | 56.2808 | 7.8867 | 76.1566 | 1.8137 | 6.1599 | 22.9057 | 166.0699 | 26.41 | 323.0123 | 196.4576 | 332.9027 | 13.0283 | 105.9775 | 11.8863 | 114 | 17.0083 | 33.1531 | 361.3402 | 0.16428
4362 | 950.8651 | 1.919 | 56.7375 | 121.0781 | 56.6077 | 7.5762 | 70.7016 | 1.2093 | 5.3499 | 16.0488 | 134.5636 | 21.3971 | 277.3481 | 141.1687 | 305.6197 | 8.4062 | 97.0474 | 12.0277 | 113 | 18.0385 | 42.9539 | 305.1329 | 0.14334
4363 | 907.3516 | 1.8424 | 60.0958 | 102.787 | 57.293 | 6.9251 | 58.6281 | 1.0343 | 5.475 | 11.9047 | 103.2746 | 9.6382 | 248.13 | 110.9683 | 274.7467 | 8.37 | 90.5392 | 12.065 | 115 | 18.2002 | 25.8516 | 264.5431 | 0.13242
4364 | 879.8897 | 1.5311 | 54.2662 | 92.3683 | 55.4357 | 8.6896 | 49.1617 | 1.1986 | 5.4847 | 10.6637 | 88.3777 | 4.5758 | 225.4257 | 102.8303 | 245.1799 | 8.1454 | 84.946 | 11.9142 | 108 | 17.3464 | 30.8066 | 233.4642 | 0.048208
4365 | 862.3919 | 2.5143 | 57.1264 | 74.4972 | 56.0105 | 8.1435 | 51.3292 | 1.1359 | 5.5743 | 10.3959 | 78.9315 | 4.5294 | 201.146 | 97.7461 | 232.4812 | 8.0666 | 80.5418 | 11.7137 | 106 | 16.682 | 33.3862 | 221.1871 | 0.012232
4366 | 864.4117 | 2.649 | 59.9742 | 114.6257 | 56.6073 | 7.5765 | 46.7769 | 1.2555 | 5.7867 | 11.4474 | 70.6511 | 5.2312 | 181.7777 | 93.3418 | 228.5677 | 8.3457 | 78.8672 | 11.903 | 104 | 16.9895 | 33.1207 | 222.7357 | 0
4367 | 850.4873 | 1.6246 | 60.1568 | 97.2214 | 55.7522 | 8.3889 | 51.7001 | 1.4598 | 6.0543 | 13.7285 | 69.2118 | 6.6469 | 167.9661 | 92.4114 | 221.1 | 8.6081 | 78.9806 | 12.6484 | 104 | 17.8758 | 42.8582 | 230.489 | 0
4368 | 848.0963 | 1.7978 | 60.448 | 88.3513 | 35.5473 | 7.0967 | 53.6806 | 1.4843 | 6.3425 | 15.2657 | 71.2634 | 7.214 | 155.413 | 93.3339 | 223.5859 | 8.9084 | 79.3204 | 12.8765 | 106 | 18.8033 | 25.6905 | 239.5126 | 0
4369 | 844.5031 | 1.5466 | 60.4489 | 89.7102 | 35.2343 | 7.394 | 53.4121 | 1.6765 | 6.3692 | 15.5081 | 71.9511 | 7.1304 | 248.632 | 92.0182 | 220.2611 | 8.5586 | 79.7235 | 12.3408 | 102 | 18.5651 | 40.7178 | 243.4429 | 0
4370 | 824.1146 | 1.2237 | 59.9066 | 100.7792 | 32.7386 | 9.765 | 55.3302 | 1.5954 | 6.3433 | 15.4304 | 71.6622 | 7.1797 | 173.0139 | 89.6208 | 209.2972 | 8.7925 | 79.6885 | 11.4743 | 103 | 18.181 | 25.9189 | 241.7573 | 0
4371 | 827.3296 | 1.2359 | 59.9041 | 133.8656 | 34.2633 | 8.3165 | 55.5674 | 1.4683 | 6.354 | 16.1436 | 71.3429 | 7.25 | 192.1067 | 88.8287 | 207.6605 | 8.6815 | 79.1975 | 11.1913 | 99 | 18.541 | 23.3873 | 238.5768 | 0
4372 | 819.4756 | 1.6753 | 59.5816 | 102.7697 | 34.4015 | 8.1852 | 54.2105 | 1.3276 | 6.4103 | 18.3817 | 69.8675 | 6.1463 | 219.6587 | 87.6523 | 203.4146 | 8.5495 | 78.8562 | 11.072 | 96 | 18.5214 | 22.0864 | 241.3823 | 0
4373 | 821.9919 | 2.2156 | 59.3254 | 93.869 | 34.7378 | 7.8657 | 51.5465 | 1.1114 | 6.3604 | 20.6541 | 68.6025 | 5.7284 | 235.6407 | 94.034 | 199.9036 | 8.3849 | 78.4695 | 10.8091 | 99 | 16.7475 | 34.5375 | 249.4521 | 0.02111
4374 | 852.8251 | 2.5013 | 62.9278 | 102.7435 | 31.9699 | 10.4952 | 60.6788 | 1.402 | 5.9401 | 30.5622 | 71.7908 | 10.8865 | 221.7905 | 118.5329 | 209.2127 | 11.8557 | 78.6256 | 10.6964 | 108 | 17.1507 | 40.0135 | 276.081 | 0.023831
4375 | 914.6629 | 2.898 | 69.8846 | 107.573 | 27.3724 | 14.8628 | 78.013 | 1.8787 | 5.7519 | 46.9598 | 84.0255 | 22.7477 | 218.9734 | 153.2327 | 228.4733 | 22.8919 | 81.8332 | 10.9558 | 119 | 23.3399 | 39.4765 | 334.1951 | 0.060776
4376 | 971.9842 | 7.6117 | 81.4638 | 122.0835 | 25.3671 | 16.7678 | 93.2916 | 2.755 | 8.2479 | 51.3088 | 115.3091 | 28.5095 | 255.0436 | 184.0468 | 265.9597 | 28.4154 | 89.0602 | 11.5885 | 132 | 30.0282 | 39.5009 | 399.7686 | 0.077011
4377 | 1017.7883 | 9.4211 | 92.5503 | 131.9509 | 24.9421 | 17.1716 | 102.7023 | 3.3326 | 8.9446 | 43.7126 | 151.9399 | 30.6926 | 297.124 | 208.2595 | 311.582 | 28.8593 | 97.9987 | 11.9079 | 133 | 28.1754 | 51.3179 | 444.4181 | 0.10056
4378 | 1059.6951 | 9.9304 | 93.2035 | 135.0816 | 25.8104 | 16.3467 | 112.0096 | 4.0291 | 7.6744 | 35.9838 | 168.4349 | 30.604 | 345.6057 | 228.002 | 343.7167 | 28.3355 | 105.6142 | 11.9196 | 130 | 29.9914 | 30.5829 | 460.4169 | 0.14739
4379 | 1073.9971 | 9.2964 | 92.4194 | 137.5294 | 26.7923 | 15.4139 | 119.3911 | 4.6129 | 8.3699 | 33.5867 | 172.0438 | 29.5838 | 326.2396 | 235.2491 | 361.3621 | 27.7176 | 108.8676 | 11.9759 | 143 | 30.6324 | 37.2101 | 465.863 | 0.15804
4380 | 1071.2613 | 5.4553 | 93.0242 | 110.2202 | 27.7523 | 14.5019 | 120.2184 | 4.2327 | 7.5176 | 33.4194 | 175.4083 | 28.7437 | 389.0445 | 231.593 | 363.1415 | 27.6076 | 107.8416 | 11.9798 | 144 | 31.4785 | 51.1468 | 474.1211 | 0.19294
4381 | 1072.1496 | 3.0613 | 93.4822 | 169.8633 | 25.705 | 16.4468 | 123.1543 | 3.7144 | 7.5165 | 35.9546 | 177.0277 | 28.741 | 345.724 | 232.9929 | 360.1265 | 27.8695 | 108.286 | 12.0476 | 147 | 31.7157 | 30.6288 | 471.8309 | 0.18531
4382 | 1066.7087 | 2.9624 | 92.7003 | 152.6206 | 27.2756 | 14.9547 | 123.9845 | 3.5958 | 7.914 | 42.4159 | 177.2398 | 29.0043 | 369.6585 | 235.3463 | 370.5354 | 28.3549 | 111.0404 | 11.9521 | 174 | 29.586 | 48.6637 | 461.7609 | 0.15418
4383 | 1047.8193 | 4.1103 | 82.5575 | 137.6524 | 30.2167 | 12.1607 | 113.6695 | 4.0168 | 7.25 | 42.9138 | 164.9151 | 28.5814 | 412.8263 | 231.6456 | 359.3006 | 29.0178 | 110.072 | 12.0244 | 165 | 24.2403 | 30.7542 | 452.8984 | 0.12435
4384 | 1011.1741 | 3.8768 | 56.7236 | 124.3281 | 33.2581 | 9.2714 | 106.0047 | 3.6218 | 6.0875 | 38.2016 | 137.2428 | 27.5198 | 324.3135 | 219.0757 | 323.7121 | 18.4901 | 104.1812 | 12.1136 | 159 | 18.8735 | 35.6153 | 419.0966 | 0.14799
4385 | 960.9161 | 2.7255 | 44.1399 | 112.2279 | 34.0433 | 8.5254 | 98.2987 | 2.3378 | 5.52 | 33.37 | 114.2892 | 26.6819 | 372.0599 | 177.3532 | 291.8852 | 9.3029 | 97.0456 | 12.1231 | 148 | 17.0174 | 35.8349 | 356.0871 | 0.10246
4386 | 915.0025 | 1.8629 | 40.7087 | 101.8354 | 34.7334 | 7.8699 | 81.8767 | 1.3335 | 5.4704 | 24.4859 | 101.9807 | 21.5139 | 279.8296 | 127.6744 | 264.784 | 7.7129 | 91.3025 | 12.1291 | 140 | 16.9522 | 34.5048 | 297.339 | 0.097077
4387 | 867.5369 | 1.276 | 39.0207 | 98.2268 | 35.0109 | 7.6062 | 63.025 | 1.1372 | 5.5138 | 15.5034 | 91.4487 | 9.5067 | 277.3167 | 104.0195 | 247.9381 | 7.5579 | 86.435 | 12.0929 | 124 | 16.6808 | 33.7635 | 261.6241 | 0.063159
4388 | 837.913 | 1.3396 | 38.8265 | 97.0267 | 34.2289 | 8.3491 | 56.8021 | 1.1842 | 5.5614 | 11.8974 | 80.6875 | 4.4742 | 250.0293 | 95.6836 | 241.7641 | 7.6142 | 81.6494 | 11.8527 | 113 | 16.5223 | 30.5738 | 243.5403 | 0.024094
4389 | 818.8909 | 2.1368 | 39.1724 | 83.2642 | 34.7328 | 7.8704 | 49.9635 | 1.1236 | 5.5347 | 10.8046 | 74.5893 | 4.5187 | 291.9398 | 89.0663 | 228.7899 | 7.4771 | 77.29 | 11.8671 | 110 | 16.8648 | 35.6727 | 234.304 | 0.0025284
4390 | 814.1294 | 2.4514 | 38.8938 | 98.2196 | 35.0218 | 7.5959 | 53.2868 | 1.3173 | 5.4906 | 11.9329 | 72.7905 | 6.1178 | 219.9905 | 86.8405 | 224.9568 | 7.7581 | 75.2409 | 11.9875 | 103 | 17.2496 | 27.2925 | 229.9182 | 0
4391 | 810.445 | 1.77 | 38.9488 | 109.386 | 34.383 | 8.2028 | 54.8464 | 1.4238 | 6.0667 | 14.3846 | 72.0321 | 7.1076 | 242.792 | 86.9072 | 230.8072 | 8.4154 | 75.3066 | 11.6741 | 103 | 17.335 | 27.2925 | 227.2311 | 0
4392 | 813.953 | 1.2755 | 52.3425 | 89.1561 | 50.0515 | 7.8933 | 50.7353 | 1.6592 | 6.1533 | 15.5343 | 70.9214 | 7.2191 | 189.2511 | 84.6849 | 228.2296 | 8.2312 | 75.3118 | 11.4885 | 108 | 17.2758 | 21.2209 | 226.1624 | 0
4393 | 803.5752 | 1.2866 | 29.1011 | 110.6551 | 50.3379 | 7.6212 | 54.6166 | 1.5964 | 6.2921 | 15.7789 | 69.9574 | 7.1639 | 194.0588 | 83.1967 | 223.7382 | 8.0989 | 75.2071 | 11.1733 | 113 | 17.3154 | 23.5339 | 226.5895 | 0
4394 | 794.4229 | 1.7094 | 35.4381 | 89.5282 | 50.3487 | 7.6109 | 54.6847 | 1.4333 | 6.2305 | 15.9409 | 69.6078 | 7.2439 | 171.1802 | 83.97 | 220.2026 | 7.8124 | 75.6794 | 10.9676 | 107 | 17.1291 | 24.0117 | 227.823 | 0
4395 | 791.6801 | 1.6243 | 38.5901 | 108.2604 | 48.8019 | 9.0804 | 55.3576 | 1.4552 | 6.0441 | 16.7571 | 70.0301 | 7.3606 | 174.1485 | 84.2928 | 212.9326 | 7.8264 | 76.308 | 10.9801 | 107 | 17.4195 | 23.6103 | 227.5058 | 0
4396 | 799.2626 | 1.8487 | 38.43 | 100.0235 | 50.6873 | 7.2893 | 52.3876 | 1.3967 | 6.39 | 18.6845 | 68.8836 | 6.9268 | 197.7909 | 82.3852 | 203.5899 | 7.5364 | 76.0902 | 10.9309 | 106 | 17.4995 | 23.4292 | 225.6857 | 0
4397 | 803.9535 | 2.5951 | 38.2551 | 95.4326 | 50.607 | 7.3656 | 56.3156 | 1.1893 | 6.2908 | 20.7239 | 66.0901 | 5.201 | 172.1826 | 80.1477 | 199.4779 | 7.6278 | 75.3325 | 10.6917 | 98 | 17.3683 | 23.4875 | 225.722 | 0.0069949
4398 | 810.9271 | 3.284 | 38.2999 | 81.5067 | 49.6398 | 8.2844 | 56.068 | 1.1898 | 5.8092 | 21.783 | 65.5193 | 4.4098 | 198.5258 | 79.5655 | 199.1717 | 7.5382 | 74.8653 | 10.6123 | 110 | 16.8747 | 37.8334 | 230.8297 | 0.0090841
4399 | 824.625 | 1.8345 | 38.5683 | 105.5534 | 50.1134 | 7.8345 | 51.2579 | 1.241 | 5.5718 | 20.8315 | 71.7805 | 6.5743 | 179.0388 | 79.4335 | 200.2944 | 7.4601 | 74.686 | 10.8938 | 113 | 19.8349 | 31.1562 | 243.5546 | 0.03229
4400 | 825.5153 | 0.98585 | 39.269 | 85.9548 | 50.3046 | 7.6528 | 57.3258 | 1.1677 | 5.4482 | 21.4933 | 91.3164 | 12.3246 | 187.1701 | 80.0549 | 216.528 | 7.3064 | 74.8203 | 11.4775 | 112 | 23.4169 | 31.1562 | 255.8771 | 0.061834
4401 | 856.0169 | 0.88259 | 41.8581 | 109.6549 | 49.7065 | 8.2211 | 57.7646 | 1.6386 | 5.6181 | 27.0289 | 117.0283 | 15.0327 | 211.9847 | 84.1479 | 236.5571 | 7.4244 | 75.805 | 11.6922 | 115 | 20.4888 | 24.0279 | 262.0626 | 0.12548
4402 | 864.4435 | 0.73549 | 43.1568 | 104.0072 | 48.6552 | 9.2198 | 55.1415 | 2.7404 | 5.584 | 32.9658 | 134.3361 | 15.0544 | 192.6495 | 89.1005 | 247.4651 | 7.5593 | 76.9104 | 11.731 | 122 | 20.471 | 28.9017 | 262.2969 | 0.15242
4403 | 858.9489 | 1.0201 | 43.3494 | 100.2688 | 48.9724 | 8.9185 | 59.301 | 3.4123 | 5.4899 | 33.1076 | 141.3476 | 14.9883 | 205.1797 | 92.1347 | 247.3349 | 7.56 | 76.93 | 11.7285 | 120 | 25.6509 | 31.5017 | 262.0349 | 0.1898
4404 | 842.094 | 1.2284 | 57.9859 | 88.5074 | 47.856 | 9.979 | 56.0438 | 3.3801 | 5.3222 | 31.4703 | 143.0176 | 14.9214 | 194.6735 | 94.1464 | 239.1331 | 7.3295 | 76.4811 | 11.6861 | 123 | 14.607 | 31.1988 | 268.6282 | 0.28606
4405 | 833.9222 | 1.6113 | 32.3933 | 100.9924 | 49.555 | 8.365 | 59.4002 | 1.9671 | 5.4058 | 31.4355 | 144.4388 | 14.9651 | 191.7936 | 96.5688 | 225.1357 | 7.2829 | 76.8511 | 11.6944 | 130 | 18.8477 | 31.2483 | 277.1917 | 0.21851
4406 | 824.9562 | 1.3495 | 38.6609 | 110.1127 | 49.6908 | 8.236 | 61.6785 | 1.2503 | 5.7167 | 32.0796 | 146.0521 | 16.1736 | 187.3822 | 98.9672 | 221.1191 | 7.3608 | 78.1359 | 11.833 | 138 | 18.1193 | 30.8713 | 275.9886 | 0.18823
4407 | 828.5398 | 0.96865 | 39.6778 | 100.8157 | 50.0801 | 7.8661 | 57.5312 | 1.4595 | 5.9237 | 28.9864 | 133.4775 | 15.4942 | 174.009 | 99.2088 | 222.547 | 7.4028 | 78.29 | 11.9388 | 130 | 16.4275 | 31.2275 | 266.6772 | 0.17403
4408 | 833.5515 | 1.0253 | 38.4281 | 82.1493 | 50.3354 | 7.6236 | 56.0238 | 1.1827 | 6.0872 | 19.9287 | 109.0915 | 8.1366 | 182.7335 | 99.6719 | 224.9316 | 7.1783 | 77.1531 | 11.9512 | 128 | 15.0853 | 31.2509 | 253.9836 | 0.11275
4409 | 838.3779 | 1.0677 | 38.4363 | 106.6568 | 50.4319 | 7.532 | 55.2826 | 0.93363 | 5.9005 | 12.8344 | 94.4082 | 4.4456 | 201.5158 | 99.1302 | 244.195 | 7.2952 | 77.1037 | 11.9519 | 127 | 15.3854 | 31.0303 | 245.6729 | 0.091731
4410 | 844.7168 | 1.0598 | 51.4561 | 101.4317 | 49.6213 | 8.302 | 50.9876 | 1.1308 | 5.4827 | 10.0513 | 89.5955 | 4.458 | 125.4339 | 98.0059 | 246.2494 | 7.5415 | 77.5244 | 11.9767 | 111 | 15.4566 | 31.2008 | 243.2194 | 0.16123
4411 | 841.4241 | 0.97538 | 28.5794 | 98.4171 | 50.8007 | 7.1816 | 51.1694 | 1.0786 | 5.4963 | 9.5664 | 83.0561 | 4.4694 | 158.6835 | 96.6117 | 222.5054 | 7.3746 | 76.8038 | 12.0474 | 108 | 15.015 | 30.6456 | 236.8769 | 0.11816
4412 | 841.102 | 1.0302 | 35.6604 | 96.7812 | 49.8612 | 8.0741 | 54.1592 | 0.98372 | 5.5357 | 9.4243 | 73.8234 | 4.5103 | 200.214 | 93.4246 | 210.4383 | 7.2572 | 75.719 | 11.9115 | 117 | 15.3111 | 30.3595 | 230.9419 | 0.061335
4413 | 835.6518 | 1.7917 | 46.4633 | 97.0065 | 50.1651 | 7.7854 | 50.8893 | 0.98103 | 5.5225 | 9.2451 | 68.8705 | 4.4851 | 180.3327 | 87.8584 | 206.703 | 7.5198 | 75.2345 | 11.3409 | 115 | 15.239 | 26.9175 | 227.9921 | 0.013802
4414 | 832.3522 | 2.6519 | 50.2941 | 101.6664 | 50.4185 | 7.5446 | 54.4473 | 1.1902 | 5.8281 | 9.6471 | 68.0719 | 4.8579 | 185.6959 | 82.0935 | 207.9144 | 7.3404 | 75.1138 | 11.5376 | 112 | 15.3417 | 24.0143 | 226.6907 | 0
4415 | 820.2122 | 1.9768 | 50.3871 | 105.4427 | 49.564 | 8.3564 | 56.2682 | 1.543 | 5.9245 | 11.9015 | 69.154 | 6.4558 | 201.3549 | 82.6356 | 213.3858 | 7.752 | 75.4069 | 11.9984 | 106 | 19.1467 | 32.1739 | 226.4885 | 0
4416 | 824.5591 | 1.2185 | 50.431 | 106.2014 | 49.3406 | 8.5686 | 51.6075 | 1.5874 | 6.0791 | 14.2723 | 71.3566 | 7.121 | 226.4847 | 85.5078 | 223.6074 | 8.0363 | 76.104 | 11.7754 | 107 | 10.9868 | 19.4409 | 226.7506 | 0
4417 | 818.4139 | 1.1988 | 50.6708 | 107.5936 | 49.4094 | 8.5033 | 54.3065 | 1.4969 | 6.5522 | 14.4811 | 72.306 | 7.1471 | 156.9788 | 84.9189 | 221.2976 | 8.2333 | 76.354 | 11.3991 | 105 | 14.0607 | 23.4133 | 226.797 | 0
4418 | 796.9916 | 1.1708 | 50.3232 | 106.6658 | 49.3381 | 8.571 | 54.871 | 1.4379 | 6.4476 | 14.1418 | 72.3051 | 7.3154 | 142.3276 | 83.3744 | 215.6748 | 8.0648 | 76.1135 | 11.0142 | 108 | 14.6716 | 24.9918 | 227.0607 | 0
4419 | 799.066 | 1.3036 | 49.9775 | 105.3937 | 50.1499 | 7.7998 | 52.194 | 1.3801 | 6.4999 | 13.4535 | 71.6568 | 6.5853 | 177.4918 | 82.5434 | 214.4047 | 7.7314 | 75.8755 | 10.7513 | 109 | 14.7808 | 25.0056 | 227.8388 | 0
4420 | 807.8445 | 1.385 | 49.814 | 102.77 | 50.4386 | 7.5255 | 55.7781 | 1.1668 | 6.1706 | 11.7016 | 69.4063 | 5.0495 | 168.3025 | 81.7446 | 211.0576 | 7.2548 | 75.4797 | 10.6804 | 105 | 14.8241 | 24.9235 | 228.0831 | 0
4421 | 813.4138 | 1.5842 | 49.4565 | 86.3114 | 50.2674 | 7.6882 | 54.4585 | 1.0224 | 5.7358 | 10.1424 | 67.1481 | 4.4482 | 191.8778 | 80.2535 | 210.6266 | 7.171 | 75.0117 | 10.708 | 103 | 14.7437 | 25.103 | 226.9701 | 0.043773
4422 | 834.6309 | 1.4284 | 48.1737 | 111.6827 | 50.3657 | 7.5948 | 51.2002 | 1.2938 | 5.6005 | 9.4984 | 66.5616 | 4.5523 | 168.0248 | 78.838 | 205.5072 | 7.6205 | 74.7153 | 10.6966 | 117 | 14.5916 | 25.3297 | 225.123 | 0.067274
4423 | 845.9552 | 1.2835 | 41.3389 | 97.606 | 49.6115 | 8.3113 | 56.9572 | 1.2257 | 5.5835 | 9.2757 | 72.0598 | 4.5671 | 173.6275 | 78.9543 | 200.7053 | 7.424 | 74.5715 | 10.9542 | 117 | 16.5665 | 32.5069 | 229.7722 | 0.11841
4424 | 840.2823 | 1.2972 | 37.9002 | 90.6469 | 50.0704 | 7.8754 | 58.2535 | 1.0953 | 5.554 | 14.3779 | 91.8875 | 4.7525 | 136.1215 | 80.5836 | 212.7623 | 7.7544 | 74.8631 | 11.5585 | 118 | 16.9482 | 19.3783 | 240.7695 | 0.20369
4425 | 835.1066 | 0.97104 | 37.7435 | 90.2025 | 48.8246 | 9.0588 | 56.6522 | 1.0979 | 5.436 | 23.8846 | 113.8962 | 4.8565 | 169.6731 | 83.9028 | 230.023 | 7.3974 | 76.1696 | 11.7993 | 117 | 15.5087 | 30.7994 | 243.9629 | 0.1996
4426 | 851.5208 | 1.0427 | 37.5853 | 93.6652 | 50.5944 | 7.3776 | 59.2808 | 1.0174 | 5.7037 | 30.6125 | 121.9368 | 4.844 | 159.6974 | 87.9629 | 239.1845 | 7.1036 | 78.093 | 11.7742 | 116 | 17.4309 | 19.3492 | 241.7244 | 0.20881
4427 | 858.5437 | 1.1841 | 37.5339 | 96.0586 | 50.6017 | 7.3706 | 56.555 | 1.0087 | 5.7954 | 31.5869 | 126.7937 | 4.7832 | 153.7747 | 91.5442 | 240.83 | 7.2986 | 79.1852 | 11.7348 | 120 | 18.3393 | 30.8284 | 241.7166 | 0.21619
4428 | 854.5466 | 1.5625 | 37.7502 | 95.7741 | 50.4365 | 7.5275 | 56.6392 | 0.98885 | 5.9999 | 29.2896 | 136.0796 | 4.8165 | 182.0218 | 95.0546 | 244.868 | 7.0597 | 79.087 | 11.8262 | 119 | 17.3367 | 25.0895 | 243.7783 | 0.24173
4429 | 844.9401 | 1.9134 | 38.0456 | 80.0537 | 50.3369 | 7.6222 | 57.7733 | 1.2541 | 6.0834 | 27.7005 | 142.4123 | 5.4553 | 159.7058 | 99.659 | 244.7532 | 7.1493 | 78.1728 | 11.9686 | 118 | 18.0362 | 19.4158 | 245.3588 | 0.27605
4430 | 852.3505 | 1.7175 | 38.2804 | 105.5036 | 50.341 | 7.6183 | 52.9479 | 1.1629 | 5.8842 | 25.1947 | 144.1868 | 6.2724 | 190.0228 | 103.6158 | 236.6894 | 7.3316 | 73.6714 | 12.006 | 122 | 16.3684 | 30.7619 | 245.3194 | 0.19093
4431 | 855.7243 | 1.1741 | 38.0382 | 99.5836 | 50.3404 | 7.6188 | 48.9181 | 0.95921 | 5.715 | 20.1745 | 132.0727 | 7.3447 | 184.2828 | 102.2736 | 234.3459 | 7.7308 | 64.6626 | 11.9673 | 123 | 15.9698 | 19.4702 | 244.6843 | 0.18744
4432 | 841.8541 | 1.4371 | 37.8817 | 97.7656 | 50.3135 | 7.6444 | 52.9644 | 0.96437 | 5.4325 | 14.9573 | 107.4779 | 5.8055 | 200.149 | 98.3498 | 227.658 | 7.4781 | 57.1709 | 11.9475 | 124 | 15.9829 | 23.517 | 238.9377 | 0.11569
4433 | 847.1169 | 1.2643 | 37.8658 | 97.2519 | 51.1124 | 6.8854 | 53.6164 | 0.93917 | 5.4616 | 11.632 | 92.4922 | 4.6337 | 204.9208 | 96.054 | 216.7803 | 7.4027 | 54.3673 | 11.9746 | 124 | 16.4945 | 32.2801 | 232.8184 | 0.20499
4434 | 827.2632 | 1.1163 | 37.8676 | 86.1832 | 49.9572 | 7.9829 | 50.1878 | 0.969 | 5.4675 | 9.7769 | 88.5331 | 4.5152 | 207.2779 | 93.7139 | 207.4371 | 7.3699 | 54.0164 | 12.012 | 108 | 15.4994 | 19.279 | 231.9451 | 0.14008
4435 | 814.2865 | 1.3284 | 37.8894 | 79.1566 | 50.7681 | 7.2126 | 51.9851 | 0.98822 | 5.4166 | 9.2128 | 84.373 | 4.5002 | 202.435 | 92.6173 | 204.7475 | 7.5561 | 54.3803 | 12.0022 | 102 | 15.3245 | 28.1339 | 229.7163 | 0.095064
4436 | 813.7347 | 1.3009 | 39.3623 | 81.5205 | 49.9799 | 7.9613 | 54.0328 | 1.2602 | 5.4365 | 9.1823 | 77.9786 | 4.4962 | 221.3181 | 92.4325 | 212.6916 | 7.4971 | 54.5952 | 11.9246 | 106 | 15.0719 | 40.4317 | 228.5685 | 0.066684
4437 | 805.9344 | 2.2024 | 46.5125 | 87.9053 | 50.7967 | 7.1854 | 49.3742 | 1.2053 | 5.6333 | 9.2005 | 73.1146 | 4.4538 | 236.6026 | 90.0681 | 217.1319 | 7.5483 | 54.2802 | 11.924 | 105 | 16.078 | 24.4297 | 232.8688 | 0.0069238
4438 | 796.4811 | 2.5193 | 49.9173 | 73.9343 | 49.1577 | 8.7424 | 49.6154 | 1.2333 | 5.6987 | 9.9926 | 71.5462 | 5.2759 | 151.2503 | 86.785 | 217.9285 | 7.4358 | 54.3502 | 11.7534 | 100 | 16.4884 | 38.3259 | 237.1051 | 0
4439 | 785.2379 | 1.795 | 50.0483 | 108.2096 | 49.1195 | 8.7787 | 55.0852 | 1.4108 | 5.849 | 12.0395 | 72.4011 | 6.833 | 193.2578 | 86.3754 | 224.6484 | 7.793 | 54.8275 | 11.9156 | 102 | 15.7073 | 15.6893 | 239.0813 | 0
4440 | 787.2375 | 1.3254 | 49.9117 | 99.9243 | 50.1018 | 7.8455 | 51.2707 | 1.4394 | 6.0618 | 13.7538 | 73.6983 | 7.2137 | 230.1945 | 86.183 | 222.9902 | 8.3379 | 54.8066 | 11.8534 | 101 | 13.0367 | 12.1075 | 237.5901 | 0
4441 | 776.5299 | 1.2853 | 49.8772 | 94.4934 | 49.5913 | 8.3305 | 52.4477 | 1.4505 | 6.1228 | 14.1746 | 74.0419 | 7.2153 | 155.4402 | 85.2198 | 216.0161 | 8.1619 | 54.7456 | 11.5263 | 101 | 13.6375 | 19.2702 | 234.0907 | 0
4442 | 764.5343 | 1.1974 | 50.0249 | 95.7459 | 50.1898 | 7.7619 | 55.2464 | 1.4587 | 6.385 | 14.1817 | 73.8842 | 7.1867 | 184.2482 | 85.1366 | 211.7478 | 7.8345 | 54.8524 | 11.1647 | 100 | 12.3953 | 12.0046 | 232.0112 | 0
4443 | 768.42 | 1.1307 | 49.8472 | 94.9341 | 48.9379 | 8.9512 | 51.6102 | 1.5838 | 6.4021 | 14.4665 | 73.0596 | 6.8138 | 166.8136 | 84.8027 | 208.4622 | 7.8829 | 54.6775 | 11.0496 | 100 | 13.9328 | 25.3759 | 231.3179 | 0
4444 | 776.2022 | 1.5305 | 49.8249 | 91.4859 | 49.7216 | 8.2067 | 49.8669 | 1.4562 | 6.4789 | 16.0758 | 70.6826 | 5.2448 | 181.187 | 84.0399 | 200.0632 | 7.6643 | 54.1522 | 10.867 | 103 | 12.3223 | 26.1988 | 238.088 | 0
4445 | 787.7292 | 1.1509 | 49.4683 | 72.3676 | 49.5917 | 8.3301 | 55.7547 | 1.1532 | 5.8843 | 18.5578 | 68.6239 | 5.4042 | 189.029 | 90.7868 | 197.8681 | 7.3377 | 53.6294 | 10.728 | 107 | 13.8983 | 24.3207 | 253.2209 | 0.040866
4446 | 821.5215 | 1.7271 | 53.5756 | 112.2879 | 45.1906 | 11.2871 | 59.3626 | 1.1094 | 5.372 | 26.8268 | 70.8239 | 10.9496 | 208.3717 | 113.514 | 199.2692 | 10.6417 | 53.6811 | 10.7185 | 132 | 12.9526 | 27.7854 | 287.967 | 0.086483
4447 | 874.319 | 2.9991 | 61.9296 | 120.7339 | 41.7828 | 15.2002 | 81.0947 | 1.6305 | 5.2633 | 39.4965 | 83.5085 | 23.2194 | 235.4914 | 84.6791 | 211.8557 | 19.4059 | 56.0382 | 11.0082 | 158 | 21.9389 | 55.8947 | 349.3528 | 0.12451
4448 | 945.8651 | 3.45 | 74.4872 | 120.0118 | 34.707 | 17.5119 | 97.441 | 2.3415 | 5.4048 | 44.507 | 115.237 | 29.561 | 164.4104 | 174.8088 | 256.6534 | 23.5569 | 62.3786 | 11.6047 | 158 | 25.0375 | 36.3043 | 408.393 | 0.19751
4449 | 1007.5795 | 3.6591 | 85.328 | 176.5913 | 31.3528 | 17.2599 | 104.9853 | 2.7543 | 5.6867 | 42.8638 | 152.5229 | 30.5401 | 224.9278 | 191.1344 | 308.222 | 24.2515 | 70.1652 | 11.8084 | 174 | 26.7872 | 43.7842 | 435.9701 | 0.20377
4450 | 1028.7145 | 3.357 | 87.9352 | 171.8789 | 33.5589 | 16.4433 | 110.6983 | 3.2691 | 5.6473 | 37.2266 | 168.1655 | 31.6067 | 295.2224 | 208.2003 | 340.3739 | 25.0693 | 80.8941 | 12.2048 | 192 | 28.5755 | 47.5434 | 439.6487 | 0.24903
4451 | 1057.0547 | 3.3057 | 82.3922 | 149.603 | 33.9879 | 16.9483 | 116.8337 | 3.7553 | 5.7364 | 31.5958 | 168.9912 | 31.9865 | 288.9 | 217.9212 | 347.5342 | 25.2753 | 95.9451 | 12.9074 | 162 | 32.732 | 47.6743 | 439.786 | 0.20459
4452 | 1054.5522 | 3.4186 | 38.0932 | 186.1437 | 36.0901 | 17.1427 | 118.6648 | 4.234 | 5.882 | 27.9696 | 173.0327 | 31.341 | 264.9866 | 223.8141 | 344.9965 | 22.4264 | 105.3149 | 12.6673 | 176 | 25.6434 | 61.2746 | 447.8275 | 0.2038
4453 | 1062.6755 | 3.4979 | 46.462 | 177.7981 | 39.1034 | 17.0211 | 117.7728 | 4.3148 | 5.8627 | 27.9197 | 177.1548 | 30.6769 | 291.5686 | 226.8018 | 350.843 | 20.3744 | 106.82 | 12.954 | 170 | 25.2994 | 36.5301 | 456.3517 | 0.23799
4454 | 1075.3036 | 3.4524 | 51.5673 | 163.3633 | 48.0018 | 14.3671 | 115.0139 | 4.2193 | 6.0179 | 32.7812 | 178.2236 | 30.1376 | 275.0026 | 227.6588 | 360.9372 | 20.7469 | 106.1355 | 13.4134 | 167 | 25.9143 | 44.4298 | 458.0947 | 0.22978
4455 | 1065.4442 | 3.4456 | 51.4813 | 115.6998 | 51.9456 | 12.6528 | 105.8004 | 4.053 | 6.1238 | 32.7115 | 165.5317 | 29.7724 | 293.1704 | 226.0414 | 362.002 | 15.8752 | 102.5443 | 12.6792 | 149 | 24.1476 | 47.4101 | 458.0875 | 0.22762
4456 | 1034.9018 | 3.5931 | 50.9152 | 104.587 | 55.5968 | 9.4857 | 98.0366 | 3.6523 | 5.7641 | 28.3302 | 139.8957 | 28.4344 | 227.8793 | 216.5497 | 340.4736 | 9.9494 | 97.5786 | 12.1341 | 128 | 20.1685 | 44.1467 | 431.1856 | 0.19952
4457 | 976.0616 | 2.9958 | 50.6306 | 90.5449 | 57.0579 | 9.1521 | 89.9337 | 2.1053 | 5.6667 | 22.9156 | 119.9115 | 27.4021 | 275.0644 | 180.1637 | 300.7794 | 7.937 | 93.7004 | 12.0159 | 126 | 15.3605 | 40.3267 | 378.2157 | 0.19254
4458 | 927.4576 | 2.3318 | 50.9915 | 95.8829 | 58.3109 | 8.1774 | 80.3452 | 1.1394 | 5.6214 | 16.6207 | 107.4674 | 22.0441 | 218.5992 | 134.6695 | 272.4176 | 7.7807 | 88.284 | 11.975 | 123 | 12.9373 | 37.5898 | 329.9374 | 0.16629
4459 | 903.0561 | 1.8764 | 51.3383 | 80.177 | 57.023 | 8.1969 | 64.9763 | 1.2886 | 5.475 | 12.3762 | 99.3155 | 9.8996 | 207.0225 | 110.6833 | 258.5596 | 8.0252 | 81.4979 | 12.0203 | 110 | 14.8081 | 35.9613 | 287.6421 | 0.12991
4460 | 880.406 | 1.4445 | 52.1369 | 68.9803 | 56.2822 | 7.9811 | 53.4026 | 1.2398 | 5.6085 | 10.5717 | 92.9498 | 4.5977 | 258.4003 | 99.5618 | 250.8211 | 7.7717 | 76.5335 | 11.8891 | 101 | 12.6257 | 44.0045 | 249.6577 | 0.072477
4461 | 844.1942 | 2.1758 | 68.5218 | 89.9262 | 56.6334 | 8.3774 | 55.456 | 1.1238 | 5.72 | 10.3274 | 84.1571 | 4.5351 | 197.8412 | 92.9855 | 237.8984 | 7.7009 | 73.8347 | 11.3069 | 101 | 13.7152 | 33.04 | 229.5004 | 0.0083549
4462 | 829.8035 | 3.9094 | 37.8352 | 104.6654 | 55.071 | 7.7261 | 52.7392 | 1.337 | 5.7285 | 10.6661 | 76.1753 | 5.1143 | 208.5311 | 90.2321 | 229.1677 | 8.0637 | 72.939 | 11.024 | 98 | 12.7144 | 25.5026 | 224.7598 | 0
4463 | 817.8447 | 6.6059 | 37.4514 | 90.4765 | 51.3962 | 8.2843 | 53.143 | 1.7445 | 5.9297 | 12.0282 | 74.3 | 6.6963 | 222.7556 | 91.127 | 227.8351 | 8.3498 | 73.369 | 11.1389 | 95 | 11.9185 | 30.896 | 222.3582 | 0
4464 | 818.5481 | 3.8385 | 37.4611 | 62.9121 | 49.9048 | 7.9146 | 54.963 | 1.7093 | 6.1293 | 13.6455 | 76.1011 | 7.2509 | 212.2041 | 90.9948 | 227.7348 | 8.3334 | 73.8618 | 11.3483 | 100 | 12.7997 | 33.1467 | 221.968 | 0
4465 | 810.4655 | 1.2689 | 37.7195 | 99.5978 | 45.5439 | 10.351 | 51.6963 | 1.5505 | 6.201 | 14.1193 | 76.9667 | 7.2727 | 190.4834 | 88.4265 | 226.7828 | 8.1782 | 73.8999 | 11.2099 | 94 | 12.4028 | 44.2489 | 225.2107 | 0
4466 | 806.3727 | 1.2316 | 37.4542 | 87.9959 | 45.426 | 9.3188 | 54.2203 | 1.5723 | 6.3716 | 14.0933 | 76.3302 | 7.2987 | 215.8609 | 87.001 | 224.2788 | 8.5354 | 73.9028 | 11.0332 | 95 | 12.8488 | 26.8056 | 227.6172 | 0
4467 | 807.3919 | 1.34 | 37.3706 | 82.0587 | 45.9335 | 7.8858 | 52.272 | 1.5502 | 6.6079 | 14.4867 | 75.3909 | 7.1416 | 208.7371 | 87.251 | 220.2252 | 8.243 | 73.8449 | 11.0232 | 96 | 13.5181 | 32.5772 | 227.486 | 0
4468 | 797.9072 | 1.7318 | 37.2702 | 59.4644 | 45.5082 | 7.5769 | 51.8951 | 1.3033 | 6.4172 | 16.3197 | 73.0032 | 5.4271 | 173.2387 | 86.1259 | 209.4985 | 8.0443 | 73.3344 | 10.8464 | 95 | 12.9528 | 34.6453 | 231.8584 | 0
4469 | 809.8135 | 1.7031 | 41.2417 | 82.4876 | 43.7405 | 8.3559 | 54.3568 | 1.3945 | 5.9067 | 19.0386 | 70.4074 | 5.5018 | 195.3226 | 92.0066 | 200.7506 | 7.7289 | 72.6034 | 10.6964 | 100 | 12.6044 | 34.8079 | 244.6985 | 0.046237
4470 | 830.1246 | 1.8249 | 56.286 | 111.9083 | 42.1429 | 9.2208 | 56.3429 | 1.3288 | 5.5467 | 27.8141 | 71.7328 | 10.9636 | 180.0876 | 113.5072 | 205.0139 | 11.0135 | 72.5199 | 10.684 | 125 | 14.0099 | 34.6441 | 281.4984 | 0.079107
4471 | 867.2259 | 3.167 | 67.1775 | 115.8829 | 37.6266 | 13.6662 | 80.4614 | 2.2178 | 5.2933 | 39.9613 | 83.496 | 22.9331 | 204.5134 | 143.9536 | 218.8197 | 17.719 | 75.4049 | 11.8618 | 143 | 32.3701 | 34.4777 | 342.815 | 0.12787
4472 | 957.8771 | 5.4666 | 108.5229 | 188.7734 | 38.859 | 15.2072 | 103.1329 | 3.2854 | 5.2777 | 42.2209 | 116.1848 | 29.0041 | 254.7942 | 174.7849 | 258.0396 | 20.5179 | 84.0471 | 12.9174 | 148 | 28.2422 | 44.7723 | 409.3608 | 0.15084
4473 | 1005.5974 | 6.452 | 62.7712 | 98.8474 | 41.0614 | 15.2275 | 108.345 | 3.5298 | 6.0966 | 38.2042 | 151.3487 | 29.6382 | 307.755 | 193.6638 | 298.3427 | 20.2322 | 92.977 | 13.1597 | 159 | 22.3558 | 26.9444 | 454.1982 | 0.20832
4474 | 1043.9677 | 6.3753 | 79.6227 | 139.2461 | 45.455 | 17.3268 | 112.3053 | 3.3423 | 6.5193 | 39.7926 | 165.1433 | 30.8537 | 267.3621 | 203.378 | 323.7874 | 20.8973 | 98.075 | 13.7582 | 181 | 37.408 | 32.2323 | 467.8628 | 0.2047
4475 | 1091.0772 | 6.198 | 87.5472 | 173.4312 | 53.9648 | 15.8766 | 118.5835 | 3.2838 | 6.1207 | 44.6171 | 170.0141 | 31.6172 | 412.1724 | 217.6944 | 343.8198 | 20.6656 | 101.2637 | 13.6406 | 163 | 44.3521 | 44.8495 | 471.5823 | 0.23686
4476 | 1086.1018 | 5.134 | 88.7668 | 164.2176 | 58.5645 | 14.525 | 120.8409 | 3.479 | 5.966 | 42.908 | 174.1491 | 30.4674 | 482.4945 | 226.9563 | 347.8729 | 20.3081 | 100.4756 | 13.7165 | 180 | 40.7748 | 26.8344 | 473.2607 | 0.2327
4477 | 1059.6026 | 4.1325 | 92.4303 | 161.5033 | 62.62 | 14.3611 | 120.9026 | 3.7446 | 5.7755 | 42.3745 | 175.3305 | 29.3369 | 438.6495 | 229.4677 | 349.9584 | 20.3063 | 98.7988 | 14.7405 | 159 | 32.9657 | 42.5158 | 477.5272 | 0.22514
4478 | 1065.1875 | 3.2215 | 84.4535 | 143.2179 | 65.5389 | 14.921 | 119.2889 | 3.7597 | 5.7356 | 46.4324 | 177.7708 | 28.8937 | 372.3558 | 234.5255 | 357.5212 | 20.403 | 100.0958 | 14.492 | 156 | 27.4376 | 26.8344 | 478.5939 | 0.22861
4479 | 1068.0019 | 3.4556 | 60.2143 | 128.2799 | 65.614 | 16.4734 | 109.6845 | 3.469 | 9.8588 | 44.2015 | 167.4065 | 28.5356 | 303.4733 | 230.6552 | 349.2075 | 16.0871 | 99.7142 | 13.1221 | 182 | 23.1747 | 32.3975 | 470.5639 | 0.21959
4480 | 1037.3044 | 3.7702 | 43.2232 | 104.4168 | 61.251 | 15.0845 | 98.9773 | 3.1456 | 11.2867 | 38.3203 | 141.5561 | 27.6246 | 306.8609 | 213.4643 | 336.0182 | 9.6312 | 96.3068 | 12.1979 | 158 | 18.6324 | 44.7943 | 438.5825 | 0.18361
4481 | 991.2514 | 2.8578 | 37.9532 | 116.6574 | 52.0807 | 11.4516 | 95.505 | 1.866 | 7.2067 | 29.525 | 120.9311 | 26.5657 | 291.2506 | 182.5922 | 319.8898 | 6.9249 | 92.0456 | 12.0404 | 139 | 17.3464 | 34.676 | 377.1798 | 0.12074
4482 | 944.5583 | 1.6494 | 36.8637 | 100.6167 | 47.1007 | 9.0581 | 84.7802 | 1.2043 | 5.4067 | 17.5573 | 108.1774 | 21.5204 | 293.0755 | 149.4127 | 306.1888 | 7.0252 | 87.8036 | 12.041 | 137 | 18.6139 | 26.8806 | 318.2687 | 0.093088
4483 | 915.8151 | 2.0472 | 34.8633 | 94.191 | 36.2256 | 7.8363 | 64.0129 | 1.1078 | 5.55 | 10.6602 | 98.35 | 9.348 | 241.5062 | 133.1982 | 289.4611 | 6.816 | 85.2367 | 12.0316 | 109 | 18.5326 | 32.3533 | 272.064 | 0.040111
4484 | 893.7281 | 2.6045 | 32.9604 | 91.0577 | 27.5188 | 8.3221 | 49.6824 | 0.97582 | 5.4863 | 9.3237 | 91.6173 | 4.2832 | 245.471 | 128.7881 | 258.3973 | 6.8817 | 81.7842 | 11.8546 | 121 | 16.1697 | 34.8499 | 238.0495 | 0.015476
4485 | 876.2523 | 3.5968 | 65.572 | 84.1926 | 37.2976 | 7.8642 | 52.642 | 1.0973 | 5.3969 | 9.369 | 87.3904 | 4.1544 | 266.2811 | 125.7184 | 230.5684 | 6.9747 | 76.7691 | 11.1109 | 117 | 16.676 | 44.6184 | 225.0045 | 0.00055159
4486 | 871.7314 | 2.9261 | 41.1257 | 112.4553 | 45.5964 | 8.2428 | 51.6062 | 1.4974 | 5.4808 | 10.8375 | 88.3342 | 5.8904 | 238.8333 | 122.2352 | 222.1483 | 7.2372 | 74.5577 | 10.9027 | 107 | 14.2928 | 26.9503 | 224.6357 | 0
4487 | 856.7391 | 1.5262 | 50.0064 | 106.1149 | 45.844 | 8.5535 | 55.6038 | 1.5673 | 5.9293 | 13.2034 | 89.778 | 6.9706 | 191.1124 | 119.711 | 223.6175 | 7.4713 | 74.7967 | 11.01 | 96 | 16.2302 | 32.358 | 222.2537 | 0
4488 | 862.5372 | 1.1393 | 55.3253 | 102.0302 | 43.7607 | 8.587 | 52.189 | 1.4413 | 6.0892 | 14.2038 | 83.3668 | 6.9326 | 222.313 | 117.6552 | 222.4309 | 7.405 | 75.0976 | 11.0542 | 98 | 14.4714 | 34.8616 | 219.838 | 0
4489 | 851.0005 | 1.1384 | 55.3686 | 102.3782 | 42.3473 | 7.8477 | 54.2406 | 1.4438 | 6.1233 | 14.2471 | 77.0454 | 6.9457 | 203.9386 | 114.7191 | 214.4837 | 7.5751 | 75.1491 | 11.0264 | 98 | 14.8275 | 34.663 | 221.7549 | 0
4490 | 840.737 | 1.1358 | 73.3126 | 102.6851 | 40.238 | 8.9774 | 54.5084 | 1.4475 | 6.2975 | 14.4255 | 75.5774 | 7.0209 | 211.5206 | 111.9417 | 215.1335 | 7.4757 | 75.0634 | 10.9966 | 97 | 15.4709 | 44.5453 | 225.0358 | 0
4491 | 840.4572 | 1.1285 | 41.1599 | 102.4842 | 40.6583 | 8.1029 | 53.8777 | 1.5792 | 6.2967 | 15.2721 | 74.4931 | 6.946 | 182.1007 | 112.2522 | 214.0492 | 7.6649 | 74.8629 | 11.0158 | 95 | 16.1112 | 26.8748 | 228.8736 | 0
4492 | 834.4444 | 1.5804 | 68.8931 | 87.1347 | 40.6005 | 7.4719 | 57.4349 | 1.4709 | 6.4133 | 17.3358 | 71.3744 | 5.7458 | 211.218 | 113.9872 | 205.3855 | 7.1608 | 74.023 | 10.9203 | 96 | 15.152 | 32.0406 | 234.7506 | 0
4493 | 840.9862 | 1.9475 | 41.2627 | 110.756 | 37.9143 | 8.3736 | 54.2087 | 1.1456 | 5.9928 | 19.7247 | 68.2666 | 5.5194 | 178.9509 | 113.9954 | 206.4249 | 6.8121 | 73.0203 | 10.7487 | 102 | 14.3495 | 35.0567 | 249.3798 | 0.0099814
4494 | 868.9193 | 2.2559 | 49.7061 | 106.5024 | 33.6583 | 10.5854 | 57.9479 | 1.2002 | 5.3751 | 26.6603 | 69.9479 | 10.6474 | 188.2922 | 125.224 | 211.1866 | 10.5193 | 72.8428 | 10.6694 | 129 | 15.2437 | 34.4562 | 283.3764 | 0.034614
4495 | 920.1017 | 2.6418 | 55.0913 | 105.6943 | 13.0014 | 13.6264 | 76.9607 | 2.8697 | 5.391 | 38.9888 | 83.2098 | 22.179 | 213.5597 | 149.7502 | 223.2256 | 17.6145 | 74.5702 | 10.9297 | 144 | 23.9526 | 34.9636 | 334.5317 | 0.072309
4496 | 985.3632 | 2.8145 | 74.0497 | 116.2365 | -10.7614 | 16.3387 | 93.5212 | 4.3178 | 5.1766 | 46.0309 | 117.4121 | 32.766 | 227.0654 | 174.9137 | 258.4323 | 21.8543 | 81.0999 | 11.5396 | 157 | 28.0731 | 34.6076 | 384.0825 | 0.11997
4497 | 1039.1353 | 3.4409 | 40.9726 | 124.4698 | -15.3989 | 15.6043 | 101.243 | 4.7551 | 6.1203 | 46.8442 | 153.1528 | 33.2939 | 254.1863 | 196.7233 | 300.5156 | 21.4753 | 90.8475 | 11.8372 | 180 | 25.9023 | 34.5834 | 423.1385 | 0.16251
4498 | 1076.8704 | 3.8326 | 50.3261 | 129.0823 | -17.2413 | 17.353 | 107.8824 | 5.4506 | 6.5152 | 46.0912 | 168.8103 | 30.3213 | 326.0794 | 209.4888 | 331.3157 | 20.6031 | 97.4017 | 12.187 | 186 | 29.5938 | 34.6544 | 449.1759 | 0.22166
4499 | 1088.3588 | 4.0245 | 54.9503 | 135.6203 | -7.9818 | 18.1361 | 119.5445 | 4.787 | 6.329 | 38.1268 | 174.2869 | 28.93 | 353.9406 | 214.7114 | 350.9861 | 20.2905 | 100.3962 | 12.4236 | 159 | 33.7968 | 34.6851 | 455.5185 | 0.22674
4500 | 1063.1258 | 3.7827 | 54.8352 | 145.8035 | 19.7794 | 18.7951 | 127.0684 | 3.7258 | 6.6267 | 29.1034 | 176.4605 | 26.5771 | 298.008 | 220.6387 | 357.1952 | 20.081 | 99.9938 | 12.4184 | 192 | 33.7874 | 42.201 | 457.2687 | 0.23815
4501 | 1064.1051 | 3.0562 | 55.0952 | 189.7913 | 33.907 | 18.9325 | 123.7841 | 3.3657 | 6.78 | 27.8157 | 177.63 | 24.6616 | 245.72 | 223.8018 | 358.1799 | 20.1278 | 98.7987 | 12.732 | 171 | 34.3989 | 44.1011 | 467.7552 | 0.19623
4502 | 1084.6012 | 3.172 | 55.5234 | 172.3574 | 40.7135 | 16.2303 | 117.4232 | 3.329 | 6.6033 | 28.5955 | 180.4645 | 26.2952 | 263.1228 | 225.9603 | 361.4559 | 19.9336 | 99.9161 | 13.6905 | 159 | 32.4907 | 43.0209 | 472.0136 | 0.2296
4503 | 1066.6415 | 3.3588 | 73.4926 | 134.6017 | 57.3477 | 12.3417 | 109.4654 | 3.0826 | 6.6 | 27.8863 | 170.0231 | 28.0442 | 307.5632 | 224.4239 | 353.7425 | 15.299 | 98.466 | 12.9901 | 154 | 35.8563 | 41.5945 | 465.0234 | 0.2389
4504 | 1023.202 | 3.5112 | 40.6531 | 102.6539 | 67.5841 | 9.8685 | 103.6971 | 2.6989 | 6.52 | 23.9395 | 145.7175 | 23.6946 | 276.6025 | 214.7865 | 334.6735 | 9.546 | 94.1966 | 12.2596 | 135 | 20.705 | 39.1392 | 434.0475 | 0.17885
4505 | 976.2976 | 3.0921 | 50.3838 | 89.0582 | 62.7481 | 8.2029 | 101.5498 | 1.8785 | 6.0353 | 17.8664 | 128.3156 | 21.1012 | 299.442 | 185.5716 | 309.4302 | 7.2824 | 90.6416 | 12.1247 | 129 | 23.0048 | 36.8204 | 382.2171 | 0.22099
4506 | 934.2265 | 2.594 | 55.2007 | 82.3236 | 57.689 | 8.344 | 89.9144 | 1.1904 | 5.819 | 13.3845 | 119.3425 | 18.1184 | 313.921 | 145.8166 | 284.4311 | 6.9901 | 87.6882 | 12.0891 | 131 | 24.0833 | 35.6105 | 328.8931 | 0.22242
4507 | 896.1479 | 2.4875 | 54.8172 | 78.2372 | 60.2873 | 7.781 | 67.5619 | 1.0574 | 6.119 | 11.2607 | 113.3308 | 8.2145 | 223.762 | 124.2594 | 273.256 | 7.189 | 84.4228 | 12.1398 | 121 | 23.8584 | 35.0923 | 282.3993 | 0.11358
4508 | 858.5821 | 1.8074 | 55.2955 | 56.7298 | 62.0929 | 7.7016 | 52.0108 | 1.0272 | 6.2343 | 10.7064 | 107.9626 | 3.7497 | 228.9285 | 113.8599 | 267.3528 | 7.2288 | 80.4283 | 11.9581 | 106 | 23.9545 | 42.7012 | 253.0631 | 0.09441
4509 | 833.3038 | 2.3121 | 73.8165 | 95.3219 | 61.3736 | 9.6143 | 54.5844 | 1.1594 | 5.8774 | 10.7915 | 98.8118 | 3.6417 | 219.0115 | 103.5925 | 249.5888 | 7.0713 | 77.1007 | 11.7029 | 100 | 22.9279 | 32.2312 | 237.6235 | 0.013864
4510 | 824.5366 | 2.7135 | 40.5698 | 89.6734 | 59.2364 | 8.9536 | 52.9753 | 1.2845 | 5.859 | 11.1387 | 88.1591 | 4.1743 | 241.8149 | 96.3738 | 230.2524 | 7.1207 | 75.797 | 11.7074 | 100 | 21.9407 | 32.2312 | 231.0684 | 0
4511 | 808.8169 | 1.8475 | 40.0448 | 67.671 | 55.4577 | 7.2609 | 55.0742 | 1.383 | 6.0118 | 12.8119 | 82.5333 | 5.6185 | 204.5833 | 93.5806 | 215.2563 | 7.8943 | 75.8855 | 11.4551 | 100 | 23.0241 | 25.0123 | 229.4233 | 0
4512 | 810.2605 | 1.2765 | 39.5719 | 100.7978 | 53.5954 | 6.6441 | 53.5776 | 1.4118 | 6.362 | 14.2443 | 81.6371 | 6.3012 | 231.6025 | 93.0436 | 211.446 | 7.7898 | 76.4088 | 11.3846 | 94 | 20.6281 | 29.8641 | 229.2149 | 0
4513 | 802.2602 | 1.1711 | 39.7159 | 91.442 | 52.3264 | 7.4047 | 55.4237 | 1.3815 | 6.4455 | 13.9071 | 82.3015 | 6.3071 | 238.6482 | 92.3322 | 211.9994 | 7.2998 | 76.6061 | 11.2738 | 102 | 22.3816 | 41.8153 | 230.138 | 0
4514 | 795.313 | 1.1261 | 39.4967 | 86.6322 | 50.848 | 9.0061 | 52.4446 | 1.6825 | 6.4903 | 13.4918 | 82.6328 | 6.3019 | 193.9852 | 91.5698 | 215.431 | 7.3837 | 76.5971 | 11.175 | 97 | 29.0981 | 24.9264 | 231.6115 | 0
4515 | 792.8689 | 1.1187 | 39.0036 | 83.9679 | 51.9824 | 7.3889 | 53.8163 | 1.5409 | 6.4485 | 13.3562 | 80.8951 | 5.7231 | 209.9729 | 89.3809 | 216.1988 | 7.4171 | 76.3081 | 11.1672 | 97 | 16.5042 | 30.3912 | 232.8298 | 0
4516 | 784.3976 | 1.1516 | 37.9974 | 81.8043 | 50.633 | 7.3445 | 52.5637 | 1.151 | 6.3395 | 14.8163 | 77.7684 | 4.1716 | 189.5158 | 84.4639 | 209.7388 | 7.429 | 75.4928 | 10.9985 | 99 | 19.9145 | 32.1652 | 237.5929 | 0
4517 | 790.8499 | 0.93637 | 42.1922 | 86.9466 | 48.2941 | 8.2547 | 54.1897 | 1.0155 | 6.0884 | 17.9155 | 76.0412 | 4.5449 | 220.293 | 84.7702 | 201.5286 | 7.469 | 74.6489 | 10.8805 | 100 | 23.1132 | 32.1251 | 249.9838 | 0.10561
4518 | 814.9689 | 1.7558 | 56.1946 | 105.8234 | 46.5881 | 9.1939 | 60.3529 | 1.0656 | 5.5667 | 23.3759 | 78.8239 | 10.1333 | 191.1134 | 101.4152 | 210.0173 | 9.8521 | 74.5463 | 10.8567 | 128 | 22.9367 | 32.0666 | 283.8722 | 0.19047
4519 | 853.3031 | 2.5866 | 68.9202 | 123.2593 | 41.8419 | 13.711 | 77.3064 | 1.6736 | 5.3408 | 28.9332 | 91.5162 | 19.3859 | 211.1246 | 133.3785 | 224.5341 | 15.7597 | 75.9607 | 11.1253 | 165 | 27.9512 | 32.2248 | 339.8666 | 0.24603
4520 | 905.6325 | 3.2762 | 80.9555 | 148.1708 | 41.0738 | 15.2213 | 97.6029 | 2.5068 | 5.4929 | 30.4711 | 119.7734 | 23.0018 | 233.0188 | 166.2711 | 259.2337 | 12.9793 | 80.8931 | 11.7462 | 150 | 30.1107 | 32.1291 | 397.1981 | 0.21938
4521 | 994.6996 | 3.5602 | 88.5162 | 144.6537 | 44.0145 | 14.4599 | 107.9313 | 3.0418 | 5.5622 | 28.2369 | 151.8724 | 23.5293 | 271.9419 | 188.2878 | 303.6313 | 8.1933 | 86.9158 | 12.2365 | 156 | 38.8315 | 32.2282 | 433.5704 | 0.23763
4522 | 1045.0339 | 3.3653 | 91.0963 | 180.9087 | 45.1248 | 14.9558 | 115.7954 | 3.5172 | 5.6017 | 23.4268 | 168.0767 | 23.9444 | 271.7776 | 198.2578 | 327.3648 | 8.3424 | 90.7698 | 12.5119 | 171 | 44.0752 | 32.341 | 444.3188 | 0.29301
4523 | 1043.8747 | 3.0812 | 90.8548 | 148.5838 | 47.6628 | 14.4994 | 118.9189 | 3.474 | 6.1071 | 20.8563 | 170.2241 | 25.3134 | 276.6868 | 203.2906 | 332.5866 | 9.0663 | 93.4113 | 12.3753 | 164 | 48.0793 | 41.7125 | 449.335 | 0.2274
4524 | 1029.1358 | 3.3794 | 93.7268 | 134.4234 | 46.9747 | 17.7069 | 119.149 | 3.1843 | 5.9515 | 19.524 | 170.0125 | 25.4376 | 313.1815 | 210.4264 | 328.0578 | 8.9735 | 93.8199 | 12.2147 | 176 | 46.8455 | 24.8729 | 453.2772 | 0.2756
4525 | 1033.0457 | 3.2496 | 96.6904 | 136.2147 | 51.6497 | 18.3404 | 118.226 | 3.3208 | 5.5073 | 21.4501 | 169.4375 | 24.165 | 277.5855 | 220.0069 | 324.6962 | 8.7288 | 93.6836 | 12.2807 | 166 | 40.1275 | 31.6512 | 451.8174 | 0.26186
4526 | 1039.3516 | 3.0124 | 84.7342 | 135.732 | 57.2526 | 17.2912 | 115.0298 | 2.8351 | 5.3799 | 26.1477 | 168.5215 | 23.2796 | 295.4382 | 224.9155 | 327.2532 | 8.6827 | 93.959 | 12.4722 | 159 | 40.0983 | 34.7567 | 445.5234 | 0.24439
4527 | 1021.8262 | 3.177 | 57.2847 | 128.3174 | 57.2345 | 13.7227 | 104.7526 | 2.4065 | 5.2228 | 27.6132 | 155.3169 | 23.6669 | 302.4346 | 216.6104 | 332.6371 | 8.4577 | 92.1069 | 12.4647 | 155 | 31.5536 | 34.2885 | 441.166 | 0.16546
4528 | 1008.3704 | 3.5289 | 38.2452 | 114.6735 | 41.9955 | 19.4762 | 97.1288 | 2.369 | 5.5617 | 24.3686 | 129.5986 | 23.7498 | 402.5628 | 196.4376 | 325.2588 | 8.0721 | 89.0712 | 12.3629 | 132 | 23.0778 | 32.4161 | 419.6249 | 0.10795
4529 | 962.9495 | 2.6844 | 32.7974 | 110.6182 | 34.571 | 12.3161 | 91.6016 | 1.7593 | 5.9621 | 16.9019 | 112.3719 | 21.6833 | 296.6812 | 164.3882 | 291.8884 | 7.4892 | 86.8304 | 12.3771 | 129 | 26.2474 | 38.2245 | 358.4303 | 0.078478
4530 | 934.6185 | 2.0898 | 32.1069 | 62.327 | 29.8205 | 9.021 | 89.1985 | 1.3674 | 5.6377 | 11.7135 | 105.9849 | 20.6845 | 337.1149 | 138.2219 | 268.372 | 7.2221 | 85.833 | 12.4044 | 132 | 17.8874 | 24.3343 | 306.1611 | 0.070675
4531 | 891.4454 | 2.2133 | 29.7376 | 82.5529 | 29.8099 | 8.8167 | 60.3733 | 1.1463 | 5.4316 | 11.5042 | 100.5897 | 10.8242 | 272.3099 | 119.141 | 262.2819 | 7.0553 | 83.5315 | 12.9337 | 111 | 19.127 | 22.8152 | 268.7895 | 0.032735
4532 | 864.5209 | 2.7567 | 30.7295 | 89.2862 | 36.1345 | 7.9455 | 51.8715 | 1.1189 | 5.5064 | 12.8219 | 92.8168 | 7.5835 | 365.1384 | 103.2357 | 251.2037 | 7.0151 | 80.0564 | 12.7427 | 108 | 21.0735 | 40.2058 | 236.1442 | 0.021334
4533 | 849.5511 | 3.4276 | 33.8026 | 88.7771 | 47.8927 | 7.2881 | 55.3979 | 1.2426 | 5.6709 | 13.6003 | 84.0696 | 7.8362 | 200.6942 | 98.1059 | 233.5546 | 7.0522 | 77.8968 | 12.1986 | 106 | 18.897 | 17.2336 | 226.093 | 0.0012589
4534 | 839.3824 | 2.6766 | 38.3247 | 43.7236 | 50.9697 | 7.5825 | 56.6796 | 1.3412 | 5.9072 | 15.1234 | 77.0665 | 9.7508 | 183.5232 | 99.3409 | 226.9502 | 7.1655 | 76.9824 | 11.93 | 102 | 19.5869 | 18.9626 | 222.9308 | 0
4535 | 811.1243 | 1.5203 | 38.459 | 102.9571 | 48.99 | 8.1821 | 55.2655 | 1.3869 | 6.3749 | 16.5416 | 74.9456 | 10.2106 | 293.928 | 99.7741 | 230.6481 | 7.8227 | 76.5072 | 12.0503 | 99 | 17.9039 | 22.8336 | 216.1963 | 0
4536 | 812.8749 | 1.1597 | 38.3372 | 73.2612 | 49.6854 | 7.8988 | 55.3088 | 1.3847 | 6.6425 | 16.3197 | 75.188 | 10.1668 | 301.5911 | 96.9607 | 227.1998 | 7.6522 | 76.1259 | 12.5002 | 102 | 19.4111 | 22.8568 | 210.7945 | 0
4537 | 809.1975 | 1.1287 | 38.5884 | 101.132 | 50.02 | 7.7012 | 54.0525 | 1.6355 | 6.6049 | 15.7945 | 74.8716 | 10.2102 | 283.2367 | 93.146 | 221.8826 | 7.6281 | 76.2968 | 12.4415 | 95 | 19.0194 | 22.9111 | 211.3822 | 0
4538 | 796.3246 | 1.4206 | 38.4042 | 73.1514 | 48.19 | 8.2795 | 57.6123 | 1.5647 | 6.5522 | 15.6313 | 74.5605 | 10.33 | 190.6082 | 90.8804 | 216.3525 | 7.5889 | 76.3232 | 11.8475 | 95 | 17.8172 | 25.1213 | 211.8481 | 0
4539 | 788.1822 | 1.3105 | 38.2962 | 100.9806 | 47.8575 | 7.8436 | 53.2233 | 1.4001 | 6.5815 | 16.2257 | 74.5866 | 10.3127 | 205.7581 | 90.6665 | 212.557 | 7.4624 | 76.6218 | 11.3196 | 99 | 19.6177 | 26.0996 | 213.6446 | 0
4540 | 790.8233 | 1.5542 | 38.0193 | 88.6867 | 47.4432 | 7.5817 | 52.9303 | 1.3278 | 6.594 | 19.4544 | 72.6309 | 9.4405 | 269.8711 | 87.897 | 207.6645 | 7.3111 | 76.3995 | 11.0498 | 97 | 16.9302 | 34.0132 | 215.3765 | 0
4541 | 802.575 | 1.7909 | 43.5075 | 87.9685 | 46.065 | 8.3588 | 54.7861 | 1.0892 | 6.0665 | 24.131 | 70.7616 | 8.908 | 266.3644 | 87.1777 | 201.0386 | 7.1838 | 74.6146 | 10.8796 | 101 | 19.5803 | 26.1547 | 218.5237 | 0.027734
4542 | 850.8371 | 2.1343 | 65.2622 | 113.9088 | 43.6895 | 10.6546 | 59.3816 | 0.9752 | 5.748 | 30.6424 | 73.2865 | 13.2577 | 251.8438 | 103.0397 | 205.0867 | 7.305 | 73.6374 | 10.8314 | 125 | 20.1814 | 20.2097 | 242.6034 | 0.090957
4543 | 895.9948 | 2.1525 | 75.4512 | 110.0267 | 40.7227 | 13.506 | 81.2195 | 1.9242 | 5.5347 | 35.922 | 83.1039 | 21.1366 | 215.5562 | 135.4407 | 215.2962 | 7.8279 | 75.846 | 11.2976 | 168 | 32.334 | 24.3491 | 297.7267 | 0.18009
4544 | 928.5177 | 3.1052 | 81.3259 | 162.0306 | 39.2936 | 14.8651 | 101.5122 | 3.1784 | 8.2297 | 34.9085 | 112.8977 | 24.6118 | 289.9931 | 168.1821 | 250.703 | 8.5686 | 81.4742 | 11.8838 | 160 | 38.6799 | 26.1668 | 378.094 | 0.18694
4545 | 971.2529 | 3.6105 | 91.0234 | 173.1842 | 38.1942 | 17.1744 | 110.8775 | 2.9818 | 11.0174 | 29.1041 | 146.8923 | 25.3497 | 256.3232 | 189.4696 | 300.5934 | 8.394 | 86.8682 | 11.9612 | 160 | 34.7318 | 25.9973 | 453.1843 | 0.21357
4546 | 1015.714 | 5.2715 | 94.1778 | 172.8736 | 40.0138 | 17.5442 | 119.7996 | 2.5391 | 8.4092 | 22.0424 | 156.9387 | 25.6916 | 266.1429 | 200.6149 | 326.1486 | 8.65 | 89.1132 | 12.066 | 188 | 40.1851 | 26.3258 | 491.9122 | 0.1636
4547 | 1037.1845 | 6.3357 | 92.7458 | 168.8153 | 44.4205 | 16.9535 | 123.7932 | 2.7574 | 7.8139 | 20.0795 | 156.9537 | 25.1139 | 339.8853 | 208.6801 | 332.1273 | 8.8791 | 90.0676 | 12.3938 | 175 | 41.3039 | 26.0641 | 479.0283 | 0.1633
4548 | 1020.5333 | 6.0815 | 92.6282 | 168.8854 | 49.5442 | 15.7788 | 123.2093 | 2.9761 | 6.7981 | 23.4939 | 161.8671 | 24.2202 | 280.1017 | 212.7388 | 327.0577 | 8.7322 | 90.3428 | 12.4359 | 181 | 39.028 | 26.1947 | 447.2655 | 0.20686
4549 | 1009.8444 | 4.13 | 92.7149 | 167.9379 | 53.5515 | 15.7859 | 125.2041 | 2.9812 | 5.904 | 27.7363 | 166.6301 | 24.4595 | 283.068 | 213.8354 | 324.2434 | 8.2842 | 89.8694 | 12.1124 | 167 | 36.8179 | 25.8698 | 433.5449 | 0.24683
4550 | 1015.983 | 3.1987 | 93.4623 | 164.0348 | 56.7193 | 14.3338 | 123.2978 | 2.9555 | 5.993 | 31.8242 | 168.8648 | 25.121 | 285.1093 | 214.7402 | 334.9801 | 8.2434 | 89.865 | 11.9535 | 171 | 46.3209 | 26.6127 | 422.027 | 0.25907
4551 | 998.3739 | 3.3522 | 43.7055 | 122.8272 | 59.0143 | 13.3265 | 114.7513 | 2.5294 | 6.1972 | 32.3406 | 156.8378 | 24.8801 | 289.069 | 206.7557 | 330.8946 | 7.9566 | 88.5824 | 11.9335 | 152 | 33.7525 | 33.7555 | 406.7855 | 0.24145
4552 | 970.5562 | 2.4488 | 72.9355 | 124.101 | 62.4081 | 9.0246 | 108.1752 | 1.8374 | 6.227 | 27.621 | 131.4174 | 24.3061 | 300.6545 | 186.8523 | 304.2644 | 7.1701 | 85.6464 | 11.8999 | 137 | 19.6867 | 26.1547 | 364.4727 | 0.20835
4553 | 929.8796 | 1.9335 | 43.3535 | 99.2776 | 58.124 | 7.5858 | 103.3751 | 1.639 | 5.6644 | 22.84 | 114.7586 | 23.0014 | 324.8777 | 164.7239 | 279.8964 | 6.8904 | 82.3169 | 11.886 | 117 | 17.7391 | 20.3099 | 300.2324 | 0.21973
4554 | 882.6377 | 1.724 | 39.4214 | 85.8604 | 50.4378 | 8.3374 | 92.0552 | 1.3125 | 5.5388 | 21.7906 | 106.2782 | 19.2061 | 213.2153 | 140.9689 | 265.2516 | 7.1974 | 78.5015 | 11.9458 | 110 | 14.6738 | 31.9981 | 251.7811 | 0.17592
4555 | 850.2437 | 1.1574 | 36.4084 | 81.6827 | 48.8147 | 7.1219 | 68.8602 | 1.0181 | 5.7045 | 22.8768 | 95.7772 | 11.0094 | 264.5939 | 117.6479 | 250.3834 | 6.8703 | 74.6244 | 12.0299 | 108 | 21.2762 | 20.2793 | 220.584 | 0.061276
4556 | 820.4258 | 0.90488 | 36.6484 | 80.9579 | 48.7414 | 7.3039 | 55.658 | 0.95022 | 5.79 | 22.8063 | 86.723 | 7.6171 | 261.0432 | 105.1328 | 244.2054 | 6.9717 | 72.3006 | 11.7589 | 101 | 9.9422 | 32.0287 | 200.088 | 0.024133
4557 | 806.0726 | 1.9463 | 43.9648 | 70.6916 | 37.9607 | 7.6467 | 58.498 | 1.0054 | 5.8233 | 21.5034 | 82.2298 | 7.6237 | 304.1731 | 98.8547 | 239.9284 | 6.9635 | 72.0028 | 11.1023 | 97 | 16.3683 | 20.2706 | 191.9179 | 0.0026106
4558 | 805.2911 | 2.5481 | 46.7073 | 92.8819 | 28.2564 | 7.6122 | 56.9475 | 1.4092 | 5.9567 | 20.1661 | 77.6611 | 8.4451 | 215.2104 | 96.5329 | 235.9906 | 6.9594 | 71.91 | 10.9231 | 102 | 14.8967 | 24.4513 | 194.2161 | 0
4559 | 791.3751 | 1.8162 | 46.5315 | 106.8989 | 26.7893 | 7.6459 | 58.8529 | 1.4934 | 6.0667 | 18.9432 | 72.8608 | 9.7954 | 283.1137 | 99.2769 | 236.2709 | 7.3237 | 71.8249 | 10.9482 | 97 | 14.7503 | 26.3181 | 197.7635 | 0
4560 | 790.5487 | 1.3622 | 47.6848 | 99.9981 | 35.2907 | 8.2263 | 57.3838 | 1.4033 | 6.3367 | 18.1959 | 71.1824 | 10.5192 | 281.449 | 99.2272 | 220.7649 | 7.5427 | 72.0301 | 10.9695 | 96 | 15.1211 | 25.8652 | 195.8507 | 0
4561 | 790.9727 | 1.2621 | 48.2129 | 76.5184 | 45.5 | 9.2304 | 58.5639 | 1.3838 | 6.3173 | 17.7554 | 71.3345 | 10.4724 | 235.2919 | 96.2848 | 211.8658 | 7.5719 | 72.1403 | 10.9794 | 96 | 15.8766 | 33.8668 | 192.1892 | 0
4562 | 775.5583 | 1.2344 | 47.2022 | 108.8032 | 49.9407 | 8.1619 | 54.0401 | 1.392 | 6.1576 | 16.8832 | 71.4208 | 10.3861 | 219.2838 | 94.1203 | 210.5007 | 7.3999 | 72.4719 | 10.9685 | 97 | 15.4674 | 20.2793 | 192.4067 | 0
4563 | 776.0217 | 1.2023 | 46.5419 | 102.3634 | 48.9167 | 7.5592 | 55.697 | 1.3834 | 6.175 | 16.7027 | 70.8561 | 10.0515 | 291.6878 | 92.8657 | 209.7896 | 7.3967 | 72.4804 | 10.9578 | 97 | 14.066 | 24.3442 | 193.4949 | 0
4564 | 780.0475 | 1.1657 | 45.9688 | 97.4516 | 45.5759 | 8.3017 | 52.977 | 1.3765 | 6.4966 | 19.748 | 68.9098 | 8.4428 | 208.7063 | 92.8645 | 202.8084 | 7.2169 | 71.6593 | 10.7853 | 94 | 15.6948 | 33.8391 | 193.2811 | 0
4565 | 776.5161 | 0.91162 | 46.936 | 96.7664 | 42.8956 | 8.531 | 54.0978 | 1.1621 | 6.2503 | 24.2315 | 66.4286 | 7.4792 | 237.1164 | 91.2553 | 198.1289 | 6.8692 | 70.8844 | 10.6885 | 90 | 14.9147 | 20.1793 | 191.1387 | 0.02947
4566 | 793.9385 | 0.74718 | 45.3724 | 97.0842 | 43.573 | 7.8521 | 52.7142 | 0.96077 | 6.0298 | 26.4637 | 65.196 | 7.3153 | 181.1324 | 88.5545 | 203.239 | 6.996 | 70.5398 | 10.6402 | 94 | 14.957 | 32.1286 | 189.8662 | 0.033804
4567 | 805.022 | 0.73529 | 37.9233 | 97.4894 | 44.6879 | 7.5997 | 55.5803 | 0.98217 | 5.6896 | 25.6158 | 70.4875 | 9.5216 | 229.1888 | 87.866 | 205.267 | 6.9441 | 70.3704 | 10.9029 | 96 | 15.801 | 20.2097 | 192.1895 | 0.062219
4568 | 811.9005 | 0.77359 | 35.3317 | 97.5528 | 44.2297 | 8.3898 | 53.7441 | 1.0344 | 7.2668 | 24.2411 | 90.3278 | 15.0973 | 235.1427 | 88.8031 | 219.7362 | 6.9141 | 70.3976 | 11.5094 | 95 | 15.6555 | 24.7357 | 194.0132 | 0.11432
4569 | 812.1359 | 1.5903 | 38.1719 | 97.5831 | 48.8376 | 8.4759 | 55.8584 | 1.0246 | 9.9512 | 25.9692 | 116.1216 | 18.1714 | 229.1163 | 90.443 | 238.8498 | 6.9342 | 70.6943 | 11.7681 | 94 | 14.5328 | 27.9705 | 196.3631 | 0.13013
4570 | 823.7512 | 1.7591 | 39.1938 | 97.3044 | 54.6078 | 7.7935 | 60.0264 | 0.97899 | 7.4719 | 29.6887 | 131.7859 | 17.9433 | 208.7148 | 92.7635 | 240.1144 | 7.033 | 71.0638 | 11.793 | 95 | 15.9767 | 28.493 | 200.1883 | 0.22913
4571 | 854.1234 | 1.3687 | 40.3259 | 83.876 | 61.5369 | 7.6285 | 54.4234 | 1.9474 | 5.8787 | 30.5306 | 138.6071 | 17.7515 | 227.3072 | 97.8925 | 246.2715 | 6.8553 | 70.9385 | 11.9907 | 104 | 15.7657 | 28.1801 | 200.6159 | 0.1549
4572 | 850.2911 | 1.3411 | 41.0657 | 108.7363 | 64.3091 | 9.0064 | 57.3431 | 3.5653 | 6.0302 | 25.962 | 141.8385 | 17.7185 | 205.0816 | 105.0287 | 252.5467 | 6.872 | 71.5027 | 12.0249 | 101 | 13.9721 | 28.4128 | 201.6265 | 0.22271
4573 | 839.3243 | 1.4659 | 41.6275 | 102.614 | 64.1888 | 8.114 | 56.7417 | 3.35 | 5.86 | 20.8734 | 141.8309 | 17.6648 | 214.1753 | 107.0955 | 251.4964 | 7.134 | 74.1988 | 12.0363 | 107 | 13.6011 | 28.5347 | 204.0655 | 0.25311
4574 | 827.8983 | 1.8626 | 40.5441 | 98.2 | 59.0752 | 8.2696 | 55.3202 | 1.8736 | 5.7249 | 19.2958 | 140.6699 | 18.4126 | 211.6806 | 106.3848 | 254.0739 | 7.0692 | 75.835 | 12.0574 | 122 | 15.4238 | 28.2972 | 201.3287 | 0.22702
4575 | 810.0901 | 1.8065 | 36.6479 | 97.9477 | 48.462 | 7.8508 | 57.7435 | 1.1072 | 5.5599 | 18.8736 | 128.2874 | 17.702 | 251.557 | 106.2804 | 247.073 | 6.8164 | 73.8465 | 12.052 | 111 | 13.2322 | 27.6842 | 197.254 | 0.17242
4576 | 804.4498 | 1.4111 | 34.7564 | 98.7776 | 33.7723 | 7.619 | 54.7796 | 1.1272 | 5.8504 | 18.1455 | 105.2434 | 10.5832 | 230.4688 | 105.7803 | 230.9924 | 6.885 | 71.0309 | 12.1074 | 108 | 13.6119 | 32.1079 | 195.4682 | 0.17692
4577 | 802.6113 | 1.2437 | 34.5261 | 86.7424 | 26.0358 | 7.657 | 54.5463 | 1.1103 | 5.7533 | 17.221 | 88.6388 | 7.2276 | 208.5637 | 110.6533 | 225.2933 | 6.9638 | 71.2874 | 12.0834 | 112 | 14.7202 | 19.0327 | 194.9143 | 0.13134
4578 | 794.8747 | 1.3248 | 34.5195 | 80.9003 | 25.2109 | 8.2729 | 58.4437 | 1.0309 | 5.5367 | 16.1956 | 78.6794 | 7.3663 | 240.5439 | 112.0954 | 220.8438 | 6.9294 | 74.0069 | 12.1656 | 105 | 12.8615 | 22.9275 | 195.6461 | 0.097694
4579 | 796.6916 | 1.4901 | 34.4408 | 80.6347 | 28.9994 | 7.8163 | 58.9706 | 0.99563 | 5.74 | 15.586 | 71.6693 | 7.3316 | 370.4067 | 104.7747 | 216.2221 | 7.0711 | 74.5086 | 12.3538 | 102 | 14.4345 | 24.2378 | 193.2988 | 0.10991
4580 | 793.9356 | 1.4293 | 35.7299 | 81.0015 | 35.4234 | 7.637 | 56.9668 | 1.1271 | 5.7304 | 15.444 | 67.9039 | 7.2524 | 189.8742 | 98.1918 | 202.5897 | 7.1255 | 72.1311 | 12.5492 | 95 | 13.8344 | 23.1474 | 189.854 | 0.053553
4581 | 791.5353 | 2.6014 | 42.8577 | 87.7903 | 46.173 | 8.254 | 54.8903 | 1.148 | 5.6979 | 15.3788 | 66.4941 | 7.3357 | 241.8599 | 95.0843 | 197.7319 | 7.0496 | 70.1517 | 12.4137 | 97 | 13.9532 | 22.4696 | 190.029 | 0.0062963
4582 | 786.3678 | 2.786 | 46.4045 | 91.1146 | 51.0376 | 8.6285 | 58.7837 | 1.2625 | 5.6559 | 15.3155 | 67.1185 | 8.1798 | 306.5918 | 95.4307 | 204.15 | 7.1503 | 69.6334 | 12.1559 | 97 | 13.9057 | 21.8006 | 189.9444 | 0
4583 | 775.9324 | 1.8627 | 46.1748 | 93.4102 | 50.4593 | 7.792 | 54.2803 | 1.4074 | 5.9221 | 15.3301 | 68.8963 | 9.552 | 191.7922 | 96.1306 | 207.5219 | 7.2546 | 69.9355 | 12.2352 | 99 | 14.2273 | 22.445 | 189.6857 | 0
4584 | 771.9052 | 1.4043 | 46.4768 | 95.4456 | 49.7883 | 7.6238 | 56.3861 | 1.4305 | 6.2671 | 15.6402 | 70.097 | 10.1241 | 144.9856 | 94.8528 | 209.2839 | 7.5425 | 70.4691 | 12.0305 | 118 | 12.4396 | 23.4818 | 190.0343 | 0
4585 | 765.2874 | 1.3122 | 59.1441 | 95.6687 | 47.8373 | 8.9898 | 55.0735 | 1.4398 | 6.5467 | 15.5416 | 70.2177 | 10.0922 | 187.973 | 93.222 | 214.2118 | 7.8028 | 70.8305 | 11.8874 | 114 | 16.0247 | 22.7738 | 190.7252 | 0
4586 | 762.3496 | 1.2782 | 43.3162 | 77.4959 | 48.765 | 7.4226 | 54.5155 | 1.6628 | 6.7445 | 14.7567 | 70.1133 | 9.9674 | 207.7728 | 92.3045 | 211.552 | 7.5038 | 71.2485 | 12.1585 | 111 | 13.6871 | 22.7939 | 191.7339 | 0
4587 | 757.2582 | 1.3214 | 32.1854 | 108.7958 | 47.7743 | 7.3296 | 54.5215 | 1.5817 | 6.8804 | 14.3917 | 69.8776 | 10.0266 | 172.2128 | 92.6836 | 208.3523 | 7.3115 | 71.2222 | 12.1573 | 98 | 13.2978 | 29.0246 | 191.8673 | 0
4588 | 754.1735 | 1.6411 | 39.8002 | 97.4011 | 45.8073 | 8.3598 | 53.8123 | 1.2102 | 6.9085 | 14.442 | 67.9343 | 8.4279 | 171.9191 | 91.5818 | 202.6629 | 7.1938 | 70.2125 | 11.9233 | 94 | 13.7646 | 17.6016 | 190.6962 | 0
4589 | 764.6246 | 1.7644 | 57.96 | 73.9984 | 45.9711 | 7.8289 | 54.6651 | 1.0362 | 6.32 | 14.4013 | 65.042 | 7.3701 | 191.9647 | 88.8794 | 196.1132 | 6.875 | 69.4085 | 11.2408 | 90 | 12.719 | 21.1819 | 188.8157 | 0.019218
4590 | 774.7295 | 1.1721 | 32.4129 | 101.9651 | 46.9865 | 7.524 | 53.3003 | 0.99873 | 6.0033 | 14.2941 | 64.0207 | 7.2959 | 158.1614 | 87.4216 | 199.2979 | 6.8872 | 69.2174 | 10.8473 | 93 | 13.1784 | 22.3911 | 187.4587 | 0.044409
4591 | 780.3841 | 0.76709 | 54.2165 | 69.1743 | 46.7153 | 8.2989 | 55.2999 | 1.0125 | 5.9167 | 14.2286 | 69.5222 | 7.3923 | 199.0521 | 87.0769 | 200.019 | 7.1259 | 69.0114 | 11.0236 | 96 | 13.1295 | 22.4476 | 188.514 | 0.043689
4592 | 793.5116 | 0.74396 | 32.139 | 92.5655 | 42.7859 | 12.6943 | 53.2676 | 1.2008 | 5.4354 | 15.5927 | 89.1186 | 7.3067 | 164.9599 | 89.7964 | 217.2596 | 7.3866 | 68.7951 | 11.5811 | 98 | 13.3034 | 22.5586 | 189.954 | 0.04448
4593 | 812.1915 | 0.73244 | 33.6305 | 84.3719 | 45.3822 | 11.524 | 57.0123 | 1.2958 | 5.3216 | 16.8455 | 110.7402 | 7.2679 | 166.8534 | 93.8756 | 238.8126 | 6.9981 | 69.084 | 11.8385 | 98 | 18.5526 | 29.3796 | 192.7317 | 0.059588
4594 | 829.9803 | 0.93655 | 34.2643 | 67.3253 | 50.5586 | 9.0462 | 54.1716 | 1.0975 | 5.3137 | 16.784 | 119.0388 | 7.2574 | 206.3894 | 98.4753 | 245.24 | 7.0586 | 69.8535 | 11.9165 | 100 | 9.8655 | 17.4095 | 197.623 | 0.11212
4595 | 841.2028 | 1.3448 | 34.8885 | 86.1097 | 54.6191 | 8.6003 | 58.0006 | 0.96034 | 5.406 | 18.2631 | 124.1187 | 7.4295 | 171.6286 | 101.8563 | 251.0859 | 7.0937 | 69.9282 | 11.9133 | 102 | 11.6514 | 27.7765 | 198.0016 | 0.10016
4596 | 841.4252 | 1.0749 | 35.2131 | 96.9542 | 58.9587 | 8.4825 | 54.5262 | 0.95922 | 5.4496 | 20.0224 | 132.4288 | 7.8085 | 182.62 | 98.2939 | 244.7445 | 6.85 | 69.3468 | 11.8593 | 102 | 15.0144 | 17.4169 | 196.4471 | 0.14767
4597 | 833.2222 | 0.8795 | 35.3767 | 86.5104 | 62.2213 | 8.5679 | 57.4063 | 0.93295 | 5.7843 | 19.8451 | 139.4582 | 7.4453 | 185.9917 | 94.8867 | 231.8491 | 6.984 | 69.371 | 11.8662 | 104 | 12.6386 | 21.17 | 197.0165 | 0.12595
4598 | 839.299 | 0.80827 | 34.9502 | 80.5846 | 63.2592 | 7.8901 | 53.9457 | 0.93737 | 5.7449 | 20.3375 | 144.8725 | 8.4879 | 187.5165 | 95.14 | 225.7655 | 6.8642 | 69.8011 | 12.0433 | 107 | 13.568 | 22.7039 | 195.9455 | 0.070123
4599 | 845.7837 | 0.83637 | 34.2069 | 63.0549 | 58.3524 | 8.3479 | 55.4128 | 0.95138 | 5.2879 | 23.3992 | 136.268 | 10.0866 | 175.9078 | 93.2039 | 221.7698 | 6.8282 | 70.1344 | 12.0822 | 103 | 14.7632 | 29.0824 | 193.8566 | 0.070121
4600 | 822.6577 | 1.0575 | 34.2749 | 94.8383 | 46.3543 | 7.8204 | 58.6809 | 1.1951 | 5.2533 | 24.1594 | 114.1675 | 8.3388 | 175.4924 | 91.6571 | 214.6428 | 6.9949 | 70.0961 | 12.0559 | 114 | 12.3248 | 17.556 | 192.0683 | 0.052443
4601 | 813.6659 | 1.2977 | 34.6994 | 67.7055 | 34.8778 | 7.5425 | 53.5768 | 1.1145 | 5.6267 | 20.5895 | 101.5722 | 7.261 | 194.8631 | 92.6116 | 214.2497 | 7.1164 | 69.428 | 12.0665 | 126 | 13.9344 | 21.0322 | 190.3383 | 0.071656
4602 | 806.9046 | 0.95976 | 35.0328 | 93.9408 | 40.0878 | 7.5659 | 57.8479 | 0.93317 | 5.4467 | 18.0146 | 97.335 | 7.2168 | 173.8455 | 91.1345 | 219.6714 | 6.8301 | 69.2452 | 12.0437 | 117 | 13.1383 | 29.1914 | 190.1268 | 0.048566
4603 | 793.4817 | 0.80861 | 34.2447 | 83.9353 | 42.3188 | 8.3087 | 54.0817 | 0.9358 | 5.1764 | 18.6665 | 89.1808 | 7.2579 | 184.8003 | 87.0093 | 215.9714 | 6.6281 | 69.4919 | 11.9973 | 117 | 13.1793 | 17.4655 | 192.8017 | 0.053491
4604 | 790.4466 | 1.0803 | 35.413 | 79.6507 | 33.4002 | 7.163 | 55.1252 | 0.94347 | 5.1931 | 19.9019 | 81.0247 | 7.3178 | 213.5719 | 85.5956 | 211.665 | 6.9882 | 68.7766 | 11.7376 | 114 | 12.2413 | 21.092 | 194.8932 | 0.02157
4605 | 784.2494 | 2.3724 | 43.2827 | 70.0692 | 27.8522 | 7.4057 | 56.718 | 1.0381 | 5.2105 | 19.5652 | 79.0844 | 7.4447 | 168.8793 | 86.207 | 209.2252 | 6.9402 | 67.7637 | 11.2136 | 101 | 14.5283 | 22.793 | 194.8536 | 0.0016178
4606 | 776.0582 | 2.4612 | 46.9809 | 107.1684 | 28.7772 | 7.5307 | 58.3085 | 1.2623 | 5.3829 | 17.3351 | 80.3744 | 8.8609 | 177.7156 | 86.406 | 210.1689 | 7.4505 | 67.8427 | 11.056 | 97 | 12.6182 | 21.9432 | 194.271 | 0
4607 | 760.1461 | 1.4892 | 47.5617 | 81.9169 | 34.7665 | 7.5999 | 56.171 | 1.5847 | 6.1405 | 14.9858 | 81.0998 | 9.776 | 172.0655 | 86.5892 | 217.5199 | 7.6629 | 68.6012 | 11.0118 | 95 | 12.8227 | 21.8724 | 193.1764 | 0
4608 | 758.1015 | 1.1215 | 46.6405 | 107.0535 | 40.6486 | 9.0573 | 53.0195 | 1.5949 | 6.49 | 14.2183 | 80.5571 | 9.9365 | 176.1621 | 86.9832 | 223.731 | 7.5336 | 69.0159 | 10.9836 | 94 | 13.8995 | 22.1244 | 192.3068 | 0
4609 | 752.8467 | 1.2531 | 46.0016 | 97.5167 | 43.99 | 8.1103 | 56.5335 | 1.4287 | 6.2933 | 14.2477 | 78.8231 | 9.9584 | 163.409 | 87.3491 | 228.0676 | 7.5441 | 69.0061 | 11.0012 | 94 | 12.7288 | 21.6264 | 191.7698 | 0
4610 | 741.2191 | 1.2769 | 46.0846 | 93.3628 | 46.851 | 7.573 | 54.3698 | 1.3663 | 6.0833 | 14.3069 | 76.5756 | 9.8824 | 234.1372 | 86.0886 | 227.9551 | 7.4265 | 68.9251 | 11.0437 | 94 | 14.1376 | 21.2176 | 192.2808 | 0
4611 | 739.1842 | 1.3228 | 45.9892 | 92.86 | 48.6511 | 7.6369 | 58.3433 | 1.3859 | 6.1567 | 15.0373 | 74.3633 | 9.9249 | 197.7311 | 84.4314 | 217.0831 | 7.3597 | 68.9912 | 11.0288 | 92 | 12.7973 | 20.9287 | 193.2666 | 0
4612 | 739.6753 | 1.7962 | 45.8944 | 74.3948 | 49.7055 | 7.5598 | 55.4398 | 1.3496 | 6.1333 | 18.5729 | 71.2598 | 8.8119 | 185.6591 | 83.1713 | 208.4997 | 7.2102 | 68.7406 | 10.8997 | 95 | 13.1999 | 20.8852 | 201.0352 | 0
4613 | 749.8389 | 2.2695 | 46.9839 | 105.447 | 49.6467 | 8.2192 | 53.5711 | 1.1035 | 5.9233 | 23.4359 | 68.0028 | 8.9255 | 175.634 | 82.6249 | 204.1221 | 7.1616 | 68.0394 | 10.7428 | 99 | 13.0572 | 20.7657 | 216.535 | 0.032022
4614 | 792.1513 | 2.4039 | 48.3892 | 83.4157 | 47.7769 | 10.7361 | 65.6245 | 0.9643 | 5.6254 | 29.2909 | 68.4733 | 15.6513 | 199.8819 | 97.4528 | 209.5974 | 7.0338 | 67.7265 | 10.7106 | 111 | 16.0527 | 21.5689 | 251.4877 | 0.026896
4615 | 857.52 | 2.4161 | 60.1975 | 131.3609 | 47.0432 | 12.8088 | 96.4353 | 2.3807 | 5.3091 | 34.8411 | 79.5762 | 25.4568 | 236.2454 | 131.0227 | 221.0616 | 7.7864 | 68.6743 | 10.9553 | 133 | 24.4416 | 29.0392 | 304.8092 | 0.047576
4616 | 897.4366 | 2.3247 | 78.0804 | 150.0696 | 46.4699 | 15.2304 | 124.6007 | 3.3477 | 7.5945 | 32.6227 | 110.8853 | 32.755 | 221.9787 | 164.8995 | 247.0112 | 8.9114 | 74.0949 | 11.5009 | 142 | 33.5751 | 32.3127 | 358.9776 | 0.11417
4617 | 935.6099 | 2.3275 | 86.5578 | 158.337 | 40.0311 | 18.3613 | 132.9263 | 3.4756 | 11.0337 | 24.5774 | 146.9272 | 32.7372 | 261.1952 | 186.5618 | 286.2163 | 9.4439 | 84.5452 | 11.7924 | 147 | 31.2879 | 32.8841 | 409.283 | 0.11876
4618 | 979.1761 | 2.7081 | 88.5006 | 163.11 | 37.0866 | 18.3214 | 131.3765 | 4.0428 | 8.4947 | 17.6257 | 159.6269 | 32.0842 | 261.1454 | 196.8837 | 314.2867 | 9.1949 | 92.7135 | 12.1547 | 147 | 37.9217 | 33.6911 | 427.0039 | 0.22498
4619 | 1000.5463 | 3.0671 | 89.0607 | 165.2283 | 38.2257 | 17.4392 | 131.0144 | 4.2049 | 5.8327 | 14.7459 | 158.2572 | 32.5212 | 319.6968 | 203.8427 | 333.4191 | 9.2404 | 94.8261 | 12.1423 | 143 | 48.8116 | 32.273 | 408.0197 | 0.21885
4620 | 1007.7131 | 2.9376 | 91.1855 | 169.8997 | 41.3952 | 15.6531 | 129.7624 | 3.7304 | 5.7767 | 16.8894 | 162.1103 | 30.4474 | 334.9797 | 209.6431 | 326.9865 | 9.2151 | 94.0805 | 11.9168 | 150 | 43.9205 | 31.2696 | 393.2766 | 0.20035
4621 | 1017.0288 | 2.5234 | 89.2937 | 168.3049 | 41.3067 | 15.8444 | 126.1246 | 3.3037 | 5.55 | 24.5871 | 167.5466 | 30.3671 | 344.36 | 214.2191 | 326.0238 | 9.2267 | 93.5807 | 11.8916 | 144 | 42.5815 | 31.0805 | 400.3472 | 0.23708
4622 | 1039.841 | 2.6444 | 91.156 | 168.1152 | 41.0367 | 14.787 | 122.6285 | 3.2148 | 5.4621 | 31.035 | 169.2897 | 29.9002 | 277.0481 | 218.1637 | 331.2937 | 9.1787 | 93.3535 | 11.9908 | 147 | 56.6249 | 31.4601 | 408.8165 | 0.17615
4623 | 1041.9284 | 2.4796 | 92.7972 | 146.4473 | 41.2066 | 12.7399 | 112.6745 | 3.197 | 5.9469 | 32.0803 | 156.4078 | 28.328 | 300.7868 | 211.4253 | 326.5277 | 9.057 | 91.5637 | 12.0032 | 141 | 55.5024 | 40.5901 | 404.4542 | 0.14365
4624 | 1014.5216 | 2.1895 | 88.0871 | 162.0772 | 42.1611 | 11.0099 | 105.5451 | 2.8618 | 5.5823 | 28.7169 | 130.9513 | 27.2041 | 306.34 | 190.8907 | 309.5081 | 8.6613 | 89.1795 | 11.9905 | 128 | 45.5032 | 24.1885 | 378.4213 | 0.18335
4625 | 968.6729 | 1.8055 | 81.1989 | 139.5118 | 36.1005 | 9.0559 | 102.5982 | 2.0638 | 5.2331 | 21.2659 | 113.1304 | 25.9828 | 296.6634 | 164.6249 | 290.7926 | 7.3649 | 87.0169 | 12.0043 | 128 | 43.0615 | 29.1628 | 328.0207 | 0.09944
4626 | 931.4216 | 1.6865 | 78.1634 | 110.2845 | 30.2246 | 7.8303 | 92.2446 | 1.4533 | 5.3028 | 16.8742 | 103.1761 | 20.8614 | 329.096 | 138.0661 | 276.5585 | 6.994 | 84.037 | 12.0188 | 134 | 42.54 | 31.4159 | 278.5529 | 0.055179
4627 | 911.1031 | 1.8172 | 72.8971 | 135.5609 | 38.1509 | 7.6558 | 69.2286 | 1.2385 | 5.3763 | 15.7941 | 95.5645 | 8.9947 | 299.6054 | 113.6892 | 265.8538 | 7.5447 | 81.0473 | 11.9963 | 118 | 40.6684 | 28.8974 | 240.4346 | 0.040577
4628 | 871.3003 | 1.9347 | 67.0409 | 109.8452 | 45.6946 | 7.6577 | 53.1764 | 1.0217 | 5.4031 | 14.1038 | 89.3307 | 3.9042 | 303.1427 | 97.8665 | 258.8665 | 6.9759 | 78.2735 | 11.6066 | 106 | 39.57 | 25.0871 | 212.525 | 0.017804
4629 | 835.2344 | 2.5178 | 71.4592 | 98.4596 | 47.408 | 7.5605 | 56.7897 | 1.0436 | 5.2767 | 12.4375 | 80.6566 | 3.8384 | 212.5893 | 90.8413 | 245.6103 | 6.9257 | 75.6575 | 10.9353 | 102 | 39.2356 | 23.1017 | 199.9958 | 0.0019454
4630 | 821.3078 | 2.5035 | 75.3838 | 99.4309 | 51.7652 | 7.6919 | 53.817 | 1.2669 | 5.1967 | 12.6451 | 74.0808 | 5.553 | 281.7263 | 90.8422 | 231.116 | 7.1294 | 74.8767 | 10.8926 | 100 | 37.9379 | 22.0208 | 194.1647 | 0
4631 | 816.5494 | 1.5295 | 75.4174 | 100.619 | 55.2736 | 8.9676 | 57.8147 | 1.4716 | 5.599 | 13.9439 | 73.7833 | 6.5349 | 205.1059 | 92.7023 | 221.3954 | 7.4829 | 75.461 | 11.0334 | 97 | 38.1921 | 21.9449 | 190.3283 | 0
4632 | 808.2711 | 1.2468 | 104.7956 | 100.8884 | 57.4704 | 7.2852 | 54.1914 | 1.5748 | 5.841 | 14.3842 | 73.9842 | 6.5327 | 215.3342 | 89.7526 | 215.7014 | 7.5168 | 75.5554 | 11.0424 | 96 | 37.355 | 21.7776 | 189.413 | 0
4633 | 796.9881 | 1.1935 | 58.3787 | 101.5032 | 56.7296 | 7.3457 | 56.8609 | 1.4495 | 6.197 | 14.3266 | 72.9098 | 6.5036 | 179.8957 | 87.021 | 211.7562 | 7.4458 | 75.0832 | 11.033 | 98 | 40.0169 | 21.7434 | 190.9125 | 0
4634 | 790.9769 | 1.1203 | 71.2503 | 80.7441 | 56.7178 | 7.658 | 54.4465 | 1.38 | 6.1066 | 14.2661 | 72.4106 | 6.509 | 191.2613 | 86.9993 | 213.6579 | 7.3811 | 74.7497 | 10.9927 | 95 | 37.0718 | 21.7614 | 195.9852 | 0
4635 | 781.7296 | 1.1225 | 105.7286 | 124.2156 | 54.4182 | 7.5537 | 57.6389 | 1.3924 | 5.77 | 14.7982 | 71.5757 | 6.4122 | 236.8217 | 86.3024 | 211.6078 | 7.3514 | 74.5449 | 11.0276 | 93 | 21.471 | 21.6669 | 199.0422 | 0
4636 | 775.3697 | 1.5522 | 58.4391 | 109.5755 | 50.14 | 7.5602 | 55.7561 | 1.2349 | 5.7824 | 16.6433 | 68.6402 | 5.2758 | 162.7942 | 83.6474 | 208.0835 | 7.298 | 73.963 | 10.9515 | 95 | 15.1204 | 21.8582 | 202.2593 | 0
4637 | 781.8938 | 1.988 | 71.355 | 103.4808 | 47.3435 | 8.2993 | 58.2416 | 1.0358 | 5.3887 | 19.0643 | 65.517 | 6.8071 | 221.2031 | 82.5269 | 205.8816 | 6.9938 | 73.4976 | 10.7688 | 94 | 16.0176 | 21.7862 | 213.2609 | 0.021008
4638 | 804.5138 | 1.7443 | 78.6269 | 105.6002 | 44.9834 | 9.9899 | 62.2106 | 1.1981 | 5.2038 | 23.6593 | 66.5991 | 13.4192 | 202.1052 | 97.2286 | 203.6431 | 7.0309 | 73.2333 | 11.4098 | 111 | 17.9669 | 36.8063 | 240.5244 | 0.047486
4639 | 856.0515 | 2.6384 | 78.03 | 112.7637 | 41.384 | 13.1538 | 85.2375 | 1.7167 | 5.2555 | 28.5507 | 76.9432 | 28.0094 | 277.0131 | 129.7705 | 214.7277 | 8.0627 | 73.648 | 11.708 | 138 | 43.6343 | 30.288 | 286.7469 | 0.076695
4640 | 897.7044 | 3.2088 | 78.3268 | 129.6743 | 40.5581 | 15.0435 | 112.1357 | 2.4871 | 5.2641 | 27.133 | 105.3705 | 35.9079 | 265.1586 | 161.0999 | 246.6332 | 8.9655 | 77.9822 | 11.8362 | 131 | 30.72 | 23.4236 | 335.4333 | 0.10412
4641 | 959.5788 | 2.5653 | 105.9435 | 139.35 | 45.4767 | 15.1995 | 124.5912 | 3.2796 | 5.2348 | 23.2047 | 136.6736 | 35.8687 | 225.4995 | 180.0758 | 287.7547 | 9.0214 | 86.3278 | 11.915 | 140 | 48.379 | 28.2758 | 371.1438 | 0.12623
4642 | 1011.0122 | 2.5541 | 59.0254 | 117.3753 | 53.4986 | 15.2876 | 127.5652 | 3.8321 | 5.3695 | 25.4956 | 148.8676 | 34.2013 | 245.3359 | 189.6631 | 318.9969 | 8.9662 | 93.0631 | 13.1592 | 162 | 27.6784 | 30.5468 | 394.4477 | 0.16206
4643 | 1032.8801 | 2.4779 | 79.7249 | 164.9469 | 58.2705 | 15.2276 | 127.1454 | 4.2977 | 5.1082 | 25.2818 | 153.9224 | 32.1449 | 281.8302 | 197.439 | 341.0148 | 8.8417 | 95.0637 | 13.5891 | 145 | 38.1997 | 32.1242 | 402.0634 | 0.10376
4644 | 1016.4226 | 2.5964 | 88.5699 | 153.4647 | 58.1887 | 16.5183 | 125.8505 | 3.8317 | 4.8326 | 20.3709 | 162.778 | 28.2267 | 311.4826 | 204.3079 | 342.8505 | 8.7673 | 94.1512 | 13.3519 | 153 | 36.5075 | 32.4449 | 397.4086 | 0.14798
4645 | 1011.9676 | 2.6378 | 87.4378 | 144.6524 | 57.5569 | 18.4202 | 122.6803 | 3.6301 | 4.5279 | 22.5753 | 169.6558 | 27.9526 | 277.021 | 210.412 | 341.3073 | 8.9517 | 93.2825 | 14.0827 | 146 | 37.6886 | 32.0231 | 402.0306 | 0.1309
4646 | 1015.0795 | 2.4879 | 82.0498 | 139.561 | 62.8225 | 15.5981 | 120.5155 | 3.0909 | 8.5329 | 31.1454 | 172.4997 | 27.4243 | 290.6864 | 215.1696 | 354.0556 | 8.9327 | 93.7558 | 13.2248 | 148 | 44.1343 | 31.5284 | 406.116 | 0.17465
4647 | 1006.6261 | 2.4457 | 57.1328 | 109.0445 | 60.9225 | 10.7588 | 112.0846 | 2.7161 | 10.357 | 35.8317 | 160.0015 | 24.6891 | 352.2088 | 207.1135 | 342.1405 | 8.6226 | 92.9376 | 12.3963 | 139 | 34.5237 | 32.2136 | 395.3995 | 0.14638
4648 | 991.0945 | 3.0075 | 43.6385 | 59.4392 | 53.106 | 8.7967 | 104.8267 | 2.3779 | 7.2837 | 31.751 | 133.6369 | 21.8588 | 235.158 | 182.9222 | 312.8403 | 7.9735 | 89.5092 | 12.1024 | 124 | 21.8665 | 27.7577 | 362.9448 | 0.19531
4649 | 956.8496 | 4.4505 | 42.1108 | 94.5184 | 51.0447 | 9.2131 | 101.2181 | 1.6261 | 5.0753 | 25.3236 | 114.156 | 20.6617 | 292.3183 | 158.5082 | 287.8617 | 7.3667 | 85.8158 | 11.9493 | 121 | 18.8175 | 25.6373 | 309.3456 | 0.10454
4650 | 915.6336 | 5.2692 | 41.447 | 59.5544 | 51.18 | 8.7626 | 84.8943 | 1.1536 | 4.8849 | 21.1804 | 103.3542 | 16.6769 | 266.3629 | 139.0829 | 267.9302 | 7.0979 | 82.7865 | 12.1493 | 128 | 18.2581 | 33.2293 | 263.332 | 0.13582
4651 | 876.3984 | 4.604 | 38.1579 | 88.3155 | 43.2397 | 7.8988 | 67.8818 | 1.0185 | 4.8356 | 18.1949 | 96.4815 | 7.3956 | 229.0742 | 123.5854 | 252.2482 | 6.8104 | 79.9864 | 12.3389 | 115 | 18.5334 | 25.6972 | 228.8085 | 0.047608
4652 | 849.167 | 4.8725 | 31.4656 | 93.2505 | 31.4409 | 7.6454 | 57.7259 | 1.059 | 4.8805 | 14.6956 | 90.1699 | 3.3969 | 246.3633 | 114.8186 | 246.4686 | 7.0047 | 77.6173 | 12.0693 | 110 | 15.6075 | 19.8861 | 200.7403 | 0.014156
4653 | 820.7103 | 5.2712 | 34.6591 | 98.7342 | 26.494 | 7.5039 | 54.8308 | 1.3361 | 5.0505 | 11.6473 | 81.3918 | 4.0878 | 221.9477 | 110.2188 | 240.7115 | 7.0517 | 76.4332 | 11.2677 | 108 | 12.351 | 31.507 | 187.9853 | 0.0011032
4654 | 798.1553 | 3.4939 | 37.9998 | 100.391 | 25.1166 | 8.2758 | 57.5031 | 1.4382 | 5.292 | 11.5101 | 75.5961 | 5.3458 | 213.2336 | 109.0217 | 233.3914 | 7.3433 | 76.4939 | 11.3491 | 107 | 15.2799 | 19.8222 | 185.9337 | 0
4655 | 786.3111 | 1.6753 | 38.0304 | 101.0543 | 35.3145 | 7.8556 | 57.158 | 1.4431 | 5.3575 | 13.0581 | 75.4097 | 5.7294 | 245.892 | 107.9183 | 223.6899 | 7.3541 | 76.3235 | 11.7542 | 99 | 13.5355 | 23.9203 | 185.2137 | 0
4656 | 777.1385 | 1.2664 | 37.9891 | 100.8295 | 43.6222 | 7.6658 | 57.0356 | 1.4829 | 5.587 | 13.6843 | 75.6974 | 5.7575 | 200.8433 | 104.6473 | 218.1926 | 7.5154 | 75.5217 | 11.8071 | 93 | 13.9562 | 25.8237 | 186.9338 | 0
4657 | 779.8098 | 1.1922 | 38.0621 | 100.678 | 42.03 | 7.6447 | 55.3175 | 1.579 | 5.863 | 13.7692 | 75.0841 | 5.7598 | 179.0689 | 102.0271 | 218.7977 | 7.593 | 75.2469 | 11.7472 | 90 | 12.1121 | 25.6902 | 190.4585 | 0
4658 | 771.0723 | 1.1305 | 38.0728 | 100.3158 | 40.4934 | 8.2266 | 58.2938 | 1.6703 | 6.0914 | 13.8493 | 74.9134 | 5.6715 | 188.3898 | 102.5658 | 217.8419 | 7.4424 | 75.1917 | 11.4703 | 94 | 13.3127 | 33.2284 | 191.0694 | 0
4659 | 769.0582 | 1.1681 | 37.8761 | 100.8883 | 39.976 | 7.8382 | 54.0861 | 1.5558 | 5.756 | 14.5807 | 74.0379 | 5.6918 | 188.1013 | 103.7993 | 214.1496 | 7.4011 | 74.9751 | 11.2712 | 91 | 14.3179 | 25.6972 | 191.5384 | 0
4660 | 768.0241 | 1.6032 | 37.8499 | 99.0787 | 39.3562 | 7.6478 | 57.4293 | 1.3187 | 5.5177 | 16.5961 | 70.4647 | 4.4612 | 190.9029 | 101.6144 | 209.405 | 7.2086 | 74.5629 | 11.0138 | 92 | 12.282 | 25.6972 | 196.5264 | 0
4661 | 776.6747 | 1.1636 | 58.8867 | 99.1893 | 38.1583 | 7.5118 | 54.4676 | 1.132 | 5.1139 | 18.8769 | 66.7679 | 6.7299 | 179.503 | 98.8591 | 203.2808 | 7.4354 | 73.8511 | 10.8104 | 96 | 14.8534 | 19.5457 | 208.2446 | 0.043025
4662 | 814.66 | 1.4638 | 71.7267 | 103.0077 | 35.4087 | 9.6958 | 63.6236 | 1.0576 | 4.8529 | 28.3817 | 72.3536 | 15.3346 | 204.511 | 104.7759 | 208.8584 | 7.3986 | 73.6457 | 12.0543 | 116 | 15.3147 | 23.9435 | 234.2445 | 0.090166
4663 | 862.3123 | 2.3649 | 71.5982 | 99.7996 | 32.9892 | 12.6835 | 83.4601 | 1.8498 | 4.9552 | 37.0561 | 92.0643 | 24.1864 | 192.2301 | 126.8963 | 221.3927 | 7.9753 | 74.5334 | 13.0821 | 133 | 30.9048 | 33.6009 | 277.4546 | 0.10664
4664 | 902.9899 | 2.765 | 77.992 | 96.1184 | 32.1852 | 13.9061 | 102.1958 | 2.5106 | 6.6534 | 36.0513 | 122.6727 | 29.8583 | 249.9618 | 153.9499 | 255.0678 | 8.7076 | 79.7146 | 13.6508 | 131 | 38.3466 | 25.6972 | 325.3208 | 0.13889
4665 | 952.9304 | 2.7526 | 84.9497 | 100.4641 | 31.4633 | 14.2979 | 109.102 | 2.3805 | 9.1183 | 35.2675 | 149.0802 | 32.3915 | 233.8332 | 174.0954 | 300.5238 | 8.8619 | 88.5517 | 14.5224 | 149 | 37.9699 | 19.9075 | 359.2189 | 0.21627
4666 | 981.9508 | 2.7251 | 86.6165 | 104.2239 | 31.1273 | 14.8805 | 114.9676 | 2.6978 | 6.7554 | 35.8146 | 156.4532 | 33.5824 | 285.5139 | 186.2969 | 321.3747 | 9.0225 | 94.6988 | 13.9896 | 151 | 37.7848 | 28.6462 | 371.4569 | 0.24272
4667 | 1014.3334 | 2.9267 | 85.2009 | 121.531 | 32.4159 | 15.276 | 121.6857 | 2.6927 | 5.2257 | 33.5827 | 156.4153 | 32.5723 | 267.0476 | 194.6346 | 334.1483 | 8.8668 | 96.006 | 12.4523 | 140 | 36.5748 | 41.1982 | 379.7788 | 0.21057
4668 | 1013.2622 | 2.3462 | 116.5624 | 129.2419 | 33.9013 | 13.8269 | 125.3495 | 2.6552 | 5.0914 | 32.7002 | 162.2338 | 31.9132 | 220.7975 | 200.478 | 340.5306 | 9.077 | 95.012 | 11.8622 | 152 | 36.0056 | 24.3733 | 391.1863 | 0.19433
4669 | 1001.062 | 2.0241 | 66.1375 | 142.4627 | 28.9491 | 16.2481 | 123.2692 | 2.6458 | 5.2043 | 35.7073 | 168.2738 | 33.1818 | 266.9514 | 204.2233 | 344.0356 | 8.7801 | 95.6279 | 11.9759 | 145 | 36.972 | 38.7384 | 398.805 | 0.2093
4670 | 1008.1005 | 1.9822 | 73.9685 | 183.912 | 30.4345 | 14.7091 | 116.9243 | 2.5485 | 5.1867 | 39.6359 | 170.6839 | 29.3225 | 261.9619 | 206.8101 | 350.9588 | 8.8133 | 97.6508 | 12.0488 | 155 | 36.8248 | 24.1659 | 406.9151 | 0.19303
4671 | 1012.3179 | 2.4933 | 56.1513 | 142.066 | 35.9778 | 10.8492 | 102.4444 | 2.9845 | 5.1712 | 37.5638 | 159.6125 | 25.9647 | 281.9104 | 201.8279 | 349.6621 | 9.0487 | 97.233 | 12.0862 | 133 | 34.815 | 38.9456 | 403.2093 | 0.19132
4672 | 1007.9726 | 2.2797 | 35.9672 | 102.6585 | 38.0581 | 9.4941 | 91.4431 | 3.0719 | 5.2224 | 27.8129 | 132.8768 | 23.1829 | 274.5185 | 178.5118 | 326.9027 | 8.4197 | 94.2994 | 12.1353 | 120 | 23.4643 | 24.41 | 369.335 | 0.13024
4673 | 969.7956 | 1.689 | 31.4861 | 91.9174 | 38.3985 | 8.1205 | 86.8748 | 2.7107 | 5.2261 | 19.7682 | 109.6264 | 21.1772 | 309.4762 | 144.0687 | 305.0111 | 7.3311 | 90.9481 | 12.1018 | 117 | 20.5995 | 27.74 | 314.1271 | 0.14606
4674 | 927.2535 | 1.2661 | 30.5811 | 69.2829 | 38.0763 | 7.6069 | 80.278 | 1.7587 | 5.272 | 15.369 | 96.8205 | 16.8103 | 201.8776 | 116.4462 | 289.4239 | 7.0246 | 87.2438 | 12.0368 | 124 | 19.7469 | 27.9607 | 265.9395 | 0.071343
4675 | 898.1486 | 1.7274 | 28.5293 | 82.1253 | 37.3257 | 8.3068 | 60.9718 | 1.5924 | 5.443 | 13.4653 | 90.9634 | 7.3059 | 243.2235 | 103.2687 | 271.3954 | 6.9666 | 83.127 | 11.9181 | 108 | 21.0025 | 27.5005 | 231.883 | 0.072824
4676 | 861.9914 | 1.7267 | 27.3042 | 91.7464 | 38.5975 | 7.8348 | 56.6226 | 1.3543 | 5.4486 | 13.2727 | 87.5709 | 3.2983 | 215.0555 | 96.2309 | 247.6307 | 7.1182 | 78.8564 | 11.651 | 100 | 14.6309 | 24.0728 | 207.0224 | 0.030777
4677 | 836.4239 | 2.5922 | 33.1314 | 72.2276 | 37.4651 | 7.5769 | 52.131 | 1.0011 | 5.4301 | 13.1305 | 79.5313 | 3.3049 | 220.0182 | 88.302 | 225.8003 | 6.854 | 75.3689 | 11.0547 | 96 | 16.1439 | 37.1866 | 195.2219 | 0.004171
4678 | 821.7685 | 2.6637 | 36.6176 | 101.2027 | 36.2839 | 7.5887 | 54.9422 | 1.2583 | 5.58 | 13.3934 | 70.5093 | 4.2882 | 211.9281 | 83.9474 | 213.2687 | 7.0376 | 73.9813 | 11.0724 | 97 | 14.8006 | 23.5742 | 193.9417 | 0
4679 | 808.028 | 1.851 | 36.6584 | 96.0275 | 33.9235 | 9.0088 | 53.7933 | 1.4037 | 5.9227 | 14.9636 | 68.1611 | 5.5107 | 201.3423 | 83.736 | 214.7835 | 7.4326 | 74.2018 | 11.2041 | 96 | 14.6743 | 28.3699 | 195.5538 | 0
4680 | 804.2609 | 1.4198 | 36.6941 | 91.5342 | 34.3889 | 8.109 | 56.8829 | 1.4017 | 6.1442 | 16.3387 | 68.9095 | 5.878 | 200.969 | 84.0036 | 217.5516 | 7.4577 | 74.5783 | 11.5112 | 94 | 14.489 | 33.7215 | 194.49 | 0
4681 | 807.266 | 1.1961 | 36.9553 | 91.3973 | 34.8533 | 7.5738 | 54.2249 | 1.6484 | 6.4697 | 16.6352 | 69.077 | 5.9003 | 202.832 | 83.4071 | 216.7191 | 7.6289 | 74.5129 | 11.3468 | 96 | 13.5808 | 19.0359 | 194.552 | 0
4682 | 798.9062 | 1.1247 | 36.6957 | 91.6368 | 34.2827 | 7.5226 | 57.1315 | 1.5733 | 6.6601 | 16.6363 | 69.5712 | 5.9442 | 252.3742 | 83.0006 | 219.4304 | 7.61 | 74.5269 | 11.132 | 92 | 14.0269 | 30.234 | 197.0732 | 0
4683 | 799.7659 | 1.1254 | 36.6722 | 107.9925 | 34.0405 | 7.7245 | 55.2194 | 1.4369 | 6.4758 | 17.2909 | 69.5361 | 5.8604 | 171.2801 | 83.1247 | 216.109 | 7.6289 | 74.4787 | 11.1254 | 92 | 14.4359 | 19.1303 | 197.8329 | 0
4684 | 793.8873 | 1.5742 | 36.426 | 114.5824 | 34.0843 | 7.5473 | 55.5907 | 1.2497 | 6.23 | 19.2145 | 66.9212 | 4.8058 | 174.1486 | 81.741 | 206.8285 | 7.0491 | 73.6638 | 11.0066 | 98 | 16.1785 | 22.7916 | 200.5588 | 0
4685 | 806.9659 | 1.4024 | 52.7839 | 113.1788 | 33.5225 | 7.6052 | 53.635 | 1.0588 | 5.7734 | 21.6651 | 63.838 | 6.6283 | 185.4168 | 79.9735 | 204.6225 | 6.827 | 73.1045 | 10.8496 | 97 | 12.5594 | 24.6503 | 212.1463 | 0.042493
4686 | 830.2313 | 1.8063 | 70.1716 | 124.8343 | 30.7632 | 9.8072 | 62.9897 | 1.0058 | 5.4545 | 29.4322 | 69.7781 | 14.1459 | 214.2736 | 92.5293 | 207.8847 | 7.2283 | 72.9692 | 10.7618 | 122 | 17.6032 | 24.8885 | 241.1322 | 0.038183
4687 | 859.5357 | 2.2382 | 72.7049 | 133.9502 | 22.9563 | 13.908 | 78.9922 | 1.4064 | 5.3664 | 41.0681 | 89.9784 | 22.48 | 209.0366 | 124.5905 | 223.0087 | 8.3638 | 73.4097 | 11.0071 | 136 | 28.9345 | 24.5705 | 283.039 | 0.089213
4688 | 907.476 | 2.7796 | 77.4133 | 124.4423 | 23.8778 | 15.8319 | 101.815 | 2.337 | 7.111 | 46.0782 | 120.423 | 27.1863 | 254.5446 | 156.1794 | 251.0109 | 8.8143 | 77.6008 | 11.6138 | 154 | 31.3418 | 31.7811 | 342.6882 | 0.09742
4689 | 978.5666 | 2.7275 | 84.5017 | 168.8758 | 28.0531 | 14.6932 | 108.8795 | 3.8159 | 10.8489 | 46.1529 | 144.2168 | 29.5578 | 233.062 | 175.158 | 287.0454 | 8.8878 | 85.1685 | 11.8706 | 165 | 34.0181 | 18.9992 | 406.5158 | 0.12268
4690 | 1024.6882 | 2.4148 | 84.4897 | 169.5151 | 30.2959 | 15.005 | 111.7417 | 3.6683 | 8.6529 | 46.3782 | 147.9717 | 28.3519 | 239.719 | 187.1389 | 317.7238 | 9.4091 | 90.7206 | 11.8426 | 152 | 33.9315 | 22.963 | 422.3716 | 0.19329
4691 | 1037.9047 | 2.8462 | 84.749 | 165.4435 | 35.0182 | 14.5113 | 120.0815 | 3.1208 | 7.4332 | 45.6074 | 147.53 | 26.8583 | 280.5335 | 194.5795 | 330.1147 | 9.3156 | 92.6852 | 11.9171 | 138 | 35.374 | 24.6115 | 405.2315 | 0.20902
4692 | 1037.7155 | 2.9093 | 85.7829 | 164.2494 | 38.306 | 15.0649 | 125.8288 | 3.4588 | 7.85 | 41.4949 | 154.8953 | 22.1692 | 248.137 | 198.1473 | 332.4963 | 9.2915 | 92.6996 | 11.8989 | 140 | 34.0578 | 24.8788 | 394.9154 | 0.19745
4693 | 1042.7392 | 2.5584 | 87.0584 | 164.505 | 44.6679 | 15.3376 | 122.1291 | 3.5865 | 7.4137 | 38.3169 | 162.3033 | 17.0533 | 244.3889 | 201.7742 | 327.6405 | 8.8602 | 92.6475 | 11.9836 | 140 | 33.7801 | 24.738 | 390.518 | 0.23704
4694 | 1053.9893 | 2.7394 | 85.5666 | 165.5696 | 52.0367 | 14.3642 | 113.6111 | 3.3976 | 7.1899 | 40.5028 | 168.2561 | 15.3712 | 222.3113 | 205.66 | 324.802 | 8.832 | 93.4706 | 11.998 | 144 | 36.0156 | 24.5332 | 388.4933 | 0.22782
4695 | 1034.4336 | 2.7828 | 57.5498 | 130.7785 | 61.9898 | 11.9769 | 104.5075 | 3.613 | 6.5112 | 38.3696 | 160.456 | 14.0507 | 232.3993 | 199.1936 | 318.1645 | 9.2054 | 93.0708 | 11.9791 | 132 | 36.3602 | 29.9779 | 383.2389 | 0.21579
4696 | 1013.5444 | 2.2518 | 37.0435 | 74.4104 | 70.1644 | 9.3232 | 96.9727 | 3.526 | 5.7443 | 29.2371 | 136.4208 | 12.9299 | 189.8104 | 177.6313 | 298.8551 | 8.458 | 90.8037 | 12.0212 | 118 | 22.2725 | 31.5845 | 356.7001 | 0.19646
4697 | 981.0101 | 2.2686 | 32.8939 | 81.4474 | 66.824 | 9.2811 | 93.411 | 2.6166 | 5.2138 | 22.5398 | 117.4956 | 12.024 | 155.8183 | 149.0576 | 282.1867 | 7.6095 | 87.0872 | 12.0359 | 121 | 18.7554 | 30.4529 | 306.5192 | 0.17329
4698 | 946.4869 | 2.2849 | 31.5209 | 91.1239 | 58.3227 | 8.8863 | 82.2916 | 1.6799 | 5.336 | 21.2337 | 108.0124 | 9.8274 | 184.8194 | 120.5525 | 279.0619 | 7.0022 | 82.8943 | 12.3429 | 123 | 20.2119 | 28.9739 | 258.681 | 0.19561
4699 | 912.4935 | 1.6075 | 28.5522 | 78.1368 | 51.0562 | 8.5413 | 64.6329 | 1.285 | 5.3654 | 23.1182 | 101.6918 | 5.6918 | 202.0954 | 102.1732 | 272.9757 | 7.1177 | 79.6978 | 12.858 | 107 | 20.5883 | 29.3079 | 223.4587 | 0.12256
4700 | 878.5148 | 1.2056 | 27.3355 | 69.7541 | 38.8285 | 7.8829 | 51.4128 | 1.1352 | 5.2743 | 23.9727 | 95.7463 | 4.0606 | 200.8388 | 95.7965 | 248.2728 | 7.5491 | 76.8629 | 12.7825 | 95 | 20.0525 | 26.7198 | 197.9823 | 0.054564
4701 | 849.6627 | 2.1469 | 27.3355 | 69.1886 | 40.7433 | 6.781 | 54.313 | 1.0495 | 5.603 | 22.7401 | 87.0338 | 4.0763 | 185.3652 | 91.3974 | 225.4858 | 7.2711 | 74.3471 | 12.3484 | 97 | 17.7836 | 23.5911 | 187.9301 | 0.0048989
4702 | 828.1369 | 2.6094 | 32.2848 | 57.1576 | 46.1072 | 7.3113 | 53.33 | 1.2731 | 5.7452 | 21.6715 | 77.5155 | 5.0034 | 186.1933 | 88.2065 | 219.7086 | 7.4659 | 73.391 | 12.4555 | 97 | 19.2809 | 22.8623 | 188.4159 | 0
4703 | 822.444 | 1.8187 | 35.4032 | 95.1703 | 44.4597 | 7.6367 | 54.7655 | 1.4524 | 5.9931 | 21.9488 | 73.3272 | 6.2606 | 194.1386 | 88.3536 | 221.7829 | 7.759 | 73.9864 | 12.4499 | 93 | 19.8072 | 29.9649 | 186.7837 | 0
4704 | 819.4181 | 1.271 | 35.5443 | 99.0101 | 47.1468 | 7.5484 | 51.7904 | 1.6617 | 6.3532 | 23.2572 | 73.4376 | 6.6151 | 245.1369 | 87.3055 | 234.3805 | 7.7962 | 74.7859 | 11.9863 | 97 | 17.3063 | 17.5428 | 184.8115 | 0
4705 | 811.3562 | 1.162 | 35.6505 | 101.9569 | 49.5288 | 7.6538 | 55.5348 | 1.6271 | 6.4422 | 24.108 | 73.5545 | 6.6225 | 158.2357 | 86.327 | 243.909 | 7.7212 | 75.0281 | 11.538 | 93 | 17.4048 | 21.5772 | 186.1839 | 0
4706 | 813.6441 | 1.3051 | 35.23 | 101.3736 | 49.1337 | 7.6641 | 54.6126 | 1.4534 | 6.3254 | 24.0318 | 72.5531 | 6.5655 | 147.3321 | 85.7088 | 232.8641 | 7.755 | 74.922 | 11.1868 | 92 | 18.4674 | 29.7488 | 186.1561 | 0
4707 | 814.1734 | 1.5423 | 35.0832 | 100.6153 | 46.9085 | 8.3139 | 53.7549 | 1.438 | 6.223 | 24.3953 | 71.4341 | 6.645 | 176.5401 | 83.9139 | 215.7694 | 7.7917 | 74.7147 | 11.1045 | 93 | 17.4537 | 22.9567 | 184.1049 | 0
4708 | 806.2969 | 1.8781 | 34.6412 | 98.6928 | 46.2129 | 7.7392 | 51.7535 | 1.2363 | 6.1667 | 26.0774 | 68.9807 | 5.1352 | 186.751 | 81.5911 | 204.0014 | 7.3816 | 74.0878 | 10.9436 | 96 | 19.5793 | 17.6326 | 190.1908 | 0
4709 | 812.8991 | 1.4299 | 41.1829 | 98.1338 | 45.7963 | 7.6582 | 55.7102 | 1.0568 | 5.6566 | 28.2643 | 66.049 | 5.7194 | 198.2792 | 80.2599 | 200.9151 | 7.1669 | 73.333 | 10.8026 | 99 | 18.4753 | 21.1915 | 204.4502 | 0.094332
4710 | 851.654 | 1.5962 | 49.5566 | 100.4943 | 44.8397 | 9.6924 | 61.9929 | 1.1703 | 5.3968 | 33.4287 | 72.0611 | 12.6975 | 181.9989 | 94.9234 | 203.7985 | 7.8193 | 73.9068 | 10.7753 | 117 | 18.5716 | 24.038 | 231.6018 | 0.10894
4711 | 905.8807 | 1.8375 | 65.1757 | 101.4554 | 44.7835 | 13.288 | 88.8476 | 1.7918 | 6.8982 | 40.4355 | 90.2086 | 22.5563 | 195.6766 | 125.4791 | 217.4582 | 8.2933 | 75.281 | 11.0358 | 131 | 27.783 | 30.4188 | 276.7312 | 0.16728
4712 | 942.0769 | 2.4001 | 72.6163 | 115.2031 | 47.3298 | 18.529 | 116.7069 | 2.2702 | 10.3679 | 41.4744 | 114.8472 | 27.1755 | 220.5882 | 154.2535 | 245.9172 | 8.4107 | 78.4083 | 11.6407 | 135 | 34.239 | 32.4128 | 322.523 | 0.23659
4713 | 975.9572 | 2.5826 | 78.2986 | 120.3172 | 59.2593 | 16.4858 | 124.941 | 2.2049 | 12.168 | 36.2719 | 138.7729 | 26.4691 | 221.991 | 175.3148 | 282.0581 | 8.9665 | 84.6157 | 11.8212 | 137 | 35.772 | 32.43 | 351.5482 | 0.23458
4714 | 997.8983 | 2.4284 | 83.8924 | 122.6705 | 62.9565 | 16.5402 | 125.2309 | 2.0481 | 9.2471 | 31.2547 | 153.0962 | 25.063 | 246.4191 | 189.0771 | 306.5404 | 9.0287 | 89.9445 | 11.8663 | 146 | 35.9057 | 33.0998 | 382.8439 | 0.24026
4715 | 1020.6263 | 2.335 | 83.0776 | 127.3112 | 58.913 | 14.9423 | 125.2261 | 2.3925 | 8.0788 | 29.2568 | 158.6856 | 24.2568 | 227.8803 | 196.632 | 316.9719 | 9.1394 | 92.3289 | 12.0068 | 140 | 38.3968 | 33.8828 | 410.205 | 0.20433
4716 | 1028.6881 | 2.7016 | 82.6903 | 127.9205 | 51.2047 | 13.5898 | 125.1088 | 2.6182 | 8.3439 | 33.5266 | 162.7258 | 24.8795 | 251.1294 | 200.8081 | 315.3718 | 9.464 | 93.414 | 12.0576 | 137 | 33.9293 | 33.8517 | 421.0315 | 0.20585
4717 | 1008.6403 | 2.5569 | 86.2032 | 127.775 | 48.4832 | 13.9174 | 123.7647 | 2.3837 | 7.3318 | 38.028 | 166.7969 | 24.8034 | 255.8795 | 203.9592 | 310.304 | 8.6782 | 95.1385 | 12.0495 | 144 | 33.8361 | 33.7516 | 413.355 | 0.27395
4718 | 1008.5372 | 2.661 | 78.667 | 131.4647 | 52.9748 | 13.4861 | 118.589 | 2.2572 | 6.5277 | 35.3839 | 169.7189 | 25.5633 | 229.491 | 206.6987 | 321.561 | 8.4303 | 96.0418 | 12.0431 | 141 | 36.4165 | 33.9932 | 386.0859 | 0.26817
4719 | 999.5317 | 3.3891 | 54.7065 | 126.6204 | 56.2691 | 12.0047 | 106.3785 | 2.1916 | 6.1202 | 30.1376 | 156.3514 | 23.2863 | 243.8243 | 198.8802 | 317.8924 | 8.6517 | 92.5955 | 12.0633 | 139 | 29.008 | 33.116 | 365.1001 | 0.26594
4720 | 963.8502 | 3.2385 | 36.5141 | 110.7014 | 56.8911 | 8.5562 | 97.0604 | 1.8196 | 5.5899 | 24.6052 | 128.4565 | 21.1622 | 262.1808 | 170.6392 | 300.2429 | 7.7868 | 86.7113 | 12.0803 | 119 | 23.5995 | 32.0257 | 331.7203 | 0.24262
4721 | 924.9468 | 2.2845 | 30.7692 | 103.7397 | 54.6439 | 7.6067 | 94.5771 | 1.32 | 5.4066 | 21.5061 | 110.2506 | 20.8478 | 223.1629 | 137.6986 | 278.0909 | 6.9115 | 81.7838 | 12.0707 | 118 | 16.8414 | 31.8181 | 283.5114 | 0.25518
4722 | 890.2525 | 2.1164 | 27.7004 | 100.7207 | 53.5343 | 7.6603 | 83.659 | 1.036 | 5.2667 | 21.8386 | 100.9619 | 16.8923 | 257.7172 | 113.4732 | 263.0468 | 6.9228 | 77.2112 | 12.2046 | 123 | 18.0414 | 30.187 | 243.7759 | 0.18568
4723 | 857.8774 | 1.5025 | 25.9211 | 98.585 | 53.1829 | 7.5829 | 66.7629 | 0.96298 | 4.9956 | 23.9439 | 90.3243 | 7.3491 | 207.8434 | 97.7751 | 253.1114 | 6.8569 | 72.7357 | 12.2398 | 113 | 14.4219 | 29.401 | 217.9392 | 0.12897
4724 | 833.0726 | 1.2425 | 27.5903 | 98.2263 | 52.3042 | 7.6099 | 54.4141 | 1.1667 | 5.4029 | 24.9617 | 80.328 | 3.3371 | 223.3782 | 93.2342 | 244.0199 | 7.095 | 70.4211 | 12.1181 | 110 | 16.27 | 33.6868 | 205.276 | 0.034127
4725 | 814.8552 | 2.4666 | 34.3422 | 97.5888 | 45.5257 | 8.2929 | 51.7688 | 1.2811 | 5.4249 | 24.6803 | 75.8788 | 3.6562 | 196.27 | 92.27 | 238.2165 | 6.9926 | 70.1542 | 11.7048 | 104 | 17.4974 | 25.2227 | 198.1435 | 0.00063021
4726 | 804.541 | 2.7862 | 37.7272 | 100.8364 | 31.5561 | 9.8957 | 55.258 | 1.3006 | 5.4733 | 26.1915 | 74.0339 | 5.2321 | 215.7231 | 89.3165 | 229.4788 | 7.2032 | 71.3232 | 12.0063 | 101 | 15.1534 | 19.3772 | 192.4727 | 0
4727 | 795.624 | 1.968 | 37.8429 | 105.6792 | 34.468 | 7.6363 | 52.8703 | 1.3565 | 5.9714 | 28.0666 | 71.8603 | 6.1252 | 190.7642 | 88.6447 | 216.5727 | 8.7444 | 72.8493 | 12.0925 | 98 | 18.1356 | 31.0667 | 190.2714 | 0
4728 | 783.5723 | 1.5753 | 38.095 | 107.7014 | 44.8859 | 6.6524 | 46.2808 | 1.3772 | 6.0685 | 27.7345 | 70.5361 | 6.1932 | 238.384 | 93.9959 | 215.9701 | 10.8624 | 72.8798 | 11.9376 | 96 | 15.3987 | 25.2227 | 189.1286 | 0
4729 | 780.2803 | 1.3475 | 37.724 | 109.3153 | 46.3891 | 7.4233 | 41.8699 | 1.3578 | 5.8605 | 25.8239 | 70.3099 | 6.0798 | 157.8571 | 100.6724 | 219.1884 | 11.9414 | 72.2095 | 11.7297 | 92 | 16.251 | 19.637 | 188.1687 | 0
4730 | 767.5061 | 1.2073 | 37.5654 | 108.8665 | 45.7571 | 7.5423 | 44.7105 | 1.3831 | 6.0023 | 24.4056 | 70.7802 | 6.1177 | 226.7458 | 97.2893 | 220.5679 | 11.8699 | 71.8227 | 11.4021 | 92 | 17.3008 | 23.3037 | 189.6911 | 0
4731 | 765.8791 | 1.3244 | 38.5532 | 107.9669 | 45.7059 | 7.7074 | 42.155 | 1.6329 | 5.8177 | 24.2535 | 71.1422 | 6.1539 | 173.3198 | 88.1523 | 213.1191 | 11.5708 | 71.6792 | 11.3595 | 94 | 14.8603 | 32.7259 | 190.1589 | 0
4732 | 767.0857 | 1.8389 | 39.3003 | 106.1759 | 46.98 | 8.9098 | 43.2617 | 1.3755 | 5.9094 | 25.5328 | 69.0738 | 4.6551 | 211.562 | 82.3025 | 202.9692 | 10.0414 | 71.2603 | 11.2072 | 92 | 16.3296 | 19.3855 | 189.6917 | 0
4733 | 766.4798 | 1.703 | 39.4405 | 103.6798 | 52.1482 | 7.404 | 44.1985 | 1.0446 | 5.6791 | 27.5555 | 65.7522 | 3.5354 | 159.8246 | 79.5586 | 198.4643 | 7.7612 | 70.578 | 10.9449 | 90 | 15.6659 | 23.7178 | 189.7169 | 0.016302
4734 | 780.2424 | 1.0633 | 37.8478 | 98.0427 | 52.995 | 7.4003 | 41.1541 | 0.96017 | 5.3174 | 29.1318 | 69.6774 | 3.349 | 157.522 | 79.3099 | 196.2983 | 7.1488 | 70.1881 | 10.8376 | 92 | 17.7952 | 25.2422 | 189.4772 | 0.031662
4735 | 791.7691 | 0.83662 | 31.1149 | 96.8723 | 54.0412 | 6.8218 | 43.333 | 1.0043 | 5.3565 | 28.5201 | 83.4691 | 5.5119 | 197.6707 | 80.8535 | 201.0459 | 7.1359 | 70.046 | 11.1189 | 96 | 19.6443 | 24.9869 | 192.0109 | 0.080341
4736 | 802.1108 | 1.3141 | 28.64 | 97.6955 | 54.8321 | 8.0521 | 40.6097 | 1.0618 | 5.5275 | 25.4357 | 101.7914 | 11.3106 | 184.411 | 82.2098 | 216.6326 | 7.0342 | 70.0818 | 11.7179 | 95 | 19.3136 | 25.1954 | 195.2577 | 0.091501
4737 | 808.636 | 1.2648 | 30.4904 | 97.6807 | 56.6853 | 8.5945 | 43.2602 | 1.052 | 6.8475 | 22.228 | 118.1477 | 16.104 | 184.9952 | 83.5889 | 236.2639 | 7.124 | 70.4271 | 11.9459 | 96 | 20.0578 | 25.4113 | 198.797 | 0.11637
4738 | 824.3589 | 0.91598 | 31.2598 | 97.1963 | 57.1256 | 7.7848 | 39.546 | 1.2771 | 5.9141 | 20.1281 | 129.4175 | 18.0016 | 174.7882 | 86.1708 | 244.6028 | 7.0079 | 70.6855 | 11.9036 | 107 | 19.7298 | 24.978 | 201.0458 | 0.070213
4739 | 844.1803 | 0.98063 | 31.5863 | 97.3722 | 54.4423 | 8.3234 | 41.3422 | 1.9775 | 4.8945 | 21.3481 | 136.52 | 15.9819 | 190.5587 | 90.6924 | 245.419 | 7.3379 | 71.1823 | 11.8981 | 110 | 19.8088 | 28.3382 | 200.1793 | 0.080695
4740 | 831.0349 | 1.3214 | 32.0664 | 98.1599 | 55.4234 | 8.5377 | 42.3569 | 3.2493 | 4.8004 | 22.6633 | 139.4306 | 15.1706 | 227.3367 | 96.5932 | 242.1488 | 6.6001 | 72.4192 | 11.8894 | 107 | 16.315 | 30.0746 | 201.2241 | 0.11718
4741 | 813.7315 | 1.1951 | 32.2318 | 97.8756 | 56.3932 | 8.5345 | 41.5149 | 3.0799 | 4.9135 | 20.8878 | 140.1482 | 17.2389 | 151.2104 | 98.5568 | 231.3389 | 6.6491 | 72.8546 | 11.8852 | 111 | 17.0716 | 29.4958 | 205.6613 | 0.11089
4742 | 796.8603 | 0.9018 | 31.25 | 98.7171 | 58.937 | 7.212 | 41.6055 | 1.8415 | 4.993 | 19.3569 | 141.6255 | 17.9661 | 173.9051 | 97.2253 | 234.6933 | 7.2811 | 72.3165 | 11.8818 | 110 | 17.8376 | 27.8698 | 208.1955 | 0.12951
4743 | 797.855 | 0.8136 | 28.6523 | 96.8186 | 60.7503 | 7.3538 | 39.9305 | 1.1312 | 5.1235 | 16.9267 | 129.4498 | 14.6453 | 236.0398 | 94.7479 | 233.5717 | 7.1487 | 71.7742 | 11.8611 | 123 | 18.794 | 27.4126 | 205.406 | 0.1342
4744 | 806.7042 | 0.9344 | 27.8189 | 96.8698 | 62.6364 | 7.6305 | 42.9303 | 0.93443 | 5.2875 | 14.4319 | 103.9588 | 6.9278 | 170.9475 | 92.9741 | 230.9857 | 6.8533 | 70.8989 | 11.8496 | 126 | 16.3657 | 31.4744 | 197.5077 | 0.11178
4745 | 798.1915 | 0.98083 | 27.7663 | 97.0248 | 61.6041 | 7.5755 | 41.3663 | 0.93305 | 5.3195 | 14.0879 | 88.7817 | 3.7009 | 167.5992 | 92.1283 | 238.6895 | 6.8297 | 69.9799 | 11.8426 | 116 | 18.0803 | 23.265 | 191.03 | 0.073952
4746 | 796.5586 | 1.0988 | 27.7859 | 98.1039 | 54.1665 | 7.5682 | 41.6449 | 1.1402 | 5.3433 | 14.3236 | 82.1022 | 3.4652 | 222.4117 | 89.6927 | 242.5448 | 7.0481 | 69.4538 | 11.8392 | 102 | 16.1659 | 17.9575 | 190.0179 | 0.086526
4747 | 796.6648 | 1.1654 | 27.6548 | 91.7653 | 49.3267 | 6.911 | 44.8333 | 1.0827 | 5.1615 | 14.4448 | 75.8631 | 3.3315 | 145.5701 | 88.696 | 229.3547 | 7.0471 | 69.6788 | 11.8983 | 98 | 14.7922 | 28.5712 | 187.9385 | 0.057005
4748 | 800.4613 | 1.6539 | 32.0631 | 76.0261 | 42.4804 | 7.3859 | 39.5191 | 0.98667 | 5.0749 | 13.7241 | 72.1385 | 3.3664 | 159.0484 | 88.9649 | 215.7208 | 6.8833 | 69.7376 | 11.789 | 96 | 16.354 | 17.9884 | 185.7755 | 0.014235
4749 | 792.8017 | 3.1928 | 34.4701 | 96.088 | 37.1686 | 7.6098 | 42.9515 | 1.0239 | 5.0585 | 12.3368 | 69.7262 | 3.5512 | 188.3667 | 88.3313 | 217.2014 | 6.9027 | 68.9168 | 11.3519 | 99 | 17.9463 | 21.841 | 188.3425 | 0.00059877
4750 | 777.4925 | 3.1708 | 37.8517 | 109.9152 | 37.3903 | 8.319 | 42.1434 | 1.271 | 5.208 | 12.7316 | 68.509 | 5.0256 | 170.6795 | 87.5502 | 216.8307 | 7.2817 | 69.1021 | 11.2578 | 100 | 15.0244 | 23.3755 | 191.2109 | 0
4751 | 758.9539 | 1.9652 | 39.3917 | 105.7367 | 41.0857 | 7.8301 | 43.5691 | 1.4116 | 5.3905 | 14.9291 | 69.6272 | 6.1687 | 175.3627 | 91.7949 | 218.7938 | 7.9595 | 70.3968 | 11.5751 | 99 | 16.949 | 23.2287 | 190.3935 | 0
4752 | 753.2383 | 1.4537 | 39.5833 | 104.0619 | 45.7322 | 7.5111 | 46.4744 | 1.6408 | 5.9035 | 16.3317 | 71.0097 | 6.1655 | 203.464 | 116.5061 | 220.6524 | 7.1655 | 70.9792 | 11.5614 | 100 | 17.7305 | 23.0495 | 188.5466 | 0
4753 | 753.2514 | 1.2926 | 39.5851 | 103.0278 | 51.7596 | 8.3292 | 40.9196 | 1.6011 | 6.1377 | 16.3948 | 71.4094 | 6.1504 | 157.3218 | 143.3208 | 220.0427 | 6.999 | 71.0202 | 11.5388 | 98 | 16.0673 | 30.1057 | 188.4608 | 0
4754 | 741.3882 | 1.2601 | 39.5109 | 104.4794 | 55.4941 | 7.8109 | 43.489 | 1.4229 | 6.1574 | 16.0573 | 71.7226 | 6.3831 | 214.3389 | 149.7389 | 210.8099 | 7.6017 | 71.1639 | 11.7072 | 96 | 15.2888 | 17.8048 | 189.7665 | 0
4755 | 738.9529 | 1.3259 | 38.7697 | 101.84 | 56.7142 | 6.95 | 41.9075 | 1.4401 | 6.222 | 15.544 | 71.8497 | 6.2078 | 153.2923 | 148.7173 | 206.4442 | 7.781 | 71.0458 | 11.5031 | 94 | 16.9878 | 21.9286 | 189.6301 | 0
4756 | 735.9302 | 1.6898 | 37.3682 | 85.0515 | 56.6999 | 8.0944 | 43.0104 | 1.3416 | 6.3805 | 13.7902 | 69.9975 | 5.1641 | 149.521 | 147.0856 | 200.0373 | 7.359 | 70.4694 | 11.0227 | 91 | 16.2796 | 23.3358 | 188.1493 | 0
4757 | 742.3523 | 1.2784 | 37.7035 | 106.623 | 56.3893 | 7.1364 | 41.6046 | 1.1228 | 6.1517 | 11.5995 | 66.9872 | 3.863 | 180.4027 | 139.2267 | 195.5464 | 6.9943 | 69.7687 | 10.7899 | 89 | 14.6856 | 23.3804 | 187.9805 | 0.040097
4758 | 752.8347 | 0.85917 | 36.6622 | 100.6247 | 55.4439 | 7.335 | 41.7446 | 1.0282 | 6.0538 | 10.8212 | 71.3712 | 3.5339 | 159.0132 | 114.8599 | 196.4704 | 6.7929 | 69.365 | 10.7567 | 93 | 15.3591 | 23.0077 | 187.2306 | 0.10919
4759 | 768.4504 | 0.77338 | 30.3793 | 97.1719 | 56.3196 | 7.5753 | 44.7058 | 1.2796 | 5.226 | 10.7183 | 84.8 | 3.8334 | 177.5131 | 91.2612 | 197.6466 | 6.6611 | 69.0698 | 11.0249 | 93 | 16.1006 | 23.2838 | 185.9661 | 0.18481
4760 | 772.3276 | 0.78676 | 27.4022 | 97.797 | 56.3146 | 8.3446 | 40.2451 | 1.268 | 6.6478 | 13.4812 | 101.6849 | 4.7121 | 166.2612 | 86.3075 | 216.118 | 6.6515 | 68.8498 | 11.6289 | 96 | 15.7972 | 30.1126 | 187.1215 | 0.20471
4761 | 774.5432 | 0.92889 | 27.1387 | 98.0814 | 56.8351 | 8.5986 | 42.4816 | 1.1002 | 9.4424 | 19.5596 | 115.261 | 7.0639 | 199.331 | 88.8426 | 232.7089 | 7.0695 | 68.951 | 11.8469 | 95 | 14.9852 | 18.0894 | 187.222 | 0.19449
4762 | 801.2524 | 1.2764 | 27.3018 | 103.3808 | 56.9441 | 7.8117 | 41.8552 | 1.0448 | 6.9367 | 25.1051 | 120.0568 | 7.4812 | 189.9926 | 91.2108 | 243.1995 | 6.9495 | 69.4509 | 11.8555 | 102 | 16.0329 | 21.642 | 190.0491 | 0.20718
4763 | 801.8852 | 1.3032 | 28.1665 | 102.5865 | 57.5826 | 7.6137 | 40.2255 | 1.0155 | 5.4876 | 29.6227 | 124.2966 | 5.092 | 125.493 | 92.4952 | 252.208 | 6.6913 | 70.0452 | 11.8784 | 103 | 16.991 | 23.3629 | 195.0582 | 0.21418
4764 | 798.9161 | 1.3473 | 28.5526 | 100.3913 | 58.6888 | 8.3359 | 43.9641 | 0.99989 | 5.8007 | 26.8152 | 133.5567 | 3.6052 | 142.0368 | 91.6903 | 245.0889 | 6.9157 | 71.0005 | 12.006 | 103 | 15.9987 | 23.3653 | 195.015 | 0.18788
4765 | 806.3946 | 1.1128 | 28.2289 | 99.0052 | 58.5104 | 7.7602 | 41.9443 | 1.0102 | 5.5945 | 18.3262 | 140.7806 | 4.7838 | 257.2648 | 90.2321 | 235.2277 | 7.1392 | 71.9701 | 12.0486 | 107 | 13.543 | 23.1282 | 190.9471 | 0.21598
4766 | 803.5045 | 0.97259 | 28.1276 | 97.5555 | 58.5697 | 8.3327 | 42.9647 | 1.2347 | 5.196 | 14.9511 | 143.215 | 7.0806 | 131.5877 | 88.5486 | 239.3258 | 6.7285 | 71.913 | 12.0012 | 103 | 17.1227 | 21.4187 | 188.8595 | 0.22909
4767 | 794.0197 | 1.1335 | 26.4661 | 97.3355 | 62.1499 | 7.8734 | 46.3928 | 1.1566 | 5.1415 | 15.6955 | 130.9361 | 7.0361 | 172.698 | 86.5563 | 239.9927 | 6.9024 | 71.2473 | 12.1333 | 103 | 14.6461 | 20.681 | 191.6731 | 0.25638
4768 | 795.7464 | 1.1494 | 25.763 | 97.3356 | 62.0497 | 7.5683 | 41.7072 | 0.97808 | 5.1577 | 15.9093 | 105.2742 | 4.5808 | 191.3145 | 88.3561 | 232.7084 | 6.982 | 70.7496 | 12.1757 | 107 | 15.681 | 20.8232 | 191.9887 | 0.20854
4769 | 799.3274 | 1.5301 | 25.9804 | 97.4783 | 56.4505 | 8.2871 | 41.1613 | 0.94758 | 5.3677 | 14.2301 | 89.8794 | 3.4594 | 188.3917 | 91.9608 | 228.0128 | 7.0718 | 70.4747 | 12.1585 | 103 | 15.959 | 20.8066 | 191.0648 | 0.18896
4770 | 775.1157 | 1.5991 | 26.0521 | 97.5261 | 42.4857 | 9.2587 | 44.9052 | 0.98447 | 5.161 | 11.957 | 86.0742 | 3.4025 | 208.7568 | 91.9856 | 230.2226 | 6.8112 | 70.4099 | 12.1883 | 101 | 17.3276 | 20.7777 | 193.4874 | 0.12449
4771 | 761.577 | 1.0957 | 26.8695 | 96.9036 | 36.4741 | 7.3959 | 41.0756 | 0.99257 | 5.0225 | 10.5799 | 80.0962 | 3.3584 | 141.2999 | 88.3675 | 232.2713 | 6.8604 | 70.6845 | 12.2259 | 97 | 14.7245 | 20.8827 | 193.7387 | 0.13894
4772 | 757.1829 | 1.3578 | 28.7118 | 96.7377 | 41.1284 | 7.2715 | 43.2217 | 1.0097 | 5.1418 | 10.2572 | 71.7261 | 3.3635 | 156.7279 | 84.3366 | 227.9235 | 6.788 | 71.0165 | 11.9646 | 92 | 16.8548 | 32.412 | 193.1455 | 0.048917
4773 | 762.2303 | 2.621 | 35.4424 | 96.6072 | 39.6712 | 6.9824 | 46.9725 | 1.1926 | 5.3258 | 10.2943 | 66.9441 | 3.3196 | 164.3133 | 82.1184 | 224.2857 | 6.7368 | 71.067 | 11.3193 | 92 | 14.4064 | 20.4871 | 194.512 | 0
4774 | 756.6413 | 2.6073 | 38.9175 | 98.9589 | 42.123 | 7.2763 | 40.5749 | 1.5385 | 5.4685 | 11.7537 | 66.9559 | 5.0951 | 204.7895 | 82.2371 | 222.2102 | 7.2791 | 71.2836 | 11.0159 | 91 | 14.0269 | 32.0042 | 194.7625 | 0
4775 | 738.8363 | 1.7713 | 39.3711 | 100.689 | 49.352 | 7.5824 | 42.4559 | 1.5682 | 5.7734 | 14.2603 | 69.4788 | 6.0573 | 157.2846 | 83.8548 | 222.7533 | 7.7926 | 71.8748 | 11.0733 | 95 | 15.3293 | 20.1164 | 195.0789 | 0
4776 | 727.5246 | 1.2578 | 39.6251 | 100.0391 | 55.0368 | 7.6236 | 45.4796 | 1.4429 | 6.0289 | 15.4144 | 70.6942 | 5.9287 | 115.1926 | 84.7919 | 218.3862 | 8.0944 | 72.1542 | 11.097 | 97 | 14.9223 | 24.4286 | 194.4444 | 0
4777 | 722.3223 | 1.0992 | 39.3477 | 99.7265 | 58.748 | 7.5743 | 43.2862 | 1.4583 | 5.9706 | 15.5446 | 70.3572 | 5.9904 | 149.1134 | 84.3323 | 208.1429 | 7.3098 | 72.1215 | 11.079 | 91 | 14.6521 | 14.076 | 191.2248 | 0
4778 | 719.2477 | 1.1051 | 39.2094 | 100.0744 | 59.2118 | 7.6758 | 44.4034 | 1.4599 | 6.1275 | 15.6094 | 70.2437 | 6.3571 | 156.9782 | 83.4973 | 207.0597 | 6.9418 | 72.1061 | 11.0876 | 94 | 13.8739 | 8.7804 | 189.2778 | 0
4779 | 719.2387 | 1.1127 | 39.1614 | 100.8711 | 58.8362 | 7.62 | 42.3171 | 1.4627 | 6.1404 | 16.4077 | 70.1893 | 6.1437 | 156.6752 | 83.4846 | 204.6199 | 7.4647 | 72.0506 | 11.1113 | 94 | 16.8693 | 8.7804 | 191.2132 | 0
4780 | 717.1491 | 1.5453 | 39.0231 | 98.5285 | 59.1146 | 7.5899 | 44.1268 | 1.2884 | 5.8566 | 18.408 | 68.2385 | 4.6915 | 163.2221 | 81.9516 | 197.6359 | 7.3424 | 71.6384 | 10.9606 | 95 | 13.5795 | 21.1451 | 201.4867 | 0
4781 | 718.1744 | 1.2296 | 44.5544 | 96.7521 | 58.6921 | 8.2757 | 42.2104 | 1.3381 | 5.4346 | 20.5102 | 65.6435 | 5.9903 | 166.6427 | 79.744 | 198.7489 | 7.0087 | 71.1311 | 10.7976 | 100 | 14.2749 | 26.1181 | 216.7123 | 0.038321
4782 | 755.1676 | 0.97644 | 55.0033 | 99.8482 | 54.9335 | 11.4381 | 50.2937 | 1.2161 | 5.0543 | 24.4304 | 72.7444 | 11.868 | 168.2254 | 92.4781 | 202.6921 | 6.9893 | 71.1318 | 10.7404 | 127 | 15.7986 | 23.4299 | 241.6988 | 0.074046
4783 | 810.5415 | 1.8674 | 62.1235 | 108.3703 | 53.1949 | 14.444 | 68.267 | 1.4032 | 6.2728 | 31.5044 | 92.5482 | 20.816 | 186.8626 | 121.2721 | 215.1022 | 7.1228 | 71.9174 | 11.01 | 144 | 33.6467 | 30.3849 | 287.1416 | 0.10589
4784 | 867.7353 | 2.2298 | 74.4864 | 117.2905 | 52.5401 | 17.1796 | 90.6532 | 2.07 | 10.2221 | 35.6444 | 119.8454 | 26.1314 | 215.8944 | 149.7241 | 242.7986 | 7.4787 | 75.8832 | 11.5924 | 169 | 39.1049 | 44.358 | 332.2467 | 0.14077
4785 | 918.8965 | 2.2153 | 80.8448 | 121.6914 | 55.3237 | 16.7796 | 98.474 | 2.5925 | 11.9926 | 34.4557 | 143.421 | 26.6287 | 236.04 | 169.1793 | 273.8273 | 8.1208 | 83.444 | 11.794 | 152 | 42.5646 | 27.0537 | 353.3528 | 0.15411
4786 | 950.3081 | 2.3219 | 81.4696 | 122.0396 | 59.338 | 15.4907 | 105.4962 | 2.5623 | 9.5651 | 33.792 | 150.4022 | 25.4066 | 249.8176 | 180.635 | 297.2398 | 9.4058 | 89.8394 | 11.7996 | 147 | 42.6688 | 32.5177 | 360.2133 | 0.19398
4787 | 964.0874 | 2.4872 | 85.7943 | 125.9963 | 56.443 | 14.4079 | 102.8421 | 2.6898 | 7.8456 | 32.043 | 152.9621 | 23.9529 | 259.0569 | 189.0402 | 306.7011 | 9.6002 | 92.3944 | 11.9467 | 142 | 39.7727 | 34.6077 | 369.6242 | 0.21933
4788 | 968.2423 | 2.5113 | 84.5179 | 126.6361 | 47.4343 | 14.2357 | 101.421 | 2.8348 | 8.0812 | 28.4014 | 159.4679 | 23.0351 | 276.5449 | 194.99 | 300.5501 | 9.1722 | 92.158 | 12.1923 | 144 | 39.2849 | 34.5855 | 374.9275 | 0.19921
4789 | 968.4528 | 2.8095 | 83.1886 | 128.2709 | 42.6647 | 15.4762 | 92.4885 | 2.5848 | 8.1242 | 30.4864 | 162.5034 | 23.1311 | 287.9538 | 198.509 | 292.7053 | 9.6096 | 90.9052 | 12.2342 | 141 | 43.5408 | 42.9798 | 371.4792 | 0.25632
4790 | 995.0972 | 2.6526 | 84.6346 | 135.4646 | 45.0384 | 14.1916 | 88.6885 | 2.5384 | 7.5167 | 35.6136 | 163.2547 | 23.2155 | 287.6139 | 203.5737 | 293.8624 | 9.8696 | 91.379 | 12.1697 | 150 | 46.8755 | 32.69 | 369.7428 | 0.24747
4791 | 988.8867 | 2.6935 | 80.954 | 124.8292 | 44.5289 | 14.6697 | 83.1795 | 2.5526 | 6.7898 | 34.2034 | 148.7014 | 22.7492 | 288.3421 | 198.1771 | 300.4392 | 9.5201 | 91.8309 | 12.1713 | 129 | 43.1908 | 25.1946 | 364.2814 | 0.24264
4792 | 951.9653 | 2.3181 | 71.247 | 113.6523 | 44.085 | 14.6666 | 73.1118 | 2.6066 | 5.7655 | 27.5144 | 121.5203 | 21.8077 | 278.8434 | 172.2975 | 283.1319 | 8.8972 | 89.0881 | 12.1967 | 119 | 30.5473 | 40.1836 | 338.785 | 0.2293
4793 | 905.0376 | 2.0007 | 66.7061 | 109.2199 | 46.3178 | 12.0337 | 72.3173 | 1.8308 | 5.1348 | 21.9786 | 106.9167 | 21.199 | 254.3417 | 141.9065 | 261.9067 | 7.7416 | 85.327 | 12.0907 | 123 | 20.5538 | 25.2432 | 294.5295 | 0.1991
4794 | 863.7922 | 1.4154 | 65.6952 | 104.3918 | 41.4597 | 8.6566 | 71.8733 | 1.1419 | 5.0745 | 19.3955 | 102.2956 | 17.2884 | 229.2734 | 117.0311 | 254.017 | 7.5722 | 82.8857 | 12.0511 | 129 | 17.0833 | 27.4905 | 255.6213 | 0.13755
4795 | 847.1546 | 0.90068 | 63.123 | 101.9722 | 40.7364 | 8.2413 | 51.4412 | 1.0544 | 5.2108 | 17.8103 | 97.3843 | 7.4139 | 209.08 | 99.5429 | 255.5271 | 7.8355 | 82.7416 | 12.108 | 114 | 14.7313 | 28.384 | 229.6312 | 0.086602
4796 | 821.4577 | 1.1972 | 61.1157 | 100.0482 | 42.2052 | 7.8025 | 44.7857 | 1.2214 | 5.2893 | 16.1858 | 90.4126 | 3.3813 | 195.2673 | 90.7916 | 249.4531 | 7.9077 | 83.2704 | 11.9108 | 114 | 16.4825 | 25.5638 | 207.5212 | 0.02822
4797 | 801.6202 | 2.6824 | 65.9831 | 99.0415 | 34.2352 | 7.6181 | 44.0802 | 1.2059 | 5.4 | 15.4948 | 79.3604 | 3.3929 | 182.2859 | 86.5133 | 241.7237 | 7.6847 | 80.6823 | 11.2708 | 110 | 16.5248 | 23.5583 | 195.7528 | 0
4798 | 789.6345 | 2.8236 | 70.4748 | 99.412 | 37.6702 | 7.6712 | 45.1556 | 1.32 | 5.7708 | 15.8616 | 70.3503 | 4.9713 | 179.0856 | 86.4381 | 240.5313 | 7.9309 | 76.9506 | 11.0266 | 106 | 18.2927 | 23.1194 | 194.5292 | 0
4799 | 764.6685 | 5.9373 | 71.4503 | 101.7352 | 46.0012 | 7.5903 | 43.9419 | 1.4767 | 6.0486 | 15.8594 | 69.1559 | 6.2993 | 157.7197 | 87.0278 | 238.6181 | 9.38 | 76.0144 | 11.0932 | 104 | 15.7398 | 22.9234 | 191.7592 | 0
4800 | 756.3357 | 4.3095 | 72.2234 | 101.6545 | 49.5834 | 7.6158 | 43.963 | 1.4878 | 6.044 | 15.2096 | 69.9418 | 6.1088 | 152.9428 | 84.8118 | 226.2562 | 11.612 | 76.4181 | 11.1621 | 98 | 15.5386 | 22.8303 | 187.7982 | 0
4801 | 751.5722 | 1.5812 | 72.5684 | 101.3253 | 30.7007 | 7.6186 | 48.0149 | 1.6183 | 6.0233 | 15.3773 | 69.4426 | 6.0451 | 159.7269 | 83.3089 | 218.7797 | 12.5746 | 76.7565 | 11.1699 | 98 | 17.5856 | 23.006 | 189.8999 | 0
4802 | 742.4788 | 1.3126 | 72.0374 | 101.1509 | 1.6549 | 8.2411 | 43.5289 | 1.6861 | 6.2167 | 15.8539 | 69.0691 | 6.0302 | 162.7073 | 83.3273 | 230.5352 | 11.3833 | 76.7986 | 11.1492 | 95 | 17.7377 | 22.9901 | 194.7657 | 0
4803 | 750.7624 | 1.3113 | 71.814 | 96.4019 | -8.0058 | 8.597 | 45.7737 | 1.5685 | 6.2214 | 16.6758 | 68.6601 | 5.945 | 168.0285 | 83.7925 | 238.0904 | 9.138 | 76.3686 | 11.1571 | 93 | 15.3706 | 39.8477 | 196.6502 | 0
4804 | 750.2753 | 1.5936 | 70.8892 | 91.0682 | -7.8933 | 8.4891 | 41.3385 | 1.2852 | 6.0289 | 18.5814 | 66.4935 | 4.1867 | 171.6063 | 82.4236 | 225.2029 | 7.8472 | 75.6495 | 11.0514 | 100 | 15.8512 | 25.4729 | 201.7883 | 0
4805 | 750.0412 | 1.115 | 71.5982 | 65.6475 | -9.4249 | 9.9409 | 44.192 | 1.1041 | 5.4297 | 20.763 | 63.671 | 4.6253 | 172.8291 | 80.8845 | 208.5198 | 7.6495 | 74.7101 | 10.8796 | 100 | 15.2514 | 30.8239 | 217.6559 | 0.054801
4806 | 786.3026 | 1.4479 | 72.2193 | 95.1056 | -11.4878 | 11.8961 | 48.3903 | 1.0843 | 5.4967 | 24.9639 | 73.4658 | 10.7874 | 177.9667 | 93.0039 | 201.8197 | 7.793 | 74.2249 | 10.8041 | 122 | 21.63 | 42.7272 | 246.9854 | 0.1232
4807 | 851.158 | 2.127 | 72.3632 | 167.7345 | 16.7643 | 12.9985 | 68.4034 | 1.7283 | 6.7133 | 25.5659 | 100.8728 | 19.7538 | 187.4428 | 124.3544 | 219.2987 | 8.4166 | 77.4716 | 11.323 | 140 | 31.356 | 33.0086 | 292.0655 | 0.18805
4808 | 879.6213 | 2.2688 | 72.4688 | 61.3038 | 39.6074 | 13.2119 | 80.2588 | 2.1642 | 11.3084 | 20.6312 | 123.8139 | 22.9334 | 219.2105 | 149.7679 | 249.2922 | 8.6725 | 82.8696 | 11.6099 | 150 | 38.0106 | 25.1547 | 327.1766 | 0.17807
4809 | 916.1226 | 2.5474 | 77.3377 | 121.2813 | 48.2835 | 15.3833 | 96.0539 | 2.2487 | 13.3426 | 19.0368 | 131.2387 | 23.0884 | 222.7467 | 163.2688 | 270.6043 | 9.3953 | 86.4992 | 11.7851 | 164 | 38.4955 | 40.8605 | 341.1421 | 0.27268
4810 | 970.6989 | 2.5652 | 82.2401 | 133.4098 | 65.0778 | 13.3811 | 101.2684 | 2.2496 | 14.9306 | 19.5134 | 133.9163 | 23.2129 | 241.7467 | 177.0812 | 292.3658 | 9.67 | 90.573 | 11.9207 | 154 | 37.5243 | 33.0086 | 348.8841 | 0.29969
4811 | 988.4598 | 2.5268 | 87.9969 | 132.5793 | 69.3361 | 13.0536 | 107.5504 | 2.5914 | 16.2743 | 19.17 | 140.1743 | 23.0448 | 252.898 | 187.9716 | 308.0429 | 10.1214 | 95.968 | 12.01 | 147 | 35.4834 | 25.4565 | 354.3651 | 0.25006
4812 | 980.4912 | 2.6175 | 88.7908 | 109.3858 | 60.7759 | 14.7275 | 105.157 | 3.1899 | 16.6909 | 20.9089 | 151.9499 | 22.8918 | 257.5596 | 194.5286 | 305.3476 | 10.7318 | 96.9348 | 12.0849 | 144 | 43.2663 | 40.5589 | 360.2252 | 0.25336
4813 | 981.6642 | 2.9499 | 88.0957 | 161.0563 | 54.4911 | 15.1141 | 106.047 | 3.2673 | 16.285 | 29.232 | 162.9166 | 22.7125 | 252.1667 | 201.3485 | 304.3916 | 10.393 | 93.3677 | 12.0792 | 151 | 46.2824 | 33.0086 | 365.7713 | 0.28951
4814 | 971.4431 | 2.5459 | 72.7541 | 143.4734 | 54.0333 | 14.5322 | 99.9087 | 2.8335 | 15.2195 | 37.5969 | 168.2445 | 23.6569 | 260.9486 | 207.2373 | 316.3905 | 9.8281 | 91.7068 | 12.0678 | 141 | 48.7226 | 25.4292 | 366.6229 | 0.28291
4815 | 945.5122 | 2.5436 | 63.8185 | 121.7011 | 52.0883 | 14.8097 | 88.1313 | 1.8524 | 14.5254 | 35.503 | 154.7893 | 23.2938 | 272.7981 | 194.5436 | 310.9066 | 9.5636 | 89.6239 | 12.0739 | 125 | 42.3778 | 40.5861 | 358.533 | 0.26109
4816 | 935.5346 | 2.8055 | 62.4369 | 116.279 | 51.4615 | 14.4814 | 85.2402 | 1.3476 | 10.4914 | 29.7149 | 129.0518 | 22.693 | 266.4135 | 173.7039 | 291.04 | 9.5057 | 86.2387 | 12.076 | 119 | 38.0523 | 19.3064 | 346.9994 | 0.20921
4817 | 921.1283 | 1.7696 | 33.705 | 105.4185 | 55.1596 | 10.8946 | 82.3106 | 1.2878 | 8.406 | 25.6089 | 117.24 | 20.8318 | 260.7101 | 152.6442 | 269.4306 | 9.3249 | 84.8615 | 12.0601 | 123 | 22.9529 | 22.9934 | 309.3223 | 0.21679
4818 | 864.3378 | 1.1012 | 32.2191 | 100.3344 | 57.591 | 8.1707 | 73.4028 | 0.92377 | 5.7153 | 22.752 | 110.2177 | 17.8179 | 224.9519 | 134.4011 | 254.1468 | 8.2006 | 83.8654 | 12.1362 | 119 | 16.438 | 31.9867 | 260.1318 | 0.077982
4819 | 853.1077 | 1.0564 | 31.0263 | 100.0736 | 57.7113 | 6.2253 | 55.5914 | 0.91739 | 5.2458 | 22.0051 | 102.1066 | 9.1509 | 205.0806 | 126.6294 | 241.7014 | 8.2283 | 82.1892 | 12.137 | 103 | 18.6026 | 31.3698 | 229.3851 | 0.051211
4820 | 825.1612 | 1.7047 | 29.3784 | 98.1281 | 56.3623 | 5.7013 | 47.7953 | 1.1157 | 5.2531 | 20.3715 | 98.4245 | 4.0916 | 199.4721 | 121.008 | 232.7914 | 8.6028 | 79.7218 | 11.8735 | 101 | 16.7016 | 28.8482 | 207.1773 | 0.037923
4821 | 810.4715 | 2.7146 | 35.4586 | 98.212 | 55.1648 | 6.4249 | 43.2227 | 1.1928 | 5.1924 | 16.9021 | 91.7734 | 3.6571 | 189.9494 | 116.3397 | 224.748 | 8.3906 | 76.5772 | 11.3124 | 95 | 18.8486 | 26.9875 | 197.8483 | 0
4822 | 788.4526 | 2.6575 | 39.2882 | 100.2734 | 53.9199 | 7.2863 | 45.581 | 1.2652 | 5.3155 | 15.192 | 83.6938 | 5.529 | 171.6704 | 114.8709 | 223.6067 | 8.765 | 75.4312 | 11.2044 | 95 | 20.1689 | 26.1383 | 195.8557 | 0
4823 | 770.9356 | 1.5895 | 39.2496 | 101.3033 | 54.0789 | 6.8826 | 49.2103 | 1.3491 | 5.6053 | 15.9378 | 80.6687 | 6.1698 | 163.151 | 114.0026 | 221.1773 | 9.6804 | 75.8046 | 11.2808 | 94 | 19.5448 | 25.6796 | 194.2984 | 0
4824 | 766.8176 | 1.1837 | 39.3582 | 101.6247 | 49.9439 | 7.4621 | 43.0406 | 1.36 | 5.6986 | 16.1895 | 79.2597 | 5.9259 | 163.9538 | 111.0498 | 215.7509 | 11.8814 | 75.3258 | 11.2123 | 93 | 18.4335 | 25.6717 | 191.9893 | 0
4825 | 764.8566 | 1.2797 | 39.4398 | 105.8259 | 36.3146 | 7.5585 | 44.7322 | 1.5636 | 5.7214 | 15.6711 | 75.4376 | 6.1337 | 177.3832 | 106.0188 | 211.4605 | 13.2501 | 74.6077 | 11.1275 | 94 | 16.793 | 25.5939 | 191.7695 | 0
4826 | 767.5489 | 1.2111 | 39.4587 | 107.6817 | 27.4197 | 6.9379 | 44.3912 | 1.5208 | 5.8086 | 15.5774 | 71.9848 | 6.067 | 178.4006 | 102.6923 | 207.7354 | 13.1517 | 74.2956 | 11.0893 | 91 | 17.8661 | 25.55 | 193.1456 | 0
4827 | 765.9726 | 1.1999 | 39.2922 | 106.1513 | 27.7002 | 7.3831 | 45.6661 | 1.3621 | 6.107 | 16.7567 | 70.7489 | 5.9629 | 177.3493 | 103.0367 | 208.0512 | 12.68 | 74.1138 | 11.0962 | 91 | 18.1552 | 25.4531 | 193.9776 | 0
4828 | 759.4368 | 1.553 | 39.0944 | 102.9805 | 36.3272 | 6.9249 | 48.8764 | 1.2927 | 5.9995 | 19.1096 | 69.3195 | 5.5069 | 184.7717 | 103.4566 | 202.1544 | 10.1948 | 73.7827 | 11.0424 | 91 | 15.7182 | 25.5747 | 198.8274 | 0
4829 | 768.5936 | 2.4594 | 49.459 | 107.7065 | 34.0863 | 7.3229 | 42.1768 | 1.056 | 5.71 | 21.4416 | 66.7375 | 6.6093 | 174.9822 | 102.0037 | 201.2359 | 8.5624 | 73.1122 | 10.8796 | 90 | 17.9913 | 26.4514 | 212.2999 | 0.0090245
4830 | 806.755 | 1.8605 | 54.7775 | 99.4302 | 35.98 | 10.4008 | 48.4392 | 0.97272 | 5.3849 | 23.3439 | 75.1265 | 12.0544 | 174.8487 | 107.7909 | 206.5264 | 8.3129 | 72.6835 | 10.7881 | 117 | 17.4283 | 26.7762 | 236.7389 | 0.020232
4831 | 855.2913 | 1.5432 | 61.701 | 97.6677 | 42.3942 | 14.128 | 69.5826 | 1.5312 | 6.9647 | 24.0438 | 102.042 | 20.1814 | 194.2569 | 128.8733 | 208.7074 | 8.6585 | 73.3668 | 11.0446 | 146 | 26.285 | 32.1624 | 272.0065 | 0.063491
4832 | 909.6859 | 1.5713 | 73.3378 | 115.6658 | 42.5044 | 15.3056 | 85.3087 | 1.9365 | 8.3189 | 23.2008 | 130.5537 | 25.2146 | 203.1803 | 153.7361 | 238.0969 | 9.9398 | 76.7653 | 11.634 | 141 | 33.2791 | 34.7178 | 314.0893 | 0.080482
4833 | 949.943 | 1.4253 | 82.7315 | 127.9569 | 43.4596 | 15.2003 | 96.3437 | 1.9661 | 8.0712 | 22.476 | 142.5528 | 25.4162 | 220.1347 | 173.9497 | 276.7695 | 11.6983 | 82.3348 | 11.8571 | 142 | 29.2984 | 34.4131 | 352.2332 | 0.099377
4834 | 964.8929 | 1.3835 | 86.5616 | 125.6793 | 45.6721 | 14.1389 | 99.3867 | 1.9795 | 7.7081 | 24.3975 | 141.854 | 24.4149 | 241.425 | 187.0775 | 295.7655 | 12.4105 | 87.0121 | 11.8628 | 163 | 36.809 | 34.5255 | 371.4323 | 0.11073
4835 | 977.3069 | 1.5738 | 87.7996 | 121.7196 | 45.026 | 14.3447 | 100.7258 | 2.1749 | 7.9796 | 28.5793 | 143.3302 | 24.0302 | 255.3634 | 192.8107 | 304.5329 | 12.161 | 89.7554 | 11.8719 | 153 | 37.2244 | 34.6943 | 371.4073 | 0.094327
4836 | 991.8295 | 1.3449 | 88.7875 | 123.6739 | 45.4645 | 14.4725 | 109.5217 | 2.6103 | 8.2446 | 31.4071 | 151.8188 | 23.4142 | 265.7552 | 194.9483 | 298.4711 | 12.0828 | 90.4488 | 11.9005 | 153 | 32.9838 | 34.5891 | 371.5452 | 0.15504
4837 | 1005.2586 | 1.4024 | 87.8215 | 123.8921 | 47.4562 | 13.516 | 102.6601 | 2.3435 | 9.1415 | 36.0666 | 159.6819 | 23.5768 | 261.9016 | 199.1171 | 296.9853 | 12.2319 | 90.9649 | 12.0617 | 156 | 36.6549 | 34.0729 | 375.1787 | 0.19182
4838 | 1016.9102 | 1.7509 | 75.0857 | 134.6849 | 51.0926 | 13.3176 | 103.7561 | 2.0506 | 8.6807 | 40.7698 | 164.0436 | 24.6149 | 264.6144 | 204.6728 | 308.7279 | 10.771 | 92.1129 | 12.0758 | 141 | 40.9539 | 34.0506 | 371.892 | 0.24059
4839 | 1006.174 | 2.5912 | 69.4924 | 118.1552 | 59.0439 | 14.0831 | 98.9593 | 2.3168 | 7.0815 | 38.091 | 154.1502 | 23.8685 | 268.546 | 200.5789 | 311.2151 | 10.2462 | 91.1397 | 12.0954 | 121 | 41.4165 | 33.7029 | 364.3249 | 0.28573
4840 | 969.0012 | 2.8451 | 54.1776 | 108.8277 | 64.3221 | 10.7549 | 89.4749 | 2.1284 | 5.9417 | 31.4172 | 131.8632 | 22.1953 | 252.767 | 181.934 | 298.0128 | 9.5537 | 87.8506 | 12.1801 | 116 | 28.8992 | 32.4118 | 346.9732 | 0.24519
4841 | 925.8324 | 2.3992 | 46.6699 | 109.4194 | 62.173 | 8.0743 | 93.3988 | 1.3759 | 5.4373 | 26.0779 | 117.0646 | 21.6135 | 239.8885 | 153.2515 | 272.1992 | 9.0263 | 84.9567 | 12.2374 | 116 | 23.6661 | 31.5964 | 310.5796 | 0.26152
4842 | 887.9767 | 1.6161 | 46.2485 | 104.8339 | 58.9345 | 8.2776 | 82.0089 | 1.2079 | 5.27 | 22.821 | 107.5307 | 18.9194 | 231.0363 | 123.8954 | 240.5485 | 8.3189 | 83.0759 | 12.2495 | 114 | 20.5639 | 31.677 | 268.7776 | 0.2419
4843 | 856.834 | 1.097 | 43.6356 | 103.5835 | 59.4378 | 7.8538 | 58.8788 | 1.1506 | 5.1936 | 21.4705 | 99.1983 | 9.5237 | 226.2756 | 106.7991 | 229.9821 | 8.567 | 81.1647 | 12.2489 | 98 | 19.7004 | 31.0501 | 232.5334 | 0.17397
4844 | 837.864 | 1.2137 | 42.4813 | 98.3312 | 60.6901 | 7.574 | 49.4773 | 1.2112 | 5.3075 | 21.2106 | 94.7422 | 5.7614 | 222.0348 | 100.2675 | 234.1882 | 8.4849 | 78.3858 | 12.0088 | 102 | 17.5477 | 28.7121 | 206.2874 | 0.071469
4845 | 814.1425 | 2.7775 | 47.8189 | 96.9435 | 59.7618 | 6.8558 | 49.016 | 1.1756 | 5.3633 | 19.8856 | 88.8094 | 5.8285 | 203.6805 | 95.9681 | 225.0689 | 8.1575 | 75.7652 | 11.3744 | 99 | 18.3834 | 25.9765 | 195.9741 | 0
4846 | 804.927 | 2.7966 | 51.954 | 98.6644 | 55.9351 | 8.7946 | 44.9946 | 1.2777 | 5.6199 | 18.4913 | 82.2057 | 7.1926 | 184.1129 | 94.1691 | 213.719 | 9.1278 | 75.1569 | 11.2693 | 97 | 20.8768 | 25.0773 | 192.7942 | 0
4847 | 793.1289 | 1.6017 | 51.8814 | 99.8454 | 55.291 | 8.713 | 47.9866 | 1.3958 | 6.1122 | 18.9502 | 81.1808 | 8.3154 | 168.8519 | 94.2012 | 208.233 | 10.1502 | 75.6109 | 11.292 | 97 | 23.9715 | 25.1863 | 193.1752 | 0
4848 | 782.3746 | 1.1995 | 50.8279 | 99.3923 | 54.6795 | 7.9076 | 51.7206 | 1.3975 | 6.2507 | 18.5356 | 81.5636 | 8.5107 | 163.9001 | 94.2262 | 204.6576 | 11.7936 | 75.6715 | 11.1924 | 97 | 23.0124 | 25.6838 | 195.4096 | 0
4849 | 778.4825 | 1.2796 | 50.5086 | 99.617 | 48.7647 | 7.6287 | 51.3851 | 1.6088 | 6.2934 | 16.5791 | 80.6694 | 8.5909 | 173.046 | 92.633 | 204.8982 | 12.7227 | 75.4285 | 11.0892 | 100 | 21.2204 | 25.9842 | 194.7476 | 0
4850 | 776.5559 | 1.2459 | 50.2997 | 99.3303 | 37.9072 | 7.6278 | 46.2532 | 1.5326 | 6.4349 | 15.5503 | 79.5099 | 10.4743 | 179.8415 | 90.3422 | 207.3425 | 13.0985 | 75.5937 | 11.04 | 96 | 20.8286 | 25.8411 | 193.5405 | 0
4851 | 774.686 | 1.1138 | 50.4051 | 100.0788 | 42.0866 | 9.0303 | 48.983 | 1.414 | 6.3214 | 16.4329 | 76.9708 | 16.343 | 178.567 | 88.7487 | 210.0485 | 13.2728 | 75.545 | 11.0254 | 96 | 20.6595 | 25.5085 | 193.2334 | 0
4852 | 767.9034 | 1.4833 | 50.2125 | 97.2843 | 51.174 | 8.0386 | 49.5887 | 1.1966 | 6.25 | 18.3553 | 71.76 | 14.6763 | 179.4982 | 85.1201 | 200.8656 | 11.8033 | 74.6572 | 10.8798 | 96 | 20.1419 | 25.4552 | 196.968 | 0
4853 | 775.145 | 1.0619 | 50.5007 | 98.6575 | 52.5814 | 6.8674 | 44.0458 | 1.028 | 5.7376 | 20.8048 | 66.9464 | 9.0761 | 182.6265 | 81.2877 | 198.0292 | 9.3719 | 73.5702 | 10.7547 | 91 | 19.1573 | 25.1378 | 208.565 | 0.089566
4854 | 796.8783 | 0.84265 | 54.8838 | 100.3159 | 50.374 | 9.4878 | 51.7435 | 0.96181 | 5.4989 | 23.6416 | 75.1583 | 11.8589 | 187.8844 | 95.0525 | 201.4856 | 9.0262 | 73.1496 | 10.7075 | 109 | 19.7037 | 26.0389 | 236.9618 | 0.097346
4855 | 841.3122 | 1.9243 | 61.5649 | 107.8485 | 50.7328 | 12.5509 | 76.4021 | 1.2234 | 6.7405 | 28.0042 | 101.8279 | 20.6341 | 193.6738 | 128.3059 | 214.135 | 8.7488 | 74.1058 | 10.942 | 140 | 32.3682 | 31.6778 | 280.1049 | 0.17277
4856 | 878.0935 | 2.4033 | 74.6476 | 117.7152 | 61.7959 | 13.1921 | 112.5847 | 1.8421 | 9.7048 | 31.4605 | 131.2421 | 24.0958 | 222.7601 | 159.8948 | 249.4308 | 9.0444 | 77.1354 | 11.6126 | 159 | 39.6236 | 34.5691 | 323.3654 | 0.28432
4857 | 919.519 | 2.2689 | 81.9807 | 123.5473 | 70.8002 | 14.0332 | 134.9927 | 2.4552 | 12.5047 | 31.8777 | 149.9454 | 24.4291 | 235.7252 | 180.4022 | 288.27 | 9.4875 | 82.5652 | 11.9321 | 157 | 38.2901 | 34.3122 | 351.1863 | 0.32796
4858 | 967.9691 | 2.0704 | 83.8987 | 125.7678 | 76.3713 | 14.9001 | 135.5694 | 2.4246 | 10.6865 | 32.06 | 157.5978 | 24.5866 | 257.2469 | 192.9016 | 303.8184 | 9.7752 | 87.7786 | 11.9895 | 155 | 36.9068 | 33.9449 | 360.8128 | 0.28241
4859 | 979.7473 | 2.9949 | 85.3878 | 125.4704 | 78.2887 | 15.3027 | 139.5379 | 2.756 | 8.8582 | 32.1129 | 162.1438 | 25.5789 | 277.0398 | 201.6917 | 308.449 | 9.4413 | 90.2976 | 11.9846 | 145 | 36.1087 | 33.3427 | 367.8427 | 0.29327
4860 | 958.9601 | 2.7945 | 87.4436 | 123.2506 | 76.5399 | 15.8356 | 147.0835 | 2.7185 | 9.7325 | 32.2132 | 166.4594 | 25.5308 | 270.7561 | 207.0007 | 310.7007 | 9.5357 | 90.7745 | 11.9941 | 144 | 36.5183 | 33.2006 | 370.8584 | 0.24351
4861 | 971.2219 | 2.2836 | 87.2878 | 124.2534 | 75.5416 | 15.4347 | 132.9753 | 2.2309 | 9.2023 | 35.4596 | 167.2674 | 25.2737 | 268.6162 | 211.7256 | 306.0586 | 10.0347 | 90.0773 | 12.0233 | 146 | 34.4432 | 33.0214 | 366.1716 | 0.26815
4862 | 1014.2524 | 2.2793 | 74.5835 | 125.9848 | 76.1421 | 14.6461 | 124.2444 | 2.3636 | 9.6433 | 40.3305 | 167.6808 | 24.9968 | 271.872 | 215.9872 | 308.9432 | 10.1467 | 89.2688 | 11.9966 | 133 | 34.925 | 32.7106 | 360.4772 | 0.25905
4863 | 1039.8658 | 2.4854 | 68.6556 | 120.5855 | 66.6787 | 15.0408 | 114.6838 | 2.2274 | 7.5727 | 37.131 | 155.4591 | 24.5147 | 270.1713 | 208.0874 | 303.9143 | 9.8778 | 88.0632 | 12.0099 | 128 | 30.717 | 32.4535 | 352.4943 | 0.20905
4864 | 1016.0137 | 2.3176 | 44.4383 | 111.3962 | 59.1129 | 11.5797 | 102.6119 | 1.9399 | 5.8828 | 27.046 | 131.7505 | 22.7274 | 265.7161 | 178.2676 | 283.4402 | 9.807 | 86.2859 | 12.041 | 118 | 24.1585 | 32.5532 | 333.4727 | 0.1657
4865 | 993.7633 | 2.0148 | 32.8984 | 103.9013 | 64.0147 | 9.7415 | 95.9742 | 1.8458 | 5.5332 | 19.4617 | 114.9274 | 21.9747 | 256.7758 | 141.9154 | 272.1989 | 9.5801 | 84.2812 | 12.1876 | 117 | 19.2098 | 32.017 | 295.4026 | 0.20398
4866 | 966.5136 | 1.6236 | 32.5862 | 100.9163 | 67.2316 | 8.7569 | 91.7025 | 1.443 | 5.4132 | 17.3923 | 104.8936 | 18.295 | 230.3652 | 114.2787 | 266.7008 | 9.1355 | 81.9347 | 12.1924 | 118 | 17.9869 | 31.5045 | 254.2625 | 0.16412
4867 | 933.2885 | 1.0394 | 31.2208 | 100.8098 | 65.9257 | 8.5909 | 65.5491 | 0.99897 | 5.3664 | 21.8979 | 107.2487 | 8.2586 | 208.8911 | 99.7184 | 253.3638 | 9.2824 | 79.6041 | 12.2722 | 103 | 17.655 | 31.6399 | 226.1093 | 0.18611
4868 | 876.1249 | 0.92221 | 28.549 | 99.0118 | 57.7369 | 8.5449 | 50.736 | 1.065 | 5.5124 | 27.3242 | 113.7669 | 4.3858 | 206.265 | 93.9677 | 235.5091 | 9.5057 | 77.2177 | 12.5478 | 111 | 16.8279 | 29.1328 | 205.8384 | 0.039203
4869 | 817.1794 | 2.3133 | 31.1275 | 99.0123 | 55.2112 | 8.5274 | 45.3051 | 1.0579 | 5.4205 | 28.4688 | 101.5218 | 4.3827 | 207.6907 | 89.2283 | 216.256 | 9.457 | 75.0823 | 11.7622 | 112 | 16.5296 | 26.349 | 193.5666 | 0
4870 | 791.9797 | 2.3959 | 36.7331 | 102.1455 | 59.6335 | 6.4375 | 49.143 | 1.1927 | 5.5484 | 28.9206 | 83.5771 | 5.7957 | 189.7439 | 88.4321 | 215.1362 | 9.6055 | 74.2148 | 12.1511 | 106 | 19.4059 | 25.6999 | 189.6973 | 0
4871 | 765.0078 | 1.4784 | 38.423 | 102.4373 | 61.0293 | 5.7231 | 53.145 | 1.3035 | 5.9612 | 29.8673 | 78.227 | 6.8319 | 171.9085 | 89.4299 | 226.5469 | 10.7428 | 74.6978 | 12.5715 | 116 | 29.9874 | 25.9171 | 188.3488 | 0
4872 | 753.0888 | 1.3266 | 38.2682 | 100.6131 | 61.2924 | 5.6512 | 53.0415 | 1.3116 | 6.192 | 29.8634 | 78.1608 | 6.9199 | 166.3621 | 87.5986 | 232.4106 | 13.2368 | 75.1276 | 11.963 | 120 | 32.2372 | 26.5075 | 187.805 | 0
4873 | 743.9698 | 1.3153 | 37.4228 | 101.4487 | 61.828 | 5.0026 | 50.7792 | 1.3042 | 6.2095 | 29.4557 | 78.3702 | 7.0962 | 165.4424 | 86.3706 | 223.2332 | 14.0101 | 74.8957 | 11.3799 | 101 | 27.3619 | 26.5005 | 188.4211 | 0
4874 | 737.646 | 1.14 | 36.767 | 100.7833 | 60.7727 | 4.8115 | 47.1457 | 1.5526 | 5.9335 | 28.8988 | 78.9057 | 9.9658 | 179.3555 | 92.7853 | 214.5991 | 13.9731 | 74.5177 | 11.1024 | 100 | 23.6971 | 25.9971 | 189.3654 | 0
4875 | 729.3832 | 1.6446 | 36.8302 | 99.9853 | 58.2972 | 5.4611 | 49.9354 | 1.4621 | 5.9885 | 28.2643 | 78.9375 | 18.8105 | 183.4816 | 99.6334 | 210.1549 | 14.3149 | 74.3455 | 11.0604 | 100 | 22.2558 | 25.9965 | 190.033 | 0
4876 | 732.3487 | 1.8 | 36.7029 | 103.1782 | 56.9098 | 6.3392 | 51.56 | 1.1138 | 5.9594 | 28.5187 | 76.3433 | 17.2907 | 185.6447 | 98.5996 | 202.3055 | 12.7429 | 73.8268 | 10.9697 | 97 | 21.1077 | 26.0385 | 195.734 | 0
4877 | 735.738 | 1.2016 | 44.1469 | 104.091 | 55.341 | 8.8084 | 51.8632 | 0.92268 | 5.644 | 30.0563 | 71.1006 | 10.1015 | 188.1113 | 94.9681 | 202.3358 | 10.3954 | 73.1574 | 10.8524 | 93 | 19.7164 | 26.0375 | 209.8243 | 0.049794
4878 | 761.8938 | 1.2778 | 53.2984 | 102.1396 | 52.8175 | 10.8789 | 57.4865 | 0.86458 | 5.3477 | 32.2945 | 77.4348 | 12.7531 | 191.9976 | 104.1556 | 204.6925 | 9.5566 | 73.2026 | 10.7628 | 118 | 19.3198 | 27.0212 | 235.695 | 0.0853
4879 | 806.1922 | 1.5429 | 53.7601 | 96.7642 | 54.9291 | 13.5521 | 78.8645 | 1.1149 | 6.7718 | 32.913 | 103.4288 | 22.025 | 200.892 | 131.0834 | 220.3049 | 10.1306 | 74.0358 | 10.9865 | 148 | 27.0741 | 32.5247 | 274.2779 | 0.16891
4880 | 839.3768 | 1.935 | 69.7557 | 121.7679 | 67.353 | 14.1588 | 123.8442 | 1.5026 | 10.118 | 30.4431 | 133.9409 | 26.9313 | 227.0038 | 159.368 | 247.1902 | 10.6401 | 76.7964 | 11.6226 | 148 | 27.5827 | 33.579 | 314.7518 | 0.29182
4881 | 878.4942 | 2.5029 | 79.9723 | 128.0956 | 77.0665 | 13.5548 | 134.6199 | 1.8613 | 12.7503 | 28.6614 | 150.528 | 26.3676 | 243.6624 | 177.9456 | 280.543 | 10.586 | 82.1271 | 12.0145 | 150 | 28.7053 | 32.6641 | 340.5076 | 0.32338
4882 | 929.6325 | 2.9311 | 81.1392 | 125.8645 | 79.4688 | 12.6908 | 141.9317 | 1.7768 | 9.4267 | 29.554 | 151.591 | 25.7186 | 253.7931 | 188.3664 | 296.7239 | 10.6211 | 87.0231 | 12.055 | 143 | 34.3421 | 32.2494 | 351.2001 | 0.31995
4883 | 980.8761 | 2.5977 | 82.5152 | 126.895 | 79.9783 | 13.0608 | 149.9997 | 1.7789 | 8.8883 | 30.7554 | 150.2723 | 25.2318 | 266.1781 | 196.1784 | 309.4371 | 11.3478 | 88.8497 | 12.03 | 140 | 35.1065 | 32.9603 | 360.2062 | 0.28273
4884 | 992.1905 | 2.1324 | 85.3414 | 128.7931 | 76.5294 | 13.8618 | 152.4618 | 1.7144 | 8.5675 | 32.3615 | 153.5294 | 24.7273 | 262.2337 | 201.6497 | 310.8095 | 11.7414 | 89.189 | 12.0394 | 141 | 35.3035 | 32.7114 | 365.1935 | 0.24878
4885 | 975.7927 | 2.6796 | 84.692 | 126.7245 | 77.0512 | 14.3295 | 140.0092 | 1.7602 | 8.345 | 36.6634 | 158.5484 | 25.3309 | 263.3792 | 204.7323 | 301.4403 | 11.7978 | 90.1273 | 12.0626 | 143 | 35.3777 | 31.6051 | 365.7486 | 0.27681
4886 | 977.1967 | 2.4897 | 82.6615 | 128.2863 | 79.6159 | 14.1731 | 134.4395 | 1.5426 | 8.358 | 39.3458 | 161.5661 | 26.0486 | 264.5568 | 207.3027 | 306.1728 | 11.7239 | 90.8012 | 12.0272 | 139 | 30.0611 | 31.3467 | 362.1281 | 0.23677
4887 | 963.968 | 2.5227 | 78.8856 | 124.9208 | 71.2902 | 15.5763 | 115.1263 | 1.0934 | 6.762 | 35.5108 | 149.3883 | 23.9408 | 262.6659 | 199.8868 | 298.4124 | 11.6254 | 88.8811 | 12.0166 | 127 | 26.7161 | 31.3841 | 351.3028 | 0.28002
4888 | 939.7313 | 2.3227 | 70.5762 | 113.1492 | 70.3614 | 9.9689 | 106.3577 | 0.8745 | 5.5548 | 27.9165 | 127.0847 | 22.16 | 258.644 | 171.2473 | 271.7693 | 11.0084 | 85.6429 | 12.0285 | 124 | 24.1577 | 31.3353 | 329.65 | 0.24109
4889 | 905.2523 | 1.5729 | 63.3792 | 105.7267 | 66.9307 | 6.973 | 104.375 | 0.83734 | 5.33 | 21.3379 | 112.4997 | 21.9024 | 252.6657 | 137.9917 | 248.1916 | 11.0543 | 82.9404 | 12.1289 | 119 | 19.2155 | 31.3251 | 290.1642 | 0.25861
4890 | 874.5182 | 1.5281 | 61.5441 | 99.6902 | 63.2434 | 6.6404 | 87.0847 | 0.85271 | 5.2753 | 19.3572 | 102.5355 | 18.2966 | 224.5 | 114.6071 | 232.0136 | 10.9706 | 77.4345 | 12.2282 | 117 | 17.4131 | 31.0114 | 248.0601 | 0.23093
4891 | 846.6196 | 1.6132 | 60.5697 | 98.4509 | 63.9869 | 7.3223 | 61.4338 | 1.1056 | 5.4081 | 22.9039 | 92.4109 | 8.2153 | 207.5434 | 102.6437 | 224.9458 | 10.6893 | 66.4916 | 12.2334 | 106 | 17.4079 | 30.9308 | 221.0505 | 0.16446
4892 | 838.8482 | 1.1799 | 59.7224 | 99.5075 | 62.3728 | 8.9248 | 50.6613 | 1.0125 | 5.4175 | 27.364 | 82.57 | 4.425 | 198.5333 | 99.5375 | 223.5105 | 10.7981 | 57.1194 | 11.9948 | 108 | 16.6996 | 27.551 | 202.5163 | 0.058979
4893 | 840.3518 | 2.161 | 62.5284 | 100.2231 | 61.2238 | 8.7762 | 48.245 | 0.94801 | 5.7317 | 28.5864 | 76.3921 | 4.3919 | 185.5856 | 93.4106 | 224.5879 | 10.9751 | 54.7217 | 11.4741 | 109 | 16.0491 | 24.9962 | 192.3252 | 0
4894 | 807.4977 | 2.9261 | 68.662 | 101.0295 | 63.9978 | 7.1685 | 47.727 | 1.1814 | 5.6577 | 29.5694 | 75.977 | 5.7368 | 170.8134 | 88.6044 | 233.1187 | 11.3887 | 54.8849 | 11.5898 | 112 | 15.8692 | 24.4718 | 190.0049 | 0
4895 | 756.8582 | 1.9302 | 71.1679 | 101.4912 | 62.1922 | 7.4037 | 45.7782 | 1.3106 | 5.7277 | 30.8774 | 78.1645 | 6.6424 | 164.1551 | 87.942 | 234.8379 | 12.521 | 54.9442 | 11.7263 | 122 | 15.933 | 25.3266 | 188.4184 | 0
4896 | 739.789 | 1.2221 | 70.9028 | 100.7143 | 59.0604 | 6.8772 | 44.6988 | 1.3222 | 6.0093 | 30.5747 | 79.2855 | 6.7605 | 167.2758 | 87.0443 | 227.9055 | 14.7802 | 55.2276 | 11.473 | 118 | 15.9395 | 25.1822 | 187.0248 | 0
4897 | 743.0497 | 1.274 | 70.1689 | 99.6691 | 57.7805 | 7.4249 | 47.7105 | 1.321 | 5.9617 | 29.7474 | 79.5023 | 6.8217 | 173.0068 | 86.5875 | 222.6998 | 16.0709 | 55.0971 | 11.2703 | 103 | 15.9357 | 24.7315 | 187.8167 | 0
4898 | 734.2519 | 1.1997 | 69.918 | 101.3772 | 57.3944 | 8.9766 | 49.6231 | 1.5595 | 5.8994 | 28.8133 | 79.792 | 6.7955 | 180.8201 | 85.751 | 229.1622 | 15.5759 | 54.6113 | 11.1399 | 100 | 15.8725 | 24.8778 | 189.6614 | 0
4899 | 731.7541 | 1.1534 | 69.545 | 104.7478 | 56.0654 | 9.4897 | 47.9375 | 1.4837 | 6.0521 | 27.809 | 80.3391 | 6.8693 | 183.7271 | 84.3624 | 227.4651 | 15.3378 | 54.5009 | 11.2375 | 97 | 15.9004 | 24.8127 | 189.9657 | 0
4900 | 721.4508 | 1.6489 | 69.1965 | 104.0404 | 56.7939 | 7.3242 | 42.3447 | 1.1627 | 5.954 | 27.9884 | 78.997 | 5.6228 | 182.4872 | 81.8363 | 210.7038 | 14.6357 | 54.1291 | 11.1581 | 97 | 15.9458 | 24.7613 | 189.3991 | 0
4901 | 722.3983 | 1.1754 | 69.0293 | 101.4995 | 56.7452 | 5.9933 | 45.7014 | 0.94511 | 5.5985 | 29.9806 | 75.859 | 4.4914 | 182.926 | 83.005 | 202.9479 | 12.4129 | 53.3934 | 11.0283 | 90 | 16.0362 | 25.1695 | 189.3044 | 0.018288
4902 | 739.227 | 0.71425 | 67.4692 | 97.5346 | 56.6936 | 6.444 | 48.2031 | 0.87791 | 5.5206 | 32.4272 | 82.6169 | 4.1089 | 179.6596 | 84.0083 | 198.3145 | 11.426 | 53.0649 | 10.9699 | 91 | 14.8959 | 25.8784 | 189.8885 | 0.048587
4903 | 757.3069 | 0.65223 | 60.9696 | 95.1843 | 59.1026 | 5.9044 | 48.2784 | 0.8814 | 5.5263 | 32.5819 | 103.3834 | 6.1532 | 174.0584 | 81.4862 | 203.8013 | 10.5769 | 52.911 | 11.1041 | 92 | 17.0213 | 26.3975 | 191.4676 | 0.08331
4904 | 762.5697 | 0.72789 | 60.1229 | 97.3372 | 61.6194 | 7.0945 | 45.7795 | 0.92001 | 6.1008 | 28.4411 | 120.3703 | 12.4009 | 180.8096 | 83.2751 | 223.4369 | 11.1627 | 52.7956 | 11.6094 | 94 | 16.8313 | 29.1157 | 195.9143 | 0.13803
4905 | 759.3534 | 1.1048 | 62.6914 | 96.9656 | 68.9846 | 6.9132 | 43.4959 | 0.9293 | 7.3813 | 24.7119 | 127.8189 | 17.75 | 188.0549 | 86.5749 | 240.8741 | 11.3782 | 53.1745 | 11.9082 | 97 | 17.4654 | 31.4068 | 201.3534 | 0.14811
4906 | 764.3279 | 1.5318 | 63.8987 | 97.6826 | 77.9561 | 8.0834 | 46.9799 | 1.4684 | 6.4902 | 25.078 | 135.8325 | 19.2465 | 177.2745 | 87.0093 | 247.5088 | 10.4648 | 53.7465 | 12.0435 | 100 | 18.2899 | 31.7319 | 204.8866 | 0.23255
4907 | 812.9163 | 1.4852 | 66.2673 | 98.3662 | 85.5948 | 7.0423 | 49.6985 | 2.1593 | 6.0172 | 27.0039 | 143.0686 | 19.2165 | 180.5821 | 88.502 | 247.904 | 10.8613 | 54.2581 | 12.0824 | 99 | 18.4087 | 31.1337 | 205.2224 | 0.32639
4908 | 851.5253 | 1.3891 | 67.5413 | 98.6615 | 87.4063 | 7.3684 | 49.9345 | 1.4505 | 5.6185 | 28.8321 | 145.9968 | 18.1408 | 181.5014 | 91.8068 | 244.5903 | 11.1644 | 54.8296 | 12.0559 | 99 | 17.3841 | 31.1848 | 204.938 | 0.3157
4909 | 850.3759 | 1.297 | 68.0178 | 99.9648 | 76.9985 | 8.3155 | 48.5379 | 0.84551 | 5.9017 | 29.5893 | 146.1747 | 15.5698 | 177.7648 | 95.1655 | 237.545 | 10.8179 | 56.4936 | 12.08 | 101 | 16.773 | 30.6283 | 213.9736 | 0.24946
4910 | 849.157 | 1.4322 | 65.9528 | 100.3501 | 72.7053 | 9.2729 | 46.8834 | 0.82889 | 5.8228 | 27.9875 | 145.7722 | 15.7009 | 197.7426 | 98.9739 | 239.6879 | 10.5356 | 58.3549 | 12.0804 | 102 | 16.9019 | 29.9748 | 220.622 | 0.2754
4911 | 866.6441 | 1.4028 | 60.8514 | 99.3526 | 75.0211 | 6.6943 | 46.1993 | 0.84486 | 5.301 | 22.8111 | 132.915 | 16.2687 | 202.3735 | 97.1344 | 235.4767 | 10.7549 | 57.7546 | 12.0662 | 100 | 16.5763 | 29.8287 | 209.141 | 0.21984
4912 | 844.0671 | 0.87294 | 59.1122 | 99.4049 | 63.35 | 6.4015 | 47.2812 | 0.84454 | 5.13 | 17.5863 | 108.7659 | 10.257 | 189.5168 | 91.8529 | 220.5115 | 11.2785 | 55.6191 | 12.0479 | 102 | 16.5989 | 29.8574 | 192.0322 | 0.15513
4913 | 831.812 | 0.92322 | 59.2668 | 100.2171 | 55.2878 | 6.7066 | 48.2761 | 0.84216 | 5.1163 | 15.3847 | 93.5068 | 5.2643 | 190.3225 | 90.9317 | 213.1161 | 11.0712 | 54.052 | 12.0934 | 101 | 16.5291 | 29.7951 | 181.9681 | 0.12781
4914 | 834.9382 | 1.1582 | 59.6325 | 100.3866 | 63.6507 | 6.6437 | 48.5202 | 1.1174 | 5.2178 | 14.5929 | 85.0616 | 4.3532 | 198.3848 | 91.1189 | 222.9603 | 10.9358 | 53.3633 | 12.0847 | 103 | 16.4582 | 29.7333 | 178.7778 | 0.085548
4915 | 817.6488 | 1.0726 | 60.2489 | 100.9772 | 66.8473 | 6.5872 | 49.5615 | 1.0304 | 5.2777 | 14.3529 | 78.5667 | 4.3922 | 183.3638 | 88.4528 | 233.0716 | 10.552 | 53.0422 | 12.0912 | 100 | 16.5764 | 30.0307 | 177.8052 | 0.047672
4916 | 791.8183 | 3.2371 | 61.5138 | 100.0276 | 60.3681 | 8.1073 | 49.9038 | 0.85388 | 5.1713 | 14.3477 | 75.5747 | 4.3229 | 177.4955 | 85.2498 | 227.9671 | 10.7829 | 53.0849 | 11.8566 | 103 | 16.59 | 30.0071 | 177.0473 | 0.010734
4917 | 758.8766 | 7.4522 | 68.7529 | 77.5209 | 59.4874 | 7.164 | 49.404 | 1.0042 | 5.1473 | 14.7195 | 74.712 | 4.4236 | 180.6852 | 84.022 | 219.4889 | 10.8382 | 53.6505 | 11.2298 | 100 | 16.5619 | 26.5177 | 174.6153 | 0
4918 | 739.7696 | 4.6741 | 71.2772 | 118.0916 | 59.3321 | 6.6385 | 45.1931 | 1.1999 | 5.488 | 16.6663 | 76.8012 | 6.1193 | 172.2958 | 86.3278 | 210.8278 | 11.2944 | 54.1916 | 11.2127 | 99 | 16.5085 | 25.1887 | 172.7439 | 0
4919 | 729.7476 | 1.6005 | 71.1893 | 107.1492 | 58.5996 | 6.6366 | 45.0847 | 1.3078 | 6.1709 | 18.3422 | 79.1084 | 6.9049 | 167.0965 | 88.8316 | 207.7743 | 12.333 | 54.4787 | 11.2449 | 113 | 16.5619 | 24.9959 | 175.3066 | 0
4920 | 727.3379 | 1.2035 | 71.036 | 101.826 | 58.6953 | 6.6426 | 48.4877 | 1.3044 | 6.4556 | 17.9323 | 78.8186 | 7.0409 | 169.1792 | 92.9762 | 212.229 | 14.5024 | 54.5683 | 11.0847 | 104 | 16.6834 | 24.937 | 178.8892 | 0
4921 | 723.7548 | 1.1263 | 70.8422 | 99.8267 | 57.1605 | 8.5852 | 49.1501 | 1.2965 | 6.8328 | 17.2415 | 78.2366 | 6.895 | 167.9839 | 97.6858 | 207.9483 | 15.7165 | 54.4454 | 11.0308 | 102 | 16.6662 | 24.5971 | 179.5719 | 0
4922 | 715.3768 | 1.0539 | 70.439 | 99.1387 | 56.5703 | 9.6279 | 47.904 | 1.5026 | 6.8745 | 17.0695 | 78.2379 | 6.8279 | 166.1728 | 98.9031 | 208.953 | 17.0259 | 54.2975 | 10.8624 | 105 | 16.5357 | 24.6941 | 179.8724 | 0
4923 | 711.3709 | 1.0467 | 70.0177 | 99.4165 | 56.7418 | 9.4962 | 46.7159 | 1.5017 | 6.7687 | 17.4508 | 78.6894 | 6.888 | 170.3592 | 99.2012 | 208.053 | 15.9132 | 54.2431 | 10.7596 | 101 | 16.5873 | 24.7181 | 180.4584 | 0
4924 | 713.2313 | 1.478 | 69.2729 | 97.5251 | 58.6343 | 6.6807 | 45.473 | 1.1844 | 6.788 | 16.3922 | 77.5253 | 5.8018 | 179.3037 | 97.1358 | 202.3612 | 13.8104 | 53.784 | 10.7618 | 97 | 16.6753 | 24.6249 | 179.4015 | 0
4925 | 708.8271 | 1.1781 | 68.7147 | 96.2724 | 58.4186 | 5.7131 | 47.4119 | 0.93892 | 6.6449 | 13.796 | 74.45 | 4.4849 | 182.2487 | 96.9575 | 199.7941 | 11.8462 | 52.9556 | 10.7874 | 94 | 16.6948 | 24.5089 | 176.3658 | 0.024248
4926 | 730.088 | 0.72587 | 67.0926 | 97.3381 | 58.8787 | 5.7415 | 48.6777 | 0.86667 | 6.324 | 12.6973 | 80.7396 | 4.1084 | 176.4141 | 96.3009 | 195.9417 | 10.9345 | 52.5503 | 10.7918 | 91 | 16.5984 | 24.4694 | 173.9501 | 0.062535
4927 | 744.9544 | 0.64849 | 60.8517 | 98.3772 | 61.1256 | 6.4224 | 49.0261 | 0.86551 | 5.6773 | 12.6558 | 100.8572 | 4.6245 | 172.0948 | 94.3657 | 202.2345 | 10.7765 | 52.609 | 10.9906 | 95 | 16.7798 | 24.6665 | 175.0222 | 0.11608
4928 | 745.1421 | 0.68772 | 59.3525 | 98.635 | 71.4959 | 7.9898 | 49.1194 | 0.91636 | 5.237 | 13.0662 | 117.9004 | 7.943 | 176.8467 | 96.4656 | 225.2997 | 10.7542 | 52.5335 | 11.615 | 97 | 16.7766 | 24.8966 | 175.8842 | 0.16842
4929 | 747.9661 | 1.0558 | 59.1549 | 99.2535 | 81.1228 | 7.1399 | 48.8994 | 0.92908 | 5.2811 | 15.0417 | 122.6767 | 9.2578 | 160.4172 | 100.7843 | 243.8938 | 10.7334 | 52.8029 | 11.9995 | 96 | 16.7689 | 25.6727 | 176.1906 | 0.20638
4930 | 756.2915 | 1.7497 | 58.8918 | 99.0621 | 83.9186 | 6.757 | 45.7808 | 1.0549 | 5.3332 | 20.0014 | 123.5062 | 9.3022 | 161.0935 | 104.2791 | 253.6495 | 10.6756 | 53.4236 | 12.0787 | 100 | 16.6349 | 25.7769 | 178.4255 | 0.16763
4931 | 805.8587 | 1.9027 | 61.0896 | 98.3694 | 85.8696 | 7.2964 | 48.935 | 1.0461 | 5.3014 | 24.2169 | 128.9955 | 8.9626 | 173.2918 | 104.5626 | 250.8417 | 10.6899 | 53.9094 | 12.0609 | 101 | 16.5247 | 25.6991 | 178.8155 | 0.25042
4932 | 819.9378 | 1.933 | 62.4374 | 98.2995 | 79.7684 | 6.8289 | 48.8423 | 0.88862 | 5.394 | 21.5414 | 137.3808 | 5.9117 | 172.0008 | 99.5984 | 245.8732 | 11.1199 | 55.6509 | 12.0231 | 94 | 16.5269 | 25.359 | 177.2338 | 0.24447
4933 | 820.4156 | 1.8085 | 63.0166 | 98.1861 | 74.5807 | 8.1939 | 48.6674 | 0.8405 | 5.556 | 16.3292 | 142.1603 | 4.5289 | 177.7021 | 95.2871 | 240.2538 | 10.982 | 57.6047 | 12.0283 | 94 | 16.534 | 24.6403 | 179.1601 | 0.24794
4934 | 850.9358 | 1.7232 | 62.3236 | 100.5532 | 77.6287 | 7.0517 | 50.3827 | 0.83879 | 5.6055 | 14.8324 | 144.3572 | 5.9976 | 183.7597 | 95.6707 | 238.7003 | 10.9667 | 56.4031 | 12.0674 | 98 | 16.4476 | 24.4036 | 182.4149 | 0.24205
4935 | 845.993 | 1.9259 | 60.3128 | 78.292 | 75.1662 | 7.3861 | 49.987 | 0.83571 | 5.7089 | 15.6563 | 132.7252 | 8.3978 | 182.2032 | 93.5636 | 233.3078 | 10.8065 | 53.7269 | 12.014 | 98 | 16.4704 | 24.3983 | 182.8073 | 0.25319
4936 | 819.7263 | 1.7976 | 59.5496 | 110.8495 | 63.2706 | 6.9079 | 50.9964 | 0.80298 | 5.232 | 15.9667 | 109.7156 | 9.0658 | 178.1891 | 89.8551 | 226.1566 | 10.8516 | 52.8857 | 11.979 | 98 | 16.5519 | 24.4512 | 182.4016 | 0.23553
4937 | 812.444 | 1.41 | 60.1574 | 99.9858 | 58.9218 | 6.6379 | 51.1332 | 0.81908 | 5.3522 | 15.2433 | 98.6615 | 6.9891 | 174.2116 | 88.664 | 216.7921 | 10.725 | 53.2274 | 11.9605 | 101 | 16.5644 | 24.1725 | 182.8664 | 0.25355
4938 | 834.5306 | 1.2314 | 59.7349 | 75.4253 | 64.7265 | 6.6204 | 50.9782 | 1.0151 | 5.3355 | 14.5247 | 95.9254 | 5.9321 | 170.0767 | 89.2896 | 208.7758 | 10.6716 | 53.5664 | 11.9853 | 99 | 16.4737 | 24.0599 | 181.3783 | 0.21797
4939 | 832.3789 | 1.2347 | 60.078 | 110.2575 | 66.4636 | 7.354 | 51.0874 | 1.0443 | 5.4277 | 14.3474 | 88.6395 | 5.8376 | 168.7041 | 90.673 | 213.1062 | 10.9456 | 53.5032 | 11.9905 | 97 | 16.495 | 24.1204 | 180.7474 | 0.15973
4940 | 817.8401 | 1.602 | 61.1019 | 100.8897 | 65.9944 | 6.9253 | 52.4077 | 0.88379 | 5.5578 | 13.8967 | 80.0935 | 5.6749 | 164.2833 | 90.2032 | 211.8688 | 10.9074 | 53.1689 | 11.7675 | 99 | 16.5099 | 24.275 | 181.9839 | 0.062795
4941 | 816.1029 | 2.6182 | 68.5016 | 83.9959 | 62.3057 | 6.6723 | 49.7225 | 0.96591 | 5.457 | 12.8423 | 75.5494 | 5.5293 | 161.3014 | 88.1436 | 209.4934 | 10.7036 | 52.9401 | 11.1447 | 99 | 16.5104 | 24.4406 | 185.7992 | 0
4942 | 768.7335 | 2.5653 | 71.5082 | 123.791 | 60.4348 | 6.6292 | 48.8364 | 1.1851 | 5.4 | 13.7523 | 75.6353 | 7.5236 | 164.5967 | 89.4575 | 203.3981 | 11.2893 | 53.6523 | 11.1768 | 110 | 16.4945 | 24.7902 | 188.7659 | 0
4943 | 721.6732 | 1.7915 | 71.9447 | 108.5018 | 59.267 | 7.4035 | 50.3345 | 1.2854 | 5.7649 | 16.0784 | 77.3971 | 17.0523 | 160.0355 | 90.9283 | 203.8544 | 12.1324 | 54.581 | 11.5439 | 116 | 16.5581 | 25.2003 | 185.2782 | 0
4944 | 724.0712 | 1.5038 | 71.4449 | 103.8278 | 59.1052 | 6.8595 | 50.0486 | 1.2749 | 6.0515 | 16.8948 | 77.2992 | 23.7969 | 161.0156 | 88.9617 | 207.3032 | 14.5258 | 54.513 | 11.3932 | 119 | 16.6252 | 25.4125 | 182.0644 | 0
4945 | 718.3562 | 1.2146 | 71.3044 | 105.7423 | 58.6167 | 7.2796 | 50.1264 | 1.2944 | 6.0196 | 16.9056 | 76.8473 | 25.246 | 165.0455 | 86.165 | 208.5038 | 15.499 | 54.0982 | 11.1887 | 116 | 16.6198 | 25.3683 | 180.3884 | 0
4946 | 711.6569 | 1.1349 | 70.6999 | 106.4291 | 57.8305 | 7.6179 | 50.3378 | 1.4462 | 5.9802 | 16.9023 | 76.799 | 26.6301 | 175.3156 | 85.2056 | 213.7826 | 15.5729 | 53.931 | 11.0817 | 98 | 16.5863 | 25.4972 | 178.934 | 0
4947 | 712.341 | 1.2126 | 69.5622 | 107.1447 | 56.8833 | 7.7154 | 49.9885 | 1.5128 | 5.8913 | 17.3362 | 76.6532 | 32.0649 | 184.1913 | 92.0976 | 208.3509 | 15.6406 | 54.0589 | 11.0655 | 94 | 16.5672 | 26.1604 | 182.0848 | 0
4948 | 703.5628 | 1.5578 | 69.4515 | 104.8247 | 58.7725 | 6.8288 | 49.0699 | 1.1946 | 5.8344 | 18.5919 | 74.7209 | 27.5268 | 187.3253 | 98.7588 | 201.4638 | 14.6985 | 53.6892 | 10.9327 | 98 | 16.5777 | 25.5868 | 191.1549 | 0
4949 | 715.0247 | 1.1493 | 68.828 | 103.1598 | 58.7318 | 7.3716 | 49.5489 | 0.93948 | 5.6383 | 19.816 | 71.9729 | 13.0595 | 186.2843 | 97.5709 | 199.1264 | 12.2842 | 52.9461 | 10.7766 | 91 | 16.6073 | 24.824 | 202.2646 | 0.089318
4950 | 750.8179 | 0.96734 | 68.4292 | 102.6346 | 57.2013 | 9.0201 | 55.2972 | 0.86679 | 5.3803 | 22.3337 | 82.2099 | 12.6162 | 187.5879 | 105.5811 | 203.1138 | 11.1875 | 53.071 | 10.7452 | 110 | 14.9857 | 24.7251 | 233.8487 | 0.14775
4951 | 802.9801 | 1.6303 | 67.7968 | 108.5201 | 57.319 | 13.6332 | 86.7341 | 1.1081 | 5.3415 | 28.5701 | 109.8722 | 22.5005 | 207.1223 | 133.1638 | 221.4108 | 10.767 | 54.1648 | 10.9823 | 138 | 35.0872 | 30.0245 | 283.5271 | 0.23269
4952 | 852.548 | 1.6422 | 76.7345 | 119.7089 | 67.6483 | 15.9379 | 123.617 | 1.5789 | 7.2057 | 30.7721 | 137.5313 | 27.6723 | 228.4037 | 167.5611 | 254.3929 | 11.414 | 57.6996 | 11.5707 | 139 | 30.9254 | 32.9227 | 323.2902 | 0.27317
4953 | 905.2675 | 2.0417 | 84.3757 | 125.0233 | 76.8427 | 16.2471 | 144.383 | 2.0723 | 9.9396 | 28.7888 | 153.7485 | 27.9801 | 245.8596 | 189.0839 | 291.5911 | 11.2389 | 63.5192 | 11.917 | 155 | 22.4151 | 33.0388 | 344.088 | 0.32089
4954 | 920.8318 | 2.5631 | 86.5911 | 126.0282 | 79.3766 | 16.1172 | 144.806 | 1.9299 | 7.4979 | 29.4986 | 157.2729 | 28.3179 | 258.7091 | 198.6737 | 308.1198 | 11.2454 | 67.8587 | 11.8294 | 142 | 21.6127 | 32.8914 | 349.4325 | 0.15266
4955 | 939.5318 | 2.5149 | 86.9043 | 127.0251 | 81.6914 | 13.236 | 148.9497 | 1.8066 | 5.847 | 31.0917 | 158.0298 | 28.681 | 268.3957 | 204.5967 | 315.5317 | 11.4872 | 70.1585 | 6.3134 | 141 | 20.4891 | 32.3075 | 354.8973 | 0.22798
4956 | 943.3234 | 2.2832 | 89.5791 | 125.3344 | 79.3068 | 13.9115 | 145.1621 | 2.1827 | 5.76 | 33.5754 | 164.389 | 30.0183 | 269.9688 | 208.4712 | 313.5273 | 11.4808 | 71.7281 | 3.7758 | 143 | 21.186 | 32.2565 | 359.4233 | 0.15651
4957 | 996.4083 | 1.9032 | 90.4637 | 125.6721 | 77.7879 | 14.2556 | 139.2109 | 2.2405 | 5.6397 | 38.454 | 170.9919 | 31.2453 | 271.052 | 219.2184 | 308.5063 | 11.4213 | 72.9328 | 3.5655 | 148 | 33.9535 | 32.2988 | 361.2787 | 0.19204
4958 | 1022.1166 | 2.3184 | 80.3289 | 126.5096 | 73.3019 | 14.8862 | 135.5916 | 1.8125 | 5.815 | 43.0883 | 172.1077 | 29.506 | 274.0969 | 231.9768 | 321.9624 | 11.2005 | 73.0647 | 3.4257 | 142 | 38.941 | 33.1484 | 366.2023 | 0.25768
4959 | 998.7575 | 3.0529 | 54.8274 | 120.7203 | 70.7653 | 13.647 | 113.5253 | 1.7674 | 5.784 | 39.4743 | 156.7152 | 25.4918 | 279.87 | 219.4928 | 330.128 | 11.404 | 73.1265 | 3.4311 | 135 | 37.888 | 32.4873 | 362.75 | 0.2507
4960 | 953.0406 | 1.9249 | 38.4947 | 108.0026 | 69.5011 | 9.8726 | 103.1839 | 1.5489 | 5.4852 | 29.8461 | 132.2899 | 22.7114 | 268.9624 | 184.3385 | 317.6787 | 11.3583 | 72.9692 | 3.313 | 133 | 34.0686 | 32.52 | 340.0029 | 0.17117
4961 | 917.7781 | 0.86027 | 34.4316 | 102.9302 | 66.4697 | 9.2108 | 103.8832 | 1.0338 | 5.3528 | 22.7857 | 117.4969 | 22.0636 | 256.5655 | 150.1191 | 307.7664 | 10.164 | 69.329 | 3.2198 | 128 | 22.1612 | 31.6499 | 296.7758 | 0.12104
4962 | 885.2088 | 0.88154 | 34.273 | 101.6758 | 64.9893 | 8.7384 | 87.7162 | 0.91205 | 5.3878 | 19.7148 | 110.6023 | 19.1116 | 237.4503 | 120.8676 | 292.6858 | 9.5989 | 64.3009 | 3.3183 | 125 | 18.1972 | 30.9453 | 251.5989 | 0.072378
4963 | 824.4375 | 1.0832 | 32.3946 | 100.2544 | 62.9135 | 7.8922 | 61.8286 | 1.0215 | 5.3622 | 19.0998 | 104.816 | 11.9006 | 213.9232 | 102.3124 | 265.8134 | 9.93 | 61.3245 | 3.3611 | 102 | 18.1291 | 30.4145 | 217.6574 | 0.044283
4964 | 786.992 | 1.4566 | 30.9225 | 99.349 | 60.7729 | 7.6892 | 50.9164 | 0.92324 | 5.3195 | 18.68 | 98.0532 | 8.0779 | 192.4436 | 94.1957 | 242.2342 | 9.8963 | 58.6117 | 3.2403 | 101 | 18.3981 | 27.2625 | 197.4091 | 0.012311
4965 | 782.0189 | 2.8107 | 36.9356 | 100.42 | 62.3631 | 7.636 | 50.5336 | 0.9888 | 5.3368 | 17.2144 | 87.9633 | 5.55 | 177.3291 | 88.3411 | 237.7706 | 10.2409 | 55.7053 | 2.8196 | 100 | 17.2352 | 24.6841 | 189.9868 | 0
4966 | 774.3275 | 2.7145 | 39.2055 | 101.9358 | 62.8543 | 7.5629 | 50.8335 | 1.2149 | 5.6051 | 16.766 | 79.1435 | 6.3034 | 159.1563 | 86.86 | 242.0621 | 10.3757 | 54.7721 | 2.8523 | 102 | 19.5798 | 24.3852 | 186.5604 | 0
4967 | 754.4427 | 1.6825 | 38.2958 | 102.468 | 61.0421 | 7.5087 | 51.5996 | 1.2925 | 6.3197 | 17.527 | 77.5311 | 9.983 | 153.2216 | 89.1823 | 242.4436 | 11.1351 | 55.0767 | 2.7246 | 117 | 29.9464 | 24.6184 | 186.7278 | 0
4968 | 744.9435 | 1.2452 | 38.1631 | 102.8966 | 60.6399 | 7.6574 | 51.8623 | 1.3721 | 6.5664 | 17.3951 | 78.1765 | 15.5115 | 154.2448 | 89.6457 | 242.132 | 13.5653 | 54.9768 | 2.512 | 114 | 33.3727 | 24.4612 | 185.9943 | 0
4969 | 739.5462 | 1.1222 | 38.2168 | 102.9779 | 60.9847 | 8.962 | 51.7189 | 1.483 | 6.387 | 17.029 | 78.0976 | 16.9335 | 159.6403 | 89.4508 | 234.5203 | 14.8537 | 54.6034 | 2.4736 | 118 | 33.4454 | 24.4413 | 182.6731 | 0
4970 | 734.8713 | 1.1235 | 37.9099 | 103.3891 | 61.9922 | 8.1363 | 52.7101 | 1.3827 | 6.3358 | 16.9792 | 78.009 | 18.9823 | 165.1014 | 95.7291 | 222.2688 | 14.723 | 54.4632 | 2.3769 | 117 | 33.5032 | 24.4602 | 181.3211 | 0
4971 | 730.0551 | 1.1082 | 36.7893 | 100.9216 | 60.4418 | 7.5805 | 51.3983 | 1.2839 | 6.4457 | 17.7426 | 77.9263 | 25.4992 | 165.8067 | 103.1311 | 219.9174 | 14.9973 | 54.345 | 2.2976 | 117 | 33.4545 | 24.4385 | 181.9881 | 0
4972 | 727.8111 | 1.4903 | 36.4901 | 99.9967 | 60.1663 | 6.843 | 49.3463 | 1.2475 | 6.3192 | 20.9334 | 77.4175 | 23.0554 | 183.0412 | 103.6785 | 214.7372 | 13.258 | 53.9565 | 2.2404 | 112 | 29.8784 | 24.5193 | 188.1127 | 0
4973 | 731.8981 | 1.6957 | 43.6107 | 98.2107 | 60.4235 | 7.2688 | 50.1774 | 1.0005 | 6.2537 | 23.7475 | 76.6106 | 10.9997 | 192.6425 | 101.0668 | 210.5581 | 10.7045 | 53.3908 | 2.0154 | 93 | 28.1611 | 24.379 | 201.7826 | 0.013797
4974 | 751.6728 | 1.8545 | 49.3048 | 99.3582 | 59.5571 | 8.9566 | 52.4375 | 0.86815 | 5.7139 | 25.1194 | 85.6645 | 11.299 | 191.4798 | 108.4451 | 210.6464 | 10.0786 | 53.0352 | 1.9267 | 114 | 22.6187 | 24.8181 | 227.1104 | 0.042443
4975 | 797.9051 | 2.0211 | 48.1841 | 95.1405 | 57.8764 | 11.7332 | 81.8582 | 1.2123 | 6.5515 | 24.5306 | 111.1445 | 21.4499 | 199.2587 | 134.2317 | 217.8076 | 10.4374 | 54.1597 | 2.3166 | 142 | 35.5194 | 30.8353 | 268.3619 | 0.090438
4976 | 839.7957 | 1.8017 | 65.0676 | 119.6264 | 59.3189 | 12.4371 | 108.6114 | 2.2306 | 10.0165 | 22.1411 | 135.7381 | 24.8392 | 223.2316 | 162.6818 | 249.5726 | 11.4914 | 57.9439 | 3.1871 | 154 | 38.2311 | 32.745 | 312.9852 | 0.11481
4977 | 899.3897 | 1.7766 | 74.2448 | 124.5902 | 56.8263 | 13.7449 | 107.1494 | 2.4959 | 11.643 | 18.3358 | 146.3035 | 25.7288 | 245.1372 | 181.6865 | 284.0268 | 12.0162 | 63.477 | 3.4147 | 160 | 39.8226 | 33.1381 | 342.7249 | 0.12997
4978 | 941.5659 | 1.7692 | 75.1875 | 121.5706 | 54.2297 | 14.9613 | 108.4098 | 2.3219 | 12.9006 | 14.1344 | 148.9968 | 25.8531 | 260.1827 | 193.7326 | 314.3707 | 11.6476 | 67.3492 | 3.6185 | 162 | 41.4232 | 33.2277 | 353.7639 | 0.25543
4979 | 967.0277 | 1.6079 | 77.4066 | 120.3378 | 55.4271 | 14.5855 | 113.8136 | 2.3067 | 13.5525 | 14.9224 | 153.7363 | 25.2903 | 275.6911 | 199.9771 | 334.12 | 10.9727 | 68.4511 | 3.8613 | 162 | 42.8258 | 32.1545 | 359.1847 | 0.27134
4980 | 951.7964 | 1.6809 | 81.5282 | 123.0177 | 55.9743 | 14.1805 | 112.9163 | 2.5589 | 13.6072 | 22.7761 | 161.908 | 25.8016 | 278.0265 | 203.951 | 325.8161 | 11.2118 | 68.8151 | 3.9263 | 163 | 37.6921 | 31.77 | 367.0277 | 0.23672
4981 | 947.8874 | 2.018 | 85.7156 | 127.595 | 54.8675 | 14.9833 | 106.7839 | 2.4717 | 13.0829 | 34.9518 | 167.1298 | 26.1776 | 278.9236 | 209.082 | 322.5984 | 12.8297 | 69.6616 | 4.0791 | 161 | 37.0786 | 32.5209 | 370.7832 | 0.24844
4982 | 950.637 | 2.4094 | 86.9938 | 125.4089 | 55.4844 | 15.7263 | 106.105 | 2.3215 | 13.3469 | 41.6506 | 171.5236 | 25.6068 | 284.0464 | 212.6727 | 336.0795 | 13.9122 | 70.4401 | 4.1868 | 154 | 38.1034 | 33.1199 | 367.6281 | 0.20633
4983 | 936.7455 | 2.2359 | 58.7945 | 119.8968 | 58.5361 | 12.6342 | 96.2019 | 2.4646 | 13.6588 | 38.5473 | 162.8089 | 23.8842 | 283.663 | 202.2344 | 333.9729 | 13.3887 | 69.4167 | 4.1937 | 138 | 35.9662 | 32.601 | 362.3056 | 0.21714
4984 | 926.9593 | 1.7802 | 37.8554 | 107.7645 | 61.7891 | 8.7244 | 82.2951 | 2.1707 | 10.8244 | 31.5104 | 138.8494 | 21.9506 | 273.3509 | 178.6783 | 311.3344 | 12.9311 | 66.7459 | 3.8059 | 122 | 31.0077 | 31.9616 | 348.4783 | 0.18923
4985 | 886.9751 | 1.4767 | 34.234 | 102.7429 | 60.8728 | 8.3286 | 81.1497 | 1.5067 | 6.7432 | 25.2923 | 119.5987 | 21.5021 | 265.8244 | 160.8205 | 292.4907 | 12.3886 | 63.7975 | 3.5019 | 123 | 21.7119 | 31.3469 | 311.2096 | 0.17919
4986 | 846.2943 | 1.197 | 33.9173 | 101.6017 | 62.0406 | 7.0996 | 79.0486 | 1.0405 | 5.2254 | 20.7005 | 107.8402 | 17.869 | 246.8264 | 145.3691 | 270.6679 | 12.4939 | 61.0641 | 3.4186 | 123 | 18.9285 | 30.3188 | 269.6947 | 0.13351
4987 | 821.4418 | 1.1108 | 31.673 | 97.7231 | 62.5942 | 6.641 | 57.5938 | 1.1077 | 5.4551 | 17.8836 | 101.8883 | 8.1085 | 232.7841 | 128.4651 | 245.9692 | 11.0229 | 58.8965 | 3.4271 | 110 | 19.0873 | 29.9917 | 240.4661 | 0.14321
4988 | 792.5463 | 1.5584 | 29.94 | 97.7403 | 59.417 | 7.338 | 59.1845 | 1.0171 | 5.467 | 16.4032 | 98.1389 | 3.958 | 218.1731 | 117.3427 | 232.7632 | 9.8214 | 56.856 | 3.171 | 132 | 18.9703 | 27.2717 | 215.5782 | 0.040949
4989 | 770.2642 | 2.8408 | 35.5347 | 99.9099 | 57.683 | 6.8623 | 70.8961 | 1.0084 | 5.5808 | 15.3462 | 90.2738 | 4.5431 | 209.2431 | 112.6177 | 224.3945 | 10.3667 | 55.5969 | 2.5362 | 123 | 18.7439 | 25.0106 | 200.0612 | 0
4990 | 763.391 | 2.8804 | 37.9298 | 104.6155 | 57.9679 | 7.396 | 54.8945 | 1.2015 | 5.6737 | 15.095 | 82.783 | 12.9946 | 199.479 | 112.0924 | 225.7599 | 10.5994 | 54.799 | 2.4635 | 104 | 21.6943 | 24.5145 | 194.4789 | 0
4991 | 746.1608 | 1.7519 | 37.8852 | 107.0903 | 56.661 | 7.6065 | 46.5307 | 1.3138 | 6.1447 | 15.0357 | 80.5044 | 19.8166 | 189.9962 | 111.9372 | 230.3242 | 11.2415 | 53.4203 | 2.4597 | 99 | 31.3497 | 24.7285 | 192.3153 | 0
4992 | 737.69 | 1.5706 | 38.8424 | 107.5109 | 54.6785 | 7.5334 | 46.5255 | 1.4432 | 6.3805 | 14.5235 | 78.2025 | 21.1702 | 201.6802 | 111.0362 | 225.693 | 13.9169 | 53.0169 | 2.4111 | 98 | 33.8233 | 24.959 | 193.1805 | 0
4993 | 738.8958 | 1.4263 | 41.7024 | 111.4117 | 52.7198 | 8.3003 | 47.7249 | 1.5004 | 6.3991 | 14.4557 | 74.5156 | 21.2077 | 180.7155 | 109.5391 | 221.6583 | 14.9784 | 54.699 | 2.395 | 96 | 31.2364 | 24.8069 | 196.883 | 0
4994 | 733.9739 | 1.147 | 42.642 | 112.8125 | 47.7839 | 7.2514 | 48.6911 | 1.3671 | 6.5073 | 14.6514 | 71.9609 | 23.5391 | 164.9109 | 115.6831 | 218.89 | 14.6448 | 56.9032 | 2.3727 | 98 | 27.9689 | 24.8324 | 197.4542 | 0
4995 | 736.2459 | 1.0887 | 42.8398 | 112.4537 | 36.6909 | 6.595 | 48.5084 | 1.3173 | 6.5454 | 15.3997 | 71.0704 | 30.1554 | 195.9784 | 126.1551 | 212.9515 | 14.7561 | 57.4973 | 2.4081 | 98 | 26.6834 | 24.8282 | 197.0559 | 0
4996 | 736.8031 | 1.5131 | 41.5407 | 107.0789 | 42.8772 | 6.7081 | 42.9857 | 1.1665 | 6.4853 | 17.6557 | 69.5558 | 24.3114 | 202.8834 | 129.0358 | 201.429 | 13.5729 | 56.193 | 2.3182 | 101 | 23.522 | 24.6778 | 201.8897 | 0
4997 | 746.8712 | 1.215 | 47.0808 | 106.4851 | 50.0823 | 7.3489 | 43.0352 | 0.96665 | 5.7227 | 19.9734 | 67.1232 | 11.3331 | 178.1799 | 126.9058 | 199.3254 | 11.4631 | 52.9643 | 2.1261 | 96 | 22.5308 | 24.8973 | 216.2089 | 0.065512
4998 | 777.2423 | 0.95639 | 50.0323 | 105.3603 | 37.8354 | 9.0471 | 52.6467 | 0.90467 | 5.4757 | 22.1597 | 76.0711 | 12.8375 | 152.9725 | 125.8131 | 200.8728 | 9.8312 | 51.0909 | 2.0579 | 115 | 20.4081 | 26.1302 | 246.3951 | 0.12241
4999 | 819.7997 | 1.6107 | 48.5819 | 102.1042 | 38.6977 | 11.5325 | 70.1459 | 1.1509 | 5.716 | 26.7358 | 102.4837 | 23.3995 | 199.7944 | 138.8579 | 212.5636 | 9.9166 | 53.3309 | 2.3388 | 154 | 31.4487 | 30.9434 | 282.4487 | 0.12525
5000 | 851.3405 | 1.6685 | 57.6356 | 112.6208 | 46.9079 | 13.0663 | 96.4688 | 2.3251 | 7.1951 | 28.1044 | 130.966 | 28.9085 | 226.9617 | 163.311 | 243.149 | 11.0794 | 58.0285 | 3.1079 | 147 | 33.595 | 32.4166 | 315.7825 | 0.14574
5001 | 891.2694 | 1.5884 | 74.0393 | 120.3425 | 46.6445 | 13.3212 | 107.4181 | 2.6486 | 7.1067 | 25.2625 | 142.8132 | 28.0255 | 235.0182 | 180.7685 | 270.6727 | 11.1768 | 63.5823 | 3.6059 | 144 | 32.8858 | 32.483 | 338.9708 | 0.18158
5002 | 922.0045 | 1.6925 | 78.8101 | 121.8474 | 48.2731 | 13.2537 | 105.4585 | 2.5037 | 5.724 | 26.4413 | 144.4698 | 25.9781 | 247.6477 | 189.2013 | 289.3502 | 11.2132 | 67.7487 | 3.6431 | 147 | 34.794 | 32.4033 | 347.5419 | 0.17293
5003 | 927.1798 | 2.0168 | 80.3853 | 125.3691 | 53.1162 | 13.3602 | 113.5071 | 2.6178 | 5.2505 | 30.0573 | 152.9575 | 24.7124 | 259.5697 | 197.8835 | 308.9972 | 10.5858 | 71.5776 | 3.6345 | 141 | 38.1388 | 32.6899 | 361.0648 | 0.14651
5004 | 920.4479 | 2.0283 | 85.8016 | 136.6522 | 54.6314 | 14.0449 | 120.9837 | 2.9529 | 5.2862 | 32.5045 | 164.0962 | 24.5659 | 267.8739 | 205.8968 | 313.2715 | 11.0313 | 80.9573 | 3.599 | 149 | 36.793 | 33.1346 | 370.4863 | 0.19547
5005 | 923.8773 | 2.2011 | 87.8174 | 139.058 | 56.6128 | 14.8587 | 116.3478 | 2.9655 | 5.5692 | 36.4702 | 170.4994 | 24.645 | 273.7827 | 211.0116 | 311.6291 | 11.8671 | 91.5546 | 3.4515 | 153 | 36.6042 | 32.765 | 369.0469 | 0.26588
5006 | 929.5578 | 2.5427 | 77.8307 | 128.4636 | 62.6184 | 15.2354 | 106.3041 | 2.6966 | 5.9277 | 40.2014 | 172.1182 | 24.635 | 278.7176 | 213.7532 | 317.667 | 10.8333 | 95.6441 | 3.4255 | 142 | 37.4921 | 32.8905 | 363.9508 | 0.19011
5007 | 928.6048 | 2.6818 | 52.9437 | 121.9704 | 68.3775 | 12.3455 | 97.3435 | 2.7356 | 6.0673 | 35.4756 | 158.0672 | 23.7188 | 304.5496 | 203.2487 | 324.6565 | 10.864 | 94.0326 | 3.4404 | 129 | 35.9062 | 33.0992 | 355.7731 | 0.24056
5008 | 909.9584 | 1.9021 | 37.7793 | 112.7475 | 68.1051 | 9.2968 | 93.4988 | 2.4413 | 5.6085 | 25.0234 | 131.6124 | 21.7886 | 230.7647 | 176.4581 | 311.896 | 10.9675 | 90.6752 | 3.4485 | 129 | 30.7638 | 32.9394 | 343.2159 | 0.18169
5009 | 877.896 | 1.6045 | 34.5811 | 107.5992 | 64.1692 | 8.5631 | 89.6822 | 1.4177 | 5.6155 | 17.706 | 113.4219 | 21.0641 | 183.8277 | 147.4884 | 287.3449 | 11.3312 | 88.995 | 3.5458 | 133 | 22.2022 | 31.4471 | 309.7311 | 0.14885
5010 | 850.1985 | 1.2734 | 34.1986 | 103.7983 | 62.0398 | 7.1441 | 75.9911 | 0.91502 | 5.351 | 14.6904 | 105.6851 | 17.3668 | 163.2269 | 123.5691 | 261.0897 | 10.4753 | 88.8227 | 3.5818 | 135 | 19.7433 | 30.219 | 268.8357 | 0.13553
5011 | 825.6709 | 1.5465 | 31.7006 | 102.4742 | 60.7078 | 7.338 | 55.4869 | 1.0896 | 5.3645 | 14.1212 | 101.1283 | 7.561 | 234.5701 | 107.2381 | 236.8034 | 10.8637 | 88.0702 | 3.5968 | 106 | 19.5804 | 30.1139 | 236.9545 | 0.044118
5012 | 801.6893 | 2.3324 | 30.5884 | 98.7177 | 58.6394 | 9.0655 | 47.8099 | 1.4243 | 5.6755 | 14.0372 | 95.6419 | 3.6719 | 270.1913 | 99.5738 | 220.2019 | 10.97 | 84.9999 | 3.4465 | 111 | 19.4725 | 28.0368 | 212.6813 | 0.017855
5013 | 775.5942 | 3.0316 | 35.8959 | 100.0041 | 60.1107 | 6.6455 | 47.5453 | 1.3661 | 5.6176 | 14.7672 | 89.3112 | 4.9382 | 212.3979 | 96.3879 | 213.9312 | 10.5993 | 80.8511 | 3.309 | 116 | 19.517 | 25.193 | 201.0829 | 0
5014 | 749.6415 | 2.5659 | 38.3542 | 101.9543 | 58.9552 | 6.3895 | 43.3002 | 1.2821 | 6.207 | 16.2844 | 85.8325 | 6.0825 | 173.2138 | 94.1449 | 222.0456 | 11.3923 | 78.604 | 3.4825 | 106 | 22.527 | 24.3643 | 196.6805 | 0
5015 | 729.802 | 1.5796 | 38.2688 | 102.6806 | 58.7046 | 7.3805 | 45.5787 | 1.3329 | 6.1762 | 16.8472 | 85.7884 | 6.5904 | 169.7643 | 90.6788 | 220.8377 | 12.4141 | 78.5355 | 3.2755 | 104 | 32.6278 | 24.2495 | 191.2905 | 0
5016 | 724.7669 | 1.2469 | 38.1623 | 106.1646 | 57.9647 | 6.8925 | 46.6793 | 1.5195 | 6.4468 | 15.8688 | 84.0847 | 6.5435 | 168.0717 | 86.8807 | 210.5045 | 13.9139 | 78.5418 | 2.8528 | 107 | 32.1298 | 24.1734 | 187.4665 | 0
5017 | 722.5659 | 1.156 | 37.214 | 107.1775 | 56.3241 | 6.6452 | 47.3462 | 1.4596 | 6.3325 | 14.6191 | 79.6271 | 6.4147 | 169.6391 | 85.8031 | 205.5346 | 15.4253 | 78.0832 | 2.4034 | 99 | 28.1002 | 24.1211 | 186.6745 | 0
5018 | 716.8557 | 1.3109 | 36.1322 | 108.1713 | 54.8375 | 7.3433 | 48.2361 | 1.3075 | 6.2447 | 14.2855 | 75.4251 | 9.3036 | 172.8435 | 91.9522 | 208.207 | 15.5478 | 77.649 | 2.2269 | 99 | 26.805 | 24.0948 | 187.0465 | 0
5019 | 711.3408 | 1.1877 | 36.1038 | 108.1027 | 55.2979 | 6.9221 | 47.8326 | 1.2962 | 5.9898 | 15.065 | 72.6838 | 17.6891 | 167.3396 | 99.7525 | 206.6018 | 15.2391 | 77.4691 | 2.2074 | 100 | 26.2722 | 23.8259 | 187.1404 | 0
5020 | 710.4385 | 1.5816 | 36.1969 | 106.6659 | 55.9764 | 6.6682 | 42.2708 | 1.2626 | 5.9283 | 18.2238 | 70.3778 | 17.5883 | 166.6348 | 100.8472 | 205.828 | 14.0663 | 77.1973 | 2.2011 | 97 | 26.1446 | 23.8456 | 189.6795 | 0
5021 | 717.7178 | 1.8725 | 43.219 | 104.4839 | 54.5307 | 6.6111 | 43.8952 | 1.0142 | 5.7997 | 21.142 | 67.3253 | 8.3682 | 167.8007 | 96.7838 | 203.2415 | 11.6686 | 76.3625 | 2.0232 | 89 | 23.39 | 23.864 | 202.6875 | 0.020576
5022 | 745.0457 | 1.2301 | 51.2934 | 103.5872 | 48.24 | 8.7179 | 51.7396 | 0.87266 | 5.5183 | 22.7343 | 75.6581 | 11.2082 | 173.2558 | 103.8144 | 197.9374 | 10.7588 | 75.8412 | 1.9134 | 112 | 21.2824 | 24.2386 | 233.7383 | 0.089221
5023 | 803.0558 | 1.4495 | 55.2121 | 105.0348 | 44.9808 | 12.3339 | 71.5533 | 1.201 | 5.2863 | 27.1898 | 100.4641 | 20.18 | 191.9152 | 130.6288 | 208.4066 | 10.9391 | 76.6577 | 2.1385 | 144 | 30.2084 | 30.7551 | 272.7205 | 0.156
5024 | 832.7424 | 1.6089 | 68.0727 | 114.8228 | 49.2778 | 14.6535 | 92.1639 | 2.1268 | 5.1448 | 30.6075 | 126.2624 | 23.4569 | 213.5905 | 158.6409 | 236.9377 | 12.1536 | 79.4839 | 2.7401 | 148 | 32.2672 | 33.5758 | 307.0866 | 0.27334
5025 | 885.68 | 1.4938 | 80.0444 | 121.8539 | 55.096 | 13.9181 | 101.5432 | 2.4373 | 5.2193 | 29.3453 | 144.9468 | 23.9435 | 227.3463 | 177.4533 | 266.1787 | 13.1676 | 83.8598 | 3.0019 | 150 | 31.0201 | 33.6725 | 331.3295 | 0.3047
5026 | 925.0413 | 2.2758 | 81.9034 | 124.553 | 53.071 | 14.7484 | 105.1033 | 2.3344 | 5.2563 | 28.2288 | 155.648 | 24.574 | 234.7901 | 188.3239 | 286.7673 | 13.9911 | 87.9213 | 3.0108 | 150 | 33.0325 | 32.1604 | 346.0363 | 0.29641
5027 | 933.9567 | 2.2152 | 81.3519 | 123.7729 | 53.8573 | 13.0647 | 111.4115 | 2.4448 | 5.4618 | 28.3298 | 159.4407 | 24.9662 | 251.7761 | 193.3242 | 305.452 | 14.7222 | 90.3851 | 3.1195 | 141 | 34.0192 | 31.9035 | 353.0798 | 0.25185
5028 | 918.099 | 2.1968 | 83.3287 | 122.2306 | 55.3529 | 13.6413 | 107.5991 | 2.6954 | 5.6035 | 28.163 | 160.336 | 24.0539 | 263.5454 | 196.977 | 305.8843 | 14.7726 | 91.4492 | 3.1825 | 144 | 33.1698 | 31.9938 | 352.6835 | 0.22705
5029 | 905.2113 | 2.4704 | 84.8674 | 123.7003 | 54.2914 | 15.6614 | 104.6916 | 2.6722 | 5.6117 | 30.1507 | 163.8903 | 23.7872 | 262.4066 | 201.6012 | 305.13 | 14.7494 | 91.3534 | 3.2081 | 141 | 33.0711 | 31.8448 | 357.4561 | 0.23908
5030 | 929.3865 | 2.3713 | 75.4937 | 124.1479 | 55.8968 | 15.4375 | 104.0309 | 2.6613 | 5.6772 | 33.0486 | 169.63 | 24.3173 | 260.3915 | 206.5865 | 306.1649 | 14.5682 | 90.0431 | 3.2231 | 139 | 35.1837 | 31.7507 | 365.7633 | 0.24625
5031 | 941.6239 | 2.4059 | 50.7277 | 117.4132 | 60.0436 | 12.3705 | 92.4939 | 2.4077 | 5.8603 | 29.4287 | 159.5435 | 23.1878 | 265.0334 | 196.5402 | 295.5173 | 12.7422 | 87.5431 | 3.2548 | 125 | 34.3609 | 31.5576 | 361.6891 | 0.22386
5032 | 917.1196 | 1.9832 | 36.8488 | 105.5507 | 62.5721 | 9.3511 | 78.341 | 2.0661 | 5.6703 | 20.7338 | 135.9286 | 21.8035 | 272.3218 | 169.2646 | 279.5497 | 11.4502 | 85.4432 | 3.3231 | 118 | 29.1876 | 31.4705 | 340.7264 | 0.22749
5033 | 880.4529 | 1.5039 | 34.3912 | 101.4191 | 61.9117 | 8.5856 | 80.9975 | 1.3392 | 5.5158 | 14.151 | 116.841 | 21.5534 | 265.1969 | 142.3068 | 261.329 | 10.6506 | 84.3921 | 3.3953 | 122 | 21.838 | 31.3983 | 304.0387 | 0.21656
5034 | 857.951 | 1.4944 | 34.0855 | 99.94 | 60.8284 | 7.8708 | 78.5554 | 1.1228 | 5.5615 | 12.1013 | 105.1273 | 17.785 | 230.398 | 120.2056 | 248.8032 | 10.0826 | 82.7455 | 3.4272 | 121 | 19.7616 | 30.0358 | 264.1416 | 0.19495
5035 | 832.3842 | 1.2007 | 33.5625 | 99.2576 | 62.3636 | 6.8333 | 53.4124 | 1.0076 | 5.5922 | 14.9119 | 100.4948 | 7.8039 | 206.4185 | 105.4978 | 244.3783 | 10.166 | 80.4541 | 3.4397 | 102 | 19.6807 | 29.6585 | 228.6314 | 0.10181
5036 | 796.2466 | 1.6103 | 34.3309 | 99.5549 | 60.7947 | 6.6117 | 44.3725 | 0.87992 | 5.5957 | 18.3754 | 96.704 | 3.9773 | 193.2427 | 98.4471 | 236.9387 | 10.4008 | 78.8204 | 3.4318 | 111 | 19.6918 | 26.8642 | 199.3245 | 0.029837
5037 | 773.1786 | 2.6386 | 39.8645 | 100.3535 | 56.5861 | 7.3881 | 47.5889 | 1.0733 | 5.7288 | 20.3451 | 88.1244 | 5.068 | 181.4367 | 93.7011 | 228.5987 | 10.4975 | 77.5116 | 3.2142 | 123 | 19.7327 | 24.4959 | 185.091 | 0
5038 | 764.1959 | 2.8496 | 41.8404 | 101.5638 | 55.2952 | 7.6814 | 48.4394 | 1.2735 | 5.9882 | 22.3279 | 79.6898 | 6.4738 | 169.0857 | 89.7929 | 222.1045 | 10.6146 | 76.0314 | 3.0842 | 112 | 22.4703 | 23.8602 | 181.7524 | 0
5039 | 738.6643 | 1.7685 | 41.643 | 104.4766 | 57.0151 | 6.8673 | 48.2389 | 1.4468 | 5.9628 | 22.5177 | 75.6335 | 6.5921 | 163.7281 | 87.6771 | 220.9746 | 11.7634 | 75.3837 | 3.0278 | 99 | 30.8489 | 23.8632 | 181.4638 | 0
5040 | 734.7321 | 1.4056 | 40.4335 | 108.4843 | 55.3547 | 7.3061 | 48.1433 | 1.4887 | 6.0758 | 21.2271 | 71.878 | 6.4515 | 160.4898 | 86.8911 | 224.2291 | 14.2328 | 75.2875 | 2.7274 | 102 | 27.3714 | 23.8908 | 182.6017 | 0
5041 | 724.7371 | 1.2303 | 39.6962 | 112.131 | 52.3625 | 7.6797 | 46.056 | 1.3574 | 6.1424 | 20.6428 | 67.7087 | 6.5719 | 158.8871 | 88.0598 | 227.8192 | 14.9397 | 75.6469 | 2.5107 | 96 | 23.4439 | 23.9854 | 183.9004 | 0
5042 | 715.8881 | 1.4837 | 39.5379 | 112.9007 | 47.8064 | 7.5513 | 42.1297 | 1.3171 | 6.1972 | 20.5897 | 65.5684 | 9.5422 | 164.7 | 94.5563 | 229.8806 | 15.4059 | 75.8495 | 2.3162 | 93 | 22.3561 | 23.8827 | 183.7275 | 0
5043 | 722.5265 | 1.3147 | 39.4871 | 112.5791 | 49.5166 | 6.8928 | 45.4363 | 1.2944 | 5.9501 | 21.3619 | 65.1239 | 18.1011 | 163.8649 | 99.5417 | 218.0302 | 14.8576 | 75.4179 | 2.2292 | 96 | 21.6906 | 23.7988 | 184.1375 | 0
5044 | 721.5456 | 1.516 | 39.2522 | 110.0043 | 50.7949 | 7.3453 | 47.4976 | 1.1606 | 5.7899 | 23.8104 | 63.8292 | 17.4306 | 173.7303 | 98.9333 | 207.875 | 13.6402 | 74.9481 | 2.1356 | 96 | 21.9903 | 23.7523 | 192.3751 | 0
5045 | 727.3277 | 1.2977 | 46.3397 | 106.7093 | 41.9977 | 6.9167 | 47.5131 | 0.94962 | 5.6538 | 26.2931 | 61.4514 | 9.9591 | 180.8832 | 96.8915 | 202.5056 | 11.2758 | 74.6356 | 1.9554 | 90 | 20.6097 | 23.9294 | 209.7266 | 0.0094922
5046 | 767.7135 | 1.0878 | 52.928 | 102.8875 | 34.0662 | 10.0517 | 49.9252 | 0.9529 | 5.2583 | 27.1064 | 69.9971 | 11.948 | 181.8363 | 105.6462 | 201.023 | 11.4207 | 74.5542 | 1.9263 | 104 | 20.5407 | 25.5567 | 236.4473 | 0.031656
5047 | 819.0781 | 1.7345 | 55.2938 | 103.016 | 37.483 | 14.9404 | 71.678 | 1.276 | 5.1683 | 27.3689 | 94.7887 | 22.5802 | 210.2383 | 132.1917 | 218.2674 | 10.5629 | 75.5494 | 2.2593 | 147 | 28.5077 | 30.2318 | 271.4075 | 0.087703
5048 | 841.6766 | 1.8461 | 67.0228 | 115.9808 | 41.9467 | 16.8767 | 95.4368 | 2.0442 | 6.7821 | 24.6753 | 121.2987 | 26.1701 | 211.2152 | 159.4063 | 248.4036 | 11.7986 | 79.8022 | 3.0584 | 137 | 34.2956 | 31.7748 | 307.7358 | 0.11318
5049 | 865.4999 | 1.9303 | 75.3126 | 121.1592 | 45.0439 | 14.9869 | 107.8703 | 2.344 | 9.4979 | 20.2059 | 138.521 | 24.4632 | 220.4566 | 178.5382 | 281.2629 | 12.3227 | 86.2587 | 3.3662 | 129 | 35.0941 | 31.6109 | 333.0913 | 0.13564
5050 | 903.2384 | 1.6077 | 75.7121 | 120.1613 | 52.0609 | 14.3806 | 118.0655 | 2.3072 | 7.2469 | 20.9428 | 150.5787 | 24.943 | 240.4483 | 190.58 | 301.1166 | 12.982 | 90.7306 | 3.4704 | 140 | 35.4686 | 31.2455 | 342.2869 | 0.27017
5051 | 925.6841 | 1.3185 | 79.1179 | 124.0023 | 56.6781 | 13.5214 | 120.2439 | 2.41 | 5.8981 | 24.0279 | 160.281 | 24.8531 | 245.1325 | 195.6897 | 308.9868 | 13.4931 | 92.547 | 3.6029 | 135 | 35.4558 | 32.0167 | 345.4741 | 0.29472
5052 | 915.9491 | 1.5875 | 81.0611 | 124.8701 | 61.8764 | 13.9362 | 120.3254 | 2.8745 | 5.8067 | 28.8457 | 165.0302 | 24.7528 | 246.5746 | 197.4924 | 306.0278 | 12.8767 | 93.0777 | 3.7886 | 136 | 34.4312 | 32.1 | 344.1192 | 0.31891
5053 | 904.4733 | 2.0152 | 80.6012 | 126.1757 | 66.1408 | 15.0092 | 119.1025 | 2.7542 | 5.4568 | 32.7528 | 166.9917 | 25.0364 | 245.6193 | 200.6095 | 304.0004 | 13.2525 | 92.6395 | 3.8553 | 172 | 29.677 | 32.1465 | 344.1353 | 0.27812
5054 | 913.6741 | 2.1852 | 73.8652 | 135.2473 | 66.3702 | 14.4635 | 113.4762 | 2.1978 | 5.5658 | 30.6933 | 167.8403 | 24.5202 | 238.6061 | 203.2559 | 305.8128 | 13.5534 | 91.8547 | 3.8731 | 174 | 39.0736 | 31.7017 | 344.4031 | 0.25478
5055 | 915.4266 | 1.9337 | 52.8124 | 113.1015 | 64.7686 | 11.4835 | 99.7653 | 1.8603 | 5.7234 | 25.4543 | 155.6703 | 23.263 | 247.0598 | 191.7246 | 300.1019 | 12.3495 | 90.3024 | 3.7511 | 128 | 33.7833 | 31.0001 | 342.1153 | 0.24393
5056 | 879.9312 | 1.4446 | 37.4634 | 101.4521 | 63.9326 | 8.3619 | 81.639 | 1.5106 | 5.4133 | 18.6479 | 133.3948 | 22.0465 | 247.9985 | 163.1515 | 284.0203 | 11.4996 | 88.1636 | 3.409 | 119 | 26.307 | 30.3873 | 319.0621 | 0.11137
5057 | 837.5671 | 1.0607 | 33.9066 | 99.4324 | 61.7069 | 7.5068 | 79.3026 | 1.5152 | 5.4669 | 13.015 | 117.0864 | 21.92 | 242.088 | 133.1613 | 271.8339 | 11.3921 | 85.962 | 3.2301 | 117 | 20.9105 | 29.8935 | 272.507 | 0.086238
5058 | 806.2007 | 0.92865 | 33.3904 | 98.2481 | 58.1957 | 6.9153 | 74.0114 | 1.1535 | 5.5934 | 11.3488 | 103.9308 | 18.1759 | 224.1515 | 112.2766 | 258.9941 | 11.0604 | 82.7063 | 3.2282 | 119 | 19.5697 | 29.3682 | 234.2738 | 0.063581
5059 | 775.7512 | 0.86047 | 32.3635 | 97.6126 | 56.6255 | 7.3243 | 51.9192 | 0.89439 | 5.4927 | 14.2545 | 92.2051 | 8.2362 | 205.435 | 100.1797 | 240.5284 | 10.974 | 79.3422 | 3.2756 | 103 | 19.2054 | 29.4358 | 211.04 | 0.021733
5060 | 752.9136 | 1.8246 | 31.6295 | 97.4955 | 58.61 | 6.9098 | 42.2924 | 0.88456 | 5.4127 | 17.6284 | 85.215 | 4.3585 | 186.9161 | 93.7263 | 238.6857 | 11.3032 | 77.6176 | 3.0082 | 99 | 18.1812 | 26.3846 | 196.2615 | 0.0085912
5061 | 752.2135 | 2.9312 | 31.6407 | 99.5336 | 57.4711 | 7.4303 | 45.3546 | 1.1399 | 5.4752 | 20.1911 | 82.4847 | 5.6875 | 171.0081 | 88.6357 | 231.8644 | 11.6961 | 76.8338 | 2.6166 | 99 | 17.7953 | 23.9332 | 189.1066 | 0
5062 | 744.4973 | 2.6562 | 31.7257 | 100.6968 | 55.5961 | 8.237 | 47.2488 | 1.3393 | 6.0811 | 22.6229 | 81.2264 | 6.7482 | 162.8111 | 85.6337 | 217.8787 | 11.4051 | 75.9521 | 2.414 | 95 | 20.7931 | 23.4836 | 186.0864 | 0
5063 | 731.4094 | 1.5749 | 31.85 | 102.187 | 56.8935 | 7.1012 | 47.2702 | 1.5462 | 5.9385 | 24.9691 | 79.3766 | 7.3199 | 158.7482 | 84.7784 | 207.6484 | 12.93 | 75.3735 | 2.3762 | 97 | 29.4306 | 23.5449 | 181.9597 | 0
5064 | 736.5236 | 1.1624 | 32.365 | 100.7618 | 55.5745 | 7.3879 | 47.3728 | 1.4369 | 5.9252 | 26.2432 | 76.9325 | 7.1732 | 154.0975 | 85.0814 | 204.8613 | 14.4864 | 75.1314 | 2.4368 | 98 | 27.3565 | 23.361 | 180.8131 | 0
5065 | 720.0634 | 1.1043 | 32.0572 | 100.0268 | 54.6912 | 6.8701 | 42.8992 | 1.3087 | 6.0068 | 25.3839 | 74.2132 | 6.9721 | 161.7455 | 88.7196 | 207.6285 | 15.5768 | 74.9672 | 2.5202 | 99 | 24.607 | 23.4029 | 182.9949 | 0
5066 | 714.0142 | 1.0703 | 31.7607 | 100.2745 | 54.3123 | 6.6746 | 44.3036 | 1.3027 | 6.0305 | 24.7887 | 71.2123 | 6.767 | 167.2206 | 96.2536 | 205.819 | 16.3016 | 74.867 | 2.4546 | 100 | 23.2937 | 23.4342 | 183.05 | 0
5067 | 721.7117 | 1.1692 | 31.7483 | 100.1252 | 52.7881 | 7.3761 | 47.2992 | 1.2942 | 5.9853 | 25.4817 | 69.1137 | 6.6017 | 179.9152 | 100.4089 | 206.1146 | 15.6092 | 74.5824 | 2.4069 | 94 | 22.8688 | 23.2522 | 182.6361 | 0
5068 | 710.5202 | 1.7413 | 31.6454 | 101.6861 | 51.8402 | 6.8982 | 47.9774 | 1.2512 | 6.001 | 28.1558 | 67.2616 | 6.2224 | 164.8583 | 98.8768 | 203.3794 | 14.5381 | 74.0716 | 2.2831 | 92 | 22.642 | 23.3273 | 182.1276 | 0
5069 | 709.6639 | 1.4535 | 31.3624 | 101.6951 | 38.6202 | 6.6088 | 47.129 | 1.0025 | 5.6305 | 30.7619 | 64.3777 | 4.6892 | 152.3417 | 94.498 | 197.9882 | 12.2628 | 73.3663 | 1.9993 | 91 | 21.8331 | 23.4936 | 182.1932 | 0.021911
5070 | 716.9092 | 1.1713 | 31.5434 | 99.5995 | 37.6051 | 7.3682 | 41.0812 | 1.1689 | 5.1767 | 31.4905 | 70.559 | 4.1342 | 175.492 | 87.2103 | 198.3392 | 11.006 | 72.7546 | 1.8879 | 91 | 18.8444 | 24.0361 | 182.8593 | 0.034186
5071 | 723.8613 | 0.97438 | 31.5452 | 97.1984 | 49.8881 | 6.9877 | 42.3756 | 1.0598 | 4.8997 | 31.044 | 91.1087 | 5.9499 | 172.5475 | 81.2015 | 197.8968 | 11.0243 | 72.9864 | 2.1514 | 96 | 18.9647 | 24.2511 | 184.6237 | 0.0567
5072 | 727.6366 | 0.87073 | 31.3059 | 96.8391 | 53.1388 | 6.608 | 45.5627 | 0.95123 | 4.8442 | 27.6142 | 108.6339 | 14.8233 | 189.9895 | 79.4505 | 214.4041 | 11.0061 | 73.2925 | 2.773 | 98 | 20.7571 | 27.9705 | 188.8613 | 0.20715
5073 | 746.647 | 0.82189 | 31.0954 | 98.3428 | 51.3269 | 7.3303 | 47.0764 | 0.95728 | 4.8703 | 23.5948 | 116.8276 | 19.0759 | 154.359 | 81.4347 | 235.4272 | 11.0361 | 73.3872 | 3.109 | 96 | 18.297 | 30.4266 | 193.2863 | 0.21827
5074 | 767.6031 | 1.0534 | 31.2795 | 97.7433 | 54.4496 | 8.2615 | 46.5968 | 0.91231 | 5.1256 | 22.3791 | 124.5459 | 19.2113 | 174.8742 | 84.764 | 242.6122 | 11.0406 | 73.9684 | 3.3211 | 99 | 18.6654 | 30.9909 | 195.6158 | 0.28487
5075 | 768.7996 | 1.7857 | 33.1262 | 98.8268 | 59.422 | 7.95 | 44.7001 | 0.87291 | 5.4928 | 22.6948 | 130.919 | 16.0839 | 162.961 | 87.8245 | 246.2517 | 10.9365 | 74.616 | 3.5396 | 97 | 18.1159 | 30.3437 | 195.8556 | 0.27838
5076 | 772.3448 | 1.6547 | 34.6782 | 100.0356 | 61.7806 | 7.5392 | 42.1961 | 0.88808 | 5.6402 | 23.201 | 135.0873 | 15.0254 | 173.8738 | 89.1015 | 235.7937 | 10.9037 | 75.5177 | 3.6425 | 97 | 18.1487 | 29.6054 | 194.6371 | 0.26316
5077 | 775.764 | 1.5153 | 35.8934 | 100.7389 | 60.2603 | 7.6443 | 44.0616 | 0.87298 | 5.4212 | 23.0113 | 139.7666 | 15.5252 | 198.05 | 89.6421 | 229.1804 | 11.1602 | 76.1037 | 3.6463 | 102 | 17.3872 | 29.481 | 195.9219 | 0.27453
5078 | 752.628 | 1.8024 | 35.4851 | 98.8533 | 60.3785 | 7.6047 | 46.5589 | 1.1661 | 5.2794 | 21.6058 | 144.0095 | 17.8123 | 133.9602 | 90.9619 | 231.8238 | 11.1909 | 76.1164 | 3.5984 | 101 | 16.5642 | 28.8521 | 196.2228 | 0.27818
5079 | 734.1135 | 1.9551 | 33.7257 | 97.9083 | 61.7463 | 6.8605 | 46.8321 | 1.039 | 5.4513 | 18.0908 | 131.7093 | 16.9012 | 149.1965 | 92.2728 | 231.0808 | 11.2643 | 75.7434 | 3.3328 | 102 | 16.3575 | 28.5777 | 190.7329 | 0.28728
5080 | 734.2328 | 2.2668 | 32.9797 | 98.2431 | 59.0595 | 7.354 | 46.7794 | 0.86379 | 5.4102 | 14.7738 | 106.3396 | 8.4505 | 165.7663 | 93.8818 | 224.6556 | 11.1356 | 74.8517 | 3.2455 | 106 | 16.4081 | 28.8927 | 185.3693 | 0.19193
5081 | 728.0405 | 2.0083 | 32.875 | 99.2617 | 58.6044 | 6.8268 | 47.4073 | 0.86492 | 5.473 | 13.8441 | 90.6984 | 4.3163 | 194.3576 | 93.8352 | 219.8125 | 11.0445 | 74.1587 | 3.2578 | 102 | 15.6326 | 29.4748 | 182.2645 | 0.19073
5082 | 725.6753 | 1.3128 | 32.3595 | 99.8605 | 59.5185 | 7.3362 | 46.8001 | 0.94807 | 5.5232 | 13.8741 | 81.4907 | 4.0361 | 148.4979 | 90.7969 | 231.8075 | 11.1159 | 73.5982 | 3.2157 | 100 | 16.2069 | 29.4111 | 180.9936 | 0.14317
5083 | 730.6558 | 1.1183 | 32.2046 | 98.4451 | 60.5553 | 6.9297 | 46.4124 | 1.4477 | 5.2808 | 13.9044 | 73.9892 | 3.8693 | 143.6036 | 88.1915 | 246.9431 | 11.1885 | 73.6516 | 3.2227 | 121 | 15.1691 | 28.959 | 179.6206 | 0.075896
5084 | 717.7459 | 1.3472 | 33.0693 | 97.5208 | 56.5332 | 8.0925 | 48.1277 | 1.2546 | 5.3682 | 13.0711 | 70.827 | 3.8344 | 157.7851 | 87.3707 | 247.7745 | 11.1527 | 74.3034 | 3.024 | 116 | 14.8669 | 28.7798 | 178.8944 | 0.025406
5085 | 719.9645 | 2.7042 | 38.1622 | 97.8908 | 52.7686 | 7.831 | 48.3891 | 1.2507 | 5.2687 | 12.028 | 69.0738 | 4.0597 | 180.1547 | 88.5474 | 233.6617 | 11.0557 | 74.6285 | 2.4869 | 101 | 14.9096 | 25.5779 | 179.1902 | 0
5086 | 712.5164 | 2.8468 | 39.5468 | 99.6318 | 43.8364 | 6.919 | 48.6316 | 1.5007 | 5.3713 | 13.7017 | 68.1643 | 5.8048 | 200.6421 | 89.3797 | 216.5147 | 11.3867 | 75.2788 | 2.3071 | 97 | 14.8741 | 24.4888 | 178.7638 | 0
5087 | 716.8053 | 1.6463 | 39.1566 | 100.9664 | 45.4664 | 6.671 | 43.8309 | 1.4484 | 5.9471 | 16.1615 | 67.9671 | 6.8151 | 169.0762 | 91.3549 | 215.9815 | 12.4362 | 75.958 | 2.1891 | 97 | 14.8424 | 24.0591 | 178.8887 | 0
5088 | 731.9218 | 1.4615 | 38.9901 | 103.9968 | 50.4295 | 7.3315 | 45.1483 | 1.3749 | 5.8909 | 16.5908 | 67.0051 | 6.6529 | 211.2666 | 115.0133 | 218.0538 | 14.4811 | 75.7 | 2.0317 | 102 | 14.7587 | 23.6967 | 179.7477 | 0
5089 | 727.6888 | 1.288 | 38.9688 | 105.8742 | 47.2722 | 8.9983 | 47.4113 | 1.3652 | 5.8897 | 16.4313 | 66.2932 | 6.5565 | 175.9032 | 144.5091 | 224.5976 | 15.9635 | 75.0583 | 1.9766 | 99 | 14.8152 | 23.721 | 180.8304 | 0
5090 | 716.761 | 1.1737 | 38.7764 | 106.0132 | 36.3073 | 6.7038 | 48.2313 | 1.3465 | 6.2341 | 16.3327 | 66.0211 | 6.395 | 206.1807 | 158.7617 | 222.2141 | 15.603 | 74.7826 | 1.9504 | 96 | 14.8288 | 23.5445 | 181.8722 | 0
5091 | 702.1111 | 1.1825 | 38.7077 | 105.1354 | 29.069 | 6.3987 | 48.4091 | 1.3592 | 6.3117 | 16.2364 | 66.1584 | 6.2294 | 197.7454 | 165.4459 | 211.0295 | 15.626 | 74.9647 | 1.9355 | 95 | 14.8049 | 23.1854 | 180.8198 | 0
5092 | 682.3783 | 1.8603 | 38.4104 | 102.6827 | 31.8077 | 8.0549 | 47.5925 | 1.2471 | 6.2534 | 15.5264 | 65.3965 | 5.6566 | 175.0137 | 171.4484 | 204.0582 | 14.6804 | 74.8146 | 1.9289 | 93 | 14.7681 | 23.1637 | 179.9313 | 0
5093 | 681.8736 | 1.944 | 37.4836 | 97.8978 | 42.1899 | 8.445 | 41.9369 | 1.3251 | 6.4851 | 13.621 | 62.8558 | 4.2525 | 217.8335 | 166.9216 | 192.7516 | 12.3517 | 74.0633 | 1.9645 | 89 | 14.7032 | 23.2041 | 177.8991 | 0.040028
5094 | 691.5433 | 1.1653 | 36.8341 | 96.882 | 52.8557 | 6.5565 | 44.1498 | 1.1102 | 5.6895 | 11.9878 | 69.5954 | 3.7578 | 201.5959 | 130.2713 | 191.9028 | 11.2265 | 73.6033 | 1.9659 | 94 | 13.7509 | 23.0223 | 175.8433 | 0.070212
5095 | 713.2339 | 0.80956 | 31.594 | 96.977 | 56.9849 | 7.8134 | 47.2012 | 0.94904 | 5.047 | 11.5088 | 92.5004 | 3.752 | 139.0535 | 92.7885 | 193.554 | 10.7722 | 73.506 | 2.1824 | 94 | 15.5831 | 22.8635 | 176.1361 | 0.16419
5096 | 718.03 | 0.99096 | 29.1856 | 96.8943 | 62.3614 | 7.1428 | 47.1284 | 0.99478 | 6.6856 | 11.478 | 112.6788 | 7.1639 | 168.8437 | 84.3073 | 212.082 | 11.0578 | 73.4411 | 2.7675 | 92 | 14.9559 | 23.0813 | 175.9512 | 0.19794
5097 | 723.1849 | 0.82722 | 29.1861 | 96.9248 | 66.0749 | 6.6571 | 47.0797 | 0.9988 | 9.5024 | 12.084 | 118.2954 | 8.7309 | 157.193 | 88.542 | 235.0844 | 10.9795 | 73.589 | 3.016 | 94 | 14.5973 | 24.0298 | 176.8398 | 0.25914
5098 | 743.7088 | 0.7651 | 29.384 | 97.258 | 63.7582 | 7.8956 | 46.2433 | 0.92779 | 7.0579 | 13.27 | 118.9042 | 5.96 | 157.1892 | 93.6258 | 238.2503 | 10.9258 | 73.6735 | 3.0444 | 99 | 13.7392 | 24.3588 | 179.107 | 0.2464
5099 | 753.2106 | 0.92537 | 31.0999 | 98.8906 | 56.7304 | 7.9064 | 43.8935 | 0.89581 | 5.4854 | 14.4628 | 122.8568 | 5.548 | 150.3561 | 95.9395 | 237.7189 | 11.1351 | 73.3449 | 3.0601 | 96 | 15.4994 | 24.2799 | 181.5622 | 0.22592
5100 | 754.28 | 0.88695 | 31.9284 | 103.3764 | 51.8346 | 7.6594 | 42.9697 | 0.90755 | 5.4019 | 14.945 | 130.6083 | 7.9619 | 174.8038 | 93.3331 | 230.2833 | 10.9293 | 73.3774 | 3.1656 | 97 | 14.9315 | 23.9784 | 181.7256 | 0.17903
5101 | 751.0918 | 1.107 | 31.4278 | 101.1334 | 47.3498 | 7.6709 | 44.2456 | 1.1909 | 5.0933 | 13.541 | 136.7989 | 7.8638 | 212.9 | 90.6278 | 221.1528 | 11.0432 | 74.7248 | 3.3029 | 100 | 14.4892 | 23.1709 | 179.5312 | 0.21043
5102 | 744.3688 | 1.5417 | 30.9221 | 98.486 | 46.4761 | 6.8904 | 47.8669 | 1.0781 | 4.9789 | 12.1026 | 139.46 | 6.1547 | 192.9911 | 91.4232 | 225.1832 | 11.1396 | 77.6798 | 3.4848 | 99 | 14.0089 | 22.7727 | 177.9044 | 0.26072
5103 | 750.0815 | 1.6116 | 29.9383 | 97.3574 | 48.654 | 6.6111 | 48.2777 | 0.8802 | 4.7989 | 12.6704 | 125.6965 | 6.8003 | 186.6034 | 92.5535 | 220.8206 | 10.8942 | 80.502 | 3.364 | 112 | 13.9273 | 22.714 | 178.2127 | 0.21247
5104 | 753.5414 | 1.3756 | 29.3892 | 97.1562 | 45.0566 | 7.9944 | 47.1832 | 0.88164 | 4.8311 | 13.6229 | 100.1266 | 5.1482 | 191.0746 | 93.7287 | 204.4065 | 11.1047 | 80.3931 | 3.227 | 112 | 15.2848 | 22.765 | 178.4271 | 0.16651
5105 | 744.9343 | 1.1813 | 29.3198 | 97.8277 | 35.0549 | 7.2092 | 46.6277 | 0.89461 | 4.8921 | 13.3641 | 86.1719 | 4.2504 | 270.7442 | 93.4195 | 198.4634 | 11.066 | 78.5351 | 3.3846 | 101 | 13.9656 | 22.9228 | 178.3437 | 0.10506
5106 | 729.6949 | 1.6319 | 28.9727 | 97.5887 | 30.0611 | 6.6477 | 47.6567 | 0.9348 | 4.8949 | 10.9415 | 80.3396 | 4.1453 | 179.9438 | 90.5473 | 197.5048 | 10.8284 | 77.416 | 3.4848 | 100 | 12.9186 | 22.8824 | 178.2713 | 0.075441
5107 | 722.4994 | 1.2963 | 29.0702 | 96.7201 | 40.8425 | 6.6192 | 47.3255 | 0.90986 | 5.0276 | 8.2654 | 72.39 | 4.016 | 217.6539 | 87.8484 | 195.9227 | 11.0234 | 77.6761 | 3.4625 | 104 | 12.6735 | 22.8714 | 177.8194 | 0.063171
5108 | 719.9608 | 1.5961 | 30.2461 | 96.5462 | 49.6502 | 6.682 | 46.3217 | 1.0509 | 5.0987 | 7.5461 | 64.8293 | 4.0118 | 204.7369 | 86.9831 | 202.6745 | 10.9737 | 78.2401 | 2.9927 | 107 | 12.6093 | 23.0066 | 178.2161 | 0.022536
5109 | 716.887 | 2.8047 | 35.7238 | 97.8312 | 53.4475 | 6.6597 | 43.377 | 1.3122 | 5.2534 | 7.7198 | 62.4024 | 6.2613 | 249.3266 | 87.2842 | 206.1938 | 11.4226 | 77.9192 | 2.2207 | 96 | 12.4495 | 23.0992 | 180.2582 | 0
5110 | 703.2646 | 3.237 | 38.1739 | 103.9718 | 55.3244 | 7.3471 | 44.8581 | 1.3751 | 5.4063 | 9.5359 | 63.4598 | 13.9159 | 161.3027 | 86.2485 | 198.1654 | 11.5 | 75.7454 | 2.1735 | 92 | 12.6065 | 23.2229 | 181.306 | 0
5111 | 703.5588 | 2.1692 | 38.2724 | 107.3763 | 56.0191 | 8.243 | 52.1299 | 1.3665 | 5.8389 | 12.0008 | 64.7225 | 16.9481 | 200.5569 | 84.9867 | 196.3351 | 12.2794 | 72.9979 | 2.2447 | 93 | 12.7897 | 23.0844 | 180.7323 | 0
5112 | 710.3105 | 1.4349 | 38.2056 | 107.5219 | 64.5378 | 7.814 | 53.6029 | 1.3629 | 5.9826 | 12.7264 | 65.2147 | 16.9061 | 178.2681 | 90.1837 | 196.3702 | 14.8325 | 72.5674 | 2.2239 | 98 | 12.8565 | 22.907 | 181.2652 | 0
5113 | 719.0745 | 1.3241 | 38.2013 | 107.8701 | 66.9763 | 6.9727 | 51.826 | 1.3616 | 5.9427 | 12.8128 | 65.0573 | 17.0066 | 154.9027 | 98.5149 | 201.6526 | 15.7928 | 74.7216 | 2.2175 | 95 | 12.955 | 22.9321 | 181.2264 | 0
5114 | 706.8147 | 1.285 | 37.9467 | 108.0806 | 66.6664 | 8.0072 | 52.6693 | 1.3548 | 5.7318 | 13.6501 | 64.3367 | 15.6875 | 212.1547 | 106.4932 | 201.8285 | 15.7186 | 76.5906 | 2.2514 | 96 | 12.9313 | 22.9652 | 181.8594 | 0
5115 | 691.2217 | 1.3196 | 38.0538 | 107.8597 | 65.9527 | 8.5204 | 53.8606 | 1.3782 | 5.7493 | 15.3169 | 63.7952 | 16.2316 | 126.2537 | 112.5698 | 201.065 | 15.7253 | 75.7397 | 2.2818 | 96 | 12.8857 | 22.9611 | 185.516 | 0
5116 | 696.9926 | 1.6619 | 38.4418 | 106.7547 | 67.6233 | 7.2212 | 54.8476 | 1.5344 | 5.677 | 18.3234 | 62.6357 | 13.8927 | 163.4819 | 114.1468 | 199.4673 | 14.6479 | 73.9696 | 2.1915 | 95 | 13.1405 | 22.7943 | 200.7626 | 0
5117 | 710.781 | 2.0626 | 47.1256 | 104.9272 | 68.7211 | 6.6343 | 55.7946 | 1.2351 | 5.333 | 20.8506 | 60.5905 | 7.891 | 154.4071 | 110.1767 | 193.3629 | 12.1503 | 73.2293 | 1.991 | 92 | 13.0592 | 22.8815 | 223.3699 | 0
5118 | 726.472 | 2.1745 | 59.0449 | 103.2187 | 65.7692 | 10.7532 | 61.5211 | 0.95834 | 4.9745 | 22.0217 | 70.7521 | 11.5071 | 166.495 | 111.9528 | 198.8461 | 11.499 | 73.4869 | 1.9421 | 112 | 16.4875 | 23.98 | 253.1044 | 0.046679
5119 | 785.7381 | 2.2725 | 64.9492 | 83.6693 | 66.0719 | 12.4864 | 83.0526 | 1.369 | 5.034 | 24.3431 | 99.9877 | 20.7759 | 179.8864 | 135.9929 | 215.7358 | 12.6775 | 74.9324 | 2.2004 | 129 | 27.7304 | 30.2157 | 302.357 | 0.18202
5120 | 825.1562 | 2.2494 | 71.5127 | 134.972 | 66.3125 | 14.5918 | 104.7528 | 2.0402 | 6.7227 | 21.1031 | 133.0568 | 24.2881 | 309.6982 | 165.0678 | 250.1729 | 13.8077 | 79.323 | 2.9223 | 149 | 29.5684 | 33.1492 | 354.8895 | 0.21528
5121 | 828.771 | 1.976 | 77.04 | 128.3431 | 65.596 | 17.1188 | 115.5145 | 2.331 | 9.4258 | 13.492 | 154.066 | 24.3502 | 181.1115 | 181.9597 | 293.6437 | 14.5531 | 86.2853 | 3.4732 | 157 | 28.1534 | 32.2652 | 382.9186 | 0.21333
5122 | 838.3247 | 1.6036 | 78.4039 | 125.283 | 64.9843 | 16.609 | 122.9801 | 2.864 | 6.7351 | 10.7066 | 157.5776 | 25.7417 | 237.3061 | 191.456 | 317.7608 | 15.0026 | 92.7876 | 3.8644 | 184 | 32.7646 | 31.5604 | 388.4277 | 0.21399
5123 | 855.8699 | 1.849 | 80.3848 | 129.19 | 59.5269 | 16.1631 | 126.3143 | 3.6374 | 5.1979 | 11.2338 | 157.6974 | 27.4791 | 191.0971 | 196.6973 | 329.1276 | 15.3294 | 95.781 | 4.156 | 164 | 34.7909 | 32.3746 | 392.1285 | 0.26975
5124 | 857.787 | 2.204 | 73.6282 | 130.3142 | 55.2239 | 14.1693 | 124.7217 | 3.6069 | 5.3777 | 13.3104 | 165.8916 | 27.9243 | 288.2882 | 198.1944 | 328.4697 | 15.7346 | 96.0297 | 4.2103 | 168 | 33.1211 | 33.0347 | 394.9046 | 0.19553
5125 | 877.8269 | 2.6658 | 48.2062 | 132.3204 | 54.112 | 13.3369 | 119.9616 | 3.4323 | 5.419 | 17.8102 | 176.05 | 25.6061 | 208.1331 | 204.2531 | 333.6499 | 15.9904 | 97.1101 | 4.3179 | 152 | 31.5542 | 33.1581 | 394.0761 | 0.26054
5126 | 901.8662 | 2.4085 | 48.2062 | 134.4007 | 56.027 | 14.0145 | 118.359 | 3.5115 | 5.3444 | 22.0598 | 179.767 | 25.5238 | 259.3636 | 210.6067 | 343.0313 | 16.5165 | 98.8491 | 4.4923 | 152 | 31.2689 | 32.8637 | 391.3954 | 0.26999
5127 | 893.6689 | 2.6137 | 36.7052 | 122.5697 | 55.9448 | 14.9905 | 110.095 | 2.9422 | 5.3412 | 22.6617 | 166.8263 | 23.3803 | 300.4245 | 197.5712 | 335.0976 | 16.5973 | 97.7586 | 4.6767 | 151 | 28.9979 | 32.4737 | 386.0314 | 0.19918
5128 | 862.3252 | 2.0323 | 44.703 | 94.9147 | 55.7003 | 10.9369 | 100.9211 | 2.1168 | 5.3571 | 19.2243 | 143.6201 | 21.4385 | 214.084 | 167.1252 | 312.2656 | 15.1273 | 93.9729 | 4.7641 | 122 | 26.1895 | 32.3714 | 362.5262 | 0.087156
5129 | 833.3216 | 1.1445 | 47.9863 | 83.4451 | 46.6717 | 9.4398 | 96.5371 | 1.6052 | 5.5194 | 13.7705 | 123.8116 | 21.048 | 305.93 | 134.7677 | 289.9147 | 14.0599 | 90.7491 | 4.582 | 127 | 20.0925 | 31.3914 | 313.0294 | 0.078009
5130 | 799.4893 | 1.0186 | 48.1383 | 62.2613 | 46.3627 | 9.4615 | 83.8026 | 1.361 | 5.4511 | 10.2543 | 107.5488 | 17.2409 | 255.703 | 109.0771 | 284.0249 | 13.9124 | 88.54 | 4.47 | 131 | 17.6835 | 30.2489 | 263.9173 | 0.12188
5131 | 773.0833 | 1.301 | 63.495 | 89.8682 | 52.217 | 8.8341 | 64.9661 | 1.0891 | 5.5199 | 9.9328 | 95.7596 | 7.3528 | 290.0063 | 95.4791 | 279.8012 | 13.7492 | 85.8851 | 4.132 | 120 | 17.5 | 29.9759 | 227.8702 | 0.079805
5132 | 757.5478 | 1.9749 | 36.6819 | 82.5023 | 43.8223 | 7.8483 | 55.8013 | 0.93564 | 5.1234 | 10.3903 | 88.3656 | 3.6011 | 191.7408 | 91.7566 | 261.7124 | 13.1669 | 82.7426 | 3.4589 | 114 | 16.1935 | 27.0476 | 201.0479 | 0.024701
5133 | 730.5664 | 5.1863 | 44.5754 | 84.5864 | 47.5188 | 6.1468 | 54.7094 | 1.1638 | 5.0263 | 10.685 | 80.7252 | 4.4085 | 220.5123 | 90.0999 | 242.015 | 13.2127 | 80.4953 | 2.6295 | 105 | 15.3793 | 24.8234 | 186.1897 | 0
5134 | 706.8678 | 3.8921 | 48.2295 | 90.7391 | 55.3391 | 6.4341 | 54.8624 | 1.451 | 5.5227 | 12.4962 | 74.9954 | 5.5963 | 210.1217 | 89.6021 | 222.8242 | 13.5556 | 79.7793 | 2.7093 | 98 | 18.0704 | 25.1218 | 186.5891 | 0
5135 | 685.1589 | 1.797 | 63.3348 | 92.735 | 57.5982 | 6.627 | 59.5246 | 1.5735 | 5.894 | 14.5091 | 74.2274 | 6.0076 | 200.095 | 89.7818 | 224.2511 | 14.1011 | 79.5295 | 2.5789 | 97 | 22.8424 | 24.5439 | 191.1323 | 0
5136 | 681.3074 | 1.2571 | 36.7052 | 92.1809 | 65.4386 | 7.3257 | 59.0785 | 1.4388 | 6.1818 | 14.9353 | 74.0715 | 5.9991 | 212.325 | 89.318 | 226.396 | 16.4901 | 78.5782 | 2.6504 | 98 | 21.3449 | 23.7922 | 185.882 | 0
5137 | 674.0416 | 1.097 | 37.0392 | 91.1203 | 68.9238 | 6.9496 | 57.4802 | 1.3629 | 5.9383 | 14.7203 | 72.9569 | 5.8474 | 211.1415 | 89.2854 | 233.8758 | 17.4598 | 77.6421 | 2.7083 | 95 | 20.1072 | 23.5338 | 181.0559 | 0
5138 | 664.2777 | 1.096 | 37.5247 | 75.3291 | 67.6371 | 8.7279 | 54.332 | 1.3627 | 5.979 | 14.6352 | 72.0936 | 8.0702 | 181.192 | 93.5088 | 238.4176 | 17.5109 | 77.652 | 2.4821 | 96 | 19.7542 | 23.617 | 181.4645 | 0
5139 | 668.8124 | 1.0977 | 37.3619 | 104.1168 | 67.6123 | 8.7751 | 56.3027 | 1.3877 | 5.8905 | 15.331 | 71.3978 | 14.4515 | 194.2937 | 98.8275 | 225.7562 | 17.683 | 78.0198 | 2.4019 | 95 | 19.7106 | 23.5512 | 183.7378 | 0
5140 | 670.6584 | 1.5055 | 37.5195 | 77.9434 | 68.32 | 8.5916 | 60.796 | 1.3569 | 5.524 | 18.5243 | 69.9965 | 14.0066 | 216.454 | 100.2492 | 217.3559 | 16.6785 | 77.911 | 2.4282 | 96 | 19.8838 | 23.5149 | 196.1149 | 0
5141 | 672.5687 | 2.2878 | 48.7801 | 112.672 | 70.4694 | 6.5105 | 57.5244 | 1.3878 | 5.3285 | 21.469 | 67.6892 | 8.1328 | 199.5332 | 97.76 | 213.9467 | 14.2524 | 77.4881 | 2.2283 | 91 | 18.6251 | 23.812 | 217.6 | 0
5142 | 702.5258 | 2.281 | 59.6745 | 113.3613 | 68.0992 | 7.8195 | 61.7542 | 1.1476 | 5.2849 | 23.9215 | 78.109 | 11.7867 | 227.9919 | 106.2997 | 214.4212 | 12.7885 | 77.1141 | 2.1118 | 110 | 18.8547 | 24.0027 | 248.3692 | 0.039462
5143 | 748.2685 | 2.5215 | 69.465 | 105.5731 | 62.9198 | 12.7772 | 83.7544 | 1.1597 | 5.0624 | 27.1228 | 107.9748 | 20.8103 | 217.8103 | 136.6065 | 217.8542 | 13.3879 | 77.9585 | 2.3666 | 138 | 25.1364 | 29.773 | 296.302 | 0.1064
5144 | 783.3456 | 2.8726 | 76.396 | 151.9445 | 61.8135 | 15.4811 | 104.5452 | 1.9693 | 5.229 | 22.4095 | 137.9727 | 23.6624 | 249.9106 | 164.7487 | 249.5708 | 15.3736 | 81.98 | 3.0634 | 158 | 27.963 | 32.9792 | 352.0463 | 0.22781
5145 | 826.1716 | 2.1222 | 81.6669 | 154.2679 | 65.5677 | 17.6338 | 112.8129 | 2.1872 | 5.0033 | 13.4229 | 152.9574 | 23.543 | 191.7261 | 178.8193 | 291.5431 | 16.2704 | 87.2031 | 3.747 | 155 | 28.7013 | 33.7784 | 385.3882 | 0.26059
5146 | 871.5496 | 2.2873 | 81.3098 | 137.5225 | 69.4339 | 18.0577 | 123.6395 | 2.1493 | 10.4058 | 10.2958 | 158.4178 | 25.5168 | 205.7301 | 193.3834 | 308.5278 | 16.5648 | 91.1755 | 4.2436 | 163 | 27.8041 | 33.1105 | 392.5676 | 0.23117
5147 | 894.4283 | 2.1442 | 81.5893 | 171.2982 | 65.8945 | 18.7749 | 129.8608 | 2.172 | 12.9462 | 10.6351 | 166.3114 | 24.8591 | 218.146 | 205.5312 | 323.9016 | 16.7206 | 94.173 | 4.4894 | 137 | 33.9513 | 32.719 | 395.231 | 0.24606
5148 | 891.8898 | 1.7641 | 82.5672 | 164.1652 | 60.1499 | 15.3594 | 128.0967 | 2.5425 | 12.9414 | 12.438 | 173.7238 | 23.4166 | 192.8744 | 211.3795 | 328.4642 | 16.5955 | 96.0619 | 4.7462 | 161 | 30.8976 | 33.6654 | 399.1467 | 0.22769
5149 | 888.6869 | 1.8995 | 86.4599 | 166.827 | 53.1787 | 14.2676 | 124.1785 | 2.5035 | 12.8595 | 17.048 | 175.2839 | 23.2796 | 334.6182 | 216.5903 | 330.9112 | 16.3326 | 97.8364 | 5.0607 | 148 | 31.6622 | 34.2712 | 405.5725 | 0.21707
5150 | 940.6481 | 2.1849 | 77.4999 | 156.1571 | 51.9452 | 12.9351 | 120.3984 | 2.2613 | 12.3052 | 23.8757 | 175.9407 | 23.1105 | 175.3891 | 222.1876 | 335.2797 | 16.2945 | 99.3418 | 5.1752 | 156 | 34.4123 | 33.6299 | 406.8428 | 0.21736
5151 | 972.3215 | 2.6325 | 50.6526 | 130.2349 | 49.9066 | 15.1316 | 108.2991 | 2.5547 | 7.8924 | 26.9247 | 167.8318 | 22.4817 | 214.8816 | 215.7531 | 334.7517 | 16.906 | 97.6813 | 5.0735 | 137 | 26.5311 | 32.9364 | 397.9898 | 0.20878
5152 | 955.865 | 1.6183 | 37.4117 | 112.0499 | 52.2992 | 11.2162 | 90.4013 | 2.1869 | 5.3281 | 22.4675 | 151.5436 | 21.5486 | 243.7125 | 187.6364 | 327.2802 | 15.5578 | 94.439 | 4.8611 | 121 | 22.2783 | 42.6594 | 367.985 | 0.18324
5153 | 913.2693 | 1.2816 | 33.6597 | 104.0309 | 57.9425 | 8.1465 | 85.5828 | 1.3136 | 5.2533 | 16.5898 | 132.4737 | 23.6865 | 266.3857 | 157.6311 | 314.924 | 13.8992 | 91.8992 | 4.4478 | 121 | 17.6236 | 25.6225 | 316.4747 | 0.1953
5154 | 861.8536 | 1.2288 | 31.0789 | 89.7017 | 64.312 | 7.5607 | 78.1583 | 0.94159 | 6.2781 | 13.8263 | 110.6587 | 20.0049 | 241.5679 | 139.8155 | 296.1275 | 13.2974 | 89.1059 | 4.2467 | 131 | 14.9423 | 30.1011 | 272.1274 | 0.18768
5155 | 840.6235 | 1.1131 | 30.0466 | 97.8544 | 66.0749 | 6.9643 | 63.9685 | 1.1334 | 5.9045 | 12.2405 | 96.8838 | 8.3337 | 205.0991 | 127.1927 | 266.5933 | 13.2401 | 85.8971 | 4.0263 | 115 | 14.266 | 31.1418 | 240.3369 | 0.11827
5156 | 814.3667 | 1.1826 | 45.0665 | 106.3257 | 65.2002 | 7.3546 | 56.1101 | 1.076 | 5.34 | 11.1386 | 89.1725 | 3.3377 | 233.2202 | 118.3349 | 235.3135 | 13.2891 | 82.071 | 3.9335 | 116 | 14.8123 | 37.6344 | 217.5346 | 0.029583
5157 | 788.1269 | 2.5336 | 26.0863 | 101.8782 | 64.9653 | 6.8776 | 56.7814 | 1.1288 | 5.2053 | 11.1581 | 79.466 | 3.7782 | 204.8956 | 113.7618 | 218.0632 | 12.9125 | 79.5124 | 3.4273 | 107 | 12.9813 | 22.4376 | 208.1158 | 0
5158 | 768.3512 | 2.8361 | 34.0317 | 100.2443 | 63.5362 | 6.6606 | 55.8029 | 1.3236 | 5.1822 | 12.615 | 71.5003 | 5.4416 | 216.1628 | 111.1991 | 212.1622 | 12.6842 | 79.021 | 3.2961 | 102 | 14.1994 | 35.288 | 204.3501 | 0
5159 | 750.4494 | 1.6568 | 38.5611 | 93.1311 | 62.0236 | 7.3387 | 54.0098 | 1.3712 | 5.5777 | 14.2521 | 69.3138 | 6.1863 | 331.3457 | 109.0516 | 216.0999 | 14.3577 | 78.7609 | 3.0583 | 101 | 12.6907 | 22.4376 | 200.4367 | 0
5160 | 749.3538 | 1.3557 | 38.5243 | 89.9711 | 63.2737 | 6.8582 | 56.707 | 1.5901 | 5.5955 | 14.7588 | 69.0339 | 6.0328 | 165.4629 | 106.4348 | 217.888 | 16.2149 | 78.0037 | 2.8966 | 98 | 15.4181 | 26.802 | 198.6832 | 0
5161 | 746.7442 | 1.4375 | 38.1907 | 89.2018 | 65.0535 | 7.3628 | 58.0846 | 1.5314 | 5.4661 | 14.8588 | 68.363 | 6.0158 | 184.2247 | 107.3125 | 223.2736 | 16.8377 | 77.3352 | 2.7117 | 96 | 12.8308 | 28.9937 | 200.3666 | 0
5162 | 740.9363 | 1.1851 | 38.335 | 88.8656 | 66.569 | 8.342 | 54.4884 | 1.3889 | 5.6618 | 14.9304 | 67.2984 | 8.1164 | 272.8783 | 114.2625 | 225.6928 | 16.9597 | 77.0256 | 2.5389 | 94 | 14.4055 | 37.2193 | 203.8966 | 0
5163 | 742.096 | 1.1126 | 35.292 | 69.5671 | 67.5145 | 7.1442 | 55.8811 | 1.3729 | 5.4988 | 15.7192 | 66.141 | 14.038 | 189.9456 | 119.7283 | 218.5773 | 17.1428 | 76.8019 | 2.8239 | 95 | 14.292 | 22.4425 | 207.1164 | 0
5164 | 748.249 | 1.5082 | 32.4031 | 82.9015 | 65.2218 | 8.1005 | 58.5362 | 1.3174 | 5.3867 | 18.5507 | 64.6519 | 13.5325 | 187.8668 | 119.5199 | 210.9696 | 16.1622 | 76.2646 | 2.9357 | 96 | 14.0345 | 27.0201 | 215.2142 | 0
5165 | 759.0527 | 1.6624 | 44.6838 | 95.1032 | 65.6159 | 6.3423 | 56.2328 | 1.0896 | 5.1267 | 21.2387 | 62.4729 | 7.6337 | 230.0016 | 115.1978 | 200.4165 | 13.6151 | 75.3286 | 2.4666 | 92 | 16.8809 | 28.4959 | 233.9133 | 0
5166 | 791.9631 | 1.7587 | 58.219 | 122.8183 | 62.3051 | 8.4618 | 61.0567 | 1.1201 | 5.0863 | 23.772 | 72.1206 | 10.8338 | 206.4529 | 117.0243 | 199.9583 | 12.4376 | 75.1107 | 2.2136 | 115 | 17.2958 | 37.4939 | 264.6043 | 0.10372
5167 | 843.59 | 1.9305 | 63.8633 | 105.9459 | 58.356 | 13.1809 | 80.7598 | 1.6831 | 4.917 | 26.1349 | 100.7387 | 20.2558 | 216.9989 | 140.539 | 210.7944 | 13.1348 | 76.8161 | 2.4045 | 143 | 29.5262 | 22.5987 | 308.0896 | 0.19826
5168 | 899.6878 | 2.1169 | 70.909 | 149.0642 | 62.2736 | 14.2304 | 106.8864 | 2.3563 | 6.6102 | 23.7745 | 131.2769 | 23.7688 | 240.6553 | 168.9562 | 245.6365 | 13.5576 | 81.3043 | 3.0388 | 165 | 37.9932 | 26.9254 | 354.3303 | 0.28008
5169 | 943.8736 | 2.149 | 74.753 | 154.3193 | 72.3203 | 13.3707 | 122.3158 | 2.2577 | 9.37 | 17.6876 | 148.3426 | 23.5751 | 289.0699 | 185.8484 | 285.0345 | 13.7174 | 87.3006 | 3.8741 | 165 | 29.8969 | 28.5018 | 382.5939 | 0.29004
5170 | 953.98 | 2.1403 | 77.1921 | 155.5902 | 78.8994 | 13.3237 | 131.3435 | 2.0498 | 6.7475 | 14.4094 | 151.457 | 25.8753 | 154.3271 | 197.33 | 297.1285 | 13.8696 | 91.553 | 5.0177 | 161 | 33.2757 | 37.4266 | 393.8965 | 0.21564
5171 | 976.1884 | 1.9953 | 81.9046 | 161.5213 | 76.0543 | 13.396 | 133.4773 | 2.2869 | 5.0803 | 15.1036 | 153.03 | 28.3078 | 133.7448 | 203.4572 | 302.1124 | 13.9186 | 93.2521 | 5.6068 | 167 | 33.2227 | 22.4231 | 396.5954 | 0.24305
5172 | 974.429 | 2.6099 | 82.5317 | 148.2728 | 66.8172 | 13.3238 | 135.7682 | 2.1727 | 4.8448 | 17.559 | 160.8509 | 29.3085 | 191.1979 | 205.8349 | 300.4438 | 13.56 | 94.0089 | 5.9317 | 179 | 31.1589 | 27.0762 | 394.8599 | 0.21435
5173 | 971.8182 | 2.7862 | 86.4888 | 182.5017 | 63.1804 | 13.3525 | 131.5282 | 2.1583 | 4.8277 | 24.5056 | 168.7333 | 29.134 | 193.877 | 213.8621 | 302.6408 | 13.464 | 95.8158 | 5.8308 | 161 | 34.4502 | 29.0099 | 398.4155 | 0.2412
5174 | 972.9111 | 1.8755 | 80.2334 | 169.1345 | 65.0805 | 14.0293 | 123.0747 | 2.0653 | 4.7762 | 30.9783 | 176.7516 | 28.979 | 223.4317 | 224.5017 | 324.4104 | 13.4 | 98.0858 | 5.5899 | 160 | 39.0675 | 36.9435 | 400.6335 | 0.20993
5175 | 979.1068 | 2.2255 | 55.1982 | 114.3931 | 62.9946 | 17.0703 | 108.6386 | 1.8604 | 5.2533 | 30.7141 | 172.876 | 28.3679 | 196.0843 | 219.2739 | 351.948 | 13.3676 | 98.0705 | 5.9337 | 145 | 30.2811 | 22.3652 | 390.7387 | 0.12855
5176 | 967.1124 | 1.8463 | 38.3653 | 114.6482 | 64.7865 | 11.6747 | 94.5975 | 1.9356 | 5.5252 | 25.919 | 151.6276 | 28.2065 | 211.1161 | 187.0681 | 355.0547 | 12.7409 | 97.0828 | 5.7163 | 127 | 21.9143 | 29.4378 | 363.8748 | 0.037096
5177 | 938.5849 | 1.2017 | 29.9476 | 76.5029 | 62.8017 | 8.7223 | 82.3894 | 1.5057 | 5.4381 | 19.6551 | 128.5281 | 28.2633 | 243.6053 | 146.3921 | 330.3052 | 12.05 | 96.7537 | 5.2217 | 121 | 13.1677 | 31.4676 | 316.5615 | 0.06755
5178 | 897.1103 | 1.3547 | 26.0419 | 92.9256 | 56.112 | 7.1444 | 73.9521 | 1.1143 | 4.9245 | 15.5295 | 108.7278 | 23.3818 | 202.3072 | 118.1407 | 299.8997 | 11.4481 | 94.2846 | 4.6635 | 119 | 14.3846 | 30.3916 | 270.1691 | 0.02973
5179 | 858.802 | 2.0065 | 34.2727 | 79.0302 | 43.109 | 8.0165 | 63.4562 | 1.1091 | 4.8811 | 14.1816 | 96.7717 | 11.2228 | 231.7256 | 105.8506 | 283.3499 | 11.4474 | 89.2658 | 4.3643 | 103 | 14.8872 | 34.5142 | 240.8295 | 0.0084306
5180 | 835.1376 | 2.6671 | 19.1159 | 73.5523 | 45.9274 | 9.3312 | 61.47 | 1.3437 | 5.2348 | 14.1374 | 91.4881 | 6.2619 | 298.3543 | 101.2351 | 259.8973 | 11.7612 | 85.2069 | 3.7141 | 105 | 14.467 | 20.1194 | 221.9737 | 0.00082776
5181 | 809.6174 | 2.789 | 28.7923 | 65.7233 | 57.8893 | 6.6602 | 60.8801 | 1.4443 | 5.373 | 16.2405 | 84.8803 | 7.9084 | 233.159 | 97.4857 | 231.7224 | 11.9168 | 83.4734 | 3.5226 | 110 | 14.6381 | 31.4074 | 211.7754 | 0
5182 | 796.5077 | 2.2986 | 33.9798 | 85.5555 | 61.1502 | 7.0914 | 60.3869 | 1.3823 | 5.7666 | 18.1845 | 77.9215 | 9.0644 | 209.8477 | 96.5813 | 219.2659 | 11.8718 | 82.8659 | 2.9738 | 111 | 14.6315 | 20.0368 | 208.0052 | 0
5183 | 787.0897 | 1.4098 | 34.3169 | 98.0088 | 66.8363 | 9.0833 | 58.777 | 1.374 | 5.62 | 17.5236 | 74.0938 | 9.2287 | 211.1103 | 95.1976 | 225.2468 | 12.6964 | 81.9363 | 2.6771 | 109 | 22.5121 | 24.1829 | 207.3373 | 0
5184 | 774.3327 | 1.2323 | 34.0756 | 99.6333 | 70.5049 | 9.3749 | 59.584 | 1.372 | 5.4573 | 16.8329 | 72.4394 | 9.1438 | 253.3889 | 91.8124 | 221.3843 | 14.8133 | 80.4516 | 2.6825 | 101 | 20.7542 | 24.9698 | 203.3581 | 0
5185 | 771.0906 | 1.1956 | 33.2638 | 100.3285 | 71.0867 | 8.8344 | 60.5024 | 1.5925 | 5.4722 | 16.8838 | 72.0691 | 9.1851 | 142.1312 | 90.6653 | 217.8935 | 15.8349 | 79.5815 | 2.6634 | 102 | 18.1598 | 36.1787 | 198.2424 | 0
5186 | 759.5204 | 1.0491 | 32.5714 | 100.4687 | 67.1764 | 9.3248 | 58.7968 | 1.5294 | 5.3556 | 16.9908 | 72.2443 | 12.0965 | 193.2611 | 97.755 | 215.9332 | 15.8727 | 79.2848 | 2.6572 | 99 | 20.0537 | 28.9019 | 197.7175 | 0
5187 | 752.852 | 1.0821 | 32.5768 | 100.9461 | 63.4376 | 8.7243 | 58.5413 | 1.3582 | 5.422 | 17.6952 | 72.1489 | 20.4952 | 205.6905 | 103.9978 | 209.5068 | 15.9985 | 78.8874 | 2.7046 | 98 | 19.0164 | 28.9019 | 202.365 | 0
5188 | 750.7813 | 1.5516 | 32.5084 | 74.2602 | 53.5473 | 7.146 | 61.8733 | 1.3654 | 5.4093 | 20.9488 | 71.5269 | 20.381 | 190.8334 | 102.3949 | 201.377 | 14.9057 | 78.4168 | 2.6797 | 96 | 18.3917 | 22.3757 | 214.1567 | 0
5189 | 756.702 | 2.087 | 61.5311 | 101.7953 | 54.4373 | 5.2837 | 60.2188 | 1.1387 | 5.2702 | 23.9217 | 69.5493 | 12.9248 | 179.6372 | 99.1271 | 205.8771 | 12.4195 | 77.865 | 2.4611 | 90 | 18.977 | 27.095 | 229.6844 | 0
5190 | 775.6887 | 1.6623 | 50.4474 | 85.4122 | 58.2633 | 6.8355 | 60.9581 | 0.96024 | 4.9334 | 25.6552 | 78.7005 | 14.5821 | 184.3149 | 108.7141 | 215.6839 | 11.3491 | 77.455 | 2.3416 | 112 | 21.5242 | 28.7372 | 255.0713 | 0.039934
5191 | 829.3071 | 1.9255 | 37.2687 | 117.1217 | 52.8439 | 11.7747 | 90.6562 | 1.1026 | 4.7701 | 27.6268 | 106.7827 | 26.1059 | 214.5455 | 141.3114 | 224.0609 | 12.3078 | 78.3666 | 2.7946 | 152 | 37.4083 | 28.8565 | 300.0577 | 0.08419
5192 | 867.888 | 1.6972 | 46.4419 | 136.0174 | 51.7246 | 14.8314 | 118.6306 | 1.8916 | 5.1012 | 25.9885 | 136.1821 | 29.8138 | 206.0678 | 177.0839 | 247.1659 | 13.834 | 82.5089 | 3.5118 | 144 | 38.8427 | 29.2288 | 349.5004 | 0.099197
5193 | 899.0502 | 1.5111 | 50.5915 | 130.0761 | 53.7719 | 13.7257 | 127.9712 | 2.0947 | 5.0512 | 22.5988 | 149.8495 | 29.4896 | 246.4079 | 196.6118 | 279.4241 | 14.6057 | 88.6795 | 4.3093 | 190 | 37.7821 | 28.7121 | 381.4927 | 0.13691
5194 | 936.437 | 1.7204 | 50.5527 | 126.4632 | 52.5892 | 14.7766 | 131.9137 | 1.9023 | 4.7774 | 21.6374 | 150.6994 | 30.7921 | 250.7266 | 207.2678 | 299.8914 | 14.8448 | 93.7289 | 4.5589 | 156 | 42.1636 | 28.9734 | 396.862 | 0.16126
5195 | 966.9034 | 2.0701 | 50.5883 | 127.2439 | 53.85 | 14.5564 | 131.7022 | 1.9811 | 5.0133 | 21.6971 | 154.9608 | 30.1561 | 252.6208 | 217.3599 | 312.7293 | 15.1726 | 96.2317 | 4.7003 | 151 | 38.9686 | 29.1681 | 407.621 | 0.23752
5196 | 955.5687 | 2.0086 | 50.6164 | 155.4565 | 55.6541 | 14.1957 | 129.367 | 2.1337 | 5.35 | 23.2468 | 165.2401 | 29.2676 | 270.4869 | 222.2821 | 314.9868 | 14.594 | 96.3361 | 5.068 | 164 | 37.1693 | 36.969 | 409.0198 | 0.20917
5197 | 958.2161 | 1.9764 | 49.8567 | 175.3035 | 57.0634 | 14.9022 | 126.4056 | 2.3662 | 5.4066 | 26.4158 | 172.9423 | 29.6373 | 257.1623 | 225.9923 | 321.9901 | 14.8679 | 96.6911 | 5.1165 | 153 | 43.6109 | 22.4239 | 404.7086 | 0.21385
5198 | 964.0276 | 2.299 | 50.4445 | 145.6142 | 62.4552 | 13.8122 | 119.3553 | 2.2522 | 5.9192 | 28.5667 | 176.6642 | 29.447 | 258.6874 | 231.987 | 344.2242 | 15.3756 | 97.9732 | 5.0549 | 162 | 44.4924 | 35.3785 | 403.4095 | 0.16322
5199 | 953.7255 | 2.2014 | 50.1849 | 148.0493 | 61.381 | 14.484 | 106.2588 | 2.3617 | 5.7139 | 29.0656 | 167.9537 | 28.4166 | 255.4912 | 222.7477 | 354.5428 | 15.1389 | 97.0382 | 4.9464 | 151 | 38.0234 | 22.1094 | 395.8606 | 0.18233
5200 | 930.4266 | 1.7498 | 51.1398 | 116.4573 | 62.0338 | 11.1766 | 98.4916 | 2.5741 | 5.1155 | 26.9169 | 148.2623 | 27.0637 | 276.7461 | 196.4229 | 331.1043 | 13.9939 | 94.0362 | 5.045 | 129 | 25.7 | 35.6927 | 366.4737 | 0.20085
5201 | 898.9316 | 1.5436 | 67.2323 | 103.584 | 63.8114 | 8.8049 | 96.2543 | 1.6067 | 4.8079 | 22.0364 | 130.5308 | 27.0505 | 253.7054 | 159.495 | 298.6536 | 12.4156 | 89.7579 | 5.1994 | 129 | 13.5212 | 28.9019 | 314.5594 | 0.16246
5202 | 878.6025 | 1.3236 | 37.5694 | 95.8977 | 64.4231 | 7.7935 | 85.7889 | 0.9197 | 4.8597 | 18.2801 | 115.0657 | 23.0527 | 223.6783 | 121.4385 | 282.6889 | 11.558 | 84.1838 | 5.4246 | 130 | 11.1036 | 28.9019 | 268.6609 | 0.12251
5203 | 842.9559 | 4.5428 | 45.533 | 88.1545 | 63.8718 | 7.59 | 69.5087 | 0.90753 | 4.9662 | 17.7365 | 103.8951 | 11.393 | 219.5779 | 98.8539 | 264.0046 | 11.4168 | 79.6325 | 5.5386 | 109 | 13.0226 | 28.9019 | 235.7004 | 0.07753
5204 | 819.9885 | 8.1475 | 68.2357 | 68.6809 | 63.1428 | 7.6288 | 59.5345 | 1.1265 | 4.9824 | 17.6903 | 97.4197 | 6.3806 | 233.3353 | 89.9405 | 242.1801 | 11.5169 | 77.0114 | 5.5047 | 108 | 11.7866 | 28.9019 | 208.5421 | 0.015826
5205 | 796.1512 | 9.4036 | 37.6083 | 107.2528 | 61.1037 | 8.9459 | 54.6229 | 1.2805 | 5.0404 | 17.2679 | 89.3955 | 7.3348 | 198.3555 | 88.0267 | 226.331 | 11.5949 | 75.4599 | 4.8805 | 105 | 10.5183 | 22.256 | 194.6145 | 0
5206 | 783.4404 | 7.5366 | 46.0815 | 101.9383 | 60.1109 | 8.8802 | 56.1092 | 1.3112 | 5.3115 | 18.0601 | 80.6964 | 8.4997 | 211.2132 | 89.4877 | 218.653 | 11.5135 | 74.8275 | 4.1407 | 100 | 16.4363 | 23.5504 | 190.8956 | 0
5207 | 767.9769 | 3.1494 | 50.4385 | 79.3091 | 49.2267 | 8.5609 | 60.6417 | 1.3289 | 5.3633 | 18.8559 | 75.6743 | 8.9639 | 195.8813 | 88.9343 | 222.7611 | 12.8055 | 74.9213 | 3.7276 | 100 | 12.8381 | 24.4458 | 192.173 | 0
5208 | 765.0628 | 1.1093 | 50.3825 | 110.3431 | 43.2759 | 6.404 | 57.078 | 1.3391 | 5.2167 | 18.5517 | 73.1559 | 9.4678 | 194.1494 | 86.6201 | 225.5176 | 14.8716 | 74.8006 | 3.5386 | 101 | 15.0913 | 24.2719 | 194.2453 | 0
5209 | 766.908 | 1.0226 | 50.3085 | 98.8047 | 44.445 | 4.9785 | 57.3254 | 1.339 | 5.3467 | 17.6677 | 71.5323 | 9.2067 | 224.7196 | 86.6682 | 224.1391 | 15.9535 | 74.6081 | 3.4089 | 102 | 14.0664 | 24.5654 | 194.8036 | 0
5210 | 751.704 | 1.1715 | 50.371 | 90.5451 | 42.446 | 6.1393 | 57.6927 | 1.5166 | 5.3937 | 16.7675 | 70.3753 | 12.0903 | 176.7893 | 92.0753 | 226.1402 | 16.057 | 74.6916 | 3.0206 | 103 | 15.0539 | 35.7477 | 195.5784 | 0
5211 | 743.4757 | 1.4559 | 51.2342 | 88.9631 | 48.9327 | 6.6516 | 56.2855 | 1.5268 | 5.5977 | 17.1437 | 69.7254 | 20.2645 | 179.1284 | 98.287 | 222.6752 | 16.025 | 75.1681 | 2.8403 | 102 | 12.1083 | 22.384 | 196.1342 | 0
5212 | 752.1175 | 1.6681 | 67.1511 | 90.3632 | 55.4896 | 7.3608 | 57.8904 | 1.3429 | 5.4918 | 20.0779 | 68.767 | 20.1808 | 247.9467 | 99.3072 | 209.9554 | 14.8428 | 75.533 | 2.8454 | 99 | 12.0292 | 26.4082 | 203.0615 | 0
5213 | 760.1209 | 1.7355 | 37.7804 | 88.4283 | 58.5478 | 7.6357 | 55.5382 | 1.0714 | 5.2182 | 22.8709 | 66.9414 | 13.2833 | 176.5894 | 96.3703 | 202.2394 | 12.581 | 75.0822 | 2.6576 | 94 | 13.8243 | 36.9369 | 219.5497 | 0
5214 | 778.6097 | 1.354 | 45.9222 | 95.5191 | 61.8588 | 8.9862 | 61.1625 | 0.94043 | 4.8691 | 25.1324 | 76.5075 | 15.8146 | 206.9959 | 106.1732 | 201.8541 | 11.6302 | 75.0934 | 2.5594 | 121 | 15.8446 | 22.1622 | 249.8337 | 0.080053
5215 | 823.182 | 1.9075 | 49.9133 | 103.7224 | 65.0828 | 12.2762 | 83.7359 | 1.0331 | 4.5795 | 26.0777 | 104.0186 | 26.1029 | 289.196 | 139.735 | 204.9301 | 12.0262 | 77.161 | 2.8116 | 148 | 35.6844 | 26.5352 | 302.0788 | 0.09451
5216 | 864.462 | 2.3102 | 50.9649 | 115.0983 | 69.4115 | 13.3923 | 102.5984 | 1.9293 | 6.3886 | 21.0334 | 133.7178 | 31.2667 | 206.872 | 172.9891 | 231.9824 | 12.7714 | 82.1989 | 3.5308 | 153 | 35.1701 | 28.7018 | 354.1215 | 0.14475
5217 | 899.2934 | 1.85 | 50.5657 | 122.1713 | 69.9933 | 14.0469 | 117.0179 | 2.6431 | 5.6848 | 15.2745 | 152.3195 | 31.4328 | 190.1784 | 190.1916 | 274.1225 | 13.2539 | 88.0134 | 4.4412 | 174 | 33.0084 | 36.9069 | 379.6013 | 0.19979
5218 | 943.2794 | 2.2337 | 67.5341 | 126.0617 | 65.5873 | 14.1659 | 123.4806 | 2.4203 | 4.6733 | 14.0162 | 155.9558 | 31.1158 | 204.8359 | 198.363 | 298.5537 | 13.0738 | 92.5955 | 5.1857 | 175 | 39.2161 | 22.1193 | 380.7739 | 0.24231
5219 | 983.3758 | 2.2495 | 37.3607 | 130.9953 | 59.7419 | 14.9137 | 123.8197 | 2.2788 | 4.6767 | 15.7271 | 156.2869 | 29.1465 | 258.9672 | 202.5304 | 309.6801 | 12.719 | 96.6525 | 5.8796 | 149 | 36.1094 | 35.033 | 384.5679 | 0.24939
5220 | 984.7556 | 2.0541 | 46.249 | 133.9802 | 58.8513 | 16.7424 | 125.9161 | 2.3874 | 4.9798 | 19.7738 | 162.1769 | 26.0237 | 195.5348 | 205.175 | 307.4433 | 12.8121 | 97.9913 | 6.1612 | 188 | 32.3491 | 22.3402 | 395.8913 | 0.22846
5221 | 966.992 | 1.6799 | 51.0144 | 132.374 | 65.205 | 14.315 | 124.9084 | 2.5079 | 5.201 | 26.0852 | 167.6622 | 24.6085 | 230.2778 | 208.6685 | 295.9553 | 12.0928 | 96.3945 | 5.9919 | 182 | 40.2142 | 26.841 | 408.233 | 0.19215
5222 | 954.5755 | 1.5349 | 50.0727 | 139.1734 | 63.0145 | 15.3473 | 116.4335 | 2.553 | 5.0915 | 34.7264 | 171.1331 | 23.8701 | 253.7801 | 210.2754 | 306.0536 | 11.3469 | 95.1545 | 5.9597 | 177 | 37.5908 | 36.548 | 410.9819 | 0.19621
5223 | 958.8695 | 2.0463 | 50.1624 | 139.7452 | 65.3345 | 12.6397 | 105.8235 | 2.3485 | 4.7265 | 39.5029 | 163.158 | 22.3967 | 266.6758 | 202.6851 | 328.718 | 10.3836 | 92.6045 | 6.5162 | 148 | 31.5805 | 28.5769 | 391.3347 | 0.20685
5224 | 946.7115 | 1.9102 | 50.4198 | 107.6508 | 71.2105 | 9.2236 | 99.9946 | 1.5034 | 4.5578 | 36.4332 | 145.4619 | 21.4819 | 224.0481 | 184.7169 | 334.3979 | 9.7283 | 88.3171 | 6.4069 | 133 | 20.629 | 28.5769 | 346.9651 | 0.17659
5225 | 928.0286 | 1.643 | 50.3505 | 94.5752 | 71.6198 | 9.2353 | 98.6656 | 0.93835 | 4.4667 | 32.0462 | 129.6674 | 22.1793 | 221.5962 | 153.8965 | 324.4101 | 9.7587 | 85.2871 | 5.5303 | 146 | 17.9193 | 22.124 | 288.2607 | 0.16813
5226 | 881.9596 | 1.6028 | 50.3854 | 91.4614 | 70.8711 | 7.9709 | 87.715 | 0.90156 | 4.6177 | 26.1218 | 113.4705 | 18.7664 | 246.9578 | 119.5318 | 302.962 | 9.6762 | 82.7907 | 4.6249 | 132 | 15.9034 | 25.9882 | 244.7719 | 0.12779
5227 | 834.9113 | 1.2979 | 50.4285 | 79.4657 | 71.5121 | 6.315 | 72.6794 | 0.91169 | 4.704 | 18.3678 | 96.731 | 9.232 | 191.1457 | 99.4649 | 261.7654 | 9.7058 | 76.7751 | 4.2609 | 112 | 11.6775 | 27.6739 | 218.8329 | 0.073317
5228 | 805.1981 | 2.7045 | 50.4151 | 98.6379 | 69.4074 | 7.7952 | 59.8361 | 1.1215 | 5.5125 | 14.6417 | 84.8591 | 5.2223 | 111.8411 | 92.7453 | 236.9831 | 9.9847 | 65.53 | 3.8445 | 102 | 17.4401 | 24.8376 | 199.7239 | 0.012073
5229 | 786.6016 | 7.5483 | 68.0586 | 98.8398 | 68.7406 | 7.1425 | 53.8971 | 1.2544 | 5.391 | 13.6566 | 80.3997 | 6.0209 | 149.0416 | 88.1358 | 232.2126 | 10.184 | 56.1167 | 3.3023 | 99 | 12.2786 | 22.5715 | 187.0407 | 0
5230 | 797.3951 | 8.9071 | 38.0895 | 99.4116 | 67.5267 | 6.7429 | 58.8141 | 1.3109 | 5.2395 | 12.5557 | 79.7165 | 7.5613 | 175.6717 | 84.6641 | 225.9172 | 10.2417 | 53.28 | 3.2631 | 101 | 17.6407 | 22.3479 | 184.8284 | 0
5231 | 804.572 | 3.981 | 33.2753 | 90.4019 | 65.1706 | 7.306 | 63.778 | 1.3402 | 5.4863 | 11.8209 | 78.4999 | 8.2516 | 147.45 | 85.6443 | 225.2063 | 11.2503 | 53.4258 | 3.6495 | 101 | 19.8128 | 22.6245 | 188.4778 | 0
5232 | 796.0529 | 3.6331 | 30.9549 | 100.304 | 62.9042 | 7.616 | 58.7424 | 1.3618 | 5.7202 | 11.8664 | 75.986 | 8.1912 | 175.9058 | 87.2616 | 228.7177 | 13.9791 | 53.6053 | 3.8341 | 109 | 18.3207 | 22.7048 | 188.5988 | 0
5233 | 794.1722 | 4.7471 | 30.8105 | 108.7399 | 50.021 | 6.8364 | 56.2262 | 1.3489 | 5.7073 | 11.9874 | 73.5498 | 8.2395 | 190.5461 | 87.7288 | 232.2401 | 14.7816 | 53.5441 | 3.8022 | 104 | 18.3589 | 22.6228 | 187.4687 | 0
5234 | 794.4823 | 2.4433 | 31.0018 | 103.0781 | 42.6679 | 6.6177 | 62.4617 | 1.5871 | 5.7373 | 11.7732 | 72.098 | 8.2896 | 264.0138 | 92.6797 | 231.8589 | 14.349 | 53.4024 | 3.9399 | 99 | 15.683 | 22.5932 | 187.9464 | 0
5235 | 774.6966 | 1.0322 | 30.6809 | 99.7711 | 42.9842 | 7.3968 | 61.8634 | 1.5168 | 5.8084 | 12.4272 | 71.6314 | 8.3593 | 163.2151 | 98.9265 | 228.3052 | 14.9442 | 53.9084 | 4.0314 | 100 | 19.797 | 22.5852 | 186.0647 | 0
5236 | 770.7678 | 1.4543 | 30.6483 | 99.968 | 41.703 | 6.9407 | 54.9896 | 1.353 | 5.749 | 15.8505 | 71.3427 | 8.223 | 194.152 | 100.7631 | 222.8705 | 13.6175 | 54.5981 | 3.4519 | 102 | 18.1093 | 22.5808 | 184.4321 | 0
5237 | 782.3655 | 2.0162 | 30.3507 | 97.7131 | 44.0638 | 8.0775 | 54.2341 | 1.1554 | 5.6633 | 20.3859 | 69.3166 | 6.4956 | 203.4753 | 97.4526 | 221.0507 | 11.0623 | 54.1415 | 2.7746 | 98 | 16.3988 | 22.6165 | 185.7262 | 0
5238 | 800.5151 | 1.4716 | 29.0558 | 96.5487 | 52.8552 | 7.7699 | 54.5556 | 0.96514 | 5.0734 | 22.8367 | 69.703 | 5.4203 | 220.1512 | 90.5234 | 211.3268 | 10.1179 | 53.2647 | 2.5431 | 94 | 21.0238 | 22.9974 | 189.1451 | 0.027853
5239 | 818.659 | 0.89822 | 23.5587 | 97.7663 | 57.2727 | 7.6417 | 56.5765 | 0.97322 | 4.8494 | 22.1846 | 79.4695 | 7.5313 | 184.5482 | 87.4462 | 204.6115 | 10.0189 | 52.8032 | 2.7641 | 94 | 25.5853 | 35.1384 | 192.4775 | 0.050726
5240 | 812.5321 | 1.1749 | 19.8162 | 97.7819 | 60.7515 | 7.5913 | 56.9485 | 1.0198 | 6.5805 | 19.0813 | 98.2184 | 13.1065 | 199.4312 | 86.6729 | 221.1822 | 10.128 | 52.636 | 3.3268 | 98 | 27.1596 | 28.285 | 198.0881 | 0.099157
5241 | 814.553 | 1.1283 | 19.5628 | 87.8165 | 66.8854 | 6.94 | 57.3577 | 1.3026 | 9.1567 | 15.6027 | 119.2416 | 14.5961 | 240.4804 | 89.8103 | 243.9574 | 10.3969 | 52.8299 | 3.6441 | 100 | 24.2872 | 22.1313 | 202.9952 | 0.11297
5242 | 836.8189 | 1.2716 | 19.5161 | 94.2261 | 68.8 | 7.3052 | 57.5877 | 1.1531 | 6.5533 | 13.287 | 133.9999 | 14.1098 | 109.3065 | 97.9625 | 251.6737 | 9.6718 | 53.7549 | 3.9297 | 103 | 26.8103 | 26.3214 | 202.0671 | 0.11586
5243 | 858.4563 | 1.1364 | 19.3573 | 94.1427 | 68.1787 | 8.2398 | 54.8168 | 0.96143 | 4.6952 | 14.6085 | 134.5278 | 14.2594 | 172.3434 | 102.457 | 243.367 | 9.4646 | 54.9686 | 4.3511 | 103 | 28.8967 | 28.8045 | 201.3092 | 0.11451
5244 | 854.9647 | 1.0445 | 19.7032 | 100.839 | 66.1882 | 9.2925 | 56.2729 | 0.97835 | 4.774 | 16.9293 | 125.9081 | 14.1674 | 183.5308 | 108.6794 | 233.8754 | 9.797 | 58.3426 | 4.6213 | 107 | 23.7201 | 29.4893 | 201.3623 | 0.15361
5245 | 836.3271 | 1.0919 | 19.5886 | 89.5217 | 65.69 | 10.9367 | 59.1794 | 0.97648 | 5.097 | 16.4031 | 121.9056 | 14.4854 | 182.8656 | 121.0276 | 224.1653 | 9.7727 | 68.1925 | 4.5121 | 105 | 26.0441 | 29.7279 | 203.4198 | 0.1171
5246 | 817.0553 | 0.90422 | 19.7015 | 101.3009 | 67.6857 | 9.2202 | 60.3467 | 0.98035 | 5.1715 | 15.5929 | 123.7971 | 16.2296 | 222.5217 | 127.0912 | 217.4717 | 9.9659 | 78.8037 | 4.5237 | 113 | 22.4834 | 29.1404 | 204.0479 | 0.13349
5247 | 806.6832 | 0.78733 | 19.8585 | 97.0372 | 65.9129 | 8.5981 | 58.393 | 0.97104 | 5.3025 | 16.1241 | 117.3025 | 15.9056 | 156.0853 | 119.9437 | 214.8387 | 9.6627 | 81.3959 | 4.5055 | 107 | 21.0029 | 28.4049 | 199.9735 | 0.13475
5248 | 793.5118 | 0.96684 | 19.9354 | 96.2663 | 56.9739 | 8.5349 | 55.6076 | 1.2479 | 5.013 | 16.6769 | 101.436 | 8.9384 | 174.7219 | 109.1498 | 212.6302 | 9.5473 | 79.7078 | 4.5488 | 111 | 21.8305 | 28.2245 | 193.9975 | 0.0887
5249 | 795.135 | 1.139 | 19.675 | 95.563 | 43.1033 | 8.5922 | 53.9452 | 1.1591 | 4.9952 | 15.7989 | 91.6247 | 5.6301 | 174.5992 | 104.0785 | 216.3227 | 9.9549 | 76.5363 | 4.416 | 110 | 17.3242 | 28.4952 | 190.1135 | 0.087231
5250 | 794.1455 | 1.0299 | 19.6032 | 95.1162 | 50.3914 | 6.4512 | 55.1309 | 0.99099 | 4.9508 | 14.4216 | 84.5674 | 5.5279 | 233.923 | 102.8436 | 229.3557 | 9.944 | 67.3517 | 4.2606 | 119 | 13.7305 | 28.6829 | 188.5809 | 0.082582
5251 | 778.7519 | 1.2961 | 19.4288 | 94.7524 | 52.3694 | 6.3932 | 58.2779 | 0.96682 | 4.7548 | 13.8591 | 76.4858 | 5.6098 | 148.2098 | 100.4285 | 228.9904 | 10.0237 | 57.0597 | 4.1296 | 115 | 17.3457 | 28.7475 | 184.5283 | 0.027437
5252 | 769.4258 | 2.0313 | 20.3784 | 95.5869 | 52.0708 | 7.3576 | 58.1665 | 0.97242 | 4.6894 | 13.7473 | 73.4003 | 5.5478 | 214.6809 | 98.2688 | 219.9614 | 10.1675 | 53.0208 | 3.6577 | 123 | 15.0608 | 28.769 | 182.5534 | 0.0098693
5253 | 755.8163 | 2.932 | 26.4226 | 102.6269 | 55.654 | 8.3033 | 57.9375 | 1.2125 | 4.7567 | 13.2908 | 74.1567 | 6.3214 | 182.0792 | 95.9129 | 211.0919 | 9.9234 | 52.9093 | 3.4664 | 119 | 16.8805 | 25.7802 | 182.9264 | 0
5254 | 749.1246 | 2.562 | 28.8715 | 99.8145 | 57.8887 | 7.155 | 56.8431 | 1.3915 | 5.15 | 12.3696 | 76.0817 | 7.8078 | 208.6439 | 92.7294 | 203.5414 | 10.0189 | 53.4197 | 4.0094 | 108 | 17.0504 | 25.2711 | 181.0739 | 0
5255 | 747.9524 | 1.8374 | 28.8968 | 112.9188 | 59.9777 | 7.3315 | 57.3436 | 1.5916 | 5.39 | 11.6689 | 78.0706 | 8.1166 | 138.2046 | 96.1228 | 208.8047 | 11.3565 | 53.5953 | 4.0879 | 104 | 14.8226 | 24.5278 | 180.8026 | 0
5256 | 740.4802 | 2.8812 | 28.6015 | 108.5012 | 63.0439 | 6.9175 | 57.9989 | 1.6209 | 5.4001 | 11.5441 | 78.2437 | 8.0512 | 184.2987 | 120.9544 | 210.5102 | 13.8716 | 53.4336 | 3.9029 | 110 | 15.2925 | 30.4593 | 182.0424 | 0
5257 | 725.9212 | 6.5788 | 28.8263 | 107.118 | 63.9377 | 8.8188 | 56.2758 | 1.4805 | 5.7271 | 11.6424 | 76.8543 | 8.1184 | 184.4205 | 146.6538 | 209.0387 | 14.6795 | 53.3442 | 3.7509 | 108 | 14.294 | 18.374 | 180.3801 | 0
5258 | 718.1346 | 8.3858 | 28.6244 | 107.1157 | 67.8897 | 7.2617 | 56.8515 | 1.4268 | 6.0628 | 11.7775 | 75.7519 | 7.7609 | 187.1097 | 151.6854 | 210.9374 | 14.2613 | 53.4021 | 3.5473 | 125 | 17.2712 | 21.9051 | 177.9072 | 0
5259 | 707.8465 | 4.6315 | 28.6983 | 106.9845 | 69.1019 | 6.669 | 55.2213 | 1.4293 | 6.0795 | 11.8874 | 75.0802 | 7.453 | 203.6732 | 150.714 | 208.1558 | 12.1728 | 53.3882 | 3.1215 | 112 | 14.5009 | 23.043 | 178.0339 | 0
5260 | 700.9982 | 1.9949 | 28.3941 | 98.7438 | 68.7297 | 7.2945 | 53.8496 | 1.3694 | 6.1862 | 12.0203 | 73.8874 | 7.1089 | 178.6842 | 152.071 | 201.4587 | 10.3504 | 53.1323 | 2.6603 | 106 | 17.1847 | 22.7658 | 179.1471 | 0
5261 | 715.2084 | 1.9155 | 27.9838 | 109.3868 | 68.404 | 6.992 | 53.077 | 1.1504 | 6.0975 | 12.169 | 71.4063 | 5.65 | 154.9641 | 144.1931 | 198.2831 | 10.108 | 52.4609 | 2.4396 | 96 | 15.5237 | 22.4598 | 178.2232 | 0
5262 | 732.3389 | 1.1655 | 26.88 | 104.2906 | 67.8523 | 6.6638 | 55.8468 | 1.0132 | 5.4482 | 12.0157 | 72.8863 | 4.3763 | 175.2909 | 117.9595 | 192.4977 | 9.7612 | 51.6551 | 2.4073 | 89 | 17.5431 | 22.3636 | 176.9266 | 0.049618
5263 | 747.0642 | 0.77178 | 21.6205 | 97.0363 | 68.1448 | 7.3372 | 54.7255 | 1.2901 | 4.8086 | 11.7558 | 84.3933 | 4.0275 | 183.9106 | 97.8546 | 196.3799 | 9.7912 | 51.1174 | 2.6996 | 92 | 14.5082 | 22.17 | 176.2509 | 0.085816
5264 | 754.6196 | 0.71142 | 19.3467 | 93.8876 | 70.9867 | 6.8582 | 54.6966 | 1.252 | 6.4188 | 14.603 | 97.0253 | 3.9149 | 181.3605 | 93.3063 | 212.7535 | 9.9116 | 51.1479 | 3.2715 | 92 | 14.1575 | 22.5349 | 177.3753 | 0.18839
5265 | 763.0966 | 0.82192 | 19.2212 | 93.2061 | 73.2959 | 7.4034 | 55.2656 | 1.0751 | 9.1945 | 19.6842 | 101.3389 | 4.1076 | 197.6558 | 94.7547 | 232.2522 | 9.689 | 51.7692 | 3.5802 | 97 | 17.2829 | 23.5312 | 181.189 | 0.16294
5266 | 772.8027 | 1.1652 | 19.4474 | 86.5241 | 73.7123 | 7.5922 | 57.2244 | 1.0065 | 6.7322 | 21.8343 | 101.8041 | 3.9415 | 174.8129 | 103.074 | 242.1973 | 9.8141 | 52.4129 | 3.922 | 102 | 19.7753 | 23.7928 | 185.4292 | 0.18437
5267 | 788.8582 | 1.0489 | 19.3373 | 99.5409 | 70.8483 | 7.5539 | 59.4868 | 1.4378 | 5.0359 | 23.6366 | 105.8587 | 4.1214 | 227.3209 | 108.2363 | 246.5981 | 9.8606 | 52.8297 | 4.1001 | 101 | 18.7037 | 23.7184 | 187.1513 | 0.16797
5268 | 807.4533 | 0.95258 | 19.4801 | 96.3583 | 64.7757 | 7.5656 | 56.8317 | 2.989 | 5.023 | 27.1955 | 114.0511 | 4.0496 | 137.4153 | 115.3976 | 241.7712 | 9.7429 | 53.4899 | 4.2402 | 107 | 18.227 | 23.7054 | 186.4742 | 0.21439
5269 | 818.4597 | 2.0856 | 19.3381 | 93.8979 | 60.5249 | 7.7235 | 53.7452 | 2.3568 | 5.0803 | 26.7482 | 122.4608 | 4.1584 | 168.0013 | 125.7519 | 230.279 | 9.6542 | 53.9775 | 4.512 | 111 | 19.2011 | 22.9727 | 185.7421 | 0.13473
5270 | 815.1152 | 3.0692 | 19.2568 | 98.7026 | 49.8445 | 7.5636 | 57.0364 | 1.1688 | 4.912 | 22.4823 | 133.2259 | 4.7918 | 189.0085 | 120.7834 | 221.3145 | 9.9025 | 54.3687 | 4.7566 | 110 | 19.2839 | 22.4606 | 186.8295 | 0.10886
5271 | 818.7981 | 1.9971 | 19.2727 | 99.5332 | 41.9206 | 6.8735 | 59.8585 | 1.1738 | 4.8661 | 19.6708 | 131.3951 | 7.188 | 190.65 | 108.9262 | 217.986 | 9.8874 | 55.382 | 4.4777 | 107 | 19.1216 | 22.6588 | 188.751 | 0.077321
5272 | 824.8397 | 0.98833 | 19.0152 | 89.771 | 50.7269 | 6.6287 | 55.8098 | 1.1001 | 5.0851 | 18.3158 | 109.375 | 7.1577 | 194.3089 | 104.0629 | 217.2123 | 9.8561 | 55.7217 | 4.1744 | 99 | 19.5142 | 22.1864 | 187.0801 | 0.14804
5273 | 816.6236 | 1.1449 | 19.0773 | 100.9844 | 58.3055 | 7.3601 | 55.8576 | 1.0043 | 4.9933 | 17.4483 | 93.1394 | 4.776 | 192.5216 | 101.5145 | 228.934 | 9.8911 | 55.0343 | 4.0005 | 106 | 19.2523 | 21.9308 | 184.1888 | 0.048854
5274 | 797.2874 | 1.0118 | 19.1462 | 88.8575 | 61.3586 | 7.6565 | 59.3964 | 1.1695 | 5.281 | 17.1711 | 89.1016 | 4.9396 | 204.2419 | 98.8013 | 238.7145 | 9.8363 | 55.5897 | 3.6996 | 121 | 18.8523 | 22.3355 | 184.7007 | 0.035089
5275 | 777.2582 | 0.82179 | 19.4197 | 100.1161 | 61.1388 | 8.9462 | 58.9389 | 1.1186 | 4.9145 | 16.9346 | 83.1334 | 5.477 | 172.879 | 96.38 | 232.5011 | 9.9443 | 56.6773 | 3.5694 | 119 | 16.7677 | 22.5115 | 185.1501 | 0.029655
5276 | 769.6362 | 2.0084 | 20.4483 | 99.0909 | 59.409 | 8.7967 | 55.0488 | 0.98099 | 4.6133 | 16.6361 | 75.7313 | 5.4524 | 177.5778 | 92.616 | 215.3712 | 10.2191 | 55.4398 | 3.3431 | 118 | 16.4924 | 29.2294 | 185.2825 | 0.0026062
5277 | 767.6772 | 2.8288 | 26.2127 | 98.4872 | 48.1315 | 8.5587 | 57.5376 | 1.2295 | 4.6767 | 16.5841 | 74.0165 | 6.5105 | 176.3901 | 88.8243 | 201.6211 | 10.3036 | 53.3978 | 2.8738 | 109 | 14.8516 | 17.64 | 183.405 | 0
5278 | 756.6173 | 2.6687 | 28.7425 | 100.0081 | 39.5612 | 7.8566 | 60.5059 | 1.3929 | 5.0367 | 16.6036 | 75.4345 | 7.6039 | 231.003 | 88.4636 | 195.0659 | 10.1087 | 52.9717 | 2.6902 | 106 | 18.7887 | 21.1811 | 179.219 | 0
5279 | 740.6349 | 1.6107 | 28.6892 | 100.6825 | 40.2939 | 6.188 | 60.237 | 1.6324 | 5.6 | 15.8753 | 75.3276 | 7.8932 | 198.222 | 89.2726 | 197.7414 | 11.308 | 53.0328 | 2.8707 | 106 | 16.5494 | 29.0918 | 176.0374 | 0
5280 | 737.9325 | 1.1455 | 28.8227 | 85.7216 | 41.7952 | 5.7007 | 57.6078 | 1.5602 | 5.6514 | 14.7795 | 73.5377 | 7.8242 | 189.8936 | 87.6758 | 202.6521 | 13.4748 | 52.8311 | 2.8235 | 102 | 15.3799 | 17.5074 | 173.7587 | 0
5281 | 733.5562 | 1.2232 | 38.5519 | 104.6619 | 49.8325 | 7.1743 | 56.3028 | 1.4152 | 6.0535 | 14.4332 | 71.7778 | 7.7272 | 203.9726 | 85.6619 | 206.5569 | 14.5447 | 53.0554 | 2.7416 | 101 | 17.6517 | 21.4122 | 175.3836 | 0
5282 | 725.3043 | 1.3528 | 21.3408 | 87.5309 | 57.1245 | 6.8641 | 56.4397 | 1.4117 | 6.0953 | 14.457 | 71.0845 | 7.9462 | 315.7466 | 85.6971 | 204.4246 | 14.4111 | 53.4323 | 2.6998 | 100 | 14.785 | 22.7569 | 177.8127 | 0
5283 | 727.541 | 1.1739 | 26.2502 | 103.2531 | 60.3934 | 5.9556 | 55.1951 | 1.4282 | 5.878 | 15.1969 | 71.0903 | 7.963 | 162.8281 | 85.3259 | 203.8457 | 11.6612 | 53.6185 | 2.6868 | 99 | 17.8596 | 22.6286 | 178.0881 | 0
5284 | 733.9089 | 1.4721 | 28.8054 | 98.4823 | 62.2735 | 7.67 | 55.7066 | 1.4423 | 5.5353 | 18.8239 | 71.134 | 7.92 | 208.7949 | 83.8388 | 201.3226 | 10.2321 | 53.5396 | 2.6918 | 98 | 14.9507 | 22.5831 | 188.5045 | 0
5285 | 734.0031 | 2.4098 | 34.6909 | 88.3926 | 66.657 | 7.1991 | 55.8953 | 1.499 | 5.4333 | 23.4754 | 69.5854 | 7.8421 | 218.3799 | 84.0646 | 200.8458 | 10.1372 | 52.9127 | 2.5671 | 93 | 15.1743 | 22.7252 | 206.3985 | 0
5286 | 764.1995 | 2.6212 | 46.9501 | 122.4663 | 68.7065 | 10.1687 | 61.0849 | 1.2525 | 5.27 | 27.5726 | 80.0415 | 13.0888 | 204.9506 | 102.7821 | 204.1596 | 9.9874 | 52.4279 | 2.4279 | 127 | 20.2707 | 23.1214 | 242.0004 | 0.030559
5287 | 817.8178 | 2.8967 | 63.1348 | 118.7752 | 69.429 | 12.7811 | 86.4736 | 1.7094 | 5.0906 | 29.3011 | 109.7097 | 22.4613 | 228.2906 | 146.2517 | 216.7619 | 12.7432 | 54.548 | 2.633 | 207 | 33.9599 | 28.2588 | 299.4573 | 0.094027
5288 | 891.3419 | 3.2656 | 72.76 | 116.9005 | 66.211 | 15.4146 | 116.7478 | 2.9849 | 6.9352 | 25.4524 | 139.0725 | 24.9268 | 169.3742 | 188.9206 | 256.5823 | 14.7802 | 60.2503 | 3.2089 | 174 | 46.8057 | 30.2165 | 354.7386 | 0.13193
5289 | 960.6936 | 2.4317 | 79.5101 | 126.3733 | 56.8848 | 16.7227 | 121.6401 | 3.7897 | 9.5775 | 20.6585 | 158.3602 | 23.9441 | 209.0794 | 218.5458 | 304.9397 | 17.399 | 68.4723 | 3.7806 | 226 | 47.847 | 30.3783 | 402.4179 | 0.044463
5290 | 977.9052 | 2.2831 | 84.5751 | 107.3959 | 52.9874 | 15.8944 | 121.8351 | 3.9888 | 6.8732 | 19.7532 | 169.0554 | 24.6222 | 204.9199 | 234.8174 | 333.1295 | 21.9769 | 81.2429 | 4.0027 | 240 | 48.3626 | 31.0977 | 429.4094 | 0.22918
5291 | 966.3952 | 2.6342 | 84.8807 | 158.451 | 53.5469 | 15.2911 | 124.1917 | 4.1509 | 5.4786 | 23.8368 | 174.9941 | 25.1217 | 230.6023 | 237.3948 | 341.5388 | 18.5687 | 95.4402 | 4.1352 | 194 | 43.3867 | 30.7323 | 428.0828 | 0.21691
5292 | 980.3958 | 2.5389 | 86.4985 | 119.2071 | 52.1944 | 15.1759 | 130.0617 | 4.0591 | 5.9049 | 28.1027 | 178.6165 | 25.5165 | 257.8525 | 236.7282 | 337.8463 | 15.4 | 102.4986 | 4.3021 | 225 | 39.3252 | 39.4387 | 419.2725 | 0.19566
5293 | 996.3281 | 2.7949 | 90.7065 | 166.4236 | 51.5555 | 16.575 | 127.9511 | 4.2421 | 5.5411 | 36.9563 | 179.5249 | 27.2156 | 223.6963 | 240.2817 | 328.783 | 15.9671 | 103.3836 | 4.5883 | 210 | 41.2412 | 23.8108 | 417.9414 | 0.1814
5294 | 1031.1974 | 2.7498 | 88.7068 | 123.2018 | 54.4105 | 15.0575 | 109.5221 | 4.5689 | 5.392 | 47.425 | 180.2135 | 26.3871 | 252.3792 | 248.0495 | 329.331 | 15.6698 | 102.8769 | 4.8444 | 205 | 47.5373 | 37.5402 | 416.748 | 0.23228
5295 | 1017.4328 | 2.8308 | 75.5204 | 143.5863 | 56.187 | 12.0887 | 84.0143 | 4.1732 | 9.3469 | 43.7251 | 169.6734 | 24.6014 | 267.3826 | 241.7265 | 334.4166 | 15.5129 | 100.3946 | 5.2225 | 183 | 45.7475 | 23.8108 | 406.9146 | 0.20039
5296 | 985.0316 | 2.5931 | 45.0555 | 119.1464 | 51.8308 | 14.2055 | 76.607 | 3.9681 | 12.5142 | 33.8087 | 149.55 | 23.3065 | 245.6935 | 222.108 | 335.0116 | 14.39 | 97.5216 | 5.2244 | 152 | 28.0626 | 28.6657 | 374.6116 | 0.1438
5297 | 945.9677 | 2.449 | 30.9372 | 108.4566 | 57.044 | 10.1629 | 74.2473 | 3.4933 | 11.359 | 26.5825 | 132.3221 | 22.2884 | 204.7879 | 204.8776 | 322.7381 | 11.458 | 95.6729 | 5.2758 | 143 | 23.7198 | 29.6879 | 316.4904 | 0.16518
5298 | 908.6793 | 2.0153 | 29.9605 | 101.285 | 60.4708 | 7.9548 | 66.8383 | 2.0484 | 7.108 | 21.0592 | 115.2842 | 17.7553 | 207.1262 | 178.2782 | 295.3463 | 9.6282 | 92.8157 | 5.0671 | 143 | 18.7033 | 33.4642 | 263.0518 | 0.078003
5299 | 861.7574 | 1.5165 | 28.4978 | 98.4324 | 60.1529 | 7.612 | 63.2499 | 1.1563 | 5.2962 | 18.5329 | 102.0039 | 7.8234 | 224.1267 | 139.9416 | 271.3648 | 9.1462 | 88.8755 | 4.4671 | 130 | 18.381 | 19.1636 | 220.9053 | 0.043219
5300 | 828.8071 | 2.5291 | 27.5171 | 99.0779 | 59.1486 | 8.2808 | 62.1498 | 1.0242 | 5.2847 | 17.8807 | 93.6077 | 3.9444 | 242.4331 | 111.6952 | 256.8828 | 9.0375 | 84.0933 | 3.8044 | 126 | 14.7994 | 30.0218 | 187.0966 | 0.0066219
5301 | 803.8327 | 3.1706 | 32.6426 | 100.0635 | 61.1742 | 7.891 | 59.4358 | 1.4229 | 5.7342 | 17.6837 | 87.1455 | 5.2013 | 259.5567 | 101.0809 | 245.5993 | 9.4523 | 80.1468 | 3.6785 | 118 | 15.1989 | 19.3057 | 172.1638 | 0
5302 | 787.3646 | 2.6894 | 35.1235 | 80.3556 | 64.1388 | 6.8378 | 55.8095 | 1.529 | 6.2786 | 17.5293 | 83.2467 | 6.2902 | 183.9497 | 97.359 | 227.9919 | 9.4198 | 78.2728 | 3.8037 | 111 | 12.4642 | 22.9679 | 169.5729 | 0
5303 | 767.2852 | 1.9211 | 34.9843 | 102.2972 | 64.0292 | 7.3475 | 62.0284 | 1.4313 | 6.3837 | 16.6329 | 80.1965 | 6.8033 | 187.7235 | 93.6341 | 216.2176 | 10.1587 | 77.7815 | 4.0173 | 106 | 11.445 | 24.4998 | 172.6535 | 0
5304 | 762.6684 | 1.6169 | 34.6073 | 95.3914 | 60.8127 | 8.9884 | 56.9329 | 1.4917 | 6.398 | 15.4527 | 77.7133 | 6.8789 | 214.3337 | 90.4368 | 211.1079 | 12.5707 | 78.8916 | 4.0107 | 105 | 13.5377 | 22.994 | 172.4549 | 0
5305 | 770.496 | 1.3048 | 33.7031 | 90.4072 | 60.7536 | 7.4098 | 56.4201 | 1.6221 | 6.2867 | 14.932 | 76.8452 | 6.8908 | 201.0767 | 88.0912 | 211.2161 | 14.0657 | 79.512 | 3.5639 | 103 | 13.3228 | 22.3199 | 168.4144 | 0
5306 | 760.8881 | 1.3302 | 33.5574 | 90.5839 | 61.1588 | 6.6058 | 58.529 | 1.5508 | 5.96 | 14.9504 | 77.0894 | 6.7109 | 212.0546 | 85.918 | 218.1784 | 12.1455 | 77.9496 | 3.3366 | 104 | 14.3126 | 22.3271 | 166.8969 | 0
5307 | 758.9607 | 1.4124 | 33.6834 | 90.4965 | 58.221 | 7.354 | 54.6163 | 1.4563 | 6.2122 | 15.8665 | 77.511 | 6.6642 | 221.8491 | 84.9745 | 218.9255 | 10.0656 | 76.6201 | 3.3202 | 101 | 12.1259 | 22.4153 | 166.3898 | 0
5308 | 762.6666 | 1.6302 | 33.5394 | 89.8373 | 57.2811 | 6.8749 | 57.0144 | 1.4396 | 6.1476 | 19.4899 | 77.4285 | 6.6162 | 226.131 | 85.1596 | 220.721 | 9.3332 | 76.4542 | 3.3546 | 100 | 13.6104 | 34.8293 | 175.5603 | 0
5309 | 765.5599 | 2.2959 | 39.7796 | 94.9436 | 55.8787 | 7.9939 | 62.2985 | 1.2123 | 5.893 | 24.2087 | 75.7973 | 7.5903 | 247.1488 | 85.6179 | 218.8406 | 9.2445 | 76.0872 | 3.1622 | 98 | 13.5659 | 21.7991 | 195.7013 | 0
5310 | 790.6435 | 2.3354 | 49.7511 | 91.25 | 50.9311 | 12.0547 | 61.3675 | 1.2627 | 5.505 | 28.3237 | 84.9401 | 14.2139 | 208.1575 | 100.9387 | 210.6131 | 9.1616 | 75.5486 | 3.0072 | 134 | 22.1397 | 34.8407 | 235.1908 | 0.050495
5311 | 836.3366 | 1.9987 | 60.7081 | 134.8835 | 46.9982 | 14.8275 | 66.9922 | 1.8538 | 5.304 | 32.8087 | 113.3228 | 22.2647 | 249.9059 | 140.9055 | 214.2881 | 10.2398 | 77.0486 | 3.3638 | 184 | 39.953 | 22.0014 | 295.7921 | 0.10891
5312 | 885.9587 | 6.7859 | 71.0796 | 150.413 | 44.1249 | 16.6263 | 88.9637 | 2.9418 | 6.5646 | 32.6093 | 144.6563 | 24.0679 | 210.155 | 181.4472 | 247.3451 | 16.3046 | 83.5167 | 3.9911 | 223 | 44.0204 | 26.4995 | 356.0634 | 0.15494
5313 | 951.1173 | 10.0676 | 78.0703 | 163.6148 | 44.4577 | 16.3306 | 96.6488 | 3.679 | 10.6596 | 27.1456 | 161.5526 | 24.351 | 247.3689 | 207.2713 | 295.8023 | 19.9887 | 94.4582 | 4.744 | 250 | 45.1551 | 36.4597 | 405.165 | 0.16927
5314 | 1016.5177 | 10.3958 | 82.3709 | 176.0544 | 46.5086 | 16.1765 | 95.1429 | 3.7941 | 13.9409 | 23.762 | 164.1324 | 24.775 | 228.3436 | 222.5428 | 321.2714 | 16.937 | 103.0019 | 5.5036 | 232 | 49.7413 | 21.8552 | 441.2174 | 0.17499
5315 | 1045.6914 | 8.3755 | 85.6569 | 181.0743 | 44.5042 | 19.0265 | 95.2061 | 4.0545 | 14.712 | 29.9223 | 166.7057 | 24.5951 | 275.2341 | 235.3655 | 327.9304 | 14.7416 | 106.2309 | 5.9371 | 227 | 54.7458 | 26.5413 | 466.8921 | 0.24039
5316 | 1048.608 | 6.0589 | 88.2478 | 184.8964 | 48.0729 | 17.1026 | 100.9262 | 4.1675 | 13.8575 | 40.2126 | 173.7044 | 24.8061 | 232.2826 | 244.9055 | 325.7262 | 14.7666 | 107.482 | 6.2153 | 238 | 50.071 | 36.5641 | 481.2818 | 0.24595
5317 | 1074.6606 | 5.5071 | 90.5066 | 175.4902 | 49.3712 | 18.2055 | 104.6471 | 3.9491 | 12.9663 | 46.1232 | 180.5899 | 25.0563 | 231.1943 | 247.7864 | 325.9635 | 14.5156 | 108.5575 | 6.2121 | 208 | 49.9226 | 21.8692 | 482.2579 | 0.26663
5318 | 1081.4802 | 5.365 | 87.8649 | 198.2411 | 50.7775 | 18.8843 | 98.3338 | 3.9084 | 8.3194 | 48.166 | 183.3251 | 28.1316 | 233.2818 | 253.0233 | 332.3185 | 14.3779 | 108.605 | 5.9343 | 202 | 52.1072 | 34.7706 | 473.916 | 0.20676
5319 | 1077.4964 | 3.4681 | 75.7352 | 168.032 | 52.5564 | 18.273 | 86.4783 | 3.8264 | 7.2708 | 44.9555 | 171.0638 | 29.1308 | 231.6678 | 248.7379 | 332.1004 | 14.4888 | 105.2324 | 6.2267 | 193 | 37.6573 | 21.7619 | 461.7411 | 0.17731
5320 | 1047.9744 | 2.3111 | 45.8959 | 121.7899 | 53.316 | 16.1093 | 76.6931 | 3.6272 | 9.7453 | 37.8058 | 149.9777 | 28.4715 | 226.2362 | 223.0616 | 323.3469 | 12.9539 | 100.5575 | 6.2874 | 156 | 27.652 | 26.622 | 429.1194 | 0.15462
5321 | 986.6639 | 2.0936 | 31.4725 | 99.9795 | 54.7608 | 13.8537 | 67.7396 | 2.6915 | 7.7741 | 31.7196 | 131.0932 | 25.3245 | 226.4827 | 188.5996 | 313.3832 | 9.3562 | 96.7094 | 6.4137 | 153 | 19.2541 | 36.5767 | 366.3146 | 0.1206
5322 | 946.1683 | 1.5797 | 29.1714 | 91.1601 | 59.6574 | 9.7567 | 61.2966 | 1.6787 | 5.8312 | 30.7888 | 112.9444 | 18.7291 | 225.9027 | 156.8916 | 291.4853 | 7.7176 | 93.6991 | 6.0307 | 146 | 17.5925 | 21.9919 | 308.8297 | 0.1196
5323 | 921.8342 | 1.5896 | 27.9025 | 84.1848 | 62.2703 | 6.4613 | 59.8062 | 1.3309 | 5.56 | 30.6895 | 100.6981 | 8.3593 | 256.8731 | 135.7364 | 267.6967 | 7.6342 | 91.0588 | 5.0931 | 128 | 17.6025 | 25.9828 | 270.3208 | 0.061034
5324 | 891.6066 | 2.5753 | 22.4285 | 77.8171 | 59.4057 | 7.0125 | 61.7086 | 1.537 | 5.7247 | 27.3346 | 93.9296 | 4.3195 | 193.372 | 127.7164 | 248.7552 | 7.7096 | 87.9784 | 4.2629 | 116 | 15.1395 | 25.2358 | 230.5224 | 0.0068912
5325 | 859.4921 | 3.3139 | 19.7086 | 76.7304 | 56.5793 | 7.5949 | 62.4839 | 1.7205 | 5.5683 | 23.8193 | 87.3526 | 5.4436 | 256.771 | 125.0378 | 239.3777 | 7.8259 | 85.3356 | 3.4607 | 111 | 15.022 | 22.7968 | 203.557 | 0
5326 | 837.2716 | 2.8496 | 19.5108 | 62.0826 | 55.5767 | 7.719 | 58.2107 | 1.7435 | 6.2895 | 22.2403 | 81.8192 | 6.7416 | 195.6925 | 126.3225 | 236.3415 | 8.0708 | 82.8413 | 3.0846 | 109 | 17.3929 | 22.3919 | 200.5632 | 0
5327 | 813.965 | 1.7334 | 19.5892 | 77.6078 | 55.5152 | 7.5641 | 56.8488 | 1.7652 | 6.3808 | 21.6433 | 78.661 | 7.0954 | 133.7475 | 122.9526 | 237.4381 | 8.2887 | 81.1471 | 3.053 | 106 | 17.97 | 22.2878 | 199.8685 | 0
5328 | 800.3764 | 1.4698 | 19.5601 | 77.7849 | 55.2914 | 6.9071 | 61.2595 | 1.7417 | 6.2333 | 19.9018 | 77.6177 | 6.918 | 149.4304 | 114.1075 | 228.5137 | 8.198 | 80.4067 | 3.1798 | 104 | 16.0351 | 30.204 | 195.1453 | 0
5329 | 796.6905 | 1.7026 | 19.3106 | 87.2554 | 52.9249 | 7.3374 | 59.894 | 2.0052 | 6.1986 | 17.9589 | 77.515 | 6.8676 | 197.6874 | 110.6605 | 215.708 | 8.0415 | 79.7811 | 3.1047 | 104 | 17.4033 | 18.3219 | 193.7911 | 0
5330 | 790.2963 | 1.4201 | 19.5255 | 79.8163 | 51.1301 | 7.5986 | 56.3203 | 1.9156 | 5.9203 | 17.4639 | 76.8879 | 7.3126 | 169.906 | 111.6299 | 219.6273 | 8.0818 | 79.4779 | 3.02 | 102 | 16.3921 | 29.0594 | 193.6625 | 0
5331 | 776.0774 | 1.4234 | 19.6427 | 61.5874 | 49.359 | 8.3734 | 60.6124 | 1.7678 | 6.0144 | 18.2317 | 75.9 | 7.0705 | 190.2474 | 111.5011 | 228.1366 | 8.1686 | 79.3557 | 2.992 | 101 | 18.4162 | 18.4807 | 194.1269 | 0
5332 | 785.1648 | 1.8301 | 19.5467 | 87.215 | 50.1239 | 7.7342 | 57.7962 | 1.8072 | 5.9451 | 21.8881 | 75.3073 | 6.7679 | 147.3799 | 109.8662 | 221.782 | 7.9016 | 79.2871 | 2.9552 | 97 | 16.0632 | 21.9933 | 200.6318 | 0
5333 | 798.2002 | 2.6577 | 27.0405 | 95.4921 | 49.3466 | 7.5964 | 57.1001 | 1.7303 | 5.8293 | 26.7283 | 74.3577 | 7.9323 | 165.8044 | 109.0267 | 217.7106 | 7.7959 | 79.234 | 2.914 | 102 | 17.0751 | 30.5985 | 218.7528 | 0
5334 | 838.3091 | 3.4111 | 42.9212 | 102.2667 | 44.0383 | 11.1297 | 65.3414 | 1.4982 | 5.8167 | 30.3184 | 84.2186 | 14.9032 | 192.2305 | 119.8663 | 216.2614 | 8.0471 | 79.184 | 2.7705 | 134 | 23.1458 | 23.6913 | 256.9653 | 0.0080676
5335 | 895.2546 | 2.9387 | 60.6199 | 104.5035 | 36.8544 | 16.2995 | 70.4472 | 2.3408 | 5.719 | 33.4243 | 111.8986 | 22.5204 | 179.3298 | 154.3112 | 223.2082 | 10.0434 | 80.5402 | 2.9455 | 178 | 47.4706 | 18.0009 | 319.7766 | 0.0293
5336 | 943.749 | 2.9962 | 71.1957 | 118.0837 | 28.1162 | 19.5704 | 84.6197 | 3.7122 | 7.5997 | 31.2297 | 143.7796 | 26.5597 | 226.8154 | 194.5691 | 256.1175 | 12.8462 | 85.9441 | 3.4997 | 231 | 51.6046 | 26.9073 | 391.2339 | 0.041203
5337 | 1005.4402 | 2.7792 | 80.4853 | 127.5143 | 20.6172 | 21.4659 | 97.4166 | 4.7033 | 9.9148 | 25.9992 | 167.8394 | 25.6871 | 266.2727 | 226.3682 | 300.9622 | 14.2025 | 95.1661 | 4.2436 | 274 | 55.1334 | 30.6724 | 441.9449 | 0.053768
5338 | 1047.4938 | 2.4104 | 80.9474 | 132.5013 | 5.0128 | 19.8165 | 99.6354 | 5.8706 | 7.1458 | 28.4143 | 180.318 | 26.2488 | 248.4425 | 249.3424 | 331.0584 | 14.8544 | 103.5823 | 5.2214 | 234 | 60.0453 | 39.1552 | 462.3532 | 0.097322
5339 | 1064.83 | 3.3918 | 81.4626 | 135.7401 | -6.9137 | 19.0454 | 107.4534 | 6.8207 | 6.2292 | 35.5586 | 187.5442 | 27.0075 | 276.2324 | 261.2783 | 343.8036 | 15.4529 | 109.2847 | 5.8457 | 231 | 63.8392 | 30.4067 | 462.9929 | 0.099628
5340 | 1072.5063 | 3.0293 | 84.1673 | 136.5905 | -6.6579 | 18.7953 | 100.6455 | 6.7675 | 6.2772 | 39.9077 | 189.82 | 26.3632 | 283.2481 | 264.8476 | 345.376 | 16.3645 | 113.147 | 5.8327 | 265 | 65.7278 | 23.4549 | 458.1492 | 0.14641
5341 | 1074.1971 | 2.9638 | 85.605 | 112.4432 | -6.2816 | 18.4379 | 95.4648 | 6.6906 | 5.6364 | 45.8415 | 186.2194 | 27.1576 | 284.3811 | 264.8946 | 341.8855 | 17.694 | 114.7003 | 6.5078 | 205 | 57.3513 | 29.0084 | 457.9175 | 0.11935
5342 | 1076.5709 | 2.8834 | 86.8239 | 165.8214 | -5.0229 | 17.2444 | 99.8041 | 5.6103 | 5.6449 | 52.1369 | 182.92 | 29.5625 | 295.3873 | 265.3515 | 354.3499 | 17.5522 | 112.7203 | 6.9157 | 202 | 60.5164 | 30.8693 | 455.555 | 0.15058
5343 | 1086.8024 | 2.8846 | 84.5358 | 140.094 | -3.617 | 15.9115 | 102.0739 | 4.6716 | 5.4499 | 50.3725 | 170.879 | 29.0287 | 318.8545 | 262.7217 | 360.672 | 16.9353 | 107.7264 | 6.9356 | 208 | 53.2661 | 33.7265 | 443.3737 | 0.16566
5344 | 1045.2849 | 2.7551 | 73.7867 | 118.7137 | 1.646 | 10.9131 | 101.0914 | 4.0166 | 5.2613 | 44.7029 | 149.3096 | 27.6484 | 305.1741 | 244.6081 | 345.9671 | 14.9142 | 102.4211 | 6.4469 | 167 | 43.152 | 18.9291 | 402.2288 | 0.146
5345 | 988.5475 | 2.4186 | 66.7979 | 88.5142 | 3.8725 | 8.7979 | 78.923 | 2.9417 | 5.2451 | 39.3513 | 128.4595 | 27.8892 | 279.221 | 208.2415 | 333.6412 | 11.0657 | 97.709 | 6.3237 | 174 | 32.8083 | 29.8963 | 332.995 | 0.15532
5346 | 947.533 | 1.8326 | 64.2548 | 102.4813 | 4.8297 | 7.8878 | 63.6332 | 1.9551 | 5.2743 | 31.8182 | 109.6475 | 23.0282 | 275.9114 | 168.0818 | 318.5326 | 9.0202 | 93.6311 | 5.951 | 154 | 23.3329 | 19.0978 | 271.9444 | 0.14956
5347 | 896.8714 | 1.3176 | 63.2564 | 99.115 | 5.22 | 7.5185 | 66.3037 | 1.5438 | 5.15 | 25.1881 | 97.0754 | 11.6121 | 230.8194 | 136.0192 | 282.9323 | 8.5737 | 90.3776 | 5.7044 | 128 | 19.92 | 29.7277 | 229.1385 | 0.097713
5348 | 863.0539 | 2.0802 | 61.8988 | 112.4179 | 5.1165 | 7.6161 | 60.0244 | 1.4192 | 5.0882 | 22.5694 | 91.4752 | 9.3786 | 242.6981 | 118.6698 | 255.4568 | 8.6297 | 87.0531 | 5.419 | 122 | 17.75 | 19.0275 | 211.0087 | 0.0061487
5349 | 848.0774 | 3.0665 | 60.7277 | 104.2474 | 5.0788 | 7.6468 | 60.7346 | 1.7482 | 5.1214 | 22.5944 | 85.6288 | 10.6853 | 217.7795 | 113.7469 | 248.9744 | 9.0478 | 83.3647 | 4.5437 | 118 | 16.9915 | 22.9421 | 216.9657 | 0
5350 | 827.3178 | 2.6162 | 61.0967 | 101.5473 | 5.2071 | 7.5317 | 63.7093 | 1.8123 | 5.6119 | 24.544 | 79.5662 | 9.1895 | 205.8523 | 112.548 | 250.2629 | 9.2499 | 80.9902 | 4.2768 | 117 | 17.0366 | 24.1983 | 226.6235 | 0
5351 | 813.6074 | 1.5069 | 61.2918 | 107.9294 | 5.0887 | 7.6485 | 65.5775 | 1.681 | 6.2767 | 26.8383 | 76.9672 | 8.3755 | 195.2583 | 110.1849 | 240.2578 | 9.3954 | 80.0713 | 4.5393 | 118 | 15.8985 | 31.4842 | 231.6425 | 0
5352 | 811.797 | 1.2193 | 60.942 | 110.9324 | 5.1627 | 7.5737 | 70.3213 | 1.6713 | 6.2833 | 27.6162 | 75.7817 | 8.3247 | 254.2849 | 105.0683 | 228.9673 | 9.6802 | 79.3388 | 4.6188 | 113 | 15.3061 | 18.9618 | 225.8507 | 0
5353 | 808.1328 | 1.2382 | 81.9651 | 110.9709 | 5.1447 | 7.59 | 75.0059 | 1.6806 | 6.1 | 27.3653 | 74.9663 | 8.285 | 193.681 | 101.1487 | 225.0977 | 9.4087 | 78.8948 | 4.3371 | 107 | 17.9241 | 29.8636 | 214.5132 | 0
5354 | 804.6773 | 1.2137 | 45.2713 | 111.3266 | 5.2169 | 7.5192 | 76.0603 | 1.8519 | 6.06 | 25.6683 | 74.8953 | 8.5508 | 253.822 | 100.7533 | 222.3731 | 8.9794 | 78.8577 | 3.6569 | 106 | 15.6611 | 18.7675 | 208.4312 | 0
5355 | 804.9681 | 1.3642 | 45.4469 | 101.1734 | 5.1083 | 7.6223 | 75.7811 | 1.8909 | 6.0397 | 23.1439 | 74.9075 | 8.7435 | 181.705 | 100.6378 | 216.6201 | 9.1028 | 78.7576 | 3.3699 | 107 | 15.9441 | 20.568 | 206.4553 | 0
5356 | 808.0713 | 1.7754 | 33.5033 | 82.8124 | 5.1032 | 7.6268 | 75.8852 | 1.7553 | 6.2118 | 25.8671 | 74.6685 | 8.7314 | 210.4703 | 99.9506 | 217.4523 | 9.1643 | 78.6032 | 3.3106 | 104 | 16.5029 | 21.3071 | 211.6634 | 0
5357 | 815.2616 | 2.4083 | 38.3656 | 68.164 | 5.0717 | 7.6595 | 76.7525 | 1.4929 | 5.8875 | 31.0394 | 72.8894 | 8.6936 | 241.2886 | 100.0363 | 216.2398 | 8.7846 | 77.9982 | 3.1056 | 105 | 14.9839 | 21.2699 | 228.7115 | 0
5358 | 845.536 | 2.5992 | 53.0444 | 116.335 | 0.7703 | 11.7434 | 82.6815 | 1.3282 | 5.4646 | 34.9886 | 86.8435 | 13.7041 | 215.2808 | 117.4333 | 215.3914 | 8.5764 | 77.1341 | 2.9479 | 124 | 23.6653 | 21.739 | 267.1868 | 0.060341
5359 | 909.6515 | 2.144 | 59.6406 | 100.6245 | -3.2192 | 15.5282 | 77.487 | 2.8793 | 5.2225 | 42.8879 | 123.3781 | 23.8946 | 224.3234 | 159.7976 | 226.5994 | 9.5704 | 78.4828 | 3.1631 | 193 | 48.511 | 35.669 | 326.405 | 0.13951
5360 | 965.2919 | 3.993 | 71.7399 | 151.5421 | -6.8349 | 18.9604 | 85.1841 | 5.3096 | 7.0855 | 51.7299 | 151.9657 | 28.4243 | 249.6314 | 204.1954 | 257.2185 | 13.0158 | 84.8884 | 3.9544 | 223 | 54.3373 | 22.6296 | 399.3999 | 0.17658
5361 | 1018.2566 | 5.6246 | 77.696 | 140.4694 | -5.568 | 17.7584 | 96.9483 | 6.2049 | 7.9551 | 55.263 | 164.7273 | 28.4845 | 223.6251 | 233.3764 | 300.6433 | 14.8759 | 94.9782 | 5.0809 | 271 | 59.3821 | 27.0063 | 447.7123 | 0.2828
5362 | 1077.0419 | 5.4974 | 79.0608 | 172.9734 | -4.1602 | 16.4235 | 99.3172 | 5.9675 | 6.6758 | 56.3214 | 174.2304 | 26.6566 | 249.8867 | 247.0962 | 335.3381 | 14.9431 | 103.5335 | 5.4675 | 232 | 68.4066 | 29.0047 | 453.3587 | 0.28402
5363 | 1090.2209 | 4.9182 | 78.8639 | 166.5568 | -3.2369 | 15.5495 | 101.6367 | 6.629 | 11.9165 | 56.7615 | 178.0149 | 24.8474 | 226.6872 | 252.5945 | 355.8395 | 15.0821 | 107.825 | 5.3878 | 241 | 73.24 | 29.2897 | 447.2237 | 0.27384
5364 | 1083.03 | 3.9607 | 79.6031 | 161.7552 | -4.1546 | 16.42 | 99.8486 | 6.2395 | 14.869 | 58.3103 | 176.7405 | 24.9602 | 255.5205 | 254.7168 | 356.2763 | 15.9907 | 108.3864 | 5.3748 | 249 | 70.4682 | 28.9266 | 441.1091 | 0.28606
5365 | 1077.7494 | 5.2335 | 83.5604 | 147.6424 | -2.7762 | 15.1107 | 103.2478 | 5.634 | 12.2794 | 62.7137 | 176.1674 | 27.755 | 228.7578 | 257.2446 | 350.0644 | 16.1988 | 107.4874 | 5.669 | 217 | 61.2303 | 29.2697 | 444.562 | 0.29072
5366 | 1086.1862 | 5.592 | 80.9189 | 165.1668 | -4.0975 | 16.3676 | 103.4301 | 4.8367 | 7.5416 | 64.403 | 176.1684 | 29.19 | 241.0819 | 257.1989 | 347.9498 | 16.0868 | 106.4613 | 5.9344 | 205 | 60.0578 | 28.9829 | 441.7451 | 0.28425
5367 | 1065.2084 | 4.0501 | 72.454 | 149.4505 | -1.118 | 13.5391 | 89.5102 | 4.2412 | 5.374 | 61.2382 | 165.8462 | 25.8512 | 303.4816 | 245.3309 | 340.1951 | 15.5712 | 103.8673 | 5.777 | 195 | 59.3921 | 37.5211 | 424.9572 | 0.28656
5368 | 1026.1406 | 3.0191 | 46.4722 | 123.2124 | 3.1367 | 9.4994 | 91.9816 | 3.8523 | 5.6543 | 56.0264 | 145.1324 | 22.9569 | 211.7629 | 215.0097 | 342.938 | 13.8274 | 99.9819 | 5.7921 | 160 | 44.2797 | 22.4983 | 388.7185 | 0.26559
5369 | 987.1761 | 2.2582 | 33.832 | 95.0269 | 3.4294 | 9.2232 | 94.087 | 3.2372 | 5.7398 | 51.2254 | 125.2724 | 24.266 | 242.1146 | 174.254 | 345.608 | 11.9829 | 95.4505 | 6.0328 | 151 | 35.652 | 26.544 | 325.6902 | 0.25037
5370 | 953.8748 | 1.6049 | 32.2405 | 82.7844 | 3.8265 | 8.8449 | 86.5484 | 2.1854 | 5.74 | 46.8384 | 107.1789 | 21.0336 | 220.2387 | 139.967 | 324.3523 | 10.958 | 89.9192 | 5.6339 | 148 | 29.2649 | 28.0988 | 267.1655 | 0.21314
5371 | 920.2755 | 2.1977 | 46.6118 | 79.5112 | 4.0951 | 8.5908 | 70.8312 | 1.3284 | 5.6983 | 43.0203 | 95.1899 | 9.0108 | 245.0023 | 120.0847 | 283.0965 | 10.0051 | 84.608 | 5.8655 | 128 | 23.295 | 27.2767 | 228.851 | 0.11868
5372 | 891.5196 | 2.729 | 35.7564 | 60.1099 | 0.43382 | 12.0709 | 61.8118 | 1.1651 | 5.6247 | 39.5345 | 89.925 | 3.9148 | 230.8562 | 108.4397 | 245.6931 | 9.8009 | 80.1805 | 6.114 | 125 | 19.2833 | 24.4318 | 207.0874 | 0.010583
5373 | 871.0171 | 3.1754 | 26.6122 | 91.5651 | -2.325 | 14.6906 | 61.4603 | 1.5939 | 5.65 | 38.2397 | 83.8254 | 5.0677 | 277.6974 | 104.126 | 233.1795 | 9.9441 | 77.1587 | 5.256 | 122 | 18.8255 | 22.1071 | 202.0747 | 0
5374 | 853.3719 | 2.9017 | 32.62 | 66.0579 | 1.6329 | 10.9305 | 67.1648 | 1.7071 | 6.0433 | 39.3584 | 77.3697 | 6.4466 | 211.17 | 111.9048 | 231.8899 | 9.647 | 75.9069 | 4.7524 | 117 | 20.2814 | 21.5995 | 203.4921 | 0
5375 | 832.0911 | 1.8788 | 35.9372 | 78.8306 | 3.8243 | 8.8512 | 74.1143 | 1.6027 | 6.2233 | 37.568 | 75.0457 | 6.608 | 179.5394 | 116.1294 | 234.4357 | 9.7111 | 75.5329 | 4.3716 | 115 | 18.0434 | 31.0155 | 203.0878 | 0
5376 | 807.8665 | 1.6303 | 36.0132 | 91.2722 | 4.8687 | 7.8574 | 76.4133 | 1.6273 | 6.2733 | 33.3714 | 74.8351 | 6.6052 | 184.2102 | 108.0574 | 227.3051 | 9.8077 | 75.3745 | 3.9451 | 109 | 19.6859 | 19.3167 | 204.3065 | 0
5377 | 810.2377 | 1.3715 | 36.5383 | 82.0465 | 4.2612 | 8.4363 | 75.8848 | 1.643 | 6.378 | 30.6114 | 74.2756 | 6.5332 | 184.3391 | 102.6385 | 222.8075 | 9.7019 | 75.2958 | 3.5854 | 112 | 18.9219 | 30.2294 | 205.5997 | 0
5378 | 813.6696 | 1.3277 | 46.8154 | 79.7543 | 4.9909 | 7.7429 | 75.1827 | 1.8546 | 6.2849 | 29.5014 | 74.0539 | 7.8819 | 199.496 | 99.2174 | 220.9146 | 9.6293 | 75.0784 | 3.342 | 110 | 19.2971 | 19.2874 | 207.3171 | 0
5379 | 812.5486 | 1.2727 | 26.5463 | 94.7156 | 4.4326 | 8.2726 | 74.9865 | 1.8151 | 6.2771 | 29.8928 | 73.9163 | 8.1326 | 179.3209 | 93.9907 | 221.5143 | 9.7302 | 74.9058 | 3.3047 | 113 | 18.3722 | 23.105 | 207.3947 | 0
5380 | 818.386 | 1.7008 | 32.6709 | 100.6047 | 4.1631 | 8.5294 | 75.2784 | 1.6469 | 6.4344 | 33.0699 | 73.0975 | 7.9365 | 205.766 | 91.1843 | 217.2788 | 9.4597 | 74.7709 | 3.2652 | 112 | 15.6428 | 24.6812 | 213.2514 | 0
5381 | 818.1496 | 1.9358 | 35.7429 | 100.4415 | 5.6578 | 7.1076 | 76.0247 | 1.4321 | 6.3673 | 36.0326 | 70.794 | 8.7962 | 167.618 | 91.0191 | 213.7996 | 8.8938 | 74.1554 | 3.0299 | 123 | 18.4326 | 24.9055 | 227.9979 | 0
5382 | 848.4945 | 2.0629 | 35.7644 | 103.6991 | 3.1787 | 9.4605 | 76.7363 | 1.3232 | 5.6262 | 38.2569 | 78.1881 | 13.6591 | 173.0128 | 105.0933 | 214.9513 | 9.3101 | 73.6604 | 3.0449 | 147 | 28.2223 | 24.5778 | 262.0886 | 0.038953
5383 | 914.4759 | 2.4213 | 48.0549 | 106.4517 | -2.3556 | 14.7138 | 88.6557 | 3.0668 | 5.263 | 43.6537 | 104.4735 | 21.2974 | 184.5607 | 137.4776 | 233.9905 | 11.4289 | 75.608 | 3.4413 | 201 | 45.1042 | 24.8216 | 318.2909 | 0.072521
5384 | 962.0019 | 2.51 | 26.5737 | 136.5425 | -2.4372 | 14.789 | 101.2166 | 6.3197 | 7.1328 | 43.8309 | 139.2531 | 27.4733 | 228.9525 | 175.1597 | 291.2577 | 14.9377 | 81.3954 | 4.308 | 233 | 50.1026 | 24.848 | 376.6867 | 0.071884
5385 | 1021.5065 | 3.0644 | 60.656 | 183.5107 | -2.565 | 14.9135 | 109.4503 | 7.3968 | 9.7671 | 37.9015 | 167.3899 | 28.2629 | 227.5974 | 208.4266 | 353.4675 | 15.9123 | 89.3876 | 5.2333 | 237 | 51.4303 | 24.9602 | 421.4142 | 0.10437
5386 | 1063.5423 | 3.1815 | 76.5502 | 182.9333 | -6.5183 | 18.6677 | 110.7703 | 7.0483 | 6.9593 | 36.6364 | 177.7389 | 26.636 | 271.8166 | 232.9895 | 387.9228 | 16.328 | 95.7938 | 5.9138 | 238 | 58.2894 | 24.6253 | 441.9806 | 0.094013
5387 | 1072.9714 | 2.4795 | 77.3935 | 172.3207 | -7.069 | 19.1877 | 115.835 | 7.0427 | 5.1885 | 39.6548 | 176.3581 | 26.1439 | 278.1934 | 243.6595 | 399.1188 | 16.7658 | 99.46 | 6.4053 | 234 | 55.6961 | 24.6502 | 442.6275 | 0.10779
5388 | 1065.3815 | 2.1771 | 80.9995 | 193.1964 | -4.6038 | 16.8486 | 114.9741 | 6.8463 | 5.3216 | 42.2819 | 178.0947 | 25.2689 | 271.788 | 243.8801 | 395.7939 | 17.169 | 101.6112 | 6.6871 | 246 | 59.5692 | 32.0462 | 439.6067 | 0.0717
5389 | 1071.9885 | 2.6704 | 82.7551 | 192.7886 | -3.2754 | 15.5877 | 117.2208 | 5.8775 | 9.8698 | 43.0245 | 182.4957 | 24.7314 | 296.3887 | 251.124 | 380.9611 | 16.9436 | 103.4804 | 6.6771 | 227 | 58.1642 | 19.2874 | 437.2854 | 0.099405
5390 | 1082.3972 | 2.4575 | 81.3937 | 194.3297 | -2.8984 | 15.2321 | 114.846 | 5.4616 | 12.8533 | 39.5412 | 184.9408 | 24.7274 | 270.0175 | 258.5941 | 378.2892 | 16.7536 | 104.786 | 6.9546 | 223 | 66.4028 | 23.2423 | 426.8935 | 0.06346
5391 | 1066.0366 | 2.4636 | 67.2887 | 166.8358 | 0.90175 | 11.622 | 103.4309 | 4.2208 | 12.2867 | 35.1134 | 174.1717 | 27.6979 | 273.4673 | 251.8087 | 381.185 | 16.1363 | 102.4339 | 6.9291 | 219 | 58.2175 | 24.6288 | 417.3557 | 0.03754
5392 | 1016.8379 | 1.9691 | 43.6812 | 122.2813 | 3.6312 | 9.0246 | 89.8325 | 2.6182 | 12.0467 | 33.9815 | 151.0811 | 27.2968 | 286.9411 | 222.1828 | 362.8487 | 12.7803 | 97.8586 | 6.3593 | 179 | 46.9659 | 24.7441 | 381.5355 | 0.025568
5393 | 976.1046 | 1.1647 | 17.2582 | 91.4871 | 4.1006 | 8.5775 | 87.6729 | 1.7152 | 13.1878 | 33.2726 | 130.4861 | 24.403 | 241.7502 | 184.4553 | 334.7171 | 9.4701 | 94.3652 | 5.9459 | 154 | 37.1297 | 31.9643 | 310.8351 | 0.01532
5394 | 930.0013 | 1.792 | 21.0084 | 101.8694 | 4.8962 | 7.8241 | 81.6157 | 1.2092 | 13.1046 | 36.7831 | 110.6721 | 19.5082 | 240.1375 | 160.7841 | 299.5516 | 8.2826 | 90.3735 | 5.9459 | 169 | 34.2277 | 19.077 | 251.7111 | 0.010763
5395 | 886.7217 | 2.7988 | 31.1096 | 81.9774 | 4.3182 | 8.3765 | 63.0814 | 1.243 | 11.2184 | 45.4463 | 91.4354 | 9.9929 | 226.8959 | 147.7882 | 269.2569 | 8.3833 | 85.1362 | 5.7269 | 152 | 34.0374 | 30.4689 | 217.8793 | 0.0031492
5396 | 864.4498 | 3.1682 | 17.2083 | 91.5607 | 4.908 | 7.8187 | 62.9892 | 1.4296 | 7.6131 | 49.3925 | 79.2355 | 6.67 | 206.9673 | 137.9125 | 250.9913 | 8.7412 | 81.4023 | 5.3497 | 146 | 34.5576 | 24.7736 | 202.8462 | 0.00024879
5397 | 850.2923 | 3.0522 | 19.9976 | 101.9394 | 5.8573 | 6.918 | 62.2899 | 1.4866 | 6.0228 | 45.2317 | 76.5786 | 8.0543 | 184.6475 | 126.1089 | 250.0466 | 8.5762 | 79.6171 | 4.7213 | 138 | 31.2278 | 19.367 | 203.7948 | 0
5398 | 841.1749 | 2.4458 | 21.567 | 96.3113 | 5.4473 | 7.304 | 56.9521 | 1.5084 | 6.4034 | 38.8569 | 77.4923 | 8.6153 | 224.8606 | 113.5682 | 249.4699 | 8.6448 | 78.6123 | 4.2829 | 134 | 30.879 | 30.1791 | 204.9515 | 0
5399 | 827.0825 | 1.7092 | 21.5013 | 82.9206 | 4.3986 | 8.2992 | 59.9066 | 1.505 | 6.3833 | 34.0737 | 76.7745 | 8.7271 | 128.9133 | 110.9127 | 245.827 | 8.8232 | 78.6172 | 4.1115 | 134 | 30.6365 | 19.192 | 200.65 | 0
5400 | 805.9859 | 1.2046 | 21.3891 | 100.1183 | 5.6057 | 7.157 | 61.5907 | 1.6852 | 5.8933 | 31.1097 | 75.3967 | 8.7698 | 187.3435 | 109.0517 | 247.2764 | 8.9057 | 78.2558 | 4.1594 | 123 | 29.9155 | 30.354 | 198.1009 | 0
5401 | 788.2199 | 1.1841 | 21.6635 | 95.3786 | 4.6541 | 8.0606 | 57.9007 | 1.6344 | 5.8108 | 29.863 | 74.4129 | 8.5315 | 202.1932 | 99.7517 | 244.6425 | 8.8248 | 77.0927 | 3.941 | 120 | 31.0097 | 24.7736 | 196.0585 | 0
5402 | 777.9273 | 1.1972 | 21.6729 | 93.2971 | 4.841 | 7.8842 | 61.1985 | 1.4907 | 6.1026 | 29.4998 | 74.1046 | 8.2488 | 162.7984 | 94.0942 | 244.5678 | 8.7795 | 76.5722 | 3.719 | 117 | 30.1665 | 19.2499 | 194.8036 | 0
5403 | 760.9589 | 1.0879 | 22.6612 | 83.3874 | 5.1868 | 7.5578 | 62.4815 | 1.4955 | 6.0012 | 30.8809 | 74.6078 | 8.0465 | 185.6899 | 92.5926 | 241.6344 | 8.741 | 76.7806 | 3.6422 | 114 | 31.6482 | 23.0761 | 194.3361 | 0
5404 | 751.2697 | 1.4798 | 26.9583 | 106.0566 | 5.8765 | 6.9001 | 57.1239 | 1.4936 | 6.0415 | 37.4731 | 74.6688 | 8.0834 | 194.8397 | 90.7179 | 237.2543 | 8.9446 | 77.1817 | 3.6381 | 110 | 28.0537 | 24.8894 | 192.8082 | 0
5405 | 752.5569 | 2.4076 | 24.009 | 96.6015 | 4.5692 | 8.1424 | 56.6815 | 1.4224 | 5.9473 | 42.5456 | 73.0632 | 7.3236 | 179.8796 | 87.6092 | 232.3471 | 8.7186 | 76.8645 | 3.577 | 107 | 29.1945 | 24.9528 | 191.0365 | 0
5406 | 771.7834 | 1.8968 | 21.474 | 91.7247 | 3.4761 | 9.1824 | 57.2774 | 1.4404 | 5.6618 | 36.5131 | 74.081 | 5.9615 | 168.4871 | 84.7269 | 219.5078 | 8.2716 | 75.8313 | 3.422 | 107 | 32.5133 | 24.6213 | 187.9814 | 0.01959
5407 | 793.095 | 0.93551 | 21.26 | 89.6501 | 6.1148 | 6.6776 | 56.512 | 1.2611 | 5.3709 | 28.0589 | 85.3315 | 7.5553 | 195.9722 | 85.1162 | 217.6285 | 8.3159 | 75.1512 | 3.5835 | 111 | 41.6673 | 24.8181 | 192.3394 | 0.067455
5408 | 805.9418 | 0.74436 | 21.29 | 78.941 | 5.7743 | 6.9936 | 60.4857 | 1.1341 | 5.5473 | 27.4182 | 106.0711 | 12.9965 | 182.3151 | 88.7955 | 230.5197 | 8.3289 | 75.4684 | 4.1558 | 111 | 41.7818 | 24.221 | 200.8689 | 0.14598
5409 | 831.1834 | 1.017 | 22.2666 | 97.8061 | 5.8174 | 6.948 | 59.128 | 1.1502 | 5.7514 | 31.7135 | 125.1789 | 14.8519 | 171.433 | 95.8162 | 250.0568 | 8.0733 | 76.4142 | 4.4197 | 122 | 47.6742 | 24.9172 | 200.2963 | 0.18912
5410 | 849.8963 | 1.4313 | 23.1806 | 84.0242 | 5.3535 | 7.3905 | 56.1105 | 1.0775 | 7.5795 | 35.1101 | 137.7286 | 15.1507 | 200.3731 | 104.4065 | 257.6715 | 8.1799 | 76.9176 | 4.9677 | 126 | 48.9649 | 24.9445 | 198.6794 | 0.22271
5411 | 858.0343 | 1.8142 | 23.3233 | 100.2512 | 5.9205 | 6.8515 | 56.0441 | 1.0191 | 11.7791 | 37.6977 | 138.2165 | 15.2773 | 194.7829 | 113.5339 | 256.1772 | 8.2037 | 76.352 | 5.4085 | 131 | 47.4142 | 32.0446 | 199.1317 | 0.23122
5412 | 843.7499 | 1.5381 | 23.2333 | 94.7573 | 5.3266 | 7.4152 | 58.7956 | 1.0379 | 13.3714 | 40.7095 | 128.1372 | 14.8792 | 233.6348 | 121.1896 | 252.4823 | 8.126 | 75.3979 | 5.8351 | 140 | 44.5995 | 24.7736 | 200.5682 | 0.19494
5413 | 842.2453 | 1.2007 | 23.0972 | 92.4667 | 5.8284 | 6.9391 | 60.0544 | 1.277 | 8.9852 | 41.249 | 123.4625 | 14.958 | 184.9838 | 127.5253 | 241.1594 | 8.103 | 75.4925 | 6.3045 | 133 | 41.0114 | 19.2916 | 200.3357 | 0.12299
5414 | 833.0968 | 0.92805 | 23.116 | 92.157 | 5.4017 | 7.3449 | 58.1335 | 1.2 | 5.9401 | 37.8703 | 124.9212 | 15.5044 | 184.4993 | 130.6271 | 240.0578 | 8.3038 | 76.4359 | 6.9444 | 134 | 36.2641 | 23.2499 | 194.2468 | 0.17528
5415 | 823.038 | 1.1901 | 21.8193 | 90.6536 | 5.8802 | 6.8902 | 56.8412 | 1.0164 | 6.1446 | 33.1111 | 117.7569 | 14.8605 | 180.6774 | 126.4326 | 245.7363 | 8.239 | 77.1615 | 7.0601 | 131 | 33.2317 | 24.6209 | 189.1022 | 0.14506
5416 | 819.0634 | 1.719 | 21.3483 | 80.7669 | 4.6687 | 8.0397 | 57.636 | 1.0323 | 6.132 | 27.0848 | 103.8186 | 8.3546 | 206.9505 | 123.0729 | 248.7278 | 8.1874 | 77.9811 | 7.5817 | 130 | 35.5647 | 31.9308 | 185.3598 | 0.04073
5417 | 804.5892 | 1.1022 | 21.1042 | 98.074 | 5.6492 | 7.1139 | 59.3754 | 1.0076 | 5.9667 | 21.4056 | 95.3049 | 5.2049 | 189.4618 | 121.5132 | 252.2527 | 8.1996 | 78.07 | 7.8412 | 134 | 32.9993 | 19.1672 | 181.6357 | 0.055486
5418 | 796.0559 | 0.8319 | 21.2169 | 93.1523 | 5.4922 | 7.2614 | 62.2231 | 1.0161 | 5.45 | 21.6577 | 87.6088 | 5.3743 | 187.5751 | 121.3409 | 243.8177 | 8.104 | 76.8527 | 7.7296 | 126 | 33.4081 | 22.9932 | 178.0234 | 0.049592
5419 | 790.7638 | 1.8519 | 20.936 | 89.8706 | 5.0867 | 7.6449 | 57.7131 | 1.042 | 5.5432 | 28.9987 | 77.5341 | 6.0087 | 183.5521 | 125.7068 | 240.0221 | 8.2843 | 75.5592 | 7.4912 | 119 | 29.5727 | 24.9631 | 177.2614 | 0.034891
5420 | 786.4 | 2.7907 | 20.7304 | 90.2101 | 5.1113 | 7.6218 | 55.9447 | 1.4903 | 5.4972 | 35.0759 | 71.3571 | 6.3162 | 210.8667 | 124.8071 | 235.3274 | 8.1596 | 74.9336 | 6.4977 | 124 | 29.6551 | 24.8854 | 179.7923 | 0.00096914
5421 | 775.082 | 2.8513 | 21.1444 | 93.4767 | 5.1564 | 7.5807 | 62.1635 | 1.6088 | 5.653 | 32.0006 | 71.5849 | 7.5181 | 179.407 | 119.5005 | 233.7537 | 8.7024 | 75.4467 | 5.5917 | 132 | 30.3292 | 24.4971 | 185.793 | 0
5422 | 766.6327 | 2.3106 | 21.3615 | 93.7963 | 5.1059 | 7.6313 | 59.3162 | 1.472 | 5.826 | 25.9041 | 73.7207 | 7.9629 | 198.6197 | 113.5842 | 236.2282 | 8.7355 | 76.006 | 5.1755 | 135 | 31.9863 | 24.9679 | 191.8928 | 0
5423 | 754.8986 | 1.489 | 21.4979 | 93.3702 | 5.1463 | 7.5961 | 56.2103 | 1.4802 | 6.1225 | 23.071 | 73.7412 | 7.9944 | 187.9807 | 113.1275 | 234.7563 | 8.504 | 75.5255 | 4.5703 | 129 | 30.6076 | 24.7014 | 192.1226 | 0
5424 | 750.8347 | 1.3531 | 21.5942 | 93.083 | 3.5953 | 9.0689 | 60.9427 | 1.4867 | 6.2817 | 22.2836 | 72.8937 | 8.274 | 239.8921 | 133.3836 | 228.509 | 8.6456 | 74.9089 | 4.2029 | 128 | 29.5157 | 32.0123 | 193.3331 | 0
5425 | 745.0745 | 1.2076 | 21.3452 | 93.0628 | 4.6246 | 8.0874 | 61.6581 | 1.4967 | 6.1924 | 21.8749 | 72.468 | 8.1331 | 176.8598 | 156.293 | 229.6659 | 8.8293 | 75.1042 | 4.1877 | 129 | 28.898 | 16.7536 | 195.927 | 0
5426 | 735.3657 | 1.2782 | 21.386 | 94.0828 | 5.1797 | 7.5618 | 60.8509 | 1.4868 | 6.1196 | 21.3874 | 72.5586 | 7.9545 | 164.3182 | 160.2032 | 236.7481 | 8.7293 | 75.3847 | 4.1771 | 122 | 29.8657 | 26.5068 | 195.5041 | 0
5427 | 723.1162 | 1.1925 | 22.7005 | 94.956 | 5.144 | 7.5995 | 58.7619 | 1.4871 | 6.0379 | 21.6251 | 73.0206 | 8.068 | 220.2914 | 156.8797 | 236.5116 | 8.8174 | 75.1786 | 4.1848 | 109 | 30.5187 | 21.6307 | 194.6217 | 0
5428 | 714.9785 | 1.4905 | 26.5998 | 98.3018 | 4.5149 | 8.1976 | 57.7769 | 1.6939 | 6.1933 | 23.3183 | 73.0478 | 8.0181 | 185.731 | 156.628 | 231.7017 | 8.679 | 74.8998 | 4.0378 | 109 | 30.6628 | 16.6 | 194.9876 | 0
5429 | 724.1351 | 2.2229 | 22.8261 | 92.0045 | 5.5512 | 7.2096 | 57.1398 | 1.4971 | 6.2213 | 23.0847 | 70.8822 | 6.2155 | 228.7028 | 147.9888 | 215.3864 | 8.2555 | 74.0015 | 3.3668 | 107 | 33.453 | 20.2708 | 187.9995 | 0
5430 | 744.9773 | 1.3744 | 27.6849 | 77.9441 | 5.368 | 7.3814 | 56.4574 | 1.1548 | 5.6952 | 19.4111 | 71.5006 | 5.082 | 151.1956 | 119.9628 | 205.8067 | 8.2198 | 72.774 | 2.9219 | 105 | 35.1561 | 21.5776 | 176.5736 | 0.074113
5431 | 752.0011 | 0.7156 | 15.602 | 96.3204 | 5.1789 | 7.5618 | 56.0828 | 1.1093 | 5.1938 | 16.5594 | 82.1869 | 4.9187 | 169.226 | 95.807 | 207.3904 | 8.2954 | 72.3753 | 3.1464 | 111 | 38.9841 | 28.0732 | 173.2069 | 0.083146
5432 | 755.9872 | 0.85907 | 19.4569 | 91.5429 | 5.1031 | 7.6312 | 54.9251 | 1.1759 | 5.1608 | 15.82 | 94.3459 | 7.4891 | 237.8282 | 93.5881 | 224.1964 | 8.122 | 72.4381 | 3.7293 | 110 | 34.9685 | 16.7212 | 174.6893 | 0.2008
5433 | 773.6208 | 1.2748 | 21.3105 | 79.8511 | 5.828 | 6.9398 | 58.4434 | 1.1624 | 5.3956 | 17.31 | 98.8686 | 8.9342 | 153.5671 | 101.3946 | 245.7588 | 8.1499 | 65.7164 | 4.2565 | 119 | 33.0593 | 26.5391 | 176.6066 | 0.27494
5434 | 799.3916 | 1.3122 | 21.4449 | 97.5007 | 6.1524 | 7.37 | 58.9761 | 1.3101 | 7.4367 | 22.8263 | 99.8061 | 8.4706 | 165.5102 | 112.3079 | 253.7991 | 8.6205 | 54.1355 | 5.2916 | 130 | 32.5942 | 16.8405 | 179.5404 | 0.27873
5435 | 805.6823 | 1.3041 | 21.3572 | 83.3389 | 8.1362 | 6.8611 | 56.6537 | 1.6605 | 11.8233 | 30.5157 | 103.5925 | 8.97 | 186.1182 | 119.6681 | 261.6612 | 8.2347 | 48.8166 | 6.3612 | 138 | 35.6663 | 20.0725 | 183.5229 | 0.26888
5436 | 804.5097 | 1.8714 | 21.417 | 99.345 | 9.2731 | 6.6259 | 54.9382 | 1.8194 | 13.487 | 35.1983 | 111.0013 | 7.9472 | 190.2446 | 123.7521 | 258.9884 | 8.1129 | 48.4991 | 6.8803 | 138 | 39.7596 | 27.978 | 185.2596 | 0.28235
5437 | 801.7323 | 1.8312 | 21.6987 | 83.6654 | 8.8393 | 7.3773 | 58.2323 | 1.4474 | 13.2085 | 36.0315 | 117.2286 | 9.0767 | 218.8875 | 127.7974 | 248.1559 | 8.4174 | 48.9678 | 7.4184 | 137 | 41.2687 | 16.6925 | 183.3062 | 0.30398
5438 | 794.5505 | 1.692 | 22.3853 | 100.4754 | 8.1058 | 7.6425 | 62.5997 | 1.1171 | 8.611 | 36.9213 | 121.2044 | 11.0204 | 202.0269 | 128.7976 | 254.9779 | 8.2324 | 49.2962 | 7.7038 | 137 | 41.4122 | 20.1177 | 182.4527 | 0.30344
5439 | 788.1936 | 1.8783 | 22.4715 | 95.7059 | 9.2019 | 6.815 | 60.2958 | 1.0374 | 8.4404 | 37.269 | 117.2118 | 10.4989 | 186.0092 | 126.13 | 274.7948 | 8.1728 | 48.701 | 8.0763 | 132 | 38.4243 | 20.7975 | 182.6762 | 0.27586
5440 | 780.1112 | 2.1381 | 22.3099 | 92.1844 | 9.6606 | 6.6939 | 56.7651 | 1.2052 | 7.1262 | 33.1689 | 105.9143 | 8.6389 | 188.847 | 121.297 | 282.6351 | 8.4656 | 47.9782 | 8.329 | 131 | 37.5396 | 20.4779 | 181.447 | 0.25343
5441 | 764.5553 | 1.8224 | 22.5784 | 81.9402 | 8.998 | 7.4182 | 57.7687 | 1.1354 | 5.5736 | 27.2014 | 98.895 | 9.9974 | 260.5237 | 116.5949 | 280.5525 | 8.4894 | 48.2296 | 7.9925 | 134 | 36.6689 | 20.9741 | 182.5591 | 0.23755
5442 | 749.1162 | 2.3016 | 23.1795 | 100.8309 | 9.5346 | 6.8331 | 60.7727 | 1.0185 | 5.2238 | 24.0463 | 95.4748 | 11.1295 | 147.059 | 117.6446 | 275.8259 | 8.4152 | 48.2457 | 7.1319 | 130 | 36.911 | 21.7436 | 183.7757 | 0.2011
5443 | 753.3618 | 1.6926 | 22.3707 | 94.9329 | 8.8181 | 7.3449 | 61.2724 | 1.0559 | 5.379 | 25.7407 | 88.2078 | 10.173 | 183.1683 | 122.6601 | 260.0935 | 8.3821 | 47.9558 | 6.2741 | 135 | 33.4103 | 28.0612 | 183.4645 | 0.10617
5444 | 762.7866 | 2.2009 | 21.2928 | 90.1437 | 9.1293 | 6.9807 | 57.1478 | 1.0866 | 5.541 | 29.5921 | 78.2017 | 6.9888 | 183.2257 | 120.1112 | 237.314 | 8.1767 | 48.4292 | 5.8963 | 132 | 35.2653 | 16.9692 | 183.8724 | 0
5445 | 753.5175 | 3.2195 | 21.3111 | 91.5076 | 8.5069 | 7.3428 | 58.5965 | 1.5819 | 5.4662 | 31.0146 | 73.3672 | 7.3519 | 171.405 | 112.5087 | 228.8427 | 8.5295 | 49.1309 | 5.7419 | 140 | 31.8445 | 23.753 | 186.2116 | 0
5446 | 745.3871 | 2.7286 | 21.4186 | 92.8805 | 8.4201 | 7.532 | 58.8618 | 1.639 | 5.6721 | 30.9598 | 73.3896 | 8.6402 | 192.4082 | 107.5754 | 232.4641 | 8.8577 | 49.7116 | 6.3079 | 134 | 30.6047 | 26.4602 | 191.366 | 0
5447 | 732.0635 | 1.9673 | 21.3444 | 59.1858 | 7.209 | 8.4037 | 61.7602 | 1.489 | 5.859 | 29.9961 | 73.0049 | 8.5166 | 197.1008 | 106.3666 | 227.6281 | 9.7851 | 50.1879 | 6.0725 | 126 | 30.1308 | 21.0701 | 194.0676 | 0
5448 | 741.8287 | 1.5188 | 21.2318 | 82.9916 | 6.5908 | 8.4858 | 62.3204 | 1.4941 | 5.8828 | 26.826 | 72.1583 | 8.0895 | 167.6158 | 102.404 | 223.7056 | 12.3603 | 50.4206 | 5.6102 | 121 | 39.0413 | 10.3236 | 194.5155 | 0
5449 | 744.4138 | 1.2561 | 21.2821 | 73.4896 | 5.4449 | 8.5239 | 56.9483 | 1.4956 | 6.0193 | 23.8224 | 72.0416 | 8.1077 | 197.3499 | 96.0064 | 225.9231 | 13.249 | 50.4069 | 5.0405 | 115 | 23.2452 | 22.0854 | 198.5362 | 0
5450 | 747.3093 | 1.0994 | 21.2143 | 69.7461 | 6.4898 | 7.1791 | 57.4378 | 1.5057 | 5.9633 | 22.9894 | 71.7753 | 8.17 | 205.8732 | 94.1901 | 232.6277 | 13.1308 | 50.2225 | 4.1259 | 110 | 27.0762 | 22.748 | 204.2146 | 0
5451 | 750.9407 | 1.1716 | 21.5022 | 69.8967 | 5.8834 | 7.391 | 57.7048 | 1.5167 | 6.0267 | 24.5492 | 71.0501 | 8.1542 | 175.6358 | 93.8281 | 235.9091 | 11.9594 | 50.152 | 3.4523 | 112 | 39.7861 | 21.7599 | 208.3158 | 0
5452 | 758.6719 | 1.5663 | 21.6689 | 52.3269 | 5.2899 | 7.4574 | 55.9293 | 1.7667 | 6.4436 | 31.6523 | 70.608 | 8.0768 | 161 | 91.3605 | 226.0515 | 9.8474 | 50.1359 | 3.2925 | 108 | 22.3196 | 32.8315 | 218.6667 | 0
5453 | 766.7149 | 2.1646 | 26.5137 | 86.2139 | 5.0424 | 7.6901 | 58.0628 | 1.4785 | 6.3089 | 36.4107 | 69.2201 | 7.9769 | 189.1408 | 90.7181 | 215.0402 | 8.6022 | 49.5049 | 3.1133 | 116 | 16.9711 | 38.0159 | 232.2566 | 0
5454 | 798.1763 | 2.4968 | 38.7835 | 92.4406 | 1.4418 | 11.1068 | 65.9836 | 1.1265 | 5.7535 | 31.4294 | 82.2441 | 11.9654 | 196.8271 | 105.5821 | 214.9866 | 8.4469 | 49.1046 | 2.9596 | 152 | 28.1561 | 36.4383 | 259.2953 | 0.037236
5455 | 850.6017 | 2.7646 | 60.8795 | 118.2557 | 18.2345 | 15.8171 | 83.1749 | 1.9544 | 7.1883 | 30.4329 | 113.8358 | 18.0299 | 206.6074 | 150.9436 | 266.1625 | 9.3051 | 51.5389 | 3.249 | 270 | 46.1196 | 25.5069 | 320.4856 | 0.064252
5456 | 909.2124 | 3.2001 | 82.3703 | 137.4081 | 44.6821 | 17.1504 | 99.1043 | 3.9472 | 10.8239 | 34.6111 | 143.8484 | 23.0104 | 237.9107 | 210.0454 | 353.6672 | 11.559 | 59.3882 | 4.7216 | 279 | 84.1562 | 19.7601 | 394.8015 | 0.13654
5457 | 981.1557 | 3.4407 | 90.7059 | 171.4975 | 52.1577 | 18.5704 | 112.5131 | 6.0092 | 10.4319 | 34.4937 | 163.0117 | 27.8846 | 255.1021 | 251.5871 | 418.6104 | 11.9564 | 70.424 | 6.0063 | 309 | 46.1581 | 23.9871 | 446.6085 | 0.22645
5458 | 1003.8237 | 3.4127 | 89.8598 | 191.8131 | 60.4656 | 16.9402 | 113.2394 | 6.0347 | 12.7533 | 39.4155 | 167.0868 | 28.8175 | 317.5294 | 275.2388 | 445.4809 | 12.0833 | 78.4526 | 6.8179 | 313 | 69.4196 | 25.5523 | 464.6589 | 0.27463
5459 | 1004.0877 | 3.5415 | 91.1138 | 185.9096 | 77.4854 | 15.2371 | 130.7424 | 4.9998 | 14.2167 | 48.5956 | 165.9504 | 28.5349 | 317.3336 | 287.6955 | 447.3977 | 12.212 | 80.7191 | 7.2686 | 295 | 75.3247 | 25.2308 | 465.7013 | 0.29175
5460 | 1012.4269 | 4.5781 | 93.7271 | 165.6927 | 92.0416 | 13.1522 | 143.6909 | 4.4543 | 13.7985 | 51.8929 | 171.4412 | 28.8206 | 415.6018 | 296.5378 | 442.62 | 12.4274 | 79.6866 | 7.3141 | 328 | 69.7884 | 33.0031 | 466.3166 | 0.29477
5461 | 1029.5916 | 8.5887 | 96.8631 | 204.3916 | 88.7309 | 15.137 | 144.3512 | 4.4413 | 13.5828 | 53.7833 | 178.3628 | 31.2999 | 289.3488 | 309.4918 | 437.0228 | 16.7803 | 80.1079 | 8.0231 | 283 | 70.5195 | 19.7941 | 473.4617 | 0.30948
5462 | 1029.9477 | 9.697 | 99.9125 | 198.3928 | 81.774 | 16.8785 | 145.9992 | 4.4179 | 13.5386 | 57.2942 | 181.5338 | 32.3021 | 345.8277 | 314.7926 | 440.4722 | 19.7565 | 81.9258 | 8.3218 | 251 | 75.5161 | 23.8426 | 472.0516 | 0.31268
5463 | 1002.438 | 5.8219 | 87.7376 | 155.4954 | 79.738 | 16.4486 | 135.9819 | 4.2084 | 14.2739 | 59.8699 | 180.7782 | 33.5567 | 324.3761 | 306.8285 | 441.7789 | 19.4261 | 81.5115 | 8.3624 | 218 | 74.1823 | 25.4656 | 460.455 | 0.28075
5464 | 972.7925 | 3.6558 | 65.0551 | 136.7392 | 80.092 | 14.7827 | 124.6612 | 3.1406 | 14.5257 | 58.8012 | 177.3258 | 34.1787 | 307.8809 | 286.3977 | 413.409 | 16.1853 | 77.6944 | 8.5269 | 188 | 63.9138 | 25.6393 | 429.0017 | 0.25689
5465 | 903.2994 | 3.443 | 54.778 | 129.7861 | 74.9347 | 9.2335 | 115.9357 | 1.9243 | 14.1137 | 50.2122 | 165.7127 | 31.6379 | 334.4411 | 238.0292 | 358.5988 | 11.5488 | 70.9394 | 8.24 | 178 | 51.6852 | 25.3549 | 364.1787 | 0.23503
5466 | 857.6393 | 2.495 | 52.3837 | 109.5819 | 68.3163 | 9.7672 | 98.9855 | 1.1801 | 14.7933 | 42.5102 | 139.2054 | 24.2588 | 243.2426 | 179.4052 | 314.0301 | 9.645 | 63.8824 | 7.3931 | 178 | 48.1946 | 25.612 | 299.4596 | 0.17686
5467 | 844.9848 | 1.5198 | 48.972 | 97.8608 | 72.7493 | 7.5945 | 75.0592 | 1.1527 | 14.5667 | 46.8704 | 113.2465 | 10.8609 | 245.1228 | 145.945 | 298.5959 | 9.2619 | 59.1607 | 7.4237 | 162 | 40.2409 | 25.5641 | 251.4561 | 0.060808
5468 | 818.5932 | 2.735 | 39.0914 | 87.2817 | 73.3434 | 6.6171 | 61.7918 | 1.1691 | 9.8133 | 49.6794 | 103.2065 | 5.3924 | 294.7225 | 135.1652 | 297.372 | 8.8119 | 56.1722 | 7.4903 | 152 | 37.4466 | 25.2788 | 223.6061 | 0
5469 | 792.8578 | 3.3075 | 32.0927 | 80.9818 | 69.3451 | 6.6941 | 60.8036 | 1.2733 | 7.7727 | 38.6979 | 102.2964 | 6.7238 | 175.5469 | 124.5834 | 278.0332 | 8.9977 | 54.0397 | 7.641 | 146 | 35.0578 | 25.6931 | 215.5682 | 0
5470 | 777.4186 | 2.6891 | 30.8429 | 98.6678 | 63.0754 | 8.7608 | 64.0954 | 1.4232 | 7.2588 | 26.2506 | 97.2552 | 8.1509 | 221.3522 | 111.9737 | 241.8076 | 9.2534 | 53.1266 | 7.3815 | 163 | 42.8075 | 32.8237 | 213.5914 | 0
5471 | 752.2369 | 1.7097 | 31.8647 | 107.8218 | 59.6131 | 7.33 | 61.9032 | 1.4422 | 6.5519 | 21.7889 | 87.0267 | 8.2121 | 215.939 | 105.6477 | 227.0907 | 10.1931 | 52.5959 | 6.1963 | 138 | 19.8088 | 19.7049 | 214.366 | 0
5472 | 735.8119 | 1.5193 | 32.0306 | 108.0612 | 59.5423 | 6.6289 | 49.4186 | 1.6594 | 6.0216 | 20.7522 | 80.3704 | 8.6333 | 195.7406 | 101.1956 | 228.1 | 11.93 | 51.6924 | 5.2539 | 132 | 27.0232 | 21.1779 | 215.8771 | 0
5473 | 731.7059 | 1.4868 | 31.5008 | 107.6769 | 58.6978 | 7.3838 | 48.9754 | 1.563 | 5.8294 | 19.796 | 76.9352 | 8.2702 | 237.519 | 95.962 | 236.1323 | 13.1683 | 51.1123 | 4.4249 | 129 | 24.5294 | 21.7322 | 214.2996 | 0
5474 | 733.0081 | 1.2911 | 30.5407 | 109.1901 | 55.4706 | 7.6537 | 52.1961 | 1.4269 | 5.7488 | 19.3974 | 74.3537 | 7.8807 | 192.8007 | 92.3019 | 237.7668 | 13.3804 | 50.8721 | 3.7071 | 127 | 27.9129 | 21.75 | 212.8873 | 0
5475 | 733.3164 | 1.1788 | 29.9846 | 98.5637 | 57.2552 | 7.5962 | 48.8173 | 1.4357 | 5.92 | 20.9514 | 73.5242 | 7.8298 | 200.0023 | 91.4978 | 231.8352 | 13.0002 | 50.5652 | 3.4681 | 126 | 28.9932 | 21.7675 | 212.5862 | 0
5476 | 741.1757 | 1.5819 | 29.6238 | 107.137 | 59.2084 | 7.5551 | 50.2373 | 1.4592 | 5.8968 | 27.9283 | 73.7117 | 7.8406 | 256.1793 | 91.8937 | 222.8009 | 10.5889 | 50.2637 | 3.4554 | 117 | 26.8691 | 21.6891 | 220.419 | 0
5477 | 777.229 | 2.3834 | 29.6871 | 113.2045 | 58.6831 | 7.5645 | 52.8747 | 1.2654 | 5.786 | 32.8518 | 72.1482 | 9.711 | 171.4901 | 91.9234 | 214.1265 | 9.0175 | 49.6993 | 3.2955 | 143 | 25.5142 | 31.7164 | 236.4216 | 0
5478 | 823.359 | 3.2017 | 70.119 | 107.2912 | 55.2281 | 10.4162 | 52.7619 | 1.2499 | 5.5599 | 28.4915 | 79.4238 | 15.4673 | 200.4737 | 108.9382 | 229.0231 | 8.6612 | 49.6571 | 3.6036 | 182 | 32.3631 | 19.6066 | 266.4361 | 0.026088
5479 | 861.9257 | 3.6634 | 44.4382 | 107.5897 | 49.4443 | 16.3134 | 72.2327 | 4.1827 | 7.673 | 25.7414 | 106.33 | 25.05 | 223.957 | 159.7509 | 289.2752 | 9.3058 | 53.6935 | 5.2618 | 259 | 48.6583 | 23.5934 | 318.223 | 0.059517
5480 | 912.0529 | 4.6488 | 76.2248 | 122.9114 | 49.1709 | 16.7251 | 98.1139 | 6.5105 | 9.3776 | 28.3065 | 138.8041 | 29.8351 | 269.245 | 220.4143 | 373.8657 | 11.14 | 63.498 | 7.7839 | 317 | 59.0546 | 25.3268 | 378.5802 | 0.074386
5481 | 985.0227 | 6.7035 | 92.4848 | 133.5025 | 49.6874 | 18.1976 | 109.441 | 6.1753 | 13.7836 | 34.7226 | 160.4394 | 33.6835 | 297.7285 | 260.6432 | 454.811 | 12.592 | 75.6431 | 11.9722 | 347 | 62.3911 | 27.9527 | 425.4854 | 0.17542
5482 | 1060.0511 | 7.8425 | 90.9346 | 137.5758 | 50.854 | 18.3851 | 114.3292 | 6.4793 | 12.6342 | 41.5757 | 171.0405 | 36.221 | 321.6281 | 278.0886 | 511.779 | 12.5763 | 84.0642 | 14.7325 | 329 | 71.4216 | 29.7846 | 457.6456 | 0.21092
5483 | 1071.3193 | 7.8135 | 133.7121 | 140.0176 | 54.0575 | 15.9832 | 118.7198 | 6.1348 | 18.3949 | 42.9974 | 175.0004 | 34.2732 | 432.2098 | 289.3935 | 521.8089 | 12.3188 | 86.6248 | 16.1416 | 310 | 72.1393 | 29.5251 | 477.5884 | 0.28275
5484 | 1062.9848 | 7.0299 | 76.3063 | 143.4538 | 58.5192 | 16.3872 | 117.4357 | 4.6588 | 21.0942 | 43.0299 | 174.3229 | 31.7316 | 273.1226 | 302.2841 | 501.0985 | 11.8819 | 85.0093 | 16.8293 | 340 | 70.369 | 29.8646 | 484.4296 | 0.27682
5485 | 1067.7203 | 10.1369 | 94.3448 | 143.7397 | 66.1719 | 17.2748 | 126.7292 | 3.9583 | 19.0626 | 44.1012 | 174.2093 | 28.5713 | 354.8287 | 307.8882 | 486.6774 | 12.2714 | 81.8445 | 17.8702 | 303 | 62.3443 | 28.654 | 484.2022 | 0.29033
5486 | 1061.681 | 11.3979 | 104.1931 | 144.0525 | 77.3842 | 16.3074 | 124.4341 | 3.5241 | 19.4097 | 46.1164 | 176.1526 | 27.2474 | 276.475 | 306.6722 | 483.8943 | 12.3257 | 81.2956 | 18.038 | 281 | 75.2907 | 37.1481 | 474.7743 | 0.29401
5487 | 1035.6799 | 6.9669 | 99.5358 | 107.1584 | 80.2346 | 14.8002 | 109.0721 | 3.4135 | 18.3298 | 50.4285 | 178.0788 | 31.7822 | 281.977 | 301.7334 | 492.8872 | 12.4383 | 81.043 | 17.012 | 263 | 69.0105 | 22.8049 | 462.97 | 0.27092
5488 | 989.9841 | 3.6663 | 90.1704 | 140.5717 | 76.8311 | 11.3983 | 101.7411 | 2.8297 | 16.4265 | 53.8171 | 177.72 | 34.9071 | 286.8617 | 290.6287 | 483.2386 | 11.7379 | 76.3632 | 16.3464 | 248 | 61.7372 | 27.0073 | 426.4776 | 0.25722
5489 | 941.4923 | 2.4334 | 84.4362 | 115.2193 | 76.1548 | 9.8294 | 95.7477 | 1.5742 | 17.4947 | 49.8394 | 165.4709 | 35.2215 | 283.8485 | 249.677 | 432.5749 | 9.711 | 69.0221 | 16.2966 | 198 | 54.9405 | 28.1384 | 352.7307 | 0.23624
5490 | 907.6496 | 2.0408 | 107.4044 | 103.8447 | 76.2158 | 8.0762 | 84.2291 | 1.174 | 21.84 | 44.367 | 136.3485 | 28.8371 | 256.7247 | 187.5525 | 369.4089 | 8.6041 | 62.9355 | 16.6377 | 180 | 48.9504 | 27.336 | 285.4037 | 0.19096
5491 | 861.5937 | 1.8929 | 59.8332 | 82.3664 | 73.5186 | 7.6346 | 64.9089 | 1.0969 | 22.2333 | 43.4709 | 109.9687 | 15.7583 | 221.0934 | 157.8416 | 324.9639 | 8.6766 | 59.6149 | 11.4568 | 153 | 39.2114 | 27.1414 | 241.1637 | 0.094062
5492 | 819.5947 | 2.9384 | 62.4953 | 114.8312 | 72.5049 | 6.8553 | 54.299 | 1.0477 | 14.5033 | 41.2455 | 100.6916 | 10.755 | 262.5596 | 155.0861 | 310.1153 | 8.3749 | 56.9316 | 7.4836 | 148 | 35.8098 | 24.7047 | 208.6901 | 0
5493 | 798.6835 | 3.4308 | 64.0627 | 106.7281 | 67.6491 | 7.9216 | 51.742 | 1.2703 | 10.4736 | 36.6638 | 97.7649 | 12.3632 | 195.7295 | 148.5408 | 310.8006 | 8.4336 | 53.8893 | 6.6055 | 142 | 34.3766 | 28.95 | 195.3656 | 0
5494 | 785.8288 | 2.8154 | 63.3076 | 104.3278 | 63.6962 | 7.964 | 49.0969 | 1.4039 | 8.3191 | 32.3214 | 89.6643 | 13.5137 | 218.31 | 139.8387 | 299.8067 | 9.0908 | 52.1838 | 5.9544 | 138 | 35.0962 | 22.2933 | 195.9309 | 0
5495 | 753.4819 | 1.7478 | 62.7139 | 102.4461 | 59.9793 | 7.5639 | 51.6338 | 1.6163 | 6.6387 | 28.6845 | 78.6112 | 12.9986 | 176.8411 | 133.6692 | 276.0921 | 8.9928 | 51.0439 | 4.6275 | 126 | 32.7378 | 17.2334 | 195.8866 | 0
5496 | 745.6804 | 1.1564 | 62.4044 | 102.9493 | 51.9369 | 6.8492 | 53.672 | 1.541 | 6.1176 | 26.8549 | 72.5882 | 12.5559 | 192.7409 | 126.9862 | 258.2295 | 8.8357 | 49.8803 | 3.8038 | 126 | 31.9891 | 20.5502 | 197.0469 | 0
5497 | 744.456 | 1.0438 | 62.1451 | 101.3737 | 51.416 | 7.4678 | 49.9159 | 1.3916 | 6.265 | 26.4457 | 70.8799 | 12.5086 | 271.1492 | 119.1286 | 249.1161 | 8.9467 | 49.8257 | 3.5285 | 118 | 33.585 | 21.8753 | 200.9293 | 0
5498 | 733.7935 | 1.0832 | 62.14 | 100.8963 | 55.9856 | 7.6297 | 47.955 | 1.4247 | 6.1591 | 26.3249 | 70.7931 | 12.5294 | 179.8621 | 114.8941 | 242.147 | 8.765 | 50.2314 | 3.3228 | 117 | 31.5139 | 21.8742 | 202.9152 | 0
5499 | 728.6748 | 1.1126 | 63.5289 | 102.178 | 58.7034 | 7.4724 | 51.5112 | 1.4076 | 6.1769 | 27.9849 | 71.2896 | 12.5295 | 201.9036 | 114.5461 | 229.5076 | 8.9336 | 50.3111 | 3.1227 | 120 | 32.5253 | 21.9095 | 204.7553 | 0
5500 | 734.5487 | 1.4935 | 87.9198 | 105.0012 | 66.3494 | 7.5648 | 53.3029 | 1.41 | 6.3816 | 34.61 | 70.8373 | 12.4608 | 207.4818 | 114.1945 | 223.5713 | 8.9317 | 50.1444 | 3.0903 | 119 | 29.7315 | 21.9037 | 210.1412 | 0
5501 | 752.0919 | 2.2051 | 48.6303 | 99.3656 | 71.6812 | 6.9554 | 50.6854 | 1.4546 | 6.3534 | 39.0775 | 68.731 | 12.3939 | 191.0371 | 113.1077 | 222.3214 | 8.4752 | 49.4971 | 2.9416 | 126 | 30.6934 | 21.8858 | 219.6272 | 0
5502 | 778.0212 | 2.2055 | 60.7227 | 102.3055 | 68.7578 | 9.5091 | 54.9631 | 1.1976 | 5.7018 | 34.0396 | 75.5681 | 15.147 | 185.5538 | 125.1241 | 230.7442 | 8.5041 | 49.2292 | 3.8433 | 189 | 38.5452 | 22.4885 | 245.9947 | 0.091236
5503 | 838.1207 | 2.8548 | 82.6473 | 107.687 | 53.7909 | 14.7495 | 73.5689 | 1.7918 | 7.7599 | 30.0095 | 101.5109 | 27.7365 | 259.2717 | 164.6714 | 273.5971 | 10.8975 | 52.0415 | 10.4607 | 286 | 50.4291 | 27.8156 | 299.1078 | 0.14776
5504 | 917.0635 | 5.6234 | 107.4661 | 88.3493 | 53.1967 | 16.6779 | 97.4764 | 3.5368 | 15.11 | 30.5477 | 134.9402 | 34.7168 | 205.3848 | 217.1648 | 353.6804 | 14.6055 | 60.1113 | 15.6608 | 333 | 58.7572 | 30.4163 | 375.2215 | 0.2877
5505 | 1017.6532 | 6.926 | 111.6398 | 161.8054 | 68.233 | 17.2405 | 110.3914 | 4.2474 | 20.365 | 29.5937 | 158.9078 | 36.1835 | 291.9321 | 262.4688 | 437.2434 | 16.9385 | 71.3661 | 15.4598 | 327 | 60.5935 | 30.4204 | 439.1114 | 0.32604
5506 | 1059.3713 | 6.95 | 112.1574 | 143.7326 | 81.3253 | 17.8278 | 126.9029 | 4.0078 | 20.3387 | 28.8156 | 171.7979 | 37.0317 | 372.471 | 291.6903 | 486.5032 | 17.4041 | 79.5935 | 15.139 | 331 | 66.175 | 30.4578 | 465.3623 | 0.33031
5507 | 1080.9322 | 7.0607 | 114.4647 | 136.7057 | 82.3709 | 15.9448 | 138.8838 | 3.6656 | 19.1263 | 30.1828 | 177.5296 | 33.935 | 284.36 | 307.3973 | 497.7377 | 24.7968 | 81.9102 | 15.6387 | 315 | 65.5808 | 30.4336 | 481.7515 | 0.27877
5508 | 1069.7497 | 7.3414 | 111.6239 | 137.9599 | 76.7705 | 17.2445 | 140.9294 | 3.7154 | 18.5867 | 36.4439 | 178.4613 | 30.9283 | 329.957 | 313.9936 | 492.4987 | 32.971 | 80.7798 | 16.3233 | 310 | 63.1358 | 38.601 | 493.1581 | 0.28859
5509 | 1053.0456 | 9.6099 | 104.2024 | 149.974 | 74.7252 | 20.1165 | 134.5699 | 3.5976 | 18.6367 | 45.0213 | 181.7956 | 35.0827 | 249.4557 | 324.6488 | 491.0118 | 34.6974 | 80.3861 | 16.5541 | 283 | 60.2703 | 29.954 | 490.2904 | 0.28327
5510 | 1045.2026 | 9.9161 | 102.6488 | 159.7438 | 80.4607 | 18.1367 | 132.9646 | 3.661 | 15.6 | 48.7358 | 185.9984 | 37.3807 | 277.4493 | 333.0213 | 499.3564 | 33.6593 | 81.9779 | 16.7825 | 261 | 75.1553 | 23.3661 | 491.9544 | 0.26773
5511 | 1019.22 | 6.4457 | 92.0084 | 121.167 | 84.5729 | 17.1632 | 121.8732 | 3.4853 | 11.7933 | 45.9831 | 184.7954 | 35.9836 | 291.6262 | 318.4901 | 495.8284 | 32.9457 | 81.3337 | 16.7496 | 238 | 66.9076 | 28.0068 | 494.6808 | 0.26101
5512 | 1009.0467 | 4.1911 | 63.7342 | 135.6829 | 87.6619 | 14.2473 | 109.2113 | 3.4738 | 12.7767 | 40.6751 | 180.4034 | 32.676 | 287.2925 | 289.0877 | 474.8816 | 27.9957 | 75.8947 | 16.094 | 204 | 56.095 | 29.8947 | 454.8608 | 0.1522
5513 | 985.2195 | 3.0775 | 48.7311 | 116.1908 | 87.9292 | 9.8497 | 100.7368 | 2.709 | 14.8167 | 41.7988 | 168.1936 | 31.163 | 226.986 | 237.0184 | 430.4906 | 15.8713 | 68.4838 | 15.2831 | 179 | 45.0365 | 28.7524 | 377.9848 | 0.082817
5514 | 948.6172 | 2.3552 | 44.9672 | 104.6943 | 81.0386 | 7.8202 | 86.9689 | 2.2352 | 15.39 | 47.6637 | 140.3385 | 26.9219 | 245.3639 | 179.5588 | 378.4602 | 9.625 | 63.227 | 12.8123 | 172 | 41.7756 | 27.7278 | 313.1252 | 0.038176
5515 | 930.2001 | 2.3966 | 41.8195 | 100.2309 | 75.0913 | 7.5382 | 65.3002 | 2.2459 | 14.0033 | 50.4927 | 113.1239 | 12.4425 | 275.7276 | 154.2944 | 333.5904 | 9.0766 | 59.4115 | 7.762 | 143 | 42.7214 | 27.4143 | 268.5887 | 0.012494
5516 | 906.9723 | 3.0541 | 35.2894 | 100.4409 | 73.0259 | 7.5943 | 54.7911 | 2.1701 | 10.45 | 49.1725 | 103.5752 | 6.6439 | 282.3882 | 146.8309 | 293.8002 | 9.0786 | 54.8367 | 5.8032 | 144 | 39.4296 | 34.0361 | 239.4589 | 0
5517 | 871.8003 | 3.2402 | 32.2986 | 102.4173 | 69.7589 | 7.585 | 54.1007 | 2.238 | 10.4592 | 42.1979 | 106.5081 | 7.6753 | 202.1972 | 135.7542 | 273.1263 | 9.3367 | 51.3077 | 6.1051 | 136 | 36.7327 | 20.2405 | 234.7265 | 0
5518 | 849.5691 | 2.5564 | 31.9398 | 104.7834 | 66.1723 | 7.606 | 49.7408 | 2.4698 | 9.8468 | 32.6916 | 111.8373 | 8.0448 | 196.1171 | 123.273 | 267.793 | 9.166 | 49.7045 | 5.5322 | 126 | 38.6559 | 24.2688 | 240.3964 | 0
5519 | 823.5317 | 1.6252 | 31.9602 | 107.506 | 58.787 | 7.5902 | 51.7315 | 1.9215 | 7.6473 | 26.9761 | 110.4714 | 7.6884 | 280.4122 | 114.6012 | 262.0966 | 9.665 | 49.3751 | 5.2851 | 123 | 34.9691 | 25.9115 | 236.4043 | 0
5520 | 820.3852 | 2.1056 | 32.2769 | 108.4416 | 46.1648 | 7.652 | 53.8548 | 1.4206 | 6.5962 | 24.5666 | 101.5807 | 7.4801 | 193.537 | 110.7217 | 247.628 | 9.4485 | 50.0186 | 4.7868 | 125 | 34.8592 | 26.3449 | 231.8473 | 0
5521 | 832.618 | 1.7923 | 32.2501 | 107.7898 | 42.442 | 7.5907 | 50.093 | 1.3756 | 6.3819 | 23.0667 | 93.3799 | 7.513 | 261.9565 | 109.1597 | 236.1873 | 9.2076 | 50.6109 | 4.1474 | 123 | 35.1791 | 20.4016 | 231.1987 | 0
5522 | 812.1911 | 1.138 | 32.1505 | 107.9066 | 45.3357 | 7.5451 | 49.5613 | 1.4004 | 6.2986 | 22.408 | 89.8325 | 10.5083 | 358.5137 | 107.3721 | 239.3283 | 9.4306 | 50.5824 | 3.3161 | 122 | 35.1674 | 10.0724 | 232.4439 | 0
5523 | 802.8239 | 1.0376 | 33.2225 | 108.1757 | 55.1945 | 8.2347 | 52.4916 | 1.4759 | 6.51 | 23.8543 | 88.5614 | 15.8963 | 193.7793 | 105.663 | 246.4581 | 9.3596 | 50.4419 | 3.1178 | 120 | 24.6243 | 21.305 | 233.6179 | 0
5524 | 809.6557 | 1.5917 | 34.9189 | 108.8348 | 65.2827 | 7.1704 | 54.3855 | 1.6062 | 6.4233 | 30.7256 | 87.9799 | 15.6188 | 214.8117 | 103.632 | 241.0935 | 9.2237 | 50.6758 | 3.0077 | 121 | 30.1385 | 23.7559 | 236.9746 | 0
5525 | 832.7963 | 2.416 | 32.6877 | 88.5946 | 63.1746 | 8.0825 | 51.7779 | 1.3309 | 6.2333 | 35.8155 | 86.776 | 11.2564 | 202.4818 | 103.1103 | 234.6709 | 9.1059 | 51.05 | 2.7455 | 119 | 24.286 | 35.5767 | 252.8147 | 0
5526 | 865.7502 | 2.6787 | 42.4233 | 119.8927 | 59.3704 | 10.0269 | 56.092 | 1.0561 | 5.7233 | 32.1195 | 95.9791 | 14.6913 | 234.1147 | 123.9258 | 231.5938 | 12.0769 | 50.2727 | 2.3601 | 199 | 38.3037 | 22.5237 | 294.704 | 0.036089
5527 | 912.3654 | 2.8629 | 75.8229 | 116.8778 | 53.7597 | 15.3153 | 75.1013 | 2.4215 | 5.5033 | 31.4991 | 123.0853 | 28.0329 | 238.8777 | 176.9151 | 266.3035 | 24.1602 | 51.5698 | 7.7035 | 271 | 62.9364 | 17.9181 | 359.234 | 0.075766
5528 | 1003.3645 | 3.0987 | 97.171 | 126.5891 | 53.8382 | 17.0276 | 97.8661 | 3.5524 | 13.57 | 35.2388 | 151.2478 | 36.6004 | 269.7192 | 235.6736 | 356.2971 | 31.9154 | 57.2879 | 12.3896 | 305 | 70.0901 | 11.5547 | 417.7657 | 0.085536
5529 | 1071.8678 | 3.2787 | 101.5836 | 138.5833 | 55.514 | 19.3334 | 113.2782 | 3.9824 | 19.447 | 35.8428 | 165.5559 | 37.7342 | 298.1695 | 278.1344 | 470.4117 | 33.4766 | 64.1674 | 13.4923 | 347 | 65.8027 | 11.5547 | 463.5514 | 0.11523
5530 | 1122.2857 | 3.3836 | 137.8413 | 102.2838 | 62.1727 | 20.8666 | 117.3887 | 4.1448 | 18.8098 | 34.0559 | 168.6234 | 35.8728 | 301.1947 | 305.5705 | 533.8461 | 34.3857 | 69.5238 | 13.9235 | 328 | 65.7245 | 20.3582 | 494.0665 | 0.21161
5531 | 1141.4619 | 4.5914 | 76.1938 | 164.9009 | 73.0757 | 19.0838 | 124.0057 | 3.9109 | 17.3119 | 30.4253 | 168.9526 | 30.5284 | 348.5036 | 315.7732 | 538.6802 | 34.0284 | 76.4206 | 14.0759 | 342 | 81.6873 | 15.5802 | 501.6511 | 0.21836
5532 | 1132.6425 | 7.8528 | 94.3452 | 148.3338 | 77.479 | 17.6334 | 123.0903 | 3.9967 | 17.1378 | 27.9992 | 169.2599 | 28.0296 | 290.5508 | 313.5431 | 532.703 | 33.3357 | 86.4554 | 14.3412 | 366 | 83.4104 | 19.0551 | 490.9623 | 0.23223
5533 | 1138.8721 | 12.9087 | 104.1336 | 138.5543 | 67.6274 | 18.6716 | 126.8932 | 3.9405 | 19.0885 | 28.5057 | 170.777 | 26.7204 | 277.3144 | 313.7635 | 530.3384 | 33.3305 | 94.3862 | 14.2848 | 334 | 80.6183 | 20.5278 | 471.5362 | 0.24774
5534 | 1137.9229 | 14.4269 | 103.401 | 141.505 | 60.8697 | 18.3002 | 122.7723 | 3.8989 | 18.7877 | 30.2544 | 173.1867 | 25.0218 | 282.6659 | 314.1413 | 531.6698 | 33.997 | 97.8856 | 14.1138 | 308 | 75.9143 | 6.0759 | 453.6423 | 0.21258
5535 | 1109.2739 | 8.3954 | 94.2951 | 130.0364 | 63.3551 | 17.9804 | 102.3049 | 3.9018 | 13.5125 | 30.0023 | 172.7949 | 23.9744 | 351.3842 | 306.7491 | 527.1917 | 33.9557 | 99.1187 | 14.3584 | 278 | 69.1671 | 0.12564 | 439.0538 | 0.19082
5536 | 1078.708 | 4.0434 | 64.2272 | 145.4476 | 71.5747 | 12.468 | 97.5709 | 3.3789 | 13.0751 | 31.5789 | 170.0466 | 23.8411 | 325.1919 | 287.1803 | 503.5049 | 28.6507 | 99.4197 | 14.8877 | 241 | 60.2159 | 0.20102 | 404.9321 | 0.17082
5537 | 1014.7762 | 3.1588 | 46.8963 | 119.186 | 73.4892 | 9.7658 | 89.5123 | 2.0164 | 9.8708 | 36.517 | 158.6244 | 29.2069 | 289.8503 | 241.0076 | 455.6132 | 16.6199 | 97.2013 | 15.0622 | 223 | 60.0819 | 0.16333 | 349.0174 | 0.13968
5538 | 973.7618 | 2.3386 | 42.2698 | 105.1613 | 72.6827 | 8.7774 | 82.8253 | 1.1378 | 12.3156 | 40.341 | 130.271 | 27.8431 | 313.5591 | 182.3841 | 389.6361 | 11.1137 | 92.1394 | 12.8551 | 225 | 48.5528 | 0.16333 | 297.2096 | 0.078674
5539 | 930.7389 | 1.9691 | 38.6229 | 99.6258 | 72.3467 | 8.5587 | 64.2254 | 0.97782 | 12.8507 | 45.1038 | 102.4844 | 15.1418 | 250.4968 | 147.4297 | 330.3759 | 11.3491 | 86.1017 | 7.8727 | 199 | 44.9765 | 0.12664 | 255.1783 | 0.03045
5540 | 894.4209 | 3.1447 | 32.9287 | 99.5616 | 71.5886 | 7.8448 | 48.1132 | 1.059 | 8.4888 | 46.0999 | 92.6375 | 9.5759 | 186.6069 | 137.5749 | 285.0334 | 11.6136 | 81.0836 | 5.6295 | 188 | 42.8669 | 0.10087 | 228.2966 | 0
5541 | 867.6914 | 3.7464 | 30.5189 | 102.0898 | 68.0179 | 7.5963 | 48.5609 | 1.4479 | 6.7361 | 38.847 | 93.2667 | 12.2401 | 252.8765 | 132.0787 | 262.8781 | 11.1832 | 77.6434 | 5.2733 | 187 | 39.3973 | 0.11582 | 219.3182 | 0
5542 | 842.699 | 2.8785 | 30.2788 | 101.9213 | 62.141 | 8.3619 | 51.8911 | 1.5448 | 7.0044 | 31.5585 | 93.56 | 13.0106 | 205.7651 | 125.3065 | 268.9629 | 11.1386 | 75.9226 | 5.2569 | 180 | 39.9219 | 0.09 | 219.1045 | 0
5543 | 827.3086 | 1.7065 | 30.04 | 101.8041 | 54.4955 | 8.4783 | 53.5647 | 1.4446 | 7.01 | 29.1174 | 89.9672 | 12.9166 | 219.9399 | 114.7078 | 279.5224 | 11.3134 | 75.8852 | 5.1246 | 164 | 38.1193 | 0.09 | 216.6489 | 0
5544 | 811.4674 | 1.1315 | 30.1437 | 102.0273 | 44.219 | 8.5312 | 53.8377 | 1.4106 | 6.5561 | 28.4964 | 85.3617 | 13.6861 | 248.3087 | 105.1607 | 271.6206 | 11.4437 | 76.2212 | 4.8844 | 156 | 37.9147 | 0.069513 | 210.0917 | 0
5545 | 795.84 | 1.1465 | 29.9746 | 100.9852 | 39.9555 | 7.8752 | 47.2873 | 1.4152 | 6.4944 | 27.8738 | 82.9244 | 11.7299 | 254.0669 | 104.7535 | 260.0391 | 11.1076 | 76.3064 | 4.389 | 150 | 34.3578 | 0.0848 | 208.777 | 0
5546 | 776.7373 | 1.381 | 29.5287 | 100.7017 | 49.3954 | 7.5867 | 47.6772 | 1.4217 | 6.5564 | 27.4074 | 81.9092 | 12.3691 | 281.6501 | 103.433 | 249.996 | 10.99 | 76.4083 | 3.554 | 157 | 37.2041 | 0.08966 | 206.4504 | 0
5547 | 763.8538 | 1.5453 | 30.6773 | 87.5943 | 60.3115 | 8.3007 | 51.6306 | 1.4366 | 6.6897 | 28.6172 | 82.1342 | 18.0935 | 280.1585 | 98.4844 | 242.3169 | 11.3073 | 75.9997 | 3.1049 | 151 | 31.8601 | 0.089619 | 201.279 | 0
5548 | 767.1745 | 1.6789 | 34.6489 | 110.9338 | 64.4342 | 7.7778 | 52.4272 | 1.6526 | 6.2599 | 33.5558 | 83.4046 | 18.1001 | 295.6243 | 95.9272 | 241.7617 | 11.382 | 75.1412 | 3.1429 | 148 | 36.6108 | 0.089762 | 207.397 | 0
5549 | 777.4897 | 2.3179 | 31.729 | 104.2304 | 64.7618 | 7.6518 | 48.3519 | 1.4876 | 6.2114 | 36.0874 | 82.6902 | 13.0509 | 177.0331 | 100.8055 | 240.08 | 10.9513 | 74.3537 | 3.1804 | 136 | 33.1883 | 0.18007 | 223.4932 | 0
5550 | 821.9099 | 2.1808 | 86.4753 | 101.6498 | 62.5354 | 10.4065 | 56.303 | 1.1321 | 5.8065 | 30.8449 | 88.3411 | 14.6823 | 203.2269 | 126.0323 | 248.6052 | 14.1057 | 73.7174 | 2.8504 | 205 | 33.6218 | 0.27989 | 251.8634 | 0.020676
5551 | 874.3116 | 4.1511 | 56.6261 | 68.089 | 58.0929 | 14.3246 | 75.157 | 1.442 | 8.4485 | 27.4496 | 112.9692 | 23.4729 | 255.2507 | 178.7192 | 289.9906 | 24.6741 | 76.3887 | 7.6279 | 236 | 51.8032 | 0.16832 | 302.5687 | 0.04211
5552 | 960.319 | 8.602 | 69.3074 | 140.1494 | 54.8432 | 18.0023 | 99.4827 | 2.629 | 14.999 | 30.1336 | 142.0939 | 25.0218 | 246.3249 | 235.4745 | 376.7994 | 31.9741 | 84.1714 | 12.2736 | 298 | 63.5708 | 0.21106 | 369.4884 | 0.16325
5553 | 1042.4495 | 9.0404 | 76.9613 | 110.936 | 60.6598 | 18.4084 | 116.2489 | 3.5894 | 18.4795 | 35.983 | 156.3293 | 22.7002 | 311.8227 | 271.9426 | 478.3758 | 33.2217 | 92.7299 | 13.5851 | 318 | 61.1901 | 0.2819 | 424.4356 | 0.18591
5554 | 1098.0852 | 4.7177 | 76.1894 | 168.8381 | 70.3651 | 17.9637 | 118.4167 | 3.6172 | 17.4195 | 47.0092 | 161.3094 | 27.3909 | 356.674 | 292.6022 | 529.7757 | 32.7788 | 98.7103 | 15.6064 | 342 | 78.6279 | 0.44203 | 444.5862 | 0.19034
5555 | 1103.9907 | 3.2574 | 75.2962 | 150.3606 | 71.274 | 19.304 | 122.2274 | 3.7262 | 15.7856 | 55.4624 | 166.566 | 30.5232 | 273.8403 | 300.6465 | 524.6937 | 32.4005 | 102.9463 | 15.7604 | 304 | 85.3913 | 0.35667 | 441.4945 | 0.16173
5556 | 1099.4346 | 4.1779 | 76.949 | 142.8121 | 63.6129 | 21.5127 | 122.8413 | 3.6062 | 16.4348 | 54.4089 | 171.1808 | 37.1964 | 293.8431 | 301.9155 | 508.9353 | 32.5513 | 104.8777 | 15.1812 | 296 | 81.2234 | 0.27696 | 441.0382 | 0.15006
5557 | 1129.2175 | 5.9167 | 102.681 | 140.1509 | 59.3665 | 19.7137 | 123.8951 | 3.3777 | 16.6933 | 54.5302 | 174.5349 | 39.7841 | 301.1842 | 311.4283 | 499.9002 | 32.2802 | 104.1808 | 14.9653 | 286 | 79.8914 | 0.36348 | 450.3769 | 0.18403
5558 | 1117.694 | 6.5535 | 56.3936 | 142.6625 | 61.669 | 17.5233 | 115.9386 | 3.179 | 15.5153 | 59.7363 | 174.9706 | 37.7523 | 349.1392 | 315.594 | 494.667 | 31.7868 | 103.0323 | 15.0834 | 251 | 81.8698 | 0.32622 | 456.5146 | 0.20144
5559 | 1056.2085 | 5.1451 | 70.0337 | 138.6516 | 69.3044 | 12.9288 | 103.2574 | 3.1309 | 13.206 | 58.7485 | 172.4916 | 32.7457 | 328.3364 | 301.8281 | 489.7822 | 31.2852 | 101.5726 | 15.3109 | 255 | 74.322 | 0.16321 | 445.5357 | 0.15842
5560 | 996.1505 | 3.4101 | 76.3806 | 129.9488 | 75.1647 | 7.1376 | 99.9603 | 2.3363 | 13.3598 | 51.3305 | 171.3551 | 27.3238 | 295.1195 | 274.9215 | 464.6227 | 20.7294 | 97.951 | 15.4255 | 236 | 70.6532 | 0.16045 | 395.8306 | 0.14827
5561 | 941.0508 | 2.9172 | 76.2822 | 117.1905 | 74.9555 | 7.1097 | 88.9188 | 1.2759 | 13.6051 | 42.8616 | 163.5548 | 23.3802 | 283.5709 | 225.502 | 406.3537 | 10.8862 | 92.6291 | 15.6513 | 210 | 58.0079 | 0.1104 | 331.725 | 0.1364
5562 | 883.8035 | 1.9438 | 102.3442 | 96.8326 | 74.8781 | 6.8964 | 80.8199 | 1.1715 | 11.9439 | 36.8262 | 139.305 | 17.4758 | 292.2768 | 186.3153 | 339.686 | 8.9925 | 87.8405 | 13.6778 | 212 | 57.8934 | 0.089916 | 286.8522 | 0.14039
5563 | 840.9917 | 1.3109 | 76.288 | 112.2854 | 74.4982 | 6.6377 | 63.6191 | 1.076 | 7.6562 | 39.8479 | 113.4932 | 7.7359 | 242.4269 | 177.6362 | 297.3733 | 9.0183 | 82.911 | 8.9453 | 200 | 59.9078 | 0.089945 | 252.4824 | 0.051914
5564 | 818.4612 | 2.7441 | 56.5562 | 99.5586 | 70.5941 | 8.0236 | 48.0918 | 1.0542 | 5.9955 | 43.3741 | 95.9208 | 4.0087 | 211.1142 | 164.1597 | 268.6534 | 9.4485 | 77.6715 | 6.4141 | 188 | 54.9611 | 0.089742 | 234.2532 | 0
5565 | 809.9304 | 3.5224 | 37.5088 | 96.4066 | 65.4139 | 7.8483 | 48.7459 | 1.2886 | 6.0267 | 37.0227 | 82.3994 | 5.3826 | 238.7893 | 149.5898 | 255.7596 | 9.5195 | 71.2902 | 5.722 | 190 | 60.244 | 0.11634 | 233.992 | 0
5566 | 807.0037 | 2.9823 | 26.5887 | 99.6115 | 58.5322 | 6.908 | 52.0259 | 1.5026 | 7.0729 | 28.3777 | 75.3838 | 6.0622 | 292.111 | 152.7462 | 255.916 | 9.4476 | 61.0993 | 5.2217 | 184 | 53.6846 | 0.069558 | 237.0709 | 0
5567 | 787.9453 | 1.8796 | 33.5761 | 100.4985 | 45.9578 | 7.3894 | 53.3205 | 1.5767 | 6.704 | 24.4211 | 73.4365 | 6.1284 | 181.3669 | 160.4224 | 260.9006 | 9.8066 | 52.3661 | 4.794 | 160 | 53.2805 | 0.08431 | 235.591 | 0
5568 | 777.5113 | 1.2342 | 24.33 | 100.4651 | 42.7491 | 7.6638 | 50.5116 | 1.4611 | 6.5393 | 25.4833 | 73.633 | 6.1067 | 268.1036 | 163.7996 | 268.4911 | 9.6308 | 49.8742 | 4.421 | 156 | 44.7278 | 0.11613 | 231.6781 | 0
5569 | 762.8909 | 1.374 | 18.0967 | 100.48 | 53.1575 | 7.5509 | 49.2749 | 1.4091 | 6.5273 | 25.9442 | 74.2305 | 6.1075 | 262.1989 | 158.9819 | 269.0877 | 9.5372 | 50.166 | 4.3032 | 148 | 46.5252 | 0.069707 | 222.0814 | 0
5570 | 753.5252 | 1.3263 | 21.4508 | 100.2854 | 56.5669 | 7.646 | 51.3011 | 1.4166 | 6.6033 | 22.76 | 74.1283 | 6.0832 | 273.5967 | 146.1132 | 258.8516 | 9.6417 | 50.1976 | 4.1848 | 147 | 44.6214 | 0.084862 | 209.5407 | 0
5571 | 745.0959 | 2.2231 | 23.3653 | 100.2878 | 54.3035 | 7.5702 | 52.6553 | 1.4432 | 6.5907 | 21.9478 | 73.9369 | 6.157 | 178.6118 | 136.8032 | 251.6692 | 9.5543 | 50.0141 | 4.0266 | 141 | 42.4419 | 0.090088 | 201.6921 | 0
5572 | 740.9365 | 2.2303 | 22.9557 | 100.4147 | 53.5181 | 7.4879 | 51.5625 | 1.4999 | 6.5595 | 28.2205 | 73.5515 | 6.1765 | 236.8498 | 131.0172 | 249.68 | 9.6811 | 49.9943 | 3.9079 | 144 | 36.8368 | 0.096107 | 199.7308 | 0
5573 | 750.514 | 2.4321 | 23.3165 | 94.5895 | 52.6423 | 7.6235 | 46.3318 | 1.5256 | 6.9767 | 33.1303 | 71.5102 | 4.9453 | 247.8667 | 127.3126 | 240.4434 | 9.4357 | 49.443 | 3.4572 | 139 | 38.6886 | 0.092541 | 200.3981 | 0
5574 | 770.2737 | 1.6465 | 32.3498 | 99.2172 | 52.4621 | 6.8723 | 47.7666 | 1.242 | 6.298 | 27.0374 | 68.9891 | 3.7755 | 279.5286 | 128.5563 | 230.2289 | 9.312 | 48.962 | 3.1303 | 139 | 40.5025 | 0.082434 | 197.7661 | 0.046156
5575 | 781.964 | 0.77915 | 49.2019 | 100.2285 | 50.588 | 8.1491 | 52.2611 | 1.0486 | 5.6437 | 18.9058 | 70.9115 | 5.5315 | 214.6453 | 128.2045 | 221.4457 | 9.0284 | 48.7173 | 3.281 | 146 | 43.9088 | 0.088164 | 197.6885 | 0.04015
5576 | 792.3837 | 0.74248 | 62.6363 | 87.7507 | 49.2953 | 9.2826 | 51.8399 | 1.095 | 5.5955 | 16.2707 | 86.9678 | 11.5824 | 230.5672 | 120.4593 | 221.1243 | 9.0491 | 47.9221 | 4.1937 | 143 | 47.1542 | 0.15509 | 201.1872 | 0.085473
5577 | 842.7019 | 0.87648 | 70.287 | 126.9718 | 50.8445 | 8.7482 | 50.5423 | 1.0994 | 5.4359 | 17.0072 | 113.7312 | 14.1001 | 229.6572 | 115.6608 | 236.7595 | 9.2663 | 47.5568 | 6.9454 | 157 | 50.4242 | 0.15738 | 203.1395 | 0.14211
5578 | 875.9861 | 1.019 | 73.6567 | 103.396 | 53.3491 | 8.5191 | 46.6624 | 1.0363 | 7.0521 | 20.1152 | 129.0732 | 13.8724 | 281.3047 | 143.0184 | 249.3729 | 8.8085 | 47.9943 | 11.9225 | 171 | 73.6904 | 0.13504 | 205.073 | 0.21486
5579 | 882.236 | 1.1384 | 73.7747 | 120.9474 | 58.7252 | 6.4536 | 48.4379 | 0.98583 | 6.4469 | 22.8323 | 118.7704 | 14.1859 | 231.8569 | 177.6616 | 253.2022 | 9.1194 | 48.9643 | 14.0124 | 173 | 43.4038 | 0.10937 | 200.7909 | 0.21018
5580 | 862.4542 | 1.0784 | 73.6117 | 135.4574 | 61.1805 | 7.8697 | 51.3905 | 1.2359 | 5.6034 | 23.516 | 98.2046 | 14.0361 | 239.6319 | 167.151 | 253.3052 | 9.0888 | 51.7146 | 14.2502 | 193 | 50.2 | 0.17916 | 189.8827 | 0.16376
5581 | 846.7038 | 1.5587 | 67.9833 | 118.9653 | 66.0985 | 7.0882 | 51.4326 | 1.1628 | 5.791 | 23.7413 | 90.0019 | 14.0098 | 257.2144 | 145.5225 | 254.5577 | 8.9218 | 55.1733 | 14.774 | 194 | 53.6534 | 0.19005 | 183.279 | 0.20099
5582 | 854.3598 | 5.2198 | 50.9494 | 76.9696 | 72.7426 | 7.9453 | 50.7696 | 1.0002 | 7.1339 | 25.125 | 91.374 | 15.2037 | 199.6247 | 140.2158 | 279.8902 | 9.0109 | 55.5619 | 15.2534 | 189 | 49.3815 | 0.099174 | 181.2864 | 0.19602
5583 | 857.4097 | 4.5367 | 42.9381 | 102.1375 | 74.9795 | 7.182 | 46.5075 | 0.98385 | 10.8452 | 26.2619 | 93.8372 | 16.524 | 200.1286 | 132.2488 | 314.2902 | 8.9509 | 53.441 | 15.4419 | 199 | 44.5361 | 0.12845 | 183.8307 | 0.069758
5584 | 869.9817 | 3.1988 | 43.4826 | 73.3341 | 71.791 | 7.422 | 47.899 | 0.99558 | 8.9702 | 24.1466 | 94.1112 | 10.7612 | 234.363 | 123.5549 | 318.9725 | 9.1334 | 51.8785 | 15.1381 | 194 | 43.4392 | 0.10597 | 188.465 | 0.067277
5585 | 871.654 | 1.7918 | 41.6653 | 100.0828 | 71.6627 | 6.1644 | 50.8103 | 0.98583 | 6.8942 | 21.6161 | 89.3795 | 5.1932 | 234.215 | 121.3347 | 306.6188 | 8.8021 | 51.7983 | 12.3592 | 190 | 44.5684 | 0.089948 | 187.2055 | 0.057023
5586 | 859.2244 | 1.2856 | 40.0514 | 89.7618 | 68.6101 | 7.8204 | 52.0406 | 0.99039 | 6.3915 | 25.2635 | 80.2529 | 4.1339 | 186.527 | 121.5301 | 284.5473 | 8.8812 | 52.2865 | 7.6064 | 191 | 40.3722 | 0.090013 | 182.8496 | 0.027076
5587 | 847.7986 | 2.7408 | 39.5214 | 83.6399 | 65.6153 | 7.7782 | 49.1659 | 1.2598 | 5.9086 | 35.7564 | 71.3661 | 4.0668 | 204.4426 | 119.9498 | 269.6035 | 8.8663 | 51.6627 | 4.8668 | 192 | 43.3579 | 0.08937 | 180.9066 | 0.0049135
5588 | 839.1947 | 3.3516 | 39.6454 | 84.7412 | 62.7781 | 6.9257 | 51.6144 | 1.4315 | 5.9869 | 43.6726 | 69.0752 | 4.9477 | 259.8376 | 118.1481 | 266.0593 | 9.1082 | 50.2792 | 4.2688 | 182 | 40.8673 | 0.090021 | 183.1859 | 0
5589 | 829.2021 | 3.14 | 39.5449 | 85.4709 | 58.9778 | 7.9773 | 54.7333 | 1.4277 | 6.3195 | 41.29 | 72.7367 | 6.2817 | 193.8675 | 118.1196 | 269.0971 | 9.6569 | 49.2608 | 4.2534 | 185 | 42.0861 | 0.089666 | 187.8302 | 0
5590 | 817.0906 | 2.5144 | 39.111 | 94.7533 | 59.4248 | 7.9208 | 53.285 | 1.4442 | 6.6181 | 34.6842 | 75.2987 | 6.7007 | 219.6753 | 119.6576 | 271.2951 | 9.474 | 48.5476 | 3.8879 | 171 | 41.0371 | 0.090389 | 188.0514 | 0
5591 | 808.267 | 1.6927 | 39.3478 | 99.8496 | 62.149 | 7.6467 | 46.7309 | 1.4573 | 6.5215 | 30.4537 | 75.4384 | 6.7096 | 224.7266 | 123.5037 | 274.8215 | 9.3459 | 48.1404 | 3.6371 | 154 | 37.673 | 0.11791 | 181.5281 | 0
5592 | 804.8935 | 1.9322 | 38.9464 | 85.9456 | 63.8205 | 7.6506 | 48.8895 | 1.4622 | 6.2575 | 26.3504 | 75.5616 | 7.0152 | 255.0348 | 141.0873 | 278.4317 | 9.3459 | 48.0335 | 3.4318 | 156 | 40.9627 | 0.090909 | 176.7707 | 0
5593 | 793.1606 | 1.6444 | 38.7812 | 100.0412 | 61.2919 | 9.7143 | 52.5399 | 1.4742 | 6.1983 | 22.6627 | 74.5652 | 7.1624 | 186.5204 | 161.0572 | 274.1959 | 9.681 | 47.9919 | 3.0527 | 155 | 39.6534 | 0.090909 | 177.2886 | 0
5594 | 783.9595 | 1.2043 | 38.5708 | 110.2449 | 61.6854 | 7.612 | 49.4448 | 1.5302 | 6.7925 | 20.648 | 72.6606 | 6.9497 | 178.8949 | 168.1187 | 256.9374 | 9.5145 | 47.9422 | 2.9929 | 161 | 39.5302 | 0.070336 | 177.6606 | 0
5595 | 791.4389 | 1.1952 | 39.4157 | 103.1089 | 60.0375 | 7.3639 | 48.7259 | 1.7233 | 6.7111 | 19.9091 | 71.9538 | 6.8221 | 206.7806 | 168.0856 | 242.2332 | 9.4445 | 47.8623 | 2.8466 | 155 | 37.9288 | 0.08534 | 178.0678 | 0
5596 | 785.5734 | 1.5547 | 43.703 | 100.1796 | 57.2981 | 8.2874 | 51.5379 | 1.6133 | 6.4365 | 21.4836 | 71.7748 | 6.8045 | 191.9753 | 164.5629 | 235.1559 | 9.6104 | 47.8813 | 2.8295 | 148 | 37.1662 | 0.090732 | 177.7733 | 0
5597 | 780.5279 | 2.3871 | 40.7165 | 98.4079 | 57.5093 | 7.7177 | 52.4013 | 1.3674 | 6.2228 | 22.0492 | 69.6266 | 5.7461 | 196.0497 | 153.9658 | 226.688 | 9.1575 | 47.5616 | 2.6851 | 138 | 37.0024 | 0.090055 | 173.2157 | 0
5598 | 799.9915 | 1.6858 | 37.9918 | 96.338 | 57.2308 | 7.6024 | 45.6746 | 1.1452 | 6.0742 | 18.7173 | 66.4153 | 4.5608 | 221.9134 | 127.7873 | 225.368 | 9.1936 | 46.9512 | 2.6557 | 136 | 36.4035 | 0.090554 | 168.6615 | 0.02033
5599 | 809.1061 | 0.87899 | 38.1621 | 95.9407 | 57.7544 | 6.991 | 47.4961 | 1.0495 | 5.7902 | 15.4796 | 65.3175 | 6.6959 | 198.5235 | 105.2701 | 218.8889 | 9.0147 | 46.4361 | 3.0492 | 131 | 31.657 | 0.11843 | 166.0258 | 0.035066
5600 | 820.259 | 0.90297 | 38.3937 | 96.6621 | 56.6755 | 8.8001 | 50.5413 | 1.0917 | 5.41 | 16.3935 | 66.8811 | 8.556 | 194.2848 | 102.9758 | 218.2128 | 8.7249 | 46.0071 | 3.6665 | 131 | 34.5399 | 0.090909 | 165.4724 | 0.054159
5601 | 827.0015 | 0.881 | 39.5327 | 96.7602 | 60.9045 | 8.6966 | 46.3903 | 1.1224 | 5.2876 | 21.9633 | 69.3681 | 6.6469 | 207.3695 | 108.2228 | 225.7499 | 9.0621 | 45.9417 | 6.6507 | 149 | 36.5885 | 0.0699 | 166.1113 | 0.14813
5602 | 837.7067 | 1.3507 | 40.156 | 79.5204 | 68.9141 | 7.2278 | 48.3013 | 2.0177 | 7.0242 | 29.6514 | 70.5225 | 4.6488 | 181.4483 | 115.8636 | 229.017 | 8.9724 | 46.1118 | 11.4472 | 163 | 35.4638 | 0.085024 | 168.8106 | 0.18415
5603 | 861.579 | 4.028 | 55.4719 | 106.2186 | 78.5893 | 6.6468 | 51.7276 | 2.459 | 11.4616 | 36.3163 | 73.7398 | 4.6141 | 250.499 | 126.7786 | 230.2937 | 9.024 | 46.0954 | 13.4434 | 165 | 39.1253 | 0.089533 | 170.9661 | 0.23228
5604 | 870.2188 | 7.208 | 30.7506 | 84.8288 | 76.7251 | 7.3699 | 51.6858 | 1.9864 | 13.1039 | 39.5683 | 84.4155 | 4.6395 | 176.2051 | 139.8292 | 231.49 | 9.4973 | 46.0837 | 13.7155 | 175 | 37.2431 | 0.090049 | 169.2714 | 0.24385
5605 | 853.8576 | 8.1183 | 38.4872 | 107.8554 | 69.0497 | 9.0066 | 51.6494 | 1.3981 | 11.5471 | 38.6655 | 102.0268 | 5.134 | 210.302 | 149.0867 | 236.158 | 9.6484 | 46.7164 | 14.1804 | 182 | 40.6731 | 0.090194 | 169.8438 | 0.27687
5606 | 844.4873 | 6.5915 | 43.4246 | 105.072 | 72.7406 | 7.4049 | 51.8783 | 1.2715 | 12.5573 | 35.6127 | 115.7949 | 5.9744 | 214.7552 | 152.155 | 255.2815 | 9.5289 | 47.0131 | 14.4612 | 172 | 38.9937 | 0.090238 | 170.7237 | 0.26198
5607 | 847.7958 | 3.3097 | 44.0556 | 103.8075 | 76.0636 | 6.5645 | 51.7618 | 1.1028 | 12.0693 | 32.9496 | 115.537 | 7.537 | 273.9931 | 147.1136 | 261.0851 | 9.2516 | 46.6045 | 15.0671 | 184 | 42.9669 | 0.088922 | 171.3751 | 0.18845
5608 | 847.1169 | 4.8347 | 44.1401 | 100.4386 | 75.1466 | 6.6907 | 48.8302 | 0.94567 | 7.8337 | 29.3445 | 109.3774 | 6.7532 | 184.6684 | 139.6806 | 260.2495 | 9.2119 | 46.7339 | 15.7914 | 180 | 40.7844 | 0.11704 | 171.8676 | 0.1525
5609 | 855.3248 | 3.5999 | 44.1821 | 99.553 | 77.1701 | 6.6668 | 48.9942 | 0.93648 | 5.849 | 25.074 | 105.1172 | 8.1404 | 213.7032 | 139.1724 | 267.7037 | 8.9848 | 47.6685 | 14.0875 | 170 | 43.9858 | 0.069707 | 167.9605 | 0.16636
5610 | 845.944 | 1.2852 | 44.1356 | 84.1232 | 77.0314 | 7.41 | 48.642 | 0.93477 | 5.9 | 22.5323 | 101.1129 | 7.8895 | 319.6278 | 138.8656 | 268.3787 | 8.8947 | 48.2843 | 9.1058 | 153 | 42.9916 | 0.11029 | 165.4654 | 0.089378
5611 | 827.92 | 1.2982 | 43.6783 | 110.7964 | 74.7618 | 6.787 | 49.2312 | 1.2024 | 5.3955 | 22.1921 | 96.4247 | 5.2485 | 117.063 | 133.428 | 254.6842 | 9.1171 | 47.9977 | 6.5553 | 145 | 41.0889 | 0.09 | 164.7586 | 0.045895
5612 | 809.3651 | 2.6585 | 42.3685 | 102.6212 | 71.5809 | 6.7244 | 50.8913 | 1.2867 | 5.4665 | 22.6514 | 90.0176 | 4.4618 | 171.3499 | 130.3991 | 228.6957 | 9.2818 | 47.6028 | 6.3243 | 133 | 42.1749 | 0.070252 | 163.4694 | 0
5613 | 775.2596 | 3.779 | 41.4239 | 99.7884 | 65.817 | 8.8004 | 51.9411 | 1.3222 | 5.6434 | 21.6828 | 85.8694 | 5.9255 | 207.4964 | 132.7098 | 217.034 | 9.1468 | 48.1188 | 6.2563 | 142 | 40.4233 | 0.083683 | 167.2118 | 0
5614 | 768.1467 | 2.9403 | 55.2602 | 99.9442 | 65.3763 | 7.3919 | 52.9809 | 1.4133 | 6.0188 | 20.0235 | 84.8477 | 6.6853 | 230.8819 | 133.1203 | 219.9935 | 9.5492 | 48.9337 | 5.7545 | 133 | 41.5505 | 0.090494 | 175.1272 | 0
5615 | 762.1372 | 1.5555 | 29.8039 | 101.8176 | 62.904 | 7.8979 | 52.8901 | 1.4262 | 6.2967 | 18.9931 | 80.8982 | 6.7548 | 206.2009 | 132.544 | 221.4349 | 10.5845 | 48.8124 | 5.0779 | 129 | 38.311 | 0.088502 | 176.6673 | 0
5616 | 750.1957 | 1.2152 | 35.9984 | 103.2165 | 50.1728 | 9.234 | 51.7724 | 1.419 | 6.0295 | 18.731 | 75.6066 | 6.7512 | 201.2765 | 132.8655 | 223.532 | 12.6103 | 48.7205 | 4.6288 | 127 | 34.6797 | 0.089881 | 172.1105 | 0
5617 | 757.3243 | 1.3419 | 39.3966 | 103.4482 | 40.6813 | 9.007 | 48.8409 | 1.4311 | 6.0805 | 18.7235 | 73.4497 | 6.7578 | 228.8925 | 126.7193 | 232.4038 | 13.9075 | 49.3927 | 3.9914 | 123 | 36.5998 | 0.084519 | 170.8501 | 0
5618 | 754.1245 | 1.1839 | 39.2845 | 104.0467 | 38.2262 | 9.2762 | 50.4964 | 1.4439 | 6.4423 | 18.6983 | 73.2747 | 7.1551 | 165.5741 | 112.3953 | 241.7675 | 13.7037 | 50.2506 | 3.4463 | 119 | 36.1233 | 0.094506 | 172.2365 | 0
5619 | 743.3069 | 1.1618 | 40.4627 | 106.0012 | 37.6894 | 9.5064 | 52.4653 | 1.7222 | 6.3733 | 20.2978 | 73.042 | 7.205 | 172.6388 | 101.3213 | 243.5293 | 13.7935 | 50.5485 | 3.2786 | 119 | 34.1268 | 0.092573 | 173.7232 | 0
5620 | 752.9224 | 1.6564 | 44.0189 | 109.1779 | 51.4416 | 6.5206 | 52.3728 | 1.6421 | 6.4667 | 27.2835 | 72.3404 | 6.8423 | 175.03 | 96.0758 | 230.9031 | 12.4896 | 50.2031 | 3.2679 | 118 | 36.3863 | 0.089031 | 181.5693 | 0
5621 | 762.1987 | 2.7001 | 40.7958 | 103.4831 | 63.977 | 5.6585 | 51.9852 | 1.3221 | 6.3113 | 32.3012 | 70.5513 | 7.3747 | 236.2678 | 94.8346 | 221.6595 | 10.2179 | 49.503 | 3.0655 | 120 | 34.6714 | 0.16772 | 196.7361 | 0
5622 | 808.111 | 2.8456 | 50.3925 | 100.0987 | 59.673 | 12.1534 | 53.869 | 1.2288 | 5.9484 | 29.0607 | 81.8804 | 11.8349 | 207.1384 | 117.9906 | 233.9199 | 12.4124 | 49.1957 | 3.284 | 167 | 40.4485 | 0.20123 | 228.8429 | 0.038098
5623 | 869.511 | 4.2584 | 79.3313 | 110.0238 | 57.8314 | 14.9211 | 81.583 | 2.0018 | 10.5641 | 30.6848 | 112.7701 | 22.7656 | 204.7736 | 173.981 | 287.8719 | 24.3948 | 51.7283 | 8.5851 | 263 | 54.3252 | 0.25032 | 288.3088 | 0.056937
5624 | 976.1755 | 6.379 | 96.7992 | 124.881 | 61.4188 | 15.2087 | 102.345 | 3.7646 | 17.8129 | 37.6545 | 142.4148 | 29.3317 | 246.9568 | 234.7052 | 383.8443 | 31.4883 | 58.784 | 13.0505 | 307 | 73.7403 | 0.28407 | 373.2291 | 0.056681
5625 | 1084.9832 | 6.8414 | 101.2773 | 137.9105 | 66.4952 | 15.9774 | 110.9314 | 5.2283 | 21.2667 | 44.1772 | 161.2959 | 31.0748 | 333.9001 | 274.5627 | 465.6647 | 34.5602 | 69.3051 | 14.0166 | 339 | 74.6095 | 0.26321 | 459.1457 | 0.10341
5626 | 1121.9464 | 6.7981 | 101.279 | 161.3245 | 73.0885 | 16.0716 | 124.9707 | 5.4907 | 20.0274 | 53.3773 | 170.673 | 30.8679 | 331.7544 | 297.8428 | 517.9256 | 36.5943 | 86.9994 | 14.4504 | 333 | 89.2078 | 0.13914 | 491.6409 | 0.21317
5627 | 1139.8289 | 5.8457 | 136.2926 | 167.2004 | 77.4977 | 17.6232 | 136.411 | 4.402 | 16.5434 | 63.49 | 173.9518 | 29.9216 | 387.2395 | 310.4086 | 535.032 | 36.5208 | 103.6345 | 14.8358 | 315 | 87.1019 | 0.16871 | 481.3259 | 0.23577
5628 | 1141.6678 | 4.8839 | 74.7832 | 169.5581 | 69.2661 | 17.9951 | 131.368 | 3.9419 | 16.7555 | 67.7501 | 175.2803 | 28.0104 | 381.1752 | 311.6674 | 535.0856 | 36.3646 | 107.3143 | 15.2757 | 337 | 82.487 | 0.17986 | 474.5662 | 0.23094
5629 | 1143.0084 | 8.4788 | 93.2834 | 148.5692 | 64.4402 | 16.0088 | 134.0171 | 3.8505 | 19.7377 | 63.6898 | 176.094 | 28.4616 | 357.0989 | 317.4781 | 539.2016 | 36.1196 | 105.9555 | 15.7267 | 281 | 72.2571 | 0.18057 | 477.2918 | 0.26973
5630 | 1137.6594 | 6.8781 | 99.6178 | 190.2328 | 67.5354 | 15.8231 | 135.9084 | 3.5585 | 19.9327 | 58.4958 | 179.3296 | 30.0914 | 381.3275 | 322.108 | 539.4017 | 34.3073 | 104.9501 | 15.8846 | 272 | 78.7507 | 0.17984 | 478.6271 | 0.25392
5631 | 1125.7188 | 3.9528 | 101.5517 | 149.3045 | 74.1976 | 11.9774 | 124.8905 | 3.3636 | 16.2834 | 55.2392 | 183.0153 | 32.0196 | 376.6442 | 309.6897 | 539.46 | 33.3029 | 103.5531 | 15.3428 | 271 | 67.8103 | 0.23186 | 467.9068 | 0.17834
5632 | 1083.388 | 3.2936 | 100.4284 | 180.3192 | 73.5541 | 11.1136 | 111.8475 | 3.619 | 17.4933 | 54.0695 | 183.2652 | 34.2816 | 394.6241 | 288.0704 | 504.5337 | 28.6518 | 101.7877 | 14.6437 | 257 | 50.3995 | 0.18 | 433.8151 | 0.17242
5633 | 1030.0484 | 2.9662 | 93.2904 | 144.4425 | 73.4722 | 8.5887 | 92.0018 | 3.1752 | 18.6035 | 49.8364 | 172.7601 | 34.2844 | 333.2825 | 243.3507 | 429.9097 | 17.3592 | 98.2168 | 14.3809 | 251 | 46.5253 | 0.13945 | 373.7461 | 0.1169
5634 | 1000.1991 | 2.1835 | 88.7014 | 119.4612 | 73.7087 | 7.5966 | 82.1048 | 2.2465 | 15.7445 | 44.9507 | 145.7801 | 27.1727 | 240.7679 | 192.6075 | 360.5003 | 11.1898 | 92.8175 | 12.1987 | 237 | 39.3488 | 0.16795 | 310.9271 | 0.078445
5635 | 950.161 | 3.399 | 73.3885 | 98.9451 | 72.6464 | 7.5889 | 65.1894 | 1.7602 | 8.6455 | 49.6162 | 117.7012 | 11.2838 | 231.9416 | 172.0926 | 323.3996 | 10.7222 | 88.4547 | 7.0654 | 211 | 38.0318 | 0.1799 | 265.0229 | 0.012903
5636 | 919.0648 | 3.886 | 44.3041 | 67.2365 | 71.0881 | 6.9196 | 53.8805 | 1.656 | 5.8695 | 53.9095 | 107.2775 | 5.7821 | 377.8032 | 159.417 | 305.2349 | 10.6986 | 85.9353 | 4.6985 | 202 | 36.5323 | 0.18089 | 239.4951 | 0
5637 | 904.7751 | 3.0827 | 31.4471 | 56.7462 | 67.7639 | 7.3594 | 56.8349 | 1.7074 | 6.1435 | 45.5134 | 107.5219 | 7.1269 | 268.2695 | 136.1628 | 283.4257 | 11.1726 | 83.4972 | 4.4925 | 196 | 39.1794 | 0.2318 | 230.042 | 0
5638 | 879.3112 | 2.5214 | 30.2882 | 28.5727 | 64.8852 | 8.2773 | 58.726 | 1.7105 | 6.7365 | 32.7687 | 101.2324 | 7.233 | 235.3609 | 116.8534 | 269.5137 | 11.0983 | 80.729 | 4.3832 | 166 | 36.8294 | 0.18 | 226.2117 | 0
5639 | 862.3814 | 1.8023 | 29.6194 | 74.8851 | 64.6504 | 8.4226 | 59.3414 | 1.8354 | 6.734 | 26.8501 | 88.9053 | 7.0394 | 247.4747 | 109.0258 | 261.3981 | 10.939 | 78.3023 | 4.2553 | 152 | 39.1751 | 0.13831 | 221.8019 | 0
5640 | 854.9926 | 1.2835 | 29.3219 | 91.0861 | 65.8292 | 7.2793 | 52.6272 | 1.5713 | 6.476 | 26.2514 | 81.4281 | 7.1372 | 256.7041 | 104.4991 | 243.3095 | 10.8164 | 77.2438 | 3.8425 | 150 | 31.8605 | 0.16311 | 218.9016 | 0
5641 | 847.1277 | 1.0693 | 28.9489 | 100.7967 | 63.8882 | 7.3699 | 48.8207 | 1.326 | 6.2924 | 25.9586 | 80.1348 | 7.1195 | 217.387 | 99.6391 | 237.7271 | 11.0918 | 77.1724 | 3.5256 | 145 | 31.198 | 0.12143 | 219.0446 | 0
5642 | 826.4135 | 1.0272 | 28.4033 | 101.0927 | 61.7023 | 6.8741 | 50.4593 | 1.3127 | 6.1467 | 24.6353 | 80.7249 | 9.2059 | 278.9405 | 97.2812 | 247.0432 | 11.1397 | 77.6076 | 4.0301 | 144 | 30.3221 | 0.09403 | 220.616 | 0
5643 | 818.7762 | 1.2862 | 29.3931 | 100.4694 | 59.9761 | 7.3452 | 50.9377 | 1.5097 | 6.1679 | 25.0094 | 81.1017 | 14.939 | 202.9221 | 95.4472 | 249.3735 | 10.844 | 77.7769 | 4.058 | 148 | 28.7962 | 0.11366 | 223.0585 | 0
5644 | 827.7075 | 1.7502 | 33.0486 | 100.1611 | 59.6041 | 7.565 | 49.9967 | 1.4527 | 6.304 | 31.5491 | 81.2531 | 14.9959 | 223.8635 | 94.2826 | 244.4452 | 11.2526 | 77.0458 | 4.0624 | 145 | 27.8905 | 0.12057 | 230.1299 | 0
5645 | 838.4391 | 2.492 | 38.4252 | 99.4157 | 53.3406 | 8.3669 | 45.3248 | 1.238 | 6.1325 | 36.7622 | 79.6403 | 11.5156 | 262.6937 | 97.686 | 232.8752 | 10.7797 | 76.0747 | 3.9565 | 141 | 24.0315 | 0.12232 | 244.8969 | 0
5646 | 875.1547 | 2.934 | 51.3299 | 102.6191 | 44.2334 | 9.2744 | 52.403 | 1.0402 | 5.7391 | 34.4886 | 85.5894 | 13.0138 | 234.2816 | 123.083 | 231.3375 | 14.0641 | 75.5759 | 3.6324 | 205 | 34.9153 | 0.1214 | 279.7443 | 0.01139
5647 | 929.9892 | 3.4274 | 77.3714 | 107.0842 | 46.1855 | 13.1368 | 78.4391 | 1.9819 | 8.7562 | 38.6641 | 110.4682 | 24.1215 | 258.8012 | 177.6998 | 287.4654 | 25.7376 | 78.5747 | 8.7735 | 282 | 50.6286 | 0.27128 | 334.5295 | 0.084247
5648 | 991.2365 | 3.8611 | 131.5968 | 121.8742 | 54.978 | 13.4737 | 105.7056 | 4.6391 | 17.678 | 44.2298 | 141.9105 | 32.2106 | 284.4475 | 234.3318 | 389.142 | 34.0448 | 86.8644 | 12.8559 | 313 | 57.2845 | 0.2929 | 395.898 | 0.17475
5649 | 1072.1948 | 6.9982 | 75.5163 | 136.3363 | 54.9738 | 16.6992 | 124.1832 | 4.4347 | 20.4968 | 44.0885 | 161.3607 | 34.4219 | 335.0637 | 272.9864 | 478.0597 | 36.7825 | 96.67 | 13.3681 | 335 | 59.5245 | 0.28469 | 455.4867 | 0.23549
5650 | 1107.4416 | 10.0323 | 92.8736 | 143.8168 | 55.8948 | 18.7524 | 125.3258 | 3.423 | 18.77 | 45.1071 | 165.0904 | 34.8372 | 308.5138 | 300.0002 | 535.5112 | 37.8776 | 104.7894 | 13.6582 | 356 | 64.7745 | 0.28869 | 482.9821 | 0.25179
5651 | 1128.9849 | 8.518 | 100.9215 | 144.6701 | 62.8803 | 16.3129 | 134.5386 | 3.4791 | 15.27 | 48.7809 | 166.7548 | 37.3806 | 362.3136 | 316.7978 | 568.2603 | 38.9522 | 110.6164 | 14.1801 | 336 | 69.023 | 0.37157 | 490.0854 | 0.24443
5652 | 1127.2733 | 5.4177 | 102.98 | 107.7414 | 71.4199 | 15.802 | 137.8301 | 3.6958 | 14.31 | 54.4501 | 176.0989 | 35.9756 | 369.6955 | 320.9361 | 569.9262 | 40.0541 | 113.1871 | 14.948 | 396 | 74.9314 | 0.288 | 497.0649 | 0.26961
5653 | 1121.8652 | 4.2034 | 104.0699 | 138.9081 | 72.957 | 17.6244 | 128.3673 | 3.6024 | 16.1976 | 62.5916 | 187.0654 | 33.7191 | 337.035 | 320.1252 | 550.7302 | 39.6587 | 112.016 | 14.9162 | 313 | 66.1792 | 0.22354 | 499.1121 | 0.28702
5654 | 1115.1256 | 4.0944 | 103.6981 | 140.0839 | 76.2642 | 14.5047 | 124.5235 | 3.6599 | 16.0047 | 66.5905 | 193.1816 | 31.2053 | 348.7776 | 320.7038 | 532.6424 | 37.3444 | 109.3699 | 14.9262 | 295 | 75.2109 | 0.19953 | 505.1557 | 0.27572
5655 | 1095.8438 | 4.4079 | 102.8742 | 167.053 | 82.8909 | 11.1671 | 116.1951 | 3.9346 | 14.0241 | 66.1195 | 193.4277 | 29.5562 | 331.0498 | 312.8706 | 519.4568 | 35.0509 | 107.3027 | 15.0018 | 287 | 65.5552 | 0.13271 | 495.8028 | 0.22781
5656 | 1054.447 | 4.1408 | 99.2171 | 141.6414 | 85.9663 | 9.0987 | 103.0948 | 3.407 | 11.6694 | 67.6879 | 189.8124 | 28.4516 | 355.191 | 291.6656 | 509.2311 | 28.8463 | 104.0334 | 14.9575 | 269 | 62.6109 | 0.14635 | 453.6102 | 0.23075
5657 | 1008.4832 | 3.3635 | 93.9624 | 118.3391 | 80.4442 | 8.4998 | 91.7908 | 2.4494 | 13.0155 | 57.4822 | 178.6041 | 27.2364 | 261.6615 | 253.6901 | 467.612 | 16.5824 | 97.7109 | 15.2766 | 242 | 55.5528 | 0.10986 | 390.9539 | 0.17958
5658 | 978.9445 | 2.4442 | 90.3409 | 105.3012 | 75.2985 | 7.7813 | 84.8188 | 1.422 | 10.5843 | 44.0373 | 152.4183 | 22.2262 | 231.9773 | 209.9074 | 398.9623 | 10.9591 | 91.2279 | 13.498 | 226 | 45.5375 | 0.089993 | 329.945 | 0.13704
5659 | 943.504 | 1.7423 | 74.3047 | 99.3452 | 72.5816 | 8.1567 | 63.5099 | 0.91883 | 7.3027 | 43.8494 | 124.8588 | 9.3608 | 329.8371 | 183.7728 | 340.3445 | 10.9585 | 86.9442 | 8.6756 | 206 | 37.2373 | 0.11603 | 279.3562 | 0.010382
5660 | 907.8813 | 2.7707 | 43.1406 | 99.3059 | 69.631 | 7.9241 | 51.3066 | 1.0391 | 5.876 | 45.7773 | 113.8512 | 4.2339 | 222.1134 | 170.6924 | 296.0572 | 11.1996 | 82.7919 | 6.3989 | 196 | 39.5483 | 0.09 | 246.146 | 0
5661 | 884.7938 | 3.6026 | 29.5321 | 102.2511 | 67.1854 | 6.9743 | 52.4236 | 1.4461 | 5.9235 | 42.9435 | 111.6448 | 5.7538 | 294.527 | 161.0417 | 277.0905 | 11.2604 | 79.7259 | 5.8054 | 183 | 31.1219 | 0.069603 | 234.445 | 0
5662 | 860.073 | 3.1046 | 28.6652 | 105.9868 | 63.3617 | 8.014 | 51.29 | 1.4515 | 6.5941 | 38.634 | 103.7703 | 7.1192 | 271.3422 | 153.4587 | 261.0038 | 11.2826 | 78.8804 | 4.3253 | 173 | 32.5862 | 0.11039 | 232.162 | 0
5663 | 846.2543 | 1.8907 | 28.0587 | 107.3485 | 59.9756 | 7.9328 | 47.3833 | 1.335 | 6.4125 | 33.244 | 91.7093 | 6.8714 | 314.965 | 141.801 | 252.3239 | 11.2317 | 78.2664 | 3.5192 | 154 | 24.1795 | 0.069692 | 231.1598 | 0
5664 | 829.0628 | 1.1264 | 27.757 | 108.2707 | 59.4029 | 6.9083 | 47.744 | 1.3273 | 6.1989 | 27.6854 | 84.9498 | 6.3744 | 210.3136 | 129.7439 | 251.8418 | 11.4407 | 77.8887 | 3.1475 | 148 | 26.3426 | 0.084366 | 232.5825 | 0
5665 | 814.3904 | 1.2655 | 27.6212 | 57.5332 | 59.2924 | 7.3243 | 49.7729 | 1.332 | 6.252 | 24.417 | 83.5973 | 6.2941 | 250.0739 | 124.0463 | 246.7598 | 11.3622 | 77.881 | 2.9598 | 138 | 25.2408 | 0.089532 | 237.5444 | 0
5666 | 803.2202 | 1.1788 | 27.3127 | 83.8972 | 56.977 | 9.0325 | 51.1437 | 1.3564 | 6.306 | 23.5534 | 83.3543 | 9.131 | 297.9297 | 122.0062 | 238.2178 | 11.5202 | 77.6168 | 2.9165 | 139 | 24.1397 | 0.090094 | 239.4684 | 0
5667 | 787.549 | 1.1326 | 28.3248 | 50.757 | 46.3257 | 9.4055 | 50.9598 | 1.5596 | 6.1965 | 25.0115 | 82.7547 | 15.456 | 270.1675 | 121.1012 | 229.9705 | 11.3988 | 77.4741 | 2.8915 | 140 | 23.2453 | 0.089161 | 237.6398 | 0
5668 | 791.2213 | 1.5132 | 47.071 | 89.7498 | 38.6086 | 9.5612 | 50.9157 | 1.4902 | 6.3965 | 31.7503 | 82.1359 | 14.6822 | 326.6784 | 119.3347 | 221.3938 | 11.0814 | 77.4844 | 2.8892 | 139 | 24.3 | 0.090314 | 241.3096 | 0
5669 | 803.6607 | 2.2987 | 27.3256 | 58.5814 | 41.8892 | 8.1169 | 45.2195 | 1.2268 | 6.202 | 37.1302 | 80.9779 | 9.4439 | 228.4331 | 117.8783 | 216.7121 | 11.087 | 76.9599 | 2.8359 | 136 | 20.219 | 0.090543 | 254.6834 | 0
5670 | 844.3424 | 2.1518 | 46.6703 | 105.5905 | 53.1648 | 8.2829 | 52.6407 | 1.0337 | 5.7624 | 35.2424 | 87.5743 | 12.0289 | 236.7285 | 135.4801 | 224.0567 | 14.675 | 76.5382 | 2.6787 | 187 | 33.5131 | 0.17425 | 281.6493 | 0.016973
5671 | 910.2628 | 2.9211 | 75.503 | 122.2767 | 60.9104 | 12.0703 | 80.2075 | 1.9986 | 7.3369 | 35.0311 | 111.9431 | 23.8474 | 304.6107 | 184.0255 | 290.6785 | 27.7527 | 79.8427 | 8.1526 | 275 | 43.3502 | 0.19598 | 333.0226 | 0.059487
5672 | 979.4442 | 3.7351 | 92.912 | 123.5708 | 61.0232 | 16.0833 | 107.3605 | 3.2167 | 14.7497 | 37.324 | 145.0875 | 29.7147 | 256.2964 | 237.7366 | 407.9313 | 36.9173 | 87.5672 | 13.1965 | 316 | 58.409 | 0.16862 | 403.3001 | 0.13532
5673 | 1051.3542 | 7.0605 | 102.0797 | 184.2939 | 58.2401 | 17.9151 | 129.6585 | 3.6514 | 19.2485 | 37.5287 | 168.9731 | 31.2481 | 250.0782 | 272.4506 | 497.6343 | 40.5311 | 96.3061 | 14.5904 | 341 | 61.1858 | 0.20144 | 467.3127 | 0.10168
5674 | 1092.265 | 9.745 | 104.4034 | 157.0665 | 55.0048 | 18.056 | 131.1148 | 3.6445 | 19.6044 | 40.5267 | 180.9091 | 34.3186 | 277.818 | 292.5147 | 564.3336 | 40.7555 | 103.5111 | 14.5198 | 358 | 65.186 | 0.1193 | 500.48 | 0.13655
5675 | 1098.6455 | 6.7615 | 104.2381 | 179.3933 | 58.0791 | 16.6247 | 136.3238 | 3.4619 | 19.2789 | 46.9252 | 188.565 | 33.6596 | 346.7104 | 304.1445 | 606.2819 | 40.8681 | 107.073 | 14.6003 | 331 | 76.6778 | 0.14409 | 507.93 | 0.10875
5676 | 1104.1483 | 3.9876 | 105.4256 | 195.3541 | 66.8166 | 15.3586 | 144.9581 | 3.3611 | 20.0191 | 51.5519 | 191.3055 | 30.8968 | 318.5026 | 313.3666 | 605.5921 | 40.7314 | 106.9741 | 14.7601 | 337 | 67.9344 | 0.1986 | 513.93 | 0.16155
5677 | 1089.2396 | 3.8113 | 142.1277 | 161.4755 | 74.5212 | 14.5339 | 142.8023 | 3.5176 | 19.6861 | 52.5971 | 190.7333 | 34.8833 | 252.6256 | 328.3158 | 593.6785 | 40.5397 | 106.672 | 14.9335 | 291 | 54.9625 | 0.11979 | 516.5875 | 0.23498
5678 | 1071.4551 | 3.7573 | 105.7033 | 142.8832 | 75.8428 | 17.0591 | 136.6498 | 4.1409 | 16.9901 | 54.5245 | 192.1584 | 34.6377 | 352.0802 | 336.7937 | 576.9672 | 38.1787 | 106.8364 | 15.3116 | 286 | 70.071 | 0.14293 | 509.7955 | 0.15015
5679 | 1059.6944 | 3.8667 | 78.6223 | 141.1309 | 78.7316 | 15.1325 | 127.0582 | 4.1254 | 14.5164 | 58.7496 | 198.2472 | 29.4944 | 256.8982 | 323.8898 | 555.253 | 35.0508 | 105.7811 | 15.4208 | 275 | 67.96 | 0.19927 | 500.3033 | 0.19991
5680 | 1029.7247 | 3.2565 | 94.0782 | 136.3998 | 81.7204 | 11.5312 | 116.4315 | 3.6144 | 13.8539 | 59.6777 | 198.857 | 25.9995 | 183.9829 | 293.3953 | 513.9741 | 28.8887 | 102.8511 | 15.2988 | 282 | 57.2749 | 0.11959 | 466.8277 | 0.15829
5681 | 987.3422 | 2.7285 | 95.4935 | 122.8422 | 79.7668 | 8.3995 | 108.2969 | 2.6454 | 11.0285 | 59.362 | 180.1535 | 26.0865 | 203.0479 | 247.5445 | 436.9376 | 16.7172 | 97.4877 | 15.7154 | 243 | 53.9248 | 0.14502 | 406.4694 | 0.11348
5682 | 933.3174 | 2.3316 | 91.0085 | 107.5534 | 74.6203 | 8.2068 | 88.2901 | 1.5186 | 7.2386 | 59.3276 | 147.8351 | 21.2554 | 318.5269 | 196.9349 | 372.0203 | 10.3241 | 91.7036 | 13.7085 | 230 | 46.1068 | 0.19739 | 341.6445 | 0.054012
5683 | 895.1887 | 2.2341 | 77.7228 | 123.2592 | 72.6621 | 9.3154 | 63.762 | 1.279 | 5.6163 | 57.5778 | 120.2525 | 9.9061 | 275.9012 | 163.3739 | 344.577 | 10.0933 | 86.5715 | 8.881 | 207 | 42.4948 | 0.11992 | 278.48 | 0.013229
5684 | 868.3724 | 3.1343 | 45.4473 | 109.1904 | 71.0258 | 10.1152 | 54.3931 | 1.2614 | 5.6454 | 52.0679 | 108.987 | 5.7535 | 211.1522 | 146.9333 | 329.1948 | 10.1906 | 81.7558 | 6.3959 | 186 | 32.9682 | 0.14358 | 235.1083 | 0
5685 | 852.6266 | 3.5897 | 30.8037 | 85.9954 | 69.0956 | 8.3532 | 54.6109 | 1.2643 | 6.3767 | 37.619 | 107.2473 | 6.8118 | 233.1757 | 139.2016 | 301.3876 | 10.1862 | 78.9878 | 5.8362 | 184 | 38.5394 | 0.15274 | 221.8404 | 0
5686 | 827.8665 | 2.7482 | 29.7646 | 96.9224 | 65.7566 | 9.0009 | 55.4423 | 1.2991 | 6.947 | 23.2597 | 100.5804 | 7.0357 | 325.7264 | 135.6061 | 283.468 | 10.0593 | 77.6149 | 5.5562 | 165 | 36.0685 | 0.1535 | 220.1652 | 0
5687 | 806.4539 | 1.6687 | 28.9514 | 95.6799 | 65.6224 | 8.0342 | 55.7088 | 1.5203 | 6.547 | 17.7759 | 89.3337 | 6.6865 | 248.433 | 128.6041 | 267.81 | 10.0018 | 76.3449 | 4.9651 | 149 | 38.7638 | 0.15269 | 218.0551 | 0
5688 | 796.2545 | 1.2417 | 28.2761 | 103.2918 | 64.8679 | 8.4089 | 56.0007 | 1.4865 | 6.7431 | 15.4857 | 83.5927 | 6.3495 | 252.7488 | 115.4862 | 260.5903 | 9.8736 | 75.8702 | 4.5222 | 147 | 36.0176 | 0.15596 | 219.9041 | 0
5689 | 791.3243 | 1.2215 | 27.9268 | 96.6943 | 64.4965 | 7.908 | 55.5972 | 1.3416 | 6.6561 | 13.9133 | 81.8789 | 6.0991 | 216.7405 | 104.0169 | 269.446 | 10.1012 | 75.9142 | 4.4625 | 145 | 34.5345 | 0.1554 | 220.6678 | 0
5690 | 779.203 | 1.2465 | 27.3872 | 93.3253 | 63.4381 | 7.5822 | 55.1011 | 1.3333 | 6.1917 | 13.5183 | 79.2569 | 8.9333 | 248.8718 | 100.6494 | 274.566 | 10.1132 | 76.0111 | 4.4406 | 143 | 33.9263 | 0.1541 | 221.0083 | 0
5691 | 774.6467 | 1.1341 | 28.266 | 93.1452 | 61.3058 | 8.3185 | 55.1305 | 1.3287 | 6.1905 | 15.133 | 76.2172 | 14.6675 | 268.6824 | 99.4968 | 259.9075 | 10.8009 | 75.8041 | 4.2881 | 144 | 29.5799 | 0.15423 | 223.8233 | 0
5692 | 778.5107 | 1.482 | 31.601 | 97.2813 | 60.2251 | 7.7914 | 52.6331 | 1.3326 | 6.42 | 22.1227 | 74.2576 | 14.5493 | 264.7193 | 96.8254 | 239.8562 | 11.9953 | 75.1571 | 4.0604 | 145 | 32.1451 | 0.15256 | 224.1009 | 0
5693 | 796.3778 | 2.839 | 40.5464 | 97.7899 | 58.4899 | 8.2664 | 51.6572 | 1.1958 | 6.2088 | 28.3848 | 73.4042 | 9.785 | 195.5154 | 98.0444 | 235.8322 | 10.7784 | 74.3976 | 3.6344 | 151 | 24.2625 | 0.12969 | 233.5143 | 0
5694 | 845.2245 | 3.2802 | 93.8186 | 100.8051 | 53.6825 | 12.0891 | 59.7606 | 1.3636 | 5.8127 | 27.5214 | 82.4503 | 15.0591 | 272.8656 | 122.3532 | 243.8534 | 13.3952 | 74.165 | 3.3623 | 193 | 33.1555 | 0.21187 | 264.5311 | 0.02614
5695 | 903.6464 | 3.5485 | 57.6347 | 105.6316 | 52.2363 | 15.4224 | 88.552 | 2.0579 | 7.305 | 32.7353 | 108.5093 | 25.0692 | 303.0914 | 178.5046 | 292.9172 | 25.8389 | 77.0008 | 8.3184 | 243 | 60.2602 | 0.25774 | 321.0528 | 0.064683
5696 | 981.7108 | 3.6833 | 86.2817 | 120.3178 | 56.2856 | 16.3128 | 120.9402 | 2.794 | 10.403 | 45.7801 | 137.9425 | 26.1853 | 256.3186 | 234.3923 | 381.9473 | 32.9026 | 84.1983 | 12.2082 | 312 | 69.3399 | 0.22643 | 395.3249 | 0.14564
5697 | 1060.0967 | 6.1892 | 104.8683 | 133.8923 | 62.918 | 15.248 | 138.5153 | 3.0782 | 12.5342 | 51.6721 | 157.602 | 24.3798 | 297.5769 | 267.9184 | 446.1008 | 37.2598 | 92.536 | 12.7876 | 344 | 73.7901 | 0.38454 | 452.7759 | 0.18081
5698 | 1106.228 | 11.1851 | 102.9092 | 130.196 | 78.2789 | 13.9269 | 161.2901 | 3.2771 | 10.7261 | 54.3422 | 172.3534 | 24.8623 | 341.6925 | 287.2812 | 494.4549 | 40.0853 | 99.0156 | 13.8593 | 356 | 84.5837 | 0.25319 | 478.8143 | 0.23141
5699 | 1115.1377 | 10.9272 | 104.0821 | 189.3112 | 90.2422 | 15.3202 | 167.2547 | 3.2917 | 12.6898 | 58.8709 | 188.5003 | 25.2241 | 373.5767 | 297.24 | 522.522 | 38.6801 | 103.6657 | 13.7424 | 362 | 81.9886 | 0.38423 | 491.1117 | 0.21997
5700 | 1131.3565 | 6.4043 | 104.6945 | 180.4594 | 91.1427 | 16.2255 | 170.4569 | 3.5748 | 13.8521 | 58.8002 | 193.1641 | 26.5209 | 266.6849 | 303.9791 | 520.3518 | 38.2056 | 105.9769 | 13.4821 | 372 | 73.8108 | 0.27019 | 497.5767 | 0.28796
5701 | 1127.2625 | 3.6593 | 104.9668 | 179.2841 | 88.1199 | 17.4921 | 171.8453 | 3.5647 | 13.8665 | 54.5712 | 186.8114 | 29.3299 | 425.5644 | 314.4867 | 523.2536 | 38.8048 | 105.6127 | 13.8903 | 330 | 76.7393 | 0.18339 | 506.384 | 0.21336
5702 | 1123.6547 | 3.8486 | 108.0789 | 182.7509 | 87.9425 | 14.6481 | 157.3554 | 3.1567 | 13.7728 | 46.6131 | 186.3233 | 31.5095 | 210.4631 | 320.8454 | 530.3232 | 37.1801 | 104.4304 | 13.8055 | 307 | 77.7724 | 0.126 | 512.7843 | 0.20937
5703 | 1101.8953 | 4.3212 | 104.6001 | 149.909 | 86.787 | 16.0539 | 143.7131 | 3.0536 | 12.7304 | 37.5467 | 190.224 | 33.4434 | 283.8073 | 309.6313 | 525.4947 | 34.9867 | 104.1 | 14.0505 | 302 | 69.8926 | 0.097276 | 500.5276 | 0.19101
5704 | 1060.7149 | 3.6469 | 98.7884 | 182.3481 | 90.7466 | 13.5294 | 131.4875 | 2.7721 | 9.7894 | 34.2107 | 191.0031 | 31.0961 | 332.1535 | 281.9544 | 495.4036 | 28.0303 | 102.4394 | 14.3433 | 260 | 69.3725 | 0.11747 | 464.4587 | 0.16497
5705 | 1008.8564 | 2.7791 | 94.81 | 151.7823 | 93.5106 | 10.7772 | 119.1151 | 2.0377 | 11.4875 | 33.7367 | 181.4063 | 27.9149 | 282.9839 | 232.5424 | 441.4707 | 15.7305 | 96.3325 | 14.1183 | 230 | 57.9577 | 0.16325 | 398.0265 | 0.13534
5706 | 972.0777 | 2.1839 | 92.2923 | 100.5464 | 92.9216 | 9.194 | 100.9532 | 1.7885 | 13.0871 | 34.3584 | 156.5274 | 23.5536 | 265.0256 | 181.9192 | 394.6737 | 9.9322 | 90.8316 | 11.6208 | 237 | 56.129 | 0.098203 | 323.9517 | 0.075964
5707 | 938.3033 | 1.8775 | 79.9192 | 127.1439 | 86.4874 | 8.6113 | 70.1557 | 1.6926 | 11.467 | 40.6283 | 126.5077 | 10.3174 | 273.0958 | 150.54 | 358.5997 | 9.4399 | 88.3041 | 6.9397 | 208 | 53.9405 | 0.15379 | 269.4666 | 0.0057336
5708 | 885.0849 | 2.6554 | 60.3141 | 83.5157 | 78.2924 | 7.8305 | 56.1057 | 1.7968 | 7.1003 | 43.999 | 109.5451 | 8.5815 | 260.9111 | 129.5899 | 316.6626 | 9.5089 | 83.9273 | 5.1586 | 190 | 58.4511 | 0.098076 | 242.5583 | 0
5709 | 865.3803 | 3.0608 | 25.5378 | 65.221 | 76.2979 | 7.492 | 55.1011 | 2.0697 | 6.1311 | 33.7552 | 105.5178 | 11.3364 | 294.5673 | 118.8819 | 276.6712 | 10.0108 | 78.8009 | 4.8104 | 180 | 58.8809 | 0.15392 | 244.4059 | 0
5710 | 840.3416 | 2.3763 | 29.6875 | 62.0569 | 76.238 | 8.358 | 54.6414 | 2.0968 | 6.6405 | 21.2705 | 98.7915 | 12.3816 | 186.0849 | 115.9397 | 257.7803 | 9.4807 | 76.0788 | 4.3516 | 162 | 56.6525 | 0.09759 | 254.1393 | 0
5711 | 799.9553 | 1.3567 | 31.7936 | 61.8069 | 74.644 | 7.8177 | 54.2593 | 2.0816 | 6.3045 | 17.1521 | 90.3287 | 10.287 | 215.5632 | 115.6743 | 253.102 | 9.1929 | 75.4463 | 4.0597 | 155 | 57.7058 | 0.2259 | 255.777 | 0
5712 | 792.1422 | 0.99365 | 31.4371 | 43.8916 | 73.635 | 7.6332 | 54.6472 | 2.2966 | 6.4043 | 16.3262 | 88.2984 | 12.6615 | 255.5077 | 113.7717 | 256.1248 | 9.5723 | 75.296 | 3.6124 | 150 | 54.4504 | 0.15284 | 248.6453 | 0
5713 | 794.2737 | 1.0013 | 30.8861 | 83.2941 | 72.8931 | 8.3313 | 54.2069 | 2.0482 | 6.5267 | 15.561 | 88.2813 | 14.0204 | 225.0268 | 105.9906 | 259.7605 | 12.0019 | 74.7898 | 3.3985 | 145 | 55.1654 | 0.1846 | 234.4008 | 0
5714 | 789.1913 | 1.2854 | 30.3345 | 71.588 | 72.8825 | 7.8175 | 53.8403 | 1.5006 | 6.3793 | 15.2266 | 87.0731 | 13.2483 | 259.863 | 96.5118 | 254.7287 | 13.5183 | 74.4202 | 3.3319 | 144 | 59.5182 | 0.19725 | 223.3512 | 0
5715 | 778.0545 | 1.4491 | 29.7621 | 65.1344 | 71.86 | 7.5643 | 52.2147 | 1.325 | 6.3962 | 17.0592 | 86.2263 | 18.5619 | 323.5313 | 92.4176 | 251.4825 | 13.7089 | 74.2759 | 2.9415 | 140 | 53.6907 | 0.19672 | 220.0985 | 0
5716 | 774.3114 | 1.6916 | 59.4744 | 64.2827 | 72.1166 | 7.6375 | 49.8257 | 1.3149 | 6.3586 | 24.095 | 86.4129 | 17.978 | 173.4417 | 91.687 | 247.4512 | 12.7532 | 74.1083 | 2.7535 | 136 | 57.5768 | 0.19792 | 225.2063 | 0
5717 | 793.3084 | 2.5586 | 48.6933 | 76.0387 | 73.0352 | 7.5805 | 51.5696 | 1.2074 | 6.2056 | 29.4135 | 86.4789 | 12.037 | 196.1509 | 93.5113 | 244.733 | 10.1624 | 73.8927 | 2.6623 | 125 | 55.2106 | 0.25566 | 239.5181 | 0
5718 | 832.7263 | 2.5095 | 35.8405 | 74.3949 | 68.7693 | 11.8262 | 59.748 | 1.0673 | 5.7366 | 29.9395 | 96.2451 | 13.1279 | 221.5655 | 115.8458 | 244.4924 | 12.3886 | 74.0283 | 2.5039 | 188 | 70.832 | 0.15271 | 268.3532 | 0.095786
5719 | 896.9088 | 3.1612 | 70.5243 | 140.9977 | 67.9921 | 14.7581 | 91.6333 | 1.9184 | 9.1531 | 32.5105 | 122.3435 | 20.7364 | 215.5269 | 170.7241 | 283.5226 | 25.3712 | 76.8349 | 7.728 | 230 | 81.5605 | 0.18463 | 320.8729 | 0.145
5720 | 955.4731 | 5.3969 | 96.4016 | 133.6288 | 70.2331 | 16.5326 | 126.7591 | 3.4776 | 14.0802 | 35.0258 | 150.5088 | 28.2333 | 281.3662 | 231.9547 | 380.8129 | 34.3589 | 82.249 | 12.1729 | 292 | 77.7844 | 0.19715 | 390.771 | 0.21635
5721 | 997.4924 | 8.9389 | 103.11 | 182.2069 | 76.5836 | 18.4278 | 149.7615 | 3.9767 | 15.002 | 36.6871 | 169.4138 | 29.893 | 322.5451 | 272.3928 | 473.9466 | 38.6771 | 83.5365 | 13.5518 | 340 | 76.4192 | 0.25551 | 446.8214 | 0.31005
5722 | 1023.8707 | 10.5739 | 107.7961 | 149.9852 | 85.5841 | 18.3255 | 165.0489 | 3.6207 | 14.238 | 37.5226 | 177.816 | 29.8189 | 299.0378 | 297.8484 | 522.5433 | 40.0403 | 81.4187 | 14.1371 | 343 | 76.0118 | 0.15212 | 475.3151 | 0.28595
5723 | 1038.0944 | 6.901 | 111.8474 | 131.2735 | 88.802 | 17.3913 | 166.9257 | 3.5989 | 13.4928 | 37.8052 | 179.8549 | 26.8615 | 322.2309 | 309.9223 | 524.8354 | 38.0401 | 81.6936 | 14.1499 | 320 | 79.5536 | 0.26325 | 495.4624 | 0.26399
5724 | 1035.2855 | 4.6846 | 112.6724 | 131.6126 | 85.2391 | 18.5966 | 168.142 | 3.6686 | 13.394 | 38.6035 | 182.1546 | 25.3164 | 376.9333 | 303.5776 | 512.3497 | 37.7107 | 80.5908 | 14.3216 | 312 | 74.8608 | 0.29838 | 497.3566 | 0.27479
5725 | 1030.8262 | 8.2097 | 109.3325 | 135.331 | 82.2394 | 19.0088 | 164.1467 | 3.4884 | 13.7792 | 37.395 | 184.7723 | 24.9784 | 350.5118 | 294.8091 | 508.4226 | 39.2758 | 78.7573 | 14.7948 | 312 | 68.066 | 0.31141 | 495.9118 | 0.18729
5726 | 1032.6944 | 9.0342 | 111.5167 | 137.4937 | 82.3316 | 18.7769 | 165.3163 | 3.5941 | 14.8146 | 34.5855 | 183.0879 | 23.8557 | 325.4736 | 292.7502 | 510.5031 | 37.8616 | 79.1604 | 14.8136 | 293 | 71.7393 | 0.26005 | 493.9152 | 0.13853
5727 | 1035.8948 | 5.6505 | 111.8996 | 173.652 | 86.7968 | 17.0826 | 156.4676 | 3.6391 | 14.6475 | 31.5789 | 178.2039 | 22.7405 | 373.8226 | 280.5085 | 507.9479 | 34.2826 | 77.7904 | 14.8201 | 284 | 68.8491 | 0.14312 | 470.4309 | 0.17819
5728 | 994.2744 | 3.2459 | 109.4953 | 190.7737 | 91.5991 | 12.6685 | 130.1061 | 2.8445 | 14.2596 | 30.4075 | 172.9747 | 21.5325 | 351.876 | 245.6509 | 482.5536 | 21.0996 | 74.7274 | 14.822 | 258 | 57.0705 | 0.10756 | 425.9849 | 0.16154
5729 | 914.1628 | 2.2866 | 89.3529 | 164.8664 | 85.0565 | 7.7816 | 109.4119 | 1.6177 | 14.949 | 30.1104 | 161.2322 | 22.2922 | 189.3697 | 192.0363 | 417.8636 | 11.3125 | 70.6845 | 14.3171 | 240 | 58.3638 | 0.094659 | 354.2223 | 0.12976
5730 | 888.1932 | 1.7909 | 53.9527 | 115.2608 | 77.9781 | 5.9517 | 88.942 | 1.0012 | 14.4646 | 31.2658 | 134.6746 | 20.0435 | 346.1078 | 146.0021 | 356.9296 | 9.4278 | 64.4931 | 11.8302 | 235 | 45.319 | 0.090875 | 284.177 | 0.089841
5731 | 868.4081 | 1.8649 | 38.2475 | 92.5655 | 76.6316 | 6.4373 | 65.3057 | 0.89028 | 9.2063 | 39.7136 | 105.2888 | 9.3951 | 130.7022 | 127.7895 | 324.4399 | 9.2135 | 57.1254 | 7.0353 | 209 | 48.0652 | 0.091748 | 242.9788 | 0.030957
5732 | 827.3734 | 3.3008 | 35.8883 | 70.1187 | 75.1542 | 6.7099 | 56.4536 | 1.0887 | 6.0839 | 46.3823 | 88.4605 | 6.3203 | 194.3612 | 127.2465 | 303.1089 | 9.2923 | 51.5966 | 5.0903 | 213 | 48.2609 | 0.091414 | 226.8973 | 0
5733 | 805.293 | 3.9412 | 34.1918 | 100.4803 | 71.1962 | 7.3349 | 56.6656 | 1.4726 | 6.8344 | 37.3847 | 81.5926 | 6.8923 | 265.9403 | 127.2056 | 300.6499 | 9.7029 | 49.7399 | 5.0591 | 200 | 46.551 | 0.11692 | 226.4646 | 0
5734 | 792.7437 | 2.8686 | 32.9442 | 90.9668 | 66.2396 | 9.0131 | 56.916 | 1.4293 | 7.2241 | 22.7511 | 79.6416 | 7.0422 | 222.1799 | 120.6607 | 287.2154 | 9.5986 | 50.0129 | 4.7678 | 180 | 51.8221 | 0.07068 | 228.1594 | 0
5735 | 777.7741 | 1.8128 | 32.2399 | 83.6483 | 65.4248 | 8.0793 | 56.7751 | 1.3043 | 6.7834 | 15.7543 | 78.1661 | 7.4777 | 238.2706 | 114.9624 | 278.0203 | 10.4361 | 51.4509 | 4.1513 | 163 | 49.5511 | 0.08455 | 223.6225 | 0
5736 | 772.7583 | 1.4938 | 32.3014 | 86.9645 | 65.1182 | 7.5279 | 56.9251 | 1.3156 | 6.6031 | 14.6644 | 75.1864 | 7.0026 | 247.6463 | 113.7565 | 282.0313 | 12.6543 | 52.89 | 3.7606 | 153 | 44.9361 | 0.11777 | 219.0293 | 0
5737 | 761.1184 | 1.4564 | 32.3019 | 71.5654 | 60.4719 | 8.2803 | 56.8888 | 1.3088 | 6.514 | 15.1522 | 72.316 | 6.1978 | 311.682 | 108.7792 | 283.1771 | 13.7868 | 51.8848 | 3.4799 | 152 | 46.8978 | 0.070015 | 218.11 | 0
5738 | 760.7573 | 1.3776 | 31.2295 | 101.534 | 60.6014 | 7.8849 | 56.3301 | 1.4165 | 6.1252 | 15.1476 | 70.0492 | 5.9415 | 226.4022 | 100.3418 | 277.3296 | 13.8042 | 50.1633 | 3.2933 | 147 | 40.9983 | 0.11198 | 217.2655 | 0
5739 | 756.1392 | 1.3734 | 30.1774 | 92.2284 | 62.6075 | 8.3082 | 53.4214 | 1.4901 | 6.3157 | 16.5063 | 69.0541 | 6.2593 | 212.54 | 97.2573 | 270.1422 | 13.5152 | 49.1951 | 3.2311 | 139 | 44.8463 | 0.070346 | 213.5319 | 0
5740 | 746.7413 | 1.7328 | 30.0405 | 88.0298 | 62.3202 | 7.1631 | 54.3645 | 1.3717 | 6.3576 | 23.7572 | 69.1755 | 6.038 | 306.336 | 99.1147 | 268.4126 | 11.212 | 49.6935 | 3.3742 | 140 | 40.5456 | 0.084122 | 208.8804 | 0
5741 | 753.8795 | 2.5386 | 29.7677 | 83.818 | 60.1328 | 7.402 | 53.4092 | 1.1977 | 6.26 | 29.7562 | 68.3294 | 5.3122 | 219.0714 | 98.8865 | 262.4406 | 9.2933 | 52.0087 | 3.5362 | 136 | 44.2473 | 0.090453 | 206.6448 | 0
5742 | 765.3731 | 2.2038 | 39.5501 | 87.797 | 58.4813 | 7.5709 | 52.2672 | 0.97598 | 5.987 | 24.7628 | 65.9364 | 4.188 | 161.0672 | 92.7981 | 251.3834 | 9.1614 | 52.748 | 3.4195 | 135 | 42.0752 | 0.089849 | 203.474 | 0.038346
5743 | 786.0966 | 1.4464 | 52.8464 | 98.9092 | 47.4182 | 7.617 | 53.2122 | 0.87997 | 5.6994 | 16.7913 | 66.954 | 6.0028 | 183.086 | 86.8302 | 246.2381 | 9.0505 | 52.186 | 3.5519 | 139 | 55.1712 | 0.14028 | 202.3647 | 0.059605
5744 | 797.8751 | 0.89783 | 62.163 | 108.0847 | 40.0363 | 7.5498 | 53.941 | 0.94611 | 5.3893 | 14.0397 | 81.9091 | 11.945 | 215.6562 | 85.6737 | 238.9409 | 8.859 | 52.4005 | 3.8126 | 140 | 66.9599 | 0.13836 | 205.2887 | 0.14723
5745 | 807.9534 | 1.0299 | 81.4393 | 117.7489 | 41.0296 | 8.3425 | 54.2558 | 1.0235 | 5.4072 | 15.1151 | 107.8036 | 14.2723 | 261.5008 | 89.7705 | 245.9759 | 8.8499 | 52.9687 | 5.839 | 148 | 67.3303 | 0.11581 | 208.1783 | 0.18653
5746 | 834.41 | 1.6758 | 43.5534 | 120.2772 | 43.975 | 8.526 | 54.9186 | 1.0968 | 7.2285 | 20.054 | 124.1428 | 14.379 | 243.8957 | 105.8702 | 255.5198 | 9.3124 | 53.0142 | 10.8594 | 154 | 63.4902 | 0.13777 | 212.4427 | 0.25262
5747 | 829.391 | 1.9924 | 53.2445 | 104.9085 | 51.8343 | 7.8657 | 54.8527 | 0.95583 | 11.589 | 25.8935 | 116.6736 | 14.768 | 196.7919 | 122.0576 | 250.199 | 9.4915 | 50.6781 | 13.3884 | 159 | 60.6842 | 0.082615 | 217.9932 | 0.25792
5748 | 825.8548 | 2.1374 | 58.7259 | 97.787 | 61.4706 | 9.0949 | 55.0831 | 0.85223 | 13.3845 | 28.4278 | 98.8634 | 17.6414 | 218.3101 | 125.9443 | 239.0896 | 9.2054 | 47.3096 | 13.9537 | 151 | 49.0256 | 0.099464 | 226.8912 | 0.27948
5749 | 832.7166 | 2.254 | 58.4746 | 97.1492 | 67.6587 | 8.7489 | 54.7234 | 0.84817 | 13.4411 | 28.6143 | 92.2562 | 18.8551 | 251.3535 | 128.6071 | 253.9812 | 9.0843 | 46.0014 | 14.039 | 153 | 49.9777 | 0.10526 | 236.8839 | 0.29014
5750 | 827.8773 | 2.2739 | 57.1031 | 97.3295 | 68.7013 | 9.7825 | 53.9769 | 0.84327 | 13.6216 | 28.9925 | 94.9652 | 17.5063 | 206.9541 | 130.3818 | 275.9113 | 8.9697 | 46.3649 | 13.9884 | 160 | 52.3198 | 0.10437 | 237.8296 | 0.29356
5751 | 826.9272 | 1.7323 | 58.5838 | 97.1145 | 73.6136 | 7.7315 | 55.0578 | 0.82751 | 11.7506 | 28.1454 | 98.6388 | 15.7045 | 249.7057 | 123.9658 | 280.7793 | 8.8756 | 48.5549 | 13.7624 | 165 | 52.8552 | 0.13828 | 239.6431 | 0.2869
5752 | 821.2875 | 1.3767 | 59.6249 | 98.1152 | 75.3696 | 6.6801 | 56.4864 | 0.83351 | 7.9986 | 23.5944 | 100.2516 | 10.7258 | 241.2346 | 119.8933 | 277.6071 | 9.0499 | 50.8777 | 13.4919 | 168 | 52.47 | 0.106 | 243.3832 | 0.23824
5753 | 811.8173 | 1.2534 | 79.0294 | 98.1163 | 74.6551 | 6.65 | 54.9673 | 1.0306 | 6.0876 | 20.7426 | 97.4789 | 8.4408 | 195.4917 | 124.9996 | 280.5669 | 8.915 | 49.6453 | 11.4784 | 170 | 48.1954 | 0.081941 | 233.3273 | 0.22186
5754 | 807.7082 | 1.1917 | 43.2939 | 95.8586 | 75.6334 | 6.6272 | 53.5887 | 1.067 | 5.47 | 23.2449 | 89.4985 | 6.9585 | 215.0552 | 124.6594 | 282.1257 | 8.7542 | 48.4405 | 7.2145 | 168 | 51.5251 | 0.098976 | 222.7873 | 0.15842
5755 | 791.4373 | 1.7961 | 41.5699 | 95.8885 | 74.6975 | 7.3022 | 53.6873 | 0.92251 | 5.3265 | 29.2186 | 80.528 | 4.786 | 234.3674 | 110.8257 | 283.4497 | 8.7862 | 50.2233 | 4.8004 | 177 | 51.2564 | 0.10517 | 218.4543 | 0.046116
5756 | 782.9548 | 3.0022 | 40.1364 | 97.7193 | 71.4589 | 6.9863 | 55.1725 | 1.0859 | 5.7261 | 32.4985 | 76.5549 | 5.3364 | 231.8739 | 96.461 | 280.6834 | 9.418 | 51.3717 | 4.1628 | 217 | 49.7324 | 0.095714 | 215.545 | 0
5757 | 776.2449 | 3.2544 | 39.8091 | 99.4053 | 66.261 | 8.055 | 56.3911 | 1.2558 | 5.9115 | 26.6885 | 75.872 | 8.3984 | 194.2055 | 95.3021 | 271.865 | 9.3554 | 51.5819 | 3.7713 | 227 | 51.8324 | 0.090104 | 226.137 | 0
5758 | 764.8637 | 3.0359 | 39.4709 | 99.7821 | 62.7992 | 7.8306 | 56.4916 | 1.2974 | 6.2191 | 18.6329 | 73.9949 | 10.4257 | 262.2857 | 99.3446 | 276.5483 | 9.057 | 52.0256 | 4.0759 | 226 | 47.9715 | 0.089911 | 245.1465 | 0
5759 | 746.8373 | 1.9923 | 39.0154 | 99.8096 | 52.4275 | 8.2483 | 54.8616 | 1.3039 | 6.1955 | 14.9185 | 71.5494 | 11.1011 | 157.1905 | 106.7521 | 281.7734 | 9.4115 | 52.6767 | 4.2205 | 222 | 49.308 | 0.089589 | 248.6006 | 0
5760 | 747.8076 | 1.2286 | 38.6987 | 87.3508 | 42.7641 | 7.8223 | 53.98 | 1.3238 | 6.4474 | 13.6159 | 70.2722 | 9.8946 | 205.0196 | 132.2793 | 272.4735 | 9.4247 | 53.4454 | 3.7966 | 222 | 47.358 | 0.089431 | 237.9858 | 0
5761 | 750.8107 | 1.4906 | 38.3183 | 110.0667 | 51.0175 | 7.656 | 50.8678 | 1.5777 | 7.631 | 13.1114 | 69.7558 | 6.9985 | 283.2278 | 159.2462 | 257.9137 | 9.3696 | 53.4645 | 3.3822 | 209 | 47.522 | 0.091167 | 226.076 | 0
5762 | 733.9365 | 1.6111 | 37.7924 | 102.9465 | 60.7414 | 7.6715 | 53.1237 | 1.5156 | 8.0617 | 12.8817 | 69.1829 | 5.6899 | 184.0406 | 168.6268 | 245.4383 | 9.3839 | 50.8169 | 3.3434 | 197 | 49.0879 | 0.090631 | 218.2939 | 0
5763 | 729.912 | 1.4657 | 38.9685 | 101.6516 | 57.6568 | 8.2084 | 55.1247 | 1.3215 | 6.8078 | 13.4082 | 68.6992 | 5.913 | 186.152 | 168.9221 | 233.8565 | 9.6898 | 47.1151 | 2.9963 | 181 | 45.4715 | 0.088647 | 222.6111 | 0
5764 | 731.2669 | 1.9625 | 38.8833 | 101.0711 | 53.6971 | 9.3478 | 54.9968 | 1.3243 | 6.0958 | 15.6416 | 68.6361 | 5.8417 | 264.4468 | 167.1335 | 234.3092 | 9.4041 | 45.8084 | 3.0321 | 163 | 44.1258 | 0.090657 | 226.5675 | 0
5765 | 742.5402 | 2.9965 | 37.5922 | 99.3428 | 54.7459 | 8.0485 | 55.5282 | 1.3228 | 5.9562 | 17.4994 | 68.1745 | 5.7592 | 247.1266 | 156.9058 | 236.16 | 9.2667 | 45.7475 | 3.2008 | 138 | 46.1861 | 0.090009 | 215.7584 | 0
5766 | 753.0545 | 3.1285 | 36.9991 | 83.6758 | 54.5356 | 8.2665 | 54.7759 | 1.1032 | 5.7275 | 16.2954 | 66.1906 | 4.3828 | 187.5206 | 126.0471 | 234.9351 | 9.0786 | 45.0497 | 3.3704 | 137 | 43.184 | 0.089375 | 200.7298 | 0.011051
5767 | 768.0915 | 2.2978 | 36.7554 | 105.0585 | 53.4572 | 9.2315 | 54.3157 | 0.93032 | 5.305 | 14.1579 | 64.3932 | 3.434 | 251.39 | 96.7807 | 233.2397 | 8.8588 | 44.3596 | 3.5029 | 135 | 41.677 | 0.089875 | 194.0644 | 0.021376
5768 | 777.9818 | 1.1918 | 36.7761 | 98.5738 | 53.2695 | 9.4944 | 54.2363 | 1.1358 | 4.961 | 13.8819 | 64.4001 | 3.5203 | 187.9212 | 89.7535 | 229.3878 | 8.9529 | 44.2592 | 3.6455 | 132 | 43.1368 | 0.11679 | 193.2389 | 0.038747
5769 | 793.5023 | 0.96593 | 36.6391 | 95.5223 | 53.3229 | 9.5786 | 49.1676 | 1.2325 | 5.0889 | 15.8048 | 65.2877 | 3.39 | 257.3529 | 93.8053 | 226.1743 | 8.9765 | 44.5229 | 5.6507 | 168 | 42.9625 | 0.09 | 196.7223 | 0.069491
5770 | 818.5172 | 0.95895 | 36.6042 | 82.6036 | 54.1679 | 8.7314 | 50.4691 | 1.4187 | 6.8356 | 19.8046 | 74.1741 | 3.3272 | 192.3617 | 101.1911 | 214.0184 | 9.0867 | 45.4287 | 10.4724 | 175 | 39.1011 | 0.09 | 205.8872 | 0.12559
5771 | 820.231 | 0.87216 | 36.7406 | 105.4112 | 55.7527 | 7.8868 | 53.5423 | 1.8002 | 6.0516 | 24.7438 | 93.077 | 3.379 | 195.4525 | 104.1315 | 222.1488 | 8.8533 | 46.8485 | 12.7505 | 169 | 48.5572 | 0.069424 | 212.0739 | 0.10147
5772 | 816.6362 | 1.2343 | 36.8228 | 100.062 | 58.1157 | 6.9133 | 54.7773 | 1.9631 | 6.0179 | 29.5895 | 100.5941 | 7.1093 | 163.0196 | 104.2754 | 237.016 | 8.9455 | 47.5333 | 13.5875 | 198 | 46.7316 | 0.08445 | 213.7183 | 0.14172
5773 | 798.7882 | 1.3561 | 36.2908 | 99.2368 | 58.9079 | 8.0714 | 55.7854 | 1.5501 | 10.993 | 31.8942 | 94.0817 | 12.4395 | 266.7583 | 107.5952 | 243.9003 | 8.8947 | 47.6488 | 14.2654 | 187 | 43.9997 | 0.090101 | 213.6006 | 0.1008
5774 | 800.8633 | 1.597 | 35.2298 | 99.4333 | 58.6675 | 8.5524 | 55.2806 | 1.0356 | 11.0645 | 29.7471 | 91.3081 | 12.331 | 176.3697 | 114.9821 | 250.4517 | 8.7577 | 48.3016 | 14.6208 | 189 | 49.272 | 0.089985 | 214.268 | 0.025693
5775 | 817.904 | 1.6463 | 34.9068 | 97.5932 | 58.0269 | 7.0598 | 54.7317 | 0.92934 | 10.235 | 25.7346 | 91.1352 | 9.1624 | 208.377 | 121.1183 | 258.1469 | 8.7139 | 49.2125 | 14.9099 | 184 | 46.4423 | 0.089643 | 217.8962 | 0.032589
5776 | 826.6921 | 1.7161 | 35.0859 | 96.6682 | 56.1932 | 7.3472 | 54.8183 | 0.92717 | 7.0805 | 21.3462 | 89.2228 | 6.9241 | 197.244 | 120.7109 | 270.2063 | 8.8507 | 49.0078 | 15.2787 | 192 | 49.8508 | 0.08953 | 215.6921 | 0.018547
5777 | 860.3306 | 1.6927 | 34.8618 | 98.1839 | 54.2308 | 9.056 | 54.8103 | 1.1388 | 5.2695 | 17.2617 | 87.7701 | 4.5179 | 219.1313 | 115.5987 | 280.0242 | 8.9837 | 47.6209 | 13.268 | 207 | 50.1584 | 0.090147 | 207.2593 | 0.02935
5778 | 875.7132 | 2.06 | 35 | 98.6517 | 54.8095 | 8.8642 | 55.3503 | 1.0708 | 5.3448 | 15.7048 | 87.6537 | 3.4966 | 226.9285 | 105.9489 | 284.5045 | 8.8499 | 46.6251 | 8.409 | 149 | 51.369 | 0.090921 | 205.5085 | 0.012803
5779 | 873.2601 | 2.9008 | 35.2464 | 98.589 | 56.8485 | 7.7547 | 51.7032 | 0.9551 | 5.3145 | 17.6079 | 86.7032 | 3.9585 | 193.2639 | 98.8822 | 275.1446 | 8.8374 | 46.0432 | 5.6734 | 130 | 48.3147 | 0.096124 | 208.1002 | 0.0031591
5780 | 838.3859 | 3.0463 | 35.5059 | 99.0278 | 57.9377 | 7.5895 | 49.6289 | 1.1708 | 5.3782 | 20.1173 | 81.6867 | 5.4218 | 226.8515 | 100.3684 | 260.961 | 9.105 | 45.4302 | 5.5268 | 130 | 50.4493 | 0.093333 | 203.7523 | 0
5781 | 810.2145 | 3.3109 | 35.1309 | 99.8801 | 59.5562 | 6.9382 | 53.0255 | 1.3286 | 5.6445 | 21.0027 | 75.673 | 6.0078 | 197.1934 | 100.6706 | 246.7569 | 9.2822 | 45.5373 | 5.0257 | 127 | 48.0735 | 0.090047 | 197.3995 | 0
5782 | 794.8287 | 2.6276 | 35.0107 | 99.3299 | 60.2159 | 7.3452 | 55.2445 | 1.3463 | 5.7535 | 19.2241 | 73.047 | 5.9738 | 257.4858 | 95.0364 | 239.6504 | 9.4097 | 45.8246 | 3.8873 | 123 | 49.0715 | 0.090331 | 195.9335 | 0
5783 | 783.5152 | 1.5239 | 35.3173 | 99.0725 | 60.929 | 7.5923 | 54.9966 | 1.5811 | 5.7955 | 16.0554 | 72.4826 | 5.9306 | 212.9221 | 88.9945 | 239.6434 | 9.3513 | 45.6634 | 3.3287 | 120 | 39.4905 | 0.08971 | 193.1683 | 0
5784 | 723.3238 | 1.1118 | 35.6333 | 98.7471 | 38.0495 | 8.2334 | 55.6813 | 1.5185 | 5.7485 | 14.4475 | 70.6005 | 5.8571 | 173.298 | 85.9113 | 225.4343 | 9.3632 | 45.42 | 3.2669 | 131 | 41.2138 | 0.089347 | 185.4837 | 0
5785 | 656.3939 | 1.3319 | 35.5531 | 99.504 | 11.0807 | 8.5454 | 51.3086 | 1.3366 | 5.97 | 13.8976 | 68.3579 | 5.9243 | 244.2684 | 84.5079 | 217.0807 | 9.4762 | 44.9613 | 3.2595 | 124 | 37.3986 | 0.089614 | 179.0404 | 0
5786 | 633.4045 | 1.2211 | 35.5235 | 98.9705 | 4.8379 | 7.8854 | 51.4449 | 1.3374 | 5.85 | 13.6659 | 68.3819 | 8.5808 | 220.027 | 83.151 | 223.3336 | 9.5615 | 44.5371 | 3.2325 | 123 | 34.1765 | 0.089899 | 176.8587 | 0
5787 | 632.8257 | 1.1283 | 37.1149 | 99.9591 | 5.7994 | 6.9737 | 53.804 | 1.3386 | 5.598 | 15.3252 | 68.7437 | 14.4555 | 180.2971 | 82.9344 | 228.4771 | 9.5206 | 44.4652 | 2.9523 | 113 | 35.9661 | 0.091035 | 176.7647 | 0
5788 | 635.3226 | 1.5112 | 40.6596 | 100.2859 | 4.6873 | 8.0255 | 54.305 | 1.3294 | 5.6244 | 22.1055 | 68.4185 | 14.0915 | 208.6964 | 81.4664 | 223.665 | 9.2697 | 44.2085 | 2.7016 | 112 | 37.6016 | 0.089833 | 187.5876 | 0
5789 | 655.087 | 2.3352 | 86.4118 | 42.4807 | 4.1227 | 8.5571 | 55.3982 | 1.318 | 5.6066 | 27.7908 | 68.8522 | 9.7565 | 238.956 | 82.2039 | 224.4807 | 9.4301 | 43.639 | 2.6782 | 112 | 38.7827 | 0.19651 | 207.9988 | 0
5790 | 693.7863 | 2.5952 | 53.1769 | 91.6276 | 3.7376 | 9.9625 | 62.3252 | 1.3847 | 5.791 | 28.0498 | 82.3374 | 13.9423 | 264.0823 | 113.6085 | 250.6659 | 13.0207 | 43.2981 | 3.23 | 191 | 37.3288 | 0.13187 | 240.8557 | 0.010961
5791 | 770.0926 | 3.6562 | 89.9227 | 84.9088 | -0.98361 | 15.3411 | 81.5926 | 1.9254 | 8.4515 | 33.2101 | 112.0279 | 28.9182 | 174.9016 | 181.285 | 314.9169 | 25.6922 | 46.106 | 9.3243 | 288 | 55.7396 | 0.29931 | 300.9079 | 0.031779
5792 | 868.4102 | 5.8084 | 53.1111 | 162.0829 | -2.0792 | 15.7422 | 114.3696 | 3.0682 | 17.776 | 48.0445 | 141.084 | 39.2449 | 254.7337 | 244.715 | 411.4792 | 34.9766 | 55.892 | 14.9079 | 308 | 59.9629 | 0.28528 | 382.4695 | 0.12269
5793 | 1005.5203 | 6.672 | 86.4707 | 138.1146 | -2.9681 | 16.6592 | 129.1109 | 3.5602 | 26.0705 | 60.8696 | 160.7008 | 40.9982 | 226.7528 | 287.2122 | 500.007 | 39.3505 | 69.6669 | 16.2193 | 325 | 67.3561 | 0.27904 | 448.7137 | 0.07268
5794 | 1080.0449 | 6.0504 | 101.4823 | 185.1542 | -5.8043 | 19.734 | 130.7262 | 4.5488 | 27.5363 | 66.1057 | 166.3596 | 42.3944 | 287.4699 | 315.2722 | 562.7412 | 41.1497 | 80.7619 | 17.1273 | 381 | 82.4366 | 0.32899 | 479.9947 | 0.089753
5795 | 1119.1369 | 6.4808 | 100.0494 | 159.9241 | -6.4628 | 19.4217 | 134.4656 | 4.832 | 26.5493 | 70.2871 | 166.4544 | 40.8275 | 220.9594 | 328.9756 | 587.0914 | 39.4616 | 85.384 | 17.5654 | 372 | 84.0831 | 0.34637 | 494.809 | 0.096157
5796 | 1135.4405 | 7.0888 | 105.0988 | 141.7413 | -6.1477 | 18.3597 | 128.0998 | 4.7745 | 21.3594 | 72.8181 | 175.4362 | 40.6519 | 314.6494 | 333.5367 | 593.7673 | 39.9237 | 83.4132 | 16.5289 | 385 | 91.5242 | 0.45162 | 500.3981 | 0.075593
5797 | 1135.91 | 9.4214 | 107.9841 | 144.9931 | -7.4677 | 19.5683 | 130.0811 | 4.5998 | 16.767 | 75.3733 | 187.0656 | 42.4903 | 387.1725 | 337.6162 | 592.1592 | 41.6534 | 80.8424 | 15.4709 | 296 | 98.2924 | 0.26828 | 494.6793 | 0.12784
5798 | 1137.5378 | 9.5655 | 106.8344 | 137.5234 | -8.728 | 20.7637 | 129.4942 | 4.5328 | 22.8119 | 79.6678 | 192.4735 | 41.7084 | 359.9001 | 338.6728 | 580.4814 | 40.5326 | 80.6322 | 14.9726 | 282 | 103.4392 | 0.43383 | 491.5449 | 0.097343
5799 | 1124.757 | 6.1554 | 107.0088 | 191.8763 | -7.233 | 19.5089 | 128.9957 | 4.6111 | 25.2221 | 80.4269 | 190.8279 | 39.3912 | 399.5571 | 326.2111 | 569.0543 | 37.2805 | 79.8732 | 14.3278 | 309 | 94.6555 | 0.28841 | 477.288 | 0.15799
5800 | 1088.0403 | 3.5648 | 103.6375 | 167.6471 | -0.56976 | 13.9226 | 117.26 | 4.5765 | 18.9345 | 73.1515 | 182.6994 | 34.8502 | 388.5922 | 300.5383 | 537.5591 | 29.4728 | 76.9362 | 14.1379 | 277 | 83.7151 | 0.13424 | 422.1345 | 0.17536
5801 | 1027.8321 | 2.8653 | 97.454 | 144.3111 | 5.1078 | 9.5559 | 92.5873 | 3.1203 | 11.8197 | 55.7062 | 165.8778 | 30.0667 | 358.636 | 253.1902 | 462.522 | 17.1276 | 71.0404 | 13.9635 | 250 | 68.8376 | 0.12775 | 344.261 | 0.10779
5802 | 963.2011 | 2.483 | 92.7814 | 99.392 | 5.6775 | 8.5677 | 80.8859 | 2.1601 | 7.4458 | 40.2963 | 136.1022 | 23.1092 | 327.9785 | 189.8392 | 381.6635 | 10.6349 | 64.2945 | 11.8875 | 239 | 51.0362 | 0.072999 | 276.4316 | 0.088948
5803 | 924.5283 | 2.776 | 74.9059 | 120.2606 | 4.1723 | 9.9802 | 65.7551 | 1.9937 | 5.919 | 39.0895 | 107.3884 | 11.1214 | 280.1529 | 141.686 | 331.7815 | 9.9889 | 59.4612 | 7.1786 | 226 | 52.9319 | 0.086285 | 229.3048 | 0.027391
5804 | 889.6178 | 3.6257 | 44.0755 | 48.0039 | 6.9458 | 8.3542 | 56.8285 | 2.0358 | 5.5805 | 42.108 | 96.6522 | 6.9626 | 317.6631 | 120.7753 | 303.1223 | 10.0115 | 55.0392 | 4.9191 | 216 | 47.4504 | 0.11904 | 199.599 | 0
5805 | 861.8427 | 3.5075 | 30.5684 | 74.4704 | 6.7276 | 7.5464 | 58.035 | 2.2153 | 6.0497 | 34.5979 | 94.7219 | 8.2223 | 259.4088 | 115.5287 | 281.721 | 10.1802 | 50.2443 | 3.8748 | 209 | 46.4061 | 0.093334 | 184.6378 | 0
5806 | 837.905 | 2.8739 | 38.9111 | 90.7384 | 5.9282 | 7.6354 | 57.0522 | 2.2788 | 6.7841 | 22.5877 | 87.6058 | 8.3113 | 246.4476 | 108.1338 | 258.3787 | 10.276 | 47.1291 | 3.3675 | 174 | 43.2787 | 0.072869 | 176.5053 | 0
5807 | 813.2707 | 1.8384 | 21.1817 | 100.3747 | 5.6724 | 7.5677 | 57.0507 | 2.4996 | 6.49 | 17.6006 | 77.8153 | 8.3826 | 241.4944 | 97.5051 | 258.4381 | 10.3286 | 45.7769 | 3.1917 | 155 | 35.6513 | 0.084196 | 170.6503 | 0
5808 | 822.5072 | 1.1674 | 25.7582 | 100.2032 | 4.4485 | 8.251 | 58.0599 | 2.4551 | 6.5512 | 17.1023 | 72.3114 | 8.4648 | 244.5719 | 92.8845 | 270.0082 | 10.0096 | 45.3858 | 2.9688 | 164 | 42.6554 | 0.089574 | 169.2281 | 0
5809 | 816.0306 | 1.1788 | 27.9607 | 39.1761 | 4.0362 | 8.6498 | 58.4177 | 2.0919 | 6.2531 | 17.0877 | 70.3993 | 8.3632 | 171.7136 | 93.5796 | 265.2537 | 10.132 | 45.4773 | 3.0918 | 161 | 38.778 | 0.090794 | 171.0329 | 0
5810 | 795.7616 | 1.2088 | 37.1373 | 69.8581 | 3.5045 | 9.1522 | 70.9548 | 1.6228 | 5.954 | 17.0499 | 69.8198 | 8.2976 | 199.8196 | 94.6304 | 255.5844 | 10.2445 | 45.538 | 2.8852 | 154 | 41.3737 | 0.24463 | 172.4127 | 0
5811 | 799.1654 | 1.2258 | 20.6528 | 54.3755 | 4.5406 | 8.1678 | 74.0769 | 1.4459 | 6.0309 | 18.774 | 69.6456 | 8.2633 | 250.888 | 94.2025 | 245.601 | 10.2439 | 45.5049 | 2.639 | 146 | 37.7425 | 0.17009 | 174.4267 | 0
5812 | 806.3504 | 1.569 | 25.1772 | 49.074 | 3.6821 | 8.9843 | 54.8732 | 1.437 | 6.3071 | 25.6927 | 69.4512 | 10.9593 | 213.004 | 91.3518 | 241.3905 | 10.2106 | 45.4782 | 2.5755 | 137 | 44.0882 | 0.2674 | 184.9353 | 0
5813 | 818.8103 | 2.5524 | 34.4785 | 28.2946 | 3.7985 | 8.8699 | 52.5698 | 1.5672 | 6.1255 | 31.7347 | 68.7434 | 10.6863 | 348.7137 | 89.7061 | 241.5268 | 10.1203 | 45.248 | 2.5147 | 138 | 39.2667 | 0.17068 | 206.0757 | 0
5814 | 858.5605 | 2.8969 | 53.8266 | 99.3025 | 7.1384 | 9.958 | 64.4968 | 1.2876 | 5.9631 | 31.1947 | 80.1116 | 17.432 | 351.443 | 112.9022 | 241.1179 | 13.7875 | 45.2856 | 2.3001 | 216 | 50.2649 | 0.20468 | 237.486 | 0.022722
5815 | 910.9776 | 3.3572 | 80.4575 | 91.648 | 29.5132 | 15.4153 | 81.3125 | 2.098 | 5.5329 | 40.1804 | 110.6337 | 32.1369 | 296.8965 | 175.0307 | 281.8086 | 26.4709 | 49.7284 | 7.5157 | 264 | 65.0085 | 0.21837 | 290.9162 | 0.084103
5816 | 998.004 | 3.8339 | 97.5237 | 166.4543 | 47.0764 | 16.2083 | 104.1745 | 2.96 | 11.6933 | 58.5053 | 141.3666 | 39.6484 | 340.1667 | 244.1777 | 377.0047 | 34.0008 | 59.3329 | 12.4804 | 327 | 73.1852 | 0.28126 | 371.4694 | 0.18281
5817 | 1095.5437 | 3.7449 | 105.0704 | 175.9894 | 47.6476 | 16.8095 | 118.3965 | 3.6344 | 20.0092 | 69.3604 | 161.7238 | 40.9768 | 322.751 | 288.7331 | 483.0069 | 35.7458 | 69.2105 | 13.903 | 351 | 76.5225 | 0.16885 | 444.0942 | 0.16918
5818 | 1130.4273 | 3.3395 | 105.1558 | 173.0979 | 48.4085 | 17.8462 | 122.2064 | 4.6921 | 24.3198 | 73.0638 | 173.4615 | 41.9056 | 343.318 | 312.9762 | 545.6809 | 37.3251 | 80.0011 | 14.6531 | 359 | 84.4693 | 0.28056 | 480.0506 | 0.19895
5819 | 1141.4277 | 3.5073 | 108.505 | 177.6316 | 49.8653 | 18.8381 | 126.5283 | 5.4635 | 25.5395 | 76.0786 | 178.9863 | 39.9079 | 405.7294 | 332.3464 | 578.3694 | 38.2685 | 88.701 | 14.7656 | 358 | 104.9099 | 0.35344 | 500.8033 | 0.19274
5820 | 1153.6738 | 5.0822 | 110.7141 | 179.0455 | 52.882 | 19.8226 | 131.2154 | 5.1025 | 23.3305 | 75.5008 | 182.1669 | 40.5882 | 387.0196 | 342.7514 | 595.2911 | 39.4748 | 89.1784 | 14.8297 | 395 | 89.927 | 0.21524 | 518.4914 | 0.20902
5821 | 1138.8739 | 8.9094 | 147.1897 | 182.9439 | 60.3573 | 17.7759 | 129.7546 | 4.7062 | 22.0783 | 77.9894 | 183.5802 | 43.4271 | 375.1454 | 340.0422 | 586.4284 | 40.0377 | 86.6998 | 14.2931 | 369 | 97.9711 | 0.19681 | 514.6838 | 0.24703
5822 | 1120.5054 | 9.4131 | 81.3315 | 161.3884 | 72.5404 | 16.3165 | 135.8155 | 4.8059 | 24.6217 | 82.5024 | 182.8627 | 42.9564 | 350.3313 | 335.7641 | 567.366 | 39.1078 | 86.6577 | 14.5418 | 362 | 101.8438 | 0.118 | 507.0897 | 0.18446
5823 | 1099.7538 | 5.9087 | 98.0612 | 201.8125 | 73.7086 | 14.7657 | 130.2453 | 4.6717 | 24.0305 | 75.4012 | 181.0393 | 39.6009 | 372.9737 | 322.3645 | 554.0291 | 36.6697 | 87.2321 | 15.0607 | 330 | 87.3957 | 0.14334 | 504.9952 | 0.11509
5824 | 1088.6962 | 3.9293 | 103.9602 | 174.0725 | 66.7532 | 11.5051 | 106.6331 | 3.5958 | 18.8895 | 63.3429 | 178.4394 | 37.1548 | 341.2467 | 292.6406 | 525.8864 | 29.428 | 84.9957 | 14.6377 | 316 | 76.0364 | 0.15502 | 476.8468 | 0.089904
5825 | 1029.6682 | 3.0102 | 97.7824 | 143.2969 | 64.8634 | 9.0098 | 91.0452 | 2.4593 | 15.072 | 50.4046 | 166.8645 | 34.572 | 391.8953 | 241.7794 | 441.4032 | 16.3367 | 78.5249 | 13.7137 | 271 | 68.1727 | 0.15238 | 407.5803 | 0.11018
5826 | 956.4092 | 2.0639 | 94.2018 | 123.3039 | 65.7468 | 7.881 | 86.1824 | 1.9071 | 8.6996 | 40.1995 | 138.9654 | 26.3946 | 263.4735 | 184.6803 | 359.6159 | 10.0996 | 71.0392 | 10.7017 | 253 | 53.0902 | 0.15321 | 327.3353 | 0.077931
5827 | 916.9618 | 2.4053 | 79.3401 | 104.2551 | 64.7522 | 8.2586 | 69.031 | 1.8152 | 5.4638 | 39.4156 | 110.6694 | 11.743 | 256.3377 | 156.1294 | 326.1268 | 9.833 | 65.7962 | 5.8565 | 233 | 50.5678 | 0.15258 | 264.6182 | 0.019691
5828 | 895.5381 | 3.674 | 50.091 | 77.0565 | 59.4209 | 9.3028 | 55.5041 | 1.9595 | 5.0733 | 40.6624 | 101.0307 | 7.3306 | 230.8123 | 146.0181 | 300.1609 | 10.0285 | 61.4215 | 4.7485 | 205 | 50.929 | 0.19699 | 223.0612 | 0
5829 | 865.8756 | 3.5117 | 37.4436 | 64.1245 | 48.7439 | 9.4207 | 55.4384 | 2.301 | 6.0553 | 32.8126 | 100.5223 | 8.3449 | 260.895 | 138.666 | 279.1936 | 10.4529 | 57.3342 | 4.9292 | 189 | 40.0733 | 0.11841 | 212.0413 | 0
5830 | 835.4336 | 2.8336 | 36.0202 | 32.0241 | 46.436 | 10.1369 | 57.0345 | 2.3267 | 6.672 | 22.5642 | 92.7744 | 8.3918 | 253.5023 | 131.1851 | 257.5803 | 10.6372 | 55.3733 | 4.8037 | 159 | 45.9934 | 0.142 | 215.5379 | 0
5831 | 818.2096 | 1.8793 | 35.016 | 77.6145 | 46.8202 | 8.3463 | 58.1372 | 2.2058 | 6.3984 | 18.5211 | 82.5162 | 8.3424 | 266.5045 | 120.5689 | 248.8385 | 10.4051 | 55.1218 | 4.2797 | 150 | 46.0343 | 0.14177 | 213.1392 | 0
5832 | 808.2623 | 1.3543 | 34.3635 | 63.1566 | 50.8621 | 7.6479 | 58.2798 | 2.2429 | 6.1381 | 17.2353 | 77.9381 | 8.3414 | 223.5984 | 113.715 | 251.6716 | 10.117 | 53.6581 | 3.619 | 139 | 46.481 | 0.074486 | 209.0107 | 0
5833 | 803.0546 | 1.1785 | 33.6443 | 54.832 | 58.6941 | 6.9186 | 51.3197 | 1.847 | 5.9635 | 16.5063 | 75.7134 | 8.5846 | 231.1739 | 109.1513 | 245.8261 | 10.4308 | 50.3207 | 3.1787 | 129 | 43.3695 | 0.089834 | 209.5624 | 0
5834 | 792.3811 | 1.0464 | 33.4565 | 53.9405 | 62.0502 | 7.4081 | 52.3933 | 1.4837 | 6.082 | 16.4306 | 73.737 | 10.9537 | 219.7912 | 107.5722 | 236.3532 | 10.3311 | 48.622 | 2.9342 | 133 | 39.0089 | 0.12375 | 209.6493 | 0
5835 | 790.5842 | 1.154 | 34.3247 | 42.9753 | 67.0303 | 7.5832 | 56.9017 | 1.6022 | 6.1345 | 17.4874 | 72.741 | 16.3608 | 209.0944 | 108.0719 | 228.1823 | 10.2257 | 50.236 | 2.8282 | 127 | 41.97 | 0.096025 | 210.6452 | 0
5836 | 795.0635 | 1.8463 | 38.1394 | 90.1272 | 69.3922 | 8.2963 | 57.3345 | 1.511 | 5.9724 | 22.4294 | 72.0683 | 16.3366 | 213.7852 | 105.9594 | 222.5303 | 10.5881 | 52.7822 | 2.8082 | 120 | 40.7821 | 0.074972 | 214.3328 | 0
5837 | 813.6784 | 2.6063 | 41.4783 | 59.4608 | 70.99 | 8.5229 | 57.4738 | 1.3188 | 5.9794 | 27.2789 | 71.2253 | 12.8585 | 217.5922 | 105.119 | 219.9375 | 10.3735 | 54.1109 | 2.678 | 122 | 40.0788 | 0.085332 | 228.1386 | 0
5838 | 865.2392 | 2.6081 | 60.7719 | 100.2405 | 72.2674 | 10.0249 | 59.3328 | 1.0734 | 5.7267 | 28.4611 | 79.6341 | 16.9724 | 368.1944 | 122.7027 | 236.6398 | 13.434 | 53.0391 | 2.593 | 204 | 50.0566 | 0.20446 | 262.0075 | 0
5839 | 931.7967 | 4.4758 | 84.4531 | 128.7166 | 70.5446 | 14.6918 | 79.9085 | 1.9991 | 7.6933 | 40.0849 | 107.4824 | 30.5127 | 312.2473 | 177.6912 | 303.4736 | 27.1197 | 52.8901 | 7.9532 | 302 | 64.7801 | 0.26342 | 321.0178 | 0.033061
5840 | 1028.8467 | 8.9768 | 100.6186 | 179.9209 | 65.7268 | 19.671 | 114.7413 | 3.5725 | 15.0833 | 61.0903 | 145.8239 | 39.1261 | 333.9467 | 247.2683 | 418.5333 | 35.5814 | 60.5891 | 12.2206 | 327 | 66.9667 | 0.22681 | 396.3457 | 0.05777
5841 | 1112.6177 | 10.7461 | 144.5885 | 186.4329 | 58.7117 | 21.7411 | 129.9092 | 4.7635 | 23.821 | 79.3256 | 175.388 | 40.5251 | 259.24 | 295.779 | 519.5609 | 41.3313 | 73.1956 | 12.947 | 384 | 77.7508 | 0.28277 | 450.0375 | 0.062782
5842 | 1142.1036 | 6.7276 | 82.4882 | 187.7785 | 53.3857 | 20.7288 | 138.1708 | 4.9202 | 23.9737 | 87.6821 | 187.582 | 41.0687 | 329.262 | 318.4637 | 580.2875 | 42.3872 | 83.0263 | 14.2441 | 352 | 85.9761 | 0.31229 | 479.3503 | 0.08859
5843 | 1138.8783 | 3.8389 | 97.4318 | 174.5512 | 53.4915 | 17.5558 | 141.6179 | 4.92 | 22.7876 | 87.597 | 188.15 | 41.3323 | 384.0817 | 331.5292 | 614.304 | 40.4269 | 88.0234 | 14.5742 | 365 | 96.3902 | 0.29364 | 500.5125 | 0.10482
5844 | 1133.2628 | 3.8688 | 143.0825 | 214.1097 | 53.7248 | 18.3416 | 143.0836 | 4.0871 | 20.0265 | 86.991 | 184.0902 | 41.5619 | 373.7216 | 336.611 | 603.8289 | 40.6077 | 87.527 | 15.1059 | 359 | 84.3183 | 0.20271 | 513.7683 | 0.16819
5845 | 1152.4784 | 10.1643 | 79.772 | 204.1211 | 58.6584 | 16.1016 | 151.5356 | 3.543 | 16.1793 | 84.5233 | 182.0756 | 39.6107 | 368.8297 | 337.7103 | 585.2483 | 41.2365 | 85.0881 | 16.1593 | 314 | 96.1113 | 0.25452 | 517.64 | 0.23436
5846 | 1162.0226 | 11.2013 | 99.7118 | 175.7872 | 61.7323 | 15.3313 | 158.4643 | 3.5946 | 19.0242 | 80.6928 | 183.5588 | 37.5377 | 407.0834 | 340.8923 | 575.876 | 38.9943 | 84.1121 | 16.4353 | 285 | 93.9425 | 0.30657 | 518.1409 | 0.23849
5847 | 1125.1392 | 5.7817 | 109.0453 | 211.2183 | 65.2588 | 15.0152 | 146.8175 | 3.3266 | 20.3308 | 72.583 | 184.8964 | 35.0041 | 415.7259 | 332.1781 | 564.5439 | 37.2527 | 82.9272 | 16.6865 | 293 | 91.3268 | 0.20215 | 511.424 | 0.18011
5848 | 1078.4185 | 3.6275 | 104.4342 | 186.0427 | 70.4834 | 12.3964 | 126.6366 | 3.0726 | 15.6725 | 58.9922 | 184.3956 | 32.7655 | 367.2121 | 307.1295 | 538.8181 | 30.2924 | 80.0099 | 16.483 | 282 | 81.6991 | 0.14887 | 472.7711 | 0.16648
5849 | 1022.7443 | 3.0182 | 99.7279 | 136.605 | 72.4246 | 9.3205 | 104.3222 | 1.9478 | 11.3812 | 45.5743 | 174.2262 | 31.6045 | 234.1816 | 256.9936 | 485.3847 | 16.6251 | 75.1654 | 15.847 | 245 | 70.1411 | 0.078914 | 404.0589 | 0.11196
5850 | 956.9709 | 2.1415 | 95.8969 | 157.3305 | 70.097 | 8.5431 | 92.6687 | 1.272 | 12.6535 | 39.2863 | 147.579 | 25.8972 | 300.6178 | 192.794 | 423.3008 | 9.5987 | 70.7256 | 12.9394 | 226 | 69.3866 | 0.12608 | 332.143 | 0.028692
5851 | 907.0263 | 2.6711 | 79.8034 | 123.3867 | 68.3086 | 8.5893 | 72.5136 | 1.3388 | 8.9685 | 41.3689 | 120.9904 | 12.5788 | 364.2005 | 149.505 | 377.321 | 8.8484 | 66.7243 | 7.4166 | 205 | 60.9427 | 0.080445 | 272.7922 | 0.0031455
5852 | 866.8322 | 3.5795 | 44.2056 | 83.8576 | 66.1889 | 8.6092 | 59.0554 | 1.3312 | 5.916 | 43.1388 | 111.1833 | 7.5719 | 311.4051 | 132.0416 | 335.3018 | 9.2416 | 61.8282 | 5.0683 | 184 | 58.3417 | 0.08684 | 235.6294 | 0
5853 | 851.1619 | 3.5021 | 28.5889 | 67.3329 | 65.7858 | 7.1026 | 57.8381 | 1.3598 | 6.3806 | 36.2836 | 107.9028 | 8.1422 | 193.6159 | 124.4246 | 295.2284 | 9.4966 | 58.311 | 4.7381 | 183 | 52.4906 | 0.08954 | 224.764 | 0
5854 | 831.9157 | 2.6108 | 26.5443 | 40.9855 | 63.6623 | 8.0588 | 54.125 | 1.3648 | 6.8494 | 27.0015 | 97.7916 | 8.4776 | 260.8904 | 119.2701 | 274.6812 | 9.6019 | 56.4248 | 4.3147 | 166 | 55.6043 | 0.096858 | 222.5875 | 0
5855 | 807.0472 | 1.6574 | 25.9515 | 77.2448 | 61.9681 | 9.2208 | 58.7899 | 1.3697 | 6.6218 | 22.6388 | 85.7271 | 8.4432 | 230.7509 | 109.7399 | 260.8879 | 9.4553 | 55.0401 | 4.6025 | 146 | 51.0952 | 0.092871 | 219.123 | 0
5856 | 801.8581 | 1.4867 | 25.4453 | 65.7602 | 76.7527 | 7.4021 | 65.7458 | 1.5918 | 6.3567 | 21.0923 | 79.5868 | 8.1677 | 283.0717 | 96.9281 | 249.0266 | 9.463 | 54.5686 | 4.3503 | 128 | 44.4363 | 0.090004 | 232.0702 | 0
5857 | 808.1736 | 1.2422 | 25.1133 | 35.9912 | 69.351 | 8.7472 | 65.0046 | 1.5283 | 6.0934 | 20.771 | 76.4022 | 8.0494 | 220.1348 | 90.5142 | 243.9036 | 9.4811 | 54.6604 | 4.1245 | 130 | 46.9337 | 0.089621 | 245.5996 | 0
5858 | 809.9401 | 1.0362 | 24.9429 | 74.8817 | 77.888 | 8.1306 | 64.1074 | 1.3658 | 5.9836 | 20.7894 | 73.5554 | 10.1077 | 213.3578 | 89.7093 | 238.2138 | 9.3778 | 52.5165 | 3.9121 | 123 | 46.5421 | 0.22242 | 244.8618 | 0
5859 | 794.8631 | 1.0339 | 25.9704 | 42.4021 | 71.6846 | 7.5825 | 65.4517 | 1.3728 | 6.112 | 22.3443 | 71.6336 | 15.9221 | 248.3958 | 89.4098 | 231.0808 | 9.5251 | 48.5912 | 3.6814 | 118 | 46.3647 | 0.15124 | 245.4749 | 0
5860 | 794.2749 | 1.451 | 29.8698 | 63.7514 | 68.3556 | 7.5834 | 62.926 | 1.379 | 6.1594 | 29.1814 | 70.3545 | 15.7789 | 242.2674 | 88.1117 | 225.4157 | 9.5383 | 46.6676 | 3.2037 | 116 | 49.4067 | 0.18303 | 246.8011 | 0
5861 | 814.0563 | 2.5823 | 42.3518 | 93.6938 | 75.535 | 8.2704 | 69.8632 | 1.3788 | 6.1508 | 35.8529 | 69.7655 | 15.1618 | 258.904 | 88.7941 | 223.8093 | 9.2577 | 46.9498 | 3.0972 | 110 | 47.2463 | 0.19636 | 261.3805 | 0
5862 | 854.5143 | 3.5069 | 117.4352 | 102.9226 | 70.3368 | 12.1055 | 75.8297 | 1.1532 | 6.241 | 35.4488 | 80.4864 | 20.4974 | 251.5843 | 113.173 | 238.3503 | 13.1601 | 48.1494 | 3.5011 | 211 | 53.9288 | 0.16602 | 295.7781 | 0
5863 | 913.0568 | 4.6683 | 73.909 | 120.82 | 70.5288 | 14.6923 | 103.2219 | 1.9141 | 5.6448 | 41.9734 | 112.4814 | 32.4754 | 244.7783 | 176.2966 | 288.7562 | 26.0647 | 51.8168 | 9.744 | 310 | 60.0671 | 0.19872 | 349.858 | 0.047467
5864 | 981.1653 | 6.2788 | 92.0415 | 130.3474 | 75.4233 | 15.9343 | 128.2265 | 3.1729 | 13.2105 | 59.9514 | 147.5907 | 38.7023 | 250.9985 | 246.2263 | 379.092 | 34.5182 | 60.8122 | 14.883 | 299 | 73.7307 | 0.11893 | 426.5736 | 0.10838
5865 | 1043.6655 | 10.4093 | 101.2564 | 195.0855 | 74.5786 | 16.1795 | 147.04 | 3.4404 | 22.8581 | 70.6857 | 166.9198 | 38.5116 | 349.5588 | 294.4041 | 482.7081 | 38.6012 | 71.7687 | 15.4604 | 350 | 80.7215 | 0.1881 | 495.2535 | 0.091199
5866 | 1096.6531 | 12.7897 | 135.0966 | 252.6292 | 72.5242 | 16.8094 | 156.5976 | 3.6567 | 25.8598 | 75.7755 | 176.0669 | 40.0088 | 325.7452 | 324.1454 | 555.7981 | 22.6745 | 78.7245 | 15.4916 | 351 | 84.4893 | 0.15352 | 529.4466 | 0.1905
5867 | 1118.0191 | 12.9145 | 74.6865 | 140.5384 | 72.1934 | 17.0338 | 157.3305 | 3.8893 | 25.3573 | 82.3455 | 181.1432 | 41.0309 | 541.2919 | 338.3071 | 578.6878 | 52.4013 | 81.2943 | 15.6318 | 323 | 85.3295 | 0.11852 | 541.0622 | 0.1163
5868 | 1103.4454 | 12.0597 | 91.5449 | 156.3956 | 73.5821 | 17.2193 | 156.154 | 3.8555 | 25.081 | 81.8296 | 180.9211 | 42.3437 | 266.1336 | 341.3072 | 576.3849 | 45.1414 | 82.6312 | 16.5171 | 371 | 87.9351 | 0.18851 | 544.539 | 0.19427
5869 | 1101.0701 | 11.1248 | 135.4943 | 222.3294 | 75.4966 | 17.0978 | 158.6685 | 3.6864 | 22.3763 | 81.9332 | 181.0709 | 42.8817 | 321.0662 | 346.813 | 575.6914 | 40.4742 | 84.9968 | 17.1468 | 344 | 89.7617 | 0.15352 | 546.7541 | 0.14463
5870 | 1106.158 | 6.7425 | 74.4714 | 184.41 | 77.6985 | 16.3934 | 158.9407 | 3.4232 | 26.4125 | 85.938 | 188.0276 | 41.6294 | 370.4651 | 347.2539 | 582.1995 | 39.7138 | 86.6382 | 17.0984 | 311 | 84.9742 | 0.15352 | 548.3944 | 0.2281
5871 | 1076.4538 | 3.9446 | 97.7375 | 208.3746 | 80.3087 | 15.5081 | 155.3889 | 3.3282 | 26.8675 | 82.0583 | 192.7044 | 40.2902 | 384.9348 | 333.0071 | 578.7022 | 36.7823 | 84.942 | 16.8093 | 278 | 76.8067 | 0.11922 | 534.8304 | 0.25543
5872 | 1027.0294 | 3.8289 | 104.2534 | 183.1032 | 80.5749 | 15.7997 | 138.0589 | 3.2891 | 15.705 | 70.584 | 186.8524 | 39.0227 | 426.2418 | 312.0328 | 550.4425 | 28.8257 | 79.2538 | 16.0505 | 257 | 77.4294 | 0.18782 | 483.6472 | 0.20483
5873 | 996.8891 | 3.2141 | 98.4907 | 135.7976 | 84.27 | 12.0107 | 121.3726 | 2.269 | 9.757 | 58.069 | 169.0563 | 33.0559 | 344.8478 | 272.5711 | 484.1513 | 16.1306 | 71.2883 | 15.2087 | 241 | 62.4066 | 0.12049 | 402.1035 | 0.1889
5874 | 964.5324 | 2.7144 | 93.2689 | 155.1633 | 87.284 | 7.4837 | 105.6633 | 1.5451 | 9.5697 | 53.4962 | 136.4288 | 23.824 | 307.5855 | 223.1132 | 408.1509 | 10.3037 | 65.6469 | 12.7998 | 247 | 58.961 | 0.14116 | 328.995 | 0.11789
5875 | 913.6702 | 3.0045 | 79.279 | 99.1151 | 85.9785 | 6.6825 | 82.9941 | 1.7019 | 9.5285 | 60.7029 | 105.2696 | 12.5874 | 328.8705 | 186.2339 | 357.6508 | 9.8953 | 61.3419 | 7.872 | 219 | 60.1078 | 0.15294 | 283.9965 | 0.016471
5876 | 872.1315 | 3.5227 | 46.3242 | 100.9741 | 75.9732 | 8.026 | 68.2718 | 1.9886 | 8.8043 | 67.6736 | 93.4825 | 8.2673 | 297.8427 | 153.5091 | 329.8996 | 9.9501 | 56.0144 | 5.6047 | 195 | 63.6649 | 0.15283 | 258.7551 | 0
5877 | 854.3291 | 3.5867 | 30.8609 | 74.7627 | 74.6901 | 7.1788 | 66.1725 | 2.1653 | 8.8331 | 61.5947 | 93.5702 | 8.5181 | 280.6363 | 131.7638 | 312.9096 | 10.2849 | 53.7944 | 5.5144 | 193 | 66.6962 | 0.15372 | 247.3313 | 0
5878 | 830.2626 | 3.0194 | 29.2908 | 41.598 | 79.68 | 7.3759 | 68.3391 | 2.1659 | 9.1883 | 50.1445 | 90.2023 | 11.8 | 327.2904 | 123.8237 | 301.8584 | 10.1273 | 54.9681 | 4.7086 | 182 | 64.5987 | 0.15516 | 244.0843 | 0
5879 | 808.9513 | 1.7505 | 28.9217 | 81.1372 | 80.9666 | 8.2759 | 62.8071 | 2.3669 | 9.0506 | 44.2629 | 81.8373 | 10.3689 | 215.1025 | 113.1762 | 302.1748 | 10.3089 | 53.4127 | 4.2852 | 184 | 63.3838 | 0.19834 | 240.4735 | 0
5880 | 808.912 | 1.2823 | 28.8944 | 33.8186 | 92.6027 | 10.5802 | 62.9516 | 2.2632 | 8.501 | 40.9436 | 76.4019 | 8.3624 | 230.5908 | 106.5961 | 297.7722 | 10.4465 | 49.793 | 3.9943 | 168 | 60.7164 | 0.11825 | 237.5582 | 0
5881 | 805.1119 | 1.4178 | 38.6278 | 71.2255 | 96.9748 | 11.4338 | 66.7679 | 1.6854 | 7.88 | 36.9271 | 74.4604 | 8.1569 | 240.0037 | 104.3012 | 287.3637 | 10.0917 | 49.1093 | 3.6442 | 156 | 67.3117 | 0.14326 | 237.3273 | 0
5882 | 796.2216 | 1.6191 | 21.0947 | 30.0267 | 102.2925 | 10.0868 | 68.2405 | 1.3889 | 7.02 | 32.2639 | 74.4171 | 10.2405 | 216.4052 | 100.9129 | 283.7035 | 9.9685 | 51.14 | 3.3336 | 136 | 59.1707 | 0.15403 | 237.9966 | 0
5883 | 787.1775 | 1.4298 | 27.0859 | 51.5933 | 105.659 | 8.1446 | 64.6504 | 1.3839 | 6.4592 | 29.903 | 74.5589 | 15.8631 | 246.0946 | 98.4769 | 268.0257 | 10.0709 | 53.74 | 3.1286 | 143 | 58.6891 | 0.15488 | 239.825 | 0
5884 | 789.7803 | 1.8762 | 33.8693 | 76.3204 | 107.4364 | 6.814 | 62.351 | 1.3996 | 6.5753 | 35.3903 | 73.4254 | 15.7309 | 218.6701 | 95.0505 | 248.4362 | 10.1211 | 55.0151 | 2.9825 | 142 | 59.4982 | 0.19719 | 247.1457 | 0
5885 | 793.4215 | 2.7355 | 44.1933 | 46.7656 | 106.9568 | 7.3705 | 61.0268 | 1.4675 | 6.4202 | 41.3732 | 73.2302 | 11.8997 | 215.5872 | 94.6086 | 240.0007 | 10.0902 | 55.3226 | 2.8571 | 146 | 52.2388 | 0.11919 | 261.3096 | 0
5886 | 831.2884 | 3.3225 | 62.1967 | 87.9727 | 103.4774 | 10.5277 | 68.4771 | 1.3456 | 6.0283 | 39.4841 | 82.8047 | 14.7488 | 198.439 | 115.5681 | 242.5082 | 13.5477 | 55.278 | 2.6254 | 210 | 56.0149 | 0.18785 | 287.4914 | 0
5887 | 902.084 | 12.7681 | 83.7584 | 133.8904 | 99.1448 | 14.8259 | 97.503 | 1.9031 | 9.293 | 47.8208 | 109.1409 | 28.4408 | 259.471 | 171.956 | 299.695 | 26.0225 | 57.2715 | 7.9903 | 250 | 61.2967 | 0.11817 | 331.7289 | 0.033746
5888 | 977.6788 | 18.1511 | 95.1445 | 148.4871 | 98.7669 | 17.6446 | 120.5307 | 3.028 | 14.5085 | 65.82 | 140.4497 | 36.2833 | 386.6323 | 236.5056 | 414.071 | 35.5369 | 64.3599 | 12.6084 | 342 | 68.7094 | 0.14449 | 389.4407 | 0.13264
5889 | 1052.1351 | 13.6209 | 98.9223 | 134.3051 | 101.3742 | 18.803 | 131.7593 | 3.8676 | 22.1227 | 75.2823 | 162.6606 | 39.3997 | 283.0393 | 279.3848 | 512.4962 | 39.0433 | 72.9987 | 14.2123 | 360 | 74.4657 | 0.1979 | 448.3167 | 0.13182
5890 | 1087.8142 | 7.7704 | 102.4197 | 187.1776 | 100.454 | 18.3065 | 144.9747 | 4.2314 | 24.3506 | 77.4107 | 171.9179 | 41.0468 | 270.8344 | 306.7494 | 565.8377 | 38.9796 | 79.6371 | 15.2912 | 369 | 81.8506 | 0.11921 | 489.763 | 0.18231
5891 | 1094.0477 | 4.6299 | 106.9021 | 150.0176 | 98.4382 | 15.1257 | 149.3298 | 3.9728 | 24.3433 | 78.333 | 173.2788 | 40.1636 | 349.9566 | 324.0892 | 604.6975 | 38.5943 | 84.2972 | 15.7078 | 347 | 87.5254 | 0.14289 | 505.276 | 0.18862
5892 | 1106.5887 | 3.8039 | 107.4712 | 190.2098 | 90.6285 | 16.3658 | 149.3567 | 4.0056 | 22.5278 | 76.9247 | 175.1308 | 38.8731 | 384.096 | 332.4818 | 614.5998 | 38.7486 | 87.0553 | 15.7825 | 378 | 85.8408 | 0.15351 | 510.7315 | 0.15671
5893 | 1109.4736 | 3.4924 | 106.8552 | 151.9522 | 84.9299 | 17.7008 | 151.8961 | 3.9686 | 21.9166 | 73.1262 | 177.9812 | 39.4627 | 417.2968 | 334.4993 | 593.8019 | 38.9268 | 88.0216 | 15.6201 | 327 | 85.4029 | 0.15266 | 522.6331 | 0.16376
5894 | 1095.2693 | 3.2605 | 106.2518 | 194.0257 | 84.8728 | 15.9398 | 151.23 | 3.7156 | 20.567 | 71.7383 | 180.3985 | 39.4742 | 373.7769 | 331.2991 | 582.3762 | 37.9497 | 87.8128 | 15.8363 | 275 | 88.6244 | 0.15379 | 527.7707 | 0.12793
5895 | 1064.6344 | 3.8703 | 104.7589 | 158.5561 | 85.359 | 12.3342 | 141.1099 | 3.8796 | 18.7905 | 69.2929 | 181.5305 | 39.2741 | 404.074 | 321.3695 | 568.0838 | 35.7676 | 86.7104 | 16.6492 | 277 | 88.6523 | 0.19905 | 511.3913 | 0.074769
5896 | 1022.6955 | 3.1596 | 100.2593 | 132.8456 | 86.815 | 10.7777 | 122.6927 | 2.8807 | 20.1474 | 62.781 | 178.7077 | 33.7495 | 369.7915 | 292.2841 | 525.0997 | 22.5341 | 83.4972 | 16.6519 | 266 | 82.8407 | 0.11878 | 458.758 | 0.064319
5897 | 962.5956 | 2.4104 | 82.3887 | 124.4336 | 88.3788 | 14.705 | 105.3552 | 1.5284 | 14.9419 | 50.2155 | 164.6735 | 28.8285 | 343.8993 | 237.9416 | 453.7304 | 10.7783 | 75.8406 | 16.2124 | 247 | 67.4967 | 0.14381 | 389.1236 | 0.050056
5898 | 904.6307 | 2.138 | 45.0722 | 99.3871 | 100.9418 | 10.5257 | 87.8996 | 1.0906 | 7.7863 | 39.3348 | 133.3989 | 22.853 | 303.0239 | 184.5508 | 374.3786 | 8.5667 | 65.2935 | 13.4372 | 231 | 58.8703 | 0.15349 | 333.9811 | 0.02487
5899 | 879.8133 | 2.7559 | 28.5247 | 100.7233 | 109.6824 | 7.8373 | 72.6134 | 1.1042 | 6.1133 | 41.6801 | 100.3669 | 11.2369 | 251.5526 | 156.6948 | 309.5499 | 8.5365 | 55.7338 | 8.1479 | 205 | 52.2728 | 0.15334 | 292.0265 | 0.002048
5900 | 848.6616 | 3.141 | 28.5247 | 110.3113 | 105.529 | 8.9371 | 67.2727 | 1.5049 | 6.6974 | 48.8736 | 82.5692 | 7.7573 | 220.4718 | 142.5677 | 275.9708 | 8.9031 | 49.9398 | 5.6513 | 198 | 56.5004 | 0.15238 | 267.0913 | 0
5901 | 824.3792 | 3.0284 | 28.4954 | 94.5266 | 97.1209 | 10.1884 | 65.6971 | 1.5801 | 7.8507 | 47.0934 | 75.7745 | 8.5525 | 199.019 | 130.2794 | 270.8515 | 8.8981 | 48.4456 | 5.3447 | 194 | 51.489 | 0.15308 | 256.9448 | 0
5902 | 816.2797 | 3.285 | 28.0309 | 99.5041 | 93.4538 | 9.7158 | 60.2384 | 1.4297 | 7.4306 | 36.9775 | 72.4024 | 8.6094 | 186.7325 | 120.5305 | 267.7218 | 8.9139 | 48.1228 | 5.1043 | 165 | 44.3401 | 0.1533 | 255.9593 | 0
5903 | 806.0181 | 2.1328 | 27.8324 | 107.4248 | 94.5699 | 8.1153 | 60.6474 | 1.4286 | 6.3942 | 28.653 | 70.6493 | 8.566 | 182.3741 | 110.9217 | 262.51 | 8.8678 | 47.6258 | 4.2418 | 156 | 47.9978 | 0.15378 | 263.1874 | 0
5904 | 789.4221 | 1.3269 | 28.1669 | 91.7751 | 96.1142 | 6.2424 | 62.8461 | 1.4304 | 5.8593 | 26.3854 | 70.3247 | 8.3759 | 166.1831 | 102.366 | 262.0255 | 8.8262 | 47.2815 | 3.8677 | 156 | 51.9108 | 0.15452 | 269.9132 | 0
5905 | 779.8706 | 1.2319 | 28.0822 | 106.8375 | 96.1149 | 5.6804 | 59.8613 | 1.4303 | 5.6598 | 26.4419 | 69.883 | 8.2869 | 160.652 | 99.4544 | 258.5922 | 8.8512 | 47.5312 | 3.9082 | 156 | 51.0013 | 0.15274 | 263.4647 | 0
5906 | 779.335 | 1.2825 | 27.8554 | 91.0379 | 95.9386 | 6.4539 | 57.7084 | 1.6689 | 5.749 | 26.2442 | 69.3081 | 8.1034 | 177.9027 | 100.7079 | 253.0833 | 8.9955 | 47.8442 | 3.8351 | 151 | 42.3638 | 0.15424 | 250.0698 | 0
5907 | 776.9984 | 1.4943 | 27.698 | 98.4341 | 96.1622 | 6.6815 | 59.7726 | 1.6123 | 5.7939 | 27.4345 | 69.6629 | 8.0144 | 160.3172 | 102.3375 | 244.4567 | 9.2057 | 47.3503 | 3.3638 | 126 | 44.1973 | 0.15463 | 242.6567 | 0
5908 | 769.5294 | 1.7256 | 27.6931 | 98.4817 | 96.1768 | 7.3114 | 60.218 | 1.4228 | 5.9609 | 34.419 | 70.566 | 7.994 | 163.7216 | 98.8264 | 236.1531 | 8.7482 | 46.8403 | 3.276 | 129 | 44.5479 | 0.15295 | 240.3228 | 0
5909 | 777.846 | 2.4491 | 29.5125 | 100.0941 | 96.8399 | 8.3519 | 57.0186 | 1.4409 | 5.9117 | 40.7644 | 70.6096 | 7.8364 | 167.255 | 94.5994 | 234.9374 | 8.8663 | 47.136 | 3.0991 | 134 | 44.1915 | 0.15401 | 239.2932 | 0
5910 | 795.5598 | 2.5445 | 39.6856 | 115.9218 | 100.5831 | 7.0988 | 57.2914 | 1.3033 | 6.0573 | 34.9747 | 69.217 | 6.1544 | 173.7712 | 91.4827 | 230.5753 | 8.3722 | 47.1641 | 2.8379 | 126 | 44.7787 | 0.15325 | 237.9204 | 0
5911 | 814.8838 | 1.3825 | 50.9721 | 86.6012 | 101.6585 | 8.0727 | 61.9911 | 1.1342 | 5.5462 | 25.2505 | 70.8611 | 6.7477 | 188.6066 | 87.4852 | 231.6704 | 8.1953 | 46.6859 | 2.9933 | 128 | 47.2949 | 0.15343 | 237.5999 | 0.049356
5912 | 836.1606 | 0.95972 | 93.6277 | 107.8559 | 105.0099 | 7.0989 | 61.0913 | 1.0843 | 5.4065 | 22.0634 | 86.5246 | 11.3883 | 163.3121 | 88.3586 | 231.2117 | 8.2277 | 46.6916 | 3.6479 | 140 | 50.0564 | 0.15304 | 240.1606 | 0.118
5913 | 860.4771 | 1.1824 | 55.0455 | 133.022 | 107.6722 | 7.3479 | 57.0133 | 1.3604 | 5.552 | 23.433 | 111.6145 | 13.9262 | 176.6699 | 93.5612 | 233.0071 | 8.3214 | 46.9547 | 5.9387 | 144 | 57.9971 | 0.19862 | 245.7237 | 0.15701
5914 | 865.2175 | 1.1359 | 70.6387 | 108.4121 | 108.9553 | 6.8743 | 58.4573 | 1.2313 | 5.164 | 28.0437 | 126.0429 | 14.2494 | 205.2335 | 100.9877 | 244.8865 | 8.3032 | 47.0089 | 10.3954 | 162 | 54.1829 | 0.11774 | 253.9 | 0.19084
5915 | 862.0481 | 1.3913 | 81.4525 | 139.3611 | 102.4462 | 8.7141 | 57.9661 | 1.0108 | 5.3733 | 33.5657 | 121.7486 | 14.1487 | 190.9828 | 110.5805 | 256.5519 | 8.064 | 47.0497 | 12.2837 | 186 | 61.996 | 0.14274 | 258.0753 | 0.21388
5916 | 853.5719 | 1.686 | 84.3281 | 133.4884 | 93.902 | 8.895 | 62.4667 | 1.006 | 6.6093 | 36.8558 | 112.1644 | 16.0377 | 196.0137 | 117.3087 | 256.0188 | 7.9818 | 47.6384 | 12.2467 | 180 | 60.3006 | 0.15458 | 252.9244 | 0.1702
5917 | 851.4781 | 1.9292 | 78.7853 | 124.8898 | 83.4807 | 7.1601 | 64.0534 | 0.99991 | 6.1889 | 36.7768 | 107.9947 | 17.934 | 202.4689 | 120.6325 | 261.6726 | 8.4771 | 48.0869 | 12.1827 | 191 | 63.0315 | 0.15459 | 244.7812 | 0.20856
5918 | 842.7145 | 1.7727 | 56.5561 | 105.6327 | 82.4003 | 7.3448 | 60.0902 | 0.99766 | 5.4214 | 35.6461 | 102.7235 | 17.357 | 207.295 | 132.7782 | 287.5693 | 8.0969 | 47.3755 | 12.5124 | 176 | 55.4099 | 0.19796 | 246.2098 | 0.24055
5919 | 830.2585 | 1.7152 | 46.2551 | 95.2519 | 92.8186 | 7.5884 | 62.0354 | 0.99318 | 5.1366 | 35.5776 | 97.2731 | 14.6025 | 199.6567 | 141.0233 | 312.2895 | 7.9675 | 46.4891 | 12.7671 | 182 | 55.9429 | 0.15352 | 250.4562 | 0.22315
5920 | 830.4907 | 1.6848 | 46.5033 | 75.2209 | 97.7358 | 6.9342 | 60.5587 | 1.1316 | 5.3055 | 35.7213 | 95.5086 | 7.0414 | 230.3825 | 135.2214 | 297.9104 | 8.0792 | 46.2828 | 12.9368 | 190 | 52.1334 | 0.11911 | 244.4223 | 0.20767
5921 | 826.6027 | 1.4926 | 46.2984 | 108.6237 | 96.7828 | 6.6119 | 57.4044 | 1.2188 | 5.9535 | 32.1502 | 93.0462 | 3.7134 | 206.049 | 131.0685 | 274.8032 | 8.0611 | 46.251 | 11.1353 | 210 | 47.0588 | 0.18792 | 237.809 | 0.15934
5922 | 819.7293 | 1.5536 | 44.878 | 97.0139 | 93.0021 | 6.6677 | 59.912 | 1.1107 | 6.2235 | 29.5941 | 84.8703 | 3.631 | 232.7455 | 124.0022 | 267.6205 | 8.2112 | 46.2339 | 6.655 | 221 | 54.6657 | 0.15352 | 237.2895 | 0.12189
5923 | 806.0663 | 2.8731 | 43.2857 | 70.7951 | 80.9076 | 8.0159 | 68.0653 | 1.0567 | 5.635 | 36.3361 | 75.6568 | 3.6532 | 226.601 | 113.5755 | 263.5784 | 8.0951 | 46.5167 | 4.4585 | 205 | 49.0132 | 0.15352 | 234.4914 | 0.0032538
5924 | 807.0623 | 3.9492 | 42.7012 | 90.4365 | 79.6475 | 7.916 | 74.6327 | 1.3181 | 6.217 | 43.0477 | 74.3908 | 5.3879 | 225.7319 | 110.7642 | 262.2375 | 8.2767 | 47.2129 | 4.0733 | 190 | 53.0862 | 0.1194 | 229.1853 | 0
5925 | 796.8076 | 3.6515 | 42.6662 | 105.4808 | 88.2915 | 7.5763 | 73.816 | 1.4499 | 7.2564 | 39.2354 | 76.1761 | 6.265 | 211.8869 | 110.6909 | 261.4834 | 8.6773 | 47.7861 | 3.4447 | 210 | 57.3003 | 0.14319 | 227.5624 | 0
5926 | 784.1435 | 2.7608 | 41.5998 | 75.5605 | 91.7713 | 8.2994 | 64.698 | 1.4747 | 7.8629 | 31.3551 | 74.5189 | 6.2638 | 232.8982 | 112.3217 | 264.5059 | 8.9068 | 47.9798 | 3.4322 | 188 | 49.6475 | 0.15323 | 226.5921 | 0
5927 | 776.2426 | 1.7381 | 41.0125 | 88.9279 | 95.6639 | 7.8755 | 58.8261 | 1.482 | 6.9982 | 27.6772 | 72.4637 | 6.2703 | 216.7349 | 122.0262 | 265.9049 | 8.6174 | 47.9664 | 3.4518 | 184 | 57.4233 | 0.19827 | 222.469 | 0
5928 | 770.2784 | 1.3528 | 40.2484 | 114.6857 | 101.1753 | 6.8334 | 58.765 | 1.6875 | 6.3029 | 26.3736 | 71.9191 | 6.3234 | 202.1942 | 144.5958 | 262.9222 | 8.4561 | 47.8257 | 3.3002 | 178 | 54.8768 | 0.11782 | 220.22 | 0
5929 | 767.9296 | 1.3101 | 37.4569 | 90.3958 | 100.9446 | 8.7337 | 57.4449 | 1.7048 | 6.1133 | 25.4661 | 72.15 | 6.2609 | 220.5649 | 164.081 | 256.1224 | 8.7067 | 47.8461 | 3.0399 | 186 | 60.1147 | 0.14291 | 223.834 | 0
5930 | 770.5288 | 1.3094 | 34.9686 | 108.1249 | 102.0376 | 7.434 | 58.6189 | 1.5309 | 5.9376 | 25.1313 | 71.9969 | 6.303 | 191.301 | 168.2742 | 247.8542 | 8.5632 | 47.8999 | 2.8437 | 175 | 51.0947 | 0.1543 | 228.7892 | 0
5931 | 760.926 | 1.3977 | 35.4038 | 102.0082 | 101.0276 | 8.0699 | 60.3049 | 1.4718 | 5.7652 | 25.5819 | 72.0264 | 7.1584 | 240.2395 | 167.2643 | 244.2435 | 8.6934 | 47.8372 | 2.7242 | 157 | 51.8659 | 0.19905 | 238.2723 | 0
5932 | 757.8162 | 1.7641 | 38.7838 | 102.8332 | 102.2407 | 7.0911 | 58.5219 | 1.4765 | 5.8205 | 27.2634 | 72.275 | 7.8473 | 185.0316 | 168.6797 | 242.0081 | 9.095 | 47.894 | 2.5975 | 157 | 53.3422 | 0.11804 | 243.405 | 0
5933 | 760.5637 | 2.4675 | 36.0763 | 84.8976 | 99.6589 | 8.7729 | 61.1692 | 1.4254 | 5.9069 | 28.2922 | 70.8662 | 7.7081 | 165.7616 | 160.9677 | 243.3226 | 8.6495 | 47.7989 | 2.4755 | 148 | 43.4158 | 0.14316 | 234.585 | 0
5934 | 772.8228 | 2.2542 | 44.3665 | 94.2251 | 98.3536 | 8.8571 | 59.5391 | 1.212 | 5.7287 | 25.3313 | 68.1999 | 6.2483 | 186.2772 | 131.0651 | 249.1618 | 8.0355 | 47.2419 | 2.4147 | 150 | 44.8084 | 0.15465 | 218.449 | 0
5935 | 798.303 | 1.6476 | 24.399 | 92.8267 | 96.6183 | 7.8202 | 56.2291 | 1.0861 | 5.3806 | 21.3865 | 66.0188 | 5.0962 | 207.4686 | 102.8507 | 244.7314 | 8.0366 | 46.7001 | 2.657 | 138 | 45.1173 | 0.15387 | 203.0928 | 0.14181
5936 | 796.3588 | 1.3827 | 30.4636 | 102.5468 | 96.3596 | 8.204 | 60.3461 | 1.3287 | 5.0808 | 21.9447 | 65.5885 | 5.8601 | 169.6282 | 96.9075 | 236.758 | 8.2802 | 46.8223 | 3.2043 | 152 | 44.4479 | 0.152 | 197.9093 | 0.17076
5937 | 802.6947 | 1.3333 | 34.1343 | 96.7393 | 98.2397 | 7.8619 | 68.3434 | 1.5448 | 4.9725 | 27.7364 | 66.9945 | 7.8378 | 201.9501 | 100.5857 | 236.4109 | 8.1072 | 47.2446 | 5.5937 | 189 | 44.9457 | 0.15321 | 200.6884 | 0.21226
5938 | 829.0751 | 1.8206 | 34.5829 | 94.1316 | 103.1582 | 7.0127 | 74.1916 | 1.6695 | 5.346 | 33.9148 | 69.0727 | 8.7332 | 176.1596 | 112.4406 | 251.5053 | 7.9656 | 47.241 | 10.4826 | 197 | 46.9139 | 0.15564 | 204.417 | 0.2613
5939 | 842.135 | 2.1579 | 34.4925 | 93.869 | 109.5926 | 6.67 | 70.5771 | 1.6545 | 5.8295 | 35.9203 | 73.7951 | 9.0429 | 206.9432 | 131.4319 | 276.8884 | 8.122 | 47.207 | 12.7541 | 209 | 49.0096 | 0.1976 | 209.347 | 0.24308
5940 | 844.8584 | 1.954 | 35.0201 | 81.7576 | 110.0905 | 7.3575 | 63.4892 | 1.308 | 5.837 | 35.7889 | 81.4912 | 8.9428 | 194.151 | 137.3931 | 285.422 | 8.132 | 47.3084 | 13.879 | 212 | 53.425 | 0.15352 | 218.3358 | 0.26112
5941 | 836.3046 | 1.8101 | 35.9124 | 107.8588 | 103.2604 | 7.5337 | 60.2459 | 1.0667 | 5.9821 | 34.9368 | 87.5333 | 7.141 | 200.4241 | 141.0619 | 269.989 | 7.9961 | 46.9973 | 14.562 | 201 | 49.5484 | 0.11878 | 226.411 | 0.26594
5942 | 832.3532 | 2.293 | 36.705 | 102.3272 | 98.4519 | 6.9137 | 61.47 | 1.0264 | 5.7323 | 34.3394 | 91.9511 | 7.8957 | 208.0028 | 148.7217 | 251.6884 | 8.1081 | 46.2164 | 14.5807 | 182 | 58.9008 | 0.18826 | 228.4683 | 0.26744
5943 | 843.2026 | 1.8508 | 37.3921 | 96.8369 | 99.3174 | 6.6371 | 88.1174 | 1.2777 | 5.7831 | 32.9673 | 97.2645 | 8.0493 | 199.3658 | 146.3806 | 263.9337 | 8.1478 | 45.4046 | 14.675 | 172 | 54.6481 | 0.11891 | 226.3496 | 0.22626
5944 | 842.9925 | 2.1943 | 37.7791 | 83.5813 | 100.1102 | 7.3942 | 89.7847 | 1.1878 | 5.4745 | 28.338 | 104.3245 | 6.4996 | 231.3559 | 139.7569 | 284.4469 | 7.9778 | 44.9721 | 14.7506 | 162 | 57.3436 | 0.18813 | 223.8374 | 0.21388
5945 | 842.9637 | 2.0217 | 37.4502 | 97.6687 | 101.9689 | 6.8156 | 73.113 | 1.0178 | 5.496 | 23.6768 | 108.8615 | 7.9659 | 204.0383 | 131.1278 | 298.0446 | 8.1975 | 45.4177 | 12.517 | 175 | 56.0601 | 0.11784 | 222.7517 | 0.18577
5946 | 849.403 | 1.4347 | 36.4743 | 97.8432 | 102.147 | 7.3059 | 62.1291 | 1.0319 | 5.1567 | 22.2306 | 111.6233 | 7.6487 | 224.2833 | 122.9783 | 289.6492 | 8.7139 | 45.743 | 7.8893 | 174 | 55.8968 | 0.14212 | 221.1427 | 0.066566
5947 | 839.6834 | 2.1759 | 35.5396 | 108.5129 | 100.9145 | 7.5833 | 55.7695 | 1.0911 | 5.1482 | 23.4774 | 117.0656 | 5.0007 | 197.8378 | 120.531 | 274.5774 | 8.2632 | 45.1704 | 5.5241 | 165 | 53.8931 | 0.1543 | 221.9886 | 0.01019
5948 | 815.7691 | 3.2578 | 35.3622 | 87.3616 | 94.7834 | 7.0203 | 56.0679 | 1.3194 | 5.1792 | 25.5562 | 114.4339 | 5.0528 | 235.2093 | 118.9981 | 264.205 | 8.2069 | 44.9859 | 4.8314 | 153 | 51.1224 | 0.19981 | 227.1924 | 0
5949 | 794.8175 | 3.6088 | 35.1512 | 96.7523 | 80.2467 | 8.7867 | 59.1547 | 1.492 | 5.4361 | 26.1088 | 99.4986 | 6.0344 | 181.9479 | 114.8201 | 249.6594 | 8.33 | 45.3045 | 3.9307 | 146 | 51.5306 | 0.15352 | 229.9147 | 0
5950 | 796.9103 | 3.0249 | 34.7463 | 96.4385 | 78.4678 | 9.5262 | 62.2116 | 1.6797 | 5.8022 | 25.7755 | 85.6134 | 6.1128 | 198.146 | 108.3286 | 235.5035 | 8.352 | 45.9398 | 3.7487 | 148 | 47.3662 | 0.15352 | 226.4309 | 0
5951 | 790.8166 | 1.8788 | 34.3172 | 106.5118 | 88.5243 | 7.3131 | 60.2078 | 1.7165 | 5.8334 | 26.3875 | 79.558 | 5.8919 | 204.609 | 105.791 | 234.9446 | 8.7155 | 46.7743 | 3.7139 | 135 | 45.8859 | 0.11814 | 221.1767 | 0
5952 | 788.2359 | 1.2511 | 33.971 | 99.6441 | 92.3836 | 7.3434 | 58.3568 | 1.5899 | 5.9838 | 26.2245 | 77.8977 | 6.0572 | 195.5273 | 101.8333 | 245.4837 | 8.8823 | 47.1316 | 3.5544 | 131 | 42.4425 | 0.14422 | 219.3475 | 0
5953 | 784.6904 | 1.2865 | 33.668 | 54.5943 | 88.0628 | 6.9031 | 58.6596 | 1.5364 | 5.9629 | 25.1386 | 77.6901 | 5.9492 | 192.751 | 93.7773 | 252.6856 | 8.6323 | 47.0869 | 3.3828 | 136 | 48.6653 | 0.15351 | 218.428 | 0
5954 | 780.1179 | 1.3505 | 78.4309 | 84.6624 | 77.6604 | 8.083 | 59.2686 | 1.5547 | 6.018 | 24.6975 | 77.655 | 6.2023 | 189.7625 | 91.2609 | 253.2404 | 8.5827 | 47.0714 | 3.1174 | 138 | 45.8947 | 0.15354 | 216.1387 | 0
5955 | 782.4997 | 1.2412 | 50.1728 | 50.853 | 74.4513 | 7.1963 | 61.418 | 1.5814 | 6.1965 | 26.3295 | 77.0035 | 6.1248 | 189.9697 | 91.5656 | 244.7435 | 8.5931 | 47.1105 | 2.8638 | 121 | 44.0314 | 0.19818 | 216.3302 | 0
5956 | 783.8671 | 1.7221 | 59.7652 | 84.8009 | 72.9023 | 8.014 | 66.4087 | 1.5818 | 6.3062 | 33.5654 | 76.2737 | 6.2431 | 176.9513 | 90.4662 | 232.307 | 8.7897 | 47.007 | 2.7401 | 111 | 44.7559 | 0.11855 | 230.5623 | 0
5957 | 791.3099 | 2.8635 | 65.7985 | 73.4269 | 70.3642 | 9.8923 | 73.1249 | 1.5491 | 6.1114 | 39.7365 | 77.097 | 7.9593 | 202.9052 | 91.1774 | 231.7403 | 9.3549 | 46.8832 | 2.6811 | 117 | 44.5465 | 0.14249 | 253.0882 | 0
5958 | 837.5927 | 3.7874 | 67.2262 | 57.9634 | 60.1933 | 13.4042 | 82.3383 | 1.8438 | 5.9075 | 38.1159 | 91.1469 | 13.4992 | 190.5379 | 121.4719 | 243.5063 | 12.2526 | 47.1028 | 3.2795 | 177 | 49.7238 | 0.1554 | 289.1747 | 0
5959 | 919.0169 | 3.8603 | 67.3768 | 114.8048 | 54.9069 | 18.592 | 92.3855 | 3.1217 | 8.1342 | 44.9573 | 118.8114 | 29.0311 | 218.367 | 192.2353 | 293.1152 | 25.5263 | 50.1946 | 8.5713 | 267 | 58.2502 | 0.15416 | 356.9159 | 0.20408
5960 | 1014.521 | 8.1344 | 66.4723 | 167.0186 | 63.1469 | 19.0728 | 117.1013 | 5.4732 | 14.1184 | 63.4377 | 144.6855 | 39.9046 | 248.4474 | 261.8526 | 379.067 | 35.3563 | 58.5933 | 14.7855 | 275 | 65.6978 | 0.15252 | 444.253 | 0.28031
5961 | 1075.6884 | 12.9259 | 66.7378 | 153.1958 | 66.262 | 19.7436 | 137.2132 | 7.0062 | 22.67 | 75.4432 | 163.5839 | 44.2254 | 318.6498 | 303.0452 | 481.8702 | 39.5978 | 68.383 | 15.6176 | 306 | 79.8344 | 0.1536 | 510.3094 | 0.31874
5962 | 1105.8526 | 12.9375 | 66.0574 | 194.7792 | 71.2182 | 18.287 | 145.7954 | 6.7476 | 26.1867 | 77.0384 | 172.8936 | 46.404 | 326.5153 | 328.5416 | 561.0247 | 41.4908 | 77.4095 | 15.5135 | 357 | 87.8258 | 0.15271 | 530.0883 | 0.29925
5963 | 1145.7618 | 11.4607 | 66.2475 | 168.0763 | 79.1435 | 17.3075 | 154.2719 | 5.2442 | 26.5737 | 76.8677 | 175.034 | 45.2389 | 376.5172 | 348.1964 | 600.7322 | 38.7097 | 87.1327 | 17.8686 | 328 | 93.0183 | 0.19873 | 536.6326 | 0.27678
5964 | 1154.828 | 7.0959 | 66.439 | 190.6585 | 87.9068 | 18.6225 | 155.9599 | 4.1864 | 23.256 | 75.295 | 176.8305 | 44.0738 | 377.0018 | 353.6339 | 608.5995 | 38.0978 | 92.4008 | 17.6303 | 415 | 99.1313 | 0.1183 | 545.857 | 0.28449
5965 | 1157.3984 | 4.2028 | 90.3498 | 197.7908 | 102.3762 | 18.3956 | 158.8976 | 3.9526 | 18.963 | 77.3763 | 179.6745 | 42.5586 | 367.0207 | 351.1363 | 593.5695 | 38.8832 | 91.3902 | 17.1118 | 302 | 100.5066 | 0.14394 | 550.5461 | 0.29773
5966 | 1136.208 | 3.8951 | 66.6044 | 197.9124 | 120.1388 | 17.9111 | 158.8855 | 4.0919 | 22.489 | 82.6234 | 184.4581 | 40.0387 | 398.5016 | 350.7583 | 581.6515 | 38.7422 | 88.2783 | 17.3604 | 281 | 102.4217 | 0.15181 | 555.6159 | 0.29883
5967 | 1117.6061 | 4.2765 | 49.7048 | 189.813 | 123.3217 | 14.6823 | 144.5257 | 3.7142 | 24.5512 | 75.2927 | 187.0165 | 39.1821 | 375.1032 | 342.1555 | 574.6148 | 38.0327 | 85.2154 | 17.3881 | 270 | 91.0945 | 0.15481 | 547.586 | 0.29268
5968 | 1081.3023 | 4.0336 | 60.362 | 180.7227 | 112.6182 | 9.7792 | 134.9754 | 3.1035 | 22.3641 | 57.8656 | 182.992 | 35.5993 | 392.7235 | 317.905 | 541.948 | 31.0608 | 82.1492 | 16.865 | 263 | 91.3777 | 0.15378 | 502.9706 | 0.22284
5969 | 1018.5994 | 3.4278 | 66.4249 | 161.8904 | 103.992 | 9.2607 | 139.3231 | 2.4222 | 18.8733 | 44.3708 | 169.6638 | 32.126 | 334.1302 | 267.511 | 464.3662 | 17.4087 | 76.9968 | 16.4395 | 246 | 85.9168 | 0.19849 | 429.313 | 0.18694
5970 | 964.5199 | 2.734 | 66.3154 | 156.4996 | 104.3148 | 8.7476 | 122.3066 | 1.9591 | 16.1574 | 38.0928 | 141.346 | 26.7334 | 305.4087 | 199.2817 | 381.5328 | 9.8594 | 70.3694 | 13.6811 | 238 | 77.6772 | 0.11787 | 363.3091 | 0.032187
5971 | 919.4953 | 2.7015 | 66.9139 | 116.6601 | 103.8048 | 8.5999 | 83.2886 | 1.4755 | 9.321 | 40.2948 | 112.2534 | 17.1329 | 332.1269 | 154.8397 | 336.5706 | 9.4038 | 65.5541 | 8.8224 | 208 | 62.8777 | 0.14439 | 314.1193 | 0
5972 | 881.3637 | 3.5323 | 89.9005 | 78.245 | 100.0238 | 7.8279 | 66.893 | 1.3277 | 6.028 | 46.1418 | 100.3477 | 11.7877 | 221.56 | 139.8226 | 303.4771 | 9.5613 | 61.208 | 6.6294 | 200 | 60.2148 | 0.15339 | 280.9689 | 0
5973 | 849.7272 | 3.5095 | 49.3366 | 42.6214 | 91.5695 | 8.2876 | 69.5982 | 1.4173 | 6.2492 | 40.7616 | 96.5215 | 10.4439 | 276.8807 | 131.4025 | 261.9045 | 9.9754 | 57.073 | 5.688 | 199 | 58.0053 | 0.15349 | 269.801 | 0
5974 | 836.8004 | 2.8922 | 59.6987 | 80.4384 | 92.7277 | 7.8177 | 64.3356 | 1.4079 | 6.7808 | 29.3184 | 87.3415 | 15.9523 | 186.8995 | 124.8144 | 234.636 | 9.6565 | 56.1462 | 5.2746 | 168 | 56.1073 | 0.15239 | 267.6749 | 0
5975 | 825.4362 | 1.8818 | 66.8731 | 44.2269 | 94.4847 | 8.3094 | 66.3208 | 1.6736 | 6.4523 | 24.4064 | 77.7594 | 17.1363 | 223.1941 | 120.5167 | 232.9209 | 9.618 | 57.0708 | 4.7 | 138 | 54.5907 | 0.15367 | 265.4277 | 0
5976 | 813.953 | 1.3263 | 90.504 | 60.8044 | 90.7346 | 8.5904 | 70.8636 | 1.6236 | 6.135 | 23.8015 | 74.2848 | 14.2321 | 227.2788 | 117.2274 | 230.9264 | 9.8262 | 58.1344 | 4.0889 | 136 | 56.493 | 0.13377 | 264.6168 | 0
5977 | 811.5321 | 1.3581 | 49.0039 | 77.4393 | 88.0791 | 7.8136 | 67.623 | 1.4422 | 6.0362 | 23.097 | 73.7856 | 10.9262 | 175.742 | 112.3553 | 227.5294 | 9.5955 | 56.7992 | 3.5905 | 131 | 51.5726 | 0.067627 | 265.2703 | 0
5978 | 799.4556 | 1.4954 | 60.8822 | 65.5975 | 85.9302 | 7.6518 | 60.6418 | 1.465 | 6.2825 | 22.2553 | 73.6047 | 10.7605 | 218.0545 | 103.3725 | 229.5706 | 9.61 | 53.1461 | 3.4024 | 134 | 54.1112 | 0.10805 | 266.1713 | 0
5979 | 792.162 | 1.3133 | 66.5681 | 37.0844 | 85.1844 | 7.5739 | 58.7542 | 1.4574 | 6.3259 | 23.5167 | 73.3147 | 12.2345 | 205.258 | 95.5691 | 233.1394 | 9.6215 | 51.9931 | 3.3875 | 137 | 52.4698 | 0.067888 | 266.6215 | 0
5980 | 796.8124 | 1.6537 | 66.8567 | 76.6548 | 83.5534 | 9.0432 | 63.9551 | 1.4685 | 6.0553 | 30.2417 | 73.0762 | 9.4551 | 188.8517 | 93.9812 | 234.5884 | 9.7508 | 53.0832 | 3.3706 | 133 | 52.1692 | 0.082357 | 272.4157 | 0
5981 | 807.3954 | 2.7497 | 66.8419 | 70.6542 | 81.9241 | 10.2636 | 63.852 | 1.4725 | 5.9299 | 35.9127 | 73.2461 | 9.3903 | 199.8698 | 95.8954 | 241.2177 | 9.5528 | 53.334 | 3.4163 | 142 | 51.4921 | 0.088083 | 290.5093 | 0
5982 | 843.264 | 3.889 | 66.4109 | 85.4078 | 78.1883 | 12.526 | 74.1532 | 1.5192 | 5.7662 | 33.9788 | 82.8913 | 18.7453 | 225.1174 | 122.7623 | 255.6709 | 13.1215 | 54.2038 | 3.2098 | 197 | 56.5362 | 0.087443 | 331.8611 | 0
5983 | 906.6999 | 4.1444 | 66.4898 | 94.8843 | 71.1769 | 17.5473 | 96.0736 | 2.7561 | 5.2475 | 41.5686 | 108.7677 | 30.6239 | 209.5622 | 182.8115 | 305.2794 | 25.6835 | 59.5354 | 8.4777 | 282 | 58.7134 | 0.087819 | 386.8299 | 0.057152
5984 | 985.9348 | 6.0853 | 89.7766 | 155.1207 | 70.8796 | 18.8548 | 124.2616 | 4.2821 | 9.9232 | 60.5868 | 140.5049 | 32.7657 | 265.0966 | 248.6953 | 398.9988 | 35.1029 | 70.0594 | 13.2656 | 282 | 72.2709 | 0.08756 | 453.311 | 0.25553
5985 | 1057.3763 | 8.5955 | 49.746 | 182.6735 | 73.6023 | 17.7859 | 150.1041 | 4.5023 | 19.411 | 73.2744 | 164.0826 | 33.3043 | 336.3328 | 302.3553 | 490.9524 | 38.4114 | 79.3904 | 15.143 | 353 | 76.3864 | 0.11373 | 518.8541 | 0.24972
5986 | 1113.1539 | 12.7579 | 83.458 | 187.5658 | 49.019 | 17.0415 | 160.0194 | 4.0307 | 24.5642 | 77.8883 | 176.7985 | 35.7613 | 393.6638 | 334.9291 | 564.9216 | 40.1148 | 82.7989 | 17.1882 | 374 | 91.7149 | 0.08784 | 540.3083 | 0.27343
5987 | 1141.244 | 16.9762 | 49.5405 | 191.583 | 30.3391 | 16.3904 | 162.7603 | 4.0062 | 25.8935 | 84.4137 | 182.0239 | 36.9189 | 406.5042 | 353.0543 | 603.7033 | 40.3124 | 83.896 | 18.2343 | 353 | 93.5718 | 0.06805 | 535.0451 | 0.25992
5988 | 1125.8208 | 13.9451 | 88.341 | 206.7759 | 27.8251 | 18.7707 | 159.8449 | 4.0885 | 21.6374 | 84.9364 | 181.8202 | 38.6071 | 438.3122 | 364.3213 | 617.4273 | 39.879 | 84.7264 | 18.1255 | 376 | 84.7684 | 0.019797 | 539.0716 | 0.23543
5989 | 1125.1423 | 7.3782 | 109.1297 | 171.1457 | 31.2023 | 17.1246 | 164.5489 | 4.2895 | 19.4098 | 79.8945 | 184.7092 | 40.8504 | 409.8053 | 366.8879 | 623.3126 | 40.6365 | 85.6573 | 17.184 | 309 | 82.1027 | 0 | 549.4104 | 0.26163
5990 | 1126.349 | 4.163 | 108.8125 | 152.4053 | 75.5501 | 16.9166 | 174.5787 | 4.6538 | 26.2598 | 79.8531 | 191.5837 | 41.0859 | 410.4733 | 364.1381 | 626.3173 | 41.0881 | 87.0873 | 16.5498 | 293 | 91.6787 | 0 | 553.8532 | 0.28191
5991 | 1071.1404 | 4.1108 | 106.9973 | 147.219 | 122.2638 | 15.0503 | 172.7105 | 4.1975 | 28.3115 | 73.4143 | 192.5145 | 39.6594 | 411.139 | 356.5231 | 628.7328 | 38.6891 | 87.3379 | 16.6481 | 305 | 80.2347 | 0 | 539.2007 | 0.27971
5992 | 1026.3012 | 3.872 | 104.3124 | 139.5377 | 112.3095 | 17.0259 | 149.204 | 3.9468 | 20.3853 | 62.4536 | 187.473 | 37.4735 | 431.9008 | 332.2721 | 593.2788 | 30.1547 | 84.3361 | 16.5112 | 262 | 76.3204 | 0 | 488.1397 | 0.20172
5993 | 978.5863 | 2.9201 | 99.1232 | 136.6377 | 94.6457 | 14.617 | 123.9111 | 3.7898 | 16.0705 | 52.4818 | 175.6581 | 35.1737 | 341.7019 | 281.7736 | 491.7998 | 16.6736 | 77.4325 | 16.4409 | 258 | 68.6573 | 0 | 416.1801 | 0.074882
5994 | 942.6675 | 1.8434 | 94.6702 | 156.4822 | 91.3336 | 11.1745 | 106.7224 | 3.0502 | 16.1375 | 44.409 | 148.311 | 28.1179 | 312.9361 | 224.3552 | 383.4441 | 10.2817 | 70.7328 | 13.8737 | 266 | 64.0228 | 0 | 353.7134 | 0.016802
5995 | 914.7625 | 3.0766 | 74.1985 | 131.4722 | 83.9788 | 8.3394 | 80.1782 | 2.722 | 15.4915 | 43.7482 | 119.2668 | 13.21 | 291.817 | 185.0165 | 326.7487 | 9.5982 | 65.9939 | 8.2387 | 260 | 58.2471 | 0 | 312.8133 | 0
5996 | 878.1709 | 4.0196 | 35.9965 | 92.8836 | 86.7172 | 8.9673 | 66.2164 | 2.5485 | 10.9752 | 48.0631 | 108.7517 | 8.1237 | 300.7768 | 166.9736 | 299.3789 | 9.5964 | 60.4822 | 5.2446 | 227 | 51.9971 | 0 | 292.2291 | 0
5997 | 843.8912 | 3.5118 | 21.0228 | 76.3089 | 96.0148 | 7.3829 | 65.1942 | 2.2545 | 8.555 | 43.6685 | 107.7466 | 8.5662 | 256.4134 | 160.2334 | 282.3362 | 9.7877 | 53.3411 | 4.2964 | 210 | 53.5054 | 0 | 281.2002 | 0
5998 | 812.0117 | 2.6261 | 20.9754 | 86.1708 | 95.6348 | 6.6827 | 64.668 | 2.3197 | 7.2893 | 31.526 | 101.1045 | 8.3353 | 234.5001 | 150.2634 | 264.1039 | 9.5139 | 47.4144 | 3.7844 | 175 | 52.3943 | 0 | 272.6477 | 0
5999 | 793.1157 | 1.6676 | 21.2371 | 97.5187 | 94.8 | 7.2426 | 64.9398 | 2.1195 | 6.0891 | 24.7354 | 91.5842 | 8.1363 | 222.9961 | 135.4214 | 253.8376 | 9.7203 | 45.4708 | 3.4337 | 164 | 51.3596 | 0 | 264.1726 | 0
6000 | 800.0228 | 1.215 | 21.2907 | 103.6548 | 94.774 | 7.686 | 60.6247 | 1.5924 | 5.7125 | 22.8148 | 86.6152 | 8.0465 | 201.1361 | 127.0261 | 246.7581 | 9.6603 | 46.2583 | 3.3789 | 147 | 50.339 | 0 | 261.0074 | 0
6001 | 811.577 | 1.1224 | 21.0019 | 103.4889 | 96.118 | 6.8347 | 58.8495 | 1.3362 | 5.87 | 21.7637 | 83.9939 | 8.0742 | 212.9532 | 125.4756 | 241.8829 | 9.5348 | 47.5665 | 3.9494 | 140 | 52.6528 | 0 | 262.804 | 0
6002 | 808.5678 | 1.2115 | 21.048 | 70.9738 | 95.779 | 7.3886 | 61.7675 | 1.3436 | 5.7849 | 21.052 | 81.1755 | 10.362 | 247.1748 | 125.5375 | 242.8894 | 9.7336 | 49.4709 | 3.8616 | 148 | 50.1297 | 0 | 260.8728 | 0
6003 | 810.4275 | 1.184 | 22.2363 | 30.7269 | 95.6246 | 7.6531 | 62.0163 | 1.5397 | 5.797 | 22.2012 | 79.4919 | 16.1217 | 216.2501 | 123.6657 | 247.7966 | 9.6478 | 49.6875 | 3.5468 | 139 | 48.5242 | 0 | 256.5505 | 0
6004 | 824.2431 | 1.7128 | 26.4119 | 59.8464 | 96.2482 | 7.5856 | 62.2379 | 1.477 | 5.7659 | 28.7017 | 79.0368 | 16.0232 | 196.5637 | 118.8751 | 246.2112 | 9.5429 | 48.7531 | 3.1645 | 129 | 46.9248 | 0 | 256.8948 | 0
6005 | 835.6678 | 2.6859 | 32.1377 | 66.3981 | 97.6062 | 6.8884 | 61.0175 | 1.3384 | 5.7805 | 34.8789 | 79.42 | 12.1502 | 232.8921 | 117.2723 | 238.368 | 9.5451 | 48.6187 | 2.8347 | 134 | 47.13 | 0 | 269.6413 | 0
6006 | 885.3838 | 5.3215 | 48.8309 | 85.5373 | 92.7813 | 11.6247 | 70.8058 | 1.2392 | 5.8891 | 34.7515 | 87.8842 | 17.4564 | 215.1611 | 137.3881 | 246.5089 | 13.1048 | 48.6793 | 2.6704 | 201 | 57.1462 | 0 | 306.4111 | 0
6007 | 978.9551 | 9.134 | 79.5471 | 120.8272 | 88.3106 | 16.8323 | 106.6592 | 2.1399 | 11.0455 | 44.7233 | 113.5153 | 31.6719 | 241.2098 | 192.4874 | 306.9694 | 26.326 | 53.664 | 8.3415 | 263 | 61.957 | 0 | 361.4701 | 0.0121
6008 | 1067.6967 | 8.9393 | 99.5441 | 160.4535 | 91.205 | 16.5746 | 145.2295 | 3.6063 | 17.2951 | 64.6597 | 147.7928 | 38.8994 | 288.1162 | 264.1917 | 420.7418 | 35.6344 | 63.7197 | 13.2367 | 288 | 74.0414 | 0 | 427.9128 | 0.042523
6009 | 1139.3012 | 4.993 | 109.5932 | 202.7116 | 91.2129 | 15.3607 | 165.9961 | 4.6221 | 23.5259 | 75.502 | 174.0851 | 41.4201 | 339.4992 | 320.0464 | 530.2441 | 40.0116 | 72.9494 | 14.4037 | 390 | 82.3632 | 0 | 497.4783 | 0.06324
6010 | 1188.5592 | 3.4137 | 111.2675 | 174.1498 | 90.3456 | 17.4289 | 170.4202 | 5.2234 | 26.3105 | 81.301 | 187.357 | 42.8708 | 362.0335 | 350.7758 | 610.8887 | 40.8498 | 81.289 | 15.9878 | 359 | 93.1144 | 0 | 535.7611 | 0.073478
6011 | 1197.0746 | 2.8634 | 113.679 | 210.7509 | 94.4877 | 19.3477 | 170.7416 | 5.1304 | 26.5112 | 87.4645 | 191.3637 | 40.0448 | 474.5639 | 370.8299 | 650.9316 | 40.5853 | 87.4517 | 15.774 | 341 | 102.1544 | 0 | 542.4535 | 0.06271
6012 | 1202.0874 | 4.3269 | 116.2692 | 172.1559 | 99.1906 | 19.2214 | 173.0453 | 5.029 | 24.8566 | 85.1208 | 191.6295 | 39.6468 | 405.1376 | 382.5698 | 653.5118 | 41.4566 | 87.4208 | 16.095 | 354 | 96.9362 | 0 | 550.6668 | 0.053068
6013 | 1209.4589 | 8.5353 | 159.3067 | 112.584 | 98.4362 | 22.6925 | 176.8109 | 4.4503 | 23.4374 | 80.1769 | 197.6947 | 38.8065 | 392.0692 | 390.0466 | 651.4334 | 41.7807 | 86.0484 | 17.616 | 316 | 94.0879 | 0 | 559.0069 | 0.098471
6014 | 1217.0226 | 13.5711 | 85.6552 | 187.2392 | 101.78 | 22.0158 | 173.6282 | 3.8663 | 22.9357 | 79.2827 | 204.9386 | 36.0971 | 365.2154 | 390.9559 | 649.5977 | 41.1132 | 87.3442 | 18.1783 | 285 | 94.2258 | 0 | 553.6018 | 0.10489
6015 | 1179.7658 | 11.3638 | 103.2054 | 163.2324 | 110.2836 | 15.6261 | 159.0704 | 3.8649 | 22.1462 | 74.8693 | 202.9436 | 31.4067 | 413.0132 | 376.3979 | 632.7662 | 39.0303 | 88.3626 | 18.2052 | 285 | 92.9872 | 0 | 548.2755 | 0.081102
6016 | 1123.0361 | 5.2699 | 110.4585 | 141.8859 | 106.0569 | 16.9424 | 137.7555 | 3.5159 | 19.6583 | 69.1859 | 194.8662 | 29.4273 | 367.6614 | 347.6827 | 585.7483 | 31.0603 | 87.5872 | 17.795 | 258 | 84.2736 | 0 | 517.5105 | 0.11309
6017 | 1056.145 | 2.962 | 104.1954 | 127.9894 | 102.4875 | 15.9036 | 120.0655 | 2.679 | 17.9229 | 60.8121 | 177.6415 | 27.1501 | 383.747 | 290.203 | 506.6078 | 17.4479 | 83.0314 | 17.0353 | 250 | 68.2099 | 0 | 442.1596 | 0.063068
6018 | 987.0405 | 2.3881 | 100.4446 | 114.1355 | 104.3848 | 12.308 | 105.478 | 2.1634 | 14.6563 | 53.369 | 147.1644 | 21.4459 | 335.3959 | 216.8425 | 428.9136 | 10.1215 | 74.0206 | 14.393 | 240 | 64.973 | 0 | 369.08 | 0.010004
6019 | 932.0402 | 2.8355 | 86.6339 | 123.3626 | 108.5949 | 8.008 | 81.7933 | 2.1892 | 10.8094 | 53.8772 | 119.7732 | 11.3378 | 300.2516 | 168.4975 | 374.5983 | 9.4726 | 63.495 | 9.6451 | 220 | 61.5463 | 0 | 316.1179 | 0
6020 | 903.8956 | 3.4705 | 47.5429 | 79.7721 | 107.9394 | 7.338 | 67.2952 | 2.2029 | 8.9106 | 52.9934 | 110.6079 | 8.2593 | 272.2866 | 146.2113 | 336.6354 | 10.2071 | 54.3552 | 7.3023 | 210 | 62.2152 | 0 | 279.8553 | 0
6021 | 887.9208 | 3.9216 | 29.1131 | 94.1353 | 106.597 | 7.6046 | 64.134 | 2.189 | 9.1487 | 42.4265 | 108.4713 | 8.835 | 237.6191 | 133.7922 | 299.7504 | 9.9149 | 50.3259 | 6.4659 | 195 | 55.3274 | 0 | 263.3567 | 0
6022 | 866.0686 | 3.2047 | 27.6728 | 80.707 | 104.4474 | 8.2488 | 61.5293 | 2.2148 | 8.9767 | 30.6368 | 101.153 | 8.3248 | 262.1865 | 124.1153 | 269.2792 | 9.6646 | 49.9577 | 5.7664 | 178 | 59.0203 | 0 | 255.7414 | 0
6023 | 839.6551 | 1.8733 | 27.3802 | 72.4313 | 105.4701 | 7.1465 | 62.5347 | 2.2545 | 7.2865 | 26.2191 | 92.7225 | 7.9563 | 208.648 | 114.9295 | 249.3914 | 9.9374 | 49.7359 | 4.822 | 159 | 56.1538 | 0 | 249.4108 | 0
6024 | 829.1694 | 1.3625 | 27.1574 | 52.5654 | 105.7465 | 7.3759 | 64.7173 | 2.5035 | 6.0975 | 24.4488 | 87.9279 | 7.8764 | 275.6425 | 109.1656 | 240.7688 | 9.7898 | 49.0275 | 3.596 | 147 | 55.6865 | 0 | 244.9711 | 0
6025 | 834.5304 | 1.3889 | 27.0283 | 87.5832 | 104.0895 | 9.0223 | 64.1399 | 2.3972 | 5.6815 | 23.0153 | 85.4481 | 8.1426 | 224.8443 | 106.2794 | 242.8434 | 9.6703 | 49.3089 | 3.0722 | 149 | 52.421 | 0 | 243.6821 | 0
6026 | 838.9267 | 1.2485 | 27.0476 | 56.4393 | 104.8451 | 7.4472 | 61.45 | 2.2391 | 5.5589 | 22.5534 | 83.7524 | 9.8858 | 247.1446 | 103.9469 | 245.0311 | 9.7013 | 51.3759 | 2.8244 | 140 | 57.5982 | 0 | 242.5935 | 0
6027 | 833.0732 | 1.2594 | 28.4139 | 73.8652 | 104.3982 | 7.9871 | 61.9414 | 1.7783 | 5.7096 | 24.2096 | 82.446 | 14.5912 | 220.2121 | 101.1008 | 237.699 | 9.7839 | 52.5223 | 2.6748 | 140 | 55.3268 | 0 | 240.5827 | 0
6028 | 829.9123 | 1.6684 | 101.9913 | 91.3826 | 103.5899 | 10.0317 | 61.2344 | 1.3532 | 5.8506 | 30.9137 | 81.7402 | 14.6606 | 230.0773 | 96.1432 | 234.0916 | 9.8432 | 52.483 | 2.6585 | 137 | 54.1823 | 0 | 240.2518 | 0
6029 | 848.9465 | 2.9021 | 67.8622 | 74.5514 | 104.8286 | 9.0615 | 62.8231 | 1.2713 | 5.8425 | 37.3102 | 82.7112 | 12.0543 | 284.4289 | 94.4128 | 231.627 | 9.6819 | 51.2126 | 2.7485 | 149 | 50.7354 | 0 | 251.8333 | 0
6030 | 880.2861 | 4.3973 | 114.6049 | 107.4329 | 103.6885 | 10.6141 | 75.3038 | 1.3618 | 6.2414 | 39.3837 | 95.8122 | 17.4014 | 254.9796 | 124.3508 | 243.8097 | 13.2606 | 48.5275 | 3.2456 | 206 | 62.8719 | 0 | 288.0698 | 0
6031 | 961.907 | 3.8855 | 66.9903 | 138.6126 | 100.5997 | 14.1134 | 105.5751 | 2.5652 | 8.327 | 49.4941 | 124.1548 | 24.708 | 249.5002 | 191.3116 | 303.4708 | 25.0571 | 49.3006 | 9.0538 | 312 | 69.2116 | 0 | 346.7337 | 0.039629
6032 | 1061.7866 | 5.5159 | 82.3295 | 195.7828 | 99.4638 | 15.9181 | 138.9394 | 4.0972 | 12.8435 | 67.656 | 155.8217 | 26.6605 | 298.5507 | 261.8284 | 403.4009 | 34.361 | 58.5289 | 14.1115 | 322 | 78.6176 | 0 | 419.2885 | 0.073446
6033 | 1124.97 | 6.8933 | 91.6343 | 209.8328 | 103.8436 | 15.512 | 160.891 | 4.4726 | 17.3043 | 80.1644 | 178.6094 | 28.9888 | 398.9464 | 311.3909 | 494.3516 | 38.6949 | 71.747 | 15.4455 | 373 | 81.1409 | 0 | 483.1346 | 0.12005
6034 | 1166.7922 | 6.881 | 91.6974 | 186.0582 | 111.4563 | 15.2625 | 174.7837 | 3.8914 | 21.2015 | 85.5537 | 187.4751 | 33.7841 | 368.5196 | 339.5285 | 553.0451 | 41.7472 | 80.1017 | 15.9431 | 418 | 88.405 | 0 | 524.2178 | 0.15176
6035 | 1206.9371 | 6.5979 | 91.3119 | 222.781 | 117.9874 | 15.8603 | 183.1508 | 3.5776 | 24.5672 | 90.061 | 188.0193 | 35.5851 | 358.6018 | 356.0099 | 582.7923 | 40.2996 | 82.658 | 16.5795 | 410 | 97.9309 | 0 | 548.3353 | 0.10807
6036 | 1211.4394 | 7.4103 | 123.4513 | 283.8961 | 120.0602 | 17.5192 | 186.0774 | 3.5674 | 23.003 | 89.8313 | 188.6782 | 35.895 | 339.5102 | 364.6052 | 587.7283 | 21.4419 | 83.1821 | 16.8486 | 385 | 92.4914 | 0 | 558.6487 | 0.15371
6037 | 1203.1011 | 8.0956 | 67.6247 | 157.444 | 120.3112 | 18.0375 | 186.4953 | 3.5498 | 21.8797 | 83.9812 | 192.0927 | 36.0952 | 546.9037 | 367.109 | 583.9406 | 53.5378 | 83.1778 | 16.8691 | 318 | 89.5969 | 0 | 561.204 | 0.22902
6038 | 1206.167 | 8.5362 | 98.4703 | 173.9642 | 123.8128 | 16.6415 | 186.0694 | 3.4179 | 22.025 | 79.6444 | 193.4446 | 35.5756 | 233.7315 | 365.2782 | 584.6792 | 45.657 | 82.3987 | 17.0432 | 299 | 94.2963 | 0 | 557.7425 | 0.19044
6039 | 1165.2789 | 6.212 | 113.7392 | 223.0114 | 127.9728 | 14.098 | 182.8986 | 3.7173 | 23.7507 | 73.5055 | 192.7999 | 34.2811 | 321.4876 | 354.2983 | 577.1438 | 38.6619 | 81.2278 | 16.6837 | 289 | 91.1592 | 0 | 541.9095 | 0.20809
6040 | 1125.7687 | 3.9811 | 111.6807 | 183.9933 | 129.3459 | 11.1772 | 157.3407 | 3.1846 | 18.4465 | 63.1029 | 191.4911 | 32.7455 | 340.2654 | 334.2601 | 549.0446 | 30.7023 | 79.3466 | 15.4869 | 254 | 81.9186 | 0 | 492.8035 | 0.10685
6041 | 1069.764 | 3.3562 | 106.479 | 178.1793 | 125.4792 | 10.484 | 131.1953 | 2.3418 | 11.6775 | 53.259 | 179.5654 | 25.7295 | 358.2496 | 282.2591 | 475.7885 | 17.4015 | 73.5897 | 14.491 | 253 | 71.7663 | 0 | 416.2039 | 0.14649
6042 | 1007.699 | 2.591 | 97.1782 | 169.0485 | 120.5912 | 8.9899 | 118.1443 | 1.8949 | 10.0545 | 50.7215 | 148.7741 | 19.0078 | 337.1002 | 206.564 | 388.9526 | 10.5325 | 65.1788 | 11.7744 | 229 | 55.5606 | 0 | 346.3483 | 0.1217
6043 | 969.8493 | 3.0275 | 80.5785 | 136.458 | 112.9307 | 8.5281 | 90.5298 | 1.8146 | 10.053 | 56.2239 | 117.6088 | 10.7422 | 276.0672 | 160.379 | 339.0348 | 9.8561 | 59.0001 | 6.6622 | 206 | 56.0167 | 0 | 293.8436 | 0
6044 | 933.9357 | 3.4304 | 40.5824 | 89.6785 | 108.0141 | 9.2496 | 92.0452 | 2.0393 | 9.8925 | 59.9368 | 107.2418 | 7.8144 | 261.2106 | 148.8802 | 313.9398 | 10.512 | 55.4223 | 4.7935 | 185 | 47.7534 | 0 | 261.8787 | 0
6045 | 911.9796 | 3.649 | 21.8377 | 70.3346 | 107.6015 | 8.071 | 89.6885 | 2.3706 | 10.854 | 50.4014 | 107.6072 | 8.1545 | 271.5747 | 144.4133 | 283.0061 | 10.2538 | 53.4628 | 4.8234 | 189 | 51.9287 | 0 | 245.3511 | 0
6046 | 879.7399 | 2.8201 | 21.2559 | 46.1912 | 106.5524 | 6.9775 | 69.6587 | 2.3202 | 10.386 | 33.3493 | 100.8765 | 8.095 | 260.9935 | 136.146 | 259.9729 | 10.2656 | 53.7353 | 4.3798 | 167 | 48.0816 | 0 | 236.0398 | 0
6047 | 841.2615 | 1.653 | 21.0277 | 65.5912 | 105.0788 | 7.3368 | 62.7166 | 2.1823 | 8.7025 | 23.0528 | 90.4063 | 7.9494 | 245.2849 | 127.7521 | 258.2297 | 11.0416 | 54.9386 | 4.0451 | 151 | 41.7886 | 0 | 231.6085 | 0
6048 | 844.0232 | 1.2124 | 20.7751 | 80.2238 | 105.4044 | 6.8531 | 65.7189 | 2.1629 | 7.5635 | 20.3323 | 85.0788 | 7.9276 | 239.6146 | 118.1531 | 260.4718 | 13.0609 | 53.4968 | 3.9382 | 140 | 46.3967 | 0 | 228.3907 | 0
6049 | 836.0606 | 1.123 | 20.7171 | 50.457 | 103.4532 | 7.3857 | 63.456 | 2.1255 | 6.9745 | 19.8787 | 81.8349 | 7.9309 | 216.2264 | 107.4708 | 257.0658 | 14.38 | 50.3615 | 3.72 | 132 | 43.3738 | 0 | 227.4052 | 0
6050 | 815.3633 | 1.3996 | 20.5938 | 64.9205 | 100.621 | 7.6424 | 61.7352 | 1.6295 | 6.3959 | 19.6919 | 77.7025 | 10.6546 | 197.4149 | 100.7922 | 248.3379 | 14.3724 | 49.4383 | 3.2697 | 130 | 42.3551 | 0 | 228.7147 | 0
6051 | 809.6766 | 1.3742 | 21.881 | 67.1121 | 97.4762 | 8.257 | 63.7298 | 1.3559 | 6.1101 | 21.4201 | 74.3648 | 16.8118 | 179.2941 | 97.5006 | 237.0739 | 13.85 | 50.1677 | 2.8676 | 136 | 37.5751 | 0 | 230.7516 | 0
6052 | 814.0217 | 1.5844 | 25.3789 | 86.0027 | 95.9521 | 7.8595 | 66.3744 | 1.5291 | 6.2225 | 28.8484 | 72.4323 | 16.6752 | 179.5095 | 95.0376 | 230.7978 | 11.4412 | 50.6713 | 2.7382 | 134 | 39.945 | 0 | 235.7593 | 0
6053 | 833.6427 | 2.5622 | 34.5221 | 69.3276 | 95.2579 | 6.9251 | 65.0671 | 1.4417 | 5.9331 | 35.6837 | 71.3325 | 12.0329 | 192.0754 | 95.2673 | 231.3754 | 10.0869 | 50.7369 | 2.7038 | 133 | 39.9582 | 0 | 249.6163 | 0
6054 | 883.1565 | 4.1161 | 51.5123 | 116.1402 | 89.1573 | 10.0798 | 71.2948 | 1.2642 | 5.8266 | 34.428 | 79.9274 | 15.0762 | 203.5015 | 122.8534 | 262.1962 | 13.6493 | 51.4297 | 3.0017 | 203 | 53.1004 | 0 | 277.9246 | 0
6055 | 953.4954 | 9.1635 | 80.3258 | 117.0501 | 85.5502 | 14.9102 | 98.7045 | 2.1112 | 11.2426 | 41.2686 | 105.2544 | 25.4994 | 345.4779 | 187.6048 | 325.0782 | 25.4116 | 55.7835 | 9.7392 | 265 | 62.8414 | 0 | 326.1028 | 0.081832
6056 | 1035.5163 | 15.8556 | 101.3381 | 186.3417 | 88.5735 | 16.974 | 130.85 | 3.6291 | 20.067 | 62.5486 | 137.8304 | 32.5542 | 231.9626 | 256.3497 | 413.9905 | 36.1573 | 64.5407 | 15.1201 | 302 | 79.4636 | 0 | 397.7145 | 0.033628
6057 | 1112.3403 | 15.4605 | 109.0948 | 202.9076 | 91.7525 | 17.0872 | 145.9304 | 4.2111 | 26.3606 | 78.3917 | 163.5979 | 35.9558 | 295.2211 | 305.7848 | 536.8688 | 40.8541 | 74.7459 | 16.505 | 377 | 85.2262 | 0 | 468.3622 | 0.099695
6058 | 1159.9859 | 9.8592 | 109.4745 | 201.7945 | 92.4511 | 19.7678 | 152.7331 | 4.1417 | 25.6705 | 81.6403 | 177.0277 | 36.7928 | 367.7095 | 334.1757 | 626.0881 | 41.8033 | 83.5868 | 17.6951 | 394 | 98.3696 | 0 | 504.5341 | 0.095793
6059 | 1169.6782 | 7.0394 | 111.4705 | 180.9445 | 92.2224 | 19.4723 | 160.5295 | 4.1492 | 24.0558 | 82.9659 | 182.6314 | 35.5109 | 387.1507 | 349.8384 | 651.6797 | 40.3497 | 88.4622 | 17.4106 | 379 | 103.5504 | 0 | 517.4321 | 0.14044
6060 | 1150.7947 | 6.9215 | 110.8665 | 215.7489 | 90.237 | 19.7375 | 161.4083 | 4.0932 | 21.7231 | 79.1283 | 183.6862 | 35.1897 | 381.2206 | 354.937 | 642.4602 | 40.2522 | 88.6795 | 16.671 | 379 | 100.656 | 0 | 529.7195 | 0.21301
6061 | 1157.9017 | 5.6371 | 110.7183 | 207.5018 | 96.83 | 19.3778 | 161.794 | 4.2256 | 18.5181 | 67.7687 | 185.7645 | 34.5849 | 420.0233 | 352.1072 | 624.2859 | 42.6765 | 87.9238 | 17.128 | 329 | 92.3363 | 0 | 536.9572 | 0.26
6062 | 1153.2207 | 4.301 | 111.9946 | 185.4993 | 109.8642 | 15.4217 | 157.1027 | 4.3926 | 22 | 62.3509 | 191.9536 | 33.957 | 411.8877 | 348.417 | 609.6997 | 42.0561 | 87.5836 | 17.373 | 286 | 93.4042 | 0 | 526.6919 | 0.28276
6063 | 1119.9456 | 4.0812 | 111.8254 | 216.8422 | 114.5094 | 14.2579 | 140.7296 | 3.6772 | 21.6095 | 59.9076 | 194.0447 | 33.219 | 414.4461 | 335.2521 | 601.1282 | 37.4485 | 85.5763 | 16.4413 | 272 | 79.7487 | 0 | 508.8736 | 0.26776
6064 | 1069.3485 | 3.3377 | 107.5604 | 191.2075 | 111.8936 | 13.4959 | 125.1009 | 2.7138 | 21.2598 | 55.5383 | 190.8219 | 31.8989 | 388.4337 | 299.755 | 564.0331 | 22.2583 | 81.4375 | 15.7239 | 277 | 76.7891 | 0 | 465.9119 | 0.21613
6065 | 1000.0258 | 2.6895 | 88.9897 | 157.859 | 110.9837 | 9.1626 | 111.7569 | 1.8531 | 21.7275 | 52.3349 | 178.3235 | 27.9327 | 346.0346 | 242.2897 | 469.0021 | 10.6668 | 75.3826 | 15.1288 | 233 | 61.3039 | 0 | 393.7214 | 0.19462
6066 | 938.9363 | 2.1429 | 47.8082 | 81.2285 | 108.3813 | 7.6424 | 95.8571 | 1.2168 | 18.9847 | 50.4417 | 147.1847 | 20.0669 | 295.5554 | 192.323 | 375.579 | 8.7107 | 67.8922 | 12.235 | 213 | 49.6672 | 0 | 326.939 | 0.10415
6067 | 899.8798 | 3.2198 | 38.223 | 89.4324 | 105.6564 | 6.9247 | 76.144 | 1.2069 | 11.6905 | 54.0357 | 115.7374 | 9.5323 | 262.0763 | 164.0687 | 337.3553 | 8.5388 | 61.3116 | 7.2285 | 206 | 54.2585 | 0 | 277.6783 | 0
6068 | 869.1357 | 3.9509 | 20.6699 | 61.9001 | 102.4603 | 7.3194 | 66.5928 | 1.3354 | 6.8987 | 57.3603 | 98.7545 | 6.8276 | 234.9283 | 147.352 | 323.5712 | 8.8943 | 57.1033 | 4.8735 | 193 | 47.3916 | 0 | 251.3997 | 0
6069 | 835.7462 | 3.4691 | 25.2613 | 77.8169 | 97.3526 | 8.2873 | 63.9197 | 1.329 | 6.5966 | 48.0593 | 87.4626 | 7.1591 | 293.5371 | 131.9516 | 304.4298 | 8.8323 | 54.3152 | 4.3194 | 186 | 47.3098 | 0 | 246.1779 | 0
6070 | 825.4914 | 2.8854 | 27.3639 | 93.192 | 92.6246 | 9.2307 | 62.7456 | 1.3327 | 6.8784 | 34.386 | 80.5167 | 6.9646 | 257.7051 | 115.3082 | 282.1636 | 8.6519 | 52.6247 | 4.2353 | 155 | 50.9888 | 0 | 257.8651 | 0
6071 | 830.0984 | 1.8745 | 27.1277 | 83.5692 | 90.5748 | 8.75 | 66.3633 | 1.3351 | 6.4623 | 28.8937 | 77.8469 | 6.5856 | 201.7712 | 104.297 | 267.1012 | 8.7964 | 52.0142 | 3.8053 | 142 | 48.6321 | 0 | 265.7057 | 0
6072 | 838.1194 | 1.8087 | 27.4019 | 78.2802 | 89.8525 | 9.3173 | 68.3851 | 1.4405 | 6.4015 | 28.7337 | 75.9778 | 6.1814 | 213.1082 | 99.627 | 267.6318 | 8.9186 | 53.0591 | 3.18 | 139 | 44.4887 | 0 | 261.5554 | 0
6073 | 833.5073 | 1.6595 | 27.2464 | 77.396 | 91.779 | 8.7631 | 64.378 | 1.546 | 6.2395 | 28.2071 | 74.3165 | 5.9672 | 200.6263 | 101.789 | 278.3091 | 8.9242 | 55.1232 | 3.2111 | 134 | 43.7865 | 0 | 260.9923 | 0
6074 | 815.2453 | 1.4176 | 27.0794 | 57.9437 | 96.0325 | 7.885 | 60.6974 | 1.4619 | 6.279 | 26.4325 | 73.3087 | 5.9411 | 231.4504 | 107.3284 | 281.7149 | 8.9242 | 54.3877 | 3.4034 | 140 | 43.7027 | 0 | 263.9473 | 0
6075 | 800.9525 | 1.2557 | 28.3711 | 95.0255 | 102.224 | 7.5245 | 64.6449 | 1.3615 | 6.2985 | 25.9231 | 72.8463 | 6.1368 | 191.2831 | 108.8747 | 272.0083 | 9.0669 | 51.8656 | 4.0515 | 135 | 39.2898 | 0 | 256.9395 | 0
6076 | 802.4308 | 1.6282 | 39.1017 | 75.142 | 106.67 | 7.6076 | 66.3176 | 1.3507 | 6.1102 | 31.0225 | 72.2703 | 5.9484 | 222.6077 | 107.4273 | 256.3288 | 8.6236 | 51.4323 | 4.6299 | 122 | 41.9738 | 0 | 243.0831 | 0
6077 | 798.854 | 2.5037 | 35.7088 | 99.7944 | 109.0717 | 6.8991 | 61.2131 | 1.59 | 6.1139 | 36.6755 | 71.5225 | 5.7907 | 200.7694 | 105.3118 | 249.8644 | 8.6968 | 51.8962 | 4.5004 | 117 | 41.6366 | 0 | 234.4999 | 0
6078 | 811.4636 | 2.4133 | 60.1969 | 69.9438 | 107.311 | 7.3671 | 63.6284 | 2.2142 | 6.1869 | 31.5824 | 69.5152 | 4.4885 | 198.8595 | 98.1301 | 240.4742 | 8.5487 | 51.7913 | 3.9737 | 117 | 42.1826 | 0 | 227.7527 | 0
6079 | 830.0941 | 1.3022 | 36.3978 | 107.6947 | 105.5029 | 7.5908 | 65.7449 | 3.3625 | 6.2585 | 22.1117 | 70.5326 | 4.4499 | 198.0662 | 90.9033 | 238.5844 | 9.6893 | 51.4115 | 4.0401 | 126 | 40.771 | 0 | 224.0766 | 0.063527
6080 | 830.898 | 0.757 | 44.4942 | 82.9698 | 105.6581 | 7.584 | 63.2527 | 3.8593 | 6.043 | 19.1405 | 89.9458 | 8.4031 | 198.6914 | 92.5249 | 239.2311 | 11.4262 | 51.4423 | 4.8331 | 150 | 50.9536 | 0 | 226.4118 | 0.069869
6081 | 845.7372 | 0.92335 | 67.152 | 113.4753 | 107.4382 | 7.6624 | 59.4407 | 2.2233 | 5.312 | 21.7409 | 120.2463 | 11.7596 | 239.9045 | 105.6446 | 232.7901 | 11.0832 | 52.0771 | 6.9934 | 151 | 50.6189 | 0 | 228.1796 | 0.16632
6082 | 856.4782 | 1.1502 | 36.5326 | 136.7429 | 110.5171 | 7.5653 | 64.7355 | 1.1586 | 4.9326 | 27.4883 | 132.7714 | 11.569 | 229.3524 | 120.2357 | 235.3613 | 10.493 | 52.2928 | 11.5328 | 157 | 46.91 | 0 | 237.8097 | 0.24444
6083 | 859.5889 | 1.3965 | 44.6307 | 107.3323 | 106.8621 | 7.6469 | 66.4522 | 1.0596 | 5.2732 | 32.6288 | 119.605 | 12.2177 | 171.6098 | 122.1545 | 236.1607 | 10.2788 | 52.0652 | 13.5619 | 156 | 53.0573 | 0 | 248.0808 | 0.23807
6084 | 852.2234 | 1.6559 | 49.7829 | 139.2031 | 104.6195 | 7.6312 | 62.7207 | 0.91372 | 5.7587 | 33.7737 | 101.5323 | 12.8613 | 202.5865 | 120.9863 | 231.8113 | 9.9204 | 52.2492 | 13.9384 | 156 | 69.9925 | 0 | 243.4249 | 0.22611
6085 | 861.1023 | 1.9654 | 49.2335 | 103.1455 | 109.969 | 6.8553 | 61.5007 | 0.90769 | 5.5754 | 33.0773 | 97.0131 | 12.649 | 203.8619 | 124.8845 | 239.4209 | 10.6383 | 53.1604 | 14.3592 | 156 | 78.3909 | 0 | 236.2673 | 0.21253
6086 | 895.0747 | 1.9294 | 48.5549 | 106.1368 | 111.9778 | 7.2954 | 61.9639 | 1.0998 | 5.7573 | 33.1355 | 98.7269 | 12.6828 | 211.9926 | 130.6339 | 267.3161 | 10.5232 | 54.3637 | 14.5041 | 156 | 73.3279 | 0 | 235.8194 | 0.25617
6087 | 922.7435 | 1.7804 | 49.914 | 82.8992 | 111.1878 | 8.3372 | 62.0835 | 1.026 | 5.909 | 31.9293 | 99.9163 | 12.4972 | 235.703 | 136.2302 | 291.0035 | 10.1726 | 54.188 | 14.616 | 159 | 49.0015 | 0 | 246.2284 | 0.25208
6088 | 918.8934 | 1.3846 | 49.1263 | 58.0638 | 112.941 | 6.4472 | 63.6447 | 0.87397 | 6.7858 | 27.8387 | 101.0566 | 9.059 | 204.628 | 134.3194 | 296.475 | 10.0291 | 52.8989 | 14.3259 | 168 | 47.9292 | 0 | 249.5308 | 0.15274
6089 | 905.0573 | 1.5812 | 67.0162 | 76.8382 | 111.8108 | 7.1016 | 67.7072 | 0.87092 | 6.8667 | 23.6952 | 99.8793 | 5.6092 | 179.6074 | 127.4049 | 293.0527 | 9.1993 | 52.4831 | 11.64 | 178 | 44.3641 | 0 | 238.9863 | 0.12661
6090 | 886.1508 | 1.8863 | 36.102 | 89.7651 | 109.9457 | 8.2869 | 64.5871 | 0.88236 | 7.2489 | 23.8479 | 92.5496 | 4.4514 | 185.1102 | 126.4032 | 291.0539 | 8.4517 | 52.2299 | 6.941 | 182 | 40.2082 | 0 | 233.5812 | 0.05576
6091 | 869.1701 | 2.8269 | 44.9269 | 57.439 | 106.619 | 9.9869 | 60.1334 | 1.2731 | 6.4118 | 30.8478 | 83.8655 | 4.5246 | 191.5051 | 128.7657 | 291.0409 | 8.4829 | 51.4953 | 5.4188 | 205 | 42.7608 | 0 | 235.3291 | 0
6092 | 860.9738 | 3.2948 | 49.1921 | 74.0154 | 102.2402 | 11.1701 | 60.4185 | 1.4284 | 5.8462 | 37.4057 | 83.0323 | 5.8592 | 164.4464 | 133.1399 | 298.6301 | 8.7844 | 51.7726 | 5.7651 | 201 | 42.3669 | 0 | 246.0735 | 0
6093 | 850.8024 | 3.4388 | 67.1723 | 91.683 | 99.3747 | 9.9529 | 61.3626 | 1.3447 | 6.1399 | 33.194 | 85.6678 | 6.463 | 163.1909 | 133.2367 | 298.55 | 8.7415 | 52.0797 | 5.1183 | 216 | 40.7899 | 0 | 253.0183 | 0
6094 | 843.4961 | 3.2081 | 36.3904 | 80.349 | 100.5124 | 7.3343 | 64.6591 | 1.3453 | 6.5063 | 24.9511 | 84.4627 | 6.5166 | 187.845 | 126.266 | 287.8778 | 8.9837 | 51.163 | 4.3193 | 215 | 45.1002 | 0 | 247.0632 | 0
6095 | 840.7696 | 1.9956 | 34.6035 | 56.3829 | 101.5338 | 6.0264 | 64.3222 | 1.3551 | 6.5374 | 21.975 | 80.9912 | 6.3945 | 216.2109 | 122.9531 | 281.7549 | 8.7781 | 50.4768 | 4.7198 | 215 | 42.2568 | 0 | 240.9442 | 0
6096 | 836.1743 | 1.4654 | 41.838 | 100.8262 | 99.3996 | 6.3911 | 61.2189 | 1.3547 | 6.3392 | 21.5757 | 77.088 | 6.3686 | 149.0343 | 139.3122 | 278.2436 | 8.5868 | 50.759 | 4.103 | 231 | 45.3051 | 0 | 240.0827 | 0
6097 | 829.8747 | 1.4805 | 46.2397 | 73.9714 | 96.2865 | 7.3469 | 64.3352 | 1.3487 | 6.9139 | 21.2601 | 73.4383 | 6.4975 | 157.6245 | 158.1195 | 274.456 | 8.6892 | 51.2639 | 3.3983 | 236 | 46.2028 | 0 | 240.1723 | 0
6098 | 823.6286 | 1.4959 | 46.1211 | 89.1003 | 95.3926 | 6.8851 | 65.42 | 1.5887 | 6.7633 | 21.2023 | 71.943 | 6.5387 | 177.7185 | 160.1075 | 266.3944 | 8.6951 | 51.9681 | 3.1133 | 221 | 46.4501 | 0 | 238.2019 | 0
6099 | 820.5206 | 1.5485 | 47.3389 | 104.9228 | 93.4867 | 8.0604 | 62.388 | 1.5525 | 6.2028 | 21.8054 | 71.6687 | 6.3056 | 213.3192 | 158.012 | 259.1733 | 8.9187 | 51.4719 | 3.1149 | 186 | 46.3157 | 0 | 237.7739 | 0
6100 | 817.2117 | 1.7357 | 52.2012 | 80.8368 | 94.8692 | 7.1564 | 59.2603 | 1.3669 | 6.0631 | 23.6793 | 71.4689 | 6.1259 | 145.3766 | 158.0331 | 256.3917 | 8.8057 | 49.9049 | 3.1512 | 158 | 48.5769 | 0 | 237.4012 | 0
6101 | 815.8338 | 2.498 | 49.2661 | 107.9033 | 95.3716 | 7.2975 | 64.5701 | 1.3609 | 6.0697 | 24.9029 | 71.5139 | 6.1789 | 152.8377 | 152.3576 | 252.9409 | 8.729 | 49.8527 | 3.0102 | 140 | 50.0312 | 0 | 237.3125 | 0
6102 | 828.92 | 2.5235 | 45.6815 | 71.9314 | 96.1088 | 6.9428 | 64.3476 | 1.1879 | 6.0506 | 22.1103 | 70.1952 | 5.0656 | 185.0686 | 131.1807 | 244.9489 | 8.6589 | 50.37 | 2.6968 | 135 | 49.542 | 0 | 234.975 | 0
6103 | 848.7694 | 1.4122 | 45.3628 | 86.4243 | 97.1048 | 6.6932 | 58.2608 | 0.9994 | 5.712 | 18.2008 | 67.334 | 4.1833 | 161.1912 | 112.2739 | 231.3067 | 8.7802 | 50.2396 | 2.7988 | 133 | 46.8596 | 0 | 229.9365 | 0.051043
6104 | 846.2118 | 0.86612 | 45.4911 | 100.2655 | 96.8953 | 7.3707 | 63.5947 | 0.97959 | 5.4492 | 17.4608 | 66.0209 | 4.2072 | 157.9991 | 106.8017 | 229.9595 | 9.5982 | 49.9441 | 3.347 | 137 | 41.3666 | 0 | 227.2667 | 0.074963
6105 | 840.8775 | 1.0248 | 45.3678 | 99.2752 | 96.6463 | 7.5439 | 62.7358 | 1.0688 | 5.332 | 19.5884 | 66.614 | 7.1078 | 156.0665 | 106.0711 | 233.4611 | 10.3414 | 50.1988 | 5.8364 | 164 | 39.5049 | 0 | 226.8844 | 0.054779
6106 | 857.9343 | 1.1609 | 45.5341 | 99.0144 | 95.978 | 8.3155 | 61.5665 | 1.2142 | 5.3423 | 25.1564 | 70.2739 | 8.568 | 187.3051 | 108.3985 | 232.0537 | 10.4495 | 51.4484 | 10.629 | 175 | 36.0859 | 0 | 229.9409 | 0.084953
6107 | 882.8417 | 1.1232 | 45.7429 | 83.3873 | 96.8876 | 7.8553 | 63.9532 | 1.0807 | 5.1058 | 32.8517 | 79.8266 | 8.8074 | 220.4354 | 114.207 | 234.2555 | 9.9576 | 52.5905 | 12.8147 | 181 | 43.9937 | 0 | 236.2472 | 0.18983
6108 | 890.3259 | 1.2637 | 46.3609 | 113.277 | 96.2484 | 7.5864 | 61.7019 | 1.0689 | 5.4254 | 39.1689 | 89.7622 | 7.936 | 176.1905 | 119.6195 | 234.0035 | 10.2271 | 52.8981 | 12.8279 | 196 | 41.1427 | 0 | 241.8944 | 0.18043
6109 | 880.5398 | 1.5636 | 45.6905 | 90.3504 | 95.7268 | 6.9019 | 61.3521 | 1.2596 | 5.667 | 39.9565 | 93.8066 | 5.1715 | 186.2029 | 126.2823 | 240.8626 | 10.3517 | 53.0407 | 12.933 | 224 | 46.5652 | 0 | 244.5014 | 0.24617
6110 | 871.8608 | 1.9252 | 45.4683 | 101.9417 | 95.9784 | 8.0757 | 63.6249 | 1.3022 | 5.9525 | 36.9701 | 99.675 | 4.8563 | 200.5906 | 133.5449 | 243.903 | 10.2346 | 53.2406 | 13.1859 | 221 | 45.6611 | 0 | 246.1586 | 0.29164
6111 | 865.5449 | 1.8796 | 45.3702 | 105.2409 | 93.4081 | 11.4534 | 62.9757 | 1.2868 | 5.5758 | 34.3341 | 111.0522 | 6.4166 | 192.5195 | 135.9092 | 250.9541 | 10.3114 | 53.6836 | 13.4093 | 221 | 47.3278 | 0 | 247.0776 | 0.25218
6112 | 873.0563 | 1.6183 | 45.9853 | 108.8993 | 91.7915 | 11.6095 | 61.1255 | 1.4036 | 5.3894 | 29.3124 | 111.7697 | 4.9565 | 206.8338 | 133.8977 | 255.5028 | 10.3067 | 53.7481 | 13.495 | 203 | 50.4285 | 0 | 245.4322 | 0.14094
6113 | 874.9168 | 2.0524 | 45.5465 | 104.7316 | 93.581 | 9.2664 | 60.6297 | 1.5029 | 5.8199 | 23.2973 | 101.3095 | 3.9906 | 211.7371 | 126.6364 | 263.6681 | 9.1402 | 53.1914 | 11.7972 | 180 | 46.1469 | 0 | 241.1209 | 0.14248
6114 | 859.5812 | 1.7004 | 61.0552 | 112.1859 | 92.7122 | 9.2065 | 59.0714 | 1.5236 | 5.9059 | 19.5537 | 94.7681 | 4.5792 | 206.8064 | 120.076 | 279.0816 | 8.5418 | 53.0039 | 7.2284 | 152 | 49.853 | 0 | 230.5957 | 0.083493
6115 | 847.855 | 3.2722 | 33.1235 | 85.7277 | 90.3726 | 9.4945 | 62.188 | 1.7179 | 5.9539 | 18.8813 | 92.6628 | 4.7758 | 216.0363 | 121.8383 | 287.4746 | 8.3204 | 53.0594 | 5.0574 | 146 | 41.2172 | 0 | 221.1684 | 0
6116 | 826.6333 | 3.9336 | 40.8248 | 111.9396 | 90.4461 | 8.0969 | 65.7127 | 2.0476 | 6.2999 | 20.9897 | 88.5735 | 5.8172 | 195.2177 | 120.4119 | 279.3057 | 8.403 | 52.7459 | 4.8344 | 146 | 44.0538 | 0 | 221.6591 | 0
6117 | 811.7101 | 3.5768 | 45.0949 | 88.9585 | 89.3809 | 8.3591 | 62.3896 | 2.1848 | 6.2157 | 22.0541 | 82.807 | 6.3919 | 184.5423 | 110.5125 | 256.7946 | 8.6494 | 52.3657 | 4.3923 | 133 | 39.8243 | 0 | 224.3445 | 0
6118 | 809.2925 | 2.8728 | 45.8207 | 113.8178 | 92.108 | 7.1081 | 61.3396 | 2.231 | 6.106 | 21.6674 | 79.9648 | 6.3884 | 203.4819 | 103.0346 | 244.4933 | 8.589 | 52.5699 | 4.099 | 139 | 40.2577 | 0 | 223.815 | 0
6119 | 811.9771 | 1.7014 | 45.4127 | 89.6591 | 95.8761 | 7.3454 | 61.4842 | 2.2862 | 6.1412 | 21.6496 | 78.3092 | 6.5665 | 183.235 | 97.8964 | 245.6828 | 8.7952 | 53.0591 | 3.8172 | 133 | 39.1178 | 0 | 222.6348 | 0
6120 | 818.8848 | 1.2703 | 45.0675 | 113.16 | 102.3885 | 7.552 | 63.9907 | 2.5337 | 6.0049 | 21.0183 | 75.619 | 6.4055 | 171.0954 | 93.8482 | 244.5462 | 8.7648 | 52.7395 | 3.2867 | 130 | 39.3374 | 0 | 224.9368 | 0
6121 | 798.3915 | 1.1889 | 45.001 | 105.6258 | 103.8576 | 8.275 | 63.95 | 2.3967 | 5.8004 | 19.8373 | 72.8688 | 6.2227 | 216.2174 | 92.3724 | 241.4929 | 8.6736 | 51.8581 | 2.8943 | 125 | 41.4328 | 0 | 228.322 | 0
6122 | 782.3158 | 1.255 | 45.0419 | 101.2425 | 102.6634 | 7.9171 | 63.4657 | 1.7531 | 5.6881 | 19.2155 | 71.0487 | 6.2525 | 201.8588 | 90.9504 | 242.8452 | 8.9103 | 51.7118 | 2.8648 | 126 | 36.8031 | 0 | 228.179 | 0
6123 | 780.2117 | 1.2218 | 44.8887 | 101.5006 | 83.7912 | 7.6099 | 61.9217 | 1.4191 | 5.7228 | 20.8963 | 69.8217 | 6.4626 | 186.7605 | 90.7249 | 235.1245 | 8.6285 | 52.1452 | 3.0286 | 117 | 39.229 | 0 | 228.1039 | 0
6124 | 786.0455 | 1.6555 | 35.0883 | 42.8255 | 52.7965 | 7.6082 | 62.0069 | 1.4217 | 5.8106 | 27.9607 | 68.4819 | 6.3746 | 199.7334 | 90.9489 | 230.7689 | 8.7493 | 52.8923 | 2.9198 | 113 | 40.0084 | 0 | 239.5548 | 0
6125 | 810.9626 | 2.7618 | 29.4022 | 54.4017 | 40.3678 | 6.8595 | 64.5381 | 1.637 | 5.9115 | 34.4846 | 68.7498 | 8.0968 | 208.4017 | 94.6487 | 233.2036 | 8.7602 | 52.6811 | 2.7797 | 119 | 36.6485 | 0 | 262.9418 | 0
6126 | 882.889 | 5.4645 | 76.2517 | 144.0022 | 34.9777 | 12.0824 | 83.1984 | 1.8513 | 6.0145 | 39.2067 | 86.8124 | 19.3594 | 213.052 | 135.8251 | 263.8474 | 29.1753 | 54.1767 | 5.8884 | 184 | 50.683 | 0 | 306.356 | 0
6127 | 925.8843 | 6.9642 | 47.385 | 51.0396 | 32.9954 | 14.0529 | 94.8685 | 1.8997 | 10.0599 | 45.1171 | 116.7388 | 25.2852 | 342.2787 | 188.0219 | 310.0204 | 17.6663 | 58.5227 | 7.7379 | 265 | 55.1368 | 0 | 349.6949 | 0.16098
6128 | 1026.9052 | 8.9211 | 83.0236 | 142.5163 | 28.8557 | 17.9845 | 111.7029 | 3.419 | 12.3818 | 56.2744 | 141.4266 | 31.7316 | 210.6308 | 233.3333 | 375.0648 | 27.889 | 67.1938 | 11.5036 | 298 | 64.4303 | 0 | 410.715 | 0.14921
6129 | 1140.5503 | 6.8649 | 107.0191 | 148.1272 | 28.5848 | 18.1465 | 132.6288 | 4.5971 | 20.4952 | 72.8822 | 165.3162 | 35.6053 | 319.5044 | 285.9873 | 476.3319 | 39.2338 | 79.5355 | 14.4336 | 368 | 71.6825 | 0 | 500.5093 | 0.099784
6130 | 1176.2862 | 3.5179 | 109.1814 | 178.9527 | 30.9018 | 15.8431 | 135.5622 | 4.3893 | 26.0227 | 80.9026 | 176.2241 | 36.7375 | 361.7745 | 318.8275 | 560.3408 | 41.5961 | 86.9906 | 15.2217 | 351 | 78.962 | 0 | 547.4758 | 0.15187
6131 | 1185.7329 | 3.3968 | 114.5949 | 184.0885 | 29.7957 | 16.8923 | 139.1744 | 4.4042 | 26.2048 | 81.4126 | 179.0427 | 35.5536 | 404.9405 | 336.4485 | 604.5365 | 40.0613 | 89.6019 | 15.6115 | 323 | 94.4276 | 0 | 550.6932 | 0.20135
6132 | 1203.0708 | 3.7877 | 113.3156 | 205.5228 | 26.3457 | 20.1692 | 145.4946 | 4.4196 | 22.6676 | 79.2982 | 189.8842 | 36.4546 | 427.8171 | 347.2529 | 616.3303 | 39.9415 | 89.8704 | 16.1541 | 386 | 91.1531 | 0 | 547.7335 | 0.23271
6133 | 1219.3403 | 3.7256 | 111.6896 | 165.9813 | 27.9927 | 18.7634 | 152.6282 | 4.2284 | 19.0154 | 79.1363 | 201.868 | 37.4393 | 451.7993 | 347.2606 | 595.0773 | 39.3924 | 86.3492 | 16.5077 | 330 | 95.9093 | 0 | 553.3829 | 0.13382
6134 | 1209.8442 | 3.3743 | 110.5187 | 183.141 | 30.1954 | 16.6394 | 153.7295 | 4.3414 | 21.7194 | 81.6992 | 208.5718 | 36.0064 | 416.7295 | 346.7913 | 578.8512 | 38.1598 | 82.8717 | 16.7855 | 281 | 90.2826 | 0 | 554.3812 | 0.14549
6135 | 1175.8973 | 3.8627 | 112.044 | 201.1554 | 32.0132 | 16.1636 | 141.5612 | 4.3243 | 23.1163 | 78.1008 | 206.9647 | 31.0305 | 443.1584 | 339.9467 | 579.2432 | 37.6039 | 83.0254 | 16.7968 | 272 | 84.939 | 0 | 535.8326 | 0.14152
6136 | 1131.9414 | 3.5897 | 108.1831 | 152.6947 | 35.1129 | 15.4155 | 129.4739 | 4.2424 | 22.954 | 69.5728 | 197.194 | 27.3993 | 449.6011 | 320.0495 | 541.2372 | 30.7061 | 83.1173 | 17.0492 | 249 | 72.1817 | 0 | 495.4089 | 0.083567
6137 | 1072.7063 | 3.3201 | 100.6943 | 150.1533 | 41.8188 | 10.2956 | 120.8695 | 3.7472 | 20.7692 | 58.5866 | 177.8902 | 28.0775 | 370.7344 | 280.1649 | 464.046 | 17.0023 | 79.2168 | 17.1437 | 255 | 66.8449 | 0 | 419.1081 | 0.07546
6138 | 1012.3996 | 3.235 | 95.1199 | 130.3994 | 43.858 | 8.5148 | 126.8727 | 2.9397 | 14.0643 | 50.6934 | 145.2758 | 24.5633 | 336.2917 | 225.9985 | 396.0687 | 9.937 | 73.3261 | 14.5782 | 231 | 62.6921 | 0 | 342.4593 | 0.034531
6139 | 968.9834 | 4.0104 | 79.6144 | 128.5686 | 42.3559 | 9.9608 | 115.0532 | 2.6239 | 9.5355 | 53.028 | 115.0208 | 14.8597 | 295.1752 | 190.2437 | 347.1797 | 9.029 | 70.0046 | 9.4129 | 214 | 57.9511 | 0 | 298.9832 | 0
6140 | 932.5028 | 4.3452 | 48.9718 | 58.6986 | 44.8386 | 7.6501 | 82.592 | 2.8165 | 7.342 | 57.1121 | 105.5788 | 10.519 | 289.117 | 167.8367 | 307.968 | 8.6381 | 67.2663 | 7.6819 | 200 | 52.6733 | 0 | 272.8126 | 0
6141 | 894.6688 | 3.7392 | 37.0285 | 86.2619 | 46.0236 | 6.6308 | 64.3596 | 2.7755 | 7.1467 | 49.9153 | 106.5805 | 10.1843 | 247.1323 | 138.2798 | 290.4296 | 8.5599 | 62.4316 | 6.9941 | 177 | 48.9827 | 0 | 259.4426 | 0
6142 | 853.8937 | 3.0361 | 36.4015 | 41.6183 | 43.7477 | 7.3087 | 61.2831 | 2.5659 | 7.1487 | 36.8448 | 100.2129 | 10.1675 | 227.1323 | 113.4162 | 272.3498 | 8.4855 | 58.625 | 6.1771 | 150 | 41.1873 | 0 | 254.7492 | 0
6143 | 830.2567 | 1.778 | 36.0064 | 98.9999 | 42.8561 | 7.6428 | 64.0131 | 2.5473 | 6.7382 | 28.988 | 88.3338 | 10.2213 | 201.7741 | 104.2211 | 258.0806 | 8.9287 | 56.9856 | 5.6923 | 153 | 43.2965 | 0 | 252.1325 | 0
6144 | 825.126 | 1.2837 | 48.525 | 110.089 | 43.5227 | 7.5755 | 67.0282 | 2.5457 | 6.7123 | 25.7509 | 80.0727 | 10.1445 | 251.6835 | 101.7178 | 247.2935 | 9.284 | 56.182 | 5.0399 | 141 | 41.344 | 0 | 251.0147 | 0
6145 | 809.023 | 1.4761 | 26.4949 | 77.4639 | 43.093 | 7.6035 | 63.3887 | 2.7534 | 6.6186 | 24.1417 | 75.4702 | 10.253 | 208.5602 | 98.2071 | 234.0847 | 8.8084 | 55.8511 | 4.6367 | 148 | 37.5398 | 0 | 249.1223 | 0
6146 | 793.6082 | 1.356 | 32.4463 | 59.2785 | 43.4132 | 7.605 | 61.4859 | 2.1881 | 6.348 | 23.5883 | 73.2182 | 10.3718 | 203.7045 | 94.4335 | 229.1294 | 8.4568 | 55.6597 | 4.5429 | 131 | 40.2413 | 0 | 245.0537 | 0
6147 | 780.0799 | 1.178 | 35.4858 | 86.3626 | 43.1163 | 8.256 | 65.5967 | 1.5369 | 6.328 | 25.1806 | 72.6698 | 10.0864 | 212.0887 | 92.2501 | 229.9821 | 8.2739 | 55.7448 | 3.7264 | 119 | 41.5456 | 0 | 242.9314 | 0
6148 | 771.4102 | 1.6358 | 48.5835 | 42.6554 | 44.5253 | 7.1758 | 62.3787 | 1.3945 | 6.383 | 32.1114 | 72.2439 | 9.9792 | 206.556 | 91.7451 | 234.7016 | 8.4513 | 56.25 | 3.1903 | 121 | 39.3157 | 0 | 250.1278 | 0
6149 | 781.5819 | 2.5511 | 26.484 | 57.83 | 43.8626 | 7.3997 | 58.1815 | 1.3955 | 6.2015 | 38.5419 | 71.9116 | 12.0084 | 188.129 | 94.0616 | 235.2858 | 8.6142 | 56.6565 | 3.141 | 118 | 38.1924 | 0 | 265.9094 | 0
6150 | 819.9406 | 3.3677 | 45.9736 | 94.2776 | 39.575 | 10.4869 | 66.8913 | 1.1949 | 6.425 | 37.7846 | 80.7964 | 15.2526 | 225.1763 | 121.2152 | 239.59 | 11.6976 | 56.6299 | 3.0874 | 191 | 43.8494 | 0 | 296.7363 | 0
6151 | 893.7971 | 3.6077 | 77.5585 | 114.615 | 35.4378 | 14.0176 | 97.6105 | 2.8792 | 9.6875 | 46.0771 | 105.3769 | 22.718 | 216.7397 | 184.3598 | 282.9152 | 22.323 | 60.0901 | 8.6844 | 272 | 61.5128 | 0 | 348.4746 | 0.16959
6152 | 988.7465 | 10.1691 | 100.8158 | 120.3519 | 33.3761 | 16.0364 | 128.6025 | 4.2036 | 15.341 | 66.471 | 135.1381 | 28.5097 | 302.1049 | 253.6313 | 382.0368 | 27.9223 | 70.0641 | 14.407 | 287 | 70.5119 | 0 | 416.0636 | 0.2495
6153 | 1058.8081 | 15.5873 | 106.3156 | 172.0401 | 33.7601 | 16.9278 | 150.3391 | 3.6105 | 19.56 | 81.9976 | 154.1342 | 34.2858 | 346.4633 | 306.3286 | 492.1281 | 27.7413 | 80.9527 | 15.6678 | 321 | 85.6394 | 0 | 474.928 | 0.22115
6154 | 1084.8316 | 17.1774 | 110.842 | 184.6756 | 36.3876 | 15.6269 | 163.4313 | 3.2246 | 22.1115 | 87.4854 | 162.0045 | 38.5347 | 368.704 | 338.3402 | 566.7939 | 27.9228 | 85.8707 | 15.8174 | 343 | 89.4937 | 0 | 504.1022 | 0.22198
6155 | 1100.776 | 14.9867 | 114.8092 | 189.3167 | 34.2885 | 17.9323 | 174.4966 | 3.4861 | 23.3805 | 88.6707 | 171.4534 | 37.5151 | 383.9326 | 354.7623 | 596.3689 | 27.7919 | 85.8636 | 16.2092 | 333 | 99.1063 | 0 | 523.3409 | 0.23714
6156 | 1102.3623 | 9.4794 | 114.7704 | 211.8054 | 32.5512 | 19.6494 | 178.9406 | 3.5648 | 20.3175 | 85.2325 | 181.9474 | 34.8561 | 398.08 | 363.1925 | 609.2979 | 27.8682 | 84.7645 | 16.7962 | 365 | 98.2139 | 0 | 536.2457 | 0.2153
6157 | 1117.4526 | 5.8242 | 116.5067 | 198.9164 | 35.1281 | 17.2287 | 189.5498 | 3.4734 | 18.0065 | 83.1717 | 187.5082 | 35.0149 | 418.1793 | 372.8637 | 610.0822 | 28.0436 | 84.0472 | 16.957 | 312 | 95.7319 | 0 | 537.441 | 0.27453
6158 | 1172.387 | 4.0856 | 114.8981 | 192.1078 | 37.2774 | 15.3132 | 190.1198 | 3.6863 | 22.865 | 84.7831 | 188.0379 | 35.7334 | 384.9697 | 380.7652 | 596.8268 | 28.4362 | 84.0298 | 16.7906 | 309 | 95.443 | 0 | 538.8996 | 0.28518
6159 | 1187.1636 | 3.9416 | 113.1697 | 150.5162 | 37.0749 | 15.6112 | 181.5797 | 3.6116 | 23.9916 | 77.9153 | 186.5584 | 36.1976 | 416.7203 | 370.162 | 590.6278 | 41.3541 | 84.4401 | 16.8616 | 296 | 84.6107 | 0 | 532.7595 | 0.24039
6160 | 1128.9192 | 4.8488 | 110.3095 | 172.1217 | 41.4931 | 11.4639 | 166.4439 | 3.3275 | 19.2938 | 67.5217 | 184.9333 | 34.5079 | 366.612 | 340.4305 | 562.1683 | -6.7671 | 83.314 | 17.0219 | 256 | 81.9186 | 0 | 486.6216 | 0.23865
6161 | 1056.0405 | 4.1405 | 105.7843 | 153.4265 | 43.5514 | 9.4796 | 149.9234 | 2.6227 | 16.0628 | 59.2713 | 172.9877 | 27.9968 | 376.98 | 281.8647 | 494.0908 | 28.3074 | 78 | 16.8074 | 217 | 71.7347 | 0 | 406.8102 | 0.17237
6162 | 993.8577 | 3.144 | 100.5928 | 135.2247 | 44.067 | 8.8051 | 145.7957 | 1.9848 | 11.419 | 53.273 | 144.1913 | 17.8515 | 302.1089 | 212.7251 | 423.2551 | 1.9942 | 72.1083 | 13.7329 | 220 | 60.5596 | 0 | 342.4304 | 0.037433
6163 | 925.4884 | 3.55 | 83.6763 | 114.8188 | 44.9475 | 7.849 | 111.07 | 1.999 | 6.7023 | 52.6762 | 117.8048 | 9.3956 | 308.646 | 180.6122 | 374.5183 | 12.0349 | 67.8836 | 8.3818 | 211 | 60.2185 | 0 | 300.111 | 0
6164 | 859.1328 | 4.1549 | 47.3575 | 78.5122 | 43.6794 | 9.0491 | 77.0473 | 2.0113 | 5.7973 | 53.4996 | 109.2905 | 7.4911 | 266.6664 | 178.7652 | 338.8187 | 10.1663 | 62.8472 | 5.9821 | 188 | 55.3959 | 0 | 269.806 | 0
6165 | 820.6453 | 4.7846 | 29.6381 | 80.551 | 43.2276 | 9.4429 | 70.584 | 1.5646 | 6.7572 | 46.2471 | 107.7424 | 7.0942 | 242.9576 | 169.6932 | 309.2555 | 8.4453 | 58.3874 | 5.667 | 164 | 53.1338 | 0 | 252.9765 | 0
6166 | 795.5518 | 3.7214 | 27.5366 | 59.1335 | 42.9884 | 9.4601 | 67.6983 | 1.3301 | 7.0941 | 33.9366 | 101.0388 | 8.4157 | 202.6054 | 150.896 | 284.3613 | 8.1471 | 56.1191 | 5.329 | 146 | 51.317 | 0 | 243.2276 | 0
6167 | 785.357 | 1.8101 | 26.5319 | 17.7935 | 44.9067 | 7.5133 | 68.6472 | 1.343 | 6.6483 | 25.3541 | 91.5555 | 10.0922 | 227.7504 | 136.1225 | 268.9747 | 8.6956 | 54.7524 | 5.1084 | 136 | 54.6511 | 0 | 237.8684 | 0
6168 | 778.9317 | 1.1623 | 25.955 | 69.1203 | 45.96 | 6.6063 | 68.934 | 1.516 | 6.2617 | 21.7086 | 85.1028 | 10.3091 | 187.4181 | 125.6297 | 259.2938 | 8.3159 | 53.5128 | 4.6665 | 137 | 53.1266 | 0 | 236.0492 | 0
6169 | 766.7913 | 1.234 | 76.996 | 24.3206 | 45.2583 | 7.358 | 65.2747 | 1.4474 | 6.4673 | 20.9303 | 81.857 | 10.267 | 195.0811 | 119.0738 | 251.0081 | 8.1612 | 52.8531 | 4.3581 | 129 | 54.1321 | 0 | 236.8312 | 0
6170 | 765.5838 | 1.1766 | 48.6471 | 46.184 | 45.6845 | 6.9197 | 63.5928 | 1.2996 | 6.4959 | 20.9217 | 80.8242 | 12.9172 | 228.8715 | 118.3881 | 242.9816 | 8.5008 | 52.641 | 4.1023 | 120 | 51.4185 | 0 | 237.1212 | 0
6171 | 761.9591 | 1.1103 | 61.4087 | 45.2098 | 45.8611 | 6.747 | 64.71 | 1.307 | 6.1305 | 22.5399 | 80.5481 | 18.915 | 201.0777 | 117.5547 | 234.0187 | 8.4519 | 52.4166 | 3.6595 | 120 | 46.2727 | 0 | 236.9522 | 0
6172 | 764.3985 | 1.5183 | 68.6453 | 66.8034 | 45.0969 | 7.4408 | 67.4373 | 1.3143 | 6.1864 | 30.0259 | 80.1945 | 18.0805 | 183.8822 | 114.0041 | 227.7646 | 8.3675 | 52.3531 | 3.4536 | 116 | 44.4828 | 0 | 237.5379 | 0
6173 | 773.2481 | 2.4673 | 66.035 | 64.6118 | 44.2221 | 8.1835 | 66.4543 | 1.294 | 6.3105 | 37.5117 | 80.7239 | 11.3316 | 219.0011 | 112.8931 | 232.4908 | 8.1567 | 52.5476 | 3.4674 | 110 | 42.8189 | 0 | 250.4697 | 0
6174 | 800.6785 | 4.2313 | 66.9649 | 76.0399 | 40.8188 | 11.4612 | 75.2906 | 1.4017 | 6.3985 | 37.7241 | 90.7607 | 14.005 | 203.923 | 132.3597 | 243.0397 | 12.0269 | 52.8402 | 3.5797 | 187 | 50.3445 | 0 | 289.0394 | 0
6175 | 886.8139 | 8.4411 | 67.2908 | 111.4609 | 36.6538 | 15.1069 | 108.6851 | 2.4689 | 6.4724 | 46.9295 | 117.5498 | 25.0272 | 228.0006 | 191.2735 | 297.0107 | 24.6268 | 56.001 | 9.3013 | 308 | 59.592 | 0 | 342.7364 | 0.029212
6176 | 995.2198 | 9.3124 | 66.8957 | 122.3814 | 34.7504 | 16.1071 | 139.2007 | 3.9578 | 11.8908 | 68.1218 | 151.7397 | 32.4088 | 275.2889 | 262.271 | 399.8166 | 33.4663 | 64.3825 | 16.0126 | 336 | 72.4867 | 0 | 404.9783 | 0.10763
6177 | 1062.2176 | 5.6138 | 91.2791 | 171.5179 | 31.0368 | 19.2723 | 154.0554 | 4.2054 | 19.5645 | 80.9267 | 174.4526 | 33.595 | 311.2061 | 311.2169 | 519.6151 | 38.555 | 74.3525 | 17.8247 | 390 | 76.9809 | 0 | 471.2824 | 0.16131
6178 | 1100.5353 | 3.9997 | 47.9143 | 180.5157 | 31.1727 | 19.9062 | 163.1714 | 3.9645 | 23.4222 | 86.9412 | 181.7723 | 33.9012 | 384.814 | 338.0632 | 589.387 | 39.5082 | 80.9665 | 17.8114 | 372 | 81.092 | 0 | 504.662 | 0.27446
6179 | 1116.4103 | 8.1872 | 60.0368 | 210.1876 | 34.1476 | 17.9555 | 174.5742 | 3.986 | 25.171 | 93.7451 | 186.1297 | 34.6787 | 363.5846 | 359.0118 | 604.1012 | 39.696 | 83.7813 | 17.8087 | 344 | 87.5271 | 0 | 508.6335 | 0.24482
6180 | 1163.2075 | 9.0868 | 93.4819 | 264.9386 | 33.5745 | 18.4385 | 190.6079 | 3.8741 | 24.1387 | 94.2337 | 190.8506 | 35.3969 | 381.4761 | 376.9746 | 600.4016 | 58.5613 | 84.5151 | 17.7564 | 339 | 87.3229 | 0 | 520.5353 | 0.2653
6181 | 1201.4375 | 7.4095 | 67.1466 | 186.9796 | 32.7403 | 18.9606 | 198.02 | 3.7678 | 21.1828 | 89.7817 | 193.2299 | 35.6823 | 524.5677 | 383.9838 | 587.7488 | 40.13 | 84.0111 | 17.7599 | 291 | 86.473 | 0 | 533.9088 | 0.29457
6182 | 1201.4375 | 7.4095 | 49.8305 | 140.9946 | 32.7403 | 18.9606 | 198.02 | 3.7678 | 20.0258 | 87.8661 | 193.8148 | 35.6823 | 360.8322 | 384.6172 | 581.6719 | 28.3912 | 83.5915 | 17.7599 | 274 | 86.473 | 0 | 537.815 | 0.15815
6183 | 1196.2001 | 5.3195 | 60.1287 | 171.7782 | 33.5199 | 17.9839 | 197.3723 | 3.5932 | 20.0258 | 84.3279 | 194.2543 | 34.224 | 330.7539 | 376.7804 | 579.0495 | 34.3242 | 83.0737 | 18.0863 | 276 | 86.7574 | 0 | 526.4124 | 0.17084
6184 | 1169.3059 | 3.6929 | 67.2824 | 145.2292 | 35.2548 | 16.0029 | 189.4683 | 3.3497 | 19.1054 | 73.9944 | 193.4138 | 32.087 | 276.94 | 350.9606 | 556.0525 | 33.3053 | 80.6989 | 17.9346 | 272 | 83.3879 | 0 | 479.8065 | 0.11225
6185 | 1110.9808 | 3.3363 | 67.7367 | 175.2818 | 40.0964 | 11.0738 | 182.9043 | 2.5989 | 14.9453 | 61.3833 | 179.9437 | 29.8714 | 321.1161 | 290.1211 | 506.3659 | 25.6336 | 76.0155 | 17.1368 | 232 | 69.4856 | 0 | 406.4702 | 0.087691
6186 | 1046.6993 | 3.0213 | 66.7009 | 129.8449 | 42.9411 | 8.0064 | 154.6442 | 2.0471 | 16.7083 | 52.044 | 147.5222 | 22.4658 | 350.3672 | 217.9565 | 455.7879 | 23.5116 | 70.8698 | 15.2802 | 222 | 64.1525 | 0 | 344.871 | 0.031924
6187 | 961.1963 | 3.5372 | 67.1866 | 108.6759 | 42.9623 | 7.643 | 118.7314 | 1.9821 | 17.5192 | 50.3025 | 117.2739 | 11.4207 | 279.2808 | 171.9829 | 399.981 | 20.3892 | 67.2323 | 10.5752 | 226 | 63.052 | 0 | 302.1023 | 0
6188 | 892.4085 | 3.9399 | 67.244 | 105.7889 | 43.1656 | 7.5768 | 116.4291 | 1.5748 | 11.7034 | 51.3931 | 106.2798 | 7.3788 | 271.6612 | 152.1933 | 335.8913 | 15.2902 | 63.5817 | 7.8269 | 199 | 57.8379 | 0 | 268.7189 | 0
6189 | 856.6029 | 3.9978 | 67.8003 | 102.1826 | 42.8492 | 7.6312 | 106.8763 | 1.4877 | 8.641 | 42.1477 | 103.2906 | 8.6285 | 259.6309 | 139.5028 | 296.9223 | 11.2305 | 59.4906 | 6.6392 | 197 | 51.5093 | 0 | 250.7788 | 0
6190 | 836.3236 | 2.9892 | 67.0231 | 99.79 | 40.7301 | 8.9973 | 84.7033 | 1.4501 | 7.6336 | 28.2214 | 94.5157 | 10.8524 | 244.9763 | 125.6974 | 282.4347 | 9.4581 | 57.0322 | 5.5099 | 150 | 49.1866 | 0 | 241.3597 | 0
6191 | 823.228 | 1.7671 | 67.2702 | 98.8943 | 39.7159 | 9.5163 | 77.8269 | 1.3551 | 6.8057 | 21.3017 | 83.3441 | 11.7601 | 247.8899 | 113.8274 | 269.4939 | 9.2922 | 55.6708 | 4.991 | 142 | 50.1075 | 0 | 233.0663 | 0
6192 | 813.5726 | 1.4938 | 67.134 | 38.67 | 39.2998 | 9.5344 | 73.9007 | 1.4291 | 6.6172 | 19.0366 | 78.1594 | 11.5649 | 227.9452 | 103.1128 | 261.9981 | 9.4441 | 54.6229 | 4.4859 | 124 | 47.7076 | 0 | 229.6269 | 0
6193 | 802.078 | 1.2826 | 67.0423 | 69.8633 | 39.9145 | 8.7714 | 77.851 | 1.4931 | 6.4885 | 18.2307 | 76.2777 | 11.3954 | 218.1239 | 97.919 | 259.3829 | 9.5385 | 54.1515 | 4.3164 | 122 | 45.8318 | 0 | 229.5101 | 0
6194 | 812.9243 | 1.1166 | 67.1287 | 67.7982 | 41.9206 | 7.1096 | 79.4532 | 1.3981 | 6.3205 | 18.149 | 73.8085 | 14.0749 | 248.0212 | 101.5399 | 252.9204 | 9.2795 | 54.5488 | 4.3173 | 119 | 45.3071 | 0 | 229.58 | 0
6195 | 809.906 | 1.4425 | 66.6887 | 38.1039 | 41.7652 | 7.3267 | 77.627 | 1.3361 | 6.3705 | 19.7455 | 71.0909 | 20.3359 | 223.0434 | 107.3889 | 243.4344 | 9.1966 | 54.8059 | 4.2191 | 114 | 45.4636 | 0 | 229.867 | 0
6196 | 810.0682 | 1.7627 | 90.9957 | 94.1202 | 40.4854 | 8.296 | 77.4559 | 1.3267 | 6.456 | 27.4375 | 70.1226 | 19.0826 | 232.32 | 109.2059 | 238.6849 | 9.2683 | 54.2382 | 3.5543 | 121 | 46.1323 | 0 | 235.1057 | 0
6197 | 823.7814 | 2.4422 | 49.4432 | 80.3216 | 40.7993 | 7.9005 | 77.6593 | 1.4023 | 6.2284 | 35.7142 | 71.125 | 12.4768 | 220.2107 | 109.6234 | 238.589 | 9.09 | 53.7683 | 2.9116 | 108 | 46.1475 | 0 | 250.7128 | 0
6198 | 863.3126 | 3.8896 | 62.3892 | 88.3623 | 40.1831 | 8.9071 | 87.889 | 1.3502 | 6.2422 | 36.6305 | 80.1137 | 12.9298 | 207.4181 | 133.1367 | 249.7111 | 12.3036 | 53.5767 | 3.4663 | 182 | 49.9498 | 0 | 284.8577 | 0
6199 | 949.7625 | 5.8217 | 87.1515 | 121.0492 | 36.8909 | 12.4123 | 112.8036 | 2.0548 | 10.0203 | 43.7111 | 105.503 | 17.8972 | 303.007 | 190.1877 | 295.8375 | 24.1176 | 56.8195 | 10.0179 | 293 | 56.329 | 0 | 337.6767 | 0.10428
6200 | 1049.4823 | 8.6634 | 107.1415 | 132.3134 | 36.1979 | 13.1952 | 135.9242 | 3.3217 | 17.1948 | 58.8182 | 140.7771 | 22.9327 | 245.653 | 255.7771 | 398.0883 | 33.792 | 66.015 | 15.7001 | 316 | 73.9962 | 0 | 404.4196 | 0.12621
6201 | 1118.7381 | 14.5187 | 110.3403 | 197.4096 | 33.8813 | 15.4846 | 148.616 | 3.6433 | 20.1882 | 71.5795 | 167.5701 | 29.8065 | 302.3092 | 305.9811 | 511.3559 | 38.3023 | 76.9377 | 16.1166 | 382 | 74.5598 | 0 | 471.7716 | 0.15008
6202 | 1187.5766 | 16.644 | 110.4844 | 163.046 | 35.6844 | 14.2109 | 163.0499 | 3.638 | 22.5362 | 80.4113 | 181.989 | 34.2679 | 326.6241 | 335.3135 | 592.3276 | 39.9918 | 83.5527 | 15.8905 | 351 | 80.435 | 0 | 499.0726 | 0.25145
6203 | 1220.4017 | 15.0263 | 114.6256 | 208.1349 | 35.7035 | 15.3423 | 172.819 | 3.3747 | 27.1169 | 83.1225 | 188.3684 | 34.2287 | 376.5851 | 355.2958 | 635.9463 | 40.1063 | 85.3011 | 16.6236 | 339 | 92.2683 | 0 | 498.4741 | 0.25063
6204 | 1228.3713 | 10.7587 | 115.9556 | 194.539 | 36.5326 | 15.3156 | 179.7226 | 3.1271 | 26.965 | 79.1717 | 185.5535 | 36.0725 | 363.2661 | 365.1907 | 626.4706 | 40.1808 | 84.5552 | 16.8993 | 381 | 85.5798 | 0 | 509.5201 | 0.27632
6205 | 1238.8973 | 5.4883 | 115.7054 | 162.344 | 35.7528 | 15.1853 | 187.3733 | 3.431 | 24.5655 | 75.8454 | 183.0845 | 36.1287 | 362.7683 | 364.992 | 610.0718 | 40.4616 | 82.7821 | 17.8388 | 332 | 88.5988 | 0 | 518.2604 | 0.29936
6206 | 1224.9328 | 3.5357 | 116.2666 | 215.1095 | 33.348 | 16.5006 | 194.8839 | 3.303 | 24.4549 | 76.5167 | 185.5551 | 34.9603 | 353.9303 | 363.266 | 606.311 | 40.9956 | 81.872 | 18.6135 | 287 | 93.067 | 0 | 517.6927 | 0.30262
6207 | 1219.0415 | 3.995 | 116.2672 | 198.6845 | 34.6947 | 15.8224 | 196.4093 | 2.914 | 22.8365 | 70.7919 | 189.693 | 33.6962 | 477.4812 | 356.6648 | 610.4128 | 37.9789 | 81.3497 | 18.9793 | 282 | 83.4371 | 0 | 509.3868 | 0.26373
6208 | 1169.6242 | 3.823 | 111.0404 | 178.6963 | 40.5481 | 11.1059 | 187.6102 | 2.699 | 13.1011 | 61.4823 | 194.3248 | 30.1124 | 281.7379 | 337.7355 | 590.4272 | 29.2604 | 79.0822 | 18.9061 | 281 | 74.8264 | 0 | 469.097 | 0.19803
6209 | 1099.2728 | 2.9744 | 104.6992 | 156.1329 | 42.1592 | 8.0541 | 166.2131 | 2.4627 | 9.502 | 52.5953 | 186.7401 | 25.3739 | 298.8454 | 283.3462 | 526.6578 | 15.6254 | 74.2214 | 17.9003 | 250 | 64.8675 | 0 | 401.4486 | 0.14083
6210 | 1055.5749 | 2.6397 | 102.32 | 137.6204 | 42.0926 | 7.5728 | 128.2963 | 2.2369 | 13.1992 | 45.4764 | 155.962 | 20.2341 | 312.2202 | 203.5875 | 448.7258 | 9.2697 | 68.0189 | 14.3716 | 228 | 56.9916 | 0 | 345.185 | 0.060326
6211 | 1007.1572 | 3.193 | 84.8204 | 117.1093 | 42.0899 | 7.5027 | 90.3672 | 2.0349 | 10.4555 | 49.4788 | 123.5247 | 14.2171 | 314.3558 | 155.934 | 381.9973 | 9.2915 | 62.5892 | 8.7314 | 200 | 55.8327 | 0 | 298.3176 | 0
6212 | 937.7758 | 3.4715 | 48.1779 | 52.8711 | 42.5314 | 6.9186 | 77.338 | 1.982 | 7.9115 | 55.2548 | 111.5273 | 10.6266 | 270.7283 | 141.1531 | 344.0658 | 9.3243 | 59.4638 | 6.2623 | 185 | 55.7952 | 0 | 260.5646 | 0
6213 | 888.9339 | 3.5663 | 31.9735 | 62.2434 | 42.346 | 7.4227 | 75.2374 | 1.562 | 7.4578 | 46.6911 | 107.8061 | 9.4453 | 291.2327 | 128.4702 | 314.4314 | 9.4897 | 57.0959 | 5.7066 | 173 | 54.1389 | 0 | 245.2014 | 0
6214 | 866.6102 | 2.9005 | 31.4607 | 78.0897 | 41.9099 | 7.6201 | 76.8921 | 1.2931 | 6.9655 | 33.066 | 97.936 | 9.7392 | 232.6277 | 122.1474 | 273.4888 | 9.3049 | 54.7886 | 5.4236 | 153 | 50.269 | 0 | 241.1095 | 0
6215 | 847.2392 | 1.7068 | 29.7361 | 60.9005 | 41.7067 | 7.5463 | 74.552 | 1.2924 | 6.572 | 27.1134 | 87.2393 | 10.3963 | 183.2265 | 117.2272 | 251.9613 | 10.1225 | 53.6214 | 4.9059 | 140 | 49.0378 | 0 | 238.9661 | 0
6216 | 824.7163 | 1.2597 | 38.8482 | 52.4542 | 41.5226 | 7.6197 | 64.2763 | 1.2887 | 6.3105 | 25.5965 | 82.243 | 10.547 | 216.8617 | 110.1041 | 248.9881 | 12.4944 | 52.5882 | 3.9694 | 129 | 48.4243 | 0 | 238.8523 | 0
6217 | 807.437 | 1.1725 | 21.4732 | 51.4208 | 40.8212 | 7.6738 | 59.5584 | 1.2813 | 6.1195 | 24.9926 | 80.811 | 13.1731 | 256.2668 | 108.1981 | 256.4412 | 13.4954 | 51.7932 | 3.4988 | 125 | 49.2735 | 0 | 239.1141 | 0
6218 | 795.6448 | 1.2068 | 34.46 | 60.8193 | 41.0014 | 7.5456 | 58.5168 | 1.3753 | 6.1334 | 23.8651 | 80.4054 | 17.9762 | 233.3692 | 114.0696 | 259.993 | 13.3315 | 51.6565 | 3.9897 | 123 | 47.0348 | 0 | 237.0889 | 0
6219 | 788.1387 | 1.3873 | 43.9416 | 40.6993 | 42.0826 | 6.874 | 52.9938 | 1.4994 | 6.3527 | 23.8711 | 78.9879 | 24.0266 | 271.875 | 122.2653 | 248.8431 | 13.6193 | 51.8402 | 3.8833 | 117 | 46.0902 | 0 | 237.0849 | 0
6220 | 796.1734 | 1.8037 | 47.2552 | 75.1216 | 41.713 | 7.3074 | 53.1447 | 1.4081 | 6.3759 | 31.0822 | 75.6977 | 21.5226 | 206.2078 | 123.57 | 234.0009 | 12.8804 | 51.924 | 3.2551 | 118 | 45.0904 | 0 | 244.6688 | 0
6221 | 812.2521 | 2.6159 | 41.5201 | 91.6147 | 42.3635 | 6.9347 | 55.3806 | 1.286 | 6.266 | 39.5203 | 72.4063 | 13.4634 | 185.9117 | 118.4592 | 239.8065 | 10.3592 | 51.6879 | 2.9941 | 110 | 44.9403 | 0 | 260.1358 | 0
6222 | 837.1803 | 3.5774 | 52.3229 | 86.8274 | 40.3767 | 8.8224 | 65.4016 | 1.1294 | 6.3277 | 39.1651 | 79.3063 | 15.5566 | 209.0671 | 126.1647 | 262.0129 | 13.0636 | 51.4947 | 2.8821 | 205 | 51.1103 | 0 | 291.4252 | 0
6223 | 909.0553 | 4.4926 | 81.9869 | 84.8912 | 35.7128 | 12.8858 | 94.0967 | 2.0644 | 7.382 | 43.9043 | 105.8223 | 25.7116 | 230.8082 | 174.5097 | 321.0207 | 24.7283 | 54.7579 | 8.2863 | 245 | 60.6922 | 0 | 342.6669 | 0.16209
6224 | 1008.1513 | 5.9476 | 101.5002 | 172.9639 | 32.4768 | 15.0066 | 115.3637 | 3.4794 | 11.3921 | 61.0193 | 141.2411 | 31.244 | 289.0963 | 246.0497 | 415.3897 | 34.8312 | 63.5005 | 13.5114 | 298 | 72.8873 | 0 | 407.4567 | 0.23881
6225 | 1108.573 | 6.3624 | 109.4735 | 183.8691 | 33.0004 | 14.5726 | 135.1033 | 4.1024 | 17.7594 | 75.2395 | 166.5901 | 34.8394 | 303.735 | 299.5031 | 496.8274 | 39.6653 | 73.3202 | 15.1047 | 410 | 83.2118 | 0 | 475.2253 | 0.17774
6226 | 1172.5669 | 6.2236 | 113.747 | 184.4523 | 34.6627 | 14.2251 | 141.8346 | 3.9661 | 21.2515 | 80.7604 | 176.6454 | 33.9991 | 336.893 | 328.3308 | 555.3349 | 40.8608 | 80.0094 | 16.3045 | 386 | 90.0584 | 0 | 515.1006 | 0.17381
6227 | 1194.338 | 6.5275 | 117.0109 | 189.9768 | 35.2008 | 14.2289 | 151.0053 | 3.7611 | 23.1598 | 85.3007 | 181.6324 | 29.8655 | 359.8636 | 349.5014 | 585.1023 | 39.8807 | 83.0304 | 16.6896 | 323 | 92.7382 | 0 | 529.3614 | 0.16536
6228 | 1184.0784 | 6.5947 | 116.2728 | 188.5519 | 34.9036 | 14.2411 | 164.8921 | 4.1277 | 20.9867 | 83.2777 | 187.3539 | 30.5245 | 387.2409 | 360.2983 | 589.6551 | 40.408 | 83.714 | 16.3927 | 327 | 88.6816 | 0 | 547.5031 | 0.20176
6229 | 1169.6587 | 5.016 | 117.2558 | 166.9465 | 33.2499 | 15.7089 | 166.4826 | 4.3105 | 15.6806 | 76.5319 | 191.4523 | 34.0189 | 360.5831 | 364.253 | 588.9389 | 42.2854 | 84.1445 | 16.7303 | 308 | 93.3511 | 0 | 569.0977 | 0.23399
6230 | 1159.4388 | 3.6729 | 116.2686 | 215.6762 | 34.5131 | 14.6527 | 161.2613 | 4.4914 | 17.2552 | 75.2311 | 194.5084 | 32.3436 | 351.563 | 367.8121 | 591.1329 | 42.3304 | 84.7069 | 16.8453 | 296 | 94.7416 | 0 | 580.3076 | 0.17391
6231 | 1120.8373 | 3.2095 | 157.3903 | 195.1326 | 34.4298 | 15.0381 | 155.2333 | 3.9874 | 19.6244 | 71.719 | 194.7862 | 29.8574 | 392.4889 | 356.9786 | 584.6459 | 37.7889 | 84.0934 | 16.479 | 300 | 86.8253 | 0 | 564.9541 | 0.14288
6232 | 1065.0222 | 2.6887 | 85.1605 | 182.5176 | 36.4639 | 13.1006 | 145.1189 | 2.8158 | 19.4043 | 63.5185 | 190.1084 | 27.5316 | 350.0021 | 319.1623 | 543.1709 | 22.905 | 80.6256 | 16.6914 | 274 | 77.3008 | 0 | 510.333 | 0.13422
6233 | 1001.4154 | 2.0938 | 79.6633 | 143.0427 | 38.9773 | 10.2175 | 126.1037 | 1.5408 | 18.2013 | 54.0817 | 177.1319 | 22.6915 | 219.1805 | 252.3695 | 467.7146 | 11.8124 | 74.659 | 16.3953 | 271 | 66.1747 | 0 | 430.3064 | 0.062169
6234 | 937.4221 | 2.5317 | 45.0485 | 79.6985 | 39.4707 | 9.3959 | 90.7383 | 1.0738 | 15.158 | 49.5136 | 148.7819 | 17.0535 | 269.153 | 191.1352 | 390.5551 | 9.5822 | 67.3132 | 13.1686 | 239 | 57.3355 | 0 | 354.2211 | 0.015809
6235 | 886.1428 | 2.9601 | 24.9462 | 87.4128 | 41.359 | 7.4509 | 63.398 | 1.3314 | 13.231 | 56.3094 | 119.8282 | 10.19 | 264.7055 | 161.0744 | 346.0102 | 9.5241 | 59.4096 | 8.2315 | 220 | 55.6272 | 0 | 304.0617 | 0
6236 | 849.3935 | 3.1467 | 23.7003 | 105.199 | 39.8758 | 8.7365 | 55.8829 | 1.3933 | 10.0011 | 62.026 | 108.5546 | 7.1227 | 257.4503 | 146.0091 | 323.1673 | 9.6068 | 54.4222 | 5.6578 | 209 | 58.1087 | 0 | 282.291 | 0
6237 | 837.512 | 3.9386 | 23.3976 | 103.7233 | 40.2408 | 8.8729 | 54.1779 | 1.3172 | 8.4785 | 51.2551 | 102.3282 | 6.8759 | 294.1202 | 133.6239 | 302.265 | 9.3978 | 52.4435 | 4.8112 | 204 | 55.797 | 0 | 281.4027 | 0
6238 | 821.7079 | 3.2566 | 22.9535 | 101.9459 | 42.6395 | 7.0669 | 52.204 | 1.3203 | 7.5964 | 34.6744 | 92.0275 | 6.6405 | 266.3081 | 119.4809 | 289.3861 | 9.3528 | 51.0573 | 4.4377 | 185 | 50.2875 | 0 | 292.6658 | 0
6239 | 794.6991 | 1.8619 | 23.2623 | 101.2485 | 42.7218 | 6.606 | 48.2338 | 1.3338 | 6.8428 | 26.0499 | 85.674 | 6.5086 | 249.0311 | 106.0958 | 288.0244 | 9.408 | 50.6056 | 4.3193 | 164 | 47.5552 | 0 | 302.023 | 0
6240 | 785.7052 | 1.5791 | 23.1822 | 83.4036 | 42.4617 | 6.7408 | 49.9193 | 1.5729 | 6.7047 | 23.9168 | 83.2129 | 6.5355 | 319.7483 | 104.5985 | 285.3164 | 9.4028 | 50.5844 | 4.3643 | 145 | 46.8888 | 0 | 305.2757 | 0
6241 | 785.5422 | 1.5852 | 27.0207 | 79.6178 | 41.2051 | 7.3446 | 52.206 | 1.5111 | 6.5381 | 23.5717 | 79.4547 | 6.5065 | 242.0079 | 107.8623 | 267.5983 | 9.6362 | 50.6049 | 4.102 | 146 | 46.5168 | 0 | 304.3369 | 0
6242 | 778.0972 | 1.5028 | 39.9451 | 94.5229 | 39.8525 | 7.6376 | 52.02 | 1.3518 | 6.554 | 23.9408 | 75.2491 | 6.7406 | 243.9285 | 112.2154 | 249.5439 | 9.2904 | 51.0743 | 4.01 | 152 | 45.8997 | 0 | 297.5147 | 0
6243 | 777.4444 | 1.3428 | 45.9738 | 101.1644 | 39.5661 | 7.617 | 50.3854 | 1.3673 | 6.5308 | 25.617 | 73.0581 | 6.8124 | 226.6833 | 117.4119 | 248.7727 | 9.1598 | 51.2492 | 3.991 | 136 | 45.5796 | 0 | 285.2544 | 0
6244 | 774.1343 | 1.6236 | 39.0043 | 93.927 | 39.6527 | 7.5359 | 49.6833 | 1.3669 | 6.3004 | 31.4256 | 72.4139 | 6.5989 | 209.035 | 117.1887 | 251.7592 | 9.3233 | 51.044 | 3.8525 | 136 | 44.9373 | 0 | 268.6886 | 0
6245 | 777.7958 | 2.6685 | 28.8094 | 81.0313 | 39.586 | 7.6019 | 49.9547 | 1.3742 | 6.0528 | 36.7804 | 72.3299 | 6.4276 | 245.0247 | 113.5737 | 248.3742 | 9.3934 | 50.8959 | 3.4064 | 128 | 44.3239 | 0 | 254.4725 | 0
6246 | 793.2092 | 3.269 | 34.708 | 63.3894 | 39.5283 | 7.656 | 48.2419 | 1.2005 | 6.2365 | 31.6073 | 71.6934 | 5.3668 | 225.0739 | 103.3275 | 246.6283 | 9.3072 | 50.8757 | 2.948 | 132 | 44.41 | 0 | 249.9628 | 0
6247 | 810.3972 | 2.0186 | 45.7428 | 104.3934 | 38.824 | 8.3235 | 52.5528 | 1.2515 | 6.9975 | 22.2534 | 72.8535 | 5.1565 | 205.4518 | 93.5361 | 238.5757 | 8.881 | 50.8552 | 3.0959 | 121 | 48.4085 | 0 | 250.6916 | 0.15874
6248 | 833.9577 | 1.5225 | 57.6201 | 107.4839 | 39.4268 | 7.7486 | 61.4265 | 1.2424 | 6.16 | 18.5193 | 89.4066 | 7.8918 | 214.7297 | 92.9954 | 229.7696 | 8.8029 | 50.9602 | 3.8314 | 118 | 52.8819 | 0 | 251.261 | 0.26203
6249 | 872.1804 | 1.6074 | 80.7048 | 125.206 | 39.5884 | 7.5933 | 73.3889 | 1.3305 | 5.4583 | 19.6211 | 118.8853 | 11.4507 | 247.3569 | 97.2424 | 228.0812 | 8.7874 | 51.5087 | 6.28 | 151 | 57.3167 | 0 | 251.2782 | 0.3002
6250 | 885.0968 | 1.5862 | 95.2345 | 120.8447 | 39.5545 | 7.6257 | 79.4417 | 2.0592 | 5.3249 | 24.0237 | 134.6861 | 13.0422 | 226.037 | 104.8845 | 228.1628 | 8.5605 | 52.111 | 11.1897 | 172 | 59.6254 | 0 | 255.5689 | 0.28191
6251 | 891.8002 | 1.3953 | 97.545 | 158.1009 | 39.5824 | 7.5979 | 78.785 | 2.8346 | 5.7001 | 27.8346 | 123.2092 | 10.2701 | 248.9125 | 109.6441 | 226.7271 | 8.8155 | 52.3071 | 13.3502 | 193 | 57.5589 | 0 | 258.4424 | 0.26632
6252 | 877.4493 | 1.2585 | 98.3676 | 120.2244 | 39.563 | 7.6158 | 79.2683 | 3.3685 | 5.9562 | 29.2377 | 100.5531 | 8.5466 | 208.6915 | 115.5657 | 223.867 | 8.7335 | 52.5442 | 13.6005 | 189 | 56.8689 | 0 | 256.6584 | 0.29503
6253 | 865.676 | 1.3832 | 87.851 | 101.5975 | 39.6129 | 7.5696 | 74.6027 | 2.1586 | 5.765 | 30.065 | 88.8628 | 11.6472 | 266.5802 | 127.7147 | 226.2785 | 8.5564 | 52.863 | 14.177 | 188 | 57.0374 | 0 | 262.7843 | 0.31894
6254 | 883.0947 | 1.5187 | 59.3625 | 102.0795 | 40.281 | 6.936 | 65.8175 | 1.0194 | 5.8746 | 30.4728 | 87.6679 | 13.2904 | 210.4696 | 139.1608 | 231.684 | 8.65 | 52.3978 | 14.6755 | 182 | 55.7831 | 0 | 268.5513 | 0.31845
6255 | 888.3545 | 1.4356 | 45.6534 | 102.1275 | 39.1472 | 8.0147 | 54.6847 | 0.94974 | 6.1639 | 29.9023 | 88.422 | 12.3973 | 302.1749 | 140.8205 | 245.7104 | 8.994 | 51.2533 | 15.2544 | 199 | 54.9175 | 0 | 262.8588 | 0.26968
6256 | 870.3978 | 1.5057 | 45.5128 | 101.0943 | 38.5684 | 8.5628 | 48.654 | 1.1251 | 6.567 | 26.5771 | 88.2604 | 10.5114 | 219.6674 | 137.0111 | 259.297 | 9.0846 | 51.052 | 15.5192 | 199 | 53.5609 | 0 | 253.8441 | 0.24919
6257 | 858.2548 | 1.5727 | 41.9279 | 100.4528 | 37.8007 | 9.2902 | 54.614 | 1.0894 | 6.6195 | 23.3885 | 90.3117 | 8.0673 | 224.4466 | 133.6332 | 274.6726 | 8.5214 | 51.5607 | 13.1292 | 184 | 53.0275 | 0 | 248.896 | 0.18199
6258 | 844.8274 | 1.8727 | 32.4727 | 99.0824 | 38.3715 | 8.7482 | 65.8532 | 0.95296 | 6.4235 | 25.1793 | 97.1435 | 5.6438 | 222.2934 | 129.9376 | 280.1332 | 8.4086 | 51.6168 | 8.0841 | 197 | 52.6275 | 0 | 253.8143 | 0.065431
6259 | 834.8136 | 2.9171 | 25.3421 | 99.242 | 39.3235 | 7.8484 | 59.0247 | 1.3077 | 6.0445 | 34.0881 | 95.1839 | 5.522 | 230.8041 | 129.1225 | 278.0873 | 9.0701 | 51.4953 | 5.7234 | 190 | 50.6702 | 0 | 262.1893 | 0
6260 | 827.0606 | 3.2919 | 21.5836 | 101.2472 | 40.3014 | 6.9251 | 51.6932 | 1.5454 | 6.9525 | 41.966 | 83.092 | 6.1294 | 247.8021 | 131.2841 | 272.588 | 9.2057 | 51.5398 | 5.5867 | 185 | 49.3898 | 0 | 262.7145 | 0
6261 | 808.747 | 3.4366 | 20.7498 | 101.8942 | 39.8439 | 7.3585 | 51.6609 | 1.5751 | 7.816 | 38.2223 | 77.3019 | 6.3757 | 222.9989 | 130.418 | 271.3077 | 9.2721 | 52.0774 | 5.5263 | 173 | 47.3565 | 0 | 258.8936 | 0
6262 | 802.4959 | 3.0573 | 20.4057 | 101.6659 | 38.8768 | 8.2715 | 51.7639 | 1.6523 | 8.1041 | 29.8889 | 76.7717 | 6.1896 | 236.5017 | 125.5034 | 273.896 | 9.2863 | 52.4567 | 5.2517 | 165 | 46.3461 | 0 | 255.1081 | 0
6263 | 786.1446 | 1.9525 | 20.3101 | 101.2417 | 39.3112 | 7.8592 | 47.6163 | 1.5368 | 6.9835 | 27.6329 | 75.1411 | 6.4455 | 224.2237 | 127.3226 | 269.6308 | 10.0816 | 52.0571 | 5.0008 | 156 | 49.3857 | 0 | 255.2274 | 0
6264 | 780.3066 | 1.4077 | 20.189 | 93.8629 | 39.5891 | 7.5979 | 48.0939 | 1.433 | 6.5348 | 27.302 | 74.1234 | 6.2826 | 210.2026 | 149.7644 | 262.768 | 12.4963 | 51.3187 | 4.4827 | 149 | 48.9677 | 0 | 257.8551 | 0
6265 | 783.2309 | 1.3823 | 20.2642 | 106.8693 | 38.8907 | 8.2611 | 50.9578 | 1.4427 | 6.3601 | 24.5066 | 74.071 | 5.966 | 249.0656 | 170.0733 | 262.3177 | 13.7908 | 50.7256 | 4.2861 | 145 | 48.381 | 0 | 254.0154 | 0
6266 | 770.3675 | 1.4054 | 20.4395 | 103.2231 | 39.9912 | 7.2127 | 51.3027 | 1.4618 | 5.9619 | 23.8955 | 73.8775 | 5.8821 | 222.0022 | 173.5158 | 268.2511 | 13.0374 | 50.7243 | 4.3035 | 145 | 49.4234 | 0 | 249.3982 | 0
6267 | 766.7786 | 1.4749 | 20.3411 | 101.0731 | 39.1214 | 8.0406 | 47.1887 | 1.4728 | 6.27 | 25.3936 | 72.7805 | 5.837 | 219.1448 | 175.0178 | 267.5243 | 10.6348 | 50.8698 | 4.1363 | 134 | 55.637 | 0 | 249.2012 | 0
6268 | 769.1087 | 1.9563 | 20.6729 | 94.5634 | 39.3363 | 7.8361 | 47.612 | 1.7285 | 7.9141 | 26.4868 | 71.4075 | 5.9263 | 215.134 | 175.8212 | 258.1365 | 9.1976 | 50.696 | 3.5792 | 130 | 57.5723 | 0 | 249.3071 | 0
6269 | 779.4416 | 2.968 | 20.3523 | 107.1412 | 40.285 | 6.9359 | 51.149 | 1.6675 | 8.2115 | 26.418 | 71.0128 | 5.9153 | 236.6538 | 167.0662 | 248.1893 | 9.2454 | 50.5882 | 2.8709 | 119 | 57.1085 | 0 | 247.7757 | 0
6270 | 786.5044 | 3.1043 | 20.1247 | 102.4378 | 39.8502 | 7.3517 | 48.238 | 1.3887 | 6.8238 | 23.5438 | 70.0831 | 5.0664 | 216.6721 | 136.482 | 237.47 | 9.3225 | 50.5342 | 2.6245 | 118 | 59.8823 | 0 | 244.255 | 0
6271 | 804.4745 | 1.8354 | 19.8298 | 98.7915 | 38.8681 | 8.2806 | 45.8119 | 1.1721 | 5.9212 | 19.449 | 67.6852 | 4.8638 | 218.2827 | 103.6994 | 226.4755 | 9.1407 | 50.3701 | 2.8398 | 131 | 56.8052 | 0 | 238.9848 | 0.050717
6272 | 817.7564 | 1.0451 | 19.7729 | 98.5914 | 39.2433 | 7.9226 | 48.3273 | 1.1416 | 5.6676 | 17.5858 | 65.8744 | 7.3177 | 238.9828 | 92.6063 | 215.7809 | 8.5515 | 50.4533 | 3.5735 | 135 | 47.3024 | 0 | 236.9728 | 0.074864
6273 | 829.7807 | 1.0546 | 19.9485 | 98.4198 | 39.6719 | 7.5146 | 49.179 | 1.1869 | 5.5629 | 19.8876 | 65.3727 | 8.511 | 214.8107 | 100.1097 | 215.9068 | 8.4427 | 51.373 | 6.1715 | 168 | 43.753 | 0 | 238.4862 | 0.097289
6274 | 852.0433 | 1.0876 | 20.0348 | 97.7038 | 40.3006 | 6.9171 | 50.1695 | 1.1216 | 6.3086 | 25.4637 | 65.7135 | 8.5744 | 206.8403 | 112.8768 | 219.2489 | 8.7912 | 52.0925 | 11.0673 | 178 | 46.0274 | 0 | 240.2141 | 0.15197
6275 | 858.9917 | 1.1321 | 20.1081 | 97.6728 | 39.8072 | 7.3832 | 63.3478 | 1.1016 | 5.8497 | 30.2 | 69.7007 | 9.041 | 235.6405 | 121.459 | 221.9957 | 8.7591 | 51.6632 | 13.814 | 154 | 47.412 | 0 | 243.1325 | 0.19595
6276 | 854.2262 | 1.1797 | 19.9818 | 97.7138 | 40.3551 | 6.8615 | 80.2281 | 1.3763 | 5.3468 | 31.9767 | 77.9926 | 6.4713 | 212.9396 | 128.7478 | 236.7619 | 8.5114 | 51.6223 | 14.4995 | 166 | 49.4412 | 0 | 248.1204 | 0.23708
6277 | 843.4624 | 1.3234 | 27.6583 | 98.685 | 39.8248 | 7.368 | 77.3684 | 1.2183 | 5.574 | 32.1466 | 91.3586 | 7.404 | 229.1646 | 133.1859 | 264.0569 | 8.7058 | 52.1774 | 14.7025 | 163 | 49.7055 | 0 | 252.3439 | 0.21747
6278 | 841.5763 | 1.3685 | 15.3052 | 100.5397 | 39.5856 | 7.5997 | 65.6306 | 1.0111 | 5.6935 | 32.5678 | 107.0391 | 8.7176 | 235.7966 | 134.3738 | 281.4564 | 8.748 | 52.5836 | 14.9833 | 173 | 49.6388 | 0 | 252.9268 | 0.14604
6279 | 848.3821 | 1.2171 | 18.6859 | 100.4375 | 40.336 | 6.8863 | 53.6143 | 1.0086 | 5.677 | 32.8853 | 109.2786 | 7.5153 | 266.2049 | 140.5634 | 290.0641 | 8.4784 | 52.986 | 15.0724 | 169 | 49.4908 | 0 | 254.4241 | 0.11292
6280 | 853.1571 | 1.2663 | 20.2004 | 99.8303 | 39.888 | 7.3065 | 48.5169 | 0.98662 | 5.592 | 30.9924 | 99.3855 | 5.0126 | 226.2551 | 146.351 | 288.3859 | 8.6512 | 52.2319 | 15.7869 | 176 | 50.4981 | 0 | 253.4643 | 0.089323
6281 | 839.0841 | 1.2534 | 20.065 | 98.9817 | 40.2992 | 6.9183 | 49.8546 | 1.011 | 5.55 | 26.7341 | 94.3096 | 4.7609 | 237.3127 | 137.3805 | 276.6864 | 8.806 | 51.2888 | 14.3851 | 165 | 51.1624 | 0 | 249.1035 | 0.05301
6282 | 830.3998 | 2.0229 | 20.2809 | 99.8759 | 39.809 | 7.3882 | 50.2654 | 1.0234 | 5.6571 | 23.13 | 95.0394 | 7.6863 | 241.6791 | 124.1256 | 258.592 | 8.9763 | 52.1736 | 9.5487 | 153 | 50.8221 | 0 | 249.577 | 0.0073639
6283 | 830.2515 | 3.4919 | 20.5704 | 77.2226 | 40.3328 | 6.8918 | 50.2448 | 1.2708 | 5.7687 | 23.6706 | 96.6485 | 9.6852 | 253.9638 | 120.0359 | 253.7657 | 9.0809 | 53.6105 | 6.8491 | 150 | 50.6288 | 0 | 251.8956 | 0
6284 | 812.8363 | 3.737 | 20.86 | 85.924 | 39.8638 | 7.3408 | 59.4235 | 1.452 | 6.0426 | 26.315 | 91.5178 | 8.054 | 224.0168 | 116.0963 | 254.3452 | 9.1371 | 53.7576 | 6.1484 | 138 | 49.1283 | 0 | 253.2652 | 0
6285 | 797.7385 | 3.4726 | 20.6764 | 85.6278 | 39.5527 | 7.6364 | 58.1664 | 1.6059 | 6.2331 | 26.1891 | 80.6161 | 6.6203 | 252.6574 | 107.8786 | 245.3759 | 9.1849 | 52.825 | 5.099 | 131 | 47.5814 | 0 | 255.4724 | 0
6286 | 788.4399 | 2.6407 | 20.4402 | 94.5875 | 38.8731 | 8.2801 | 53.5167 | 1.7212 | 6.4615 | 23.5308 | 75.1005 | 6.4159 | 224.9243 | 100.0966 | 234.4127 | 9.0296 | 51.8018 | 4.5723 | 134 | 46.0048 | 0 | 253.5546 | 0
6287 | 778.2608 | 1.7542 | 20.3618 | 74.8828 | 37.8563 | 9.2419 | 50.8216 | 1.5753 | 6.3035 | 21.4366 | 73.7349 | 6.1759 | 231.9523 | 95.2517 | 221.7954 | 9.4737 | 50.6202 | 4.4181 | 133 | 44.6053 | 0 | 250.1113 | 0
6288 | 778.7642 | 1.4564 | 20.2743 | 93.666 | 36.0366 | 10.9691 | 46.3289 | 1.4941 | 5.9985 | 20.9227 | 71.911 | 5.8292 | 215.2878 | 93.0918 | 223.2996 | 9.324 | 50.2362 | 4.2746 | 122 | 43.9875 | 0 | 247.5941 | 0
6289 | 771.8718 | 1.3447 | 20.0981 | 87.2495 | 38.5796 | 8.5566 | 48.1834 | 1.497 | 5.9096 | 20.9554 | 69.8948 | 5.9204 | 217.1502 | 90.8745 | 232.5904 | 9.2282 | 51.0103 | 3.8746 | 113 | 43.6648 | 0 | 242.798 | 0
6290 | 757.6321 | 1.2025 | 20.0353 | 72.0873 | 38.174 | 8.94 | 51.0672 | 1.4888 | 6.0737 | 20.7622 | 68.858 | 6.0566 | 199.2516 | 89.6548 | 231.5538 | 9.3006 | 51.2879 | 3.1501 | 111 | 44.7365 | 0 | 241.4659 | 0
6291 | 757.634 | 1.201 | 20.4207 | 94.4995 | 37.6443 | 9.4445 | 45.924 | 1.5561 | 6.0994 | 22.1803 | 68.7453 | 5.8502 | 205.9789 | 88.7543 | 227.2818 | 9.1591 | 50.9331 | 2.8935 | 114 | 45.0189 | 0 | 247.9941 | 0
6292 | 772.4808 | 1.6674 | 26.4361 | 94.1687 | 38.2896 | 8.831 | 47.8268 | 1.591 | 6.3533 | 28.8237 | 69.0746 | 5.7997 | 215.8837 | 86.6175 | 226.2893 | 9.0099 | 50.8535 | 2.8724 | 109 | 44.3625 | 0 | 265.1332 | 0
6293 | 796.1167 | 2.5038 | 26.8924 | 91.8654 | 41.4462 | 5.8307 | 52.7753 | 1.8352 | 6.318 | 35.1807 | 70.5888 | 7.2357 | 242.3791 | 87.6401 | 227.4439 | 9.2766 | 50.8914 | 2.9084 | 110 | 44.7467 | 0 | 287.3805 | 0
6294 | 827.7477 | 3.8634 | 45.5216 | 112.5801 | 38.3109 | 8.8126 | 59.9649 | 1.659 | 6.3511 | 35.6514 | 87.1766 | 11.8133 | 335.3038 | 112.5152 | 252.8963 | 23.4842 | 51.4806 | 3.4564 | 181 | 52.3878 | 0 | 319.7973 | 0
6295 | 935.2296 | 8.6849 | 125.0794 | 228.614 | 31.0604 | 16.1501 | 95.495 | 3.1412 | 9.369 | 48.0263 | 124.1421 | 23.7489 | 217.4854 | 189.1857 | 337.3852 | 30.3487 | 57.6838 | 9.8429 | 286 | 62.8708 | 0 | 394.3101 | 0.039342
6296 | 977.4198 | 11.1549 | 86.821 | 156.1506 | 30.686 | 16.1612 | 109.9859 | 4.0732 | 16.2067 | 68.3494 | 152.2047 | 28.9568 | 391.4315 | 256.8845 | 430.7196 | 13.0021 | 65.1141 | 13.1656 | 302 | 63.5202 | 0 | 449.2054 | 0.054722
6297 | 1069.6978 | 12.5926 | 110.9525 | 151.6488 | 27.6272 | 18.9992 | 134.319 | 4.6531 | 18.89 | 77.018 | 166.6731 | 31.8694 | 205.2871 | 298.9279 | 500.3948 | 11.3395 | 71.568 | 14.9986 | 322 | 80.5922 | 0 | 485.2781 | 0.079012
6298 | 1145.1679 | 13.7723 | 118.3626 | 149.2891 | 29.5769 | 17.1005 | 142.1181 | 6.4302 | 22.7967 | 81.544 | 178.0332 | 35.9242 | 277.2489 | 335.8322 | 567.7504 | 7.8694 | 80.7303 | 17.2812 | 387 | 87.582 | 0 | 521.9836 | 0.15574
6299 | 1207.1884 | 10.2357 | 122.5472 | 146.6285 | 30.5747 | 16.1503 | 143.0288 | 6.5273 | 25.9967 | 86.004 | 180.738 | 36.3985 | 332.5993 | 351.7618 | 619.0945 | 5.4648 | 88.217 | 17.7383 | 354 | 102.0086 | 0 | 527.595 | 0.17394
6300 | 1211.1699 | 7.4197 | 127.1298 | 149.929 | 27.5758 | 18.9992 | 145.3801 | 5.8404 | 23.6133 | 82.4109 | 181.4943 | 35.1914 | 339.2377 | 355.4653 | 639.9051 | 5.8043 | 90.8995 | 17.9855 | 396 | 93.8486 | 0 | 530.5062 | 0.16083
6301 | 1209.0792 | 5.7409 | 126.1565 | 157.1724 | 23.5771 | 22.7989 | 151.4356 | 5.4398 | 20.2225 | 76.2184 | 185.9062 | 38.0846 | 341.6779 | 358.3622 | 626.7824 | 8.2324 | 89.4239 | 18.4691 | 308 | 96.0419 | 0 | 547.6732 | 0.1534
6302 | 1217.985 | 3.9283 | 127.2387 | 153.4313 | 24.6977 | 21.8503 | 153.0653 | 5.4479 | 21.3097 | 78.3818 | 189.1405 | 38.1661 | 347.9693 | 358.5375 | 614.6354 | 7.7953 | 88.4319 | 18.7419 | 286 | 97.1182 | 0 | 567.3932 | 0.1598
6303 | 1187.2536 | 3.2861 | 127.0994 | 147.6992 | 26.0195 | 21.85 | 142.3923 | 5.2189 | 21.5078 | 81.5186 | 188.311 | 37.7449 | 342.0781 | 345.6457 | 602.4563 | 8.0025 | 88.3088 | 19.3553 | 276 | 97.2933 | 0 | 567.8511 | 0.098666
6304 | 1138.531 | 3.096 | 116.5174 | 141.9835 | 30.9399 | 17.1013 | 133.7802 | 4.8949 | 20.4467 | 73.8529 | 184.6666 | 37.3874 | 329.9626 | 321.6757 | 553.1847 | 11.7141 | 85.5863 | 18.992 | 267 | 91.1278 | 0 | 523.776 | 0.08097
6305 | 1064.7677 | 6.8039 | 105.8497 | 125.6482 | 34.8822 | 12.3513 | 124.6544 | 3.4785 | 18.82 | 59.091 | 171.5592 | 34.1357 | 326.308 | 271.6003 | 472.9063 | 16.9806 | 79.1206 | 18.1153 | 234 | 82.8542 | 0 | 435.9996 | 0.045749
6306 | 1018.4377 | 7.6108 | 94.5577 | 111.1532 | 38.0537 | 9.5008 | 98.5846 | 2.2933 | 12.5133 | 48.3999 | 142.3954 | 26.7701 | 319.6536 | 213.579 | 385.0149 | 19.7739 | 72.6909 | 15.021 | 226 | 73.5752 | 0 | 364.1458 | 0.010029
6307 | 978.2474 | 5.2173 | 77.5595 | 107.8364 | 36.9148 | 10.4497 | 72.694 | 2.3156 | 8.9033 | 49.3464 | 115.1569 | 14.1429 | 310.2976 | 177.1556 | 332.2478 | 22.1399 | 67.9414 | 9.317 | 206 | 63.9134 | 0 | 309.6303 | 0
6308 | 944.9794 | 3.9216 | 37.2369 | 107.2066 | 38.5855 | 8.5505 | 73.3113 | 2.6196 | 8.0167 | 54.3452 | 106.0187 | 9.0034 | 307.8141 | 148.3755 | 301.6333 | 25.0012 | 62.6406 | 6.454 | 191 | 58.6727 | 0 | 268.5628 | 0
6309 | 919.9003 | 3.4269 | 23.5196 | 105.277 | 38.5884 | 8.55 | 73.9469 | 2.4931 | 7.2367 | 47.0267 | 103.8923 | 9.0616 | 305.9609 | 124.9795 | 265.6581 | 27.5556 | 57.4809 | 5.3657 | 172 | 56.1113 | 0 | 256.0681 | 0
6310 | 889.4278 | 2.7007 | 23.0488 | 103.1406 | 38.5916 | 8.55 | 62.7847 | 2.3875 | 6.7233 | 34.5594 | 96.2433 | 8.9555 | 303.2459 | 111.5617 | 234.1037 | 27.6943 | 54.4587 | 5.0196 | 147 | 52.8483 | 0 | 255.8573 | 0
6311 | 867.6608 | 1.7923 | 23.52 | 102.4251 | 35.589 | 11.3992 | 52.675 | 2.0165 | 6.4333 | 28.6297 | 87.0893 | 9.0426 | 299.0042 | 102.251 | 230.0827 | 28.5487 | 53.3285 | 4.9456 | 124 | 49.7269 | 0 | 254.1617 | 0
6312 | 851.279 | 1.2469 | 22.7156 | 102.2748 | 40.5819 | 6.6513 | 54.7398 | 1.6089 | 6.3033 | 25.5624 | 83.2817 | 9.0419 | 296.2507 | 96.2866 | 245.1097 | 29.0326 | 52.5611 | 4.5451 | 120 | 48.8222 | 0 | 246.7589 | 0
6313 | 855.8347 | 1.2081 | 22.5806 | 102.4291 | 38.5808 | 8.5495 | 56.3785 | 1.7355 | 6.2067 | 23.1418 | 82.2696 | 8.8032 | 295.6324 | 92.7299 | 256.0849 | 28.8601 | 51.9543 | 4.3806 | 113 | 48.4398 | 0 | 240.5484 | 0
6314 | 857.3052 | 1.2676 | 22.3335 | 102.198 | 38.5849 | 8.55 | 49.9693 | 1.6503 | 6.2033 | 22.3936 | 81.5326 | 8.7325 | 293.1326 | 90.3685 | 255.5288 | 43.7393 | 51.8303 | 4.3617 | 114 | 47.3662 | 0 | 240.2736 | 0
6315 | 845.3383 | 1.222 | 22.6133 | 102.0514 | 37.5887 | 9.4997 | 53.3392 | 1.5072 | 6.26 | 24.045 | 80.9389 | 8.7884 | 294.2884 | 89.1744 | 240.4742 | 18.1432 | 52.0616 | 4.3242 | 112 | 46.7252 | 0 | 240.1302 | 0
6316 | 846.7576 | 1.623 | 22.9745 | 102.3239 | 39.5858 | 7.6005 | 56.5759 | 1.5241 | 6.2133 | 31.0034 | 80.829 | 8.7104 | 295.5158 | 87.5188 | 232.422 | 25.2356 | 52.0779 | 3.9144 | 108 | 46.4566 | 0 | 242.575 | 0
6317 | 867.1554 | 3.3251 | 31.6149 | 103.7913 | 38.5834 | 8.5497 | 51.3825 | 2.0004 | 6.1467 | 37.7107 | 81.4318 | 10.328 | 294.7786 | 89.1746 | 234.6606 | 28.9604 | 51.806 | 3.2192 | 108 | 45.9651 | 0 | 257.1636 | 0
6318 | 907.6826 | 4.6463 | 49.5783 | 107.5221 | 35.5805 | 11.3992 | 64.7661 | 2.3404 | 6.6967 | 38.5009 | 91.0437 | 18.3285 | 296.7972 | 122.4499 | 244.9831 | 29.1053 | 51.7954 | 3.1369 | 202 | 52.9194 | 0 | 305.1544 | 0
6319 | 1001.9211 | 4.6448 | 75.4276 | 110.8627 | 30.5811 | 16.1487 | 90.669 | 4.3194 | 7.4933 | 44.364 | 116.3101 | 31.8437 | 303.4121 | 192.4111 | 300.0669 | 24.3786 | 55.3357 | 9.1664 | 294 | 59.4156 | 0 | 359.2416 | 0.021589
6320 | 1086.4976 | 3.9877 | 95.079 | 129.1886 | 29.5821 | 17.0997 | 109.6685 | 5.2223 | 9.9167 | 59.3413 | 146.8835 | 42.3661 | 310.3586 | 262.4433 | 405.1634 | 17.0761 | 65.2369 | 14.6987 | 323 | 73.5931 | 0 | 419.1371 | 0.092488
6321 | 1182.5589 | 3.545 | 102.106 | 144.6954 | 26.5822 | 19.9492 | 122.025 | 5.2249 | 19.1067 | 72.4035 | 168.3516 | 43.614 | 315.4493 | 316.3766 | 517.7846 | 10.4777 | 77.7536 | 16.7624 | 381 | 82.6696 | 0 | 482.9085 | 0.093961
6322 | 1239.0183 | 3.213 | 104.3999 | 148.3648 | 28.5807 | 18.0505 | 126.4181 | 5.3701 | 25.2133 | 78.2844 | 180.0395 | 43.4714 | 322.3287 | 354.5632 | 594.6193 | 7.2119 | 87.1114 | 17.5634 | 395 | 88.4313 | 0 | 531.8301 | 0.08405
6323 | 1279.1761 | 7.122 | 108.8333 | 150.2818 | 25.58 | 20.8992 | 133.0437 | 4.8354 | 25.44 | 82.5675 | 187.2557 | 43.0372 | 323.6973 | 375.1873 | 623.0893 | 6.7599 | 90.4296 | 17.9939 | 363 | 104.5172 | 0 | 556.8683 | 0.088339
6324 | 1269.9873 | 10.2735 | 110.0472 | 153.9176 | 22.6447 | 23.7492 | 133.6317 | 4.299 | 24.6533 | 83.8411 | 188.0111 | 42.2905 | 322.2166 | 376.2822 | 630.6417 | 8.7589 | 88.0436 | 18.4477 | 369 | 97.0356 | 0 | 555.1032 | 0.070653
6325 | 1256.1061 | 9.127 | 111.9379 | 151.1652 | 29.0056 | 19.0013 | 142.0305 | 3.8194 | 25.52 | 82.8231 | 184.8743 | 44.4837 | 326.8575 | 378.2809 | 629.5823 | 7.9977 | 86.5099 | 18.5877 | 321 | 101.9118 | 0 | 574.5822 | 0.097205
6326 | 1245.942 | 5.248 | 111.3113 | 150.7077 | 32.8283 | 17.1005 | 150.6533 | 3.7837 | 26.9456 | 82.6575 | 184.3384 | 44.0833 | 332.1383 | 383.05 | 617.9434 | 8.4991 | 87.508 | 18.3185 | 295 | 101.025 | 0 | 562.5579 | 0.096755
6327 | 1233.0493 | 3.6728 | 108.3298 | 145.8632 | 31.6782 | 18.0497 | 150.9227 | 4.2606 | 26.6287 | 76.8903 | 185.5744 | 40.7992 | 332.1499 | 374.5673 | 608.1351 | 10.9294 | 86.1123 | 17.7255 | 302 | 98.53 | 0 | 523.8806 | 0.086132
6328 | 1183.3583 | 3.3174 | 104.1454 | 141.0821 | 31.7703 | 18.9997 | 147.0557 | 4.4418 | 21.9051 | 69.3472 | 185.4999 | 36.2091 | 330.8684 | 352.3534 | 589.5743 | 12.9276 | 83.2833 | 17.2068 | 262 | 87.4484 | 0 | 470.3546 | 0.048983
6329 | 1095.8034 | 2.8273 | 100.5792 | 128.2683 | 41.893 | 10.4524 | 133.9455 | 2.9313 | 20.2073 | 62.6456 | 174.8773 | 30.3108 | 317.4579 | 299.4678 | 522.5218 | 16.3938 | 78.8711 | 16.3424 | 253 | 72.7021 | 0 | 384.8239 | 0.028707
6330 | 1020.3095 | 2.942 | 96.5636 | 114.2 | 43.6712 | 8.5505 | 106.5957 | 1.9615 | 19.9999 | 55.1504 | 146.2771 | 22.0574 | 302.5053 | 234.338 | 447.8318 | 20.9542 | 72.0861 | 13.5692 | 223 | 68.8048 | 0 | 325.9701 | 0.0027566
6331 | 983.3468 | 3.915 | 79.8012 | 108.5926 | 42.7399 | 9.4997 | 78.4 | 2.2402 | 17.41 | 52.5436 | 119.0974 | 11.186 | 293.9603 | 194.4906 | 401.206 | 22.5305 | 66.5962 | 8.3348 | 191 | 64.6238 | 0 | 273.4944 | 0
6332 | 935.7328 | 3.9464 | 35.6715 | 107.3089 | 40.5417 | 9.5 | 62.8336 | 2.3816 | 12.5933 | 50.1706 | 110.8738 | 8.3579 | 286.4245 | 170.7335 | 341.6262 | 25.7851 | 61.6206 | 5.6504 | 173 | 61.4719 | 0 | 229.3848 | 0
6333 | 937.4885 | 3.5517 | 20.5204 | 105.6049 | 37.0117 | 12.3492 | 56.7813 | 2.244 | 10.1933 | 37.7311 | 107.6524 | 8.4942 | 285.2996 | 155.7492 | 287.7888 | 27.067 | 57.1651 | 4.664 | 165 | 55.7698 | 0 | 220.0114 | 0
6334 | 906.4867 | 2.6419 | 20.0327 | 103.4109 | 38.1182 | 12.35 | 55.5959 | 2.0546 | 8.74 | 24.5661 | 95.3668 | 8.0122 | 288.0264 | 144.8507 | 267.7747 | 26.978 | 55.3607 | 3.9897 | 161 | 50.699 | 0 | 221.6308 | 0
6335 | 862.9807 | 1.5176 | 19.797 | 102.4056 | 38.0324 | 11.4003 | 50.8566 | 1.616 | 7.7267 | 20.3985 | 82.4295 | 7.7844 | 281.1473 | 132.7599 | 256.2408 | 28.4029 | 54.0102 | 3.6349 | 136 | 50.0008 | 0 | 215.3899 | 0
6336 | 869.8047 | 1.2491 | 19.5743 | 102.1373 | 39.6575 | 9.5005 | 50.3398 | 1.6703 | 7.0833 | 20.0734 | 76.4648 | 7.8066 | 281.2046 | 122.3824 | 246.0869 | 28.8201 | 52.6096 | 3.4595 | 134 | 49.4314 | 0 | 203.4751 | 0
6337 | 870.8752 | 1.2088 | 19.4634 | 102.9142 | 39.5469 | 10.4497 | 53.1355 | 1.5643 | 6.65 | 20.1076 | 73.4319 | 7.931 | 285.5106 | 113.5601 | 246.0409 | 28.5071 | 52.3063 | 3.0379 | 128 | 46.7355 | 0 | 201.8756 | 0
6338 | 845.7306 | 1.1282 | 19.4061 | 103.4487 | 40.2426 | 9.5003 | 54.6866 | 1.4342 | 6.42 | 20.2576 | 71.6938 | 7.847 | 284.0894 | 109.4014 | 246.6257 | 29.3969 | 52.389 | 2.6911 | 126 | 46.4395 | 0 | 205.6867 | 0
6339 | 847.1681 | 1.1202 | 19.3249 | 103.0982 | 43.329 | 5.7011 | 47.7215 | 1.436 | 6.5268 | 21.7578 | 71.2981 | 7.8542 | 283.4196 | 109.3101 | 241.7473 | 28.5508 | 52.5209 | 2.6353 | 118 | 45.9721 | 0 | 207.582 | 0
6340 | 855.4325 | 1.6648 | 25.384 | 102.4006 | 42.869 | 6.6497 | 50.2495 | 1.4456 | 6.4285 | 28.6724 | 71.2224 | 7.8074 | 283.3673 | 109.5326 | 235.3547 | 27.9496 | 52.9393 | 2.6238 | 118 | 46.0418 | 0 | 211.3487 | 0
6341 | 848.3909 | 2.9518 | 28.5218 | 102.5428 | 42.0333 | 6.65 | 55.3612 | 1.4581 | 6.5548 | 35.3581 | 71.7421 | 10.5235 | 286.708 | 109.6418 | 233.3979 | 28.4614 | 53.2398 | 2.5862 | 116 | 45.3299 | 0 | 224.3638 | 0
6342 | 896.824 | 4.2772 | 43.5485 | 107.4076 | 37.4705 | 10.4489 | 61.4075 | 1.9127 | 6.9867 | 37.6956 | 82.4916 | 16.3436 | 289.1606 | 133.1498 | 242.4983 | 28.07 | 53.6575 | 2.5358 | 188 | 50.6024 | 0 | 257.0969 | 0
6343 | 957.7265 | 6.588 | 68.5434 | 107.7253 | 31.0646 | 16.1484 | 86.3685 | 2.5293 | 12.45 | 48.5038 | 110.7581 | 29.5826 | 297.5718 | 187.3249 | 286.6352 | 23.342 | 57.1878 | 8.0514 | 320 | 59.6438 | 0 | 307.4765 | 0.03005
6344 | 1067.0286 | 9.4598 | 92.7897 | 128.0988 | 26.5812 | 19.9489 | 110.4196 | 3.5016 | 16.72 | 69.3862 | 148.0431 | 39.0152 | 308.2671 | 248.3942 | 385.6462 | 16.584 | 66.1815 | 13.2794 | 311 | 76.8703 | 0 | 383.0206 | 0.062379
6345 | 1159.7341 | 10.1788 | 101.6299 | 142.1918 | 27.5787 | 19.0003 | 119.5526 | 4.0369 | 19.8633 | 82.9781 | 171.4286 | 42.0077 | 317.3748 | 292.5231 | 511.7818 | 11.7983 | 76.1409 | 14.5222 | 384 | 82.1188 | 0 | 450.0391 | 0.1511
6346 | 1208.1171 | 11.838 | 104.0121 | 150.4011 | 31.2766 | 16.1508 | 124.8033 | 4.126 | 22.1433 | 82.2154 | 180.0757 | 45.094 | 325.1723 | 320.5022 | 595.8876 | 10.5252 | 81.0454 | 15.0412 | 374 | 90.9222 | 0 | 482.9097 | 0.21271
6347 | 1193.9372 | 12.3542 | 107.6429 | 152.2359 | 29.9017 | 18.0495 | 130.401 | 4.6427 | 23.5933 | 80.8897 | 183.3811 | 44.6202 | 330.4901 | 347.7849 | 637.0435 | 8.7808 | 83.0388 | 17.3013 | 351 | 101.5197 | 0 | 505.6759 | 0.21476
6348 | 1198.5305 | 12.0506 | 111.1792 | 150.084 | 30.9141 | 18.05 | 130.3088 | 4.1874 | 19.7467 | 80.1969 | 177.6924 | 44.7675 | 335.3047 | 359.3875 | 629.0677 | 8.4975 | 83.9864 | 17.4084 | 356 | 89.2122 | 0 | 525.7021 | 0.1863
6349 | 1184.0402 | 15.0311 | 114.7846 | 151.2796 | 29.8825 | 19.9495 | 143.3302 | 4.0099 | 15.6972 | 77.6383 | 176.6727 | 45.3894 | 336.6402 | 354.9767 | 603.5884 | 7.5324 | 85.1018 | 17.5905 | 310 | 92.5836 | 0 | 530.4754 | 0.21985
6350 | 1173.8037 | 12.0344 | 114.3293 | 152.6239 | 31.1966 | 19.0003 | 147.6914 | 3.963 | 18.8555 | 78.7185 | 185.6948 | 43.2796 | 338.2612 | 353.7975 | 598.1884 | 8.2751 | 86.4451 | 18.3349 | 280 | 94.4446 | 0 | 523.6416 | 0.22741
6351 | 1127.5498 | 5.7744 | 110.3801 | 149.2931 | 28.0387 | 21.8492 | 145.4502 | 4.2315 | 19.1294 | 73.4727 | 190.8386 | 42.0431 | 338.2775 | 347.1106 | 596.8202 | 8.6105 | 86.7588 | 18.8153 | 290 | 90.7392 | 0 | 514.5084 | 0.19592
6352 | 1068.0838 | 3.4859 | 105.1344 | 143.2032 | 30.4685 | 18.0511 | 134.0966 | 3.5558 | 11.8246 | 61.8803 | 188.6513 | 39.5675 | 332.1826 | 323.3538 | 565.8101 | 11.0873 | 85.5479 | 18.2778 | 259 | 80.6772 | 0 | 474.7223 | 0.1789
6353 | 1037.5883 | 2.923 | 100.7375 | 127.1702 | 35.199 | 13.3013 | 116.7222 | 2.6931 | 8.5967 | 51.7197 | 173.2685 | 33.138 | 325.0979 | 270.9665 | 490.3659 | 14.9862 | 81.0952 | 17.3636 | 244 | 68.8307 | 0 | 392.8561 | 0.087957
6354 | 983.6575 | 3.7578 | 95.6729 | 111.5282 | 39.6292 | 9.5011 | 101.7589 | 1.6416 | 9.2067 | 44.6987 | 136.6136 | 27.1593 | 314.4882 | 208.4957 | 415.1731 | 17.0456 | 76.0989 | 14.8226 | 228 | 63.0822 | 0 | 318.7541 | 0.014955
6355 | 926.1179 | 4.1327 | 82.4836 | 110.8165 | 36.6554 | 11.3995 | 89.9436 | 2.0197 | 9.7962 | 45.662 | 104.1917 | 16.4206 | 304.698 | 170.4877 | 375.6169 | 19.2002 | 72.1457 | 10.1944 | 195 | 59.4121 | 0 | 270.9222 | 0
6356 | 912.5385 | 3.7821 | 40.2296 | 111.3368 | 39.7487 | 7.6011 | 80.7016 | 1.8331 | 8.9537 | 46.1778 | 95.6721 | 10.3935 | 298.9261 | 148.9592 | 339.5408 | 23.3897 | 66.2374 | 7.6043 | 173 | 56.4572 | 0 | 249.8567 | 0
6357 | 885.4559 | 3.5244 | 25.3628 | 108.2841 | 40.5874 | 6.6503 | 66.5268 | 1.4225 | 7.7801 | 35.2686 | 94.895 | 9.9717 | 298.469 | 134.6398 | 291.8455 | 25.0957 | 60.2932 | 6.1954 | 171 | 52.7399 | 0 | 255.4773 | 0
6358 | 849.3622 | 2.7867 | 25.1153 | 104.7103 | 38.5897 | 8.5495 | 59.5192 | 1.3198 | 7.26 | 23.6412 | 87.5113 | 8.9805 | 293.3751 | 121.042 | 260.4961 | 26.6078 | 57.0719 | 5.3849 | 147 | 49.4095 | 0 | 254.3259 | 0
6359 | 833.7815 | 1.8003 | 25.0515 | 103.308 | 39.5909 | 7.6003 | 57.3673 | 1.29 | 6.6443 | 20.2866 | 78.8276 | 8.0562 | 288.1694 | 108.0051 | 262.136 | 26.7693 | 55.2079 | 5.0832 | 130 | 47.9163 | 0 | 248.3832 | 0
6360 | 832.414 | 1.3234 | 20.5303 | 103.0966 | 37.5947 | 9.4995 | 64.1981 | 1.3007 | 6.3643 | 19.6879 | 76.1484 | 8.0586 | 284.1226 | 102.4385 | 257.6038 | 26.2695 | 55.095 | 4.9383 | 124 | 45.509 | 0 | 244.2895 | 0
6361 | 824.9051 | 1.2731 | 18.5961 | 102.9459 | 38.5928 | 8.5503 | 69.7793 | 1.5568 | 6.458 | 18.6031 | 76.038 | 8.0035 | 283.8351 | 99.1849 | 240.1236 | 25.2919 | 56.8863 | 4.7169 | 131 | 44.5092 | 0 | 238.593 | 0
6362 | 823.1335 | 1.2779 | 18.3431 | 102.9998 | 38.5911 | 8.55 | 71.7542 | 1.4473 | 6.5767 | 17.8462 | 74.9383 | 8.3497 | 287.3133 | 96.0483 | 232.4657 | 40.5753 | 57.4354 | 3.5762 | 129 | 44.3917 | 0 | 238.8691 | 0
6363 | 820.9931 | 1.185 | 18.4163 | 103.5339 | 38.5908 | 8.55 | 71.4978 | 1.2988 | 6.4567 | 19.3127 | 73.5667 | 9.0147 | 286.8811 | 93.6137 | 232.001 | 16.5232 | 55.2422 | 2.797 | 116 | 44.008 | 0 | 241.8944 | 0
6364 | 836.4144 | 1.6844 | 18.6217 | 103.2685 | 38.5944 | 8.55 | 70.9451 | 1.3074 | 6.4467 | 26.0912 | 72.9586 | 8.2055 | 284.9617 | 89.736 | 230.8087 | 23.4097 | 54.0251 | 2.7278 | 118 | 43.1501 | 0 | 247.2686 | 0
6365 | 839.0017 | 2.8932 | 25.2243 | 103.3337 | 37.5908 | 9.4997 | 72.5296 | 1.2979 | 6.5067 | 34.2647 | 73.1837 | 8.8752 | 285.3875 | 87.9744 | 233.3108 | 26.6146 | 54.3244 | 3.3684 | 115 | 44.103 | 0 | 263.961 | 0
6366 | 887.7292 | 5.8268 | 42.3857 | 109.9987 | 36.5833 | 10.4526 | 79.4231 | 1.1919 | 6.86 | 34.8692 | 84.1852 | 17.5349 | 285.9977 | 119.8783 | 252.8725 | 27.0156 | 54.6899 | 4.9768 | 193 | 51.923 | 0 | 298.1363 | 0
6367 | 947.8127 | 9.5741 | 66.7335 | 111.8494 | 30.5882 | 16.1455 | 96.7621 | 1.894 | 7.4767 | 42.1194 | 111.7902 | 31.0424 | 294.3178 | 192.8291 | 294.4433 | 21.9403 | 58.803 | 11.7159 | 279 | 56.1467 | 0 | 343.8275 | 0.023915
6368 | 1039.6561 | 10.6585 | 88.9569 | 129.1708 | 29.5835 | 17.0997 | 111.3702 | 3.724 | 11.3733 | 58.261 | 144.4084 | 38.0087 | 307.063 | 264.5596 | 373.7212 | 15.3754 | 67.9845 | 16.8408 | 305 | 77.3083 | 0 | 411.9622 | 0.054481
6369 | 1146.2044 | 5.7457 | 97.1475 | 142.9912 | 27.5819 | 18.9995 | 121.4079 | 5.2023 | 17.67 | 70.0519 | 168.1867 | 39.5587 | 313.8632 | 306.1042 | 485.8822 | 11.3417 | 77.3038 | 17.4972 | 355 | 77.1367 | 0 | 481.8834 | 0.075051
6370 | 1186.6872 | 3.0887 | 102.3754 | 149.6277 | 25.5797 | 20.8995 | 123.8941 | 7.1519 | 22.84 | 77.6842 | 182.1074 | 42.1155 | 325.185 | 330.3713 | 553.4991 | 9.4063 | 83.7665 | 17.7163 | 359 | 79.2454 | 0 | 519.8495 | 0.16385
6371 | 1213.0477 | 3.4795 | 106.1322 | 151.3897 | 27.5782 | 19.0005 | 132.4204 | 8.0284 | 27.3847 | 80.9574 | 192.5708 | 41.9214 | 331.8575 | 349.9003 | 581.0993 | 6.5338 | 87.8604 | 18.0322 | 315 | 91.6821 | 0 | 533.7915 | 0.11634
6372 | 1195.6831 | 3.6683 | 109.3651 | 149.5177 | 26.5801 | 19.9497 | 129.0598 | 5.9898 | 24.6916 | 80.4003 | 193.4217 | 41.1991 | 329.5941 | 357.7805 | 598.3003 | 6.6723 | 88.9269 | 18.0182 | 358 | 89.8007 | 0 | 540.1066 | 0.14255
6373 | 1188.6308 | 3.45 | 110.0665 | 146.8687 | 28.5776 | 18.0505 | 134.5806 | 4.8931 | 18.4237 | 78.8403 | 187.4689 | 41.6949 | 329.757 | 362.7771 | 603.2617 | 7.8162 | 87.4616 | 18.2381 | 314 | 86.5478 | 0 | 547.6485 | 0.191
6374 | 1208.7043 | 6.6654 | 107.5594 | 150.0514 | 28.5777 | 18.05 | 135.5124 | 4.8023 | 21.8833 | 78.9761 | 188.3752 | 40.9046 | 341.7696 | 369.6927 | 605.5259 | 8.0522 | 86.6577 | 18.6973 | 286 | 86.1209 | 0 | 549.5477 | 0.16939
6375 | 1175.9905 | 7.7993 | 106.5099 | 151.0839 | 29.5763 | 17.1003 | 127.8856 | 4.2432 | 23.8967 | 78.7135 | 192.4395 | 39.2434 | 347.372 | 364.3626 | 605.2369 | 8.9253 | 85.9496 | 19.1788 | 276 | 81.0875 | 0 | 542.2561 | 0.13286
6376 | 1119.1476 | 7.2069 | 106.5229 | 143.7699 | 29.5775 | 17.1 | 123.0361 | 3.8226 | 20.9133 | 72.3358 | 190.2889 | 37.521 | 343.0523 | 338.0458 | 572.612 | 11.4467 | 84.3807 | 19.0505 | 247 | 76.0932 | 0 | 493.9585 | 0.081388
6377 | 1034.5046 | 4.3565 | 102.2955 | 127.0981 | 36.5753 | 10.4518 | 110.9236 | 2.8993 | 19.0733 | 58.4616 | 174.9536 | 32.5643 | 341.6783 | 279.3017 | 506.6549 | 16.2629 | 79.5592 | 18.0108 | 227 | 68.5537 | 0 | 404.6679 | 0.031754
6378 | 982.0815 | 3.3768 | 96.0159 | 111.8293 | 38.5806 | 8.5505 | 97.5261 | 2.0845 | 17.2333 | 49.3254 | 140.6594 | 23.7931 | 337.2187 | 208.7751 | 429.6293 | 19.7876 | 72.1576 | 14.578 | 223 | 64.6433 | 0 | 331.8241 | 0.0041408
6379 | 947.6967 | 3.9553 | 79.8245 | 109.2842 | 37.5856 | 9.4997 | 84.5885 | 2.2074 | 13.4767 | 51.3905 | 110.1354 | 12.905 | 317.9433 | 166.6948 | 377.91 | 22.7841 | 66.1284 | 9.0766 | 195 | 61.394 | 0 | 282.6482 | 0
6380 | 910.6106 | 4.0973 | 38.8547 | 107.9261 | 39.5837 | 7.6005 | 77.1416 | 2.236 | 9.5367 | 52.6767 | 101.9871 | 8.5914 | 308.3449 | 142.6185 | 351.3739 | 24.4704 | 61.38 | 6.6263 | 177 | 56.6203 | 0 | 254.2815 | 0
6381 | 872.8133 | 3.7244 | 25.2193 | 104.7233 | 36.588 | 10.4492 | 71.3447 | 2.1347 | 7.75 | 42.1999 | 99.0983 | 8.1273 | 304.0572 | 125.9465 | 320.4567 | 26.4372 | 57.6587 | 5.8829 | 156 | 51.6529 | 0 | 249.2511 | 0
6382 | 847.3416 | 3.3409 | 24.6415 | 102.3859 | 36.5872 | 10.45 | 68.4802 | 1.6024 | 7.1433 | 29.2843 | 89.9083 | 7.7402 | 299.9081 | 115.5086 | 290.8605 | 26.9803 | 55.4211 | 5.2464 | 146 | 49.7254 | 0 | 245.9339 | 0
6383 | 835.5494 | 2.3488 | 24.7999 | 103.7583 | 35.5881 | 11.3997 | 71.4448 | 1.3715 | 6.6333 | 24.2842 | 80.1259 | 7.6289 | 294.0262 | 104.9661 | 266.8911 | 27.2998 | 54.5474 | 4.8524 | 130 | 46.3368 | 0 | 239.331 | 0
6384 | 826.4453 | 1.4326 | 24.5166 | 102.9927 | 36.5917 | 10.4503 | 75.5853 | 1.3631 | 6.3974 | 23.1215 | 75.2747 | 7.4874 | 290.4194 | 97.8103 | 259.1823 | 26.8846 | 54.4031 | 4.5957 | 125 | 44.4385 | 0 | 232.9588 | 0
6385 | 830.8163 | 1.634 | 24.637 | 102.0709 | 37.5947 | 9.5003 | 70.2738 | 1.3746 | 6.3579 | 22.2538 | 74.2217 | 7.5473 | 288.7149 | 93.2557 | 261.3735 | 26.8901 | 54.4177 | 4.4507 | 149 | 42.6542 | 0 | 231.3711 | 0
6386 | 814.1247 | 1.6415 | 24.7074 | 102.3626 | 38.5943 | 8.5503 | 63.8774 | 1.4067 | 6.4447 | 21.9693 | 73.9342 | 7.5627 | 287.8769 | 90.951 | 262.0339 | 27.2014 | 54.4117 | 4.4438 | 145 | 43.09 | 0 | 229.7103 | 0
6387 | 817.1051 | 1.6617 | 20.5494 | 101.756 | 38.5941 | 8.55 | 66.0843 | 1.6355 | 6.4633 | 23.4822 | 73.5317 | 7.5463 | 289.7282 | 89.9839 | 245.524 | 26.9318 | 54.3968 | 4.3904 | 136 | 43.1512 | 0 | 230.5986 | 0
6388 | 813.8059 | 1.8156 | 18.4921 | 101.6523 | 38.5935 | 8.55 | 67.8071 | 1.5136 | 6.63 | 30.1388 | 73.4622 | 7.4638 | 289.0369 | 88.2037 | 237.2833 | 26.6806 | 54.3721 | 4.3141 | 120 | 43.3462 | 0 | 238.1812 | 0
6389 | 832.5811 | 2.4961 | 25.0017 | 103.3784 | 38.5893 | 8.55 | 69.0465 | 1.3994 | 6.6333 | 36.3313 | 74.1013 | 9.8572 | 286.8872 | 89.0044 | 243.3176 | 27.4868 | 54.2574 | 4.2766 | 113 | 42.7188 | 0 | 253.3825 | 0
6390 | 862.7165 | 3.9485 | 42.9587 | 108.136 | 36.5865 | 10.4495 | 77.0295 | 1.3799 | 6.73 | 36.244 | 85.1487 | 16.1711 | 292.188 | 112.5202 | 261.7881 | 26.1859 | 55.247 | 3.6508 | 202 | 51.1571 | 0 | 285.7751 | 0
6391 | 917.4731 | 4.627 | 66.4559 | 109.0115 | 30.589 | 16.1484 | 96.2938 | 2.0718 | 11.2867 | 45.111 | 109.8341 | 27.738 | 300.3467 | 177.6016 | 330.3863 | 21.2612 | 59.555 | 8.503 | 233 | 53.9744 | 0 | 339.9115 | 0.03433
6392 | 1030.5384 | 4.0048 | 87.2852 | 126.6501 | 27.5848 | 18.9992 | 112.7661 | 2.8676 | 18.5833 | 64.1264 | 136.36 | 34.5408 | 306.5745 | 256.8759 | 436.9594 | 16.6261 | 66.8627 | 12.9654 | 293 | 63.7192 | 0 | 411.494 | 0.081241
6393 | 1096.1602 | 3.408 | 97.561 | 140.8005 | 26.5777 | 19.9497 | 122.6408 | 4.1987 | 24.1567 | 75.1051 | 153.1863 | 40.348 | 321.468 | 309.6384 | 529.5447 | 10.7658 | 76.1518 | 15.1752 | 393 | 77.7535 | 0 | 477.2054 | 0.20495
6394 | 1142.9815 | 3.2804 | 100.4436 | 145.5511 | 26.5774 | 19.95 | 128.8354 | 5.1947 | 24.9867 | 79.7982 | 166.3791 | 43.1987 | 331.0392 | 335.4552 | 573.8394 | 7.5306 | 84.6565 | 16.1978 | 386 | 87.3785 | 0 | 505.8911 | 0.23403
6395 | 1156.8901 | 3.1386 | 110.2864 | 146.4708 | 29.5782 | 17.1008 | 130.2588 | 4.4687 | 24.6133 | 82.9685 | 177.0837 | 42.4284 | 334.9365 | 349.522 | 590.4219 | 6.7642 | 88.1242 | 16.3676 | 366 | 89.7864 | 0 | 507.58 | 0.16944
6396 | 1136.1448 | 3.2415 | 110.7766 | 147.7268 | 31.5795 | 15.2005 | 131.3596 | 3.5522 | 22.0267 | 80.8219 | 178.7449 | 41.4196 | 354.5219 | 352.3855 | 581.3143 | 8.5243 | 86.608 | 16.5289 | 377 | 77.3732 | 0 | 512.6257 | 0.15899
6397 | 1132.425 | 3.3713 | 105.9263 | 149.5503 | 29.5806 | 17.0995 | 129.9872 | 3.6261 | 17.0557 | 80.723 | 180.0264 | 37.6717 | 403.0056 | 347.912 | 573.3222 | 6.7331 | 86.9203 | 17.1834 | 318 | 83.211 | 0 | 523.8486 | 0.10704
6398 | 1132.9379 | 3.3105 | 106.6022 | 148.6347 | 26.5808 | 19.9492 | 132.4409 | 3.5258 | 16.8648 | 83.6962 | 181.8855 | 35.8348 | 432.3841 | 343.7959 | 581.6606 | 4.6658 | 90.3189 | 17.4148 | 281 | 83.4567 | 0 | 524.8491 | 0.11815
6399 | 1096.8128 | 3.3154 | 103.0292 | 144.791 | 26.5791 | 19.95 | 126.6595 | 3.2886 | 17.3182 | 76.8799 | 180.5963 | 37.1944 | 432.2939 | 336.4253 | 574.4218 | 6.4565 | 91.1082 | 17.2982 | 287 | 75.8451 | 0 | 503.4505 | 0.13904
6400 | 1034.0682 | 2.6475 | 98.6019 | 135.9904 | 28.5821 | 18.0505 | 115.9218 | 3.0023 | 17.7779 | 60.9937 | 178.1075 | 34.516 | 417.4806 | 310.2418 | 530.0685 | 10.1671 | 88.0352 | 17.086 | 262 | 68.3944 | 0 | 444.7217 | 0.10985
6401 | 974.0263 | 2.0778 | 82.2664 | 126.0741 | 36.5813 | 10.4521 | 96.724 | 1.682 | 15.889 | 48.7311 | 166.5936 | 30.178 | 381.7105 | 248.5654 | 468.2621 | 15.3214 | 81.2153 | 16.9877 | 239 | 61.9246 | 0 | 361.7802 | 0.11642
6402 | 923.7068 | 2.4214 | 41.3308 | 109.974 | 38.5793 | 8.5529 | 77.0628 | 1.0496 | 9.4872 | 45.1554 | 135.6658 | 23.8384 | 326.9352 | 181.4507 | 408.919 | 20.4712 | 72.5664 | 14.1089 | 212 | 55.0363 | 0 | 302.4525 | 0.014861
6403 | 882.8595 | 2.975 | 27.0148 | 104.6992 | 38.5856 | 8.5476 | 54.1675 | 1.2658 | 6.4783 | 51.2671 | 105.7299 | 13.2186 | 281.7601 | 153.1706 | 361.5459 | 23.1654 | 64.9867 | 8.398 | 189 | 55.5544 | 0 | 269.3805 | 0
6404 | 849.1368 | 3.1856 | 24.6551 | 105.2971 | 39.5865 | 7.6003 | 51.6849 | 1.6384 | 6.9655 | 55.3659 | 97.1055 | 8.3394 | 252.4062 | 146.054 | 344.9035 | 25.3768 | 59.6664 | 5.7123 | 179 | 52.3435 | 0 | 244.7652 | 0
6405 | 843.3182 | 3.2703 | 21.198 | 104.3323 | 36.5913 | 10.4492 | 51.299 | 1.5296 | 7.4033 | 43.8183 | 96.8199 | 7.9501 | 232.5134 | 131.9199 | 324.2828 | 26.0338 | 56.7745 | 4.7323 | 182 | 50.0782 | 0 | 234.1134 | 0
6406 | 817.3017 | 2.99 | 19.9429 | 102.8555 | 39.5869 | 7.6008 | 48.5471 | 1.4114 | 7.2667 | 29.1486 | 89.5384 | 7.8146 | 208.8043 | 120.1291 | 294.2996 | 26.3608 | 55.6128 | 3.9882 | 174 | 47.7313 | 0 | 232.1478 | 0
6407 | 793.3516 | 2.0371 | 19.7608 | 102.3046 | 38.5914 | 8.5497 | 51.7975 | 1.4176 | 6.9358 | 23.3723 | 80.551 | 7.7516 | 195.6216 | 115.7247 | 272.3488 | 25.7327 | 55.7751 | 3.1917 | 157 | 46.5438 | 0 | 238.8432 | 0
6408 | 778.3557 | 1.5555 | 20.0695 | 102.2704 | 39.5925 | 7.6003 | 48.2416 | 1.4232 | 6.7246 | 22.8699 | 77.9901 | 7.7893 | 193.1042 | 111.4913 | 263.8996 | 25.419 | 56.3814 | 2.792 | 153 | 45.8704 | 0 | 249.9423 | 0
6409 | 789.0884 | 1.2824 | 18.8334 | 101.8245 | 37.5959 | 9.4995 | 49.84 | 1.4163 | 6.5329 | 23.1399 | 78.2275 | 7.8325 | 194.8996 | 104.0963 | 257.5048 | 25.4885 | 56.29 | 2.71 | 145 | 45.7888 | 0 | 244.9988 | 0
6410 | 783.9225 | 1.3762 | 17.8147 | 103.2223 | 39.5928 | 7.6005 | 52.4001 | 1.6948 | 6.3667 | 22.9943 | 77.9779 | 8.0768 | 195.3207 | 97.7585 | 250.4339 | 26.1605 | 55.8923 | 2.6742 | 138 | 42.8164 | 0 | 236.3924 | 0
6411 | 778.8326 | 1.5084 | 17.1513 | 104.2856 | 38.5937 | 8.5497 | 45.3719 | 1.5621 | 6.4667 | 24.192 | 78.0216 | 8.0419 | 192.6555 | 95.834 | 256.5093 | 26.0867 | 55.6481 | 2.7085 | 131 | 42.7336 | 0 | 234.1766 | 0
6412 | 784.6767 | 1.885 | 17.1225 | 103.3409 | 39.5917 | 7.6003 | 50.1268 | 1.4408 | 6.36 | 30.7953 | 78.4897 | 7.8486 | 191.7917 | 94.9065 | 260.5168 | 25.5456 | 55.8729 | 2.7297 | 130 | 43.1765 | 0 | 232.2976 | 0
6413 | 787.209 | 2.5952 | 18.6012 | 102.3307 | 38.5903 | 8.5497 | 52.9956 | 1.438 | 6.3833 | 36.8035 | 78.3522 | 7.9973 | 192.532 | 94.4231 | 261.2025 | 26.0422 | 55.7944 | 2.6901 | 125 | 43.9505 | 0 | 232.4907 | 0
6414 | 802.0495 | 2.8828 | 34.7017 | 101.435 | 38.5894 | 8.55 | 46.9077 | 1.3383 | 6.2867 | 32.0117 | 77.1341 | 7.2061 | 191.7611 | 94.4756 | 251.395 | 26.3609 | 55.1153 | 2.6104 | 129 | 43.8833 | 0 | 232.5943 | 0
6415 | 813.9248 | 1.8733 | 43.8791 | 99.0869 | 37.5952 | 9.4997 | 52.3004 | 1.1467 | 6.2833 | 23.0077 | 78.1468 | 7.6488 | 190.1072 | 91.5384 | 236.9833 | 27.072 | 54.4957 | 2.7127 | 134 | 51.5994 | 0 | 225.9704 | 0.081092
6416 | 834.8639 | 1.4187 | 50.7304 | 99.3351 | 39.59 | 7.6005 | 60.2282 | 1.1084 | 6.2423 | 19.1025 | 94.9149 | 12.3506 | 202.6872 | 88.8525 | 234.8394 | 26.7149 | 53.9793 | 3.2324 | 126 | 60.5879 | 0 | 219.8013 | 0.14337
6417 | 850.2536 | 1.2122 | 62.38 | 98.8679 | 38.587 | 8.5497 | 58.9866 | 1.86 | 5.6947 | 19.8438 | 121.3017 | 14.3639 | 211.9623 | 94.0528 | 243.3664 | 26.3545 | 54.4208 | 5.7104 | 161 | 60.6494 | 0 | 219.0643 | 0.22846
6418 | 876.1881 | 1.3317 | 72.7981 | 98.8767 | 37.59 | 9.4997 | 61.7442 | 2.9065 | 5.473 | 24.1527 | 136.1998 | 14.1472 | 223.1374 | 104.9439 | 252.1679 | 26.0309 | 55.2553 | 11.1023 | 181 | 60.8651 | 0 | 219.2343 | 0.23499
6419 | 868.3085 | 1.5143 | 73.7694 | 98.7845 | 38.5864 | 8.5526 | 64.4323 | 3.6063 | 6.06 | 28.2118 | 129.2301 | 14.1163 | 235.1706 | 116.5459 | 252.0445 | 26.2847 | 55.3804 | 13.1855 | 188 | 56.0517 | 0 | 220.3418 | 0.22146
6420 | 859.7338 | 1.7028 | 73.5524 | 100.0952 | 38.5903 | 8.5476 | 64.9207 | 2.1968 | 6.1233 | 28.9883 | 110.9534 | 16.2625 | 235.9385 | 120.2461 | 240.59 | 26.2854 | 55.3109 | 13.2168 | 201 | 56.4526 | 0 | 219.0921 | 0.24926
6421 | 864.9616 | 1.6164 | 68.7341 | 101.1972 | 38.5883 | 8.55 | 64.4195 | 1.3947 | 5.8167 | 28.8324 | 101.9156 | 18.4729 | 234.0627 | 120.2751 | 244.9401 | 25.8104 | 55.5302 | 13.3603 | 219 | 53.2584 | 0 | 220.716 | 0.14566
6422 | 847.2222 | 1.6314 | 31.1012 | 101.1866 | 38.5859 | 8.55 | 76.9504 | 1.128 | 5.74 | 29.0719 | 100.6335 | 18.3266 | 236.7353 | 124.4628 | 267.0727 | 26.5893 | 55.2401 | 13.8481 | 204 | 52.5614 | 0 | 230.9481 | 0.1753
6423 | 850.978 | 1.5875 | 17.544 | 102.9344 | 38.5861 | 8.55 | 83.3551 | 0.99147 | 5.6433 | 28.3007 | 106.7788 | 16.446 | 233.3029 | 124.7218 | 297.0923 | 26.5783 | 54.3108 | 13.9349 | 200 | 53.647 | 0 | 236.7881 | 0.12891
6424 | 871.287 | 1.8252 | 16.8153 | 104.5279 | 39.5874 | 7.6003 | 67.5802 | 0.96512 | 5.7367 | 25.4032 | 115.1211 | 10.3762 | 228.241 | 123.5857 | 317.7582 | 26.9549 | 53.8537 | 13.8106 | 215 | 55.1444 | 0 | 229.955 | 0.090257
6425 | 855.6688 | 1.9433 | 16.6323 | 107.1748 | 36.5892 | 10.4492 | 61.4752 | 1.0304 | 5.77 | 22.452 | 109.4661 | 6.8777 | 228.5459 | 124.6079 | 308.0385 | 27.4138 | 53.6465 | 11.5042 | 216 | 57.3263 | 0 | 226.8551 | 0.046025
6426 | 837.8357 | 2.4332 | 16.2874 | 106.3167 | 37.5861 | 9.5003 | 63.4253 | 1.3347 | 5.8633 | 22.6025 | 90.9577 | 7.7648 | 226.5883 | 124.7307 | 289.3828 | 27.0899 | 53.1519 | 6.6192 | 218 | 55.9244 | 0 | 226.184 | 0.002954
6427 | 827.8151 | 3.1495 | 16.342 | 104.1012 | 36.5864 | 10.4497 | 56.8728 | 1.4642 | 5.92 | 30.2413 | 78.7894 | 8.2298 | 219.9806 | 130.3631 | 289.995 | 26.9929 | 53.2363 | 4.7375 | 210 | 50.8889 | 0 | 228.6357 | 0
6428 | 820.0106 | 3.3667 | 16.3716 | 103.2968 | 38.5855 | 8.5505 | 51.9539 | 1.4488 | 6.26 | 37.4187 | 79.627 | 6.7375 | 212.1135 | 137.5816 | 294.5745 | 26.7204 | 53.7914 | 5.0582 | 193 | 50.2498 | 0 | 235.2136 | 0
6429 | 808.0721 | 3.4102 | 16.3722 | 103.2854 | 38.5884 | 8.55 | 44.8143 | 1.4742 | 6.55 | 32.7728 | 82.3564 | 6.0666 | 204.4663 | 135.0059 | 286.4702 | 26.7346 | 54.0523 | 5.0498 | 189 | 48.2537 | 0 | 232.3069 | 0
6430 | 802.2015 | 2.7585 | 16.4586 | 103.286 | 38.5922 | 8.55 | 47.5029 | 1.4655 | 6.7767 | 25.2381 | 82.2182 | 6.0517 | 191.5323 | 122.2557 | 281.8908 | 27.1517 | 54.1128 | 4.8358 | 176 | 46.3094 | 0 | 226.7843 | 0
6431 | 787.618 | 1.8831 | 16.5169 | 104.1846 | 38.5907 | 8.55 | 52.1074 | 1.4925 | 6.8087 | 22.9715 | 81.2129 | 6.0911 | 186.3613 | 115.1269 | 276.5538 | 26.6903 | 54.1506 | 4.4067 | 182 | 46.4799 | 0 | 228.531 | 0
6432 | 793.9243 | 1.631 | 16.1075 | 103.6169 | 38.5879 | 8.55 | 44.4025 | 1.4744 | 6.8865 | 22.6728 | 80.1665 | 5.9872 | 184.7115 | 139.5933 | 266.4922 | 26.6297 | 54.0933 | 3.9035 | 168 | 45.4138 | 0 | 225.4033 | 0
6433 | 783.5786 | 1.415 | 16.0187 | 103.1326 | 39.5843 | 7.6003 | 47.7151 | 1.7683 | 6.5115 | 22.2218 | 78.635 | 5.8534 | 187.9943 | 167.7133 | 263.3586 | 26.2071 | 54.2573 | 3.75 | 165 | 43.3435 | 0 | 216.9659 | 0
6434 | 774.9101 | 1.3247 | 16.1513 | 103.9749 | 38.5823 | 8.5497 | 50.011 | 1.623 | 6.52 | 21.9736 | 78.1229 | 5.9003 | 189.5072 | 168.5956 | 265.2272 | 41.7862 | 54.2207 | 3.7385 | 149 | 41.6554 | 0 | 212.6469 | 0
6435 | 769.5017 | 1.3296 | 16.145 | 102.593 | 38.5829 | 8.55 | 43.8799 | 1.4862 | 6.27 | 22.4587 | 79.0169 | 6.0689 | 190.792 | 163.8066 | 260.663 | 15.7017 | 54.1688 | 3.7548 | 160 | 41.1549 | 0 | 209.4003 | 0
6436 | 765.7257 | 1.7111 | 16.1913 | 102.1409 | 39.5838 | 7.6003 | 47.7039 | 1.4744 | 6.07 | 24.4198 | 79.7165 | 5.8988 | 192.3714 | 165.4771 | 245.7506 | 22.949 | 54.1669 | 2.848 | 156 | 43.7243 | 0 | 206.0212 | 0
6437 | 773.9649 | 2.7007 | 16.327 | 103.3122 | 38.5846 | 8.5497 | 50.7153 | 1.4815 | 6.3133 | 25.9607 | 79.4079 | 6.0378 | 192.6606 | 157.7522 | 231.062 | 27.162 | 53.7002 | 2.3798 | 150 | 45.1337 | 0 | 204.9568 | 0
6438 | 794.6954 | 2.9852 | 16.3833 | 102.1699 | 38.5861 | 8.55 | 44.6701 | 1.4131 | 6.3 | 24.1077 | 78.2534 | 5.4428 | 189.0175 | 128.5333 | 231.951 | 27.0396 | 53.6257 | 2.3858 | 142 | 45.7718 | 0 | 204.2159 | 0
6439 | 808.3566 | 1.8141 | 15.8985 | 99.6919 | 38.59 | 8.55 | 47.2954 | 1.1942 | 6.11 | 21.0161 | 76.1537 | 3.9945 | 184.9352 | 103.6436 | 226.5912 | 27.1006 | 53.6054 | 2.6092 | 138 | 44.8666 | 0 | 198.1888 | 0.043911
6440 | 815.6856 | 0.95512 | 15.9847 | 99.2415 | 38.5934 | 8.55 | 46.4881 | 1.4535 | 5.77 | 18.9646 | 74.6832 | 3.5126 | 181.8958 | 99.6381 | 221.0787 | 27.1635 | 53.376 | 3.316 | 144 | 41.281 | 0 | 194.4778 | 0.13477
6441 | 830.5631 | 1.109 | 16.1872 | 99.3039 | 38.5904 | 8.55 | 47.841 | 1.3104 | 5.5767 | 19.0355 | 76.8492 | 3.5103 | 184.69 | 101.8599 | 219.1185 | 27.0932 | 53.2641 | 5.832 | 183 | 43.0229 | 0 | 194.2323 | 0.16616
6442 | 859.1587 | 1.3797 | 16.194 | 99.5556 | 37.5868 | 9.4997 | 61.4638 | 1.0936 | 5.3967 | 23.3013 | 83.8515 | 3.806 | 192.048 | 107.3898 | 224.756 | 27.0762 | 53.345 | 10.7061 | 175 | 48.4544 | 0 | 195.0658 | 0.19087
6443 | 863.3687 | 1.2465 | 15.8052 | 100.3466 | 38.5878 | 8.5503 | 68.3601 | 1.0271 | 5.5933 | 28.6979 | 91.3564 | 3.9937 | 206.1176 | 114.054 | 241.1562 | 26.7167 | 53.6364 | 13.0322 | 195 | 52.4996 | 0 | 198.5214 | 0.18066
6444 | 856.4923 | 1.2255 | 15.9395 | 100.8693 | 38.5848 | 8.5524 | 57.5749 | 1.0388 | 6.01 | 31.0479 | 99.1363 | 3.6092 | 215.3214 | 116.404 | 241.7716 | 27.1565 | 53.7385 | 13.496 | 187 | 54.2142 | 0 | 199.1586 | 0.19674
6445 | 852.2284 | 1.0386 | 15.9945 | 103.6761 | 38.5878 | 8.5476 | 54.5893 | 1.006 | 6.33 | 31.5192 | 113.0059 | 3.5265 | 220.5005 | 120.2239 | 249.0445 | 27.56 | 53.1717 | 13.6747 | 187 | 55.765 | 0 | 199.224 | 0.20458
6446 | 844.3889 | 0.9007 | 15.8294 | 104.7918 | 38.5851 | 8.55 | 70.253 | 0.9939 | 6.0733 | 33.4981 | 124.3442 | 4.5825 | 223.4925 | 125.7786 | 271.2778 | 27.0233 | 52.8327 | 13.5295 | 172 | 57.7874 | 0 | 200.9625 | 0.20702
6447 | 839.6517 | 1.2609 | 15.7423 | 103.9121 | 38.5849 | 8.55 | 68.214 | 1.1063 | 5.9467 | 34.6 | 129.0132 | 6.2099 | 226.3384 | 131.2227 | 274.7826 | 27.5123 | 53.1048 | 13.4464 | 175 | 59.3105 | 0 | 206.0082 | 0.2125
6448 | 833.6359 | 1.3684 | 16.1135 | 103.6057 | 38.5809 | 8.55 | 56.8782 | 1.2034 | 5.81 | 31.4072 | 127.9248 | 5.1159 | 228.3448 | 131.8451 | 285.5163 | 28.241 | 52.5473 | 13.5659 | 183 | 59.4577 | 0 | 209.8966 | 0.17058
6449 | 824.6676 | 1.2412 | 15.9673 | 102.7339 | 39.585 | 7.6003 | 52.625 | 1.0678 | 5.7433 | 26.1018 | 123.9308 | 3.8815 | 230.1299 | 126.1462 | 310.3613 | 27.6752 | 52.084 | 11.8263 | 180 | 56.9334 | 0 | 208.4176 | 0.11542
6450 | 831.1954 | 2.3679 | 15.5524 | 101.038 | 39.5855 | 7.6 | 46.6766 | 1.0299 | 5.9167 | 22.9335 | 123.0113 | 3.7577 | 225.792 | 123.4251 | 315.2041 | 27.6994 | 52.3014 | 7.5056 | 145 | 54.5596 | 0 | 205.4955 | 0.013032
6451 | 833.2577 | 3.7777 | 15.8599 | 102.8226 | 36.5844 | 10.4492 | 58.9943 | 1.302 | 5.7933 | 25.1219 | 116.1771 | 5.1871 | 222.1169 | 125.2928 | 299.1617 | 26.1303 | 53.6312 | 5.8661 | 135 | 51.6417 | 0 | 211.312 | 0
6452 | 808.3167 | 4.0827 | 16.4535 | 103.278 | 37.5879 | 9.5003 | 60.6973 | 1.4662 | 5.9433 | 28.6604 | 100.3177 | 6.2259 | 215.4917 | 129.0574 | 272.7914 | 25.5689 | 55.5118 | 5.3527 | 137 | 48.8242 | 0 | 225.2248 | 0
6453 | 790.0059 | 3.5586 | 16.1642 | 103.1883 | 35.5851 | 11.3995 | 51.4575 | 1.4604 | 6.33 | 27.6785 | 87.8258 | 6.2688 | 202.9046 | 123.1073 | 262.2554 | 25.8353 | 56.1744 | 4.3078 | 122 | 49.0689 | 0 | 228.5546 | 0
6454 | 771.4494 | 2.782 | 15.8854 | 102.7308 | 38.5827 | 8.5508 | 41.9015 | 1.4858 | 6.4533 | 25.0899 | 86.2357 | 6.2108 | 190.3956 | 110.5817 | 255.8491 | 26.2248 | 55.8036 | 3.8555 | 121 | 46.1593 | 0 | 225.0748 | 0
6455 | 759.8871 | 1.7041 | 16.0733 | 102.6438 | 38.5846 | 8.55 | 44.1337 | 1.7749 | 6.2833 | 24.6022 | 92.3977 | 6.4213 | 183.8681 | 104.2539 | 249.0422 | 26.2928 | 54.8605 | 3.7747 | 124 | 44.4489 | 0 | 224.305 | 0
6456 | 763.881 | 1.2222 | 16.1448 | 102.6541 | 39.5877 | 7.6003 | 47.5538 | 1.6514 | 6.4533 | 23.9303 | 95.2787 | 6.3058 | 183.7586 | 100.161 | 235.2267 | 26.6349 | 54.2255 | 3.594 | 129 | 43.4687 | 0 | 224.8638 | 0
6457 | 756.6305 | 1.218 | 16.1104 | 102.5612 | 38.5878 | 8.5497 | 45.7373 | 1.5173 | 6.3133 | 22.5806 | 87.8674 | 6.2272 | 188.8602 | 95.0196 | 234.0395 | 26.9583 | 54.1769 | 3.1748 | 120 | 42.2677 | 0 | 226.854 | 0
6458 | 752.4608 | 1.3531 | 15.9733 | 102.6034 | 38.5867 | 8.55 | 48.8572 | 1.5301 | 6.46 | 22.0563 | 79.8659 | 6.6789 | 191.1515 | 92.4154 | 233.4217 | 41.2324 | 54.3249 | 2.8397 | 116 | 41.8705 | 0 | 229.194 | 0
6459 | 753.624 | 1.3805 | 16.143 | 102.4586 | 38.5867 | 8.5524 | 45.8121 | 1.5282 | 6.5733 | 23.7731 | 77.2529 | 6.4062 | 190.4258 | 92.119 | 229.2054 | 15.9212 | 54.4249 | 2.7411 | 109 | 41.7647 | 0 | 230.2987 | 0
6460 | 755.1779 | 1.7439 | 16.6304 | 102.863 | 38.5888 | 8.5476 | 44.4145 | 1.5302 | 6.5867 | 30.8757 | 76.0903 | 6.1893 | 190.1881 | 91.3478 | 230.205 | 22.9707 | 54.4116 | 2.7144 | 109 | 41.6066 | 0 | 238.7917 | 0
6461 | 783.2305 | 2.913 | 19.7555 | 103.656 | 36.5839 | 10.4495 | 49.7133 | 1.5107 | 6.4333 | 37.518 | 75.5907 | 8.1814 | 195.6698 | 92.5387 | 231.0424 | 26.1857 | 54.5376 | 2.7142 | 111 | 41.7188 | 0 | 255.252 | 0
6462 | 810.8276 | 4.0867 | 41.731 | 107.6486 | 35.5813 | 11.3997 | 56.2196 | 1.7552 | 7.7233 | 37.3968 | 88.6437 | 14.9218 | 204.9811 | 117.9985 | 247.9367 | 26.7282 | 54.5871 | 3.416 | 177 | 48.4707 | 0 | 297.9944 | 0
6463 | 889.8557 | 4.3724 | 68.3901 | 113.6867 | 28.9267 | 18.0482 | 84.6918 | 3.7046 | 8.57 | 48.1579 | 117.3124 | 30.2311 | 245.8915 | 183.2665 | 298.5715 | 22.3036 | 57.5367 | 8.7944 | 300 | 51.8859 | 0 | 364.6561 | 0.018612
6464 | 994.0929 | 7.643 | 92.8713 | 126.9227 | 26.8215 | 19.9495 | 106.8774 | 6.1097 | 14.89 | 69.4181 | 145.2732 | 40.9621 | 297.8966 | 256.8924 | 383.688 | 15.3181 | 66.7081 | 14.8055 | 321 | 63.6668 | 0 | 430.2234 | 0.078429
6465 | 1059.2375 | 9.9224 | 92.5495 | 135.5564 | 27.5721 | 19.0055 | 120.0901 | 6.9348 | 24.0833 | 81.9265 | 163.0173 | 42.75 | 364.7871 | 301.3995 | 487.0708 | 8.6238 | 78.3098 | 15.4254 | 364 | 69.1841 | 0 | 493.2573 | 0.077823
6466 | 1084.4212 | 9.0364 | 88.9237 | 141.5785 | 28.5835 | 18.045 | 124.0245 | 7.2491 | 27.36 | 83.962 | 165.7133 | 41.5844 | 417.092 | 315.4086 | 572.9499 | 5.9721 | 87.0678 | 15.8871 | 360 | 80.162 | 0 | 525.3852 | 0.060362
6467 | 1123.0206 | 5.2364 | 91.9537 | 147.8848 | 30.5792 | 16.1505 | 127.7455 | 7.1972 | 27.7533 | 87.0943 | 168.3974 | 41.2456 | 432.5444 | 332.8739 | 621.1435 | 3.1205 | 93.3932 | 16.9767 | 321 | 96.8825 | 0 | 539.4928 | 0.082303
6468 | 1109.9787 | 3.6925 | 97.8534 | 149.5596 | 28.8592 | 18.0495 | 139.4641 | 7.1379 | 24.6833 | 91.5402 | 179.9335 | 41.3051 | 449.3952 | 357.5238 | 643.3212 | 4.0159 | 95.6004 | 17.7392 | 345 | 96.1942 | 0 | 555.187 | 0.093691
6469 | 1111.6181 | 3.8693 | 102.4715 | 152.0141 | 29.9002 | 18.05 | 145.1333 | 6.3982 | 19.0933 | 88.6627 | 189.7061 | 44.64 | 454.583 | 375.659 | 642.0398 | 3.9742 | 94.826 | 18.2189 | 350 | 90.2752 | 0 | 586.0458 | 0.083361
6470 | 1118.743 | 4.1193 | 105.858 | 159.5226 | 30.7937 | 17.1003 | 141.518 | 5.4151 | 20.8667 | 85.8322 | 194.5898 | 43.1685 | 466.6604 | 384.8877 | 640.1221 | 4.2615 | 94.3424 | 18.2979 | 341 | 90.1308 | 0 | 613.259 | 0.090309
6471 | 1102.3237 | 3.926 | 102.1282 | 157.935 | 28.8844 | 18.0497 | 137.9905 | 4.9594 | 22.5735 | 81.8011 | 195.6513 | 38.3862 | 463.3913 | 376.6817 | 637.6719 | 5.0337 | 93.4859 | 18.6867 | 276 | 86.9151 | 0 | 601.2423 | 0.062563
6472 | 1074.4729 | 4.8146 | 94.7706 | 150.9744 | 27.5851 | 18.9997 | 123.2416 | 4.6037 | 22.4519 | 73.5338 | 192.144 | 34.8185 | 446.9599 | 346.476 | 582.4588 | 7.9114 | 92.1882 | 18.8396 | 253 | 79.7981 | 0 | 539.2012 | 0.036422
6473 | 1014.9321 | 4.4189 | 86.8535 | 136.0657 | 39.5834 | 7.6032 | 106.3881 | 4.2601 | 21.3846 | 62.2962 | 175.2605 | 29.6569 | 427.4915 | 285.8308 | 487.394 | 12.0559 | 87.8022 | 18.3622 | 224 | 70.5387 | 0 | 439.623 | 0.014171
6474 | 978.8208 | 4.2521 | 79.1456 | 120.8092 | 43.3005 | 4.7508 | 86.6629 | 3.0898 | 18.6067 | 50.1332 | 140.427 | 22.9789 | 375.8194 | 223.8193 | 394.4898 | 15.9793 | 80.5796 | 14.8842 | 220 | 63.8085 | 0 | 364.987 | 0.0010578
6475 | 944.2109 | 4.3339 | 69.1854 | 114.5402 | 42.2165 | 5.6997 | 68.9734 | 2.3582 | 12.8 | 47.0754 | 110.7289 | 13.0608 | 304.0838 | 189.1066 | 335.1609 | 20.0565 | 72.6294 | 8.7827 | 204 | 61.6447 | 0 | 307.6715 | 0
6476 | 913.4245 | 4.2604 | 30.2693 | 110.5273 | 41.6859 | 5.7 | 56.3805 | 2.0055 | 9.7267 | 46.4899 | 102.6129 | 8.3256 | 255.6654 | 160.4037 | 305.6712 | 24.1118 | 65.2433 | 5.818 | 190 | 60.7887 | 0 | 256.7583 | 0
6477 | 881.1312 | 3.3651 | 15.9579 | 107.861 | 42.5884 | 4.7503 | 57.829 | 1.8782 | 8.1333 | 35.2663 | 101.1776 | 9.1584 | 235.5471 | 134.1495 | 273.235 | 24.9007 | 60.5085 | 4.9476 | 187 | 57.5063 | 0 | 228.3501 | 0
6478 | 859.3412 | 2.561 | 15.1887 | 106.436 | 41.5859 | 5.6997 | 56.9447 | 1.9612 | 7.2 | 24.3479 | 92.8689 | 8.3295 | 214.6183 | 114.9877 | 238.9406 | 25.8142 | 58.4431 | 4.3716 | 153 | 55.2971 | 0 | 213.432 | 0
6479 | 832.261 | 1.7651 | 15.0855 | 105.5767 | 42.5866 | 4.7503 | 55.8674 | 1.9858 | 6.5933 | 21.2977 | 81.2491 | 7.5806 | 203.008 | 101.0399 | 222.5856 | 26.3241 | 57.5392 | 4.1283 | 136 | 47.8755 | 0 | 208.5249 | 0
6480 | 826.9401 | 1.1671 | 15.1298 | 104.5915 | 42.5933 | 4.75 | 58.4147 | 1.8898 | 6.41 | 19.7541 | 75.34 | 7.5758 | 194.2489 | 95.8135 | 222.6036 | 26.2152 | 57.3018 | 3.9235 | 130 | 48.5342 | 0 | 208.1878 | 0
6481 | 824.2026 | 1.1568 | 15.063 | 104.7043 | 41.5937 | 5.6997 | 52.6903 | 1.8522 | 6.4767 | 18.6347 | 73.9144 | 7.5651 | 195.8723 | 92.4918 | 226.7833 | 26.0478 | 57.3318 | 3.8473 | 124 | 44.712 | 0 | 209.735 | 0
6482 | 822.0782 | 1.1092 | 15.0377 | 104.0661 | 42.5892 | 4.7503 | 55.0492 | 1.8483 | 6.5667 | 18.4127 | 73.3029 | 7.5716 | 202.0412 | 89.2661 | 234.3717 | 25.5248 | 57.5492 | 3.8488 | 124 | 43.8794 | 0 | 211.5291 | 0
6483 | 820.9035 | 1.1201 | 15.1421 | 103.4063 | 41.592 | 5.6997 | 58.555 | 1.8553 | 6.58 | 20.0308 | 72.4188 | 7.5758 | 197.5785 | 88.3326 | 236.4188 | 26.1357 | 57.5244 | 3.8836 | 114 | 43.8216 | 0 | 212.7045 | 0
6484 | 808.3268 | 1.5129 | 15.0872 | 104.126 | 42.5899 | 4.7503 | 52.5281 | 2.0748 | 6.47 | 26.7852 | 71.6715 | 7.5488 | 192.1978 | 88.5166 | 232.9112 | 25.8351 | 57.2968 | 3.8562 | 118 | 43.4064 | 0 | 220.6 | 0
6485 | 820.6892 | 2.4517 | 28.6626 | 104.5339 | 42.584 | 4.75 | 55.881 | 1.9808 | 6.5067 | 33.2069 | 71.8191 | 10.1175 | 196.8711 | 90.9617 | 235.5334 | 26.3292 | 57.1992 | 3.6712 | 114 | 42.38 | 0 | 235.9465 | 0
6486 | 861.4908 | 4.2111 | 51.5973 | 107.5278 | 39.5853 | 7.5992 | 68.7614 | 2.1589 | 7.2367 | 33.2428 | 82.1393 | 18.8774 | 204.779 | 119.439 | 240.1924 | 25.8911 | 57.1447 | 3.201 | 189 | 47.0308 | 0 | 268.115 | 0
6487 | 944.6368 | 5.4344 | 68.3659 | 112.6377 | 28.5856 | 18.0471 | 90.5064 | 3.2943 | 8.389 | 39.6962 | 110.123 | 28.4216 | 241.5874 | 181.4642 | 289.5443 | 21.0758 | 60.3992 | 8.8698 | 253 | 54.7726 | 0 | 332.5665 | 0.031671
6488 | 1044.7378 | 11.6688 | 87.7254 | 132.2466 | 27.5805 | 18.9997 | 106.4307 | 5.104 | 12.6912 | 54.9405 | 139.798 | 32.7613 | 294.5391 | 253.7431 | 375.0622 | 15.4657 | 69.6654 | 16.0024 | 308 | 72.0155 | 0 | 417.1535 | 0.10955
6489 | 1132.2194 | 17.2206 | 90.8184 | 143.8775 | 30.5765 | 16.1508 | 116.3297 | 6.8195 | 18.107 | 68.0045 | 158.9875 | 35.7879 | 362.6539 | 311.7155 | 465.2819 | 11.0974 | 78.8844 | 17.1739 | 353 | 80.055 | 0 | 485.4218 | 0.067501
6490 | 1173.4788 | 16.9085 | 91.4711 | 147.0637 | 27.5819 | 18.9992 | 125.617 | 7.8777 | 21.0662 | 79.3312 | 172.8397 | 35.934 | 408.8432 | 344.0992 | 538.3677 | 8.9752 | 83.2618 | 17.5055 | 350 | 83.9286 | 0 | 527.2935 | 0.18003
6491 | 1177.753 | 8.7625 | 97.625 | 148.1128 | 27.6494 | 19 | 127.3663 | 7.8681 | 23.3966 | 86.6242 | 184.1835 | 34.0755 | 423.3717 | 368.381 | 573.3782 | 6.7054 | 87.359 | 17.6375 | 333 | 93.9918 | 0 | 552.4802 | 0.1664
6492 | 1183.011 | 3.9733 | 99.246 | 148.3781 | 28.3834 | 19 | 128.4204 | 5.9522 | 22.4033 | 81.4498 | 188.591 | 36.9608 | 439.9603 | 381.4705 | 585.8517 | 7.3356 | 89.3438 | 17.3853 | 355 | 78.2618 | 0 | 562.0994 | 0.21414
6493 | 1174.7279 | 4.6695 | 98.0135 | 152.1534 | 28.575 | 19.9497 | 128.9303 | 4.4783 | 21.0667 | 76.6824 | 186.5372 | 39.7218 | 433.9418 | 377.0412 | 577.762 | 8.1533 | 87.5429 | 17.5546 | 277 | 79.1995 | 0 | 562.2614 | 0.22113
6494 | 1174.5696 | 5.7623 | 101.692 | 155.4678 | 31.6373 | 18.0505 | 136.2405 | 4.0759 | 24.67 | 78.3432 | 184.1978 | 39.4126 | 440.2174 | 370.7678 | 562.4485 | 9.4231 | 85.9195 | 17.7849 | 290 | 80.8947 | 0 | 541.9578 | 0.25367
6495 | 1133.5629 | 4.4494 | 102.4597 | 152.0986 | 32.1928 | 18.05 | 129.8181 | 3.7703 | 24.3367 | 72.096 | 182.9717 | 39.2867 | 450.6001 | 363.3248 | 555.4204 | 10.4608 | 84.9255 | 18.2203 | 270 | 78.3943 | 0 | 517.0513 | 0.22744
6496 | 1097.5325 | 3.4765 | 98.6704 | 142.6847 | 34.8273 | 15.2008 | 121.78 | 3.1985 | 20.8733 | 60.3189 | 180.7898 | 37.401 | 446.5138 | 342.382 | 521.3957 | 11.4039 | 84.6654 | 18.6199 | 257 | 71.9071 | 0 | 472.7173 | 0.12345
6497 | 1025.374 | 3.5862 | 96.6408 | 127.4434 | 42.9691 | 6.6524 | 108.8512 | 2.096 | 18.3133 | 49.9848 | 168.0508 | 31.0773 | 422.4739 | 296.3671 | 448.3317 | 14.3212 | 82.7268 | 18.4235 | 228 | 65.9204 | 0 | 399.1214 | 0.027186
6498 | 980.467 | 3.6983 | 95.1806 | 113.3733 | 40.5303 | 7.5997 | 92.4564 | 1.4218 | 13.5867 | 43.5254 | 138.0514 | 22.1188 | 371.8448 | 235.0472 | 373.804 | 16.9819 | 77.7773 | 15.2198 | 210 | 60.0917 | 0 | 346.8298 | 0
6499 | 943.0256 | 4.6421 | 77.9126 | 107.3181 | 41.5719 | 6.6503 | 70.5862 | 1.4253 | 11.8433 | 45.6357 | 111.8202 | 12.0905 | 315.7607 | 198.3323 | 328.3255 | 18.402 | 73.8852 | 9.1931 | 194 | 58.3873 | 0 | 304.1559 | 0
6500 | 931.8833 | 4.9974 | 36.7452 | 105.811 | 43.4716 | 5.7003 | 55.478 | 1.7034 | 10.3867 | 48.945 | 103.6431 | 8.2142 | 272.4515 | 187.5693 | 294.8573 | 22.0486 | 68.9969 | 5.7874 | 179 | 53.2167 | 0 | 264.3253 | 0
6501 | 879.8041 | 4.3012 | 23.7962 | 104.8388 | 42.7401 | 6.6497 | 55.7313 | 1.6157 | 8.8367 | 41.3028 | 101.3625 | 8.8275 | 241.9545 | 170.2637 | 267.4606 | 25.5698 | 61.7255 | 4.5977 | 170 | 47.7715 | 0 | 246.6324 | 0
6502 | 843.8264 | 3.2032 | 23.6184 | 100.4557 | 43.8636 | 5.7003 | 54.0004 | 1.5353 | 7.3467 | 29.4773 | 94.4661 | 11.1136 | 217.8729 | 150.8397 | 244.6929 | 26.3273 | 57.4625 | 4.2705 | 153 | 44.8513 | 0 | 240.2369 | 0
6503 | 814.381 | 1.8747 | 23.5871 | 98.7293 | 41.9829 | 6.6497 | 50.5706 | 1.5289 | 6.4633 | 23.4112 | 86.0624 | 10.8996 | 198.2781 | 138.9071 | 231.3462 | 26.6924 | 56.5736 | 4.2062 | 136 | 41.339 | 0 | 230.1055 | 0
6504 | 806.0513 | 1.3451 | 23.6218 | 98.4091 | 42.7853 | 5.7003 | 54.0833 | 1.5881 | 6.3169 | 22.1029 | 83.9503 | 8.4057 | 188.4303 | 130.0498 | 222.1061 | 26.5978 | 56.5075 | 4.1873 | 127 | 40.5391 | 0 | 219.0961 | 0
6505 | 813.0496 | 1.2932 | 23.5274 | 98.5492 | 42.5383 | 5.7 | 48.6452 | 1.7674 | 5.9216 | 22.1574 | 84.5037 | 7.4807 | 191.0805 | 122.6298 | 219.2185 | 26.3144 | 56.3432 | 4.1579 | 127 | 40.568 | 0 | 215.9364 | 0
6506 | 801.6718 | 1.3114 | 23.5407 | 98.4384 | 42.9466 | 5.7 | 50.8231 | 1.6702 | 5.8448 | 22.3044 | 81.6692 | 7.4721 | 194.0608 | 117.318 | 221.1718 | 26.766 | 56.2814 | 3.5199 | 131 | 40.5187 | 0 | 214.5609 | 0
6507 | 801.2958 | 1.2878 | 23.5244 | 98.1999 | 42.7919 | 5.7 | 53.5361 | 1.5435 | 5.94 | 23.743 | 76.9538 | 7.4789 | 193.6559 | 115.1773 | 216.0588 | 26.1128 | 56.2561 | 2.9946 | 129 | 39.5957 | 0 | 217.4778 | 0
6508 | 811.5066 | 1.6112 | 23.6788 | 98.922 | 40.879 | 7.5995 | 48.6612 | 1.5624 | 5.98 | 30.1048 | 74.499 | 7.4767 | 191.0174 | 114.2348 | 210.4402 | 26.6621 | 56.181 | 2.8925 | 132 | 39.2335 | 0 | 223.6878 | 0
6509 | 819.0146 | 2.6362 | 33.4521 | 99.1993 | 39.7502 | 8.5497 | 52.774 | 1.5459 | 5.93 | 36.191 | 74.2406 | 8.88 | 192.4554 | 115.9885 | 215.5783 | 26.9635 | 56.0395 | 2.8722 | 123 | 39.2463 | 0 | 238.0603 | 0
6510 | 863.9583 | 4.0583 | 55.5671 | 101.3338 | 38.4259 | 9.4997 | 65.244 | 1.5203 | 6.4733 | 36.833 | 83.7147 | 15.5116 | 202.2468 | 138.989 | 227.5241 | 26.2912 | 56.1924 | 2.8196 | 197 | 44.3549 | 0 | 273.5904 | 0
6511 | 922.7318 | 4.9952 | 74.6811 | 105.9627 | 34.01 | 13.2989 | 91.5969 | 2.6313 | 11.1867 | 46.812 | 105.5987 | 29.0999 | 233.2334 | 191.9877 | 284.0078 | 20.5984 | 59.5041 | 8.4179 | 279 | 52.1894 | 0 | 331.4696 | 0.019838
6512 | 1012.0773 | 5.3623 | 93.588 | 127.7787 | 31.6275 | 15.1995 | 110.9557 | 3.8207 | 16.2444 | 68.2062 | 123.4844 | 37.5136 | 291.4764 | 255.8771 | 384.1183 | 16.0659 | 66.5641 | 13.0475 | 305 | 64.8156 | 0 | 415.566 | 0.094834
6513 | 1097.1304 | 8.3845 | 97.3686 | 146.7881 | 31.5789 | 15.2 | 122.3706 | 4.5061 | 22.6576 | 81.4936 | 134.1268 | 40.3018 | 358.8629 | 300.7574 | 487.0624 | 10.9212 | 76.4177 | 14.5154 | 344 | 74.7396 | 0 | 503.1832 | 0.11583
6514 | 1139.7697 | 10.6964 | 98.896 | 151.2538 | 28.9365 | 18.0542 | 128.8438 | 4.9759 | 24.8064 | 84.7651 | 144.9015 | 41.3137 | 412.2427 | 320.3723 | 561.4254 | 9.288 | 84.9778 | 16.2187 | 361 | 80.1242 | 0 | 548.1455 | 0.15229
6515 | 1144.9551 | 7.146 | 102.3578 | 149.453 | 31.0932 | 16.1455 | 127.9052 | 4.685 | 23.8783 | 88.5203 | 159.1808 | 41.436 | 424.3523 | 340.6547 | 587.9718 | 6.9338 | 88.8607 | 15.8711 | 307 | 94.8635 | 0 | 548.6141 | 0.17596
6516 | 1142.8263 | 4.0409 | 104.1854 | 151.8126 | 32.0079 | 15.2003 | 121.3417 | 4.4556 | 22.7588 | 86.4109 | 172.1793 | 41.9601 | 432.0956 | 356.1308 | 587.8208 | 6.7328 | 89.6177 | 16.0426 | 362 | 76.3856 | 0 | 542.8576 | 0.22531
6517 | 1134.5409 | 3.3321 | 104.6012 | 153.4714 | 31.8657 | 16.1497 | 127.2794 | 4.3874 | 22.1182 | 80.5363 | 181.4935 | 43.4811 | 436.5744 | 357.247 | 588.079 | 7.0041 | 88.5366 | 16.8583 | 307 | 81.5497 | 0 | 563.595 | 0.17611
6518 | 1144.0557 | 3.5016 | 107.7459 | 154.9609 | 32.3739 | 16.15 | 145.589 | 4.1607 | 20.7763 | 79.8363 | 187.3195 | 42.6218 | 443.9802 | 359.0354 | 588.0345 | 6.4079 | 88.6815 | 17.1017 | 287 | 81.0427 | 0 | 567.9262 | 0.14185
6519 | 1129.8552 | 3.781 | 104.8123 | 149.7825 | 29.9282 | 18.0495 | 148.3264 | 4.1422 | 18.5668 | 77.0067 | 186.5577 | 40.6013 | 436.5313 | 359.4113 | 589.8719 | 6.8645 | 90.0127 | 17.1015 | 290 | 77.7189 | 0 | 545.4278 | 0.10121
6520 | 1082.4093 | 3.7213 | 98.4025 | 142.7652 | 32.0047 | 15.2008 | 130.3699 | 4.6852 | 13.3137 | 70.8494 | 181.9822 | 38.0128 | 417.4928 | 348.4383 | 561.1331 | 10.0635 | 88.8408 | 16.7855 | 251 | 75.9695 | 0 | 493.1631 | 0.027369
6521 | 1025.321 | 3.7527 | 93.6649 | 126.7905 | 38.9597 | 8.5518 | 110.4843 | 4.2483 | 11.0933 | 60.4929 | 167.7583 | 33.561 | 399.1898 | 292.0986 | 483.46 | 14.6147 | 83.2364 | 16.417 | 252 | 69.8951 | 0 | 413.1421 | 0.013663
6522 | 976.5412 | 3.9647 | 90.1765 | 111.6181 | 41.0268 | 6.6505 | 93.6379 | 2.3405 | 11.2213 | 48.7496 | 136.9371 | 24.9265 | 360.3198 | 205.5714 | 405.3001 | 17.5216 | 76.8937 | 14.2362 | 233 | 60.6853 | 0 | 354.4465 | 0
6523 | 924.0581 | 4.4849 | 76.1029 | 106.7915 | 42.1606 | 5.7003 | 82.0929 | 2.5602 | 10.8385 | 46.0238 | 110.4034 | 12.5857 | 310.494 | 152.3606 | 356.8831 | 20.0318 | 71.6555 | 8.9994 | 218 | 53.4219 | 0 | 308.8638 | 0
6524 | 886.7157 | 3.649 | 38.6008 | 103.2878 | 43.8433 | 4.7503 | 70.5052 | 2.2466 | 8.693 | 45.666 | 102.3814 | 8.5809 | 273.4714 | 136.8393 | 322.273 | 23.3719 | 65.8562 | 6.263 | 198 | 48.4629 | 0 | 279.5602 | 0
6525 | 839.738 | 3.2512 | 24.7856 | 101.4092 | 43.2232 | 4.75 | 62.4187 | 1.5822 | 7.3353 | 35.98 | 98.8637 | 9.4 | 241.4565 | 129.7365 | 282.8732 | 24.6033 | 61.4171 | 4.6341 | 170 | 46.4351 | 0 | 272.1273 | 0
6526 | 809.7836 | 2.8494 | 23.5375 | 100.4316 | 42.9127 | 4.75 | 54.1917 | 1.4541 | 6.8672 | 27.9598 | 90.0838 | 12.065 | 208.5098 | 121.3023 | 247.8121 | 25.5501 | 59.2527 | 3.7332 | 151 | 44.241 | 0 | 272.5523 | 0
6527 | 782.8465 | 1.7704 | 23.4867 | 101.5654 | 43.6126 | 4.75 | 60.0661 | 1.5813 | 6.3332 | 29.0849 | 79.6827 | 10.6896 | 194.1851 | 111.845 | 226.4924 | 25.636 | 58.2603 | 3.3903 | 144 | 40.2227 | 0 | 261.079 | 0
6528 | 780.3223 | 1.2961 | 23.4788 | 102.7066 | 43.1224 | 4.75 | 70.019 | 1.4718 | 6.0443 | 30.5449 | 75.5681 | 7.9734 | 184.2008 | 102.9476 | 213.6218 | 25.6378 | 58.1896 | 3.2673 | 130 | 39.5363 | 0 | 241.4747 | 0
6529 | 771.164 | 1.3005 | 23.4345 | 102.2013 | 43.1659 | 4.75 | 71.251 | 1.4182 | 6.0478 | 30.112 | 75.5747 | 7.25 | 183.3329 | 96.4725 | 216.2177 | 25.4083 | 58.3485 | 3.1405 | 125 | 37.6287 | 0 | 231.5596 | 0
6530 | 765.6169 | 1.2223 | 23.3815 | 101.6996 | 41.9704 | 5.6997 | 72.6506 | 1.3927 | 5.9812 | 29.7556 | 75.5614 | 7.25 | 184.5469 | 92.8904 | 219.1451 | 25.8276 | 58.0507 | 2.7047 | 123 | 36.1614 | 0 | 231.5395 | 0
6531 | 763.4147 | 1.147 | 23.2562 | 101.9539 | 43.2383 | 4.7503 | 74.8285 | 1.6592 | 5.9332 | 30.3799 | 75.2327 | 7.3824 | 183.4563 | 94.0759 | 215.8273 | 26.0093 | 57.7269 | 2.4888 | 120 | 37.403 | 0 | 233.4258 | 0
6532 | 765.6854 | 1.5583 | 23.2499 | 101.991 | 44.0791 | 3.8003 | 75.7192 | 1.5344 | 5.7728 | 34.8435 | 75.2028 | 7.2532 | 180.8143 | 94.5493 | 212.9574 | 25.7789 | 57.8114 | 2.4581 | 117 | 37.6459 | 0 | 236.5231 | 0
6533 | 775.3056 | 2.6206 | 32.3928 | 102.9009 | 43.3565 | 4.7497 | 79.0009 | 1.4223 | 5.7683 | 41.2283 | 75.8611 | 8.274 | 184.5103 | 93.3894 | 216.3751 | 25.8058 | 57.6984 | 2.8912 | 126 | 36.2305 | 0 | 252.9792 | 0
6534 | 823.2128 | 4.156 | 53.319 | 107.8839 | 41.8192 | 6.6495 | 82.6133 | 1.4017 | 6.128 | 42.3478 | 86.4725 | 18.2293 | 195.7322 | 123.5626 | 227.306 | 26.2931 | 57.2676 | 4.1189 | 190 | 40.6067 | 0 | 286.6736 | 0
6535 | 897.6091 | 5.2891 | 74.959 | 113.0234 | 38.6258 | 10.4489 | 108.5651 | 2.0176 | 7.0112 | 47.2628 | 112.7003 | 29.9387 | 233.1281 | 196.7664 | 289.6043 | 21.9571 | 60.1336 | 9.6529 | 312 | 51.3188 | 0 | 342.082 | 0
6536 | 993.8297 | 7.6253 | 92.6007 | 131.384 | 36.2363 | 13.2992 | 125.3026 | 2.9958 | 9.0037 | 60.8214 | 138.746 | 29.8846 | 288.7257 | 269.3345 | 399.7091 | 14.8739 | 69.5165 | 15.9541 | 292 | 66.421 | 0 | 419.9958 | 0.014319
6537 | 1064.0475 | 10.4905 | 100.0793 | 148.3412 | 35.7127 | 13.3 | 131.6489 | 4.1428 | 13.5557 | 74.5102 | 153.5577 | 32.1932 | 353.7703 | 313.111 | 504.9617 | 7.6804 | 82.0377 | 16.5597 | 377 | 71.2256 | 0 | 490.5043 | 0.016108
6538 | 1112.8485 | 10.3086 | 103.483 | 152.5346 | 34.4193 | 14.2497 | 145.0919 | 5.1934 | 20.3462 | 85.4512 | 162.8424 | 38.2629 | 399.4432 | 337.8289 | 568.6966 | 6.2818 | 89.8915 | 17.1494 | 363 | 75.0023 | 0 | 533.6874 | 0.021972
6539 | 1136.7806 | 5.3565 | 106.0666 | 154.16 | 30.488 | 18.054 | 146.9659 | 5.141 | 26.7458 | 88.3789 | 170.1312 | 39.0893 | 418.3667 | 357.0025 | 593.6167 | 5.9444 | 91.8541 | 17.9055 | 359 | 85.6184 | 0 | 563.898 | 0.037405
6540 | 1147.3944 | 3.2392 | 109.3702 | 152.821 | 31.3895 | 17.0953 | 144.6863 | 4.572 | 25.8352 | 81.5661 | 177.4946 | 38.1806 | 428.2877 | 357.2739 | 585.3308 | 6.4203 | 91.0901 | 18.4014 | 352 | 76.4884 | 0 | 582.4709 | 0.091759
6541 | 1152.8844 | 3.3142 | 108.4961 | 152.3678 | 33.334 | 15.2005 | 144.4242 | 4.3649 | 21.588 | 77.8582 | 187.9426 | 37.8448 | 422.9947 | 355.0695 | 580.3983 | 5.5812 | 90.9664 | 18.74 | 336 | 79.1681 | 0 | 586.4477 | 0.1198
6542 | 1159.7174 | 3.5659 | 105.3595 | 157.4709 | 32.7138 | 16.1497 | 151.9485 | 4.156 | 23.9852 | 81.169 | 197.4626 | 38.7402 | 426.2831 | 365.876 | 573.3293 | 5.4198 | 92.3024 | 18.7927 | 292 | 78.9495 | 0 | 581.6435 | 0.17926
6543 | 1147.3399 | 3.5894 | 103.3981 | 150.8303 | 32.4924 | 16.1545 | 143.9882 | 3.3339 | 24.1993 | 78.5221 | 199.1844 | 38.8687 | 422.2434 | 368.2526 | 568.5224 | 7.732 | 90.6825 | 18.6141 | 289 | 76.1101 | 0 | 556.5944 | 0.15741
6544 | 1125.0735 | 3.4433 | 101.4759 | 141.8496 | 35.3718 | 13.2963 | 131.6454 | 2.7465 | 18.283 | 69.9879 | 194.3016 | 36.8638 | 413.0234 | 352.2387 | 547.335 | 11.0494 | 86.9951 | 18.2899 | 261 | 70.4427 | 0 | 498.3027 | 0.10771
6545 | 1072.5956 | 3.4155 | 95.9246 | 125.1855 | 42.3942 | 6.6518 | 116.0834 | 1.6012 | 15.4737 | 58.5043 | 179.1441 | 31.4334 | 391.5492 | 292.9867 | 477.3196 | 15.6114 | 81.184 | 17.8587 | 235 | 60.7345 | 0 | 409.4469 | 0.034411
6546 | 999.584 | 4.0549 | 89.4837 | 110.7788 | 43.6241 | 4.7505 | 107.0415 | 1.1076 | 10.3358 | 47.4523 | 146.2245 | 23.3901 | 347.2098 | 215.4125 | 403.8652 | 18.1772 | 74.8554 | 15.1134 | 224 | 51.0983 | 0 | 343.301 | 0
6547 | 936.4664 | 3.7433 | 75.1961 | 105.6734 | 42.8177 | 4.75 | 96.8645 | 1.4968 | 7.9717 | 49.3672 | 117.7367 | 13.1281 | 297.6925 | 173.2556 | 352.5544 | 20.1644 | 71.077 | 10.0796 | 209 | 47.5165 | 0 | 304.2856 | 0
6548 | 891.5488 | 3.3581 | 36.2959 | 101.6703 | 41.5858 | 5.7013 | 82.6239 | 1.4827 | 8.6165 | 55.4109 | 108.4386 | 9.2044 | 265.4176 | 151.1092 | 307.6851 | 23.0922 | 66.17 | 7.1227 | 194 | 45.7139 | 0 | 274.2744 | 0
6549 | 855.4365 | 3.6224 | 23.5854 | 101.56 | 42.7717 | 4.7487 | 76.6872 | 1.3961 | 8.467 | 47.1447 | 102.8665 | 8.8516 | 246.3518 | 132.4261 | 270.4426 | 25.6979 | 60.3943 | 5.9299 | 185 | 43.5037 | 0 | 255.793 | 0
6550 | 827.9207 | 3.2714 | 23.1936 | 99.8441 | 42.771 | 4.75 | 75.0674 | 1.4782 | 7.1983 | 33.4011 | 91.8746 | 8.8991 | 221.0985 | 119.6297 | 252.1082 | 26.5501 | 57.3686 | 5.5282 | 164 | 41.6668 | 0 | 243.6646 | 0
6551 | 799.2848 | 2.066 | 23.1256 | 99.4759 | 42.6248 | 4.75 | 74.5129 | 1.6192 | 6.5064 | 27.0985 | 81.299 | 8.9742 | 203.7177 | 108.624 | 241.705 | 26.0898 | 56.8618 | 5.4727 | 157 | 39.3937 | 0 | 241.1038 | 0
6552 | 800.4746 | 1.6325 | 23.1026 | 98.1049 | 42.5856 | 4.75 | 73.4856 | 1.493 | 6.2045 | 25.2109 | 77.5275 | 8.89 | 193.4828 | 101.8142 | 228.2099 | 26.301 | 56.8596 | 5.0099 | 140 | 37.1793 | 0 | 234.1113 | 0
6553 | 798.7064 | 1.6139 | 23.2228 | 97.9551 | 42.5897 | 4.75 | 72.9284 | 1.4217 | 5.9292 | 24.281 | 77.5866 | 8.8899 | 192.8819 | 100.9288 | 225.7656 | 26.1327 | 56.9774 | 4.6702 | 127 | 37.9452 | 0 | 231.8233 | 0
6554 | 789.8959 | 1.5468 | 23.2753 | 97.0599 | 41.5923 | 5.6997 | 74.0975 | 1.4286 | 6.0072 | 24.1718 | 77.3739 | 8.9134 | 192.91 | 99.428 | 228.165 | 25.9509 | 57.3568 | 4.6265 | 126 | 37.6586 | 0 | 237.8729 | 0
6555 | 783.5645 | 1.7463 | 23.2725 | 98.1779 | 42.5883 | 4.7503 | 73.5262 | 1.4355 | 6.2235 | 25.6707 | 76.2864 | 8.8517 | 189.6578 | 95.8148 | 226.6125 | 25.8292 | 57.572 | 4.6686 | 121 | 38.4736 | 0 | 240.5534 | 0
6556 | 784.771 | 1.8375 | 23.2237 | 98.5432 | 42.5874 | 4.75 | 73.7198 | 1.6711 | 6.167 | 32.0829 | 75.8087 | 8.7759 | 185.2285 | 96.9127 | 229.6803 | 25.7118 | 58.0367 | 4.5269 | 128 | 36.2772 | 0 | 247.202 | 0
6557 | 793.177 | 4.1155 | 31.8857 | 99.1988 | 42.5861 | 4.75 | 73.4902 | 1.5891 | 5.8298 | 38.4183 | 76.904 | 10.8627 | 191.5899 | 101.4977 | 228.7708 | 25.7395 | 57.998 | 4.3352 | 119 | 35.8277 | 0 | 267.1407 | 0
6558 | 838.9343 | 7.438 | 51.5111 | 102.3037 | 39.5848 | 7.5992 | 80.8701 | 1.4835 | 5.9588 | 41.0892 | 87.649 | 16.0409 | 203.5345 | 132.3809 | 247.6349 | 25.8224 | 57.7919 | 4.0089 | 190 | 40.6951 | 0 | 312.3816 | 0
6559 | 894.4032 | 8.3906 | 74.7086 | 106.3279 | 33.58 | 13.2984 | 94.3022 | 2.759 | 10.0669 | 49.515 | 113.9882 | 27.058 | 237.7908 | 202.7637 | 319.883 | 22.5269 | 59.9244 | 9.3311 | 237 | 47.2157 | 0 | 367.6818 | 0
6560 | 974.7382 | 12.4528 | 89.4018 | 128.2106 | 32.5772 | 14.2497 | 106.4992 | 3.7627 | 14.0078 | 63.4898 | 145.837 | 33.4066 | 293.3196 | 273.7613 | 411.2083 | 16.5545 | 66.4895 | 14.5097 | 296 | 59.2336 | 0 | 433.1202 | 0.060121
6561 | 1044.6123 | 16.5193 | 94.3058 | 142.6903 | 28.5781 | 18.0489 | 122.4118 | 4.8733 | 19.2423 | 77.1029 | 168.0911 | 38.0616 | 352.5861 | 322.2518 | 485.7615 | 11.4676 | 75.7394 | 16.5412 | 383 | 75.1967 | 0 | 501.2246 | 0.14065
6562 | 1100.7129 | 13.9846 | 96.5972 | 143.9094 | 29.5804 | 17.1003 | 132.6122 | 5.808 | 22.1247 | 84.4729 | 178.6602 | 41.5497 | 395.8138 | 357.0457 | 544.5825 | 22.6019 | 83.8227 | 18.1644 | 355 | 66.4505 | 0 | 539.2635 | 0.1271
6563 | 1116.2453 | 6.8057 | 100.9791 | 147.8887 | 27.5821 | 18.9995 | 135.1772 | 4.7394 | 22.5437 | 88.6196 | 184.1556 | 42.3052 | 420.3896 | 379.4891 | 589.0731 | 27.5147 | 88.9899 | 18.784 | 341 | 76.5214 | 0 | 570.5931 | 0.14335
6564 | 1097.9329 | 3.6942 | 102.9833 | 147.9837 | 30.5803 | 16.1508 | 133.7795 | 3.8201 | 20.7802 | 81.8431 | 188.2936 | 41.806 | 442.4987 | 376.3679 | 599.1999 | 27.8318 | 89.9559 | 18.6365 | 379 | 72.1504 | 0 | 581.8126 | 0.11592
6565 | 1093.6945 | 3.6404 | 101.9038 | 148.1045 | 30.5841 | 16.15 | 134.2711 | 3.567 | 13.8305 | 65.3326 | 192.5494 | 40.641 | 440.1252 | 356.3478 | 592.0022 | 29.0055 | 88.2087 | 18.4193 | 338 | 75.2475 | 0 | 573.454 | 0.10461
6566 | 1113.4079 | 3.6743 | 101.8538 | 148.3977 | 30.5846 | 16.15 | 132.8912 | 3.8595 | 13.5703 | 58.4215 | 197.3856 | 39.2117 | 442.2536 | 339.0617 | 577.0565 | 38.6407 | 85.7421 | 18.6236 | 317 | 73.8338 | 0 | 570.6114 | 0.1185
6567 | 1093.7635 | 3.8686 | 99.8989 | 143.6498 | 30.5719 | 16.1545 | 121.7837 | 3.5206 | 14.6708 | 56.4882 | 198.379 | 37.6295 | 434.0394 | 321.8933 | 554.0554 | 39.1378 | 83.3059 | 18.5742 | 306 | 65.6865 | 0 | 547.261 | 0.13316
6568 | 1055.3787 | 3.7351 | 95.0153 | 134.9622 | 32.5815 | 14.246 | 113.8429 | 2.9112 | 14.308 | 54.0866 | 192.8537 | 36.1078 | 413.7959 | 294.152 | 507.7128 | 23.8943 | 80.2372 | 18.2812 | 286 | 57.1751 | 0 | 473.5421 | 0.056814
6569 | 993.041 | 3.5573 | 79.5209 | 127.0239 | 41.5812 | 5.7024 | 101.7404 | 1.9081 | 13.708 | 49.3199 | 177.6117 | 32.1502 | 376.1732 | 240.9181 | 421.2326 | 12.1523 | 74.3273 | 17.0845 | 279 | 48.7575 | 0 | 384.9947 | 0.017477
6570 | 930.9134 | 3.623 | 39.2171 | 110.1342 | 42.5841 | 4.7503 | 85.5094 | 1.3672 | 14.756 | 46.3241 | 145.663 | 24.3196 | 319.4765 | 180.2222 | 347.8152 | 8.9115 | 67.3979 | 14.0584 | 271 | 44.2665 | 0 | 325.9266 | 0
6571 | 878.9847 | 3.5157 | 25.1845 | 102.72 | 41.5854 | 5.6997 | 69.1198 | 1.438 | 14.401 | 51.7169 | 115.8179 | 18.6968 | 265.8605 | 146.6303 | 326.924 | 8.7155 | 61.9872 | 8.9116 | 247 | 39.5827 | 0 | 291.4836 | 0
6572 | 839.4149 | 3.5839 | 24.0984 | 100.7381 | 42.5842 | 4.7503 | 58.3145 | 1.731 | 9.932 | 55.3935 | 100.1278 | 17.7227 | 235.2829 | 133.0527 | 306.9979 | 8.628 | 58.5537 | 6.4236 | 285 | 39.7349 | 0 | 272.6002 | 0
6573 | 813.5433 | 3.3822 | 23.7598 | 99.8856 | 42.5828 | 4.75 | 56.2082 | 1.6004 | 7.844 | 45.999 | 90.6027 | 14.7054 | 213.7562 | 125.2696 | 278.7155 | 8.5379 | 56.1885 | 5.7841 | 261 | 40.0022 | 0 | 264.057 | 0
6574 | 799.1753 | 2.7299 | 23.7121 | 99.7217 | 42.5847 | 4.75 | 57.91 | 1.4993 | 7.35 | 34.5496 | 87.544 | 16.4923 | 194.5111 | 116.4872 | 260.919 | 8.6782 | 54.3157 | 5.4503 | 236 | 40.0391 | 0 | 262.3135 | 0
6575 | 776.4745 | 1.7025 | 23.5764 | 99.3467 | 41.5851 | 5.7013 | 49.593 | 1.5055 | 7.06 | 31.2253 | 87.2845 | 14.8809 | 191.6584 | 108.9159 | 250.3937 | 8.5718 | 53.3746 | 5.1165 | 207 | 38.1321 | 0 | 259.3094 | 0
6576 | 782.9437 | 1.4456 | 23.3351 | 100.2672 | 24.5326 | 4.7487 | 57.4479 | 1.5301 | 6.741 | 29.1496 | 85.6786 | 9.4831 | 194.7863 | 101.4395 | 240.5632 | 8.631 | 52.5486 | 4.8303 | 204 | 37.1814 | 0 | 251.4666 | 0
6577 | 778.7399 | 1.2946 | 22.336 | 99.9375 | 24.5321 | 4.75 | 62.9252 | 1.545 | 6.546 | 26.0933 | 84.0551 | 7.5681 | 198.0626 | 93.3193 | 236.845 | 8.6272 | 52.8342 | 4.8961 | 179 | 37.6721 | 0 | 245.311 | 0
6578 | 757.9983 | 1.1614 | 21.9281 | 99.8635 | 23.5297 | 5.6997 | 65.0888 | 1.7834 | 6.503 | 23.9889 | 83.6517 | 7.5529 | 196.6975 | 88.5503 | 244.3539 | 8.5111 | 53.3044 | 5.2292 | 168 | 34.4063 | 0 | 243.7068 | 0
6579 | 762.9971 | 1.2565 | 22.0817 | 99.3728 | 24.5309 | 4.7516 | 67.0123 | 1.6406 | 6.528 | 24.1407 | 83.8817 | 7.604 | 191.1602 | 84.7215 | 245.5571 | 8.7553 | 52.3609 | 4.5781 | 142 | 35.5664 | 0 | 243.4246 | 0
6580 | 770.6411 | 1.8881 | 22.0002 | 99.7692 | 22.5373 | 6.6482 | 64.7667 | 1.5689 | 6.61 | 30.6022 | 84.0889 | 7.5443 | 187.5602 | 83.2653 | 236.5976 | 8.7072 | 52.4578 | 3.9158 | 135 | 34.9233 | 0 | 243.0184 | 0
6581 | 770.7593 | 2.7484 | 22.105 | 99.733 | 21.5295 | 7.5997 | 61.4528 | 1.5413 | 6.563 | 36.8426 | 84.0225 | 7.4633 | 186.8983 | 82.9017 | 216.7703 | 8.7675 | 54.8845 | 3.5622 | 124 | 33.1488 | 0 | 245.2988 | 0
6582 | 791.2745 | 2.9443 | 22.4038 | 99.5968 | 21.5263 | 7.6 | 61.0845 | 1.5208 | 6.761 | 32.1861 | 83.6077 | 7.2092 | 182.8397 | 85.4746 | 204.2591 | 8.6487 | 54.6914 | 3.4116 | 127 | 32.9972 | 0 | 250.5591 | 0
6583 | 807.9243 | 1.9756 | 21.9864 | 100.5103 | 22.5293 | 6.6503 | 63.2195 | 1.255 | 6.293 | 23.1676 | 85.137 | 7.5958 | 176.1119 | 84.3623 | 208.2128 | 8.0584 | 51.6048 | 3.4878 | 119 | 33.4843 | 0 | 244.3296 | 0
6584 | 824.3786 | 1.5147 | 32.0889 | 100.7024 | 24.5282 | 4.7505 | 72.1277 | 1.5907 | 5.9652 | 20.7468 | 101.7464 | 12.108 | 171.7631 | 81.0933 | 217.276 | 8.1021 | 50.3543 | 3.9066 | 120 | 36.1878 | 0 | 237.1742 | 0.16641
6585 | 843.2383 | 1.5043 | 48.1073 | 100.0636 | 24.5238 | 4.75 | 83.4205 | 2.8736 | 5.6415 | 22.9502 | 128.0628 | 13.7757 | 175.7771 | 83.6763 | 212.8726 | 8.105 | 50.396 | 5.9791 | 133 | 37.9201 | 0 | 235.2819 | 0.18746
6586 | 852.37 | 1.3944 | 64.9781 | 99.563 | 24.5262 | 4.75 | 91.1888 | 2.0927 | 7.1114 | 26.459 | 143.3654 | 13.6878 | 188.6579 | 93.6325 | 215.0423 | 8.2142 | 50.676 | 11.2665 | 177 | 39.2964 | 0 | 233.2471 | 0.19976
6587 | 867.9796 | 1.218 | 74.2145 | 100.1807 | 24.5284 | 4.75 | 90.0408 | 1.2697 | 6.579 | 29.9042 | 135.1669 | 13.8121 | 205.2678 | 106.3317 | 229.6434 | 8.1891 | 50.8531 | 13.3055 | 173 | 43.1359 | 0 | 234.9496 | 0.16696
6588 | 858.5152 | 1.2983 | 74.9316 | 100.1205 | 24.5262 | 4.75 | 83.316 | 1.1313 | 6.165 | 31.3633 | 116.7873 | 14.6353 | 213.7314 | 115.0225 | 246.6099 | 7.9107 | 51.9978 | 13.3272 | 182 | 45.4726 | 0 | 236.2861 | 0.19242
6589 | 859.8768 | 1.4743 | 71.5146 | 100.3294 | 23.5233 | 5.6997 | 83.6754 | 1.1043 | 6.035 | 31.973 | 116.8983 | 14.631 | 215.7075 | 122.016 | 251.5243 | 8.0263 | 55.1837 | 13.4607 | 187 | 46.2219 | 0 | 253.2151 | 0.19896
6590 | 850.7776 | 1.2364 | 45.3758 | 100.2831 | 24.5875 | 4.7503 | 79.9571 | 1.1135 | 5.729 | 33.4025 | 128.6936 | 15.701 | 211.1379 | 128.119 | 265.3127 | 8.11 | 56.9487 | 13.9869 | 209 | 46.2771 | 0 | 266.4358 | 0.19684
6591 | 855.4526 | 1.1353 | 35.7581 | 100.4033 | 25.7528 | 3.8003 | 71.3729 | 1.3858 | 5.826 | 33.6355 | 128.7396 | 15.3482 | 200.2529 | 128.1032 | 285.7819 | 8.0267 | 56.4216 | 14.5724 | 195 | 47.1287 | 0 | 263.898 | 0.17865
6592 | 842.1264 | 1.2896 | 35.5592 | 101.6079 | 24.0858 | 5.6995 | 74.7637 | 1.2537 | 6.204 | 33.0445 | 118.6455 | 7.8209 | 201.9266 | 121.8968 | 290.4685 | 8.1152 | 55.1579 | 15.0459 | 222 | 46.6912 | 0 | 263.1642 | 0.11588
6593 | 835.7684 | 1.5369 | 34.9773 | 101.7805 | 25.1281 | 4.7503 | 80.5716 | 1.1164 | 6.848 | 32.1167 | 108.5319 | 4.3231 | 205.3489 | 120.4484 | 279.1264 | 7.9004 | 53.402 | 13.3367 | 218 | 44.208 | 0 | 253.734 | 0.06848
6594 | 833.4045 | 3.1013 | 34.6067 | 100.4719 | 23.8006 | 5.6997 | 83.7602 | 1.2366 | 7.574 | 31.4212 | 101.6212 | 4.6617 | 199.9507 | 124.9514 | 265.1068 | 8.1336 | 52.1156 | 8.7111 | 202 | 42.4573 | 0 | 240.7967 | 0
6595 | 828.827 | 3.4946 | 34.7673 | 100.2964 | 21.5706 | 7.5995 | 75.2919 | 1.4802 | 7.818 | 36.6805 | 100.7811 | 6.0747 | 199.1097 | 129.726 | 262.6941 | 8.4208 | 52.0041 | 6.6714 | 201 | 41.0648 | 0 | 241.2095 | 0
6596 | 806.5568 | 3.276 | 34.7704 | 98.501 | 22.5269 | 6.6503 | 72.0998 | 1.5724 | 8.579 | 41.9673 | 97.5242 | 6.5719 | 195.6089 | 128.6376 | 261.4005 | 8.6023 | 52.6006 | 5.9262 | 202 | 38.4671 | 0 | 252.6431 | 0
6597 | 796.7029 | 3.2697 | 34.9311 | 97.2983 | 21.5297 | 7.5997 | 77.349 | 1.5886 | 8.389 | 36.7003 | 90.7518 | 10.8247 | 186.5154 | 120.3887 | 267.2538 | 8.7315 | 52.101 | 5.3374 | 198 | 37.953 | 0 | 267.3525 | 0
6598 | 782.4068 | 2.7536 | 34.9079 | 97.6931 | 22.5298 | 6.6503 | 79.1494 | 1.8997 | 7.456 | 28.7844 | 87.1286 | 15.826 | 172.5208 | 110.0027 | 273.777 | 8.4598 | 51.1862 | 5.1997 | 178 | 36.1383 | 0 | 277.6298 | 0
6599 | 765.6489 | 2.0419 | 34.8404 | 96.9216 | 23.5321 | 5.7003 | 78.6271 | 1.7431 | 6.807 | 27.0647 | 85.2644 | 13.2793 | 165.6255 | 107.6939 | 270.7853 | 8.6258 | 51.1748 | 4.9294 | 168 | 36.7095 | 0 | 278.2569 | 0
6600 | 790.3733 | 1.8192 | 35.1388 | 97.5301 | 14.5027 | 5.7 | 77.6827 | 1.6241 | 6.681 | 26.9717 | 84.2501 | 8.1123 | 165.1105 | 135.0614 | 253.7691 | 8.6185 | 51.5225 | 4.5487 | 166 | 35.7075 | 0 | 276.7556 | 0
6601 | 779.1094 | 1.4577 | 34.9841 | 97.9344 | 15.499 | 4.7503 | 76.9 | 1.6272 | 6.732 | 25.9402 | 83.8031 | 5.6379 | 173.5517 | 165.7485 | 250.2483 | 8.6478 | 51.4505 | 4.3476 | 166 | 33.9836 | 0 | 278.1952 | 0
6602 | 758.1073 | 1.2204 | 35.6114 | 98.1519 | 10.5013 | 9.4987 | 77.0972 | 1.6365 | 6.827 | 25.2942 | 83.2341 | 5.1981 | 178.5001 | 171.1105 | 248.0656 | 8.711 | 51.2768 | 4.0647 | 159 | 33.2718 | 0 | 272.0555 | 0
6603 | 766.089 | 1.1713 | 36.333 | 98.6748 | 10.5022 | 9.5 | 77.016 | 1.6364 | 6.622 | 24.9881 | 83.2195 | 5.1959 | 178.908 | 168.3855 | 240.7171 | 8.5068 | 51.635 | 3.3666 | 148 | 34.3096 | 0 | 257.4516 | 0
6604 | 750.5835 | 3.5291 | 36.4189 | 99.8977 | 11.4997 | 8.5503 | 76.8965 | 1.6481 | 6.534 | 25.8451 | 82.9926 | 5.1731 | 177.0146 | 164.279 | 241.8553 | 8.6528 | 52.5897 | 3.1294 | 140 | 33.4832 | 0 | 247.2693 | 0
6605 | 751.1167 | 5.7907 | 37.5613 | 102.4552 | 14.5008 | 5.7008 | 76.7471 | 1.9806 | 6.26 | 26.8404 | 81.984 | 5.1638 | 175.1907 | 154.588 | 234.5723 | 8.6093 | 54.5643 | 3.0085 | 133 | 32.8467 | 0 | 245.0623 | 0
6606 | 766.9574 | 4.3399 | 37.9916 | 102.4404 | 15.5037 | 4.7503 | 77.2394 | 1.8296 | 6.448 | 25.1225 | 81.6297 | 5.2027 | 171.8551 | 129.2218 | 228.1932 | 8.6197 | 54.1679 | 2.9617 | 136 | 31.9386 | 0 | 246.177 | 0
6607 | 781.5348 | 2.5425 | 37.8707 | 100.2968 | 14.5018 | 5.6997 | 72.7715 | 1.4247 | 6.426 | 21.9674 | 80.8904 | 4.7235 | 168.1757 | 108.8726 | 219.8537 | 8.3407 | 51.2353 | 3.2188 | 132 | 32.0969 | 0 | 242.2965 | 0
6608 | 787.403 | 1.3172 | 37.7525 | 99.4111 | 15.4999 | 4.7503 | 64.6871 | 1.3309 | 6.164 | 20.8004 | 80.9687 | 6.547 | 169.8296 | 109.1808 | 219.7691 | 7.9764 | 49.9253 | 4.2491 | 129 | 34.469 | 0 | 235.9245 | 0.051213
6609 | 792.4283 | 1.0167 | 37.5969 | 99.9335 | 14.4972 | 5.6997 | 57.5437 | 1.3024 | 5.884 | 22.8273 | 87.2047 | 6.2276 | 175.8716 | 113.6428 | 225.0272 | 8.1535 | 49.998 | 6.6072 | 170 | 37.0696 | 0 | 233.3415 | 0.11235
6610 | 814.4542 | 1.027 | 37.7367 | 100.5378 | 13.4962 | 6.6497 | 76.1851 | 1.2762 | 7.018 | 25.3991 | 98.6275 | 5.9025 | 178.3749 | 116.17 | 225.937 | 8.2042 | 50.2434 | 11.6891 | 167 | 39.2369 | 0 | 235.1825 | 0.1591
6611 | 840.7418 | 1.0622 | 37.5434 | 100.7576 | 12.4953 | 7.5997 | 76.4871 | 1.2238 | 7.155 | 27.4058 | 110.7447 | 7.3191 | 189.8498 | 113.9669 | 224.8057 | 8.0896 | 50.3584 | 13.8888 | 173 | 40.9379 | 0 | 238.6491 | 0.18695
6612 | 858.3634 | 1.592 | 37.6501 | 101.2586 | 13.5 | 6.6503 | 63.8027 | 1.5178 | 6.416 | 29.7296 | 120.7446 | 7.8741 | 196.6105 | 112.6622 | 230.482 | 8.1476 | 50.7318 | 14.3081 | 175 | 47.0324 | 0 | 239.6228 | 0.14724
6613 | 860.4584 | 1.773 | 38.0352 | 102.1102 | 14.5644 | 5.7003 | 73.8669 | 1.3295 | 6.093 | 31.4104 | 128.5907 | 7.9259 | 202.6632 | 116.0385 | 235.2652 | 7.9234 | 52.3037 | 14.1223 | 179 | 47.7245 | 0 | 241.2688 | 0.21026
6614 | 851.8592 | 1.5905 | 38.1221 | 103.3085 | 15.8505 | 4.7503 | 89.7091 | 1.1578 | 6.081 | 32.08 | 128.4673 | 5.6379 | 207.3371 | 118.9943 | 237.8979 | 8.0614 | 54.0448 | 13.99 | 177 | 46.8765 | 0 | 243.2256 | 0.20695
6615 | 852.9578 | 1.7402 | 38.1548 | 102.014 | 15.4225 | 5.6997 | 84.2947 | 1.137 | 6.027 | 30.5917 | 115.9719 | 5.834 | 208.3657 | 117.5025 | 247.1694 | 8.201 | 52.7887 | 14.8128 | 186 | 46.1951 | 0 | 242.3562 | 0.17191
6616 | 849.717 | 1.9056 | 38.1998 | 103.6519 | 17.0207 | 4.7503 | 69.9127 | 1.1308 | 5.965 | 25.7532 | 103.6675 | 4.2812 | 206.9623 | 115.3888 | 255.6832 | 8.1681 | 50.5253 | 15.2503 | 184 | 45.0929 | 0 | 239.1793 | 0.087185
6617 | 840.6519 | 1.6719 | 38.1389 | 105.4258 | 17.2403 | 4.75 | 63.6343 | 1.1592 | 5.705 | 22.6903 | 100.6364 | 4.0891 | 209.7269 | 114.7265 | 272.642 | 8.2045 | 50.5268 | 12.8811 | 169 | 44.448 | 0 | 234.7549 | 0.042687
6618 | 833.8193 | 2.7309 | 38.1491 | 104.1398 | 16.658 | 4.75 | 62.8765 | 1.3184 | 5.719 | 23.37 | 106.6514 | 6.1321 | 206.7434 | 115.0793 | 275.4401 | 8.0205 | 51.9425 | 7.5455 | 156 | 44.7812 | 0 | 238.0328 | 0
6619 | 827.866 | 3.1865 | 38.0078 | 101.642 | 15.8063 | 4.75 | 70.8673 | 1.8761 | 6.127 | 26.8186 | 113.6169 | 11.0073 | 201.6743 | 115.5424 | 252.1063 | 8.5201 | 53.5137 | 5.7919 | 146 | 42.0204 | 0 | 252.1964 | 0
6620 | 814.513 | 3.6871 | 38.2132 | 101.3614 | 14.505 | 5.6997 | 78.5217 | 1.8155 | 6.553 | 30.162 | 107.2524 | 12.3698 | 196.2299 | 112.8466 | 236.6976 | 8.7087 | 53.6907 | 5.7315 | 145 | 39.2974 | 0 | 258.2793 | 0
6621 | 789.5378 | 3.2756 | 38.3495 | 100.208 | 15.5056 | 4.7503 | 77.4919 | 1.6669 | 6.817 | 28.8113 | 94.6169 | 9.6217 | 191.5689 | 105.8451 | 225.1479 | 8.6248 | 53.0658 | 5.1261 | 142 | 35.8771 | 0 | 253.0329 | 0
6622 | 777.3777 | 2.6592 | 38.1631 | 100.6638 | 13.5035 | 6.6495 | 79.316 | 1.6778 | 6.845 | 25.6676 | 87.3549 | 7.5064 | 179.3345 | 98.9664 | 209.5103 | 8.6663 | 53.0516 | 4.8253 | 138 | 33.9958 | 0 | 249.1955 | 0
6623 | 758.0695 | 1.7354 | 38.0001 | 100.0367 | 12.5002 | 7.5997 | 73.9957 | 1.6912 | 6.746 | 24.2198 | 82.8205 | 7.0711 | 173.7868 | 94.4649 | 216.0309 | 8.527 | 53.0484 | 4.9287 | 121 | 32.467 | 0 | 243.9582 | 0
6624 | 752.3788 | 1.4056 | 38.0442 | 99.7166 | 12.4986 | 7.6 | 70.9145 | 1.7041 | 6.682 | 23.1763 | 80.4595 | 7.0966 | 169.0617 | 94.6587 | 219.8598 | 8.5581 | 53.246 | 4.5493 | 117 | 32.2946 | 0 | 239.1127 | 0
6625 | 746.7609 | 1.2657 | 38.0408 | 99.398 | 13.5048 | 6.6503 | 76.8084 | 1.7228 | 6.516 | 21.9802 | 80.0866 | 7.3313 | 172.1161 | 100.7019 | 218.7971 | 8.658 | 53.8044 | 4.102 | 114 | 31.7109 | 0 | 238.3952 | 0
6626 | 737.5634 | 1.3559 | 38.2405 | 99.4415 | 14.5036 | 5.7003 | 79.1799 | 2.0556 | 6.478 | 21.6459 | 80.1649 | 7.231 | 173.4394 | 103.9474 | 218.7271 | 8.569 | 53.3905 | 3.6715 | 110 | 31.8965 | 0 | 239.0152 | 0
6627 | 743.1087 | 1.6486 | 38.146 | 100.0632 | 14.5014 | 5.7 | 79.0279 | 1.9045 | 6.546 | 23.1832 | 80.162 | 7.0566 | 172.3038 | 103.8059 | 209.902 | 8.691 | 53.2858 | 3.5211 | 108 | 31.7875 | 0 | 239.7045 | 0
6628 | 749.0593 | 2.1797 | 40.3797 | 99.7177 | 15.5004 | 4.7503 | 78.9532 | 1.7817 | 6.584 | 29.7758 | 80.149 | 7.0773 | 171.6952 | 103.513 | 207.2289 | 8.452 | 54.4262 | 3.5366 | 107 | 31.5757 | 0 | 258.6019 | 0
6629 | 754.5226 | 2.9298 | 42.2417 | 99.1157 | 14.4958 | 5.6997 | 79.96 | 1.7694 | 6.555 | 36.5729 | 80.5886 | 8.0149 | 175.7178 | 103.9324 | 214.0395 | 8.6667 | 56.2769 | 3.6111 | 110 | 31.6987 | 0 | 285.4535 | 0
6630 | 810.2121 | 4.4057 | 48.5755 | 105.6322 | 9.4966 | 10.4487 | 90.2187 | 1.7788 | 7.086 | 36.7812 | 94.3255 | 17.5008 | 181.2842 | 138.4171 | 232.8918 | 12.0747 | 55.7108 | 4.3763 | 162 | 39.7813 | 0 | 325.372 | 0
6631 | 904.5339 | 4.9839 | 75.1539 | 111.2883 | 3.7839 | 16.1484 | 117.0989 | 3.7372 | 7.25 | 45.6927 | 121.9095 | 29.3624 | 218.4925 | 213.6944 | 298.9379 | 26.9289 | 55.6614 | 9.8233 | 238 | 45.606 | 0 | 394.4918 | 0
6632 | 995.6107 | 4.049 | 91.6388 | 127.7424 | 0.66679 | 18.9992 | 136.9455 | 8.3332 | 12.729 | 66.456 | 148.6414 | 35.5094 | 274.3774 | 285.4014 | 391.9162 | 35.8272 | 62.7082 | 14.724 | 271 | 61.2957 | 0 | 464.658 | 0.17568
6633 | 1085.2043 | 3.8806 | 98.8687 | 138.3884 | 1.4924 | 18.0503 | 154.832 | 9.2827 | 19.241 | 80.4989 | 171.4739 | 38.7441 | 334.0124 | 332.4367 | 483.9956 | 41.2239 | 73.3112 | 15.7117 | 394 | 71.1972 | 0 | 521.217 | 0.2452
6634 | 1142.9722 | 9.5823 | 100.1542 | 142.6578 | -1.5072 | 20.8992 | 153.0933 | 8.4376 | 22.651 | 81.099 | 185.2441 | 42.1493 | 386.9427 | 358.7851 | 542.8394 | 42.8864 | 82.5311 | 16.9661 | 340 | 75.0459 | 0 | 554.1425 | 0.28166
6635 | 1182.2032 | 13.1739 | 104.4915 | 143.0027 | 1.4884 | 18.0558 | 148.9125 | 7.1316 | 21.712 | 79.0966 | 191.3492 | 41.6779 | 407.2675 | 376.6829 | 570.671 | 41.0651 | 89.9419 | 17.48 | 348 | 85.8566 | 0 | 580.9814 | 0.24986
6636 | 1177.1353 | 10.466 | 106.8029 | 146.3153 | 0.50358 | 18.9947 | 143.309 | 6.832 | 19.197 | 76.6766 | 195.9349 | 40.8595 | 421.7043 | 381.7093 | 585.8316 | 42.7657 | 91.1838 | 17.9162 | 329 | 74.0999 | 0 | 583.0059 | 0.27917
6637 | 1167.5052 | 7.0543 | 106.7833 | 138.9191 | 0.49458 | 19 | 144.4137 | 7.1052 | 15.025 | 76.9969 | 196.4352 | 42.752 | 416.713 | 375.31 | 575.8119 | 43.6422 | 87.9969 | 17.787 | 282 | 77.8061 | 0 | 578.0011 | 0.29984
6638 | 1152.1587 | 6.1308 | 106.7927 | 145.8071 | 1.4956 | 18.0503 | 155.7308 | 7.1513 | 19.415 | 83.0309 | 192.1675 | 42.733 | 415.9779 | 367.5358 | 557.511 | 42.1106 | 86.5823 | 17.8705 | 266 | 79.1988 | 0 | 576.3744 | 0.29857
6639 | 1123.7954 | 5.6344 | 106.3363 | 146.6859 | 2.4973 | 17.1003 | 163.7856 | 5.508 | 21.941 | 83.8397 | 190.4649 | 42.5733 | 412.309 | 351.6013 | 553.3814 | 39.5025 | 85.0668 | 18.0887 | 264 | 75.9832 | 0 | 562.2095 | 0.2746
6640 | 1079.2479 | 4.0554 | 100.4722 | 139.7155 | 5.497 | 14.2508 | 147.3866 | 3.9139 | 24.127 | 79.8356 | 191.7825 | 41.1632 | 407.8926 | 327.3716 | 525.7978 | 32.0271 | 82.9235 | 17.9599 | 248 | 71.0241 | 0 | 518.7602 | 0.20053
6641 | 1032.5596 | 3.3973 | 93.1646 | 129.1102 | 7.4929 | 12.3505 | 134.605 | 2.4691 | 23.786 | 71.4623 | 182.1545 | 34.0794 | 381.3707 | 277.0292 | 442.7101 | 15.4731 | 78.5309 | 17.647 | 232 | 58.659 | 0 | 429.4547 | 0.1015
6642 | 986.2409 | 4.1828 | 87.4276 | 115.9592 | 14.494 | 5.7018 | 110.445 | 1.7534 | 14.28 | 59.0522 | 153.655 | 26.1351 | 336.5444 | 214.6984 | 362.1669 | 9.3217 | 72.7039 | 15.4897 | 213 | 52.1506 | 0 | 355.3142 | 0
6643 | 949.59 | 4.7708 | 73.9439 | 110.8137 | 15.4985 | 4.7503 | 94.8907 | 1.7071 | 8.158 | 57.3264 | 127.1918 | 15.5703 | 288.2864 | 178.6616 | 312.1817 | 9.0321 | 68.0214 | 9.8789 | 195 | 49.3112 | 0 | 310.8687 | 0
6644 | 922.8386 | 4.1877 | 39.8273 | 107.4643 | 14.4964 | 5.7013 | 100.7031 | 1.7908 | 7.6 | 61.7916 | 118.4055 | 11.7817 | 258.9721 | 158.0726 | 268.7229 | 9.0773 | 63.0647 | 6.9136 | 193 | 45.2137 | 0 | 274.4836 | 0
6645 | 884.733 | 3.6689 | 25.1969 | 104.8233 | 15.5026 | 4.7487 | 102.0741 | 1.8679 | 7.878 | 52.0936 | 114.5819 | 11.6573 | 234.3475 | 134.6082 | 246.8132 | 9.0748 | 59.4657 | 6.0714 | 163 | 41.5444 | 0 | 251.4681 | 0
6646 | 855.8485 | 2.9643 | 23.4958 | 102.7139 | 14.4984 | 5.6997 | 96.3895 | 1.7762 | 7.591 | 36.477 | 103.4851 | 11.595 | 208.2819 | 119.2464 | 227.7775 | 8.9707 | 57.9552 | 5.4147 | 142 | 38.1605 | 0 | 239.036 | 0
6647 | 846.0439 | 1.7304 | 23.4763 | 100.6084 | 14.4982 | 5.7 | 85.8003 | 1.7301 | 7.002 | 27.9628 | 90.9376 | 11.7068 | 192.2929 | 116.098 | 225.3873 | 9.6089 | 56.839 | 4.7792 | 131 | 35.3429 | 0 | 231.0096 | 0
6648 | 844.5245 | 1.4308 | 23.675 | 98.95 | 13.4991 | 6.6497 | 82.0455 | 1.761 | 6.74 | 25.0782 | 86.518 | 11.7315 | 184.8696 | 115.9177 | 228.6777 | 9.9246 | 56.1633 | 4.4399 | 123 | 34.2197 | 0 | 227.4447 | 0
6649 | 839.1309 | 1.5965 | 23.598 | 98.3966 | 12.499 | 7.5997 | 81.3842 | 2.0085 | 6.787 | 24.3499 | 85.4039 | 11.7356 | 182.4935 | 114.4678 | 228.5384 | 9.9983 | 55.738 | 4.6665 | 119 | 34.1126 | 0 | 223.8464 | 0
6650 | 830.0902 | 1.5235 | 23.5971 | 96.1298 | 12.4998 | 7.6 | 81.4636 | 1.9117 | 6.883 | 24.478 | 83.7474 | 11.5729 | 185.3771 | 110.3488 | 229.6492 | 9.8852 | 55.6254 | 4.7847 | 120 | 33.4094 | 0 | 222.9788 | 0
6651 | 826.8549 | 1.3576 | 23.6524 | 95.0983 | 12.4995 | 7.6 | 72.5428 | 1.8087 | 6.819 | 26.031 | 82.4571 | 11.4998 | 184.3484 | 107.8774 | 232.0943 | 9.7977 | 55.5505 | 4.5074 | 113 | 33.0222 | 0 | 221.983 | 0
6652 | 829.6231 | 1.8301 | 23.6541 | 95.6015 | 14.4999 | 5.7005 | 71.2456 | 1.8243 | 6.822 | 32.6003 | 81.7019 | 11.5203 | 179.7814 | 103.6875 | 227.4069 | 10.0204 | 56.2837 | 3.7628 | 112 | 33.0661 | 0 | 233.4277 | 0
6653 | 837.8559 | 2.9517 | 34.5559 | 96.8391 | 14.4986 | 5.7 | 85.7314 | 1.8409 | 6.714 | 40.3142 | 81.6591 | 11.9134 | 179.1568 | 99.0973 | 225.2253 | 9.8389 | 58.6119 | 3.4845 | 115 | 33.4647 | 0 | 264.1175 | 0
6654 | 870.2825 | 6.1507 | 54.4496 | 99.8646 | 9.4995 | 10.4487 | 99.8403 | 2.1155 | 7.038 | 46.736 | 90.4798 | 17.2621 | 187.7465 | 126.0263 | 241.4503 | 13.02 | 60.3845 | 3.4949 | 188 | 41.2559 | 0 | 316.6845 | 0
6655 | 955.5181 | 13.6618 | 77.3183 | 106.5775 | 0.49413 | 18.9976 | 113.0682 | 3.5246 | 12.268 | 62.9774 | 117.4426 | 31.726 | 217.7495 | 191.1701 | 301.3563 | 28.6326 | 62.431 | 10.241 | 282 | 46.9053 | 0 | 376.9172 | 0
6656 | 1057.5226 | 18.3605 | 90.5759 | 123.3778 | 0.48881 | 19 | 136.8047 | 7.1816 | 15.707 | 84.7876 | 151.2603 | 40.2379 | 269.0042 | 256.3508 | 391.7639 | 35.1836 | 67.8595 | 14.9314 | 338 | 65.5223 | 0 | 438.4242 | 0.21838
6657 | 1140.9539 | 16.0543 | 94.2929 | 131.4089 | -0.50761 | 19.9497 | 156.3581 | 8.186 | 16.047 | 97.2276 | 175.8305 | 41.2014 | 339.3232 | 299.2282 | 468.3765 | 39.4237 | 73.6502 | 16.4286 | 356 | 73.292 | 0 | 513.2543 | 0.27296
6658 | 1188.5062 | 13.9829 | 96.5809 | 136.4651 | -0.50447 | 19.95 | 168.3068 | 7.9777 | 19.768 | 98.6914 | 185.7357 | 42.9227 | 395.9186 | 327.6665 | 528.4103 | 40.6663 | 77.9843 | 17.6082 | 360 | 78.0178 | 0 | 561.2145 | 0.2818
6659 | 1215.7004 | 16.2436 | 99.8788 | 142.7184 | 0.49398 | 19.0003 | 155.7341 | 8.24 | 25.033 | 98.9224 | 188.2166 | 42.8895 | 418.4347 | 350.8515 | 564.4266 | 41.032 | 81.2212 | 18.5287 | 317 | 89.5229 | 0 | 569.2666 | 0.24763
6660 | 1203.2948 | 9.4142 | 100.0187 | 143.0103 | -0.50337 | 19.9497 | 140.7118 | 9.5239 | 25.834 | 99.2046 | 188.8864 | 43.1976 | 427.4232 | 356.3337 | 568.0016 | 41.4122 | 81.6963 | 18.8987 | 353 | 84.8221 | 0 | 565.6005 | 0.27868
6661 | 1193.846 | 4.2301 | 101.1256 | 147.4324 | -0.50214 | 19.95 | 148.8349 | 6.6938 | 22.255 | 98.9054 | 187.9655 | 43.9423 | 417.9959 | 356.5663 | 547.7112 | 42.9604 | 82.7953 | 18.9742 | 293 | 83.2516 | 0 | 568.9702 | 0.28042
6662 | 1198.5616 | 3.892 | 103.9436 | 147.4661 | -0.50323 | 19.95 | 152.4298 | 5.5146 | 23.737 | 98.5977 | 188.6267 | 43.8507 | 420.672 | 361.4969 | 536.4724 | 43.03 | 84.7052 | 19.0703 | 297 | 83.8805 | 0 | 577.5229 | 0.27309
6663 | 1156.7191 | 4.4577 | 99.7989 | 140.3638 | 1.4943 | 18.0505 | 158.4872 | 5.9944 | 24.004 | 92.6588 | 189.4324 | 42.2071 | 420.9788 | 351.7723 | 534.4353 | 41.4809 | 83.8955 | 18.8773 | 279 | 77.5178 | 0 | 580.6175 | 0.20623
6664 | 1107.2764 | 3.4371 | 96.2387 | 131.5273 | 8.4892 | 11.4018 | 143.547 | 6.1206 | 22.904 | 86.7237 | 189.2388 | 38.5433 | 412.0211 | 330.6994 | 500.8321 | 32.6771 | 82.2998 | 18.6861 | 255 | 71.7326 | 0 | 541.6411 | 0.14452
6665 | 1024.1666 | 3.3051 | 93.7306 | 122.4117 | 14.4954 | 5.7016 | 121.7715 | 4.0511 | 21.448 | 77.0173 | 179.8197 | 32.4703 | 399.2327 | 283.3303 | 421.9941 | 16.1042 | 78.1527 | 18.2141 | 241 | 63.4099 | 0 | 443.6165 | 0.065899
6666 | 959.0566 | 3.9472 | 90.305 | 112.3106 | 14.4988 | 5.7 | 108.4893 | 3.3062 | 20.341 | 63.8947 | 149.9425 | 28.1488 | 362.3847 | 217.302 | 347.8017 | 9.9542 | 70.9218 | 15.1948 | 229 | 52.2785 | 0 | 360.0009 | 0
6667 | 929.8941 | 3.761 | 78.7103 | 105.2389 | 15.4969 | 4.7503 | 91.9986 | 3.5776 | 15.446 | 61.2786 | 119.7314 | 19.9156 | 310.7697 | 178.6923 | 307.1329 | 10.1841 | 65.5994 | 9.531 | 190 | 48.388 | 0 | 311.0655 | 0
6668 | 885.4093 | 4.2212 | 39.9291 | 100.5851 | 14.5024 | 5.6997 | 84.7652 | 4.0913 | 11.0472 | 62.2078 | 108.6382 | 11.1471 | 267.42 | 165.1055 | 279.5786 | 10.3438 | 61.6725 | 6.647 | 185 | 42.2569 | 0 | 280.8812 | 0
6669 | 858.4567 | 8.6984 | 24.8148 | 97.7212 | 15.501 | 4.7503 | 81.9253 | 4.1079 | 9.0498 | 52.3685 | 102.5965 | 8.5639 | 231.0779 | 152.5033 | 250.9101 | 10.2392 | 57.4154 | 5.5865 | 166 | 39.4541 | 0 | 262.321 | 0
6670 | 832.6864 | 7.1283 | 24.1926 | 95.0603 | 12.4968 | 7.5992 | 81.0067 | 4.1255 | 7.866 | 38.4499 | 91.3366 | 8.4447 | 196.8673 | 142.2716 | 235.7112 | 10.766 | 54.5403 | 5.0346 | 148 | 36.6385 | 0 | 249.3963 | 0
6671 | 804.5073 | 2.9349 | 24.3705 | 94.1779 | 12.5 | 7.6 | 80.3568 | 4.2847 | 7.011 | 31.4536 | 81.3555 | 8.4339 | 183.4579 | 131.5391 | 228.0152 | 11.0046 | 53.4385 | 4.5961 | 128 | 34.5969 | 0 | 247.6442 | 0
6672 | 799.0827 | 1.7238 | 24.2643 | 94.8704 | 12.5056 | 7.6 | 81.0785 | 4.4983 | 6.934 | 28.62 | 78.2661 | 8.4805 | 175.9523 | 118.2181 | 226.015 | 11.0636 | 53.3991 | 4.3836 | 124 | 35.1322 | 0 | 249.8163 | 0
6673 | 798.8948 | 1.4556 | 24.4437 | 94.6352 | 12.5028 | 7.6 | 80.9674 | 4.4216 | 6.818 | 27.1144 | 78.4746 | 8.5114 | 172.238 | 110.0307 | 220.6506 | 11.1806 | 53.545 | 3.5668 | 121 | 33.3901 | 0 | 253.3347 | 0
6674 | 789.4686 | 1.6196 | 24.2774 | 94.165 | 12.5025 | 7.6 | 76.8882 | 4.4057 | 6.726 | 27.0518 | 79.1157 | 8.5142 | 179.265 | 107.1412 | 222.4634 | 11.214 | 53.5202 | 3.1882 | 118 | 33.6556 | 0 | 258.3691 | 0
6675 | 793.8273 | 1.5462 | 24.2735 | 93.9182 | 13.5009 | 6.6503 | 68.8133 | 4.5107 | 6.713 | 28.4873 | 79.2521 | 8.5019 | 181.4092 | 106.259 | 225.5499 | 11.1292 | 53.5604 | 3.1615 | 115 | 32.8858 | 0 | 259.2026 | 0
6676 | 794.9166 | 1.8395 | 24.3814 | 93.9679 | 14.4983 | 5.7003 | 75.6783 | 4.604 | 6.584 | 34.8193 | 78.6625 | 8.4614 | 172.7884 | 105.6223 | 217.4089 | 11.0278 | 54.3395 | 3.1408 | 118 | 34.1773 | 0 | 265.6631 | 0
6677 | 806.849 | 2.8222 | 33.143 | 93.9997 | 14.4969 | 5.7 | 77.92 | 4.9071 | 6.6 | 41.1496 | 78.5401 | 10.9374 | 171.8129 | 107.0162 | 222.6705 | 11.0771 | 56.5041 | 3.1569 | 114 | 32.78 | 0 | 297.0034 | 0
6678 | 839.6989 | 4.6048 | 49.8012 | 98.5479 | 10.4954 | 9.4989 | 79.7144 | 5.1725 | 7.582 | 45.3595 | 88.6214 | 22.3522 | 180.1053 | 134.3821 | 245.7964 | 13.71 | 56.4899 | 3.177 | 182 | 38.7977 | 0 | 340.9374 | 0
6679 | 919.6923 | 5.0078 | 73.8218 | 101.9576 | 0.49313 | 18.9974 | 109.489 | 4.9245 | 10.314 | 62.9352 | 115.5491 | 31.9664 | 213.0908 | 195.3084 | 301.3371 | 28.8929 | 57.8198 | 8.8479 | 251 | 46.4759 | 0 | 392.7371 | 0
6680 | 1021.9861 | 4.2203 | 89.4017 | 116.3439 | -1.5165 | 20.9053 | 135.6771 | 5.675 | 17.491 | 86.8916 | 145.2458 | 39.6065 | 283.1465 | 258.6611 | 386.4311 | 36.5971 | 65.1459 | 14.6499 | 306 | 65.2776 | 0 | 465.2001 | 0.21345
6681 | 1092.3038 | 3.7401 | 98.0034 | 127.9727 | 1.4926 | 18.045 | 142.7032 | 5.6754 | 24.221 | 95.3885 | 164.8523 | 42.1711 | 349.2909 | 302.8698 | 485.2653 | 40.6348 | 74.3282 | 16.5107 | 353 | 66.9544 | 0 | 540.5456 | 0.27279
6682 | 1146.2749 | 3.8058 | 97.9698 | 133.5415 | -1.5106 | 20.8992 | 155.2865 | 7.7408 | 25.641 | 98.9517 | 178.3527 | 43.4249 | 390.9533 | 325.4078 | 543.2371 | 40.4037 | 83.393 | 16.8332 | 359 | 74.2106 | 0 | 584.4539 | 0.28145
6683 | 1179.4481 | 3.7195 | 99.4478 | 133.5742 | -1.5126 | 20.9 | 159.8598 | 8.1845 | 24.366 | 106.9343 | 189.1716 | 40.6689 | 400.8901 | 340.086 | 568.1353 | 39.3191 | 88.5302 | 17.0597 | 333 | 82.4583 | 0 | 588.4713 | 0.24755
6684 | 1158.0656 | 4.0031 | 101.5847 | 132.9705 | -1.5136 | 20.9 | 149.3753 | 7.9554 | 21.381 | 106.022 | 187.0828 | 40.2694 | 411.6433 | 347.5229 | 575.467 | 40.3296 | 87.3036 | 17.2504 | 400 | 73.4036 | 0 | 588.0868 | 0.279
6685 | 1153.9446 | 3.7002 | 101.9932 | 137.6774 | 0.48743 | 19.0005 | 152.8625 | 6.1377 | 19.113 | 101.1537 | 180.4393 | 42.6984 | 409.9921 | 346.7095 | 564.5789 | 41.2862 | 85.9798 | 18.2552 | 307 | 74.7441 | 0 | 619.0734 | 0.2993
6686 | 1164.8109 | 3.5771 | 100.7483 | 138.5731 | -0.5038 | 19.9497 | 166.6536 | 6.3371 | 21.561 | 99.6246 | 182.6839 | 41.4347 | 410.4769 | 348.1148 | 560.6694 | 41.3216 | 86.8769 | 18.7007 | 274 | 75.1082 | 0 | 648.7424 | 0.29854
6687 | 1137.1993 | 3.7857 | 100.9154 | 137.5933 | 2.4978 | 17.1008 | 156.3526 | 5.9559 | 20.814 | 92.5492 | 184.6869 | 39.1491 | 461.7735 | 344.0019 | 566.0095 | 38.0845 | 87.2099 | 18.618 | 271 | 74.4168 | 0 | 646.846 | 0.27579
6688 | 1096.8006 | 3.7594 | 94.4652 | 131.2803 | 2.4993 | 17.1 | 148.0474 | 4.5454 | 15.183 | 83.2146 | 182.4943 | 37.9319 | 450.6313 | 327.3871 | 535.571 | 30.6378 | 85.971 | 18.4675 | 230 | 72.7134 | 0 | 591.4646 | 0.20511
6689 | 1041.9814 | 3.8315 | 88.4403 | 116.9582 | 11.4993 | 8.5524 | 136.4593 | 4.1697 | 14.498 | 69.5881 | 169.983 | 32.4993 | 401.1395 | 278.9727 | 464.9995 | 15.9979 | 80.0755 | 18.0256 | 220 | 63.2907 | 0 | 492.4137 | 0.093577
6690 | 989.8033 | 4.2362 | 85.1729 | 104.6299 | 13.4976 | 6.6505 | 121.5811 | 4.2844 | 18.811 | 55.3758 | 140.2722 | 25.724 | 345.9487 | 209.8933 | 382.8825 | 10.3289 | 73.2841 | 15.6866 | 217 | 56.023 | 0 | 430.1433 | 0
6691 | 931.4941 | 4.1738 | 76.8183 | 100.4567 | 15.4991 | 4.7505 | 109.7571 | 5.1997 | 19.696 | 57.2837 | 113.6905 | 14.5201 | 297.3725 | 167.0322 | 330.8382 | 9.4824 | 68.3046 | 10.4283 | 199 | 54.2057 | 0 | 379.3521 | 0
6692 | 887.0961 | 3.8269 | 40.5063 | 96.2826 | 14.5035 | 5.6997 | 99.1587 | 4.7952 | 13.335 | 61.6402 | 104.0615 | 10.3118 | 260.3068 | 150.0842 | 298.1163 | 9.1349 | 62.5869 | 7.0256 | 179 | 46.9853 | 0 | 319.1198 | 0
6693 | 859.9816 | 3.5394 | 26.1088 | 93.9221 | 15.4984 | 4.7503 | 88.3413 | 3.5805 | 14.044 | 50.348 | 98.2849 | 10.9244 | 232.6286 | 132.9966 | 256.8387 | 9.1668 | 57.8799 | 5.5061 | 165 | 41.6368 | 0 | 286.3369 | 0
6694 | 827.3083 | 2.8931 | 25.1464 | 93.5717 | 14.4976 | 5.6997 | 85.0352 | 3.3822 | 17.595 | 35.2299 | 86.5566 | 10.2576 | 208.7766 | 116.7231 | 237.908 | 9.2238 | 55.5589 | 4.7672 | 150 | 40.5349 | 0 | 269.672 | 0
6695 | 803.1163 | 2.0189 | 24.9247 | 91.5934 | 15.4997 | 4.7503 | 84.2392 | 3.5802 | 12.903 | 28.6809 | 75.0969 | 9.775 | 190.8396 | 109.2661 | 234.1607 | 9.1663 | 55.0111 | 4.3064 | 136 | 35.3366 | 0 | 261.8099 | 0
6696 | 801.2137 | 1.5199 | 24.8854 | 92.0299 | 14.5005 | 5.6997 | 83.3095 | 3.9613 | 7.686 | 27.4595 | 71.7989 | 9.7245 | 180.1145 | 110.7766 | 233.209 | 9.2237 | 54.8715 | 4.1484 | 125 | 32.483 | 0 | 256.5586 | 0
6697 | 788.7858 | 1.5531 | 24.8758 | 91.2677 | 13.499 | 6.6497 | 83.9114 | 4.1474 | 6.375 | 27.4084 | 71.8635 | 10.0394 | 174.7017 | 106.7176 | 239.4214 | 9.6057 | 54.7611 | 3.8143 | 115 | 29.7316 | 0 | 256.2591 | 0
6698 | 780.3852 | 1.7323 | 24.9098 | 92.4091 | 14.4986 | 5.7003 | 84.0943 | 4.2499 | 6.505 | 27.501 | 71.3156 | 9.6266 | 173.9162 | 95.4111 | 238.926 | 9.8711 | 54.854 | 3.9211 | 115 | 30.803 | 0 | 256.8893 | 0
6699 | 774.3943 | 1.6847 | 24.8674 | 93.0942 | 14.4997 | 5.7 | 84.132 | 4.5512 | 6.538 | 29.1968 | 70.8583 | 9.6047 | 174.4878 | 90.0838 | 231.3518 | 9.888 | 54.8973 | 3.6253 | 108 | 32.2512 | 0 | 255.3986 | 0
6700 | 788.065 | 2.2615 | 24.3106 | 93.3621 | 13.5039 | 6.6497 | 77.9906 | 4.5219 | 6.541 | 35.9173 | 70.9313 | 9.3462 | 175.6762 | 88.8023 | 219.6451 | 9.9629 | 55.6793 | 3.44 | 111 | 31.3326 | 0 | 266.4691 | 0
6701 | 797.7224 | 3.227 | 37.0968 | 92.9339 | 12.4999 | 7.5997 | 79.3839 | 4.394 | 6.669 | 43.9876 | 71.5474 | 13.8017 | 181.1147 | 89.6942 | 218.7287 | 9.969 | 57.9617 | 3.4023 | 113 | 31.6123 | 0 | 303.168 | 0
6702 | 825.8277 | 4.6562 | 54.9583 | 97.3844 | 5.4999 | 14.2482 | 100.2285 | 4.3903 | 7.084 | 50.9168 | 83.3701 | 19.0713 | 190.9417 | 117.5388 | 241.8253 | 12.6822 | 58.0423 | 3.3688 | 194 | 40.3825 | 0 | 355.511 | 0
6703 | 922.5111 | 4.9198 | 72.7819 | 102.094 | -0.50545 | 19.9484 | 126.4097 | 5.0866 | 12.735 | 65.3334 | 112.2968 | 25.6364 | 219.2212 | 184.5373 | 295.7473 | 27.8377 | 58.216 | 9.769 | 290 | 45.1976 | 0 | 416.7923 | 0
6704 | 1021.8885 | 4.1751 | 85.191 | 113.5828 | -1.5074 | 20.8997 | 135.9913 | 6.9138 | 16.14 | 81.1324 | 141.2749 | 28.5114 | 277.2268 | 254.1732 | 374.8725 | 35.0939 | 64.08 | 15.6905 | 303 | 61.4494 | 0 | 488.6707 | 0.19804
6705 | 1106.6244 | 3.9121 | 93.0734 | 126.5129 | -0.50389 | 19.9503 | 152.7275 | 6.4188 | 19.012 | 90.7276 | 161.081 | 32.1665 | 339.3043 | 299.6717 | 454.8844 | 40.5588 | 73.229 | 16.6007 | 399 | 63.9561 | 0 | 574.809 | 0.27481
6706 | 1153.4521 | 3.9173 | 94.6282 | 133.6362 | -1.5058 | 20.8997 | 162.1637 | 5.8665 | 23.298 | 97.8726 | 173.4288 | 38.8884 | 384.3506 | 319.2796 | 516.7738 | 42.5308 | 82.3644 | 16.863 | 363 | 65.7419 | 0 | 634.5729 | 0.28587
6707 | 1150.0167 | 3.898 | 95.2802 | 130.5142 | -2.5074 | 21.8497 | 161.6542 | 5.6025 | 27.567 | 104.6389 | 178.8157 | 40.6936 | 397.2876 | 328.3697 | 548.6305 | 42.3035 | 87.9983 | 17.5129 | 324 | 78.815 | 0 | 648.0862 | 0.25282
6708 | 1133.1069 | 4.1198 | 95.3761 | 132.9484 | 0.4945 | 19.0008 | 155.4402 | 5.8913 | 24.8479 | 107.794 | 182.0127 | 40.4838 | 402.0563 | 337.0337 | 550.9624 | 41.2546 | 87.7918 | 18.1168 | 333 | 74.1449 | 0 | 649.4082 | 0.28117
6709 | 1144.7762 | 7.9316 | 98.0191 | 136.3366 | -0.50356 | 19.9497 | 153.5395 | 4.623 | 20.7301 | 105.2062 | 189.0453 | 41.0335 | 393.5311 | 347.0744 | 555.7653 | 43.4102 | 85.9631 | 18.1691 | 290 | 76.604 | 0 | 636.2691 | 0.30451
6710 | 1165.409 | 9.7075 | 100.9077 | 139.8896 | 8.4033 | 19.95 | 166.8306 | 5.2044 | 24.691 | 102.1535 | 198.7307 | 41.0558 | 408.4855 | 358.2915 | 553.2134 | 43.9797 | 84.9643 | 18.2024 | 271 | 75.2448 | 0 | 627.9616 | 0.29779
6711 | 1142.2481 | 6.6265 | 98.1004 | 134.514 | 12.4664 | 16.1511 | 168.6572 | 4.5079 | 25.344 | 96.868 | 204.1438 | 40.8452 | 412.3341 | 354.3003 | 537.2405 | 40.3975 | 84.3173 | 18.2195 | 277 | 73.6581 | 0 | 637.1207 | 0.26367
6712 | 1114.9523 | 3.9166 | 92.3904 | 126.9483 | 11.5739 | 10.4516 | 151.3927 | 4.9561 | 22.282 | 90.5852 | 201.4133 | 39.138 | 405.7433 | 328.4282 | 514.0076 | 32.4755 | 83.6573 | 18.6056 | 252 | 68.0039 | 0 | 602.9632 | 0.17022
6713 | 1049.4873 | 3.1553 | 88.7923 | 113.505 | 12.4966 | 7.6008 | 129.9239 | 4.2178 | 21.698 | 84.0736 | 187.7737 | 36.93 | 382.7002 | 275.0697 | 465.0347 | 15.8864 | 79.4625 | 17.8932 | 224 | 56.5241 | 0 | 490.7227 | 0.081809
6714 | 979.278 | 3.8869 | 82.3332 | 101.6067 | 13.4953 | 6.6503 | 125.318 | 2.7136 | 20.679 | 75.5561 | 157.6386 | 31.207 | 336.7582 | 211.4174 | 413.2963 | 10.1011 | 72.8517 | 14.2476 | 218 | 48.3538 | 0 | 387.7524 | 0
6715 | 949.0315 | 4.5872 | 70.9676 | 98.0027 | 14.497 | 5.7003 | 104.8813 | 3.3875 | 17.248 | 75.0614 | 126.8202 | 18.2792 | 288.2063 | 171.2279 | 372.3071 | 9.498 | 67.6366 | 8.5374 | 178 | 44.2223 | 0 | 332.8709 | 0
6716 | 899.828 | 4.444 | 34.5505 | 93.9179 | 15.4986 | 4.7503 | 91.8277 | 3.7323 | 13.627 | 78.5461 | 111.4481 | 13.3817 | 254.6057 | 147.3118 | 311.0572 | 9.1704 | 63.8964 | 6.4896 | 173 | 41.2886 | 0 | 291.3547 | 0
6717 | 866.2597 | 3.9621 | 21.8432 | 90.7302 | 14.4938 | 5.6997 | 95.9746 | 3.7355 | 12.099 | 68.9471 | 100.7576 | 13.5298 | 234.8266 | 130.9547 | 255.0811 | 9.1492 | 59.558 | 6.061 | 166 | 39.147 | 0 | 269.9759 | 0
6718 | 831.5729 | 3.1671 | 21.586 | 88.9475 | 14.4944 | 5.7 | 97.0111 | 3.8296 | 10.067 | 51.7347 | 87.4761 | 13.5207 | 209.6076 | 121.0817 | 239.1785 | 9.1425 | 55.7305 | 5.3875 | 149 | 36.0442 | 0 | 263.8372 | 0
6719 | 809.1346 | 1.9164 | 21.5462 | 90.3722 | 15.502 | 4.7503 | 87.6219 | 3.1782 | 7.533 | 37.6575 | 77.5124 | 13.6704 | 187.7714 | 116.5017 | 239.6224 | 9.1039 | 54.6792 | 4.7287 | 128 | 35.5545 | 0 | 260.1287 | 0
6720 | 799.5378 | 1.4148 | 21.3242 | 89.4085 | 14.4988 | 5.6997 | 82.9969 | 3.0669 | 6.927 | 28.8711 | 74.8695 | 13.2631 | 177.9707 | 115.3943 | 243.0178 | 9.286 | 54.7023 | 4.7625 | 129 | 33.9404 | 0 | 254.5602 | 0
6721 | 786.2925 | 1.3977 | 21.4756 | 91.3236 | 14.4992 | 5.7 | 82.2834 | 3.7339 | 7.032 | 25.9618 | 75.1996 | 13.0636 | 174.7481 | 107.9128 | 246.9744 | 9.139 | 54.5653 | 4.7562 | 126 | 30.9469 | 0 | 250.5065 | 0
6722 | 771.2942 | 1.44 | 21.6001 | 92.0999 | 15.4978 | 4.7503 | 82.1263 | 4.0324 | 6.966 | 25.5462 | 75.4185 | 13.0702 | 174.907 | 100.7279 | 249.594 | 9.5719 | 54.5652 | 4.6195 | 119 | 30.3862 | 0 | 252.1725 | 0
6723 | 760.2033 | 1.6382 | 21.6161 | 91.5711 | 14.4958 | 5.6997 | 82.23 | 4.2042 | 6.888 | 27.008 | 74.6945 | 13.0772 | 174.0271 | 95.5907 | 248.6049 | 9.8204 | 54.558 | 4.5777 | 118 | 30.3159 | 0 | 254.1764 | 0
6724 | 780.3434 | 2.0095 | 21.6574 | 92.3188 | 15.4971 | 4.7503 | 82.1847 | 4.2838 | 6.744 | 33.5063 | 74.0569 | 13.0519 | 170.3448 | 90.7147 | 240.5606 | 9.8695 | 55.2415 | 4.5353 | 115 | 30.4872 | 0 | 264.4806 | 0
6725 | 788.2133 | 5.8158 | 37.1629 | 93.0442 | 13.4936 | 6.6513 | 88.0677 | 4.1522 | 6.676 | 39.3819 | 74.5501 | 13.9615 | 173.1998 | 91.1708 | 233.3368 | 9.8053 | 57.4583 | 3.7269 | 125 | 30.6028 | 0 | 294.0163 | 0
6726 | 831.3518 | 5.9131 | 59.4927 | 98.7769 | 4.4939 | 15.2 | 108.6994 | 4.351 | 6.817 | 44.2315 | 87.8414 | 18.2638 | 181.8172 | 120.1033 | 241.3776 | 11.8978 | 58.7369 | 4.3589 | 195 | 36.7743 | 0 | 336.2551 | 0
6727 | 889.4129 | 9.9716 | 76.2652 | 100.4503 | 0.49828 | 18.9947 | 127.3767 | 4.8711 | 11.234 | 56.0243 | 122.2906 | 28.2967 | 214.282 | 187.9695 | 298.5979 | 26.6367 | 59.5706 | 11.8305 | 235 | 45.3675 | 0 | 378.3281 | 0
6728 | 969.4938 | 11.3563 | 87.9638 | 116.1206 | -0.51146 | 19.9497 | 142.531 | 5.24 | 12.078 | 64.5351 | 154.9548 | 30.5376 | 280.3419 | 253.2899 | 408.4125 | 36.2217 | 66.2086 | 15.5451 | 315 | 59.8334 | 0 | 436.0056 | 0.11911
6729 | 1051.9275 | 7.0564 | 92.6277 | 129.4171 | -0.5094 | 19.95 | 157.6293 | 5.4094 | 7.615 | 64.1494 | 169.3319 | 31.7092 | 342.7339 | 285.8065 | 502.808 | 40.7123 | 75.9458 | 16.514 | 330 | 66.4614 | 0 | 530.845 | 0.23654
6730 | 1095.2943 | 4.4418 | 93.3878 | 133.8624 | 1.4929 | 18.0505 | 167.9884 | 5.4898 | 8.753 | 61.0612 | 176.2798 | 34.9208 | 389.5002 | 300.7268 | 552.0257 | 42.469 | 81.9775 | 17.6731 | 335 | 68.0522 | 0 | 589.7272 | 0.23638
6731 | 1109.6573 | 3.9339 | 93.8383 | 136.0551 | 2.4955 | 17.1003 | 165.6974 | 5.9524 | 14.068 | 62.4779 | 181.7578 | 34.9328 | 399.7917 | 311.0521 | 573.9705 | 42.2399 | 85.0448 | 17.7901 | 285 | 69.0583 | 0 | 590.2754 | 0.23562
6732 | 1094.9074 | 3.9875 | 95.3681 | 134.0483 | 0.49508 | 18.9995 | 154.5645 | 5.0806 | 13.727 | 70.8204 | 184.2497 | 34.7678 | 400.9007 | 314.838 | 579.2668 | 42.5905 | 85.7327 | 17.8281 | 345 | 67.7282 | 0 | 580.888 | 0.26155
6733 | 1116.8636 | 3.6787 | 97.5013 | 134.719 | 4.4955 | 15.2011 | 160.6484 | 6.0437 | 8.742 | 70.0204 | 187.8165 | 38.1581 | 396.425 | 317.2499 | 579.6256 | 41.8676 | 85.8452 | 18.3059 | 335 | 66.7895 | 0 | 571.1259 | 0.28203
6734 | 1116.4746 | 3.6841 | 98.2932 | 137.1044 | 5.4946 | 14.2503 | 166.6394 | 5.5531 | 6.92 | 61.0095 | 195.1758 | 38.931 | 403.9344 | 319.9843 | 577.1833 | 41.7786 | 87.9075 | 18.9832 | 295 | 65.7736 | 0 | 555.1068 | 0.28676
6735 | 1084.9045 | 4.7385 | 95.5033 | 131.1104 | 4.4945 | 15.1997 | 165.045 | 4.8505 | 10.061 | 59.3933 | 200.3183 | 38.2173 | 402.0803 | 312.0979 | 551.3046 | 40.0764 | 89.3839 | 18.8663 | 281 | 63.5229 | 0 | 531.5169 | 0.18324
6736 | 1037.0179 | 3.5742 | 88.7901 | 126.9379 | 10.4923 | 9.5016 | 153.6513 | 4.1138 | 10.587 | 60.1077 | 198.8482 | 35.8654 | 388.1634 | 290.3389 | 497.8503 | 29.6234 | 87.88 | 18.2228 | 258 | 61.0769 | 0 | 485.1878 | 0.056683
6737 | 971.5097 | 3.0748 | 73.9377 | 121.4951 | 13.4912 | 6.6508 | 129.1811 | 3.0176 | 10.517 | 54.5337 | 186.098 | 34.506 | 366.5133 | 245.4034 | 418.3028 | 18.7896 | 82.599 | 17.726 | 235 | 53.1122 | 0 | 399.3312 | 0.010645
6738 | 929.0371 | 3.9166 | 35.0521 | 105.246 | 13.4953 | 6.65 | 111.8684 | 3.4194 | 9.408 | 50.814 | 154.3112 | 28.1397 | 316.2336 | 195.8178 | 347.4011 | 11.6452 | 73.5998 | 15.0418 | 225 | 47.195 | 0 | 327.3362 | 0
6739 | 896.2608 | 3.8497 | 22.2965 | 96.1607 | 12.495 | 7.5997 | 91.4576 | 3.5695 | 7.529 | 59.7688 | 117.2586 | 16.8349 | 267.2749 | 167.9985 | 303.8247 | 9.2403 | 63.5153 | 9.3457 | 195 | 42.1141 | 0 | 293.2001 | 0
6740 | 853.96 | 3.5456 | 22.0698 | 93.8594 | 15.491 | 4.7508 | 88.9694 | 3.3437 | 7.65 | 66.3722 | 93.0625 | 13.0158 | 231.3949 | 150.6721 | 273.5832 | 8.7903 | 57.1277 | 6.4588 | 189 | 40.613 | 0 | 274.8834 | 0
6741 | 826.744 | 3.2371 | 22.0427 | 92.5563 | 14.4941 | 5.6997 | 89.6004 | 2.4594 | 7.733 | 55.8464 | 82.4502 | 13.0418 | 205.6231 | 137.901 | 256.2289 | 8.817 | 54.7568 | 5.3127 | 182 | 36.4741 | 0 | 266.6453 | 0
6742 | 813.1006 | 2.8662 | 22.1091 | 92.9002 | 15.493 | 4.7503 | 87.5241 | 3.0807 | 7.409 | 43.9362 | 78.9005 | 12.8434 | 183.6724 | 127.8152 | 253.2689 | 8.7078 | 53.6912 | 5.6962 | 172 | 36.3163 | 0 | 261.9462 | 0
6743 | 792.463 | 2.1066 | 22.1311 | 92.9292 | 15.4948 | 4.75 | 86.1249 | 3.7496 | 6.876 | 40.5158 | 76.4511 | 13.0168 | 172.4353 | 112.3802 | 253.3462 | 8.8032 | 53.5675 | 5.7424 | 169 | 33.9836 | 0 | 251.6088 | 0
6744 | 783.4685 | 1.8035 | 22.5932 | 90.879 | 14.4996 | 5.6997 | 86.8997 | 3.9377 | 6.501 | 39.1195 | 75.8529 | 13.0514 | 170.8728 | 98.7799 | 247.109 | 8.9007 | 54.1847 | 5.2312 | 157 | 35.0127 | 0 | 245.6475 | 0
6745 | 784.3549 | 1.6628 | 22.5214 | 91.288 | 14.4999 | 5.7 | 87.3406 | 3.8542 | 6.525 | 38.32 | 77.0003 | 13.058 | 175.8111 | 91.7397 | 243.5638 | 8.8909 | 54.632 | 5.0511 | 148 | 34.7069 | 0 | 247.7644 | 0
6746 | 782.5106 | 1.4932 | 22.3418 | 92.252 | 14.5045 | 5.7 | 86.4692 | 3.3881 | 6.689 | 37.3091 | 76.5891 | 13.0965 | 176.1362 | 87.8296 | 253.6847 | 8.859 | 54.5205 | 5.1632 | 150 | 32.5402 | 0 | 245.7397 | 0
6747 | 773.8877 | 1.3792 | 22.3469 | 91.6804 | 15.4997 | 4.7503 | 86.1162 | 2.694 | 6.817 | 36.7998 | 74.7784 | 13.2181 | 173.4325 | 87.2414 | 259.9741 | 8.7357 | 54.3278 | 5.343 | 142 | 32.9332 | 0 | 247.3523 | 0
6748 | 785.8606 | 1.7687 | 22.4933 | 93.8186 | 14.499 | 5.6997 | 85.8249 | 3.3057 | 6.815 | 41.5943 | 74.1173 | 13.0045 | 170.2463 | 87.2329 | 246.0233 | 8.8342 | 54.9693 | 4.7256 | 138 | 32.753 | 0 | 264.6522 | 0
6749 | 784.2903 | 2.7166 | 22.3488 | 95.4617 | 15.4999 | 4.7503 | 85.4884 | 4.0029 | 6.765 | 45.7135 | 74.149 | 12.8426 | 167.8524 | 86.0781 | 235.674 | 8.8554 | 57.2002 | 4.0476 | 133 | 31.2455 | 0 | 276.8247 | 0
6750 | 800.5085 | 3.5691 | 39.5756 | 94.1322 | 12.4983 | 7.5992 | 85.8171 | 3.9891 | 6.701 | 40.6671 | 74.3476 | 12.8463 | 164.1374 | 85.42 | 241.9351 | 8.7254 | 57.0029 | 3.7125 | 127 | 33.9011 | 0 | 275.217 | 0
6751 | 813.3551 | 3.7568 | 48.5703 | 94.4018 | 12.4981 | 7.6 | 88.2115 | 3.6701 | 6.764 | 31.9169 | 75.8751 | 13.3441 | 165.4817 | 84.7487 | 245.9338 | 11.7063 | 54.1278 | 3.6706 | 123 | 41.7086 | 0 | 267.1316 | 0
6752 | 831.9628 | 2.0612 | 54.7341 | 93.7285 | 12.4957 | 7.6 | 94.5916 | 3.2645 | 6.464 | 32.4464 | 94.5459 | 18.5403 | 178.7338 | 87.5371 | 236.9938 | 12.4247 | 52.552 | 4.5669 | 121 | 48.5958 | 0 | 248.6501 | 0.054662
6753 | 849.2087 | 1.1922 | 64.8992 | 95.146 | 12.494 | 7.6 | 98.161 | 2.2866 | 5.991 | 41.2043 | 127.179 | 19.8195 | 193.917 | 93.9226 | 223.8581 | 11.7665 | 52.4328 | 7.1529 | 128 | 49.3746 | 0 | 240.4512 | 0.13808
6754 | 856.0436 | 1.4768 | 72.3196 | 97.01 | 13.492 | 6.6503 | 97.963 | 3.6116 | 5.92 | 49.2804 | 142.7383 | 19.5665 | 207.6836 | 104.0442 | 224.6095 | 11.0904 | 52.7292 | 12.4576 | 138 | 50.9142 | 0 | 242.7587 | 0.13993
6755 | 876.9575 | 1.5888 | 72.2471 | 95.7706 | 14.4911 | 5.7003 | 91.3145 | 4.701 | 5.95 | 53.4646 | 127.6791 | 19.5935 | 219.5167 | 116.0455 | 236.063 | 10.7324 | 53.1227 | 14.5469 | 163 | 52.8791 | 0 | 244.8532 | 0.12907
6756 | 871.0859 | 2.2753 | 72.1809 | 95.5512 | 14.4946 | 5.7 | 89.749 | 4.6255 | 6.048 | 53.7738 | 104.0461 | 22.61 | 226.3459 | 126.579 | 248.3255 | 11.2112 | 53.8065 | 14.4176 | 172 | 52.3336 | 0 | 248.3597 | 0.12654
6757 | 859.3011 | 1.7483 | 66.6086 | 96.9762 | 14.4917 | 5.7 | 97.6186 | 6.0453 | 5.999 | 56.0492 | 95.1337 | 24.661 | 230.8918 | 136.6952 | 270.444 | 11.0778 | 56.321 | 14.1007 | 167 | 50.7403 | 0 | 260.0428 | 0.14908
6758 | 862.9327 | 1.3524 | 34.716 | 96.7025 | 15.4921 | 4.7503 | 98.0153 | 5.3226 | 6.219 | 58.9615 | 93.8223 | 25.3132 | 228.9688 | 145.2462 | 297.9374 | 11.1131 | 58.1829 | 14.4629 | 175 | 50.1803 | 0 | 271.0776 | 0.14438
6759 | 865.5915 | 1.1595 | 23.2684 | 95.5567 | 14.4957 | 5.6997 | 90.6431 | 3.6865 | 6.33 | 55.914 | 91.9628 | 23.4265 | 225.1319 | 144.7503 | 316.476 | 11.2319 | 56.1589 | 14.4641 | 180 | 51.4531 | 0 | 269.6173 | 0.11331
6760 | 864.5303 | 1.5703 | 23.0371 | 95.9009 | 14.4921 | 5.7 | 86.1664 | 2.2577 | 6.358 | 45.781 | 89.7772 | 15.2334 | 221.2262 | 139.3726 | 310.8339 | 11.3304 | 53.9625 | 14.3592 | 191 | 51.4888 | 0 | 263.5039 | 0.054203
6761 | 875.3357 | 2.3761 | 22.8489 | 95.5898 | 15.4946 | 4.7503 | 86.9165 | 2.7788 | 6.335 | 38.2672 | 88.5136 | 8.4513 | 216.9983 | 143.5121 | 285.5126 | 9.9484 | 53.8947 | 12.5904 | 192 | 48.709 | 0 | 259.3863 | 0.0070844
6762 | 853.637 | 3.3953 | 22.5413 | 93.2077 | 15.4979 | 4.7513 | 87.5904 | 3.6714 | 6.495 | 40.8896 | 84.3578 | 7.8268 | 211.2263 | 145.73 | 254.525 | 9.41 | 54.7441 | 7.9647 | 186 | 43.9052 | 0 | 261.2777 | 0
6763 | 827.3346 | 3.5449 | 22.543 | 90.5013 | 14.5018 | 5.6984 | 87.2379 | 3.8017 | 6.612 | 49.2059 | 79.3689 | 8.4803 | 198.7659 | 141.904 | 249.0334 | 9.7667 | 55.9876 | 5.9902 | 180 | 41.9892 | 0 | 264.452 | 0
6764 | 821.9068 | 3.4086 | 22.501 | 91.8236 | 13.5053 | 6.6497 | 86.5573 | 3.7771 | 6.714 | 53.275 | 78.6412 | 8.2947 | 188.4547 | 139.5358 | 256.161 | 9.8726 | 56.1481 | 5.588 | 188 | 40.4009 | 0 | 263.6301 | 0
6765 | 816.3003 | 3.3331 | 22.6493 | 92.1037 | 12.4989 | 7.5997 | 85.8542 | 3.4875 | 6.855 | 46.6219 | 78.6746 | 7.9326 | 181.2401 | 133.7395 | 254.1809 | 9.8447 | 54.7792 | 5.9 | 178 | 38.4496 | 0 | 261.5721 | 0
6766 | 800.0955 | 2.8983 | 22.6286 | 91.3973 | 12.4983 | 7.6 | 86.1528 | 3.2907 | 6.683 | 38.5755 | 77.3953 | 7.8673 | 167.9406 | 125.767 | 242.9088 | 9.6847 | 53.8973 | 6.5491 | 172 | 38.4867 | 0 | 258.2064 | 0
6767 | 781.9302 | 1.8843 | 22.7033 | 91.9167 | 12.4986 | 7.6 | 86.666 | 3.3761 | 6.555 | 36.1622 | 75.8866 | 8.3375 | 162.6724 | 121.8937 | 233.0729 | 9.6106 | 53.8251 | 5.6828 | 173 | 42.4922 | 0 | 254.4199 | 0
6768 | 789.3106 | 1.8865 | 22.6138 | 90.0755 | 12.4956 | 7.6 | 85.5479 | 3.7653 | 6.771 | 36.0214 | 74.182 | 8.0902 | 161.9203 | 119.9692 | 236.1878 | 9.6635 | 53.7998 | 5.0855 | 165 | 41.763 | 0 | 252.3314 | 0
6769 | 795.4462 | 1.7091 | 22.6734 | 89.8961 | 15.4979 | 4.7508 | 85.8612 | 3.9024 | 6.87 | 36.1588 | 72.1436 | 7.8413 | 162.1907 | 113.0592 | 242.4158 | 9.7285 | 53.7344 | 5.1262 | 158 | 38.107 | 0 | 253.3743 | 0
6770 | 785.9489 | 1.5296 | 22.5797 | 90.6992 | 9.4989 | 10.4484 | 85.5754 | 3.9249 | 6.73 | 35.3391 | 71.0722 | 7.8773 | 163.5525 | 104.6165 | 240.8245 | 9.6204 | 53.7292 | 4.4613 | 149 | 38.629 | 0 | 254.1521 | 0
6771 | 768.7535 | 1.5096 | 22.5854 | 89.5015 | 10.4986 | 9.5003 | 85.71 | 4.2296 | 6.565 | 33.9075 | 70.7395 | 7.9299 | 163.2121 | 99.7653 | 233.2309 | 9.7192 | 53.6316 | 3.994 | 139 | 38.5683 | 0 | 254.4285 | 0
6772 | 762.2354 | 1.7785 | 22.6006 | 90.471 | 11.4946 | 8.5503 | 85.4899 | 3.7146 | 6.681 | 34.0079 | 70.5686 | 8.1997 | 163.7137 | 95.9938 | 220.9457 | 9.6295 | 54.4345 | 3.7196 | 145 | 38.0783 | 0 | 253.1495 | 0
6773 | 761.207 | 2.6574 | 22.6521 | 91.4041 | 14.4955 | 5.7008 | 85.1822 | 3.266 | 6.687 | 34.2214 | 70.6171 | 7.9898 | 162.1296 | 92.9486 | 218.7814 | 9.724 | 56.7974 | 3.6028 | 137 | 37.6167 | 0 | 248.6533 | 0
6774 | 769.1446 | 3.2013 | 22.635 | 93.9105 | 14.5037 | 5.7 | 85.9197 | 3.4019 | 6.618 | 32.3561 | 71.0752 | 9.9846 | 159.2924 | 92.1338 | 225.8519 | 9.7543 | 56.7818 | 3.6101 | 129 | 35.0519 | 0 | 251.0023 | 0
6775 | 793.3737 | 3.29 | 22.5474 | 93.9504 | 15.498 | 4.7503 | 85.4681 | 3.5691 | 6.698 | 28.5085 | 70.0079 | 10.8589 | 158.7249 | 94.242 | 229.0663 | 10.202 | 54.145 | 3.9007 | 126 | 34.1174 | 0 | 246.718 | 0
6776 | 794.4929 | 1.909 | 22.2957 | 91.5323 | 14.499 | 5.6997 | 84.7103 | 3.7019 | 6.215 | 29.7257 | 68.8479 | 8.6467 | 162.6449 | 100.3053 | 222.1961 | 10.5966 | 52.6931 | 4.6026 | 117 | 35.5854 | 0 | 240.3026 | 0.063015
6777 | 797.56 | 1.4355 | 22.2647 | 92.1981 | 13.4934 | 6.6497 | 87.5752 | 3.6293 | 5.885 | 37.5772 | 71.374 | 8.6005 | 169.3698 | 107.0734 | 221.9468 | 10.7086 | 53.1054 | 6.7842 | 160 | 37.484 | 0 | 240.0036 | 0.054186
6778 | 809.2751 | 1.1857 | 22.4344 | 92.9284 | 12.4928 | 7.5997 | 96.4202 | 3.8182 | 5.889 | 46.2648 | 78.8811 | 8.4676 | 178.0494 | 112.792 | 240.1434 | 10.7262 | 54.2803 | 12.0191 | 162 | 40.8044 | 0 | 241.9663 | 0.072367
6779 | 830.2157 | 1.1756 | 22.9437 | 91.3052 | 13.4963 | 6.6503 | 100.1535 | 3.039 | 5.812 | 52.8425 | 86.8108 | 8.6114 | 193.3914 | 119.6117 | 258.0584 | 10.3434 | 54.8135 | 14.5141 | 161 | 43.0095 | 0 | 244.6408 | 0.089665
6780 | 846.845 | 1.3662 | 22.1789 | 92.0853 | 12.4937 | 7.5997 | 94.4046 | 2.27 | 5.707 | 52.9658 | 91.2921 | 8.8435 | 209.7796 | 126.9403 | 264.8723 | 10.3372 | 55.1503 | 14.7736 | 168 | 44.0738 | 0 | 245.5481 | 0.14053
6781 | 840.6038 | 1.7296 | 22.0829 | 93.8039 | 13.4959 | 6.6503 | 78.1696 | 2.7984 | 5.708 | 51.9567 | 95.4426 | 9.7791 | 217.0837 | 135.5651 | 263.7146 | 10.4521 | 56.5063 | 15.3218 | 166 | 44.93 | 0 | 252.561 | 0.079255
6782 | 852.0683 | 1.4984 | 22.0194 | 94.6902 | 14.4987 | 5.7003 | 68.0382 | 3.0874 | 6.154 | 53.7235 | 98.6189 | 10.7013 | 226.5684 | 141.8335 | 271.4391 | 10.4979 | 57.5352 | 16.046 | 168 | 46.7559 | 0 | 254.1628 | 0.13976
6783 | 844.0159 | 1.9049 | 22.1755 | 94.7753 | 15.4985 | 4.7503 | 71.3496 | 2.3602 | 7.222 | 53.2016 | 100.2749 | 12.5605 | 230.7645 | 141.3628 | 291.4435 | 10.5577 | 56.4476 | 16.0917 | 171 | 46.4497 | 0 | 256.4717 | 0.09173
6784 | 846.4327 | 2.0881 | 22.1136 | 96.7026 | 15.5016 | 4.75 | 92.1534 | 2.4407 | 7.005 | 46.6218 | 100.0182 | 14.3789 | 226.0188 | 136.9278 | 297.3164 | 10.538 | 55.2228 | 15.9257 | 166 | 45.9914 | 0 | 263.9997 | 0.059932
6785 | 849.9012 | 2.5172 | 22.2869 | 95.9787 | 14.4988 | 5.6997 | 101.4524 | 3.4052 | 6.897 | 38.4277 | 97.6533 | 14.3352 | 223.7701 | 134.5827 | 290.949 | 8.8732 | 54.9039 | 13.3227 | 159 | 44.445 | 0 | 267.163 | 0.015809
6786 | 844.9307 | 3.5245 | 22.4915 | 95.4699 | 14.4993 | 5.7 | 95.1638 | 3.706 | 7.247 | 34.7889 | 96.5817 | 15.3788 | 212.6749 | 137.1799 | 283.0949 | 8.4046 | 54.6839 | 8.2225 | 145 | 43.3851 | 0 | 267.517 | 0
6787 | 840.3482 | 3.8247 | 22.779 | 96.5642 | 15.5001 | 4.7503 | 87.8315 | 3.8118 | 7.321 | 35.6587 | 95.3844 | 16.6745 | 204.2991 | 142.4882 | 274.7291 | 8.4497 | 55.4566 | 6.4595 | 139 | 41.9061 | 0 | 272.2005 | 0
6788 | 816.1186 | 3.6571 | 22.5858 | 95.26 | 14.501 | 5.6997 | 95.4324 | 3.9496 | 7.069 | 36.6086 | 87.0498 | 14.6962 | 199.944 | 139.2674 | 257.7353 | 8.6964 | 55.8623 | 6.0189 | 148 | 42.7348 | 0 | 272.2802 | 0
6789 | 799.2091 | 3.9081 | 22.7524 | 93.9293 | 15.4992 | 4.7503 | 100.3597 | 3.9844 | 6.984 | 34.3797 | 76.3827 | 13.0025 | 193.8898 | 128.5266 | 237.5429 | 8.6413 | 54.5958 | 5.0703 | 129 | 40.8935 | 0 | 262.5067 | 0
6790 | 792.2194 | 3.3181 | 22.6964 | 92.7583 | 14.496 | 5.6997 | 91.3008 | 3.3472 | 6.913 | 32.0179 | 72.7356 | 10.7137 | 179.3995 | 116.2756 | 227.0902 | 8.5702 | 53.6788 | 5.1636 | 118 | 39.1272 | 0 | 260.5359 | 0
6791 | 779.8035 | 1.9583 | 22.7832 | 94.1561 | 13.4994 | 6.6497 | 85.6996 | 2.9903 | 7.041 | 31.489 | 71.8509 | 7.7146 | 178.0333 | 106.8548 | 226.4175 | 8.6688 | 53.5764 | 5.3692 | 114 | 38.4372 | 0 | 268.5189 | 0
6792 | 776.9448 | 1.3208 | 22.7326 | 93.1934 | 12.5015 | 7.5997 | 84.5341 | 3.839 | 6.879 | 30.7912 | 70.4326 | 6.7422 | 171.8455 | 101.7336 | 224.3214 | 8.605 | 53.8437 | 5.3857 | 112 | 35.853 | 0 | 272.1475 | 0
6793 | 763.5565 | 1.3213 | 22.8621 | 94.3238 | 13.4967 | 6.6503 | 83.7347 | 4.0073 | 6.843 | 29.4422 | 70.3074 | 6.7154 | 164.399 | 99.1708 | 223.438 | 8.6851 | 53.891 | 5.3131 | 107 | 34.8914 | 0 | 265.4907 | 0
6794 | 747.9863 | 1.3356 | 22.7034 | 94.9069 | 12.4996 | 7.5997 | 83.481 | 3.8677 | 6.695 | 28.9611 | 70.2619 | 6.6885 | 163.4978 | 100.0772 | 233.0686 | 8.6339 | 53.6542 | 4.1402 | 109 | 33.8534 | 0 | 258.9439 | 0
6795 | 743.6009 | 1.2833 | 22.7882 | 93.5428 | 14.4985 | 5.7005 | 83.2872 | 3.8908 | 6.473 | 30.4349 | 69.7555 | 6.6663 | 162.7253 | 103.0252 | 240.8468 | 8.5789 | 53.8457 | 3.636 | 109 | 34.0175 | 0 | 256.2012 | 0
6796 | 762.7338 | 1.6605 | 24.3681 | 96.2672 | 15.499 | 4.7503 | 83.1003 | 3.8726 | 6.347 | 37.048 | 69.6332 | 6.6578 | 162.3703 | 98.7851 | 237.3986 | 8.6382 | 54.7596 | 3.6481 | 106 | 33.5476 | 0 | 276.236 | 0
6797 | 775.9547 | 3.0683 | 32.5881 | 95.3409 | 14.4978 | 5.6997 | 88.3923 | 3.4663 | 6.313 | 43.2293 | 69.7682 | 9.6699 | 166.468 | 94.2053 | 231.2149 | 8.4879 | 56.72 | 3.5984 | 105 | 33.8512 | 0 | 306.3471 | 0
6798 | 823.4067 | 4.2935 | 46.609 | 99.2568 | 7.4934 | 12.3482 | 103.9696 | 3.012 | 7.815 | 46.6879 | 84.4057 | 16.1094 | 174.7692 | 122.5047 | 241.034 | 12.8232 | 56.5236 | 3.5634 | 184 | 41.3506 | 0 | 343.7561 | 0
6799 | 886.0146 | 10.9514 | 73.4138 | 105.0431 | -0.14791 | 19.9479 | 124.4289 | 4.5074 | 11.456 | 56.5788 | 114.8947 | 32.1923 | 205.7635 | 188.7524 | 287.5286 | 28.4733 | 57.0734 | 10.3989 | 305 | 43.0836 | 0 | 391.9013 | 0
6800 | 1014.4982 | 17.1641 | 89.4948 | 116.9124 | -1.2966 | 20.8997 | 144.1902 | 6.3196 | 18.312 | 69.2318 | 141.5306 | 40.9432 | 265.687 | 256.4798 | 376.5056 | 36.7042 | 64.5427 | 15.5307 | 282 | 60.7755 | 0 | 446.1335 | 0.014905
6801 | 1098.2403 | 15.0102 | 95.6152 | 131.7916 | -2.5074 | 21.8497 | 166.9742 | 7.834 | 25.999 | 79.9023 | 160.3279 | 42.124 | 331.9093 | 303.7483 | 485.514 | 42.5279 | 74.7786 | 16.8172 | 316 | 67.3804 | 0 | 505.024 | 0.039273
6802 | 1171.9028 | 8.4937 | 96.455 | 136.6357 | -1.5086 | 20.9003 | 170.7786 | 7.9465 | 26.779 | 87.24 | 175.1417 | 41.0278 | 397.6741 | 329.3532 | 570.886 | 43.4634 | 81.6284 | 19.1674 | 351 | 73.9938 | 0 | 540.847 | 0.045032
6803 | 1215.164 | 9.7467 | 97.1355 | 133.8137 | -3.5089 | 22.7995 | 167.1886 | 6.2378 | 23.823 | 90.4864 | 184.2176 | 40.7143 | 432.3765 | 347.1731 | 600.4778 | 43.4449 | 85.0655 | 19.2619 | 311 | 82.7602 | 0 | 560.8534 | 0.053561
6804 | 1201.217 | 11.0878 | 102.219 | 136.562 | -3.5079 | 22.8 | 165.4264 | 6.7397 | 21.269 | 89.8445 | 187.0226 | 42.0958 | 442.3978 | 354.5128 | 593.4231 | 44.2412 | 85.3887 | 18.7139 | 359 | 78.5553 | 0 | 571.4297 | 0.06584
6805 | 1240.6213 | 6.8266 | 101.7265 | 140.9372 | -5.5063 | 24.6995 | 158.8657 | 7.0614 | 19.655 | 88.6376 | 188.1733 | 42.9266 | 429.3613 | 358.7221 | 583.8702 | 44.4995 | 85.3874 | 19.3691 | 287 | 83.0362 | 0 | 594.3079 | 0.091152
6806 | 1257.1411 | 4.1592 | 97.0229 | 140.2447 | -1.5069 | 20.9011 | 160.7234 | 5.522 | 20.755 | 88.989 | 191.5983 | 41.65 | 428.8777 | 365.8773 | 569.3984 | 42.9067 | 88.2314 | 19.6578 | 262 | 82.9584 | 0 | 606.0988 | 0.12725
6807 | 1215.887 | 5.1778 | 94.8596 | 142.5817 | 1.4921 | 18.0508 | 164.4749 | 4.9552 | 22.072 | 87.1855 | 193.7936 | 39.9297 | 436.2556 | 362.0765 | 570.44 | 39.658 | 90.4706 | 19.537 | 282 | 78.7149 | 0 | 584.3523 | 0.10359
6808 | 1169.6777 | 4.0811 | 91.156 | 139.9374 | 4.495 | 15.2008 | 154.5413 | 5.2628 | 22.437 | 84.2464 | 190.8069 | 36.1695 | 433.6871 | 344.1595 | 548.659 | 32.1338 | 88.8615 | 19.5185 | 231 | 74.8764 | 0 | 534.0467 | 0.084231
6809 | 1055.0374 | 3.921 | 86.8547 | 125.0221 | 7.4955 | 12.3508 | 140.1223 | 4.812 | 22.148 | 71.0246 | 177.9591 | 35.172 | 411.8666 | 289.3901 | 480.0467 | 17.1748 | 81.9629 | 19.0565 | 217 | 64.3861 | 0 | 451.1905 | 0.032927
6810 | 979.2224 | 4.1538 | 83.866 | 108.1248 | 14.4937 | 5.7034 | 128.3068 | 4.3362 | 13.96 | 56.0086 | 150.7197 | 30.4828 | 354.6501 | 212.6748 | 401.3545 | 10.3347 | 73.7013 | 15.694 | 210 | 56.2674 | 0 | 394.283 | 0
6811 | 945.5841 | 4.2654 | 74.5567 | 100.763 | 14.4991 | 5.7 | 105.0615 | 3.9231 | 8.928 | 57.0322 | 126.8202 | 22.5692 | 333.8412 | 176.2247 | 356.495 | 9.3321 | 68.1985 | 9.2472 | 199 | 49.6824 | 0 | 349.786 | 0
6812 | 922.0633 | 3.8334 | 36.4659 | 97.1501 | 13.5034 | 6.65 | 91.6185 | 3.7381 | 8.229 | 60.1934 | 118.4846 | 17.7717 | 364.7908 | 168.4842 | 320.4201 | 9.3317 | 63.0586 | 7.0255 | 178 | 46.344 | 0 | 308.5836 | 0
6813 | 902.534 | 3.4006 | 22.7491 | 98.2426 | 14.5015 | 5.6984 | 88.8408 | 3.5454 | 7.534 | 51.3205 | 111.5358 | 17.2861 | 360.3829 | 147.4068 | 288.1559 | 9.8226 | 57.4283 | 5.9187 | 180 | 38.9591 | 0 | 287.1817 | 0
6814 | 878.0168 | 4.1717 | 22.2976 | 95.5035 | 14.4983 | 5.7 | 88.6495 | 3.8544 | 7.072 | 38.5778 | 96.2801 | 17.1706 | 330.33 | 125.6468 | 266.4608 | 9.9943 | 53.9112 | 4.8158 | 141 | 34.351 | 0 | 266.9341 | 0
6815 | 837.9105 | 7.2001 | 22.3715 | 95.4146 | 14.5008 | 5.7 | 88.62 | 4.1726 | 6.433 | 32.2797 | 82.7643 | 13.9933 | 311.8465 | 115.742 | 251.9234 | 9.993 | 52.9297 | 4.5577 | 127 | 31.8933 | 0 | 260.9884 | 0
6816 | 825.4496 | 7.3962 | 22.4703 | 95.8012 | 15.5018 | 4.7503 | 88.5447 | 4.5102 | 6.288 | 30.2522 | 78.0437 | 12.3244 | 303.3837 | 109.7655 | 236.0851 | 10.0565 | 52.9461 | 4.5123 | 114 | 30.2515 | 0 | 260.4262 | 0
6817 | 814.8908 | 3.2987 | 22.4805 | 96.28 | 14.5003 | 5.6997 | 88.5903 | 4.4462 | 6.386 | 28.7748 | 77.8262 | 12.5237 | 304.0836 | 105.3437 | 222.5202 | 10.0552 | 53.0971 | 4.2657 | 115 | 29.7016 | 0 | 256.8681 | 0
6818 | 814.6879 | 1.4864 | 22.391 | 92.3168 | 12.502 | 7.5995 | 89.7789 | 4.3671 | 6.333 | 27.9468 | 79.3524 | 12.683 | 309.1651 | 101.9962 | 223.2339 | 9.9542 | 53.2567 | 3.7441 | 109 | 29.7918 | 0 | 254.5665 | 0
6819 | 806.3772 | 1.4616 | 22.3593 | 93.0207 | 12.5022 | 7.6021 | 89.5674 | 4.323 | 6.391 | 29.0921 | 80.4656 | 12.1845 | 309.518 | 98.3383 | 231.4815 | 9.7302 | 53.2569 | 3.4546 | 105 | 30.2404 | 0 | 255.4474 | 0
6820 | 804.2412 | 1.8682 | 22.3698 | 92.3013 | 12.5031 | 7.5979 | 89.2487 | 4.2852 | 6.374 | 35.3969 | 80.2358 | 11.9021 | 303.1342 | 94.347 | 230.8332 | 9.3801 | 53.8603 | 3.4072 | 107 | 30.3033 | 0 | 269.0573 | 0
6821 | 828.4313 | 3.2263 | 33.5696 | 93.884 | 13.4982 | 6.6503 | 94.915 | 4.0041 | 6.336 | 41.4249 | 79.3062 | 13.0844 | 304.4125 | 96.2759 | 228.4774 | 9.1699 | 56.0691 | 3.3968 | 106 | 30.3973 | 0 | 303.0283 | 0
6822 | 862.359 | 4.8638 | 50.8157 | 97.0014 | 6.497 | 13.2982 | 111.6403 | 3.948 | 6.855 | 48.1194 | 88.9244 | 19.9702 | 311.587 | 125.5169 | 239.5091 | 12.3506 | 56.3829 | 3.5894 | 176 | 39.3901 | 0 | 362.8169 | 0
6823 | 920.5623 | 5.5941 | 69.3279 | 102.1444 | -0.50389 | 19.9482 | 132.1948 | 4.4394 | 7.297 | 67.8455 | 121.1475 | 30.6352 | 354.9203 | 189.7233 | 289.1894 | 28.2203 | 57.3573 | 12.3012 | 242 | 49.2262 | 0 | 413.8842 | 0
6824 | 1021.4742 | 6.7377 | 83.887 | 114.2658 | -0.51181 | 19.95 | 150.6033 | 5.8595 | 7.243 | 87.2271 | 155.6497 | 33.7981 | 412.7514 | 260.5353 | 398.1136 | 36.4797 | 63.728 | 17.9866 | 303 | 66.686 | 0 | 460.89 | 0.039684
6825 | 1094.986 | 15.9432 | 86.6789 | 129.4498 | -0.51298 | 19.95 | 168.5499 | 7.266 | 10.092 | 94.4596 | 174.5461 | 37.0612 | 492.7504 | 312.0691 | 519.0841 | 40.5637 | 73.6685 | 18.2708 | 392 | 66.6203 | 0 | 507.98 | 0.074369
6826 | 1157.8768 | 24.2715 | 85.8268 | 136.763 | 0.48832 | 19.0003 | 174.1258 | 7.6208 | 17.052 | 99.7557 | 182.1923 | 41.8171 | 555.3074 | 342.3912 | 580.2142 | 41.7531 | 83.1694 | 18.904 | 327 | 73.8426 | 0 | 543.2529 | 0.095404
6827 | 1194.855 | 17.2715 | 94.2313 | 141.1505 | -2.5106 | 21.8492 | 173.4661 | 7.4715 | 23.651 | 104.9268 | 185.9293 | 43.2782 | 583.9884 | 363.4691 | 596.409 | 42.1713 | 87.5428 | 19.5291 | 355 | 88.8157 | 0 | 572.9941 | 0.073147
6828 | 1176.3664 | 7.3806 | 97.919 | 142.1731 | -3.5075 | 22.7997 | 168.6811 | 7.2294 | 23.554 | 104.3215 | 189.9971 | 44.9162 | 578.3713 | 370.0407 | 591.4567 | 43.1695 | 86.2331 | 19.6893 | 307 | 81.8586 | 0 | 590.5141 | 0.10675
6829 | 1162.5045 | 5.1188 | 98.6234 | 150.7088 | -2.5109 | 21.8503 | 163.3475 | 6.7254 | 20.573 | 104.4921 | 191.9587 | 46.1697 | 567.235 | 367.8422 | 586.7575 | 45.1957 | 86.4799 | 19.9092 | 274 | 83.4172 | 0 | 609.5004 | 0.10612
6830 | 1183.4842 | 5.6545 | 95.6035 | 149.1096 | -2.5095 | 21.85 | 164.9781 | 6.9191 | 23.903 | 105.6872 | 194.4734 | 45.8341 | 580.4805 | 369.7371 | 600.7156 | 45.6204 | 89.2762 | 20.1031 | 263 | 80.7736 | 0 | 622.2317 | 0.066762
6831 | 1189.5276 | 5.9395 | 93.0098 | 139.0231 | 2.4916 | 17.1013 | 166.9513 | 7.0854 | 25.429 | 100.9438 | 194.9631 | 41.5012 | 603.2878 | 366.7061 | 592.9536 | 42.8294 | 88.8786 | 20.1124 | 263 | 77.1737 | 0 | 609.0815 | 0.046882
6832 | 1127.242 | 4.3265 | 87.9192 | 129.2884 | 4.4905 | 15.2005 | 156.2844 | 6.9445 | 22.094 | 95.7516 | 189.8698 | 37.9519 | 592.0667 | 349.3552 | 540.5569 | 33.1073 | 86.4896 | 19.3017 | 222 | 71.0805 | 0 | 552.2021 | 0.037697
6833 | 1064.5255 | 3.9937 | 79.7148 | 117.8414 | 11.4869 | 8.5518 | 136.5314 | 4.054 | 19.425 | 84.6491 | 177.7256 | 30.8971 | 563.1236 | 294.4641 | 455.0124 | 16.3708 | 80.699 | 18.692 | 226 | 59.7021 | 0 | 459.9795 | 0.00418
6834 | 1002.7205 | 4.571 | 75.3529 | 105.6248 | 13.4882 | 6.6505 | 120.1905 | 3.024 | 15.384 | 67.5467 | 156.1336 | 25.0633 | 515.8134 | 225.6678 | 377.6029 | 9.9328 | 71.8211 | 16.6277 | 213 | 54.7679 | 0 | 380.5188 | 0
6835 | 976.2053 | 4.438 | 66.73 | 100.1631 | 14.4886 | 5.7003 | 97.5666 | 3.8073 | 13.855 | 59.2467 | 133.8871 | 14.6498 | 471.5265 | 184.5168 | 334.2556 | 9.2946 | 64.2887 | 11.0841 | 195 | 48.2877 | 0 | 324.7957 | 0
6836 | 940.8887 | 3.9497 | 29.2462 | 96.8549 | 15.4972 | 4.7503 | 89.4436 | 4.0216 | 10.48 | 56.7637 | 117.8246 | 10.8414 | 426.2171 | 166.9342 | 302.8863 | 9.5572 | 58.5791 | 7.5813 | 185 | 46.165 | 0 | 286.7888 | 0
6837 | 899.8716 | 3.5495 | 18.0371 | 91.5213 | 14.4998 | 5.6997 | 87.107 | 4.068 | 8.676 | 47.8638 | 105.3043 | 10.7236 | 349.4941 | 155.6751 | 276.4053 | 9.8826 | 54.5609 | 6.5101 | 174 | 42.1634 | 0 | 273.4904 | 0
6838 | 865.6295 | 3.2696 | 16.6443 | 91.6171 | 15.5002 | 4.7503 | 85.2629 | 4.366 | 8.485 | 37.3409 | 92.6649 | 10.5075 | 234.9976 | 145.9443 | 263.995 | 10.0802 | 52.9575 | 5.8861 | 146 | 35.3914 | 0 | 264.0509 | 0
6839 | 850.1814 | 2.1357 | 15.8273 | 89.9849 | 14.5003 | 5.6997 | 84.9348 | 4.336 | 7.693 | 32.5252 | 82.9695 | 10.6998 | 188.8928 | 138.7774 | 256.105 | 10.1979 | 52.6381 | 5.3811 | 127 | 33.5728 | 0 | 255.0099 | 0
6840 | 829.6816 | 1.3818 | 15.7701 | 90.6739 | 14.4973 | 5.7 | 84.6149 | 4.2136 | 7.276 | 30.0924 | 80.1969 | 7.6455 | 181.3413 | 132.2855 | 244.5973 | 10.0263 | 52.6315 | 5.1893 | 119 | 30.9044 | 0 | 256.3009 | 0
6841 | 816.0521 | 1.6143 | 15.8514 | 90.0312 | 15.4976 | 4.7503 | 77.868 | 4.115 | 7.149 | 28.0966 | 80.0907 | 6.0127 | 180.7229 | 125.6674 | 230.2327 | 10.0107 | 52.7348 | 5.0071 | 116 | 30.7233 | 0 | 258.3158 | 0
6842 | 798.097 | 1.633 | 15.768 | 90.7337 | 14.4988 | 5.6997 | 80.2693 | 3.7639 | 6.753 | 27.2631 | 79.6347 | 5.914 | 183.6231 | 119.7762 | 225.3392 | 9.4176 | 52.5479 | 4.8396 | 115 | 30.9282 | 0 | 254.8285 | 0
6843 | 808.2593 | 1.3571 | 15.7431 | 92.0246 | 14.497 | 5.7 | 84.6414 | 3.4317 | 6.775 | 28.3719 | 78.9157 | 5.9117 | 183.5994 | 116.4516 | 227.2792 | 9.2997 | 52.2636 | 4.6684 | 127 | 30.6079 | 0 | 253.5887 | 0
6844 | 814.8643 | 1.7051 | 15.6629 | 92.093 | 15.4937 | 4.7503 | 85.7273 | 3.6027 | 6.633 | 34.481 | 78.0293 | 5.9251 | 182.0156 | 113.1935 | 225.1203 | 9.3761 | 52.9642 | 4.4995 | 126 | 30.5852 | 0 | 263.0512 | 0
6845 | 812.404 | 3.0441 | 29.8842 | 92.2271 | 14.4957 | 5.6997 | 91.2211 | 4.3429 | 6.533 | 41.1409 | 78.0584 | 9.2135 | 184.6295 | 111.4318 | 225.4446 | 9.2756 | 55.2115 | 4.4721 | 128 | 30.9782 | 0 | 295.3941 | 0
6846 | 854.9641 | 4.8727 | 50.3791 | 96.7036 | 3.4978 | 16.1471 | 107.4929 | 4.6095 | 6.551 | 49.0536 | 90.7435 | 16.0643 | 194.3783 | 138.7287 | 241.8713 | 12.2387 | 55.3237 | 4.392 | 201 | 36.9237 | 0 | 345.38 | 0
6847 | 937.0303 | 6.8201 | 71.186 | 100.4076 | -3.5069 | 22.7982 | 127.7077 | 4.8412 | 11.39 | 70.8291 | 125.3825 | 30.8417 | 226.7634 | 201.3577 | 301.2614 | 27.3323 | 56.3164 | 10.1019 | 289 | 47.3492 | 0 | 402.6645 | 0
6848 | 1016.944 | 8.4594 | 83.0724 | 114.014 | -3.509 | 22.8 | 146.5329 | 5.7007 | 16.834 | 93.5577 | 162.5502 | 35.1113 | 284.115 | 263.0867 | 406.7197 | 36.608 | 63.0502 | 16.047 | 287 | 62.3309 | 0 | 472.7444 | 0.015802
6849 | 1101.3095 | 14.0373 | 91.0886 | 130.1205 | -3.5122 | 22.8 | 161.3304 | 6.2691 | 24.272 | 104.8136 | 180.3925 | 37.1706 | 354.0123 | 305.1341 | 517.2431 | 41.6705 | 71.9404 | 17.3085 | 336 | 66.2068 | 0 | 531.1689 | 0.048814
6850 | 1153.3772 | 18.7422 | 88.0243 | 136.0584 | -4.5099 | 23.7497 | 167.4605 | 5.8005 | 26.063 | 108.156 | 186.5561 | 40.6847 | 405.4364 | 332.9985 | 582.7616 | 43.6973 | 79.5969 | 17.6607 | 356 | 74.4604 | 0 | 571.455 | 0.10672
6851 | 1183.88 | 12.521 | 88.9419 | 139.8711 | -1.5087 | 20.9008 | 169.4731 | 6.7469 | 25.422 | 108.9414 | 190.4399 | 40.5339 | 423.7464 | 354.2906 | 597.1773 | 43.6432 | 83.1701 | 18.224 | 345 | 82.4759 | 0 | 590.3829 | 0.083161
6852 | 1182.5794 | 5.2117 | 92.0534 | 136.4347 | -1.5067 | 20.9 | 163.3376 | 7.1807 | 22.588 | 105.4137 | 188.5365 | 39.2965 | 435.948 | 364.2412 | 585.0536 | 43.6154 | 83.6108 | 18.3428 | 322 | 78.3628 | 0 | 601.4462 | 0.1087
6853 | 1193.6813 | 3.4655 | 95.2496 | 138.7479 | -1.5062 | 20.9 | 160.4918 | 7.8438 | 18.07 | 97.3319 | 190.0788 | 40.9509 | 425.7113 | 368.4245 | 576.4024 | 45.1788 | 85.6427 | 18.7245 | 290 | 75.5646 | 0 | 620.6547 | 0.11813
6854 | 1193.9121 | 3.4505 | 97.8667 | 144.3783 | -3.5067 | 22.7995 | 167.1772 | 6.2066 | 18.884 | 97.5737 | 196.4092 | 41.5414 | 427.9739 | 371.3448 | 581.4568 | 43.22 | 88.621 | 19.0768 | 289 | 76.1209 | 0 | 634.0434 | 0.095552
6855 | 1145.1408 | 5.3456 | 96.5038 | 139.7133 | 2.4945 | 17.1016 | 168.0373 | 5.5121 | 18.842 | 102.3413 | 199.1569 | 40.6881 | 435.6146 | 362.9782 | 587.8875 | 39.3582 | 89.8029 | 19.371 | 254 | 72.4398 | 0 | 644.4837 | 0.068525
6856 | 1115.1829 | 4.622 | 92.8037 | 131.68 | 4.4983 | 15.2005 | 152.6906 | 5.973 | 17.325 | 98.584 | 198.3743 | 38.3109 | 418.9237 | 344.2718 | 563.8101 | 32.5973 | 88.2926 | 19.2194 | 252 | 67.5846 | 0 | 602.2752 | 0.042921
6857 | 1066.4493 | 4.9683 | 90.8732 | 116.1698 | 11.4972 | 8.5518 | 136.0652 | 4.5948 | 16.398 | 85.9214 | 183.9785 | 31.1769 | 383.4346 | 299.6806 | 488.8183 | 16.2695 | 82.6291 | 18.982 | 234 | 56.1366 | 0 | 495.8331 | 0.0052044
6858 | 997.9719 | 5.1302 | 85.3627 | 102.7479 | 11.4968 | 8.55 | 125.642 | 3.6751 | 18.622 | 73.5164 | 150.8044 | 27.5064 | 339.863 | 233.9583 | 403.4924 | 9.4937 | 74.8726 | 17.0863 | 221 | 50.9486 | 0 | 398.354 | 0
6859 | 944.8709 | 4.1719 | 72.5326 | 98.0302 | 12.4996 | 7.6003 | 110.1964 | 4.347 | 17.735 | 67.9581 | 120.9989 | 16.5629 | 295.1009 | 184.0789 | 347.4734 | 8.8866 | 68.1285 | 12.2194 | 211 | 44.409 | 0 | 334.4666 | 0
6860 | 868.9684 | 3.7828 | 37.1481 | 93.9795 | 13.5004 | 6.6503 | 98.0056 | 4.4682 | 11.24 | 63.365 | 108.3966 | 11.6152 | 262.3849 | 157.4687 | 310.0001 | 8.6662 | 61.8829 | 9.2757 | 190 | 40.9907 | 0 | 301.3235 | 0
6861 | 838.8895 | 3.3874 | 23.8085 | 92.2673 | 14.4959 | 5.7003 | 97.3507 | 3.9994 | 8.012 | 49.8681 | 101.5172 | 10.0404 | 241.5257 | 139.4774 | 285.3174 | 8.657 | 56.6187 | 6.6367 | 174 | 37.8862 | 0 | 292.9964 | 0
6862 | 794.2002 | 2.7634 | 22.8293 | 94.0253 | 15.5002 | 4.7503 | 98.1448 | 3.9027 | 7.544 | 35.9166 | 90.3705 | 7.5786 | 216.0844 | 125.9124 | 264.1411 | 8.6236 | 54.9345 | 5.1147 | 161 | 33.9533 | 0 | 287.4482 | 0
6863 | 793.2624 | 1.6966 | 22.6694 | 91.689 | 14.5036 | 5.6997 | 87.8987 | 3.9696 | 6.832 | 30.0115 | 79.799 | 6.7255 | 199.1378 | 115.3242 | 249.6874 | 8.6323 | 54.5702 | 4.7539 | 141 | 31.9086 | 0 | 281.3703 | 0
6864 | 791.7511 | 1.3329 | 22.5768 | 91.2923 | 14.5045 | 5.7 | 83.173 | 3.4372 | 6.69 | 27.1845 | 75.8079 | 6.5374 | 187.6041 | 106.1802 | 245.0978 | 8.7101 | 53.6804 | 4.7204 | 133 | 28.1964 | 0 | 278.2112 | 0
6865 | 797.2695 | 1.3873 | 22.7251 | 90.9319 | 15.5045 | 4.7503 | 82.943 | 3.3291 | 6.638 | 25.0179 | 74.7527 | 6.2438 | 183.1549 | 100.4374 | 243.3542 | 8.6442 | 53.3492 | 4.3225 | 123 | 26.0597 | 0 | 281.6864 | 0
6866 | 781.5381 | 1.3508 | 22.7544 | 91.6169 | 14.5034 | 5.6997 | 83.0039 | 3.7966 | 6.667 | 24.3971 | 74.6021 | 6.2159 | 185.469 | 97.5069 | 240.4466 | 8.6767 | 53.381 | 4.0368 | 123 | 28.1077 | 0 | 281.1536 | 0
6867 | 751.1273 | 1.3157 | 22.7328 | 92.793 | 14.497 | 5.7 | 82.7411 | 4.0139 | 6.798 | 25.8655 | 74.9215 | 6.2259 | 185.1681 | 97.4052 | 234.3435 | 8.5358 | 53.4366 | 3.9623 | 121 | 27.7446 | 0 | 277.3207 | 0
6868 | 896.2053 | 3.8483 | 71.7622 | 136.7754 | 6.1534 | 13.6232 | 109.8512 | 4.9738 | 6.7546 | 42.1323 | 94.8676 | 20.1417 | 184.1653 | 148.1536 | 289.3921 | 21.3569 | 59.1479 | 9.4699 | 119 | 51.5543 | 0 | 345.4031 | 0
6869 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 11.7359 | 63.8942 | 125.0632 | 26.8735 | 376.6469 | 213.1176 | 377.4508 | 26.3804 | 67.0474 | 12.2427 | 127 | 53.9935 | 0 | 420.2896 | 0
6870 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 189 | 53.9935 | 0 | 427.3853 | 0
6871 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 260 | 53.9935 | 0 | 427.3853 | 0
6872 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 296 | 53.9935 | 0 | 427.3853 | 0.04925
6873 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 338 | 53.9935 | 0 | 427.3853 | 0.083642
6874 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 386 | 53.9935 | 0 | 427.3853 | 0.070103
6875 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 350 | 53.9935 | 0 | 427.3853 | 0.094828
6876 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 366 | 53.9935 | 0 | 427.3853 | 0.091446
6877 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 299 | 53.9935 | 0 | 427.3853 | 0.10628
6878 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 272 | 53.9935 | 0 | 427.3853 | 0.068683
6879 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 269 | 53.9935 | 0 | 427.3853 | 0.048432
6880 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 292 | 53.9935 | 0 | 427.3853 | 0.0254
6881 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 251 | 53.9935 | 0 | 427.3853 | 0.0051734
6882 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 237 | 53.9935 | 0 | 427.3853 | 0
6883 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 199 | 53.9935 | 0 | 427.3853 | 0
6884 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 182 | 53.9935 | 0 | 427.3853 | 0
6885 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 170 | 53.9935 | 0 | 427.3853 | 0
6886 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 144 | 53.9935 | 0 | 427.3853 | 0
6887 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 124 | 53.9935 | 0 | 427.3853 | 0
6888 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 117 | 53.9935 | 0 | 427.3853 | 0
6889 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 113 | 53.9935 | 0 | 427.3853 | 0
6890 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 112 | 53.9935 | 0 | 427.3853 | 0
6891 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 109 | 53.9935 | 0 | 427.3853 | 0
6892 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 106 | 53.9935 | 0 | 427.3853 | 0
6893 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 116 | 53.9935 | 0 | 427.3853 | 0
6894 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 184 | 53.9935 | 0 | 427.3853 | 0
6895 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 256 | 53.9935 | 0 | 427.3853 | 0
6896 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 295 | 53.9935 | 0 | 427.3853 | 0.047145
6897 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 358 | 53.9935 | 0 | 427.3853 | 0.090571
6898 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 366 | 53.9935 | 0 | 427.3853 | 0.13413
6899 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 333 | 53.9935 | 0 | 427.3853 | 0.12781
6900 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 367 | 53.9935 | 0 | 427.3853 | 0.18865
6901 | 967.0151 | 5.2242 | 65.4223 | 111.5577 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 317 | 53.9935 | 0 | 427.3853 | 0.28172
6902 | 967.0151 | 5.2242 | 51.7855 | 89.0119 | 6.1471 | 13.6292 | 122.532 | 5.4429 | 14.0613 | 70.8369 | 135.5392 | 26.8735 | 317.2626 | 230.8068 | 407.3988 | 26.3804 | 69.234 | 12.2427 | 292 | 53.9935 | 0 | 427.3853 | 0.25132
6903 | 1033.5383 | 5.0274 | 83.6669 | 117.9762 | 4.4828 | 15.2109 | 134.6709 | 5.0248 | 14.0613 | 77.3127 | 150.7488 | 35.9693 | 242.8351 | 264.8275 | 447.9609 | 36.1698 | 74.417 | 16.885 | 311 | 67.1073 | 0 | 485.4125 | 0.13961
6904 | 1037.1424 | 3.6267 | 89.1565 | 122.2095 | 11.4946 | 8.5519 | 137.8016 | 4.8883 | 17.5884 | 81.8749 | 174.0898 | 36.4546 | 347.5687 | 291.626 | 481.5939 | 25.5321 | 80.2598 | 18.8766 | 303 | 65.4342 | 0 | 503.2467 | 0.074724
6905 | 964.3596 | 3.3392 | 78.4625 | 111.7039 | 13.4961 | 6.6505 | 126.711 | 4.0315 | 18.386 | 73.5365 | 170.1289 | 30.6348 | 365.2638 | 247.2465 | 434.5059 | 14.4706 | 77.3254 | 17.715 | 255 | 55.9835 | 0 | 423.8029 | 0.021139
6906 | 903.6879 | 3.8895 | 62.291 | 96.1036 | 12.5027 | 7.5997 | 113.7515 | 3.9151 | 13.201 | 63.7651 | 138.7928 | 24.587 | 314.6555 | 189.5883 | 370.5316 | 10.4567 | 71.1523 | 14.627 | 260 | 50.1529 | 0 | 359.8014 | 0
6907 | 860.6788 | 3.8766 | 49.2034 | 91.0319 | 12.5004 | 7.6 | 93.5361 | 3.8343 | 10.69 | 63.9926 | 109.2564 | 12.6039 | 271.0587 | 163.7781 | 334.162 | 10.114 | 65.2472 | 8.7832 | 251 | 47.5498 | 0 | 313.052 | 0
6908 | 825.5764 | 3.7163 | 23.2773 | 90.7742 | 13.4935 | 6.6503 | 84.1663 | 3.7235 | 9.9727 | 65.3492 | 91.5488 | 6.6487 | 242.5572 | 147.0792 | 316.3274 | 10.2565 | 59.5611 | 5.807 | 242 | 42.7462 | 0 | 291.3325 | 0
6909 | 791.2068 | 3.7725 | 15.1012 | 90.533 | 12.4973 | 7.5997 | 82.3952 | 3.7223 | 9.3936 | 54.7581 | 80.9468 | 5.9275 | 223.5573 | 131.1747 | 301.2509 | 10.145 | 55.9526 | 4.8997 | 216 | 41.4096 | 0 | 287.1639 | 0
6910 | 780.5492 | 3.3059 | 15.0548 | 91.5047 | 14.4994 | 5.7005 | 81.705 | 3.6808 | 8.7897 | 41.9447 | 76.6555 | 6.0341 | 207.7487 | 116.805 | 293.4569 | 10.154 | 54.313 | 4.5307 | 204 | 38.6619 | 0 | 287.5372 | 0
6911 | 767.3093 | 2.0239 | 14.9889 | 91.5993 | 14.4983 | 5.7 | 82.5826 | 4.1202 | 7.561 | 36.664 | 74.6931 | 5.955 | 197.9769 | 102.2688 | 286.9903 | 10.1806 | 54.0602 | 4.0466 | 196 | 36.4837 | 0 | 291.9093 | 0
6912 | 767.4599 | 1.6833 | 15.2561 | 91.8565 | 15.4978 | 4.7503 | 77.3355 | 4.5332 | 7.043 | 36.0227 | 73.859 | 5.9056 | 188.4072 | 95.2045 | 273.7245 | 10.0524 | 54.0327 | 4.267 | 193 | 36.0426 | 0 | 284.5674 | 0
6913 | 754.8836 | 1.6623 | 15.2399 | 90.6423 | 14.4974 | 5.6997 | 68.8417 | 4.6342 | 6.877 | 35.9209 | 73.3224 | 5.9132 | 182.716 | 93.0291 | 262.8443 | 10.2472 | 53.7809 | 4.2717 | 192 | 36.7114 | 0 | 277.1 | 0
6914 | 747.1882 | 1.4883 | 15.1316 | 91.0342 | 15.4969 | 4.7503 | 76.5484 | 4.5998 | 7.639 | 34.7038 | 72.7028 | 6.1753 | 186.6848 | 94.9467 | 262.8055 | 10.1219 | 53.67 | 3.9101 | 171 | 34.1566 | 0 | 274.4972 | 0
6915 | 751.8837 | 1.5249 | 14.9347 | 89.8878 | 14.496 | 5.6997 | 80.1011 | 4.6653 | 7.836 | 34.2059 | 72.4787 | 6.4956 | 186.9782 | 96.1152 | 264.1575 | 10.2513 | 53.552 | 4.0012 | 149 | 34.1835 | 0 | 276.1792 | 0
6916 | 755.6602 | 1.9132 | 15.1018 | 91.6042 | 15.4979 | 4.7503 | 68.2787 | 4.6997 | 7.798 | 39.3073 | 71.747 | 6.233 | 183.1277 | 92.8597 | 256.1812 | 10.2012 | 54.243 | 3.8783 | 152 | 33.5032 | 0 | 283.4036 | 0
6917 | 750.9957 | 2.7257 | 15.7478 | 90.8795 | 14.4995 | 5.6997 | 63.8349 | 4.7588 | 7.264 | 44.6581 | 71.1019 | 6.1146 | 177.7382 | 92.9251 | 251.8453 | 10.1165 | 56.5649 | 3.7687 | 132 | 32.9845 | 0 | 286.4205 | 0
6918 | 767.4212 | 3.182 | 30.4528 | 90.6711 | 15.4983 | 4.7503 | 75.9565 | 4.7869 | 6.498 | 40.2688 | 71.2526 | 6.3286 | 173.4324 | 92.9045 | 254.9349 | 10.3531 | 56.511 | 3.7544 | 129 | 32.2585 | 0 | 286.2496 | 0
6919 | 791.2195 | 3.2094 | 41.8634 | 89.5496 | 14.4958 | 5.6997 | 82.7718 | 4.9134 | 6.214 | 32.4395 | 73.698 | 7.027 | 172.1564 | 92.0318 | 248.6504 | 15.0568 | 53.8844 | 3.8477 | 122 | 33.9726 | 0 | 277.5681 | 0
6920 | 797.8748 | 2.2952 | 51.3334 | 91.8726 | 15.4954 | 4.7516 | 77.4637 | 4.5205 | 5.945 | 34.0814 | 91.1923 | 11.9034 | 181.5979 | 93.0624 | 232.318 | 28.0414 | 52.7309 | 4.2512 | 129 | 37.4956 | 0 | 265.1872 | 0.049062
6921 | 808.3707 | 1.7769 | 64.2514 | 92.709 | 14.4943 | 5.6984 | 76.3301 | 4.3609 | 5.623 | 45.6561 | 118.2823 | 17.051 | 191.0271 | 98.5642 | 222.6936 | 35.5196 | 52.8475 | 6.188 | 141 | 38.897 | 0 | 265.0208 | 0.08861
6922 | 830.8258 | 1.6796 | 73.4858 | 93.6674 | 14.4899 | 5.7016 | 87.3746 | 5.4275 | 5.768 | 57.9897 | 130.7064 | 18.3018 | 201.3898 | 111.0925 | 223.8629 | 38.9644 | 53.6975 | 11.3615 | 172 | 43.4364 | 0 | 268.8815 | 0.059833
6923 | 862.1304 | 1.5324 | 75.0919 | 92.5251 | 15.4947 | 4.7487 | 93.5324 | 5.6834 | 5.66 | 62.0626 | 117.3612 | 15.2811 | 215.9227 | 130.6005 | 228.3897 | 39.9986 | 54.1441 | 14.4253 | 185 | 47.7694 | 0 | 271.9889 | 0.1215
6924 | 856.0272 | 1.6012 | 75.7609 | 92.7003 | 14.4921 | 5.6997 | 94.615 | 6.381 | 5.619 | 60.2199 | 103.047 | 13.9268 | 223.3873 | 148.2526 | 234.5329 | 40.3481 | 53.7814 | 16.0461 | 217 | 50.0178 | 0 | 273.6292 | 0.094923
6925 | 854.6049 | 1.7098 | 75.2339 | 94.3989 | 15.4923 | 4.7503 | 95.3412 | 4.8437 | 5.773 | 59.8204 | 107.9049 | 16.3822 | 224.4838 | 156.0788 | 253.8956 | 38.693 | 54.4361 | 16.5852 | 185 | 51.6513 | 0 | 274.0871 | 0.10817
6926 | 858.087 | 1.5321 | 66.4387 | 95.8521 | 13.4919 | 6.6495 | 90.0704 | 3.4901 | 5.97 | 56.0901 | 107.2606 | 20.7242 | 222.4813 | 154.2952 | 286.5219 | 33.2041 | 55.3674 | 16.8399 | 177 | 52.5363 | 0 | 275.4638 | 0.15807
6927 | 859.8338 | 1.6134 | 59.1621 | 93.6532 | 12.4916 | 7.5997 | 82.2651 | 2.579 | 5.904 | 49.3767 | 96.71 | 19.4405 | 223.0922 | 148.7587 | 310.2595 | 25.6665 | 55.4967 | 16.6026 | 190 | 50.3282 | 0 | 276.6741 | 0.12426
6928 | 836.2484 | 1.9588 | 32.3686 | 92.9104 | 13.4961 | 6.6503 | 78.4039 | 2.7355 | 6.242 | 41.102 | 90.6329 | 8.8146 | 227.4593 | 151.1863 | 309.1571 | 13.7829 | 55.3277 | 16.3592 | 197 | 49.1922 | 0 | 285.8486 | 0.018554
6929 | 815.0484 | 3.6903 | 22.3144 | 94.1863 | 13.4947 | 6.65 | 77.3852 | 3.3587 | 6.34 | 32.9714 | 88.3861 | 7.2215 | 227.2539 | 154.8572 | 293.4076 | 8.8673 | 55.911 | 14.1428 | 196 | 47.4893 | 0 | 289.0068 | 0.0013248
6930 | 808.4352 | 3.9767 | 21.7731 | 93.5161 | 13.4943 | 6.65 | 79.2861 | 4.0788 | 7.934 | 34.1765 | 83.522 | 9.5692 | 217.9334 | 147.1984 | 280.5038 | 8.4523 | 56.3564 | 9.2001 | 186 | 44.5466 | 0 | 282.3914 | 0
6931 | 813.6838 | 3.4128 | 21.6896 | 91.0867 | 15.4968 | 4.7505 | 82.9264 | 4.1723 | 8.651 | 44.0643 | 82.611 | 7.4504 | 209.2672 | 135.7293 | 272.3764 | 8.496 | 55.7756 | 7.3189 | 173 | 43.0293 | 0 | 277.9303 | 0
6932 | 810.3892 | 3.2504 | 21.5987 | 90.0985 | 14.5018 | 5.6997 | 84.2049 | 4.1213 | 8.303 | 49.8196 | 88.1124 | 6.3398 | 200.9246 | 126.4758 | 264.3654 | 8.4107 | 55.4293 | 7.0146 | 176 | 39.6845 | 0 | 281.3114 | 0
6933 | 797.2481 | 3.1598 | 21.7449 | 90.9217 | 15.5022 | 4.7503 | 84.3454 | 4.1938 | 8.059 | 43.001 | 86.5002 | 6.2056 | 194.765 | 116.3864 | 263.3513 | 8.5793 | 55.0432 | 6.2777 | 160 | 38.0193 | 0 | 294.2169 | 0
6934 | 791.2993 | 2.7114 | 21.6221 | 92.0449 | 15.499 | 4.75 | 83.0746 | 4.2704 | 7.446 | 34.4182 | 79.3714 | 6.0116 | 184.5385 | 107.7733 | 270.4416 | 8.8768 | 54.4715 | 5.8873 | 150 | 34.8958 | 0 | 304.3245 | 0
6935 | 779.4494 | 1.8443 | 21.5856 | 91.3588 | 14.4984 | 5.6997 | 81.9158 | 4.4991 | 6.493 | 32.5943 | 74.3777 | 5.9734 | 177.9962 | 104.9895 | 265.4781 | 9.2253 | 53.9774 | 5.471 | 137 | 33.8197 | 0 | 301.4934 | 0
6936 | 763.3802 | 1.5967 | 21.6107 | 90.9272 | 15.5022 | 4.7503 | 81.3349 | 3.9948 | 6.085 | 33.2191 | 71.7252 | 5.9881 | 174.3162 | 104.0975 | 251.4383 | 9.2805 | 53.8896 | 4.845 | 127 | 33.4666 | 0 | 295.2191 | 0
6937 | 748.422 | 1.6588 | 21.6863 | 91.7502 | 14.5028 | 5.6997 | 82.2814 | 3.7644 | 7.237 | 33.1366 | 71.4243 | 5.9974 | 172.1802 | 100.7858 | 241.2742 | 9.208 | 54.0109 | 3.6327 | 123 | 33.4617 | 0 | 300.1124 | 0
6938 | 744.4985 | 1.6161 | 21.6843 | 91.1321 | 9.5019 | 10.4487 | 82.2618 | 3.8034 | 6.553 | 32.1307 | 72.258 | 5.9897 | 171.8394 | 97.0177 | 240.494 | 9.3386 | 54.0204 | 3.2029 | 123 | 33.2494 | 0 | 300.3604 | 0
6939 | 751.9675 | 1.4965 | 21.6299 | 91.7907 | 10.4998 | 9.5003 | 81.4448 | 3.8291 | 6.061 | 31.8439 | 72.4367 | 6.2676 | 170.2321 | 96.7402 | 241.676 | 9.3217 | 54.0469 | 3.197 | 119 | 33.8907 | 0 | 283.0906 | 0
6940 | 751.459 | 1.8269 | 21.5582 | 91.4394 | 11.5021 | 8.5503 | 81.0186 | 4.4526 | 6.224 | 33.4518 | 72.1032 | 6.575 | 168.7097 | 96.0929 | 234.7992 | 9.2805 | 54.7842 | 3.1668 | 130 | 32.412 | 0 | 273.2677 | 0
6941 | 757.413 | 2.8063 | 21.9737 | 91.7634 | 15.5001 | 4.7511 | 81.4992 | 4.4982 | 5.968 | 34.5362 | 71.3885 | 6.1964 | 167.3414 | 93.8177 | 222.7126 | 9.2135 | 56.9639 | 3.1565 | 114 | 31.8371 | 0 | 269.5503 | 0
6942 | 778.7155 | 3.1718 | 35.97 | 92.6909 | 14.4994 | 5.6997 | 81.6728 | 4.3861 | 5.97 | 32.9842 | 70.5353 | 5.9663 | 164.5677 | 93.622 | 217.0042 | 9.1663 | 56.8357 | 3.1857 | 113 | 31.0802 | 0 | 262.759 | 0
6943 | 782.9251 | 3.2159 | 46.1917 | 93.4212 | 15.4969 | 4.7503 | 81.3605 | 4.2372 | 5.939 | 30.3473 | 69.3881 | 5.2215 | 163.97 | 94.163 | 217.3086 | 9.6868 | 54.2739 | 3.4004 | 115 | 32.2784 | 0 | 260.3912 | 0
6944 | 774.0821 | 2.4647 | 58.1538 | 95.7954 | 14.4974 | 5.6997 | 81.0036 | 4.0165 | 5.585 | 31.8818 | 68.4326 | 4.2716 | 171.9746 | 105.0335 | 217.8872 | 10.8175 | 53.2247 | 4.091 | 126 | 35.0556 | 0 | 253.6162 | 0.014556
6945 | 781.837 | 1.4997 | 63.5455 | 94.9688 | 15.4934 | 4.7503 | 83.9265 | 3.9068 | 5.394 | 37.0806 | 69.5494 | 7.0166 | 177.9201 | 123.3964 | 233.398 | 11.2514 | 53.1519 | 6.6639 | 170 | 41.4961 | 0 | 249.9373 | 0.016363
6946 | 795.4829 | 1.0625 | 63.5686 | 95.2727 | 14.4917 | 5.6997 | 91.951 | 3.7986 | 5.447 | 43.3463 | 72.2494 | 8.1133 | 186.1059 | 137.5237 | 265.7111 | 10.3428 | 53.1907 | 12.2897 | 170 | 39.1364 | 0 | 251.6437 | 0.020264
6947 | 814.4986 | 1.5071 | 62.394 | 97.2738 | 12.4933 | 7.5995 | 96.1026 | 3.9213 | 5.564 | 51.2582 | 77.7049 | 5.9997 | 199.7565 | 149.496 | 287.0882 | 9.399 | 53.0474 | 15.2051 | 195 | 45.2181 | 0 | 257.4574 | 0.037183
6948 | 824.787 | 1.4929 | 62.273 | 97.2142 | 12.4915 | 7.6 | 97.1721 | 3.2977 | 5.516 | 56.9075 | 92.7838 | 8.0812 | 211.2542 | 157.7391 | 293.8325 | 9.7248 | 53.0411 | 15.9931 | 200 | 47.6794 | 0 | 263.2989 | 0.017773
6949 | 823.8113 | 1.6621 | 62.2835 | 100.9969 | 12.4928 | 7.6 | 93.8186 | 2.9981 | 5.62 | 56.127 | 110.1015 | 8.9296 | 220.3655 | 160.336 | 298.0559 | 9.5969 | 53.192 | 16.2517 | 204 | 47.7045 | 0 | 265.6836 | 0.01438
6950 | 826.9411 | 1.5396 | 62.3837 | 104.1038 | 13.4953 | 6.6503 | 86.0793 | 3.1613 | 6.03 | 54.5185 | 112.1565 | 8.9625 | 227.4253 | 162.1225 | 302.2289 | 9.3477 | 53.0593 | 16.8379 | 182 | 49.7411 | 0 | 271.3174 | 0.012605
6951 | 826.3979 | 1.4793 | 59.255 | 101.3757 | 14.4955 | 5.7003 | 87.7076 | 3.5209 | 6.054 | 53.5783 | 103.6542 | 9.6022 | 228.7647 | 160.1197 | 297.7288 | 9.3149 | 53.2509 | 17.2186 | 196 | 48.9604 | 0 | 281.0746 | 0.011171
6952 | 826.9956 | 3.2473 | 41.2234 | 96.7495 | 15.4947 | 4.7503 | 94.3184 | 3.702 | 5.846 | 47.5841 | 96.7404 | 9.6182 | 229.8652 | 151.5333 | 286.1115 | 9.4342 | 53.8354 | 16.4576 | 196 | 47.4983 | 0 | 283.864 | 0.011599
6953 | 827.5907 | 4.1742 | 35.1669 | 99.1118 | 15.4968 | 4.75 | 90.0348 | 3.7628 | 5.766 | 41.0784 | 95.3771 | 8.8945 | 227.4731 | 139.6769 | 286.7136 | 8.9641 | 54.2342 | 13.8519 | 191 | 48.3948 | 0 | 277.7405 | 0.00093532
6954 | 825.7265 | 3.7463 | 35.4096 | 98.4879 | 13.5021 | 6.6495 | 86.9981 | 4.3178 | 5.921 | 41.4138 | 98.2535 | 11.5303 | 223.8152 | 131.9995 | 290.8053 | 8.3947 | 54.6211 | 8.9368 | 165 | 46.1835 | 0 | 279.9792 | 0
6955 | 809.6054 | 3.4699 | 35.5594 | 96.339 | 10.5019 | 9.4992 | 85.157 | 4.2485 | 6.543 | 43.9504 | 97.8454 | 11.786 | 217.6475 | 130.0094 | 280.0806 | 8.2558 | 54.6957 | 6.737 | 149 | 43.2832 | 0 | 285.2624 | 0
6956 | 783.4223 | 3.4847 | 35.6091 | 95.4121 | 14.5022 | 5.7011 | 94.0051 | 4.1191 | 6.906 | 42.4546 | 89.3052 | 10.6442 | 212.7652 | 126.0491 | 266.3895 | 8.2829 | 54.5235 | 5.7485 | 140 | 38.7025 | 0 | 285.2665 | 0
6957 | 766.5932 | 3.4045 | 35.4735 | 96.4892 | 14.5032 | 5.7 | 99.3026 | 4.0126 | 7.772 | 37.8345 | 80.8581 | 10.7469 | 200.5854 | 116.4384 | 247.3381 | 8.1952 | 54.7007 | 4.6472 | 139 | 35.9654 | 0 | 276.6162 | 0
6958 | 768.2031 | 3.211 | 35.3258 | 93.4094 | 15.4997 | 4.7503 | 94.8705 | 3.5765 | 7.889 | 32.5786 | 77.4875 | 7.4444 | 187.4963 | 104.3233 | 230.7534 | 8.2911 | 54.3524 | 4.1992 | 137 | 33.2128 | 0 | 267.4804 | 0
6959 | 760.3271 | 2.0677 | 35.2896 | 93.0765 | 15.499 | 4.75 | 96.6087 | 3.4086 | 6.845 | 30.0918 | 74.3598 | 5.9359 | 180.4424 | 98.5755 | 219.7481 | 8.2959 | 53.6804 | 4.2067 | 133 | 33.0538 | 0 | 265.2368 | 0
6960 | 752.092 | 1.4092 | 35.4375 | 93.8518 | 14.5029 | 5.6997 | 97.9914 | 3.5155 | 6.426 | 29.8024 | 72.3395 | 5.9831 | 175.2206 | 95.3816 | 217.7894 | 8.2709 | 53.5382 | 4.3354 | 133 | 31.1427 | 0 | 263.8726 | 0
6961 | 729.6339 | 1.4474 | 35.4373 | 94.6828 | 15.5007 | 4.7503 | 87.9888 | 4.2437 | 6.28 | 29.8746 | 72.0297 | 5.9708 | 169.4382 | 92.1228 | 225.233 | 8.3404 | 53.6244 | 4.2214 | 122 | 32.0623 | 0 | 265.3443 | 0
6962 | 721.2149 | 1.3018 | 35.3248 | 94.7838 | 14.5017 | 5.6997 | 82.0498 | 4.2386 | 6.108 | 29.9233 | 72.0335 | 6.2836 | 169.258 | 94.0491 | 234.6669 | 8.1843 | 53.7163 | 3.6879 | 120 | 31.2198 | 0 | 266.2472 | 0
6963 | 714.3333 | 1.4539 | 35.3244 | 92.8147 | 15.5007 | 4.7503 | 81.1775 | 4.0955 | 6.361 | 31.7054 | 71.9055 | 6.0827 | 169.2641 | 97.8113 | 234.8713 | 8.2603 | 53.6188 | 3.4601 | 112 | 30.7019 | 0 | 268.0457 | 0
6964 | 721.0621 | 1.7978 | 37.0322 | 94.4636 | 15.4988 | 4.75 | 81.1102 | 4.0549 | 6.406 | 38.2694 | 71.2395 | 5.8443 | 168.295 | 95.7116 | 222.4906 | 8.2465 | 54.2449 | 3.4574 | 116 | 30.9773 | 0 | 284.8812 | 0
6965 | 734.8137 | 3.1363 | 38.6126 | 95.3646 | 14.4972 | 5.6997 | 87.8328 | 4.0695 | 6.314 | 44.0009 | 70.7048 | 7.6101 | 170.2796 | 97.7913 | 218.18 | 8.2867 | 56.4053 | 3.4679 | 116 | 32.4896 | 0 | 312.5141 | 0
6966 | 784.0475 | 4.6209 | 50.1881 | 98.4463 | 8.4968 | 11.3984 | 101.4377 | 4.0524 | 6.556 | 48.187 | 85.4795 | 15.3503 | 178.5788 | 131.3092 | 240.9036 | 12.3477 | 56.4369 | 4.9696 | 164 | 40.6963 | 0 | 353.4886 | 0
6967 | 827.5287 | 5.9181 | 71.165 | 105.1931 | -0.15038 | 19.9476 | 119.7945 | 4.7587 | 10.751 | 64.1411 | 122.6047 | 28.8696 | 212.142 | 196.297 | 313.117 | 26.9917 | 57.6145 | 12.1852 | 243 | 45.1099 | 0 | 419.5673 | 0
6968 | 911.0269 | 10.6816 | 88.3072 | 118.7555 | -0.29807 | 19.95 | 137.9644 | 6.0621 | 15.664 | 82.8514 | 155.715 | 34.5668 | 276.2315 | 256.9509 | 418.8706 | 35.9497 | 64.7892 | 18.062 | 288 | 61.2823 | 0 | 477.0731 | 0.0081474
6969 | 993.939 | 14.2528 | 97.2326 | 136.8047 | -5.5098 | 24.6987 | 159.6699 | 6.467 | 21.374 | 90.0626 | 170.6371 | 37.6403 | 356.016 | 295.6366 | 511.9753 | 42.203 | 74.1984 | 18.972 | 308 | 68.4609 | 0 | 520.3954 | 0.017263
6970 | 1062.2911 | 16.8025 | 100.8674 | 138.8039 | -3.5112 | 22.8005 | 165.2002 | 7.2485 | 24.199 | 89.699 | 175.4463 | 42.4833 | 417.1932 | 321.464 | 576.1519 | 43.5588 | 83.1743 | 19.5301 | 336 | 69.7194 | 0 | 572.3462 | 0.027527
6971 | 1110.7575 | 14.9528 | 102.6474 | 138.975 | -2.5091 | 21.8503 | 165.3419 | 7.3531 | 25.541 | 89.8754 | 176.4329 | 43.3388 | 443.0786 | 343.9084 | 610.2743 | 41.8171 | 88.2073 | 21.4145 | 320 | 83.4603 | 0 | 618.2149 | 0.029597
6972 | 1114.6004 | 10.1212 | 101.8788 | 141.334 | -0.50738 | 19.9505 | 166.2849 | 7.8104 | 22.244 | 85.5422 | 179.6437 | 42.6564 | 461.6944 | 351.2904 | 616.1348 | 42.2376 | 89.432 | 21.2385 | 366 | 76.18 | 0 | 626.4991 | 0.031803
6973 | 1115.4868 | 5.347 | 101.6659 | 146.5761 | -2.5044 | 21.8495 | 170.5779 | 7.4377 | 16.278 | 82.2731 | 184.6831 | 43.6374 | 457.0958 | 348.559 | 608.4201 | 43.9612 | 89.7883 | 22.0708 | 315 | 75.0727 | 0 | 629.373 | 0.030236
6974 | 1116.1819 | 3.9408 | 104.0627 | 149.2202 | 2.4966 | 17.1013 | 167.162 | 6.0639 | 19.132 | 91.2038 | 186.4379 | 42.7931 | 453.843 | 351.606 | 599.7642 | 42.9866 | 90.035 | 21.3345 | 303 | 74.4861 | 0 | 625.3431 | 0.041724
6975 | 1097.0371 | 6.2766 | 103.6851 | 145.0565 | 5.496 | 14.2508 | 158.2459 | 6.377 | 20.131 | 95.962 | 185.3931 | 41.4672 | 445.7914 | 351.2543 | 592.8179 | 41.0614 | 91.1409 | 20.91 | 281 | 72.2835 | 0 | 611.9366 | 0.018196
6976 | 1063.4263 | 5.858 | 99.6314 | 139.0572 | 8.4954 | 11.4008 | 150.178 | 6.084 | 19.816 | 93.2333 | 182.7995 | 40.0007 | 427.8315 | 336.9111 | 563.9459 | 31.9471 | 90.2176 | 20.9119 | 254 | 68.5927 | 0 | 573.8849 | 0.011652
6977 | 1020.3196 | 5.0748 | 94.8508 | 122.1446 | 12.4951 | 7.6011 | 136.5631 | 4.8979 | 18.848 | 86.7984 | 170.1683 | 34.315 | 400.9391 | 291.7778 | 493.19 | 14.9284 | 82.9113 | 20.4722 | 231 | 60.0688 | 0 | 478.5819 | 0.00049681
6978 | 961.0432 | 4.6442 | 88.8432 | 110.1813 | 14.4971 | 5.7005 | 127.1398 | 3.5505 | 12.306 | 77.9422 | 141.9643 | 29.3652 | 352.1001 | 231.1533 | 412.5278 | 9.4954 | 72.9223 | 17.2358 | 219 | 52.8684 | 0 | 407.9783 | 0
6979 | 925.8669 | 4.3799 | 77.6845 | 104.7338 | 14.4987 | 5.7 | 113.0267 | 2.8917 | 9.284 | 73.1551 | 115.3427 | 16.2688 | 298.9925 | 191.3625 | 361.0231 | 8.9668 | 66.6882 | 10.6059 | 196 | 45.4254 | 0 | 356.7992 | 0
6980 | 898.6417 | 4.3472 | 40.6385 | 99.8336 | 13.5019 | 6.6497 | 94.3356 | 3.3832 | 8.494 | 68.5927 | 103.5919 | 8.2901 | 259.6391 | 161.8142 | 324.824 | 8.9044 | 61.8873 | 7.4771 | 186 | 39.5993 | 0 | 307.7804 | 0
6981 | 862.9127 | 3.7598 | 23.412 | 96.3719 | 12.4996 | 7.5997 | 85.3801 | 3.6628 | 8.671 | 55.0305 | 98.4178 | 6.4359 | 227.054 | 131.8881 | 289.6459 | 8.9764 | 56.6249 | 6.2109 | 192 | 35.4069 | 0 | 285.6781 | 0
6982 | 807.6402 | 2.7461 | 21.7033 | 96.8861 | 13.4992 | 6.6503 | 82.7694 | 3.8914 | 8.818 | 37.9792 | 89.8656 | 5.9858 | 202.4818 | 115.9126 | 261.884 | 8.6874 | 53.8869 | 5.2943 | 158 | 34.5492 | 0 | 274.5949 | 0
6983 | 793.3458 | 1.8232 | 21.6465 | 96.3232 | 12.4977 | 7.6018 | 82.6017 | 3.8133 | 7.974 | 29.4247 | 81.0676 | 5.9597 | 189.185 | 105.9673 | 246.7867 | 8.8976 | 53.0914 | 4.8667 | 142 | 31.2205 | 0 | 272.0643 | 0
6984 | 782.256 | 1.4907 | 21.8563 | 96.2073 | 14.5069 | 5.6984 | 82.4968 | 3.1683 | 7.053 | 26.9468 | 77.8573 | 5.9713 | 180.6108 | 96.237 | 238.5413 | 8.9139 | 52.7421 | 4.7678 | 121 | 30.2561 | 0 | 272.1799 | 0
6985 | 777.6822 | 1.3647 | 21.8388 | 95.8393 | 14.5039 | 5.7 | 82.128 | 2.8929 | 6.726 | 25.203 | 78.4808 | 5.9966 | 180.3078 | 91.6547 | 236.4322 | 8.843 | 52.7054 | 4.7039 | 121 | 28.5842 | 0 | 271.7508 | 0
6986 | 751.1106 | 1.2956 | 21.9158 | 94.2354 | 15.5011 | 4.7503 | 81.4756 | 3.3349 | 6.627 | 24.2731 | 80.3353 | 6.406 | 185.2915 | 90.282 | 242.5906 | 8.9036 | 52.7316 | 4.6444 | 116 | 28.9149 | 0 | 273.7832 | 0
6987 | 748.4133 | 1.253 | 21.9764 | 94.9882 | 15.5026 | 4.75 | 81.1011 | 4.0153 | 6.6 | 25.6823 | 81.3704 | 6.2322 | 186.6435 | 89.367 | 246.2439 | 8.7256 | 52.761 | 4.6355 | 116 | 28.256 | 0 | 274.5805 | 0
6988 | 740.0447 | 1.6745 | 21.937 | 92.6952 | 14.5014 | 5.6997 | 81.1749 | 3.9439 | 6.691 | 32.1492 | 81.3058 | 6.0647 | 182.2198 | 87.8513 | 237.0785 | 8.8357 | 53.773 | 4.2604 | 116 | 28.3211 | 0 | 282.1752 | 0
6989 | 755.7877 | 3.0463 | 36.6139 | 95.8917 | 15.4956 | 4.7503 | 87.2635 | 3.8317 | 6.436 | 38.1893 | 80.421 | 9.0167 | 181.6715 | 89.3829 | 230.1889 | 8.8945 | 55.9652 | 3.4808 | 121 | 29.7707 | 0 | 307.5105 | 0
6990 | 782.0365 | 4.9946 | 58.6565 | 98.5201 | 6.4966 | 13.2976 | 101.4175 | 4.0088 | 7.15 | 44.6512 | 90.9803 | 21.8779 | 187.953 | 120.4489 | 240.642 | 11.2463 | 55.7763 | 3.3602 | 187 | 38.4461 | 0 | 346.1634 | 0
6991 | 835.6136 | 5.812 | 73.9693 | 103.0342 | -0.50925 | 19.9482 | 120.2833 | 4.9075 | 8.126 | 65.2032 | 118.4111 | 34.7792 | 221.316 | 188.6007 | 313.4864 | 27.3901 | 57.1161 | 10.5081 | 283 | 48.7619 | 0 | 412.2262 | 0
6992 | 914.8722 | 6.2119 | 88.2643 | 121.7401 | 2.4923 | 17.1008 | 137.8461 | 5.2999 | 9.979 | 85.3339 | 147.2189 | 37.9131 | 287.7371 | 257.2554 | 440.2874 | 34.951 | 64.1416 | 17.2403 | 274 | 68.8897 | 0 | 491.2638 | 0.0083929
6993 | 1028.6749 | 9.4501 | 90.4515 | 128.8808 | 2.4889 | 17.1 | 152.5594 | 6.0576 | 17.086 | 93.7352 | 164.7652 | 39.3068 | 346.4511 | 307.2889 | 537.5189 | 38.9139 | 73.3079 | 18.9065 | 349 | 74.4555 | 0 | 557.4216 | 0.017634
6994 | 1088.6854 | 10.7442 | 91.0672 | 132.5532 | 3.4891 | 16.1503 | 157.5531 | 7.3943 | 23.13 | 98.7688 | 176.5065 | 42.1419 | 386.1678 | 336.2333 | 589.3033 | 40.2942 | 81.9052 | 19.6848 | 371 | 79.0844 | 0 | 588.9305 | 0.025785
6995 | 1125.9644 | 10.8893 | 92.3732 | 135.1654 | 1.4928 | 18.0495 | 160.6375 | 7.7729 | 24.708 | 101.0909 | 184.1688 | 40.8365 | 405.1709 | 355.789 | 620.9885 | 41.0034 | 87.3517 | 19.8554 | 378 | 89.852 | 0 | 590.3943 | 0.029707
6996 | 1143.2766 | 13.2259 | 96.9299 | 137.7803 | -5.5057 | 24.6982 | 162.4894 | 7.7542 | 22.792 | 102.6993 | 183.3063 | 41.956 | 424.2375 | 365.0075 | 625.014 | 41.6236 | 89.1633 | 19.482 | 411 | 84.2192 | 0 | 603.6448 | 0.029979
6997 | 1154.3615 | 17.9247 | 99.3492 | 147.0066 | -3.507 | 22.8005 | 162.3432 | 6.5656 | 18.895 | 102.6568 | 181.6827 | 42.412 | 432.0626 | 364.0698 | 611.5249 | 44.2029 | 90.8976 | 20.4235 | 351 | 78.697 | 0 | 625.8821 | 0.029077
6998 | 1166.2244 | 14.2224 | 103.0914 | 148.0711 | -3.5059 | 22.8 | 166.3084 | 5.6259 | 21.482 | 98.6554 | 180.7651 | 41.108 | 432.6153 | 364.9043 | 603.3432 | 45.5286 | 92.528 | 21.0033 | 286 | 75.9559 | 0 | 626.568 | 0.024241
6999 | 1146.2663 | 7.691 | 102.7179 | 144.468 | 0.49423 | 19.0011 | 162.1789 | 5.5708 | 22.681 | 95.3278 | 178.5071 | 39.8594 | 440.1387 | 361.7816 | 588.6963 | 42.2941 | 91.8679 | 20.5638 | 296 | 72.3124 | 0 | 614.8129 | 0.015482
7000 | 1084.485 | 5.5547 | 98.3667 | 139.5016 | 4.4976 | 15.2011 | 154.6157 | 5.9444 | 19.932 | 95.4606 | 174.6426 | 38.6572 | 429.1463 | 346.0758 | 544.8404 | 34.7381 | 89.8976 | 20.2007 | 263 | 70.0796 | 0 | 586.5722 | 0.0058442
7001 | 1024.2156 | 4.7765 | 93.1792 | 126.0584 | 11.4944 | 8.5518 | 140.1577 | 5.1806 | 18.889 | 89.5234 | 162.2992 | 38.0197 | 401.8251 | 308.5034 | 480.9939 | 19.7093 | 84.2879 | 20.0951 | 228 | 64.9682 | 0 | 505.0255 | 0.00022081
7002 | 958.926 | 4.4711 | 86.1281 | 111.4713 | 9.5024 | 10.4495 | 121.9132 | 3.9931 | 18.875 | 77.9816 | 135.5467 | 34.9893 | 363.37 | 260.9352 | 421.1433 | 11.7344 | 76.6459 | 17.471 | 224 | 59.079 | 0 | 420.4937 | 0
7003 | 920.0372 | 3.811 | 76.9378 | 103.269 | 12.5009 | 7.6008 | 100.9103 | 3.901 | 17.005 | 71.8237 | 109.6102 | 26.5099 | 330.2766 | 229.7748 | 371.8554 | 10.2946 | 69.9026 | 11.4795 | 207 | 50.1463 | 0 | 357.3811 | 0
7004 | 892.617 | 3.5241 | 40.4153 | 100.2966 | 12.5015 | 7.6 | 91.5311 | 4.3753 | 12.164 | 66.7647 | 98.3998 | 18.9893 | 295.251 | 205.3645 | 321.5915 | 10.4401 | 62.9063 | 9.2427 | 196 | 43.6267 | 0 | 308.1092 | 0
7005 | 854.5867 | 3.6043 | 27.6427 | 98.5266 | 12.5003 | 7.6 | 87.8203 | 4.4616 | 8.981 | 54.2536 | 93.5256 | 13.0058 | 258.0455 | 173.5015 | 283.6314 | 10.1261 | 57.8417 | 7.8525 | 176 | 38.3519 | 0 | 287.4625 | 0
7006 | 825.1985 | 3.023 | 27.2697 | 97.1613 | 12.499 | 7.6 | 90.9476 | 4.141 | 7.912 | 39.8434 | 84.3946 | 9.0106 | 224.7159 | 147.3379 | 256.4209 | 9.669 | 55.8037 | 6.4457 | 144 | 33.871 | 0 | 276.207 | 0
7007 | 799.808 | 1.8917 | 27.1928 | 96.4509 | 12.4982 | 7.6 | 96.5448 | 3.1811 | 7.524 | 31.3919 | 74.0029 | 8.027 | 205.6571 | 132.9034 | 239.4367 | 9.1247 | 54.7715 | 5.7558 | 130 | 29.3883 | 0 | 269.6769 | 0
7008 | 781.4483 | 1.32 | 27.1235 | 97.5118 | 13.4992 | 6.6503 | 87.9327 | 2.738 | 7.286 | 27.912 | 69.8686 | 8.0202 | 198.025 | 126.511 | 228.2312 | 8.9698 | 54.2043 | 5.2788 | 127 | 28.6945 | 0 | 268.7154 | 0
7009 | 768.0423 | 1.2348 | 27.2509 | 97.7864 | 12.4991 | 7.5997 | 82.6082 | 3.3353 | 7.283 | 26.5745 | 69.5969 | 8.0258 | 194.5725 | 122.9484 | 227.7304 | 9.0444 | 54.2734 | 4.1152 | 120 | 28.9021 | 0 | 273.8734 | 0
7010 | 734.9864 | 1.2424 | 27.2398 | 97.469 | 14.4991 | 5.7005 | 81.7143 | 3.6615 | 7.366 | 26.4247 | 69.8422 | 8.911 | 195.01 | 116.3662 | 237.1149 | 9.0076 | 54.6272 | 3.5688 | 117 | 28.6618 | 0 | 275.9911 | 0
7011 | 730.1445 | 1.2945 | 27.2334 | 98.0656 | 14.5028 | 5.7 | 81.7952 | 3.9178 | 7.488 | 27.8918 | 69.9126 | 8.9071 | 192.9704 | 109.7961 | 241.2449 | 8.9125 | 54.7993 | 3.4864 | 117 | 27.5448 | 0 | 275.1973 | 0
7012 | 737.6366 | 1.7539 | 27.2698 | 98.0371 | 15.5009 | 4.7503 | 81.6605 | 3.653 | 7.537 | 34.1695 | 69.855 | 8.4538 | 189.6391 | 107.0605 | 232.4568 | 8.9651 | 55.3651 | 3.4634 | 115 | 29.2048 | 0 | 283.0921 | 0
7013 | 745.99 | 3.0954 | 39.5495 | 97.4989 | 15.4965 | 4.75 | 87.2651 | 2.6436 | 7.442 | 42.1869 | 70.5941 | 10.2495 | 192.1536 | 108.8631 | 224.145 | 8.857 | 57.5543 | 3.4638 | 117 | 30.1838 | 0 | 301.8543 | 0
7014 | 784.5905 | 4.9116 | 54.5675 | 101.8791 | 11.494 | 8.5489 | 101.8744 | 3.0492 | 7.869 | 48.5733 | 82.0986 | 16.229 | 201.9149 | 137.0455 | 239.3333 | 12.3712 | 57.4016 | 3.6148 | 184 | 39.3173 | 0 | 349.9683 | 0
7015 | 842.2401 | 5.8744 | 75.7141 | 104.3836 | 0.49283 | 18.9971 | 123.2571 | 4.6127 | 13.243 | 61.9822 | 109.4165 | 28.9122 | 238.0342 | 197.4899 | 311.9837 | 28.4498 | 58.7145 | 10.7747 | 270 | 45.7856 | 0 | 429.1806 | 0
7016 | 887.5716 | 6.0855 | 85.0144 | 122.2146 | -0.51081 | 19.9497 | 143.7652 | 5.6909 | 19.268 | 78.2573 | 137.2244 | 34.6327 | 300.9976 | 257.4168 | 417.9007 | 35.1174 | 66.8527 | 17.3952 | 324 | 63.5968 | 0 | 500.8775 | 0.01544
7017 | 953.1254 | 13.5338 | 91.0412 | 135.7776 | -6.5084 | 25.6484 | 163.1326 | 6.5299 | 21.88 | 92.3956 | 155.7923 | 38.7581 | 364.8552 | 301.7154 | 510.3198 | 41.0382 | 77.4934 | 19.1493 | 361 | 68.4232 | 0 | 543.8773 | 0.03707
7018 | 1003.7125 | 17.5135 | 93.9345 | 142.1199 | -3.5071 | 22.8008 | 170.2459 | 5.8134 | 20.697 | 103.5884 | 167.5698 | 42.1262 | 403.2339 | 334.8813 | 578.0534 | 42.57 | 87.629 | 19.8414 | 330 | 75.466 | 0 | 569.5299 | 0.039991
7019 | 1051.5843 | 8.116 | 98.2322 | 143.1207 | -2.5063 | 21.8503 | 172.3513 | 6.6303 | 20.57 | 104.3556 | 172.4421 | 43.0156 | 420.4849 | 360.1515 | 609.4341 | 43.2378 | 103.7057 | 20.2273 | 323 | 86.1988 | 0 | 583.8023 | 0.046875
7020 | 1069.3266 | 3.5421 | 100.0914 | 145.2155 | 4.5082 | 21.85 | 168.1664 | 7.5361 | 19.956 | 100.2532 | 172.3568 | 42.6088 | 434.5036 | 369.595 | 611.0716 | 43.8881 | 118.9761 | 20.0648 | 398 | 79.6926 | 0 | 592.7093 | 0.10807
7021 | 1066.3662 | 6.0414 | 100.0477 | 146.8488 | 22.7852 | 21.8561 | 158.2462 | 6.5376 | 19.142 | 97.2084 | 172.4217 | 42.7163 | 436.8102 | 367.4828 | 603.0052 | 44.8129 | 121.942 | 20.574 | 326 | 80.3073 | 0 | 590.9624 | 0.05003
7022 | 1074.2362 | 6.0734 | 100.381 | 147.2926 | 11.5784 | 20.8942 | 158.1132 | 6.2023 | 19.699 | 95.9746 | 171.3185 | 41.9952 | 448.6571 | 368.7342 | 596.8631 | 43.1352 | 120.786 | 20.8736 | 329 | 78.3122 | 0 | 578.1006 | 0.040363
7023 | 1046.7776 | 5.122 | 98.1457 | 142.912 | 0.18742 | 19.0005 | 148.4537 | 6.7928 | 19.859 | 95.1809 | 169.737 | 40.6929 | 439.5146 | 364.7986 | 598.1336 | 38.8 | 119.5319 | 20.9982 | 313 | 75.988 | 0 | 578.4103 | 0.018637
7024 | 1018.4929 | 4.7365 | 101.0333 | 137.4404 | 5.1727 | 14.2513 | 139.4731 | 6.1951 | 19.027 | 90.3162 | 169.5253 | 34.9344 | 438.9461 | 348.2171 | 581.3644 | 32.3856 | 116.696 | 20.7792 | 279 | 72.9551 | 0 | 554.9052 | 0.008472
7025 | 970.3636 | 4.9354 | 97.2817 | 123.244 | 11.169 | 8.5516 | 136.8182 | 4.3932 | 18.231 | 82.0083 | 161.2374 | 32.1503 | 414.3921 | 302.492 | 509.5759 | 17.043 | 109.9278 | 19.8945 | 229 | 67.1795 | 0 | 467.5387 | 0
7026 | 916.2448 | 4.753 | 90.4633 | 113.2986 | 11.1721 | 8.55 | 125.8487 | 3.6378 | 17.337 | 74.9994 | 136.9647 | 30.7761 | 370.513 | 232.9351 | 429.2458 | 9.8196 | 101.7631 | 17.4743 | 214 | 63.492 | 0 | 383.4295 | 0
7027 | 885.0451 | 4.6334 | 80.2259 | 109.6072 | 12.1738 | 7.6003 | 109.4624 | 4.5077 | 14.478 | 72.5728 | 111.5166 | 21.7974 | 325.2899 | 178.0187 | 383.1131 | 8.6558 | 96.3926 | 11.7435 | 202 | 58.8314 | 0 | 334.8829 | 0
7028 | 855.0473 | 4.1923 | 38.8864 | 106.6212 | 12.171 | 7.6 | 93.0936 | 2.7535 | 10.909 | 69.9373 | 100.1993 | 12.9316 | 289.7076 | 153.755 | 339.9181 | 8.5932 | 91.2229 | 8.2962 | 192 | 49.8214 | 0 | 299.1413 | 0
7029 | 828.6734 | 3.5724 | 18.913 | 103.8833 | 12.1723 | 7.6 | 86.8429 | 3.0494 | 9.374 | 56.8891 | 94.2801 | 8.0216 | 262.1666 | 143.2972 | 287.3258 | 8.4467 | 86.1042 | 6.9988 | 174 | 42.6343 | 0 | 279.7428 | 0
7030 | 794.4683 | 2.6865 | 16.1337 | 100.5644 | 13.1737 | 6.6503 | 90.0975 | 3.4872 | 9.772 | 39.5721 | 83.8627 | 9.5739 | 235.9149 | 127.5708 | 256.2985 | 8.531 | 83.2679 | 5.9992 | 157 | 38.8317 | 0 | 272.9564 | 0
7031 | 771.1111 | 1.8096 | 15.9954 | 100.9611 | 12.1711 | 7.5997 | 96.0316 | 3.3796 | 8.259 | 29.8661 | 74.5661 | 8.2436 | 216.8954 | 113.7324 | 243.8662 | 8.4508 | 81.7304 | 5.359 | 139 | 34.8885 | 0 | 266.96 | 0
7032 | 770.6266 | 1.3775 | 16.1866 | 101.1139 | 15.1711 | 4.7508 | 89.613 | 2.5017 | 6.569 | 26.3187 | 71.6905 | 6.3502 | 203.2724 | 109.4061 | 234.9384 | 8.5062 | 81.4887 | 5.1391 | 124 | 32.3099 | 0 | 263.0215 | 0
7033 | 756.2523 | 1.3361 | 15.903 | 98.8598 | 14.1742 | 5.6997 | 84.6503 | 3.1332 | 5.981 | 25.2283 | 71.4203 | 6.0301 | 194.8924 | 106.836 | 227.841 | 8.5362 | 81.7816 | 4.4994 | 122 | 31.2457 | 0 | 265.7677 | 0
7034 | 741.8954 | 1.3217 | 15.9995 | 98.3396 | 15.1707 | 4.7503 | 83.7319 | 3.6008 | 5.872 | 25.1693 | 71.7586 | 6.997 | 192.4388 | 103.4635 | 228.7971 | 8.4443 | 81.5087 | 3.6 | 119 | 29.79 | 0 | 264.0849 | 0
7035 | 741.6316 | 1.7265 | 15.8278 | 97.972 | 15.1721 | 4.75 | 84.1861 | 3.587 | 6.126 | 26.7019 | 72.1234 | 6.9891 | 191.6694 | 102.9606 | 230.029 | 8.4835 | 81.3843 | 3.3278 | 117 | 30.6725 | 0 | 258.6546 | 0
7036 | 739.2738 | 2.48 | 15.9685 | 98.5531 | 14.1743 | 5.6997 | 83.5608 | 3.5751 | 6.24 | 33.1091 | 71.3914 | 6.1927 | 191.4887 | 100.5452 | 224.5226 | 8.4735 | 82.0047 | 3.2911 | 119 | 30.3277 | 0 | 264.994 | 0
7037 | 745.3973 | 3.2481 | 29.8336 | 97.8545 | 15.1708 | 4.7503 | 88.5899 | 2.7537 | 6.24 | 41.3359 | 71.0904 | 7.2587 | 194.0025 | 96.2135 | 221.4039 | 8.398 | 84.3202 | 3.624 | 122 | 31.5332 | 0 | 295.5529 | 0
7038 | 783.0421 | 4.8639 | 49.1692 | 105.3027 | 8.1741 | 11.3982 | 102.6985 | 3.0305 | 7.136 | 48.2956 | 82.026 | 18.6516 | 202.8938 | 123.3302 | 239.0302 | 12.011 | 84.3842 | 6.5066 | 183 | 41.2502 | 0 | 348.6171 | 0
7039 | 829.3422 | 8.822 | 68.0586 | 108.9715 | -0.82372 | 19.9476 | 120.8266 | 4.3562 | 8.885 | 63.032 | 111.2377 | 33.614 | 235.9059 | 194.3329 | 310.4337 | 27.4535 | 84.5309 | 12.5842 | 246 | 45.8829 | 0 | 419.5818 | 0
7040 | 869.6079 | 8.8133 | 90.4794 | 122.5845 | 0.16498 | 19.0055 | 138.0121 | 5.5695 | 8.98 | 75.642 | 141.4204 | 41.0018 | 297.6322 | 268.2288 | 410.6086 | 35.973 | 91.3899 | 17.4684 | 315 | 65.0849 | 0 | 485.6922 | 0.021278
7041 | 968.5499 | 9.4723 | 96.4486 | 132.2289 | -2.8215 | 21.8439 | 154.0019 | 5.6895 | 10.898 | 82.1058 | 160.4822 | 41.6202 | 362.2037 | 318.3289 | 501.0605 | 40.1922 | 101.358 | 18.6211 | 374 | 70.4058 | 0 | 514.3593 | 0.048443
7042 | 1004.5323 | 10.1671 | 99.3322 | 140.4248 | -3.8258 | 22.7997 | 153.3321 | 5.5355 | 17.452 | 92.2312 | 174.6884 | 44.2195 | 407.4952 | 348.0327 | 566.5819 | 42.8524 | 109.771 | 19.549 | 365 | 72.2478 | 0 | 540.2696 | 0.094145
7043 | 1015.1131 | 7.9438 | 103.3236 | 141.5268 | -4.7955 | 23.7497 | 147.9383 | 6.119 | 26.492 | 100.5206 | 184.6431 | 45.8414 | 435.9176 | 363.9195 | 598.64 | 43.5927 | 113.8992 | 20.391 | 358 | 82.5927 | 0 | 578.6484 | 0.097072
7044 | 1035.3908 | 5.1134 | 103.2116 | 140.7741 | -0.79827 | 19.9511 | 138.9533 | 5.6523 | 25.55 | 102.8 | 187.3221 | 43.5611 | 443.6494 | 364.9577 | 603.5344 | 43.1016 | 112.9991 | 20.4725 | 375 | 76.755 | 0 | 586.6544 | 0.11623
7045 | 1036.6429 | 10.6027 | 105.663 | 146.0676 | -1.6991 | 21.8495 | 142.1021 | 4.4047 | 18.449 | 104.5145 | 186.5527 | 43.8475 | 442.905 | 363.7846 | 593.6008 | 44.6223 | 114.4748 | 20.6048 | 282 | 74.2284 | 0 | 594.8372 | 0.055341
7046 | 1042.1547 | 13.1046 | 107.0419 | 150.8744 | 22.9348 | 22.7997 | 149.6205 | 5.2126 | 25.697 | 107.5205 | 186.1796 | 44.6183 | 442.9431 | 370.6766 | 586.2972 | 45.3735 | 118.6407 | 20.6585 | 293 | 77.3815 | 0 | 602.7883 | 0.047788
7047 | 1026.4457 | 9.7075 | 103.4486 | 147.6891 | 19.3285 | 17.1016 | 160.1876 | 5.3798 | 28.025 | 108.1663 | 184.6031 | 41.3874 | 451.8003 | 372.1042 | 574.4078 | 42.0173 | 113.7553 | 20.7366 | 300 | 76.5413 | 0 | 598.436 | 0.02436
7048 | 999.4025 | 7.6872 | 96.9245 | 140.58 | 4.608 | 15.2005 | 155.3202 | 4.2052 | 21.912 | 105.3225 | 180.4463 | 34.284 | 472.5601 | 356.6016 | 535.5238 | 33.684 | 99.0314 | 20.1711 | 291 | 71.8089 | 0 | 550.6947 | 0.0071306
7049 | 956.5461 | 7.6569 | 92.0583 | 125.0628 | 11.4847 | 8.5518 | 137.5697 | 3.3232 | 18.01 | 94.2262 | 166.325 | 32.1547 | 521.9236 | 302.7828 | 465.7959 | 16.5133 | 83.2888 | 19.2942 | 281 | 70.9616 | 0 | 446.4645 | 0
7050 | 920.7431 | 5.5206 | 87.644 | 114.2637 | 12.4891 | 7.6003 | 120.6642 | 3.4111 | 17.698 | 79.212 | 136.2881 | 33.1227 | 508.9232 | 229.5806 | 404.7309 | 9.8181 | 72.8041 | 15.4944 | 259 | 61.3756 | 0 | 373.7267 | 0
7051 | 897.5502 | 4.3284 | 76.4972 | 108.1539 | 12.49 | 7.6 | 99.8547 | 3.7782 | 16.894 | 76.0102 | 109.576 | 27.3744 | 453.3746 | 187.2559 | 355.1784 | 9.1596 | 67.4633 | 9.8919 | 237 | 54.949 | 0 | 327.8323 | 0
7052 | 866.3352 | 4.2336 | 36.0768 | 104.3244 | 12.4889 | 7.6 | 88.2225 | 3.6719 | 14.359 | 78.4743 | 99.6162 | 18.9136 | 407.2775 | 166.8138 | 304.5611 | 9.2725 | 62.844 | 8.3243 | 202 | 49.59 | 0 | 291.6342 | 0
7053 | 832.7335 | 4.1314 | 22.2912 | 101.4018 | 12.4917 | 7.6 | 84.3188 | 2.6225 | 13.296 | 66.9165 | 95.1432 | 14.0804 | 380.7759 | 150.0463 | 259.3967 | 9.3158 | 58.3479 | 7.2174 | 221 | 45.8217 | 0 | 272.4534 | 0
7054 | 794.0848 | 3.0973 | 22.0561 | 98.2015 | 13.4973 | 6.6503 | 82.9559 | 3.0654 | 11.123 | 48.4818 | 88.6852 | 11.0706 | 357.752 | 136.6497 | 228.4358 | 9.1319 | 55.6602 | 6.2278 | 190 | 40.0515 | 0 | 263.0323 | 0
7055 | 772.9128 | 1.7431 | 22.0458 | 97.5835 | 12.4937 | 7.5997 | 82.4565 | 3.7346 | 9.569 | 37.8014 | 80.2118 | 9.851 | 340.2459 | 119.6674 | 225.6634 | 9.2882 | 54.5851 | 5.726 | 156 | 35.7851 | 0 | 258.998 | 0
7056 | 771.08 | 1.2571 | 22.1882 | 95.4738 | 12.4916 | 7.6 | 81.8288 | 3.9519 | 7.897 | 34.5271 | 74.2025 | 9.7373 | 331.4498 | 103.3085 | 233.323 | 9.7441 | 54.3644 | 5.3099 | 123 | 33.888 | 0 | 253.7231 | 0
7057 | 761.9853 | 1.2893 | 22.038 | 95.9801 | 12.4905 | 7.6 | 81.0218 | 3.9548 | 6.915 | 33.0286 | 72.7728 | 9.735 | 334.7509 | 94.8561 | 236.9258 | 9.9974 | 54.234 | 4.8636 | 112 | 33.4294 | 0 | 255.9333 | 0
7058 | 749.9275 | 1.2758 | 22.1903 | 94.5148 | 12.4898 | 7.6 | 80.4926 | 3.9698 | 6.736 | 32.0981 | 72.5591 | 10.3979 | 330.6071 | 93.5418 | 235.8902 | 9.6042 | 54.0797 | 3.9716 | 110 | 31.553 | 0 | 254.9636 | 0
7059 | 749.6178 | 1.7336 | 22.0225 | 97.1372 | 12.4907 | 7.6021 | 80.3261 | 4.2203 | 6.66 | 33.7363 | 71.7289 | 10.3877 | 325.9002 | 93.0268 | 230.0933 | 9.1657 | 54.0549 | 3.3662 | 117 | 30.8429 | 0 | 249.6412 | 0
7060 | 747.3137 | 2.103 | 22.0854 | 96.3135 | 15.4962 | 4.7487 | 80.371 | 4.0458 | 6.693 | 40.6143 | 71.0203 | 9.952 | 323.976 | 91.1562 | 223.5916 | 9.0754 | 54.9865 | 3.0824 | 130 | 29.8488 | 0 | 270.2067 | 0
7061 | 747.2663 | 2.693 | 37.9826 | 96.7299 | 14.4902 | 5.7013 | 86.6495 | 3.3354 | 6.594 | 46.7451 | 71.5694 | 10.5627 | 324.3721 | 94.3543 | 227.0819 | 8.9979 | 57.2648 | 2.9537 | 121 | 32.2479 | 0 | 312.005 | 0
7062 | 785.8461 | 6.4346 | 59.238 | 101.473 | 8.4939 | 11.3968 | 102.0124 | 3.0982 | 6.904 | 51.7441 | 82.1499 | 15.9282 | 332.2691 | 127.886 | 248.9089 | 13.064 | 57.4138 | 3.4947 | 194 | 50.5797 | 0 | 355.7646 | 0
7063 | 829.5449 | 11.1183 | 79.5999 | 106.3683 | 31.6295 | 19.9476 | 121.8858 | 5.21 | 12.226 | 70.3795 | 109.1301 | 29.339 | 369.0756 | 193.7683 | 316.3263 | 28.276 | 58.4657 | 12.0928 | 254 | 37.2893 | 0 | 415.658 | 0
7064 | 878.6421 | 11.4719 | 91.2569 | 117.1671 | 50.9991 | 20.8997 | 135.5833 | 7.3733 | 15.602 | 88.753 | 138.0582 | 37.0814 | 432.2657 | 259.1048 | 430.8575 | 36.8602 | 65.4062 | 17.9405 | 273 | 61.3078 | 0 | 483.7622 | 0.011278
7065 | 947.0326 | 7.1923 | 99.0434 | 129.9943 | 54.2816 | 19.0005 | 150.645 | 8.4133 | 17.815 | 92.7103 | 160.0691 | 39.958 | 491.1017 | 304.8012 | 534.3338 | 42.15 | 74.7076 | 17.5921 | 344 | 70.3378 | 0 | 526.9169 | 0.020174
7066 | 998.3409 | 4.1386 | 99.7634 | 141.7817 | 53.2995 | 20.8995 | 164.0018 | 8.3912 | 21.182 | 97.7395 | 174.3628 | 42.495 | 541.9485 | 334.9322 | 589.6907 | 43.2278 | 83.1662 | 19.2698 | 361 | 70.1021 | 0 | 558.3281 | 0.032909
7067 | 1020.0852 | 3.6394 | 103.723 | 144.9225 | 53.2703 | 20.9 | 165.6717 | 6.517 | 24.739 | 100.5761 | 179.2346 | 42.1973 | 564.4549 | 355.5866 | 609.2259 | 41.3478 | 86.747 | 20.1424 | 324 | 79.1676 | 0 | 594.1789 | 0.028743
7068 | 1015.9007 | 3.1485 | 103.3107 | 140.2696 | 54.5187 | 19.9503 | 164.7107 | 4.7132 | 23.75 | 94.0215 | 180.5907 | 40.7408 | 563.4583 | 358.9324 | 601.0108 | 42.3844 | 84.8697 | 20.4136 | 337 | 68.745 | 0 | 598.0216 | 0.069752
7069 | 1005.1875 | 3.0576 | 107.046 | 146.2427 | 59.6529 | 15.2013 | 166.5756 | 5.1183 | 20.612 | 87.4116 | 181.9375 | 40.8488 | 541.9247 | 353.9263 | 585.6041 | 44.3516 | 83.6984 | 20.4615 | 268 | 67.9685 | 0 | 597.4685 | 0.095962
7070 | 996.9116 | 3.3289 | 103.6274 | 147.1174 | 60.9151 | 14.2503 | 165.1109 | 5.5559 | 20.137 | 89.2803 | 181.9252 | 39.6954 | 563.5232 | 354.1929 | 586.3097 | 42.7538 | 84.6129 | 20.4593 | 271 | 71.6137 | 0 | 610.5003 | 0.056379
7071 | 988.3646 | 4.6279 | 101.7284 | 142.1502 | 61.4499 | 14.25 | 155.2904 | 5.1102 | 20.203 | 96.4323 | 179.7713 | 39.2193 | 575.3515 | 352.3029 | 582.9124 | 39.3584 | 85.2332 | 20.5215 | 297 | 67.2388 | 0 | 602.4678 | 0.02324
7072 | 961.2136 | 4.0996 | 98.8813 | 134.7258 | 66.786 | 9.5013 | 143.9729 | 4.5164 | 18.971 | 99.0083 | 177.5498 | 34.7885 | 548.3937 | 332.2301 | 543.5829 | 23.3671 | 84.3031 | 20.4526 | 267 | 65.694 | 0 | 539.2996 | 0.0077158
7073 | 938.742 | 4.6433 | 88.7518 | 121.1977 | 67.9668 | 7.6005 | 132.4052 | 3.5756 | 18.491 | 92.9347 | 166.5902 | 31.1264 | 435.0422 | 279.8207 | 468.257 | 12.8088 | 80.1515 | 19.2706 | 232 | 60.8051 | 0 | 433.2786 | 0
7074 | 921.1156 | 4.4802 | 73.257 | 111.2527 | 68.6769 | 4.7508 | 122.9286 | 3.6344 | 17.282 | 80.3437 | 139.0615 | 27.605 | 353.1572 | 220.5935 | 399.0365 | 9.6936 | 73.5399 | 16.6551 | 219 | 56.2754 | 0 | 349.4991 | 0
7075 | 896.1349 | 3.8413 | 58.9402 | 105.9631 | 59.4758 | 5.6997 | 107.5419 | 3.8406 | 15.423 | 72.8265 | 111.1494 | 19.8835 | 311.9154 | 185.821 | 357.659 | 9.4294 | 64.925 | 10.6785 | 199 | 49.9028 | 0 | 297.3745 | 0
7076 | 863.0485 | 3.4047 | 31.3598 | 101.4413 | 64.0779 | 4.7503 | 101.5338 | 4.1084 | 12.526 | 68.3877 | 94.3274 | 14.0819 | 276.2337 | 167.7912 | 330.3196 | 9.5473 | 58.2323 | 7.0639 | 189 | 41.6203 | 0 | 266.6176 | 0
7077 | 856.4645 | 3.2254 | 22.4014 | 100.0562 | 66.9291 | 5.6997 | 99.3816 | 4.0067 | 13.357 | 53.2943 | 85.3993 | 12.7123 | 261.8982 | 154.3814 | 298.4852 | 9.4473 | 56.2031 | 5.3525 | 184 | 39.5118 | 0 | 264.0529 | 0
7078 | 838.6832 | 2.7487 | 22.0707 | 98.4166 | 65.9704 | 4.7503 | 97.2987 | 3.9251 | 13.804 | 36.8848 | 82.0866 | 12.0471 | 241.4695 | 140.2965 | 271.5073 | 9.388 | 55.3326 | 4.6186 | 160 | 36.7316 | 0 | 264.2558 | 0
7079 | 821.2333 | 1.8562 | 22.1824 | 95.469 | 61.7483 | 5.6997 | 89.8966 | 3.9687 | 11.357 | 30.6155 | 80.9197 | 11.6605 | 226.3599 | 123.0188 | 260.1902 | 9.3952 | 54.4392 | 4.4812 | 139 | 35.6401 | 0 | 252.7492 | 0
7080 | 831.346 | 1.558 | 22.2405 | 95.5062 | 62.5627 | 5.7 | 93.0679 | 3.6057 | 8.494 | 30.0072 | 79.87 | 11.6846 | 213.3743 | 108.7147 | 251.6244 | 9.3558 | 54.1243 | 4.3709 | 122 | 34.7205 | 0 | 255.1472 | 0
7081 | 823.5179 | 1.7284 | 22.2661 | 93.6109 | 65.2165 | 4.7503 | 89.792 | 3.4072 | 7.417 | 29.6266 | 79.4495 | 11.7118 | 212.2194 | 102.2899 | 246.1968 | 9.2527 | 54.3569 | 3.7293 | 116 | 33.4835 | 0 | 268.8864 | 0
7082 | 802.9635 | 1.658 | 22.0443 | 96.0029 | 63.0012 | 5.6997 | 83.2428 | 3.3537 | 7.384 | 27.9167 | 79.8747 | 11.7017 | 210.2035 | 102.2184 | 248.4253 | 9.271 | 54.5425 | 2.8034 | 119 | 31.9799 | 0 | 274.7157 | 0
7083 | 813.9961 | 1.5426 | 22.0074 | 94.195 | 63.1043 | 4.7503 | 81.2785 | 3.785 | 7.238 | 27.875 | 80.3562 | 11.9645 | 207.7696 | 103.951 | 244.4457 | 9.4 | 54.4978 | 2.4958 | 114 | 32.1496 | 0 | 264.988 | 0
7084 | 804.5696 | 1.7995 | 21.8872 | 94.8525 | 62.2655 | 5.6997 | 74.7067 | 4.0554 | 7.433 | 33.6918 | 80.2775 | 11.7494 | 204.9667 | 98.6502 | 233.3991 | 9.187 | 55.221 | 2.4901 | 110 | 32.1325 | 0 | 253.4596 | 0
7085 | 805.6054 | 2.6749 | 22.4644 | 94.6297 | 62.8123 | 5.7016 | 72.2771 | 4.0574 | 7.291 | 39.0127 | 79.8798 | 11.5954 | 201.0389 | 91.6788 | 226.0317 | 9.2112 | 57.7929 | 2.5036 | 109 | 31.0421 | 0 | 255.5448 | 0
7086 | 821.1723 | 3.0521 | 37.2109 | 92.9798 | 60.3103 | 7.5979 | 78.4335 | 4.1517 | 7.565 | 34.9148 | 80.2868 | 11.6812 | 198.2146 | 91.2746 | 223.5364 | 9.3066 | 57.8079 | 2.5107 | 108 | 32.5724 | 0 | 260.4125 | 0
7087 | 828.5681 | 3.6034 | 46.6253 | 95.0694 | 60.0432 | 7.6 | 83.8521 | 4.3759 | 7.947 | 36.2931 | 84.2943 | 17.3718 | 202.0523 | 96.5409 | 224.4391 | 11.4996 | 55.1478 | 3.4074 | 119 | 50.9912 | 0 | 263.3892 | 0
7088 | 835.9789 | 3.8248 | 51.9425 | 96.362 | 61.5312 | 6.6503 | 80.0355 | 4.4161 | 11.351 | 52.2953 | 101.0615 | 23.8166 | 222.9726 | 105.5401 | 237.8674 | 12.6956 | 53.6339 | 5.6617 | 125 | 57.551 | 0 | 264.2969 | 0.0066461
7089 | 865.8977 | 3.3667 | 64.1406 | 98.0453 | 60.9266 | 7.5997 | 83.9198 | 6.7687 | 17.278 | 67.095 | 127.2733 | 27.2551 | 243.7601 | 117.2293 | 266.002 | 11.9542 | 53.038 | 9.5784 | 138 | 56.405 | 0 | 260.3463 | 0.0094078
7090 | 880.7861 | 2.0678 | 77.3502 | 96.1716 | 62.6375 | 6.6503 | 90.8904 | 5.9042 | 20.617 | 72.6174 | 142.455 | 26.4553 | 258.4235 | 129.4759 | 290.6663 | 11.6728 | 53.2295 | 15.9571 | 224 | 58.6429 | 0 | 261.3444 | 0.014493
7091 | 911.2298 | 1.6794 | 81.0074 | 95.1811 | 64.6844 | 5.7003 | 83.8563 | 4.5517 | 20.947 | 74.5734 | 130.4303 | 25.0604 | 267.4951 | 144.7961 | 304.1924 | 11.4946 | 55.0006 | 18.2212 | 206 | 60.3401 | 0 | 272.595 | 0.024093
7092 | 933.9829 | 1.5946 | 84.0007 | 96.63 | 65.3198 | 5.7 | 80.0247 | 3.8268 | 21.019 | 74.8767 | 114.3544 | 27.2198 | 273.0501 | 161.8356 | 316.5735 | 11.3868 | 58.438 | 18.4068 | 201 | 63.5341 | 0 | 279.3817 | 0.051584
7093 | 925.1216 | 1.5922 | 84.1717 | 96.73 | 66.4022 | 4.7503 | 90.0652 | 3.6834 | 18.797 | 73.2336 | 115.9706 | 29.0357 | 277.9578 | 171.6367 | 334.51 | 11.4455 | 60.0597 | 18.2321 | 212 | 63.1576 | 0 | 285.0723 | 0.057708
7094 | 927.0368 | 1.5025 | 82.6389 | 99.2863 | 65.0894 | 5.6997 | 91.4079 | 3.741 | 20.547 | 72.1339 | 114.3018 | 28.9386 | 279.1126 | 172.7812 | 338.7848 | 11.3497 | 57.1149 | 18.856 | 246 | 60.5166 | 0 | 292.9344 | 0.037842
7095 | 941.5243 | 2.9379 | 72.8435 | 96.6034 | 64.5456 | 5.7 | 74.1644 | 3.6745 | 20.453 | 69.1118 | 106.8956 | 28.9004 | 272.5267 | 174.3338 | 333.7997 | 11.418 | 53.5941 | 19.7239 | 261 | 59.947 | 0 | 300.8611 | 0.018925
7096 | 946.5394 | 3.7979 | 35.5046 | 94.7588 | 64.9764 | 4.7503 | 82.8914 | 3.6411 | 15.766 | 63.6784 | 104.7564 | 26.5201 | 266.7257 | 175.5807 | 337.3901 | 11.062 | 53.6488 | 19.9419 | 260 | 60.104 | 0 | 294.707 | 0.007174
7097 | 944.2465 | 3.9525 | 22.5943 | 98.7082 | 64.0726 | 5.6997 | 93.0057 | 4.1106 | 15.383 | 59.5121 | 103.7838 | 25.6281 | 262.3064 | 169.7319 | 353.4503 | 9.73 | 54.669 | 18.0154 | 255 | 59.853 | 0 | 280.4187 | 0
7098 | 919.6392 | 3.827 | 22.8401 | 100.634 | 64.1315 | 5.7 | 79.1351 | 4.3895 | 15.532 | 54.2846 | 97.6335 | 17.7957 | 258.7281 | 157.4287 | 352.4674 | 9.3116 | 54.6513 | 12.7273 | 260 | 47.437 | 0 | 280.0433 | 0
7099 | 894.4698 | 3.8993 | 22.7181 | 95.9022 | 65.0084 | 4.7503 | 70.8312 | 4.4185 | 14.486 | 52.3947 | 89.9063 | 9.7622 | 246.5196 | 146.4954 | 322.1999 | 9.4094 | 54.6517 | 9.765 | 288 | 41.334 | 0 | 281.5897 | 0
7100 | 877.7784 | 3.403 | 22.3256 | 96.3281 | 62.5549 | 6.6495 | 77.1332 | 4.4467 | 12.496 | 55.1387 | 90.4435 | 9.0935 | 232.4804 | 142.2723 | 288.0738 | 9.3275 | 54.9221 | 8.4671 | 321 | 38.5605 | 0 | 283.0314 | 0
7101 | 873.5311 | 3.0564 | 21.8946 | 94.0689 | 62.4583 | 6.65 | 77.5251 | 4.4873 | 9.581 | 51.1809 | 95.49 | 11.5165 | 219.6993 | 137.7162 | 267.9325 | 9.4716 | 54.9363 | 7.5021 | 272 | 36.0711 | 0 | 280.7872 | 0
7102 | 870.0697 | 2.8437 | 22.0815 | 96.2538 | 60.8435 | 7.5997 | 65.7171 | 4.806 | 8.238 | 44.258 | 92.1217 | 10.7384 | 211.1694 | 126.7427 | 255.8868 | 9.4299 | 54.9446 | 6.3901 | 229 | 34.4876 | 0 | 277.0973 | 0
7103 | 839.581 | 2.0199 | 21.9014 | 93.4048 | 60.9157 | 7.6 | 66.8681 | 4.7759 | 7.608 | 40.9466 | 82.8337 | 8.1681 | 203.633 | 113.5818 | 247.1079 | 9.5233 | 54.9187 | 5.44 | 185 | 32.1859 | 0 | 275.8354 | 0
7104 | 834.9496 | 1.7385 | 22.0043 | 92.7929 | 62.1976 | 7.6 | 73.5772 | 4.8955 | 8.537 | 38.2534 | 78.4658 | 7.3611 | 199.877 | 109.9602 | 241.1881 | 9.459 | 54.6792 | 4.7718 | 187 | 32.2839 | 0 | 272.2554 | 0
7105 | 830.1496 | 2.3726 | 21.8655 | 96.5792 | 63.0282 | 7.6 | 65.9943 | 4.8849 | 8.978 | 36.0769 | 78.362 | 6.6812 | 197.6072 | 109.1792 | 239.7986 | 9.5479 | 54.7118 | 4.3117 | 154 | 31.159 | 0 | 273.1254 | 0
7106 | 839.4812 | 2.1281 | 22.0524 | 96.7247 | 59.9868 | 10.4492 | 63.3058 | 4.887 | 7.175 | 34.7628 | 78.6931 | 6.3112 | 198.3092 | 102.8329 | 243.3529 | 9.4391 | 54.6908 | 4.0535 | 139 | 30.5241 | 0 | 275.7198 | 0
7107 | 837.1883 | 1.6199 | 21.9302 | 95.4756 | 60.4632 | 9.5003 | 72.0343 | 4.9312 | 6.851 | 33.6157 | 79.098 | 6.527 | 198.7674 | 97.2554 | 245.286 | 9.5796 | 54.1386 | 3.7885 | 131 | 30.4571 | 0 | 273.3028 | 0
7108 | 828.0083 | 1.8275 | 22.1122 | 95.2418 | 61.4393 | 8.5503 | 67.5316 | 5.1443 | 7.054 | 34.439 | 79.1333 | 6.2407 | 197.7413 | 94.8739 | 240.5273 | 9.4725 | 54.8227 | 3.5593 | 109 | 31.1981 | 0 | 271.5978 | 0
7109 | 829.2013 | 2.7237 | 22.6317 | 93.8845 | 64.1349 | 5.7008 | 62.026 | 4.982 | 6.822 | 35.5119 | 78.8147 | 5.9835 | 196.4098 | 94.38 | 236.1863 | 9.4888 | 57.1194 | 2.7779 | 105 | 31.3876 | 0 | 270.4003 | 0
7110 | 834.9559 | 3.2863 | 37.2422 | 97.382 | 63.9735 | 5.7 | 71.7734 | 4.8838 | 7.028 | 34.0485 | 79.4083 | 5.9604 | 193.154 | 95.5341 | 235.9611 | 9.3684 | 56.5452 | 2.3854 | 104 | 30.6387 | 0 | 271.7154 | 0
7111 | 850.3717 | 3.4023 | 46.5316 | 94.6213 | 64.385 | 4.7503 | 71.1578 | 4.8849 | 7.419 | 32.5919 | 79.8931 | 7.4968 | 187.8286 | 99.8749 | 241.5469 | 11.4364 | 54.5425 | 3.1163 | 117 | 33.4683 | 0 | 271.5602 | 0
7112 | 845.5712 | 3.1341 | 59.0213 | 92.7411 | 62.9243 | 5.6997 | 62.9665 | 4.6502 | 7.369 | 35.4816 | 81.3343 | 9.0951 | 186.927 | 108.1227 | 259.2189 | 12.0885 | 53.7394 | 5.515 | 117 | 38.6062 | 0 | 266.4375 | 0.0074971
7113 | 891.4127 | 1.7593 | 71.8871 | 92.3367 | 62.8323 | 5.7 | 80.3226 | 4.3702 | 8.574 | 43.3442 | 87.5042 | 9.3277 | 204.3795 | 118.212 | 285.1688 | 11.1758 | 52.897 | 9.214 | 150 | 40.4763 | 0 | 263.4513 | 0.019751
7114 | 936.4474 | 1.2646 | 78.7061 | 95.9794 | 62.1822 | 5.7 | 99.9864 | 4.3415 | 10.275 | 50.825 | 93.8517 | 9.7407 | 219.5547 | 131.7346 | 297.3975 | 10.7076 | 52.7748 | 16.3748 | 169 | 42.708 | 0 | 266.1567 | 0.036394
7115 | 955.1861 | 1.4257 | 78.7479 | 95.0543 | 61.2791 | 5.7 | 87.9761 | 3.2786 | 12.436 | 55.9717 | 95.7053 | 15.1027 | 231.6591 | 147.8212 | 299.1709 | 10.3052 | 52.9019 | 19.2212 | 172 | 44.3986 | 0 | 267.3702 | 0.042385
7116 | 954.0887 | 1.7246 | 80.8371 | 95.3568 | 60.5655 | 5.7 | 86.416 | 3.2029 | 15.411 | 63.0764 | 96.8073 | 19.9653 | 242.11 | 157.9397 | 308.0615 | 10.0476 | 53.8254 | 19.3304 | 173 | 50.0044 | 0 | 266.2017 | 0.053237
7117 | 950.5642 | 1.7405 | 81.4519 | 96.0575 | 58.6046 | 7.5995 | 102.9655 | 3.5956 | 16.247 | 66.8755 | 98.4603 | 21.5478 | 246.5888 | 160.413 | 320.0444 | 9.9587 | 55.0165 | 20.0108 | 170 | 52.6317 | 0 | 262.7187 | 0.043746
7118 | 932.98 | 1.7487 | 79.9049 | 104.1259 | 58.5197 | 7.6 | 104.2801 | 3.9579 | 16.498 | 68.2932 | 99.4975 | 22.3071 | 253.0397 | 161.4494 | 336.0615 | 9.7705 | 54.7168 | 20.1846 | 179 | 48.6936 | 0 | 264.6409 | 0.040403
7119 | 928.8362 | 1.7972 | 72.0162 | 101.352 | 58.3616 | 7.6 | 96.3957 | 4.0536 | 16.273 | 69.3669 | 108.7309 | 22.277 | 260.0751 | 161.2771 | 346.4818 | 9.8075 | 53.9826 | 20.2028 | 164 | 52.3288 | 0 | 264.941 | 0.024303
7120 | 943.5242 | 2.5297 | 45.3657 | 98.7619 | 59.4441 | 6.6503 | 97.1212 | 4.0354 | 13.306 | 61.1331 | 118.6281 | 22.5494 | 261.2473 | 163.4592 | 340.498 | 9.9983 | 54.5698 | 19.8373 | 168 | 51.1422 | 0 | 257.9793 | 0.01093
7121 | 945.7409 | 3.5434 | 36.4644 | 98.7211 | 60.3842 | 5.7003 | 100.3111 | 4.4497 | 16.265 | 50.688 | 112.2794 | 19.6798 | 253.2311 | 165.1913 | 339.234 | 9.132 | 55.4573 | 16.7033 | 169 | 51.4402 | 0 | 256.928 | 0
7122 | 940.0577 | 3.6395 | 36.3497 | 97.7735 | 60.5051 | 5.7 | 99.2743 | 4.705 | 17.406 | 49.156 | 101.5078 | 18.5132 | 249.6467 | 161.5571 | 343.8551 | 9.2621 | 55.7874 | 11.4009 | 161 | 47.8195 | 0 | 262.5796 | 0
7123 | 920.742 | 3.6295 | 36.3842 | 99.9199 | 61.2957 | 4.7503 | 90.8446 | 4.753 | 13.959 | 50.4246 | 96.7007 | 13.3267 | 246.9484 | 156.0148 | 331.1947 | 9.2945 | 55.5233 | 8.5035 | 159 | 43.9719 | 0 | 267.1966 | 0
7124 | 896.3225 | 3.4882 | 36.4709 | 98.0223 | 61.1339 | 5.6997 | 84.3039 | 4.5439 | 11.319 | 47.3391 | 89.1204 | 11.0855 | 232.3158 | 147.9866 | 297.8031 | 9.3771 | 55.0157 | 6.6979 | 136 | 40.9526 | 0 | 269.3607 | 0
7125 | 874.1455 | 3.4434 | 35.7674 | 96.9917 | 61.8218 | 4.7503 | 77.3013 | 4.3163 | 10.322 | 41.9692 | 79.6837 | 10.8343 | 217.7262 | 139.4507 | 274.1843 | 8.8398 | 54.6021 | 5.5799 | 135 | 38.6454 | 0 | 269.1842 | 0
7126 | 868.108 | 3.061 | 35.5428 | 94.4283 | 60.1435 | 5.6997 | 76.0497 | 4.161 | 8.506 | 38.0402 | 74.7229 | 9.0491 | 208.2425 | 128.5942 | 266.0564 | 8.4284 | 53.7548 | 4.982 | 127 | 38.1363 | 0 | 264.8618 | 0
7127 | 857.2986 | 1.8149 | 35.2968 | 93.884 | 61.1613 | 4.7503 | 78.5781 | 3.8388 | 6.914 | 36.8094 | 71.3464 | 6.5313 | 201.1325 | 116.0751 | 260.6686 | 8.5147 | 53.2532 | 4.4302 | 121 | 34.6118 | 0 | 260.4121 | 0
7128 | 853.2379 | 1.5134 | 35.368 | 94.5732 | 61.1538 | 4.75 | 78.9109 | 3.9898 | 6.334 | 36.1903 | 69.1184 | 5.9095 | 188.7551 | 107.8376 | 247.1612 | 8.4529 | 53.3776 | 4.202 | 121 | 32.9963 | 0 | 260.877 | 0
7129 | 839.9633 | 1.382 | 35.407 | 94.8171 | 57.4171 | 5.6997 | 79.787 | 3.8257 | 6.264 | 35.4767 | 69.0644 | 6.1806 | 179.5856 | 103.6785 | 234.5213 | 8.4975 | 53.4711 | 3.8317 | 109 | 30.0695 | 0 | 263.5837 | 0
7130 | 825.2968 | 1.2873 | 35.502 | 93.4502 | 51.3809 | 4.7503 | 79.5997 | 3.7533 | 6.424 | 34.9869 | 69.1437 | 6.8108 | 178.4678 | 103.9244 | 231.2113 | 8.4062 | 53.5424 | 3.0273 | 107 | 30.059 | 0 | 262.5419 | 0
7131 | 825.0232 | 1.4171 | 35.6298 | 94.3092 | 48.9203 | 5.6997 | 78.7023 | 3.9645 | 6.462 | 34.7675 | 68.6533 | 7.0136 | 173.6404 | 105.476 | 233.4075 | 8.468 | 53.5612 | 2.7181 | 103 | 30.5327 | 0 | 263.7204 | 0
7132 | 830.1161 | 1.7845 | 38.6306 | 95.6776 | 57.3151 | 4.7503 | 78.448 | 4.2001 | 6.345 | 39.3208 | 69.0103 | 6.1142 | 171.4091 | 99.7791 | 230.9978 | 8.8633 | 54.0836 | 2.6989 | 102 | 30.4366 | 0 | 284.7035 | 0
7133 | 827.6583 | 2.7302 | 38.9356 | 95.3811 | 51.644 | 7.5992 | 84.6015 | 4.3282 | 6.37 | 45.2827 | 70.7278 | 8.3921 | 176.6413 | 93.0674 | 229.2041 | 9.3115 | 56.2144 | 2.8074 | 103 | 32.2451 | 0 | 314.6311 | 0
7134 | 859.6215 | 4.5021 | 46.439 | 97.9512 | 48.9317 | 12.3487 | 97.6994 | 4.5073 | 6.68 | 52.6308 | 89.2102 | 15.7426 | 182.5912 | 124.6349 | 241.9459 | 14.0647 | 56.4337 | 3.6586 | 148 | 39.6282 | 0 | 354.2655 | 0
7135 | 916.9755 | 10.7026 | 73.459 | 104.3609 | 40.8259 | 24.6966 | 112.121 | 5.5944 | 11.987 | 75.7202 | 124.3713 | 31.121 | 218.9662 | 192.5727 | 299.2283 | 28.1785 | 58.3064 | 11.2713 | 253 | 52.6318 | 0 | 418.7968 | 0
7136 | 1016.2448 | 19.3825 | 91.269 | 113.5388 | 41.2017 | 24.7 | 138.2412 | 6.8606 | 18.207 | 99.3812 | 149.0121 | 38.0378 | 278.8076 | 257.0445 | 398.4463 | 36.4737 | 66.6835 | 17.3868 | 302 | 65.7648 | 0 | 479.5051 | 0.037964
7137 | 1077.5917 | 20.5838 | 100.3463 | 121.7852 | 43.6818 | 22.8005 | 159.8475 | 7.5808 | 22.349 | 105.9391 | 161.7308 | 39.7476 | 342.4325 | 302.188 | 502.8594 | 41.5415 | 75.3408 | 20.0752 | 346 | 68.9577 | 0 | 520.8587 | 0.14019
7138 | 1124.5033 | 15.2185 | 100.6932 | 129.2197 | 45.1495 | 22.8 | 154.9754 | 7.5779 | 23.124 | 107.0965 | 171.831 | 41.6145 | 387.7071 | 322.5945 | 576.8178 | 41.5788 | 82.378 | 19.6675 | 371 | 65.0544 | 0 | 560.2695 | 0.13132
7139 | 1152.1035 | 8.6988 | 101.5193 | 128.8175 | 46.0633 | 20.9005 | 159.4728 | 7.0687 | 23.283 | 107.695 | 175.8494 | 42.5057 | 400.5529 | 330.9704 | 596.9156 | 39.8571 | 87.5213 | 18.9722 | 313 | 66.3503 | 0 | 590.8342 | 0.18272
7140 | 1164.9331 | 6.146 | 99.4077 | 132.1192 | 45.7983 | 20.9 | 167.4323 | 5.8702 | 22.819 | 104.7503 | 175.7312 | 43.738 | 398.3325 | 336.4867 | 590.6243 | 40.5483 | 87.4654 | 19.4019 | 347 | 67.429 | 0 | 594.3523 | 0.14593
7141 | 1177.6229 | 4.8208 | 104.4371 | 136.4691 | 41.5175 | 24.6989 | 169.9016 | 5.3818 | 21.044 | 104.2944 | 175.2642 | 43.7777 | 386.833 | 336.207 | 588.6726 | 41.3448 | 88.4556 | 19.6367 | 296 | 69.1596 | 0 | 602.0946 | 0.16575
7142 | 1185.6172 | 4.021 | 103.2577 | 143.6659 | 47.4803 | 19.9513 | 169.689 | 5.917 | 21.314 | 106.2439 | 175.3237 | 39.269 | 387.994 | 332.4193 | 575.883 | 42.2423 | 99.7678 | 19.9254 | 271 | 65.1362 | 0 | 614.0192 | 0.15221
7143 | 1158.9166 | 4.9858 | 102.3324 | 138.8156 | 50.6162 | 17.1008 | 162.7035 | 6.3253 | 22.025 | 105.4149 | 177.0197 | 35.3774 | 394.3819 | 325.7239 | 561.759 | 40.5342 | 111.814 | 20.1991 | 262 | 67.3813 | 0 | 610.1189 | 0.084059
7144 | 1111.6961 | 4.1439 | 97.7311 | 130.9164 | 57.626 | 9.5021 | 152.6213 | 5.4116 | 22.223 | 103.9811 | 175.1329 | 33.5139 | 388.972 | 309.6409 | 535.3978 | 33.8087 | 114.1341 | 20.5006 | 241 | 67.8641 | 0 | 572.858 | 0.032197
7145 | 1061.785 | 4.8256 | 92.1714 | 117.5847 | 59.5693 | 8.5503 | 138.2667 | 4.7607 | 22.124 | 96.3358 | 161.674 | 33.3428 | 370.1574 | 270.3169 | 473.1735 | 17.972 | 109.6566 | 20.2553 | 203 | 66.8207 | 0 | 464.7215 | 0
7146 | 1025.4028 | 4.9283 | 89.8476 | 107.5299 | 55.442 | 11.3992 | 122.4317 | 4.0516 | 21.111 | 81.8401 | 134.6747 | 29.0021 | 339.696 | 218.7176 | 411.6934 | 10.6164 | 103.7381 | 17.3042 | 213 | 56.354 | 0 | 372.1924 | 0
7147 | 978.8208 | 4.3687 | 76.5981 | 105.4302 | 58.672 | 7.6011 | 104.2124 | 4.0976 | 14.995 | 73.1843 | 110.6152 | 17.2629 | 293.2787 | 185.3601 | 371.4749 | 9.5687 | 98.6147 | 11.9116 | 196 | 51.206 | 0 | 324.5299 | 0
7148 | 942.8101 | 3.9412 | 44.1199 | 101.8377 | 58.269 | 7.6 | 105.6369 | 3.9907 | 10.464 | 68.5677 | 101.262 | 13.2791 | 264.8514 | 169.0661 | 341.6561 | 9.6448 | 92.8693 | 9.4184 | 176 | 43.9539 | 0 | 293.5867 | 0
7149 | 907.2202 | 3.4185 | 29.0022 | 98.253 | 56.8089 | 8.5497 | 99.8611 | 3.8674 | 9.444 | 55.0794 | 96.8273 | 11.0827 | 243.3859 | 152.746 | 304.8908 | 9.7287 | 88.4989 | 8.1386 | 169 | 41.1891 | 0 | 287.1042 | 0
7150 | 869.0559 | 2.6558 | 26.8437 | 96.6658 | 58.877 | 6.6505 | 90.6357 | 3.8776 | 8.991 | 38.4233 | 87.3436 | 9.2617 | 215.539 | 133.9064 | 265.0709 | 9.5476 | 86.0261 | 6.7624 | 137 | 38.8001 | 0 | 273.8443 | 0
7151 | 844.6062 | 1.7237 | 26.7354 | 95.679 | 59.9595 | 5.7003 | 87.7825 | 4.0783 | 8.414 | 29.6554 | 77.2053 | 9.1257 | 198.3981 | 116.1719 | 234.0873 | 9.4718 | 84.493 | 5.7862 | 128 | 35.9081 | 0 | 265.7754 | 0
7152 | 846.5979 | 1.3053 | 26.7464 | 95.5346 | 60.1798 | 5.7 | 87.3149 | 3.4168 | 8.058 | 26.921 | 73.6889 | 9.0707 | 186.7675 | 101.1974 | 219.203 | 9.589 | 83.9261 | 5.3312 | 114 | 34.603 | 0 | 263.4462 | 0
7153 | 837.7673 | 1.4917 | 26.7777 | 96.7784 | 60.1541 | 5.7 | 86.5484 | 3.1318 | 7.833 | 25.9774 | 74.7193 | 9.1814 | 185.3642 | 91.0964 | 217.4284 | 9.5803 | 83.5996 | 5.0197 | 114 | 34.2164 | 0 | 260.8648 | 0
7154 | 823.9291 | 1.4909 | 26.7708 | 96.2064 | 61.1649 | 4.7503 | 85.0284 | 3.3185 | 7.854 | 25.7449 | 76.8185 | 9.1711 | 188.9224 | 86.321 | 222.1981 | 9.6436 | 83.7361 | 4.7997 | 110 | 33.0074 | 0 | 259.9013 | 0
7155 | 824.2621 | 1.3163 | 26.8255 | 95.6058 | 60.0529 | 5.6997 | 84.324 | 4.0621 | 7.89 | 27.3425 | 77.8364 | 9.0666 | 186.2736 | 85.555 | 232.6933 | 9.6002 | 83.9428 | 3.9192 | 106 | 32.4842 | 0 | 255.9793 | 0
7156 | 825.3021 | 1.708 | 26.8165 | 95.4718 | 59.9544 | 5.7 | 84.5117 | 4.0668 | 7.855 | 34.1564 | 77.7768 | 9.0099 | 180.4889 | 85.5117 | 239.8925 | 9.6027 | 84.442 | 3.4736 | 109 | 33.1286 | 0 | 263.9655 | 0
7157 | 836.6784 | 2.9647 | 29.411 | 95.9283 | 60.7961 | 4.7503 | 94.4073 | 3.9922 | 7.623 | 40.3419 | 76.5146 | 11.0434 | 183.6856 | 86.1748 | 241.0866 | 9.5299 | 86.2717 | 3.3391 | 122 | 33.9142 | 0 | 302.7161 | 0
7158 | 878.4882 | 4.4616 | 41.089 | 103.3479 | 58.5131 | 6.6495 | 107.639 | 4.5536 | 6.823 | 49.4089 | 86.5925 | 18.5669 | 192.4843 | 117.3137 | 245.0691 | 13.7685 | 86.1303 | 3.3093 | 186 | 36.7177 | 0 | 358.6295 | 0
7159 | 940.036 | 9.0477 | 73.6985 | 108.3544 | 52.5679 | 12.3484 | 118.3938 | 5.2014 | 10.769 | 75.3777 | 119.9833 | 30.3873 | 230.6362 | 183.85 | 289.4111 | 28.3794 | 87.7674 | 10.7165 | 264 | 51.3738 | 0 | 421.1198 | 0
7160 | 1023.5877 | 8.9746 | 92.2028 | 117.5945 | 50.0595 | 15.1992 | 144.842 | 7.74 | 17.021 | 100.0864 | 151.9892 | 33.6357 | 296.5154 | 247.1773 | 388.3535 | 35.2597 | 95.841 | 17.8979 | 295 | 69.292 | 0 | 487.8735 | 0
7161 | 1078.9134 | 9.5817 | 100.1982 | 128.6426 | 52.1237 | 14.2503 | 160.3709 | 7.728 | 20.383 | 105.2771 | 165.8111 | 32.4998 | 360.4174 | 291.2713 | 488.3337 | 39.6704 | 105.6764 | 18.7834 | 347 | 66.9021 | 0 | 523.4106 | 0.067857
7162 | 1118.0717 | 8.2266 | 101.4335 | 135.9016 | 51.3516 | 16.1495 | 152.5478 | 6.7725 | 20.73 | 102.5272 | 173.3533 | 33.6841 | 395.5762 | 314.7756 | 545.8473 | 39.6821 | 114.5349 | 18.7113 | 357 | 71.3536 | 0 | 543.1581 | 0.075711
7163 | 1159.4396 | 5.1169 | 103.8002 | 133.5248 | 53.6531 | 15.2003 | 153.7932 | 6.0985 | 20.792 | 102.436 | 178.1569 | 34.205 | 410.9131 | 326.0544 | 564.5372 | 40.7233 | 119.0907 | 19.3199 | 318 | 70.8563 | 0 | 568.8813 | 0.12628
7164 | 1161.437 | 4.9427 | 105.7442 | 132.7865 | 52.9892 | 16.1497 | 157.9076 | 6.4159 | 20.604 | 102.9627 | 179.345 | 36.4092 | 435.0396 | 333.7035 | 573.7587 | 40.2085 | 118.0275 | 19.9465 | 350 | 65.6688 | 0 | 572.6077 | 0.088889
7165 | 1150.1492 | 8.8449 | 104.0348 | 137.0997 | 52.8392 | 16.15 | 161.8175 | 6.4193 | 20.287 | 102.0378 | 181.8186 | 40.3169 | 446.2767 | 336.0817 | 581.2882 | 41.0192 | 116.6334 | 20.2275 | 337 | 62.0128 | 0 | 572.3002 | 0.094761
7166 | 1162.3587 | 10.1376 | 101.558 | 138.179 | 52.9558 | 16.15 | 166.3796 | 6.2631 | 21.635 | 99.3174 | 184.1696 | 40.9201 | 447.9775 | 336.715 | 576.0694 | 41.4191 | 112.3944 | 20.0541 | 274 | 63.6352 | 0 | 573.5468 | 0.078549
7167 | 1141.244 | 7.0432 | 101.2164 | 134.7153 | 53.0749 | 16.15 | 163.3409 | 5.6811 | 22.789 | 97.7994 | 184.6048 | 40.8847 | 464.2057 | 336.4964 | 558.5778 | 38.6958 | 99.4314 | 19.7301 | 277 | 63.334 | 0 | 566.1487 | 0.055171
7168 | 1119.2832 | 5.5317 | 99.0151 | 128.9839 | 54.2522 | 14.2505 | 153.9339 | 5.4437 | 22.873 | 96.8986 | 182.8244 | 40.9032 | 464.5952 | 325.8348 | 519.2761 | 32.6995 | 86.7094 | 19.5694 | 257 | 66.4366 | 0 | 538.9613 | 0.019878
7169 | 1076.3221 | 5.4406 | 93.1921 | 117.2412 | 60.7636 | 7.6018 | 139.8197 | 5.5555 | 22.649 | 90.4273 | 169.7093 | 39.3724 | 441.2959 | 289.4881 | 450.9345 | 15.4824 | 80.137 | 19.1275 | 232 | 65.7312 | 0 | 472.8619 | 0
7170 | 1038.0091 | 5.4055 | 88.3796 | 107.9197 | 62.5328 | 5.7005 | 126.4289 | 5.4147 | 22.377 | 75.7682 | 140.7923 | 31.2819 | 391.9584 | 235.3325 | 385.061 | 9.02 | 79.3031 | 16.2002 | 216 | 55.0496 | 0 | 399.8439 | 0
7171 | 996.3768 | 5.0906 | 72.8917 | 104.9015 | 62.5929 | 5.7 | 114.9848 | 4.7786 | 14.695 | 63.0882 | 113.4141 | 15.2009 | 339.3561 | 192.1284 | 358.2925 | 8.7652 | 77.3223 | 10.2117 | 183 | 49.4231 | 0 | 339.1599 | 0
7172 | 943.7505 | 4.0954 | 30.535 | 100.3838 | 63.6929 | 4.7503 | 109.261 | 4.2875 | 9.34 | 58.1459 | 106.7524 | 9.6698 | 298.9201 | 163.6573 | 340.7569 | 9.2914 | 69.4192 | 7.2209 | 168 | 42.6984 | 0 | 301.3605 | 0
7173 | 912.9773 | 3.5057 | 15.4418 | 97.8815 | 62.8611 | 5.6997 | 101.7018 | 4.2689 | 8.153 | 48.7202 | 112.3715 | 9.2722 | 267.6925 | 149.1563 | 304.2532 | 9.5043 | 63.128 | 6.3732 | 157 | 39.4139 | 0 | 287.5701 | 0
7174 | 888.4775 | 2.8582 | 15.0773 | 95.9674 | 63.5783 | 4.7516 | 85.8036 | 4.2775 | 7.624 | 36.3619 | 101.9975 | 9.157 | 238.4479 | 139.0308 | 264.3657 | 9.5542 | 60.9518 | 5.8584 | 135 | 38.1875 | 0 | 277.6278 | 0
7175 | 860.7699 | 1.7755 | 15.0644 | 95.2973 | 62.6649 | 5.6984 | 70.811 | 4.1042 | 7.429 | 30.0034 | 81.1078 | 9.2184 | 220.4034 | 126.7395 | 243.3785 | 9.5878 | 60.8544 | 5.5098 | 121 | 35.756 | 0 | 275.5096 | 0
7176 | 849.204 | 1.3822 | 15.0072 | 94.4454 | 63.3045 | 4.7503 | 77.2799 | 3.6922 | 7.322 | 28.3834 | 73.5966 | 8.85 | 212.0567 | 120.1314 | 237.7545 | 9.4488 | 60.3234 | 4.8845 | 113 | 32.555 | 0 | 277.0662 | 0
7177 | 848.9211 | 1.4558 | 14.9336 | 94.8507 | 62.6869 | 5.6997 | 82.4018 | 3.5665 | 7.147 | 28.208 | 73.2623 | 8.7739 | 208.2318 | 118.1924 | 238.5016 | 9.5553 | 59.3014 | 4.0291 | 112 | 29.8262 | 0 | 279.9433 | 0
7178 | 836.3027 | 1.3947 | 15.0323 | 95.5352 | 62.5677 | 5.7 | 77.133 | 3.9662 | 7.146 | 28.3 | 72.9595 | 8.961 | 206.326 | 116.0628 | 242.092 | 9.6631 | 59.0209 | 3.6563 | 109 | 29.6992 | 0 | 283.6305 | 0
7179 | 834.2829 | 1.4272 | 14.9273 | 95.1928 | 60.4556 | 7.5995 | 66.3802 | 4.2802 | 7.149 | 29.6647 | 72.5956 | 8.7493 | 204.5373 | 111.5759 | 239.2528 | 9.5741 | 58.9965 | 3.4681 | 106 | 29.8664 | 0 | 286.7008 | 0
7180 | 831.7905 | 1.8265 | 14.8767 | 94.2835 | 59.6615 | 7.6 | 69.8154 | 4.7454 | 7.189 | 35.458 | 72.5618 | 8.5905 | 202.9113 | 108.0343 | 227.5158 | 9.5878 | 59.6812 | 3.4211 | 106 | 29.9408 | 0 | 294.9659 | 0
7181 | 836.2204 | 3.0751 | 26.1876 | 94.9363 | 59.2281 | 7.6 | 84.5659 | 4.7881 | 7.336 | 40.9942 | 74.1744 | 10.9321 | 205.7248 | 110.5968 | 223.0926 | 9.5434 | 61.8679 | 3.4368 | 105 | 31.8117 | 0 | 326.8819 | 0
7182 | 870.764 | 4.5993 | 37.4271 | 102.2351 | 50.8925 | 16.1476 | 96.9416 | 4.8296 | 9.007 | 47.9279 | 87.577 | 22.198 | 202.1915 | 132.7851 | 235.7362 | 13.606 | 62.0524 | 3.4205 | 178 | 38.362 | 0 | 371.0763 | 0
7183 | 936.5939 | 9.812 | 63.7083 | 104.3123 | 45.9175 | 22.7982 | 111.1061 | 5.7443 | 9.791 | 71.8258 | 115.4016 | 38.2909 | 224.6966 | 183.3692 | 284.9108 | 29.3518 | 64.8702 | 9.9983 | 311 | 50.6665 | 0 | 416.4854 | 0
7184 | 1007.6862 | 11.6415 | 86.1929 | 117.7768 | 47.315 | 20.9005 | 130.6178 | 7.1578 | 13.61 | 99.1926 | 146.0923 | 39.8101 | 295.5301 | 245.9266 | 370.6995 | 37.1909 | 74.1498 | 16.1049 | 322 | 64.0605 | 0 | 478.3586 | 0
7185 | 1097.6415 | 14.2739 | 97.1417 | 133.6694 | 46.5323 | 21.8497 | 157.4978 | 7.0133 | 20.76 | 110.3014 | 166.9849 | 39.0131 | 366.4931 | 295.0459 | 470.7758 | 42.6153 | 83.5804 | 18.4315 | 360 | 63.1296 | 0 | 532.6134 | 0.032329
7186 | 1149.1996 | 18.411 | 97.6848 | 139.1085 | 44.1702 | 23.7495 | 160.4623 | 6.9178 | 23.158 | 110.8606 | 177.4184 | 41.8334 | 414.5445 | 321.495 | 545.3869 | 41.8108 | 93.732 | 19.1682 | 315 | 58.6726 | 0 | 552.4549 | 0.079488
7187 | 1159.6154 | 12.5237 | 99.4591 | 142.0651 | 44.3738 | 23.75 | 150.4561 | 5.7619 | 22.932 | 109.8426 | 182.8246 | 43.024 | 436.2669 | 333.7569 | 571.0246 | 41.1773 | 108.6244 | 19.1841 | 374 | 81.2905 | 0 | 569.0106 | 0.095856
7188 | 1154.8951 | 5.917 | 102.1598 | 141.0142 | 44.3345 | 22.8003 | 156.2156 | 6.1967 | 22.389 | 110.4793 | 183.2349 | 44.1203 | 437.3245 | 337.4315 | 569.7517 | 43.2428 | 119.7237 | 19.4268 | 400 | 85.6709 | 0 | 586.5406 | 0.11633
7189 | 1146.0096 | 3.5892 | 103.2997 | 141.8302 | 43.256 | 22.8 | 174.4766 | 6.6053 | 21.633 | 112.4013 | 182.8009 | 45.2322 | 430.1301 | 336.5171 | 557.5701 | 44.4393 | 122.4891 | 19.8832 | 371 | 69.9121 | 0 | 587.896 | 0.092016
7190 | 1158.0845 | 3.2085 | 103.0551 | 138.6043 | 44.1224 | 21.8563 | 179.3794 | 6.7351 | 23.581 | 111.4727 | 181.5696 | 43.6798 | 440.7896 | 331.6642 | 547.1241 | 44.1361 | 123.4791 | 19.8058 | 300 | 68.3414 | 0 | 576.0228 | 0.094261
7191 | 1150.0758 | 4.0931 | 100.9768 | 137.369 | 47.8839 | 18.9947 | 171.0576 | 6.4465 | 24.625 | 108.264 | 177.5787 | 41.0121 | 447.1035 | 324.4335 | 534.9613 | 40.496 | 123.6982 | 19.3665 | 286 | 91.9574 | 0 | 567.9542 | 0.046503
7192 | 1125.2908 | 5.0083 | 95.8615 | 130.1307 | 57.9186 | 10.4524 | 156.1495 | 5.75 | 23.487 | 103.2988 | 171.9196 | 39.0809 | 440.9707 | 311.0341 | 497.2412 | 33.5557 | 121.2149 | 18.9587 | 259 | 92.2951 | 0 | 542.8176 | 0.010517
7193 | 1067.3639 | 5.2604 | 90.5166 | 119.2002 | 58.6786 | 9.5003 | 144.3788 | 4.8111 | 22.728 | 93.0608 | 159.8054 | 38.5354 | 435.9739 | 274.0751 | 428.7292 | 17.5238 | 113.4361 | 18.5795 | 223 | 87.0245 | 0 | 475.3251 | 0
7194 | 1004.1065 | 5.0737 | 85.064 | 107.5839 | 55.5916 | 12.3492 | 131.0037 | 4.6948 | 22.34 | 77.9974 | 134.9307 | 32.2516 | 390.7951 | 219.6986 | 372.5302 | 10.8569 | 103.3372 | 16.3506 | 221 | 81.7788 | 0 | 408.9501 | 0
7195 | 958.0036 | 4.6264 | 73.198 | 103.7915 | 59.4479 | 8.5511 | 121.2912 | 5.6435 | 16.046 | 67.3233 | 111.9075 | 16.5208 | 331.1399 | 173.8083 | 346.2589 | 9.8955 | 96.3174 | 10.6865 | 199 | 74.7935 | 0 | 348.136 | 0
7196 | 918.2224 | 4.306 | 35.5987 | 100.9983 | 59.4363 | 8.55 | 119.2783 | 4.5396 | 9.991 | 63.0979 | 102.6072 | 12.1387 | 294.3288 | 145.9454 | 321.4347 | 9.6253 | 83.9355 | 7.413 | 187 | 57.4074 | 0 | 309.4663 | 0
7197 | 892.0521 | 4.2527 | 22.6852 | 101.9162 | 63.0897 | 5.7008 | 106.4909 | 3.1477 | 8.138 | 51.7928 | 98.2199 | 15.4914 | 262.4226 | 125.2777 | 290.7094 | 9.5713 | 65.622 | 6.2737 | 167 | 48.5573 | 0 | 293.9688 | 0
7198 | 868.752 | 3.0209 | 22.4482 | 97.599 | 61.7328 | 5.7 | 98.9903 | 3.6548 | 7.746 | 36.8393 | 89.467 | 14.5064 | 233.7491 | 107.6652 | 264.4593 | 9.7135 | 54.7923 | 5.4225 | 137 | 39.5891 | 0 | 284.8791 | 0
7199 | 835.3728 | 1.8666 | 22.5168 | 96.6222 | 60.8234 | 5.7 | 90.1857 | 4.0143 | 7.146 | 28.4881 | 79.7521 | 12.8303 | 212.1983 | 100.2183 | 251.6845 | 9.5106 | 52.0562 | 5.213 | 130 | 36.8588 | 0 | 278.111 | 0
7200 | 834.2901 | 1.417 | 22.2828 | 96.9124 | 62.4181 | 4.7503 | 85.1879 | 4.155 | 6.846 | 25.8007 | 76.0818 | 12.153 | 203.37 | 99.2977 | 236.3999 | 9.5632 | 51.8628 | 4.796 | 126 | 37.7106 | 0 | 272.4531 | 0
7201 | 826.5713 | 1.5046 | 22.1935 | 97.9545 | 61.7542 | 5.6997 | 84.4811 | 4.0058 | 6.782 | 25.2762 | 75.7245 | 12.1037 | 198.0303 | 96.8129 | 223.8888 | 9.4564 | 51.8893 | 3.8976 | 128 | 35.5607 | 0 | 274.778 | 0
7202 | 815.7384 | 1.4934 | 21.9448 | 99.1809 | 63.3878 | 4.7503 | 84.1415 | 3.1901 | 6.812 | 25.2866 | 75.9807 | 12.7872 | 195.0894 | 93.665 | 222.2973 | 9.6331 | 52.3149 | 3.6059 | 126 | 35.8617 | 0 | 273.91 | 0
7203 | 821.1613 | 1.3327 | 21.7602 | 99.5586 | 62.8092 | 5.6997 | 83.7575 | 3.2247 | 6.697 | 26.704 | 76.098 | 12.5686 | 194.6653 | 91.7663 | 221.9576 | 9.5905 | 52.5708 | 3.2746 | 121 | 33.9252 | 0 | 273.0558 | 0
7204 | 832.292 | 1.6553 | 21.6376 | 98.7166 | 63.1954 | 4.7503 | 83.9312 | 3.6808 | 6.738 | 33.0324 | 75.5707 | 12.1236 | 192.0062 | 89.3907 | 216.3902 | 9.6566 | 53.0463 | 3.0649 | 115 | 35.5539 | 0 | 279.142 | 0
7205 | 844.5719 | 3.0177 | 36.4369 | 99.6058 | 61.8638 | 5.7013 | 89.254 | 3.7513 | 6.899 | 41.2855 | 75.7547 | 13.5983 | 193.9525 | 88.5156 | 218.3246 | 9.6392 | 55.0835 | 3.1662 | 112 | 34.1329 | 0 | 304.1207 | 0
7206 | 883.134 | 4.5643 | 54.6793 | 105.8427 | 58.861 | 9.4974 | 87.14 | 4.0567 | 7.839 | 48.2091 | 87.4645 | 20.0358 | 203.1506 | 115.4371 | 234.757 | 13.0125 | 55.1334 | 4.1837 | 192 | 40.6967 | 0 | 344.5075 | 0
7207 | 942.6525 | 8.8513 | 78.8944 | 111.2506 | 48.1312 | 18.9974 | 95.8724 | 3.9024 | 11.02 | 69.9473 | 115.6238 | 34.3948 | 234.8761 | 179.6942 | 289.0366 | 27.6671 | 56.6365 | 12.6409 | 302 | 56.2297 | 0 | 390.1512 | 0
7208 | 1015.6576 | 7.1694 | 91.5984 | 119.9154 | 47.0068 | 20.9053 | 120.3629 | 5.5332 | 14.089 | 96.9364 | 144.0481 | 37.0206 | 292.3052 | 243.1047 | 395.9198 | 37.066 | 63.8305 | 16.245 | 323 | 65.5752 | 0 | 450.782 | 0
7209 | 1098.1257 | 4.1763 | 98.4469 | 129.5216 | 46.668 | 20.8942 | 136.8244 | 5.8966 | 19.965 | 104.9317 | 167.9938 | 38.116 | 347.6666 | 282.8726 | 499.4573 | 41.8549 | 73.5246 | 17.5046 | 394 | 65.005 | 0 | 510.2513 | 0.1411
7210 | 1142.2439 | 4.689 | 100.6225 | 131.9089 | 45.4261 | 22.7995 | 143.2113 | 5.6386 | 23.232 | 103.9017 | 184.9775 | 40.6044 | 383.6834 | 305.9748 | 553.6073 | 43.9637 | 81.5218 | 18.7506 | 391 | 61.3165 | 0 | 554.8871 | 0.14842
7211 | 1164.8504 | 5.6596 | 103.3265 | 136.9086 | 46.6676 | 21.8503 | 150.318 | 4.9184 | 23.763 | 105.9972 | 187.4261 | 43.199 | 399.7509 | 322.9754 | 575.2654 | 43.3586 | 84.9472 | 18.9158 | 371 | 63.1875 | 0 | 578.9587 | 0.16377
7212 | 1165.1469 | 6.1168 | 104.5446 | 134.8952 | 50.2417 | 21.85 | 146.9588 | 5.233 | 23.279 | 109.2681 | 183.3375 | 43.1419 | 409.3634 | 319.4501 | 584.1409 | 43.597 | 85.1508 | 18.8416 | 371 | 59.6237 | 0 | 579.5381 | 0.16616
7213 | 1178.0013 | 5.9724 | 104.5185 | 141.8886 | 54.7943 | 21.85 | 145.5924 | 5.0393 | 20.379 | 111.3568 | 183.758 | 42.4354 | 408.8985 | 310.6637 | 587.152 | 43.5237 | 88.3257 | 18.6072 | 341 | 59.3041 | 0 | 575.3873 | 0.21908
7214 | 1169.9051 | 5.6263 | 101.908 | 152.2399 | 61.0265 | 19.9505 | 149.8018 | 4.9339 | 21.9283 | 113.4942 | 186.7167 | 42.6237 | 415.6097 | 314.649 | 577.9009 | 42.9338 | 100.5114 | 18.4717 | 320 | 62.8704 | 0 | 574.0414 | 0.18538
7215 | 1130.0771 | 7.339 | 99.0439 | 145.0167 | 60.2052 | 17.1055 | 144.4371 | 5.5018 | 23.5715 | 112.6968 | 186.1764 | 43.1314 | 436.621 | 311.2339 | 562.7203 | 40.3458 | 110.0709 | 18.1582 | 292 | 65.5517 | 0 | 571.0522 | 0.12011
7216 | 1105.337 | 11.0065 | 94.21 | 137.2927 | 64.6195 | 9.4974 | 135.6588 | 4.8829 | 23.8172 | 109.6438 | 182.779 | 41.7235 | 432.1039 | 299.7532 | 535.6756 | 33.1469 | 109.2924 | 17.5546 | 259 | 68.714 | 0 | 531.3804 | 0.011127
7217 | 1053.4679 | 8.4972 | 90.1792 | 127.3394 | 64.4658 | 8.5526 | 118.1307 | 4.4446 | 23.791 | 101.4924 | 168.4127 | 41.3325 | 412.2372 | 264.3725 | 482.6618 | 17.045 | 103.6571 | 17.2104 | 234 | 67.4541 | 0 | 447.8282 | 0
7218 | 1009.2882 | 5.0207 | 87.6522 | 115.737 | 64.4671 | 7.5979 | 105.3162 | 4.1864 | 22.888 | 84.8601 | 137.7573 | 37.9428 | 371.1349 | 209.1616 | 420.692 | 10.3113 | 96.6889 | 14.4205 | 222 | 56.182 | 0 | 373.6931 | 0
7219 | 956.109 | 4.1423 | 73.7988 | 112.3152 | 65.2637 | 6.6503 | 89.5498 | 2.7934 | 13.403 | 73.0174 | 110.6823 | 34.9522 | 328.1176 | 164.5014 | 382.7988 | 9.6976 | 81.7392 | 8.6591 | 214 | 48.8212 | 0 | 317.4901 | 0
7220 | 930.5782 | 3.9846 | 34.969 | 106.048 | 67.3811 | 4.7505 | 81.0286 | 3.0873 | 8.17 | 67.3827 | 101.9851 | 31.6726 | 295.627 | 133.4009 | 347.1757 | 9.6784 | 63.0696 | 6.1356 | 191 | 42.4591 | 0 | 280.0477 | 0
7221 | 902.6899 | 3.4432 | 22.0541 | 104.0654 | 67.1954 | 4.75 | 72.0546 | 3.531 | 7.684 | 53.4836 | 100.1926 | 18.1388 | 271.9542 | 118.7603 | 304.0631 | 9.4961 | 54.7788 | 5.0852 | 174 | 38.3916 | 0 | 267.9917 | 0
7222 | 860.0201 | 2.7244 | 21.6458 | 103.4194 | 66.4301 | 5.6997 | 66.701 | 2.8029 | 7.566 | 36.7908 | 90.8766 | 11.8397 | 243.9655 | 109.5537 | 274.7355 | 9.6595 | 52.2055 | 4.3633 | 148 | 36.1464 | 0 | 261.2135 | 0
7223 | 838.2628 | 1.8113 | 21.4673 | 100.1256 | 67.5864 | 4.7516 | 63.0797 | 3.0392 | 7.311 | 29.2441 | 78.5803 | 11.2285 | 228.1978 | 101.141 | 254.6691 | 9.5513 | 50.2532 | 3.6089 | 134 | 36.5628 | 0 | 258.8862 | 0
7224 | 842.4865 | 1.7294 | 21.4033 | 99.6817 | 66.7437 | 4.7487 | 59.8799 | 3.4276 | 7.335 | 27.9444 | 73.9037 | 10.3647 | 213.0959 | 97.8292 | 243.8381 | 9.6392 | 49.7272 | 3.0332 | 127 | 38.8269 | 0 | 257.8849 | 0
7225 | 822.0786 | 1.6948 | 21.3207 | 98.9415 | 65.4792 | 4.75 | 53.6244 | 2.9192 | 7.436 | 27.8029 | 73.5292 | 9.8333 | 206.157 | 92.5524 | 236.4971 | 9.5461 | 49.8712 | 2.7321 | 120 | 38.8908 | 0 | 257.2848 | 0
7226 | 806.6985 | 1.7241 | 21.3166 | 99.1866 | 64.5366 | 5.6997 | 57.4278 | 2.754 | 7.313 | 27.7017 | 73.2047 | 9.8891 | 206.5731 | 85.6198 | 231.589 | 9.4993 | 49.7075 | 3.0322 | 117 | 36.1442 | 0 | 258.394 | 0
7227 | 818.587 | 1.4413 | 21.2857 | 98.8761 | 65.6187 | 5.7 | 58.9911 | 3.4992 | 7.383 | 29.2428 | 72.502 | 9.8331 | 205.5727 | 81.2876 | 228.7596 | 9.5609 | 49.4809 | 3.1982 | 118 | 35.8878 | 0 | 259.1394 | 0
7228 | 823.4669 | 1.6517 | 21.1549 | 99.7539 | 63.2395 | 7.5995 | 59.4692 | 3.9377 | 7.405 | 35.8704 | 72.1764 | 9.7625 | 205.5236 | 80.2035 | 222.3569 | 9.561 | 50.1248 | 3.2259 | 117 | 35.2264 | 0 | 266.0363 | 0
7229 | 831.6224 | 2.959 | 37.4258 | 99.2878 | 64.1607 | 6.6503 | 65.2503 | 2.9151 | 7.453 | 42.0155 | 72.7833 | 10.8833 | 206.6263 | 82.5771 | 220.0202 | 9.5677 | 52.3708 | 3.2243 | 116 | 37.2401 | 0 | 288.6388 | 0
7230 | 871.5699 | 4.9675 | 56.1381 | 104.2361 | 57.7982 | 12.3484 | 71.7289 | 3.5186 | 8.53 | 47.4113 | 82.5692 | 18.546 | 215.1578 | 110.2313 | 230.2511 | 12.0888 | 53.6259 | 3.4434 | 185 | 43.2568 | 0 | 322.2425 | 0
7231 | 936.847 | 13.337 | 77.1371 | 109.8469 | 48.6534 | 20.8976 | 99.4822 | 4.8924 | 9.365 | 69.5066 | 108.9241 | 35.3102 | 241.0664 | 171.2206 | 274.0342 | 26.7007 | 56.0954 | 11.7789 | 261 | 53.7422 | 0 | 368.2991 | 0
7232 | 996.3153 | 15.1341 | 94.9326 | 121.2231 | 49.3834 | 20.9 | 120.6481 | 4.6096 | 13.653 | 96.4169 | 141.9728 | 40.5154 | 308.8292 | 228.4898 | 373.4571 | 36.0483 | 63.442 | 15.9317 | 311 | 66.2067 | 0 | 431.2863 | 0
7233 | 1073.2063 | 15.5643 | 95.6293 | 133.8525 | 50.5736 | 19.9503 | 130.9162 | 5.2 | 19.263 | 107.1657 | 165.5763 | 39.465 | 364.3949 | 260.7947 | 481.0748 | 40.5708 | 72.4919 | 15.4295 | 360 | 63.5691 | 0 | 492.6637 | 0.18594
7234 | 1113.824 | 18.3483 | 95.4086 | 141.3885 | 49.3974 | 19.95 | 136.9336 | 5.7511 | 21.218 | 108.0017 | 176.7904 | 39.6657 | 391.4629 | 274.643 | 535.0093 | 40.9607 | 80.8125 | 15.4553 | 356 | 60.5431 | 0 | 521.5934 | 0.20947
7235 | 1135.2352 | 16.3078 | 98.8026 | 141.7791 | 52.0326 | 17.1008 | 136.4217 | 5.0573 | 22.127 | 109.3982 | 183.1271 | 41.0868 | 393.1321 | 274.7265 | 549.9693 | 39.6082 | 85.6099 | 15.3017 | 340 | 58.3187 | 0 | 540.8181 | 0.22969
7236 | 1118.7086 | 9.2338 | 98.3849 | 137.7442 | 52.1441 | 18.0497 | 128.3836 | 5.159 | 22.425 | 108.9076 | 188.8912 | 43.0385 | 398.5138 | 279.6338 | 548.8091 | 39.958 | 84.8431 | 15.4768 | 344 | 58.2192 | 0 | 553.0731 | 0.2591
7237 | 1110.8596 | 6.3578 | 99.8272 | 141.0713 | 59.5566 | 11.4018 | 131.8554 | 5.7696 | 22.48 | 105.8255 | 194.2849 | 43.9388 | 395.7838 | 293.2053 | 548.097 | 41.6305 | 84.5707 | 15.4284 | 305 | 57.1958 | 0 | 552.1872 | 0.27075
7238 | 1106.1327 | 5.4591 | 98.1558 | 140.1373 | 57.2626 | 13.2995 | 135.5211 | 4.3426 | 23.245 | 105.8066 | 195.2449 | 43.2686 | 398.8788 | 301.4735 | 553.5878 | 42.0771 | 85.5575 | 15.1795 | 290 | 55.1972 | 0 | 544.8258 | 0.25874
7239 | 1085.0505 | 7.2556 | 94.0373 | 135.2678 | 52.4977 | 18.0487 | 131.1562 | 4.6247 | 22.251 | 106.317 | 192.3766 | 39.7197 | 399.9976 | 298.9659 | 545.4782 | 38.3204 | 83.6592 | 15.2363 | 298 | 56.4526 | 0 | 521.7168 | 0.19764
7240 | 1042.0048 | 5.2945 | 88.8082 | 125.5158 | 62.7537 | 8.5526 | 123.8165 | 3.9516 | 20.36 | 102.1214 | 187.921 | 34.7668 | 376.7613 | 281.0198 | 504.4496 | 23.2154 | 78.7362 | 15.024 | 268 | 57.443 | 0 | 468.49 | 0.095005
7241 | 997.8666 | 4.1609 | 72.1414 | 114.4435 | 63.7753 | 6.6505 | 119.5875 | 2.9915 | 19.321 | 90.3349 | 174.3374 | 32.9515 | 352.2975 | 235.0877 | 429.8035 | 12.5575 | 71.8869 | 14.7583 | 245 | 57.175 | 0 | 384.7113 | 0
7242 | 956.2944 | 3.9861 | 34.2392 | 105.9745 | 61.7987 | 7.5997 | 114.8143 | 2.952 | 16.992 | 76.1032 | 146.3683 | 28.6805 | 320.111 | 182.2804 | 357.513 | 10.6186 | 65.9687 | 12.5621 | 230 | 48.0594 | 0 | 323.0542 | 0
7243 | 923.5853 | 3.6147 | 22.0435 | 102.2112 | 61.7083 | 7.6 | 96.0116 | 3.4577 | 12.608 | 70.0027 | 119.5769 | 13.9484 | 272.2248 | 154.2711 | 314.7583 | 10.302 | 58.9713 | 7.2408 | 219 | 41.1594 | 0 | 295.8011 | 0
7244 | 875.792 | 3.5234 | 21.2046 | 99.475 | 60.7481 | 7.6021 | 85.5012 | 3.769 | 8.74 | 67.2282 | 107.1427 | 7.7785 | 234.7736 | 135.8311 | 279.1814 | 8.9787 | 53.1758 | 4.6566 | 210 | 37.8354 | 0 | 284.6224 | 0
7245 | 848.9723 | 3.6289 | 20.8022 | 97.4628 | 60.1716 | 7.5979 | 81.8 | 3.831 | 7.629 | 53.7146 | 101.8208 | 7.6284 | 210.1628 | 120.7793 | 247.9765 | 8.5467 | 51.3565 | 4.1292 | 202 | 35.9557 | 0 | 275.8625 | 0
7246 | 832.5683 | 4.1367 | 20.947 | 94.8039 | 60.3903 | 6.6503 | 80.6886 | 2.8341 | 7.555 | 37.4381 | 96.0941 | 7.6163 | 194.2665 | 112.8815 | 230.3896 | 8.4175 | 50.3586 | 3.6192 | 178 | 34.9425 | 0 | 271.5412 | 0
7247 | 816.5919 | 3.2645 | 20.8035 | 96.2455 | 62.1146 | 4.7505 | 79.4452 | 3.4133 | 6.917 | 29.4321 | 86.9714 | 7.62 | 183.6093 | 108.8481 | 226.2309 | 8.5563 | 49.8938 | 2.9055 | 141 | 34.7358 | 0 | 262.3674 | 0
7248 | 821.0059 | 2.3981 | 21.048 | 96.3931 | 61.9168 | 5.6997 | 78.5664 | 3.9178 | 6.958 | 27.3585 | 76.726 | 7.6513 | 175.8638 | 104.4317 | 225.696 | 8.5419 | 49.2913 | 2.5173 | 136 | 34.9786 | 0 | 249.8151 | 0
7249 | 814.5682 | 1.6895 | 20.9899 | 94.9351 | 62.6005 | 4.7503 | 78.5936 | 3.9625 | 7.251 | 27.2501 | 70.9313 | 7.6847 | 172.6395 | 97.28 | 226.42 | 8.5098 | 48.35 | 2.3573 | 133 | 35.5984 | 0 | 246.4262 | 0
7250 | 798.631 | 1.4049 | 20.7946 | 94.3857 | 61.1272 | 5.6997 | 78.5821 | 3.9598 | 7.159 | 27.2668 | 69.9321 | 7.9093 | 171.8585 | 92.2252 | 230.0991 | 8.4751 | 48.0366 | 2.2781 | 129 | 34.3773 | 0 | 249.0986 | 0
7251 | 797.7955 | 1.4247 | 20.9676 | 93.8256 | 62.2092 | 4.7503 | 77.7473 | 3.6853 | 7.146 | 28.4117 | 69.5205 | 7.797 | 173.2374 | 90.3663 | 228.944 | 8.4898 | 47.9584 | 2.4155 | 122 | 34.2298 | 0 | 250.3019 | 0
7252 | 800.9919 | 2.0354 | 20.8956 | 94.7264 | 61.0966 | 5.6997 | 77.8465 | 3.2334 | 6.967 | 34.5997 | 68.3865 | 7.8371 | 173.425 | 88.6572 | 220.7054 | 8.5141 | 48.5057 | 2.4922 | 118 | 34.5488 | 0 | 247.0382 | 0
7253 | 806.1785 | 2.7576 | 22.1822 | 93.4757 | 60.5369 | 6.6497 | 77.7935 | 3.5607 | 6.789 | 40.1079 | 67.8931 | 7.799 | 172.1596 | 84.5133 | 217.5322 | 8.5607 | 50.7462 | 2.5535 | 115 | 34.1514 | 0 | 252.2006 | 0
7254 | 824.1982 | 3.1165 | 37.8032 | 94.0639 | 56.5128 | 7.5997 | 78.2636 | 3.9804 | 6.897 | 35.942 | 68.0912 | 7.8532 | 167.3898 | 82.3309 | 218.1827 | 8.4594 | 51.1494 | 2.4004 | 110 | 35.3731 | 0 | 257.2898 | 0
7255 | 850.2116 | 3.2731 | 48.6887 | 95.4899 | 58.1146 | 6.6503 | 80.6202 | 4.0067 | 7.401 | 37.8749 | 74.4417 | 18.645 | 168.0802 | 82.5403 | 218.0008 | 8.4109 | 48.8533 | 2.458 | 116 | 49.7272 | 0 | 255.2857 | 0
7256 | 861.1392 | 2.6605 | 55.509 | 91.8406 | 59.0968 | 7.5997 | 86.4959 | 3.9893 | 12.805 | 52.4829 | 99.4652 | 23.822 | 190.2774 | 83.837 | 215.21 | 8.1439 | 47.2305 | 2.7798 | 123 | 58.052 | 0 | 252.2468 | 0
7257 | 883.4374 | 1.9083 | 67.3137 | 91.6899 | 58.8566 | 7.6 | 88.3817 | 5.0875 | 18.582 | 61.7467 | 131.7794 | 25.0947 | 204.1394 | 88.0167 | 210.6112 | 7.9292 | 46.6625 | 5.0789 | 124 | 54.8789 | 0 | 250.5158 | 0.17838
7258 | 900.5555 | 1.4995 | 72.1243 | 89.9591 | 60.6633 | 6.6503 | 89.407 | 5.0826 | 21.262 | 63.1674 | 145.4782 | 29.3036 | 216.7165 | 100.5426 | 218.9939 | 8.0067 | 46.8573 | 10.3597 | 164 | 51.8365 | 0 | 248.747 | 0.21045
7259 | 915.9568 | 1.6295 | 73.0227 | 89.8059 | 61.8179 | 6.6518 | 79.7304 | 6.743 | 21.326 | 63.9903 | 132.5834 | 27.5296 | 236.3166 | 112.9652 | 232.2054 | 7.8718 | 47.6408 | 12.3632 | 160 | 50.193 | 0 | 246.4777 | 0.22499
7260 | 909.374 | 2.0803 | 73.9607 | 89.3502 | 64.2883 | 4.7487 | 66.1904 | 6.2287 | 21.091 | 66.1961 | 112.9917 | 21.4392 | 245.9811 | 117.0655 | 247.5142 | 7.9402 | 48.6056 | 12.3484 | 166 | 51.6382 | 0 | 247.3555 | 0.25717
7261 | 898.7106 | 1.7675 | 67.6821 | 89.7621 | 65.1873 | 4.75 | 62.0807 | 4.3201 | 19.488 | 69.3584 | 107.955 | 16.7558 | 247.9054 | 115.9816 | 277.3405 | 7.8992 | 48.6694 | 12.2394 | 176 | 52.9712 | 0 | 257.1926 | 0.26675
7262 | 904.1706 | 1.7455 | 33.1966 | 90.8502 | 64.7736 | 4.7513 | 62.5731 | 2.6123 | 20.231 | 72.0564 | 109.9395 | 16.1424 | 249.1377 | 116.6949 | 300.0227 | 7.9729 | 47.7915 | 12.0587 | 196 | 57.0602 | 0 | 263.9113 | 0.25947
7263 | 912.6285 | 1.4129 | 21.0571 | 90.2156 | 63.965 | 5.6984 | 66.6986 | 3.2316 | 19.237 | 72.9658 | 110.3517 | 15.5412 | 241.4721 | 111.3633 | 301.9302 | 8.0049 | 47.2125 | 10.2754 | 204 | 58.3643 | 0 | 258.045 | 0.19764
7264 | 912.0047 | 1.954 | 20.948 | 92.3654 | 63.8036 | 4.7503 | 74.2155 | 3.6986 | 14.189 | 67.3969 | 108.9162 | 8.0033 | 234.5201 | 101.4655 | 295.2954 | 8.0263 | 47.4599 | 5.963 | 198 | 55.4412 | 0 | 255.0596 | 0.088371
7265 | 893.2347 | 3.8419 | 21.3389 | 93.0295 | 61.4857 | 5.6997 | 77.54 | 3.7962 | 13.776 | 57.5029 | 106.1735 | 7.86 | 227.0768 | 104.9154 | 294.0913 | 8.0234 | 48.0596 | 4.385 | 194 | 60.3861 | 0 | 254.3084 | 0
7266 | 876.7422 | 4.3668 | 22.0641 | 93.6753 | 59.0415 | 7.5995 | 77.142 | 4.2965 | 13.168 | 51.0364 | 102.9387 | 13.5018 | 215.6503 | 118.0926 | 299.0768 | 8.4337 | 48.7714 | 4.904 | 195 | 52.0563 | 0 | 259.1326 | 0
7267 | 865.3669 | 3.9791 | 22.5916 | 94.3732 | 59.3606 | 7.6 | 75.9033 | 3.9185 | 9.994 | 51.9077 | 101.7324 | 15.4277 | 204.7707 | 120.9875 | 281.6762 | 8.7643 | 49.3611 | 5.3512 | 216 | 44.2551 | 0 | 266.7445 | 0
7268 | 851.52 | 3.7065 | 22.9251 | 94.1861 | 60.5357 | 6.6503 | 75.6123 | 3.4362 | 8.377 | 53.8956 | 102.196 | 14.1333 | 195.3704 | 113.5845 | 264.3896 | 8.6879 | 48.9847 | 4.877 | 202 | 41.5472 | 0 | 267.8917 | 0
7269 | 851.1794 | 3.783 | 21.8745 | 94.7965 | 59.929 | 7.5997 | 78.3862 | 3.551 | 8.149 | 47.6913 | 99.4642 | 11.5978 | 186.9824 | 109.6342 | 260.0355 | 8.5432 | 48.3118 | 4.2569 | 200 | 43.9141 | 0 | 277.2035 | 0
7270 | 841.7109 | 3.2609 | 21.755 | 94.5046 | 61.4797 | 5.7005 | 80.2114 | 4.3368 | 7.937 | 39.1739 | 98.5216 | 10.6426 | 182.2159 | 107.6037 | 256.5236 | 8.8771 | 48.1696 | 3.8867 | 181 | 40.9793 | 0 | 282.7502 | 0
7271 | 829.7295 | 2.2385 | 21.8705 | 93.3223 | 61.4657 | 4.7503 | 80.0532 | 4.5358 | 7.465 | 34.8286 | 100.6775 | 10.088 | 181.933 | 107.3594 | 247.4056 | 9.2252 | 48.1165 | 3.6021 | 151 | 42.8265 | 0 | 276.0085 | 0
7272 | 828.682 | 1.8487 | 21.8409 | 93.2103 | 60.4218 | 5.6997 | 79.4451 | 4.4861 | 7.363 | 33.6598 | 99.6731 | 10.3182 | 181.9462 | 105.545 | 241.8356 | 9.2562 | 47.9997 | 3.3854 | 152 | 44.1055 | 0 | 266.3367 | 0
7273 | 532.52 | 1.141 | 13.8438 | 58.0213 | 49.7582 | 2.3759 | 50.2717 | 2.9986 | 8.489 | 26.6 | 77.7116 | 6.7323 | 177.8674 | 83.0734 | 203.0912 | 5.8708 | 39.1006 | 2.1759 | 149 | 23.5516 | 0 | 195.7831 | 0
7274 | [8 empty] | 7.504 |  |  |  | 111.6751 | [5 empty] | 151 |  |  |  | 0
7275 | 1308.1063 | 2.5116 | 35.1224 | 148.3603 | 64.1535 | 19.9451 | 109.8837 | 7.3155 | 13.692 | 40.4788 | 112.2264 | 15.5103 | 282.1205 | 143.7765 | 396.6533 | 14.9051 | 77.3367 | 4.0792 | 153 | 80.5886 | 0 | 508.8761 | 0
7276 | 1081.3454 | 2.2322 | 27.6502 | 115.0914 | 74.0848 | 9.5029 | 97.908 | 6.324 | 6.777 | 35.5319 | 98.9843 | 13.591 | 215.5414 | 106.615 | 327.5177 | 11.7157 | 60.3465 | 3.0316 | 144 | 44.0645 | 0 | 285.0032 | 0
7277 | 827.7175 | 1.8863 | 21.9601 | 92.045 | 60.2827 | 5.7026 | 79.3303 | 4.9325 | 7.03 | 30.1473 | 74.8367 | 10.0439 | 168.3829 | 79.7139 | 234.1593 | 9.2424 | 49.3637 | 1.9917 | 139 | 40.3823 | 0 | 262.1869 | 0
7278 | 826.7695 | 2.8394 | 21.997 | 91.5874 | 61.7291 | 4.75 | 68.7747 | 4.7873 | 7.304 | 30.0863 | 75.2445 | 9.9495 | 164.1065 | 81.2172 | 232.0523 | 9.3015 | 52.4561 | 1.9811 | 128 | 35.9496 | 0 | 261.0943 | 0
7279 | 826.3011 | 3.2384 | 21.7742 | 91.3709 | 60.8261 | 5.6984 | 68.5467 | 4.7805 | 7.426 | 26.1652 | 74.4983 | 9.6327 | 162.5776 | 84.3256 | 225.4044 | 9.144 | 49.137 | 1.9884 | 136 | 34.2128 | 0 | 264.4057 | 0
7280 | 822.0584 | 2.604 | 21.612 | 88.8904 | 59.583 | 7.5995 | 76.2509 | 4.5808 | 6.841 | 21.7417 | 76.2676 | 9.0201 | 170.0508 | 80.3096 | 220.7546 | 8.8183 | 46.7956 | 2.0069 | 131 | 33.4538 | 0 | 251.3651 | 0
7281 | 825.9995 | 1.7341 | 21.8546 | 87.8763 | 61.6877 | 6.6503 | 70.5591 | 4.184 | 6.307 | 27.24 | 81.8716 | 7.7522 | 172.9769 | 81.2822 | 212.6527 | 8.6304 | 46.501 | 2.0089 | 129 | 29.4418 | 0 | 251.6589 | 0.14878
7282 | 849.6495 | 1.3586 | 21.9316 | 89.74 | 60.474 | 7.5997 | 65.2111 | 3.5642 | 6.288 | 40.4832 | 85.168 | 6.9943 | 175.311 | 86.0529 | 215.0384 | 8.4343 | 46.8111 | 2.002 | 145 | 28.1631 | 0 | 251.8016 | 0.19664
7283 | 873.1067 | 1.7084 | 21.6269 | 89.1108 | 57.3118 | 7.6 | 82.4391 | 3.7688 | 6.309 | 49.6979 | 87.4729 | 6.861 | 185.5471 | 93.2882 | 224.3472 | 8.0776 | 47.0655 | 1.9641 | 166 | 28.5278 | 0 | 256.473 | 0.092503
7284 | 871.6389 | 1.6798 | 21.4598 | 88.4701 | 58.0268 | 7.6 | 93.7401 | 3.8775 | 6.384 | 49.6196 | 92.8939 | 7.0656 | 196.804 | 95.6969 | 229.8313 | 7.8644 | 47.2161 | 1.9649 | 182 | 29.1263 | 0 | 263.8521 | 0.18405
7285 | 872.885 | 1.4528 | 21.3417 | 89.3025 | 60.3399 | 7.6 | 102.4222 | 3.7144 | 6.714 | 51.1818 | 94.6447 | 7.1218 | 199.9097 | 108.1233 | 236.5788 | 7.9174 | 48.2083 | 2.1005 | 194 | 29.5994 | 0 | 253.1024 | 0.24118
7286 | 868.5137 | 1.4404 | 21.0664 | 91.8613 | 63.4409 | 4.7508 | 103.5448 | 3.5244 | 6.595 | 51.1308 | 88.0498 | 7.2432 | 200.9512 | 103.8968 | 252.2726 | 7.7991 | 48.4174 | 2.1329 | 194 | 30.2312 | 0 | 257.7603 | 0.2292
7287 | 870.5548 | 1.4258 | 20.9214 | 94.8731 | 63.9673 | 4.75 | 95.6656 | 2.4874 | 6.553 | 47.4516 | 86.9982 | 8.0238 | 197.7304 | 100.4761 | 267.3595 | 7.9669 | 47.822 | 2.1068 | 181 | 33.6547 | 0 | 262.6473 | 0.058108
7288 | 865.3944 | 2.2735 | 21.2201 | 94.0554 | 62.9374 | 5.6997 | 94.9255 | 2.7754 | 6.629 | 44.5087 | 92.0955 | 10.4848 | 195.7778 | 94.1817 | 273.3059 | 8.0171 | 48.468 | 2.6031 | 179 | 38.4176 | 0 | 252.4913 | 0.011493
7289 | 866.8682 | 3.1124 | 21.297 | 93.3907 | 62.6976 | 4.7503 | 96.3264 | 3.98 | 7.357 | 33.5235 | 95.6574 | 10.9806 | 197.2578 | 98.5011 | 266.9469 | 8.1025 | 49.5013 | 3.3693 | 171 | 42.6042 | 0 | 261.0736 | 0
7290 | 872.887 | 3.3101 | 21.5428 | 96.0589 | 61.1811 | 5.6997 | 88.1951 | 4.1916 | 7.982 | 28.7797 | 113.8155 | 11.166 | 201.5527 | 111.8262 | 256.1047 | 8.3564 | 49.4569 | 3.4726 | 153 | 43.2799 | 0 | 269.2732 | 0
7291 | 884.7788 | 3.3878 | 21.7762 | 94.2144 | 61.9231 | 4.7503 | 84.4971 | 4.162 | 8.505 | 30.9172 | 116.1695 | 11.3404 | 198.929 | 121.1872 | 249.7065 | 8.3986 | 50.1289 | 3.2501 | 150 | 43.352 | 0 | 270.4348 | 0
7292 | 882.1958 | 3.8483 | 21.8348 | 96.2251 | 60.671 | 5.6997 | 85.0545 | 4.5529 | 8.656 | 35.6176 | 90.031 | 10.6331 | 200.3357 | 108.5921 | 242.0159 | 8.5718 | 49.584 | 2.5519 | 134 | 41.1388 | 0 | 268.8105 | 0
7293 | 859.8302 | 4.1149 | 21.9496 | 95.8705 | 58.4337 | 7.5995 | 82.9371 | 4.7762 | 8.72 | 35.1566 | 79.1647 | 10.2732 | 199.7529 | 91.1645 | 236.7588 | 8.5089 | 48.3367 | 2.237 | 135 | 38.4406 | 0 | 260.3811 | 0
7294 | 848.8013 | 4.2195 | 22.0376 | 95.2075 | 58.2269 | 7.6 | 80.8744 | 4.1384 | 8.372 | 30.0517 | 75.0819 | 10.4965 | 190.1427 | 87.9851 | 243.0928 | 8.5808 | 47.9213 | 2.7219 | 118 | 37.0058 | 0 | 260.7532 | 0
7295 | 838.5449 | 3.7405 | 21.9557 | 96.0662 | 58.0855 | 7.6 | 79.3663 | 3.6477 | 7.734 | 27.0001 | 68.0096 | 10.241 | 176.2634 | 83.9846 | 240.4682 | 8.5591 | 47.9473 | 3.2095 | 114 | 36.4051 | 0 | 262.9979 | 0
7296 | 817.621 | 2.3574 | 22.024 | 93.6227 | 58.0451 | 7.6 | 77.7659 | 3.8959 | 7.509 | 26.9001 | 65.4222 | 10.1172 | 168.1824 | 84.7162 | 235.7176 | 8.4381 | 47.868 | 2.9061 | 113 | 34.3468 | 0 | 254.1853 | 0
7297 | 810.9562 | 1.6652 | 21.9065 | 94.2373 | 58.24 | 7.6 | 76.9003 | 4.1188 | 7.486 | 26.4617 | 64.5422 | 10.2552 | 166.4415 | 81.844 | 224.9292 | 8.5342 | 47.7289 | 2.2032 | 111 | 33.3418 | 0 | 256.2179 | 0
7298 | 801.295 | 1.6277 | 21.8992 | 94.356 | 60.0766 | 5.7005 | 76.24 | 4.3911 | 7.459 | 25.9783 | 63.9507 | 11.6376 | 167.0426 | 83.6271 | 219.2735 | 8.5026 | 47.7277 | 1.9989 | 108 | 33.508 | 0 | 258.2861 | 0
7299 | 790.2679 | 1.4397 | 21.9959 | 94.2086 | 60.9712 | 4.7516 | 76.1883 | 4.4707 | 7.429 | 25.8734 | 65.4664 | 10.6548 | 167.1625 | 83.5134 | 217.2611 | 8.5379 | 47.745 | 1.9628 | 107 | 33.6213 | 0 | 258.7571 | 0
7300 | 792.86 | 1.2989 | 21.8698 | 94.3434 | 59.8844 | 5.6984 | 76.3352 | 4.4498 | 7.378 | 28.5844 | 64.6164 | 9.9575 | 168.8138 | 85.7316 | 215.6089 | 8.4727 | 47.7567 | 1.952 | 103 | 33.2065 | 0 | 259.3609 | 0
7301 | 794.6171 | 1.7488 | 25.0695 | 95.7313 | 60.7808 | 4.7503 | 75.9002 | 4.4704 | 7.262 | 38.3868 | 63.9518 | 9.9415 | 176.8216 | 77.9008 | 214.3213 | 8.4446 | 49.0727 | 1.9469 | 103 | 33.2524 | 0 | 308.9092 | 0
7302 | 815.7377 | 3.0775 | 26.0993 | 95.8449 | 59.8172 | 5.6997 | 82.3349 | 4.6498 | 8.305 | 41.2347 | 66.2446 | 12.6789 | 187.0802 | 75.5656 | 225.2569 | 8.4205 | 52.9843 | 1.9693 | 106 | 37.0716 | 0 | 327.0488 | 0
7303 | 849.0884 | 4.438 | 49.7804 | 101.978 | 56.0349 | 9.4989 | 97.7277 | 4.5723 | 11.255 | 51.3724 | 94.6534 | 22.5316 | 215.9546 | 121.7489 | 251.3272 | 11.6098 | 50.1339 | 1.9717 | 170 | 43.8703 | 0 | 378.297 | 0
7304 | 904.8353 | 14.0476 | 75.7689 | 106.0042 | 45.4979 | 19.9471 | 120.9714 | 4.4469 | 14.959 | 78.9622 | 126.0661 | 33.8239 | 272.4209 | 193.3765 | 359.4354 | 26.0244 | 54.8206 | 2.7937 | 268 | 47.388 | 0 | 434.6776 | 0
7305 | 1010.8011 | 16.0103 | 84.3612 | 118.2723 | 47.3332 | 19.0055 | 143.4389 | 4.4905 | 24.259 | 90.8038 | 151.3341 | 34.8165 | 321.8061 | 250.6408 | 457.2844 | 31.8179 | 65.4595 | 4.1559 | 302 | 60.087 | 0 | 496.2458 | 0.019755
7306 | 1082.3641 | 8.7858 | 89.169 | 130.8887 | 47.1357 | 19.9445 | 159.5687 | 6.0378 | 28.852 | 90.3285 | 169.6553 | 36.8912 | 360.106 | 285.7386 | 513.5416 | 32.2178 | 74.6509 | 4.4197 | 347 | 67.9399 | 0 | 518.5161 | 0.033353
7307 | 1128.5654 | 4.0105 | 85.2093 | 136.7934 | 43.0532 | 24.6987 | 158.0777 | 7.0265 | 30.132 | 93.5083 | 177.6533 | 40.529 | 382.356 | 298.7183 | 553.5377 | 32.1907 | 82.6723 | 6.2931 | 376 | 64.5915 | 0 | 525.8908 | 0.050502
7308 | 1145.2424 | 3.1606 | 90.8553 | 139.9577 | 46.7225 | 22.8005 | 139.8888 | 5.4942 | 26.644 | 98.5484 | 178.9454 | 39.7467 | 390.9726 | 303.4068 | 547.0827 | 31.9246 | 83.6116 | 5.2213 | 352 | 73.455 | 0 | 557.3736 | 0.061997
7309 | 1141.268 | 3.3165 | 92.0799 | 136.4577 | 46.4997 | 22.8 | 131.1426 | 5.8749 | 21.101 | 89.6424 | 178.0976 | 39.1038 | 392.3237 | 302.4672 | 528.5932 | 32.8552 | 79.1531 | 5.0952 | 403 | 65.6906 | 0 | 573.2444 | 0.049396
7310 | 1141.134 | 3.4034 | 96.1582 | 136.725 | 47.7398 | 22.8 | 137.7372 | 6.1491 | 23.378 | 90.1188 | 178.4919 | 40.6288 | 393.3889 | 302.842 | 532.2197 | 32.627 | 79.5551 | 6.9444 | 314 | 70.6848 | 0 | 567.3756 | 0.05961
7311 | 1153.2278 | 3.5663 | 94.5516 | 137.3224 | 49.3001 | 21.8503 | 145.8727 | 5.6021 | 23.39 | 94.465 | 178.5469 | 40.1341 | 399.1035 | 306.9993 | 523.4858 | 31.4503 | 79.876 | 7.6488 | 302 | 72.418 | 0 | 569.2933 | 0.022166
7312 | 1128.1466 | 4.1204 | 91.367 | 140.797 | 54.0259 | 17.1013 | 153.0581 | 5.1724 | 19.716 | 88.6099 | 178.6897 | 34.6791 | 395.7972 | 292.6536 | 522.9891 | 32.7782 | 79.1144 | 7.7267 | 286 | 73.0381 | 0 | 540.1605 | 0.0066866
7313 | 1090.6389 | 5.0297 | 87.7012 | 137.2488 | 55.8139 | 15.2005 | 150.9353 | 6.2948 | 16.791 | 83.575 | 179.1433 | 30.7384 | 383.7282 | 276.6481 | 488.0322 | 30.418 | 76.9917 | 7.8003 | 290 | 70.159 | 0 | 472.5626 | 0
7314 | 1049.361 | 5.372 | 82.6732 | 124.1223 | 61.7011 | 8.5518 | 138.0205 | 6.1056 | 11.852 | 74.3393 | 160.5502 | 30.7367 | 342.8238 | 231.1032 | 403.5673 | 16.2986 | 71.6667 | 6.9514 | 237 | 61.7687 | 0 | 390.9225 | 0
7315 | 1008.9414 | 5.081 | 78.9038 | 111.6745 | 62.5992 | 7.6003 | 122.224 | 5.5304 | 11.902 | 60.0705 | 122.3822 | 26.5487 | 291.4821 | 177.1755 | 344.1504 | 10.329 | 65.3524 | 5.5964 | 213 | 53.9991 | 0 | 352.3956 | 0
7316 | 959.2874 | 4.5003 | 64.8609 | 107.4197 | 63.5823 | 6.6503 | 99.3293 | 4.2096 | 10.288 | 64.1859 | 103.585 | 12.5009 | 261.2363 | 157.0956 | 310.65 | 9.8176 | 62.3578 | 4.4957 | 192 | 46.2051 | 0 | 296.7899 | 0
7317 | 912.8151 | 3.8448 | 27.8102 | 103.7073 | 62.4699 | 6.65 | 87.7374 | 3.7775 | 8.8183 | 59.0699 | 100.4863 | 6.7304 | 237.3701 | 140.6947 | 290.3623 | 9.9374 | 56.6868 | 3.7715 | 193 | 40.6981 | 0 | 274.3408 | 0
7318 | 884.0434 | 4.1028 | 16.0441 | 101.7998 | 65.1451 | 4.7505 | 85.2004 | 3.9805 | 8.7608 | 41.2635 | 99.8665 | 6.6802 | 212.432 | 126.6834 | 267.4877 | 9.9587 | 52.327 | 3.5602 | 167 | 39.432 | 0 | 273.0315 | 0
7319 | 865.9076 | 3.3987 | 15.8618 | 99.7281 | 63.4174 | 5.6997 | 83.545 | 3.3977 | 8.236 | 31.9415 | 84.7666 | 6.6871 | 191.787 | 114.9471 | 252.9075 | 9.8869 | 51.0325 | 3.5893 | 149 | 33.8326 | 0 | 261.8645 | 0
7320 | 848.9608 | 2.7832 | 15.7264 | 98.9041 | 64.6376 | 4.7503 | 81.9635 | 2.812 | 7.682 | 29.9708 | 76.3889 | 6.6773 | 185.4146 | 109.8189 | 240.883 | 9.8375 | 50.9435 | 3.6039 | 133 | 33.552 | 0 | 256.8086 | 0
7321 | 839.578 | 1.7446 | 15.5982 | 99.1483 | 59.9781 | 4.75 | 81.3685 | 3.384 | 7.123 | 29.6441 | 76.1342 | 6.5504 | 185.6832 | 102.8833 | 223.099 | 9.8949 | 51.2124 | 2.8651 | 130 | 32.7618 | 0 | 248.8989 | 0
7322 | 827.9459 | 1.2119 | 15.6958 | 99.1206 | 59.3342 | 5.6997 | 82.0245 | 3.917 | 6.961 | 29.851 | 78.3635 | 8.0105 | 191.186 | 89.1274 | 218.8426 | 9.9784 | 51.2411 | 2.4254 | 127 | 31.4959 | 0 | 254.9984 | 0
7323 | 810.2813 | 1.2269 | 15.6949 | 98.8429 | 61.358 | 4.7503 | 81.9068 | 3.5196 | 6.942 | 30.0731 | 80.5562 | 7.1586 | 188.9303 | 83.5025 | 225.3055 | 9.9453 | 51.2024 | 2.4041 | 117 | 31.7003 | 0 | 247.843 | 0
7324 | 803.8946 | 1.2172 | 15.7442 | 98.5659 | 60.1478 | 4.7513 | 81.4398 | 2.7539 | 6.972 | 32.9353 | 80.9918 | 6.4677 | 183.8646 | 81.4474 | 228.9342 | 9.9882 | 51.2383 | 2.4344 | 115 | 31.1914 | 0 | 247.2799 | 0
7325 | 806.101 | 1.248 | 15.6627 | 98.3692 | 59.033 | 5.6984 | 81.3502 | 3.3106 | 6.829 | 42.8117 | 80.9399 | 6.4358 | 186.2387 | 81.6079 | 224.0826 | 9.8451 | 52.5629 | 2.4211 | 116 | 31.7618 | 0 | 267.0105 | 0
7326 | 816.6534 | 1.9217 | 33.1781 | 100.8413 | 60.079 | 4.7503 | 86.9947 | 3.6889 | 7.32 | 48.4102 | 82.4081 | 10.1102 | 194.4135 | 86.2064 | 228.844 | 9.9354 | 55.5197 | 2.4134 | 124 | 32.837 | 0 | 300.8556 | 0
7327 | 850.1805 | 3.0399 | 47.277 | 108.0044 | 54.5042 | 10.4484 | 102.3325 | 3.6274 | 12.985 | 60.9147 | 103.7265 | 16.5243 | 222.5915 | 132.6896 | 247.112 | 13.6305 | 53.6854 | 2.392 | 199 | 39.0869 | 0 | 357.068 | 0
7328 | 911.4735 | 8.0289 | 72.3525 | 109.4812 | 46.0351 | 18.0479 | 121.9434 | 3.7927 | 18.306 | 78.3672 | 139.6736 | 29.1973 | 273.2239 | 205.8934 | 344.2456 | 26.8323 | 58.1774 | 3.2215 | 258 | 46.9635 | 0 | 396.3941 | 0
7329 | 997.5391 | 13.0456 | 89.009 | 123.4721 | 46.9417 | 18.05 | 142.0505 | 5.2694 | 20.283 | 88.5017 | 161.8055 | 37.7711 | 331.971 | 248.2885 | 482.8443 | 32.1276 | 66.9112 | 4.5012 | 313 | 54.686 | 0 | 465.7895 | 0.026258
7330 | 1097.8653 | 11.5866 | 90.7387 | 136.484 | 45.4698 | 18.9997 | 159.6989 | 5.8964 | 21.889 | 95.2106 | 173.6908 | 39.5126 | 385.109 | 275.4435 | 555.5976 | 33.3991 | 76.2835 | 5.1079 | 395 | 65.6389 | 0 | 545.4683 | 0.035748
7331 | 1158.3656 | 10.2711 | 92.1853 | 140.6066 | 45.1954 | 22.7989 | 164.7125 | 5.876 | 24.473 | 87.0123 | 180.444 | 40.5309 | 409.9356 | 293.0879 | 588.9073 | 34.6108 | 99.0744 | 6.2181 | 384 | 72.4861 | 0 | 542.0416 | 0.097774
7332 | 1194.3009 | 12.7509 | 96.7569 | 144.279 | 50.8727 | 21.8503 | 165.5697 | 5.1193 | 21.833 | 88.1722 | 182.0965 | 40.5485 | 419.1834 | 310.5039 | 599.0306 | 34.0711 | 109.4237 | 5.9707 | 343 | 79.1225 | 0 | 553.0161 | 0.063579
7333 | 1165.5675 | 13.7696 | 97.6316 | 142.1075 | 50.6256 | 21.85 | 163.0885 | 6.3893 | 18.041 | 82.6384 | 180.8556 | 41.7394 | 417.5253 | 309.3006 | 585.6898 | 34.0086 | 100.6019 | 7.409 | 377 | 67.9627 | 0 | 574.7468 | 0.081213
7334 | 1162.5466 | 10.6279 | 94.0936 | 142.2161 | 49.6174 | 22.3249 | 170.1752 | 6.8796 | 21.61 | 84.6938 | 179.4672 | 43.2503 | 423.7825 | 305.276 | 574.0463 | 34.5971 | 100.0444 | 8.712 | 307 | 70.1694 | 0 | 579.3179 | 0.1185
7335 | 1175.2498 | 9.4121 | 94.1838 | 143.7902 | 50.68 | 22.3312 | 168.2779 | 5.6216 | 23.119 | 85.4282 | 179.2685 | 41.1194 | 430.8849 | 300.5081 | 563.4407 | 33.761 | 96.3796 | 8.4413 | 292 | 70.8683 | 0 | 585.3312 | 0.055202
7336 | 1157.3315 | 6.434 | 94.838 | 140.2482 | 57.508 | 17.1015 | 160.8725 | 5.4434 | 24.799 | 78.6439 | 175.3808 | 34.0035 | 425.3197 | 283.8962 | 559.0822 | 32.3556 | 84.5257 | 8.3606 | 308 | 68.6488 | 0 | 599.7027 | 0.0286
7337 | 1158.9455 | 5.3096 | 90.3093 | 131.7126 | 60.4242 | 13.3011 | 151.0105 | 6.0508 | 24.935 | 71.7488 | 172.654 | 30.3924 | 402.5471 | 259.9351 | 509.4691 | 28.1523 | 78.8948 | 7.9462 | 288 | 67.6411 | 0 | 500.0727 | 0
7338 | 1114.148 | 8.9727 | 82.0934 | 118.8912 | 64.2636 | 8.5513 | 137.4258 | 5.6314 | 22.459 | 72.6199 | 155.9052 | 33.9274 | 349.74 | 211.5735 | 406.9392 | 15.9744 | 71.271 | 7.0476 | 256 | 61.3896 | 0 | 395.9403 | 0
7339 | 1039.1939 | 10.2648 | 76.4151 | 107.6683 | 65.1906 | 6.6524 | 125.0819 | 4.5911 | 21.149 | 67.8001 | 123.5254 | 27.9267 | 300.3383 | 172.5514 | 350.2858 | 10.9821 | 64.2729 | 5.3185 | 228 | 58.6631 | 0 | 339.5354 | 0
7340 | 974.2181 | 7.2352 | 63.3259 | 102.4622 | 66.2747 | 4.7487 | 114.9672 | 4.1658 | 20.199 | 64.8993 | 108.5813 | 14.554 | 257.7645 | 153.5077 | 318.9844 | 10.5953 | 60.4534 | 4.3911 | 205 | 58.2123 | 0 | 289.9775 | 0
7341 | 926.157 | 3.5364 | 28.117 | 99.3859 | 64.8269 | 5.6997 | 94.3867 | 4.0067 | 14.904 | 55.2199 | 99.9288 | 8.5225 | 229.2613 | 137.4373 | 274.8459 | 10.6853 | 54.2479 | 4.1263 | 202 | 53.1099 | 0 | 271.1467 | 0
7342 | 894.5156 | 2.1805 | 16.3975 | 96.049 | 65.2357 | 5.7 | 85.5787 | 3.8088 | 9.574 | 37.766 | 91.9998 | 7.9818 | 208.6764 | 124.9274 | 240.8302 | 11.3089 | 49.5033 | 4.0431 | 186 | 48.1318 | 0 | 259.564 | 0
7343 | 847.5557 | 1.7167 | 16.248 | 94.2007 | 65.7835 | 4.7503 | 82.8958 | 3.8002 | 7.752 | 30.0093 | 79.4005 | 8.0508 | 193.928 | 118.0698 | 230.0571 | 11.4369 | 49.011 | 3.796 | 168 | 45.8162 | 0 | 259.1966 | 0
7344 | 808.0889 | 1.5438 | 16.1984 | 92.7462 | 63.9387 | 6.6513 | 71.2035 | 4.0872 | 7.763 | 27.9703 | 72.8788 | 8.4132 | 185.7954 | 115.6916 | 231.7834 | 11.4232 | 48.7532 | 3.5642 | 151 | 43.6944 | 0 | 260.4398 | 0
7345 | 800.4838 | 1.7878 | 15.9075 | 91.8164 | 64.7901 | 4.7487 | 72.8316 | 4.6296 | 7.458 | 27.2429 | 69.7959 | 8.0211 | 182.0452 | 111.2759 | 233.4902 | 11.2763 | 47.802 | 3.5501 | 144 | 42.2584 | 0 | 263.2718 | 0
7346 | 793.4422 | 1.772 | 16.0628 | 93.4354 | 64.4878 | 5.6997 | 79.3938 | 4.7342 | 7.304 | 27.4187 | 68.4083 | 7.4449 | 183.6795 | 107.34 | 241.274 | 11.2973 | 47.3138 | 3.8476 | 147 | 35.0445 | 0 | 262.5174 | 0
7347 | 786.9867 | 1.8812 | 15.8839 | 93.1652 | 65.3134 | 4.7516 | 71.8372 | 4.775 | 7.464 | 27.7274 | 68.5988 | 7.5783 | 184.1122 | 108.4421 | 240.6554 | 11.3628 | 47.5306 | 3.3784 | 145 | 34.1487 | 0 | 268.9362 | 0
7348 | 783.1788 | 1.9493 | 16.067 | 91.9235 | 63.7848 | 5.6984 | 68.1641 | 4.8246 | 7.544 | 30.638 | 68.4609 | 7.5037 | 182.0075 | 103.4251 | 236.5363 | 11.4749 | 47.6023 | 2.7737 | 131 | 32.8283 | 0 | 268.6607 | 0
7349 | 781.5659 | 1.9057 | 15.9938 | 93.4383 | 64.8738 | 4.7503 | 77.8139 | 4.8216 | 7.564 | 40.7039 | 68.7878 | 7.4389 | 184.0252 | 100.3645 | 233.4624 | 11.3333 | 49.1727 | 2.6217 | 121 | 32.9948 | 0 | 292.9343 | 0
7350 | 798.9326 | 2.0189 | 32.2357 | 93.6331 | 63.6193 | 5.6997 | 79.1795 | 5.203 | 7.955 | 45.6067 | 70.7134 | 11.7186 | 191.8947 | 102.5332 | 241.1554 | 11.4155 | 51.5285 | 2.6149 | 126 | 35.7705 | 0 | 339.0973 | 0
7351 | 841.569 | 3.0973 | 46.5555 | 99.2101 | 54.3477 | 13.2979 | 85.5803 | 5.0661 | 12.565 | 56.6436 | 97.1953 | 21.1869 | 226.6489 | 136.0568 | 263.1526 | 14.2908 | 48.9276 | 2.6517 | 180 | 39.1455 | 0 | 399.672 | 0
7352 | 898.7059 | 6.1026 | 74.8555 | 100.2519 | 44.1052 | 21.8476 | 103.2186 | 5.2486 | 17.529 | 87.0701 | 139.5779 | 34.1805 | 280.6908 | 208.716 | 375.9612 | 27.9262 | 52.7098 | 3.4959 | 284 | 48.0058 | 0 | 433.315 | 0
7353 | 996.083 | 5.6587 | 89.988 | 110.6037 | 42.3841 | 22.7997 | 132.5504 | 6.537 | 25.553 | 96.4987 | 163.502 | 41.1183 | 339.6768 | 271.0887 | 476.1668 | 32.8861 | 63.5244 | 5.7688 | 295 | 60.4408 | 0 | 505.4495 | 0.045466
7354 | 1074.462 | 8.6061 | 96.6988 | 123.7747 | 40.2887 | 25.6492 | 152.0445 | 8.5495 | 29.207 | 94.2603 | 171.4693 | 41.6149 | 395.6979 | 278.1165 | 558.105 | 34.4272 | 75.8355 | 6.7547 | 393 | 63.8008 | 0 | 545.2983 | 0.024178
7355 | 1113.7909 | 10.5896 | 95.518 | 130.9319 | 42.307 | 25.65 | 149.2388 | 8.6543 | 29.491 | 103.1679 | 174.2109 | 42.7248 | 422.5651 | 278.9869 | 603.0316 | 35.7609 | 100.3377 | 7.8994 | 378 | 70.5577 | 0 | 536.8528 | 0.037518
7356 | 1135.6608 | 12.8994 | 97.513 | 130.9497 | 44.8944 | 24.7003 | 146.807 | 7.836 | 26.572 | 95.0616 | 174.6405 | 41.9722 | 436.3552 | 291.4344 | 613.2357 | 35.8687 | 103.4947 | 13.9298 | 359 | 76.8584 | 0 | 537.6871 | 0.035492
7357 | 1122.6678 | 12.0562 | 98.417 | 132.4557 | 45.9287 | 24.7 | 155.7402 | 6.6449 | 20.122 | 79.5295 | 177.6327 | 41.5547 | 436.0016 | 293.8289 | 587.7037 | 35.424 | 96.2612 | 16.8383 | 365 | 66.3288 | 0 | 546.1445 | 0.044372
7358 | 1136.1824 | 7.1523 | 97.2126 | 137.3075 | 46.0525 | 24.7 | 162.4834 | 6.6037 | 20.578 | 83.1489 | 179.5716 | 41.2293 | 438.8507 | 300.7154 | 587.2101 | 35.4206 | 95.8622 | 17.6255 | 301 | 66.9333 | 0 | 574.957 | 0.059343
7359 | 1173.8758 | 3.9316 | 97.1971 | 140.3099 | 44.4581 | 25.6497 | 154.9971 | 7.0472 | 21.373 | 96.6987 | 179.0159 | 37.6047 | 442.9176 | 300.8983 | 595.6773 | 35.7947 | 98.5037 | 17.8964 | 276 | 71.6825 | 0 | 566.7126 | 0.032674
7360 | 1174.7969 | 3.6999 | 97.3563 | 133.7242 | 49.5499 | 19.9516 | 150.9086 | 7.8727 | 19.827 | 79.9114 | 177.5872 | 37.3588 | 435.6182 | 294.4856 | 588.4494 | 36.3902 | 98.1474 | 17.8376 | 289 | 72.2264 | 0 | 574.7428 | 0.0067372
7361 | 1134.2007 | 4.7395 | 94.4857 | 128.9712 | 56.9471 | 13.3018 | 147.386 | 8.3788 | 18.677 | 67.415 | 177.6406 | 38.7488 | 410.4279 | 291.0499 | 527.9948 | 32.7004 | 97.9646 | 17.2466 | 273 | 69.6274 | 0 | 521.1307 | 0
7362 | 1089.5114 | 4.7612 | 89.1704 | 122.512 | 61.6352 | 9.5011 | 125.9312 | 6.7552 | 13.547 | 67.1303 | 157.8305 | 37.2503 | 365.8051 | 229.0171 | 418.2249 | 19.1534 | 90.739 | 15.5042 | 240 | 59.9468 | 0 | 416.0363 | 0
7363 | 1026.0544 | 3.6093 | 85.1162 | 109.697 | 66.4357 | 5.7011 | 110.3475 | 5.9572 | 11.912 | 60.7229 | 122.195 | 31.0471 | 329.4272 | 166.8866 | 346.4017 | 13.4227 | 85.4555 | 14.9972 | 223 | 48.6729 | 0 | 383.6806 | 0
7364 | 981.0834 | 3.156 | 71.741 | 103.1959 | 65.9336 | 5.7 | 116.5101 | 6.1256 | 10.388 | 67.6082 | 105.0114 | 15.6257 | 296.1619 | 138.4694 | 313.0552 | 13.0432 | 80.3757 | 15.3061 | 204 | 40.8524 | 0 | 323.5142 | 0
7365 | 950.3639 | 2.4092 | 43.7421 | 99.6831 | 64.7586 | 5.7 | 104.2013 | 5.5389 | 9.412 | 65.6408 | 114.3718 | 10.1165 | 273.8263 | 126.7747 | 288.8754 | 11.7674 | 74.3131 | 14.6404 | 188 | 38.1361 | 0 | 281.7383 | 0
7366 | 916.9283 | 2.0183 | 33.9162 | 95.3107 | 64.3621 | 5.7 | 77.3467 | 5.4595 | 8.911 | 46.2999 | 115.029 | 10.0286 | 248.667 | 109.1837 | 271.6013 | 11.0218 | 70.0242 | 13.5457 | 164 | 37.6156 | 0 | 274.2828 | 0
7367 | 872.8059 | 1.8602 | 32.9297 | 92.802 | 64.39 | 5.7 | 69.2683 | 5.9255 | 7.998 | 31.1827 | 87.993 | 9.7729 | 226.7038 | 98.1273 | 264.8223 | 10.2743 | 68.5632 | 12.9673 | 140 | 34.186 | 0 | 267.4026 | 0
7368 | 846.5857 | 1.7523 | 32.7135 | 95.6992 | 65.9834 | 4.7503 | 76.395 | 5.9278 | 7.414 | 28.1474 | 74.0454 | 9.6338 | 214.4423 | 91.6954 | 256.88 | 9.8321 | 67.1441 | 12.66 | 129 | 34.5978 | 0 | 266.4245 | 0
7369 | 839.7044 | 1.6691 | 32.624 | 96.8748 | 65.1313 | 5.6997 | 73.5612 | 5.8132 | 7.671 | 28.4955 | 73.9344 | 9.5879 | 211.8405 | 86.968 | 245.3147 | 9.8605 | 66.7604 | 11.8178 | 122 | 34.3341 | 0 | 268.3138 | 0
7370 | 825.3839 | 1.6209 | 32.8457 | 98.2255 | 64.1345 | 6.6497 | 68.662 | 5.7018 | 7.774 | 29.5147 | 73.8964 | 9.7078 | 214.0896 | 82.5777 | 239.4046 | 9.7505 | 67.0509 | 11.1713 | 121 | 33.6705 | 0 | 275.0614 | 0
7371 | 802.0746 | 1.7929 | 32.7374 | 96.8932 | 62.1794 | 6.65 | 67.7603 | 5.9459 | 7.785 | 30.761 | 73.5203 | 9.7111 | 211.6099 | 80.1211 | 235.3487 | 9.7834 | 67.1097 | 10.991 | 120 | 32.9457 | 0 | 270.314 | 0
7372 | 788.5713 | 1.9265 | 31.6539 | 96.9192 | 61.2971 | 6.65 | 71.0339 | 5.8819 | 7.716 | 33.9357 | 72.9553 | 9.7046 | 209.3635 | 75.7113 | 231.9971 | 9.7666 | 66.9913 | 10.9898 | 118 | 33.4307 | 0 | 278.3734 | 0
7373 | 792.2667 | 2.3416 | 31.1211 | 96.4075 | 60.7377 | 6.65 | 72.1501 | 5.9444 | 7.456 | 44.3923 | 73.0714 | 9.7117 | 212.5843 | 74.3695 | 226.9356 | 9.801 | 68.5188 | 10.9955 | 114 | 33.1568 | 0 | 299.6528 | 0
7374 | 799.4102 | 3.8045 | 33.1008 | 95.8543 | 54.1129 | 6.65 | 74.3097 | 5.983 | 7.318 | 47.8625 | 75.0487 | 13.683 | 221.8297 | 79.3441 | 234.9224 | 9.6213 | 71.9547 | 11.1797 | 112 | 35.0172 | 0 | 342.7626 | 0
7375 | 833.2962 | 4.9106 | 43.6582 | 98.8076 | 47.1451 | 8.5495 | 84.9073 | 6.1345 | 13.201 | 58.0611 | 95.1538 | 19.5081 | 247.0843 | 140.8692 | 267.291 | 12.0191 | 68.7625 | 13.3902 | 163 | 40.5964 | 0 | 396.006 | 0
7376 | 886.2168 | 12.8716 | 73.646 | 100.3469 | 33.1428 | 20.8966 | 103.6031 | 6.9356 | 19.72 | 87.4807 | 124.5124 | 32.687 | 309.1318 | 209.8828 | 372.9404 | 23.4067 | 72.8194 | 14.958 | 266 | 47.4149 | 0 | 437.8783 | 0
7377 | 978.8039 | 19.7302 | 92.7156 | 109.0093 | 34.6159 | 22.7995 | 119.8469 | 8.9772 | 25.035 | 102.1834 | 145.458 | 39.9688 | 367.7648 | 260.555 | 464.4594 | 31.0548 | 81.1502 | 15.9338 | 310 | 59.0696 | 0 | 488.6048 | 0.17566
7378 | 1078.718 | 16.9935 | 91.5767 | 120.7184 | 40.8849 | 21.8503 | 133.3682 | 8.6841 | 27.364 | 109.1161 | 161.7973 | 40.0916 | 411.104 | 291.1408 | 520.0367 | 32.4745 | 91.0014 | 15.7572 | 352 | 59.5433 | 0 | 532.7115 | 0.19981
7379 | 1140.5143 | 9.1485 | 86.4641 | 125.8052 | 41.7617 | 22.7997 | 137.2644 | 8.3611 | 28.61 | 102.2291 | 168.4825 | 40.1139 | 427.9409 | 306.2476 | 573.8275 | 30.9384 | 95.5149 | 15.8689 | 388 | 60.9976 | 0 | 575.8052 | 0.1923
7380 | 1173.7397 | 5.3638 | 99.3442 | 131.0987 | 37.0835 | 20.9005 | 148.5996 | 8.4046 | 25.15 | 107.853 | 168.8567 | 40.301 | 418.1342 | 325.9397 | 579.5847 | 30.6504 | 95.7206 | 17.0788 | 360 | 70.8268 | 0 | 596.2925 | 0.21677
7381 | 1167.6698 | 4.3059 | 105.1582 | 130.2243 | 34.2617 | 20.9 | 149.972 | 8.2044 | 20.875 | 101.6006 | 172.9239 | 41.9654 | 418.1733 | 325.0216 | 564.0266 | 30.6335 | 93.0651 | 16.9484 | 363 | 65.2212 | 0 | 605.0306 | 0.10982
7382 | 1184.9765 | 4.1174 | 107.3001 | 132.0051 | 30.7201 | 24.6989 | 148.8688 | 7.3716 | 25.224 | 99.1847 | 177.6343 | 44.1258 | 426.4507 | 334.0018 | 567.5659 | 32.3177 | 90.1332 | 17.1329 | 341 | 68.9557 | 0 | 578.7132 | 0.040281
7383 | 1195.8142 | 4.8443 | 107.87 | 137.5973 | 39.8889 | 20.9011 | 153.066 | 6.9622 | 26.331 | 101.7934 | 178.97 | 42.6113 | 425.6045 | 338.987 | 583.8724 | 33.0613 | 90.3888 | 17.6136 | 294 | 72.4039 | 0 | 559.0735 | 0.020266
7384 | 1181.31 | 6.8948 | 103.2219 | 134.6655 | 51.206 | 15.2016 | 156.888 | 7.356 | 20.249 | 106.9347 | 177.688 | 39.7611 | 412.0797 | 332.1851 | 589.9661 | 31.1208 | 92.4851 | 17.7133 | 302 | 73.1518 | 0 | 559.482 | 0.0031907
7385 | 1144.3205 | 6.4174 | 97.1712 | 134.536 | 61.1674 | 7.6021 | 139.1083 | 7.8082 | 16.19 | 108.254 | 174.7718 | 40.1032 | 396.3849 | 310.9371 | 548.7862 | 25.9339 | 93.3801 | 16.8318 | 290 | 72.28 | 0 | 525.1068 | 0
7386 | 1094.4768 | 5.6741 | 92.5641 | 119.0939 | 65.162 | 5.7021 | 121.2173 | 6.33 | 12.635 | 95.4995 | 153.152 | 38.0485 | 352.2461 | 239.0246 | 466.7889 | 14.1132 | 88.469 | 15.4251 | 253 | 65.0808 | 0 | 401.4052 | 0
7387 | 1023.1437 | 4.9732 | 90.3309 | 107.1808 | 64.8998 | 6.6482 | 113.5393 | 5.5063 | 11.875 | 80.9422 | 116.6562 | 30.1603 | 300.5974 | 178.742 | 410.6679 | 9.4574 | 82.6358 | 16.1052 | 261 | 54.9843 | 0 | 338.7961 | 0
7388 | 974.577 | 5.1436 | 78.5195 | 103.343 | 64.444 | 5.7003 | 94.4853 | 5.3663 | 10.264 | 87.9077 | 100.8867 | 15.8977 | 265.1894 | 147.1966 | 368.8718 | 9.2567 | 78.7396 | 15.3147 | 232 | 46.5256 | 0 | 288.439 | 0
7389 | 932.3566 | 4.7282 | 40.5734 | 100.2058 | 63.939 | 4.7503 | 92.7912 | 5.2889 | 9.511 | 86.673 | 98.7296 | 11.7475 | 245.9539 | 131.567 | 329.8611 | 9.1908 | 73.7716 | 13.9068 | 217 | 43.5988 | 0 | 264.195 | 0
7390 | 889.627 | 4.0015 | 27.3244 | 98.6196 | 60.4221 | 5.6997 | 90.6899 | 5.3668 | 9.282 | 67.291 | 91.8021 | 13.1251 | 220.1288 | 118.8022 | 294.8028 | 9.2212 | 69.5964 | 13.3421 | 202 | 42.2328 | 0 | 260.7998 | 0
7391 | 859.5185 | 3.018 | 26.9923 | 96.8316 | 47.7738 | 7.5995 | 86.3206 | 5.7243 | 9.803 | 50.2921 | 79.865 | 11.3528 | 205.2844 | 102.2375 | 291.0595 | 9.1122 | 67.9671 | 12.9544 | 194 | 42.832 | 0 | 260.3307 | 0
7392 | 831.4225 | 2.2492 | 26.7934 | 96.4765 | 45.8329 | 4.7508 | 76.5938 | 5.6789 | 8.817 | 46.0961 | 72.0908 | 9.227 | 207.1609 | 92.7222 | 277.9326 | 9.2392 | 68.3779 | 12.7674 | 188 | 43.1081 | 0 | 264.3587 | 0
7393 | 834.8702 | 6.4019 | 26.8354 | 96.8786 | 45.8249 | 5.6997 | 68.9602 | 5.6204 | 8.378 | 43.1636 | 70.1412 | 8.6124 | 199.7833 | 88.4254 | 263.78 | 9.2626 | 67.9065 | 12.089 | 184 | 42.8015 | 0 | 272.4628 | 0
7394 | 829.9315 | 5.6384 | 26.9949 | 97.69 | 45.3735 | 4.7503 | 73.5678 | 5.6098 | 8.434 | 38.109 | 69.5696 | 10.1639 | 194.4938 | 87.4389 | 257.7835 | 9.2753 | 67.6943 | 11.8061 | 166 | 43.045 | 0 | 271.4499 | 0
7395 | 816.6115 | 2.4334 | 26.9189 | 97.765 | 50.1996 | 5.6997 | 75.3421 | 5.9135 | 8.209 | 32.9135 | 69.3354 | 9.1271 | 188.9049 | 83.4435 | 258.7713 | 9.2545 | 67.7905 | 11.614 | 155 | 43.6272 | 0 | 267.5273 | 0
7396 | 813.8293 | 1.6527 | 26.8941 | 97.0556 | 49.1896 | 5.7 | 69.0184 | 5.7717 | 7.83 | 33.9582 | 69.3881 | 8.4946 | 182.9567 | 81.4662 | 255.6219 | 9.3417 | 67.8793 | 11.5018 | 142 | 45.2458 | 0 | 273.3831 | 0
7397 | 813.9508 | 2.0716 | 26.9995 | 96.8547 | 45.253 | 4.7503 | 66.3423 | 5.6582 | 7.528 | 45.4339 | 69.4273 | 8.3848 | 188.6503 | 79.6379 | 244.431 | 9.3323 | 69.1562 | 11.5403 | 140 | 45.3429 | 0 | 300.6808 | 0
7398 | 819.068 | 3.0279 | 35.745 | 97.3472 | 45.9107 | 4.75 | 75.6378 | 5.6756 | 7.723 | 46.6652 | 70.4612 | 9.1015 | 195.9618 | 85.002 | 234.231 | 9.4163 | 71.831 | 11.5813 | 147 | 44.3424 | 0 | 346.956 | 0
7399 | 840.6068 | 4.3909 | 53.4005 | 105.6227 | 39.9347 | 9.4987 | 101.2225 | 5.644 | 8.176 | 56.3217 | 89.8598 | 16.1951 | 223.3289 | 150.1779 | 250.464 | 11.6889 | 68.903 | 11.8033 | 202 | 46.3325 | 0 | 384.2572 | 0
7400 | 904.1076 | 5.4063 | 75.3233 | 107.8353 | 34.1389 | 19.9471 | 114.0797 | 6.9152 | 9.65 | 88.797 | 121.3965 | 30.9073 | 270.5648 | 221.3026 | 333.8539 | 22.9096 | 70.7764 | 12.0635 | 254 | 50.8446 | 0 | 427.6903 | 0
7401 | 980.4032 | 5.4418 | 88.7209 | 117.5425 | 31.841 | 21.8495 | 118.2678 | 8.3155 | 14.945 | 98.8072 | 148.2817 | 38.9821 | 314.4294 | 256.9495 | 467.2205 | 27.6028 | 78.3424 | 13.0964 | 312 | 61.5858 | 0 | 480.2937 | 0.0083444
7402 | 1055.8439 | 5.3968 | 88.4446 | 126.0293 | 31.1408 | 20.9003 | 130.4962 | 8.4645 | 19.763 | 104.0241 | 160.7752 | 40.0764 | 351.1898 | 266.3165 | 539.8808 | 29.2217 | 88.3578 | 13.1674 | 352 | 66.5909 | 0 | 513.9915 | 0.017316
7403 | 1097.516 | 6.3988 | 86.1646 | 131.4801 | 38.0379 | 21.8497 | 143.7557 | 8.1609 | 23.2395 | 103.5475 | 156.5279 | 39.625 | 363.4293 | 298.174 | 571.43 | 30.3441 | 93.6546 | 13.4585 | 355 | 72.4215 | 0 | 547.8618 | 0.018359
7404 | 1129.2643 | 4.8862 | 90.1397 | 132.2448 | 33.8819 | 23.7495 | 138.8094 | 9.224 | 21.5738 | 103.5912 | 160.207 | 37.473 | 360.5756 | 332.0429 | 565.3312 | 30.5081 | 94.9727 | 14.0109 | 361 | 73.1159 | 0 | 527.1861 | 0.020405
7405 | 1124.0555 | 3.6896 | 66.0966 | 132.9803 | 35.725 | 21.8505 | 130.7595 | 9.9701 | 13.3637 | 95.8489 | 167.3192 | 32.8525 | 351.249 | 337.334 | 545.7796 | 30.7011 | 94.1246 | 14.8202 | 382 | 65.5899 | 0 | 501.6932 | 0.01588
7406 | 1110.7262 | 3.3397 | 44.7957 | 132.7928 | 48.3522 | 14.2521 | 130.3759 | 8.9218 | 10.069 | 89.9699 | 167.9449 | 28.8472 | 347.2732 | 334.6064 | 535.4411 | 31.2011 | 94.625 | 15.6848 | 330 | 61.36 | 0 | 513.4508 | 0.013397
7407 | 1099.514 | 3.5941 | 40.4313 | 131.2334 | 51.8942 | 13.3003 | 138.0209 | 6.4549 | 9.464 | 88.2299 | 167.9579 | 25.6747 | 345.3994 | 330.8754 | 524.2511 | 31.1461 | 93.5869 | 16.1844 | 347 | 59.1984 | 0 | 502.8827 | 0.010021
7408 | 1080.4502 | 4.3449 | 38.9926 | 127.4348 | 53.1286 | 14.2497 | 127.6999 | 5.0599 | 8.21 | 78.6055 | 166.0706 | 24.6944 | 333.6923 | 314.725 | 498.7754 | 30.9755 | 78.9302 | 15.9481 | 262 | 56.932 | 0 | 488.1694 | 0.0019408
7409 | 1053.1667 | 4.9376 | 38.4808 | 125.1278 | 61.6709 | 7.6018 | 117.6825 | 5.0529 | 7.753 | 75.1159 | 165.995 | 26.7135 | 314.3658 | 291.9098 | 443.5658 | 19.9094 | 70.7331 | 15.0616 | 269 | 54.8947 | 0 | 442.5908 | 0
7410 | 1005.7782 | 4.7992 | 36.2052 | 118.4385 | 65.2709 | 5.7021 | 119.0198 | 5.4943 | 10.165 | 70.6382 | 150.4529 | 27.6879 | 278.648 | 213.5775 | 365.178 | 12.1877 | 63.6963 | 14.2584 | 239 | 48.4858 | 0 | 363.1749 | 0
7411 | 961.5275 | 4.3855 | 27.0122 | 106.8125 | 65.7707 | 5.6984 | 113.2737 | 5.451 | 9.73 | 61.8428 | 117.6769 | 24.058 | 243.8402 | 146.0494 | 321.6744 | 9.6831 | 59.146 | 13.609 | 226 | 44.7748 | 0 | 317.7389 | 0
7412 | 912.951 | 3.8462 | 22.7028 | 100.6585 | 66.6399 | 4.7503 | 80.9672 | 5.3237 | 9.303 | 67.7098 | 95.3048 | 14.052 | 220.5616 | 131.3474 | 289.3834 | 9.3071 | 51.7708 | 12.4502 | 209 | 43.2925 | 0 | 276.1686 | 0
7413 | 880.1459 | 3.487 | 22.122 | 98.9374 | 63.7455 | 6.6495 | 66.9551 | 5.5381 | 9.292 | 64.9157 | 80.6359 | 10.0803 | 207.9002 | 113.2933 | 262.8895 | 9.1981 | 49.888 | 12.1756 | 207 | 39.6356 | 0 | 260.7916 | 0
7414 | 852.0027 | 4.3211 | 22.045 | 98.5558 | 65.025 | 4.7505 | 74.8686 | 5.5148 | 8.921 | 46.6305 | 75.1078 | 10.1442 | 195.022 | 100.9118 | 252.213 | 9.1433 | 48.4055 | 12.3102 | 196 | 37.5446 | 0 | 258.1858 | 0
7415 | 841.1056 | 7.7861 | 21.9387 | 96.3047 | 63.7902 | 4.75 | 82.1759 | 5.3673 | 8.829 | 36.5573 | 73.0597 | 10.1228 | 193.3495 | 100.408 | 244.2688 | 9.0259 | 47.6032 | 12.3989 | 174 | 38.5143 | 0 | 273.8605 | 0
7416 | 817.2102 | 5.3217 | 21.976 | 95.3017 | 62.5961 | 5.6997 | 71.7992 | 5.3351 | 10.978 | 35.1267 | 70.5975 | 10.1235 | 191.4163 | 98.8784 | 242.5437 | 9.0512 | 47.0569 | 13.1757 | 155 | 38.8135 | 0 | 271.2816 | 0
7417 | 818.3745 | 2.1388 | 22.2355 | 93.9849 | 62.9513 | 4.7503 | 66.1555 | 5.2605 | 8.929 | 34.391 | 69.6488 | 11.7863 | 187.8242 | 85.5566 | 233.2784 | 9.159 | 44.8667 | 12.4524 | 146 | 39.5098 | 0 | 254.993 | 0
7418 | 815.0466 | 1.6673 | 22.2639 | 93.0854 | 61.1791 | 5.6997 | 68.842 | 5.014 | 7.058 | 33.8928 | 69.6697 | 10.8436 | 185.1039 | 87.8607 | 230.8098 | 9.1558 | 44.5202 | 12.1271 | 151 | 39.2655 | 0 | 262.4346 | 0
7419 | 798.6559 | 1.5652 | 21.9709 | 93.4008 | 61.1772 | 4.7503 | 79.6925 | 5.1766 | 6.751 | 33.357 | 71.3582 | 9.7687 | 181.3547 | 91.9202 | 235.3169 | 9.0815 | 44.8402 | 12.2776 | 149 | 37.3543 | 0 | 259.6226 | 0
7420 | 793.2239 | 1.5688 | 21.9803 | 92.8269 | 59.6526 | 5.6997 | 79.1152 | 4.9838 | 6.947 | 34.1318 | 71.6397 | 8.9008 | 177.2456 | 85.8988 | 236.9999 | 9.0683 | 44.4118 | 12.2129 | 137 | 37.6428 | 0 | 256.7599 | 0
7421 | 792.8526 | 2.1058 | 21.992 | 92.5429 | 60.3475 | 4.7503 | 69.2315 | 4.7435 | 6.97 | 37.761 | 71.0554 | 8.7881 | 174.7199 | 80.3679 | 229.0159 | 8.9447 | 44.4061 | 11.984 | 136 | 37.7808 | 0 | 263.6587 | 0
7422 | 779.0927 | 2.8106 | 23.1509 | 92.4184 | 49.2106 | 7.5992 | 65.3733 | 4.7781 | 7.122 | 40.2082 | 71.1413 | 8.6062 | 168.3917 | 81.7858 | 219.0479 | 9.2604 | 46.3291 | 11.8466 | 127 | 36.8908 | 0 | 286.0531 | 0
7423 | 779.9504 | 3.2359 | 55.5209 | 93.1143 | 54.081 | 5.7005 | 75.3019 | 4.8078 | 7.557 | 39.0607 | 72.0234 | 8.4737 | 171.9563 | 81.805 | 221.6585 | 9.2654 | 44.9141 | 11.8394 | 118 | 36.5631 | 0 | 271.6799 | 0
7424 | 796.4698 | 3.0573 | 62.8469 | 91.9213 | 53.5066 | 4.7503 | 81.6337 | 4.832 | 7.234 | 34.939 | 72.2657 | 8.0165 | 174.3925 | 85.6092 | 224.3257 | 9.1827 | 43.6787 | 11.8536 | 121 | 38.9004 | 0 | 258.0969 | 0
7425 | 806.2534 | 3.423 | 63.3624 | 89.78 | 50.639 | 6.6495 | 69.8659 | 5.0736 | 6.428 | 40.0829 | 83.517 | 6.2855 | 191.7894 | 92.7332 | 220.8468 | 8.8085 | 43.1544 | 12.2411 | 126 | 39.8979 | 0 | 253.611 | 0.0040502
7426 | 825.7857 | 2.3436 | 71.4352 | 90.4816 | 45.8953 | 7.5997 | 70.121 | 4.9924 | 6.254 | 55.4012 | 98.5206 | 5.5392 | 195.7955 | 94.6153 | 220.0882 | 8.7621 | 43.3749 | 12.4487 | 134 | 39.2119 | 0 | 249.7717 | 0.0068989
7427 | 838.3001 | 1.5277 | 72.5907 | 89.6154 | 39.0803 | 9.4995 | 79.2431 | 5.6431 | 6.276 | 61.1071 | 109.4019 | 5.517 | 194.2712 | 100.1024 | 230.9856 | 8.7425 | 43.945 | 12.0472 | 184 | 40.4358 | 0 | 252.3449 | 0.012281
7428 | 845.8228 | 1.1496 | 72.6417 | 89.1299 | 43.4873 | 6.6508 | 86.5056 | 6.0424 | 6.494 | 70.3809 | 100.9617 | 5.525 | 196.9805 | 104.3945 | 246.3251 | 8.8231 | 43.9649 | 12.233 | 191 | 42.7584 | 0 | 265.2367 | 0.0118
7429 | 838.5622 | 1.1905 | 70.7983 | 89.725 | 43.8778 | 5.7018 | 93.0388 | 5.2706 | 6.996 | 60.0296 | 92.7254 | 5.5306 | 205.8157 | 107.2001 | 257.5461 | 8.6754 | 46.633 | 12.8528 | 188 | 44.8784 | 0 | 267.1264 | 0.016654
7430 | 845.0484 | 2.0313 | 63.2124 | 89.9315 | 43.956 | 5.6984 | 79.2549 | 4.6865 | 7.009 | 56.0968 | 92.3359 | 5.564 | 211.6581 | 112.3039 | 280.097 | 8.6271 | 47.9483 | 12.9065 | 177 | 47.8403 | 0 | 267.4165 | 0.018064
7431 | 854.0644 | 2.6813 | 42.5232 | 90.3985 | 45.4043 | 4.7503 | 74.2677 | 4.5997 | 7.122 | 59.2335 | 90.7737 | 6.0188 | 207.5228 | 121.8762 | 292.482 | 8.6859 | 49.0097 | 12.737 | 202 | 49.9644 | 0 | 301.8196 | 0.0095877
7432 | 854.098 | 3.3387 | 24.6977 | 91.1199 | 45.3524 | 4.75 | 89.9314 | 4.9345 | 7.116 | 54.0352 | 89.4972 | 7.0758 | 213.7723 | 126.9037 | 298.4026 | 8.6324 | 48.8761 | 12.9075 | 207 | 49.0386 | 0 | 292.1779 | 0.0010484
7433 | 862.2006 | 3.696 | 21.0229 | 94.2081 | 42.4342 | 6.6495 | 90.325 | 5.2021 | 8.305 | 43.0651 | 105.2694 | 9.747 | 212.4807 | 132.2687 | 297.8181 | 9.0554 | 49.961 | 13.1775 | 196 | 47.9207 | 0 | 295.4476 | 0
7434 | 856.2844 | 3.5859 | 21.004 | 96.2204 | 41.7421 | 8.5495 | 75.3474 | 5.3097 | 9.516 | 39.404 | 112.6224 | 11.5214 | 216.4625 | 124.198 | 285.1567 | 9.1942 | 47.3899 | 12.8816 | 196 | 43.8893 | 0 | 305.9801 | 0
7435 | 827.3843 | 3.5344 | 21.0421 | 96.4832 | 39.9669 | 9.4997 | 69.0097 | 5.2512 | 11.609 | 37.5034 | 86.8543 | 16.3592 | 216.1962 | 119.0737 | 274.518 | 9.2799 | 46.6369 | 12.4153 | 193 | 42.448 | 0 | 282.1701 | 0
7436 | 808.5106 | 3.8158 | 20.8555 | 98.1648 | 51.0364 | 5.7011 | 69.5446 | 5.2229 | 10.497 | 38.5759 | 73.5631 | 13.259 | 208.5593 | 120.1517 | 255.5516 | 9.2302 | 46.7685 | 12.3894 | 188 | 40.5789 | 0 | 283.2366 | 0
7437 | 805.0528 | 4.4081 | 20.7449 | 97.4352 | 49.0796 | 4.7516 | 78.2725 | 5.4955 | 9.144 | 39.5982 | 71.668 | 10.6298 | 190.154 | 120.6724 | 249.8294 | 9.3883 | 47.7475 | 12.244 | 192 | 40.4867 | 0 | 275.0972 | 0
7438 | 803.5161 | 4.2699 | 20.9644 | 96.7114 | 43.799 | 5.7 | 74.0396 | 5.3473 | 8.784 | 38.178 | 71.2815 | 8.5725 | 183.5846 | 117.3794 | 257.6151 | 9.2652 | 46.9215 | 12.0512 | 185 | 37.6951 | 0 | 274.4726 | 0
7439 | 793.7031 | 3.0973 | 20.8895 | 96.2876 | 43.8794 | 5.6984 | 66.7892 | 5.3093 | 8.464 | 40.1144 | 70.9094 | 7.661 | 178.6655 | 112.2039 | 260.0758 | 9.2557 | 45.6126 | 11.9216 | 171 | 40.6721 | 0 | 292.4567 | 0
7440 | 781.3477 | 2.3719 | 20.9094 | 96.4658 | 46.3875 | 4.7503 | 64.7285 | 5.2851 | 8.238 | 39.1015 | 71.9505 | 7.5118 | 183.4515 | 96.2467 | 255.8446 | 9.1769 | 45.4347 | 11.9401 | 149 | 42.0857 | 0 | 313.0391 | 0
7441 | 786.4832 | 2.9545 | 20.9057 | 96.8007 | 44.6724 | 5.6997 | 68.5471 | 5.3386 | 8.267 | 37.5547 | 71.1385 | 7.5791 | 179.6364 | 93.6217 | 254.4496 | 9.2712 | 47.6749 | 12.2104 | 140 | 40.8259 | 0 | 306.1579 | 0
7442 | 809.4444 | 2.1186 | 20.8868 | 100.057 | 43.479 | 5.7 | 76.3246 | 5.609 | 8.307 | 37.625 | 70.1893 | 7.4503 | 179.7878 | 92.1426 | 251.1106 | 9.2774 | 48.3608 | 12.0433 | 142 | 40.6513 | 0 | 288.5875 | 0
7443 | 796.6595 | 1.575 | 20.7273 | 101.9933 | 43.7936 | 10.4487 | 70.3146 | 5.9831 | 8.303 | 36.4426 | 69.3648 | 7.2999 | 178.3009 | 90.4051 | 245.9062 | 9.2847 | 48.3178 | 11.8972 | 144 | 38.7434 | 0 | 278.2068 | 0
7444 | 788.2281 | 1.7462 | 20.7221 | 103.479 | 47.9743 | 9.5003 | 65.711 | 6.0069 | 8.209 | 35.8023 | 69.4355 | 7.523 | 181.8683 | 86.5419 | 242.466 | 9.18 | 48.161 | 11.9583 | 139 | 38.4032 | 0 | 281.5638 | 0
7445 | 769.0857 | 2.2803 | 20.4322 | 104.0483 | 40.0937 | 11.3995 | 64.8873 | 6.0311 | 8.387 | 39.1695 | 69.533 | 7.3774 | 176.6518 | 85.2162 | 236.1097 | 9.2194 | 49.6509 | 11.9631 | 139 | 38.5149 | 0 | 274.3341 | 0
7446 | 754.2696 | 2.9271 | 20.4881 | 104.5614 | 44.2784 | 6.6513 | 66.4008 | 6.1247 | 8.494 | 40.67 | 69.5278 | 7.0489 | 174.5447 | 85.0303 | 233.5237 | 9.1169 | 52.0936 | 11.4108 | 130 | 35.6426 | 0 | 279.8881 | 0
7447 | 760.2333 | 3.1109 | 20.5993 | 103.4371 | 45.4122 | 5.7003 | 75.4718 | 6.1724 | 8.731 | 37.1099 | 70.1535 | 6.9661 | 171.1729 | 83.7103 | 231.3742 | 9.2502 | 49.133 | 11.0711 | 128 | 35.0749 | 0 | 276.0597 | 0
7448 | 764.7787 | 3.1078 | 20.4208 | 101.0114 | 44.4189 | 5.7 | 70.0201 | 6.0461 | 8.032 | 33.6953 | 66.9846 | 5.7363 | 174.8296 | 84.3469 | 227.5261 | 8.8482 | 47.0207 | 11.0357 | 121 | 34.157 | 0 | 275.1967 | 0
7449 | 771.0787 | 2.5187 | 20.4727 | 99.8273 | 53.6568 | 5.7 | 64.1421 | 6.2637 | 8.334 | 42.7013 | 69.6355 | 4.4153 | 187.9026 | 89.332 | 224.3537 | 8.6512 | 46.6972 | 11.0311 | 120 | 33.2906 | 0 | 267.4707 | 0.01504
7450 | 789.1922 | 1.6682 | 23.9047 | 99.8918 | 48.7009 | 5.7 | 66.1063 | 6.0877 | 10.185 | 58.3401 | 76.1889 | 4.063 | 197.4378 | 99.2174 | 223.2464 | 8.6074 | 47.2978 | 11.0299 | 152 | 34.4789 | 0 | 266.3553 | 0.029302
7451 | 810.3924 | 1.6936 | 30.776 | 100.5826 | 43.9827 | 5.7 | 80.509 | 5.8125 | 12.253 | 67.7086 | 90.8802 | 6.5425 | 215.9198 | 107.1294 | 222.4323 | 8.5396 | 47.7166 | 10.976 | 150 | 36.3541 | 0 | 271.4135 | 0.038837
7452 | 819.4668 | 1.7939 | 57.9539 | 100.1621 | 40.7637 | 9.4989 | 97.1947 | 5.4074 | 15.685 | 70.2749 | 95.8708 | 6.0712 | 216.195 | 116.0781 | 245.4451 | 8.6142 | 47.1808 | 11.0894 | 151 | 37.7999 | 0 | 287.603 | 0.054386
7453 | 822.7736 | 2.0435 | 56.6155 | 101.6255 | 50.5516 | 7.6026 | 90.4487 | 5.3078 | 16.592 | 69.1508 | 95.288 | 5.4952 | 211.499 | 117.191 | 282.9492 | 8.6442 | 47.4506 | 11.9042 | 175 | 39.3667 | 0 | 288.4934 | 0.041837
7454 | 822.395 | 2.2834 | 32.8499 | 102.1389 | 49.6436 | 5.6984 | 81.3177 | 5.3284 | 13.401 | 72.0657 | 96.4705 | 5.473 | 206.7069 | 121.2631 | 298.5505 | 8.5372 | 47.6358 | 12.141 | 175 | 39.9297 | 0 | 283.8197 | 0.03729
7455 | 825.6884 | 2.0991 | 25.6443 | 102.5133 | 46.1337 | 4.7503 | 75.4263 | 5.3756 | 9.962 | 68.6699 | 98.834 | 6.1714 | 210.4529 | 123.0183 | 305.5899 | 8.5753 | 46.5431 | 12.127 | 186 | 42.2033 | 0 | 287.4366 | 0.015266
7456 | 838.0427 | 3.3261 | 25.5811 | 103.9845 | 44.8695 | 5.6997 | 77.958 | 5.7827 | 9.274 | 60.1963 | 97.2299 | 8.7138 | 205.4886 | 120.537 | 315.4408 | 8.6094 | 46.2027 | 12.7244 | 168 | 41.8276 | 0 | 281.5298 | 0.0019545
7457 | 846.2083 | 3.954 | 25.6839 | 106.3916 | 44.9367 | 6.6497 | 87.4901 | 6.1772 | 10.511 | 43.0966 | 99.659 | 10.6262 | 204.1512 | 119.9159 | 336.8331 | 8.8077 | 47.2359 | 13.4906 | 162 | 41.5984 | 0 | 291.8268 | 0
7458 | 831.34 | 4.9662 | 25.7203 | 105.6734 | 45 | 6.65 | 82.8029 | 6.6824 | 11.56 | 38.1109 | 100.8469 | 11.6152 | 205.1126 | 115.9758 | 336.8787 | 9.0743 | 48.707 | 13.2331 | 163 | 41.855 | 0 | 325.7881 | 0
7459 | 835.7811 | 4.7607 | 25.6534 | 104.7701 | 45.1265 | 7.5997 | 68.0175 | 7.0724 | 11.506 | 42.5235 | 100.8181 | 10.393 | 202.9921 | 111.6858 | 300.6092 | 8.9503 | 50.0147 | 12.9058 | 150 | 41.5824 | 0 | 326.0167 | 0
7460 | 824.2994 | 4.0376 | 25.5627 | 103.1636 | 45.73 | 6.6503 | 63.7685 | 7.4752 | 9.7 | 45.3984 | 95.4347 | 9.9268 | 196.4509 | 106.3294 | 270.2553 | 9.0936 | 50.6122 | 12.1674 | 127 | 40.6346 | 0 | 306.0128 | 0
7461 | 793.4736 | 4.1907 | 25.7558 | 102.4948 | 51.0694 | 6.65 | 70.8817 | 7.0031 | 8.966 | 44.7131 | 83.4625 | 10.057 | 192.7696 | 101.5011 | 261.8604 | 8.9908 | 50.6907 | 11.7538 | 134 | 40.4389 | 0 | 292.2596 | 0
7462 | 776.6406 | 4.032 | 25.9066 | 102.1739 | 55.0288 | 7.5997 | 68.1214 | 6.9395 | 8.687 | 41.6406 | 78.7922 | 9.4986 | 184.2049 | 96.9262 | 253.7541 | 9.0571 | 49.7801 | 12.1644 | 147 | 38.4674 | 0 | 294.0753 | 0
7463 | 763.8498 | 3.3498 | 25.7958 | 100.719 | 53.28 | 6.6503 | 63.3829 | 6.8372 | 8.01 | 39.6421 | 76.8976 | 10.2755 | 166.4246 | 95.1653 | 246.6434 | 9.0762 | 49.0791 | 11.8992 | 126 | 34.0323 | 0 | 285.9888 | 0
7464 | 750.8483 | 2.4316 | 25.864 | 98.7165 | 58.8636 | 5.7003 | 62.4009 | 7.4118 | 7.952 | 38.4468 | 76.3512 | 9.2025 | 162.7905 | 92.3533 | 242.5857 | 8.9471 | 48.8682 | 11.4271 | 117 | 33.257 | 0 | 285.4167 | 0
7465 | 750.7918 | 2.0788 | 26.1054 | 97.6684 | 54.1007 | 5.7 | 62.5235 | 8.5963 | 7.904 | 38.1679 | 74.3196 | 8.4978 | 160.2801 | 90.0237 | 252.3081 | 8.9785 | 48.1923 | 11.108 | 114 | 35.0889 | 0 | 287.2263 | 0
7466 | 746.7264 | 2.3473 | 26.0102 | 97.1541 | 46.7354 | 5.7 | 66.9662 | 7.4041 | 7.626 | 38.1358 | 73.536 | 8.5477 | 162.2685 | 85.6308 | 251.2627 | 8.9254 | 48.1941 | 11.0172 | 115 | 36.3766 | 0 | 291.6805 | 0
7467 | 736.6794 | 2.1304 | 26.1404 | 97.5254 | 51.2512 | 5.7 | 64.6246 | 6.7161 | 7.411 | 37.7614 | 73.6326 | 8.6217 | 162.0255 | 86.6586 | 238.4271 | 9.053 | 48.3409 | 11.0357 | 116 | 38.1625 | 0 | 287.5114 | 0
7468 | 739.0573 | 2.1361 | 26.0389 | 96.9374 | 55.0843 | 5.7 | 62.0205 | 6.9559 | 7.43 | 41.7645 | 73.7364 | 8.5159 | 161.9978 | 92.1351 | 228.7594 | 8.9935 | 48.3129 | 11.0633 | 110 | 35.2543 | 0 | 288.7294 | 0
7469 | 747.5208 | 2.5022 | 26.0897 | 97.7562 | 51.2516 | 4.7503 | 61.8598 | 8.874 | 7.488 | 50.9129 | 73.9692 | 8.4511 | 164.9252 | 89.9539 | 225.4518 | 9.0557 | 49.7743 | 11.0735 | 112 | 34.8673 | 0 | 322.7959 | 0
7470 | 755.6823 | 3.2992 | 41.2206 | 97.7687 | 45.7481 | 6.6495 | 71.0146 | 8.1352 | 7.92 | 53.1846 | 76.4716 | 9.3184 | 176.1177 | 90.4369 | 242.0285 | 9.0379 | 52.1445 | 11.2368 | 126 | 36.826 | 0 | 345.6013 | 0
7471 | 798.5025 | 4.2857 | 61.0273 | 101.7382 | 48.4989 | 11.3987 | 85.2502 | 6.9953 | 11.817 | 63.4219 | 103.6828 | 22.3387 | 206.7561 | 156.8009 | 270.8994 | 11.6398 | 49.6726 | 12.4818 | 168 | 40.175 | 0 | 409.4362 | 0
7472 | 888.6732 | 5.8241 | 79.7265 | 106.2077 | 43.4987 | 20.8974 | 102.4485 | 7.2849 | 16.273 | 97.0693 | 131.1047 | 37.2449 | 264.1447 | 238.0621 | 351.5417 | 25.0739 | 53.5948 | 12.9189 | 282 | 48.0538 | 0 | 453.0818 | 0
7473 | 992.138 | 11.6045 | 92.1572 | 116.5442 | 29.9514 | 23.7492 | 118.595 | 10.0531 | 24.213 | 111.2744 | 157.095 | 40.577 | 326.5438 | 304.7194 | 486.0899 | 32.2514 | 63.4456 | 12.901 | 279 | 56.5718 | 0 | 555.3548 | 0.079805
7474 | 1082.9659 | 15.049 | 97.2263 | 125.1286 | 25.059 | 23.7566 | 141.1473 | 11.3525 | 27.594 | 112.1212 | 172.6483 | 39.5573 | 377.3102 | 347.7237 | 573.0268 | 34.2783 | 70.6606 | 12.9832 | 350 | 60.426 | 0 | 559.8076 | 0.19418
7475 | 1118.6031 | 14.1157 | 98.1127 | 130.0854 | 33.3759 | 24.6931 | 147.286 | 11.0567 | 27.803 | 105.2596 | 180.0391 | 40.5277 | 411.9439 | 360.8533 | 605.1097 | 35.9565 | 78.97 | 13.776 | 368 | 63.4465 | 0 | 567.645 | 0.18286
7476 | 1154.9104 | 8.2569 | 105.6191 | 129.0399 | 29.8543 | 24.7 | 146.1941 | 10.7753 | 23.53 | 109.4796 | 181.2706 | 40.8275 | 430.0634 | 381.2313 | 602.8663 | 36.5401 | 80.4582 | 14.8546 | 365 | 77.5711 | 0 | 581.2444 | 0.15695
7477 | 1173.3017 | 4.9347 | 103.7961 | 128.6871 | 24.7369 | 23.7503 | 153.9764 | 10.7248 | 18.606 | 102.1667 | 175.7181 | 39.7215 | 431.9835 | 380.3918 | 616.0427 | 36.261 | 78.7126 | 16.0239 | 391 | 73.8093 | 0 | 615.0629 | 0.10293
7478 | 1192.1986 | 4.0296 | 102.943 | 129.0755 | 27.3919 | 25.6495 | 152.6366 | 9.3134 | 26.352 | 100.9661 | 177.165 | 40.5079 | 432.3713 | 367.9845 | 609.0875 | 36.7109 | 79.843 | 15.6263 | 275 | 71.7423 | 0 | 654.5583 | 0.14651
7479 | 1198.2662 | 5.1277 | 103.9451 | 135.9228 | 31.7341 | 25.65 | 156.4322 | 9.0644 | 27.328 | 106.8028 | 181.1678 | 40.8402 | 444.1126 | 363.3944 | 600.8841 | 35.7925 | 78.2776 | 15.3084 | 280 | 71.1093 | 0 | 644.6453 | 0.076041
7480 | 1175.124 | 5.3854 | 102.9987 | 137.0471 | 35.9908 | 18.0521 | 150.57 | 9.7684 | 20.711 | 98.7765 | 179.2438 | 39.5227 | 432.4769 | 367.0297 | 583.1079 | 35.1975 | 80.4298 | 16.3399 | 268 | 73.152 | 0 | 583.183 | 0.012625
7481 | 1133.934 | 5.9444 | 100.7986 | 133.6999 | 43.6956 | 13.3013 | 137.667 | 10.6366 | 17.906 | 97.1468 | 180.5827 | 37.192 | 405.9195 | 352.3347 | 540.0129 | 31.0924 | 80.7283 | 17.49 | 247 | 70.6963 | 0 | 542.298 | 0
7482 | 1069.6079 | 6.3152 | 92.243 | 122.3691 | 48.8184 | 9.5011 | 123.6942 | 9.5828 | 15.471 | 86.2081 | 162.4389 | 36.7797 | 368.0306 | 266.4189 | 471.3194 | 17.1644 | 72.3655 | 17.6592 | 223 | 62.0334 | 0 | 425.9369 | 0
7483 | 1014.712 | 5.3453 | 85.9301 | 111.2237 | 45.1538 | 7.6005 | 102.6556 | 8.4919 | 15.577 | 70.9911 | 125.0657 | 33.9225 | 318.5195 | 187.442 | 406.6101 | 10.6367 | 64.1074 | 17.1375 | 212 | 58.8733 | 0 | 365.8323 | 0
7484 | 960.8182 | 4.5446 | 74.388 | 105.5403 | 53.3355 | 5.7005 | 83.6516 | 7.4386 | 12.425 | 70.7812 | 106.7867 | 21.8955 | 281.7422 | 151.3905 | 349.0368 | 9.6695 | 60.4948 | 16.0217 | 187 | 52.1946 | 0 | 311.6064 | 0
7485 | 921.1102 | 4.273 | 37.5055 | 101.1292 | 53.6429 | 5.7 | 72.8342 | 8.0999 | 10.873 | 65.9756 | 104.0532 | 19.054 | 257.96 | 133.4803 | 301.5763 | 9.6032 | 55.8419 | 14.6153 | 181 | 46.2244 | 0 | 281.5587 | 0
7486 | 885.1497 | 4.0999 | 24.9189 | 98.0904 | 50.8819 | 6.6497 | 67.9759 | 8.7931 | 9.26 | 47.4457 | 101.8413 | 23.2166 | 228.72 | 120.3238 | 267.8216 | 9.4425 | 51.6865 | 13.1479 | 175 | 40.5605 | 0 | 280.2043 | 0
7487 | 860.596 | 3.3881 | 24.8081 | 95.3287 | 54.8535 | 9.4992 | 69.4274 | 7.4986 | 8.003 | 35.9539 | 88.529 | 21.4991 | 210.6325 | 110.2777 | 252.1398 | 9.5199 | 50.4244 | 12.6027 | 151 | 37.663 | 0 | 278.3482 | 0
7488 | 844.417 | 2.2409 | 24.7958 | 95.0104 | 47.4361 | 9.5 | 66.8451 | 6.9709 | 7.851 | 35.2504 | 80.8741 | 15.1472 | 197.8449 | 100.9628 | 255.2613 | 9.5203 | 50.193 | 11.9491 | 133 | 36.5683 | 0 | 277.0268 | 0
7489 | 832.7211 | 1.8606 | 24.8941 | 94.4595 | 53.2072 | 7.6005 | 62.2549 | 8.6009 | 7.666 | 33.7845 | 78.1057 | 13.098 | 198.1472 | 92.3629 | 247.1728 | 9.4945 | 50.2252 | 12.1779 | 123 | 35.7041 | 0 | 279.7167 | 0
7490 | 825.6254 | 1.6643 | 24.8828 | 93.9789 | 52.9957 | 8.5497 | 61.4226 | 8.5035 | 7.577 | 34.8937 | 79.8868 | 12.8406 | 197.7299 | 87.6815 | 232.1598 | 9.5133 | 50.2933 | 11.7067 | 113 | 35.6425 | 0 | 281.6795 | 0
7491 | 814.4409 | 1.4686 | 24.8457 | 94.1722 | 43.9361 | 9.4997 | 65.5413 | 7.3331 | 7.762 | 34.5701 | 81.5493 | 12.6762 | 198.853 | 86.6135 | 231.1397 | 9.3375 | 50.3555 | 11.2504 | 110 | 34.9599 | 0 | 288.6863 | 0
7492 | 806.8866 | 1.5766 | 24.9826 | 94.9833 | 48.0918 | 7.6005 | 65.2758 | 7.4511 | 7.679 | 37.2748 | 80.438 | 12.6752 | 194.6816 | 86.1813 | 232.72 | 9.4552 | 50.4175 | 11.2234 | 110 | 35.059 | 0 | 286.9572 | 0
7493 | 807.7723 | 2.2826 | 24.7289 | 94.1173 | 50.4142 | 8.5521 | 62.8533 | 8.9728 | 7.631 | 48.0416 | 78.7465 | 12.6569 | 197.7356 | 85.9117 | 240.0487 | 9.4225 | 51.8013 | 11.4071 | 112 | 35.5247 | 0 | 313.7141 | 0
7494 | 813.2325 | 3.3448 | 35.8732 | 94.1971 | 44.3707 | 9.4974 | 67.6812 | 7.6853 | 7.654 | 50.8364 | 78.5726 | 14.3346 | 202.6828 | 92.7631 | 254.4278 | 9.4434 | 54.704 | 11.2579 | 123 | 36.3404 | 0 | 362.7411 | 0
7495 | 843.3642 | 4.9516 | 58.8935 | 100.5657 | 41.311 | 10.4497 | 82.4178 | 7.028 | 12.896 | 65.4704 | 98.7458 | 19.4006 | 238.1435 | 161.425 | 257.7317 | 12.0053 | 51.8157 | 11.155 | 190 | 41.8977 | 0 | 404.4865 | 0
7496 | 924.0919 | 9.5518 | 82.7332 | 102.6955 | 28.5029 | 23.7529 | 108.1392 | 8.0654 | 20.012 | 101.5602 | 129.9869 | 33.0352 | 290.6556 | 251.4471 | 338.9081 | 25.0147 | 54.1479 | 12.6824 | 285 | 47.7189 | 0 | 452.4215 | 0
7497 | 1063.8973 | 13.8394 | 93.8971 | 112.9525 | 23.7561 | 26.5926 | 125.5771 | 10.4952 | 26.16 | 111.8617 | 159.2639 | 39.6004 | 351.8796 | 309.6286 | 465.0203 | 33.6799 | 61.4943 | 15.5746 | 293 | 55.4439 | 0 | 529.0078 | 0.019193
7498 | 1177.6805 | 13.754 | 100.1337 | 125.1569 | 31.0595 | 23.7508 | 140.7146 | 11.0922 | 27.242 | 110.2404 | 176.3968 | 40.1781 | 396.1215 | 340.0877 | 555.1476 | 40.3223 | 72.093 | 17.4389 | 366 | 61.429 | 0 | 579.1969 | 0.025143
7499 | 1228.8404 | 13.0464 | 100.1334 | 129.0154 | 28.6643 | 26.5992 | 148.895 | 11.6417 | 26.33 | 104.7046 | 181.8337 | 41.0536 | 408.2651 | 352.5942 | 610.574 | 41.074 | 79.1135 | 17.3199 | 401 | 72.6173 | 0 | 593.4467 | 0.092395
7500 | 1245.6862 | 8.8 | 108.3941 | 132.7274 | 27.5705 | 23.7508 | 158.2926 | 11.4668 | 23.387 | 113.1472 | 186.1673 | 41.7993 | 419.4087 | 385.334 | 634.5696 | 41.3565 | 78.2209 | 16.7648 | 352 | 83.0184 | 0 | 607.6342 | 0.1099
7501 | 1218.4523 | 5.4022 | 115.6328 | 127.9684 | 14.7127 | 24.6997 | 150.7512 | 10.9711 | 20.0255 | 105.6413 | 193.4663 | 43.5349 | 424.2613 | 376.9453 | 609.7863 | 39.946 | 74.9372 | 16.87 | 388 | 74.6071 | 0 | 610.0382 | 0.048662
7502 | 1212.1119 | 4.3005 | 112.4825 | 133.4551 | -3.2254 | 22.8005 | 145.4435 | 10.7204 | 25.6986 | 111.473 | 192.0952 | 43.4034 | 426.752 | 361.7202 | 590.9344 | 40.5892 | 91.0061 | 17.4503 | 356 | 75.2108 | 0 | 605.8578 | 0.027569
7503 | 1223.9479 | 3.8897 | 109.0753 | 131.1551 | -11.1327 | 22.8 | 148.7981 | 10.1904 | 26.5472 | 109.5077 | 184.317 | 42.7816 | 437.2259 | 355.583 | 585.4821 | 41.7054 | 107.4068 | 18.1055 | 332 | 76.0278 | 0 | 617.5026 | 0.022708
7504 | 1205.5021 | 5.056 | 109.2815 | 131.6254 | -6.1389 | 18.0513 | 158.0734 | 10.2995 | 21.3693 | 100.6863 | 181.1046 | 35.2502 | 429.1117 | 350.5763 | 578.9817 | 41.219 | 107.9227 | 18.775 | 344 | 72.9956 | 0 | 618.5479 | 0.00279
7505 | 1148.1637 | 7.5061 | 105.2502 | 125.0645 | 1.8548 | 10.4521 | 147.1603 | 9.8285 | 20.3998 | 95.1839 | 179.756 | 32.4843 | 403.1041 | 325.8588 | 518.2039 | 34.5655 | 97.2636 | 18.73 | 284 | 68.6278 | 0 | 550.1711 | 0
7506 | 1059.6199 | 6.5014 | 96.9069 | 114.9414 | 34.1076 | 7.6008 | 128.7178 | 8.541 | 20.2398 | 83.3852 | 159.509 | 34.7283 | 356.6101 | 259.2946 | 404.9421 | 17.7122 | 89.2957 | 17.5909 | 241 | 59.0862 | 0 | 420.3371 | 0
7507 | 1002.9226 | 5.5382 | 92.293 | 105.9393 | 51.6254 | 7.6 | 112.2341 | 7.5894 | 17.5488 | 64.9769 | 122.9477 | 30.5448 | 312.504 | 198.1255 | 344.5025 | 11.6132 | 82.928 | 16.2123 | 221 | 53.6856 | 0 | 382.7006 | 0
7508 | 966.5344 | 4.4944 | 80.5804 | 104.4131 | 46.1589 | 7.6 | 98.9773 | 6.719 | 11.9375 | 63.7857 | 105.6879 | 16.2942 | 283.9125 | 167.57 | 311.4616 | 11.3339 | 77.4932 | 15.4791 | 201 | 46.8616 | 0 | 324.3344 | 0
7509 | 921.8408 | 4.1033 | 39.0122 | 104.0689 | 47.1125 | 5.7005 | 78.488 | 6.5728 | 9.1927 | 62.0985 | 102.2431 | 9.5241 | 258.2173 | 152.0966 | 288.5115 | 11.2044 | 71.967 | 15.4029 | 191 | 42.3397 | 0 | 299.8556 | 0
7510 | 890.9496 | 3.896 | 25.6562 | 99.0858 | 56.9278 | 5.7 | 68.548 | 6.9543 | 8.3498 | 46.5778 | 97.5275 | 8.7156 | 228.3469 | 145.5746 | 276.7871 | 11.3163 | 68.8095 | 14.3725 | 187 | 41.6845 | 0 | 288 | 0
7511 | 862.0723 | 3.5567 | 25.2808 | 95.6596 | 51.7839 | 5.7016 | 65.7824 | 7.698 | 7.1065 | 37.5722 | 85.2489 | 8.5617 | 207.66 | 135.1208 | 259.1869 | 11.1751 | 67.0691 | 13.7433 | 170 | 39.1609 | 0 | 294.759 | 0
7512 | 841.5498 | 2.2598 | 25.6394 | 95.1872 | 49.6799 | 5.6984 | 68.5939 | 8.673 | 6.7258 | 36.3563 | 77.7631 | 8.6346 | 201.6126 | 122.9557 | 239.5826 | 11.3016 | 66.7792 | 13.262 | 158 | 37.2756 | 0 | 291.8019 | 0
7513 | 833.9172 | 1.7038 | 25.6427 | 95.2082 | 59.3244 | 5.7 | 70.5583 | 7.3984 | 6.8045 | 35.3117 | 75.5398 | 8.752 | 198.5824 | 121.6681 | 237.1548 | 11.1663 | 66.9713 | 12.8078 | 148 | 36.6957 | 0 | 294.177 | 0
7514 | 834.4075 | 2.178 | 25.6879 | 95.3831 | 62.8675 | 5.7 | 66.9395 | 6.7198 | 6.6365 | 36.1228 | 74.8555 | 8.486 | 196.4985 | 116.6362 | 254.2546 | 11.2528 | 67.1539 | 12.3342 | 140 | 36.8026 | 0 | 297.7382 | 0
7515 | 827.68 | 1.9449 | 25.7203 | 94.4821 | 62.2351 | 5.7 | 65.3997 | 6.9079 | 6.5313 | 36.6701 | 74.2926 | 8.3005 | 194.7877 | 114.8844 | 268.6166 | 11.2444 | 66.8139 | 11.9143 | 121 | 37.3178 | 0 | 295.4799 | 0
7516 | 823.2783 | 1.7496 | 25.7907 | 94.2872 | 54.7392 | 5.7 | 65.0973 | 8.9781 | 6.434 | 38.8686 | 73.7974 | 8.2756 | 193.6454 | 114.7235 | 255.2 | 11.1165 | 66.6554 | 11.7249 | 117 | 36.43 | 0 | 295.0421 | 0
7517 | 824.1765 | 2.1044 | 25.9186 | 94.4117 | 50.4199 | 6.6497 | 69.5732 | 8.1924 | 6.4788 | 48.0564 | 73.8527 | 8.4634 | 194.8746 | 114.9665 | 243.9095 | 11.2072 | 68.1181 | 11.8274 | 119 | 34.8116 | 0 | 314.3854 | 0
7518 | 843.0991 | 3.1341 | 38.4109 | 95.2316 | 59.3314 | 5.7003 | 73.0706 | 7.0196 | 6.8898 | 50.68 | 75.147 | 12.1736 | 205.9562 | 118.1863 | 253.9386 | 11.0686 | 70.6703 | 11.7319 | 124 | 35.5576 | 0 | 367.9707 | 0
7519 | 877.982 | 4.7345 | 61.1893 | 101.8565 | 60.754 | 7.5995 | 84.8615 | 7.2814 | 13.0313 | 63.0314 | 97.1544 | 21.5957 | 233.1928 | 165.6681 | 286.6291 | 13.7554 | 67.7775 | 12.0977 | 195 | 39.1835 | 0 | 419.1326 | 0
7520 | 944.904 | 8.207 | 83.3024 | 102.5742 | 47.8147 | 18.9968 | 104.2368 | 9.2798 | 17.9943 | 100.9788 | 123.5532 | 35.5353 | 285.3536 | 228.6379 | 349.2489 | 27.3504 | 70.5971 | 13.2914 | 263 | 46.1057 | 0 | 484.9784 | 0
7521 | 1036.0192 | 11.9904 | 93.8142 | 113.2284 | 41.1871 | 23.7553 | 130.87 | 10.1688 | 25.3267 | 121.1608 | 145.8784 | 42.4624 | 356.3588 | 284.6458 | 450.082 | 34.8619 | 78.8703 | 15.6569 | 338 | 57.5147 | 0 | 541.9816 | 0.14691
7522 | 1125.8757 | 15.5397 | 100.3195 | 121.7217 | 32.8232 | 24.7 | 149.6762 | 10.9867 | 27.519 | 123.3812 | 166.1042 | 41.8087 | 403.9859 | 313.7074 | 560.5693 | 38.495 | 89.1763 | 14.9637 | 374 | 65.3257 | 0 | 578.8624 | 0.10519
7523 | 1178.3679 | 9.2969 | 103.6302 | 125.7665 | 37.537 | 24.6931 | 150.1373 | 10.6474 | 28.0235 | 110.8918 | 177.9954 | 41.3896 | 425.9086 | 337.2505 | 632.898 | 38.6393 | 96.9026 | 16.1118 | 372 | 73.2413 | 0 | 595.7671 | 0.11196
7524 | 1189.9364 | 9.2118 | 104.5948 | 130.0634 | 42.6104 | 23.7503 | 148.2881 | 10.5574 | 26.9227 | 116.1569 | 177.5509 | 41.1068 | 433.8899 | 360.8121 | 634.5539 | 38.5453 | 97.9413 | 17.2269 | 380 | 75.847 | 0 | 602.8335 | 0.1906
7525 | 1179.4664 | 9.1742 | 103.0437 | 130.2939 | 33.8392 | 22.8003 | 160.5735 | 10.8534 | 21.3232 | 111.0338 | 178.2467 | 41.8099 | 432.1883 | 363.9855 | 597.3374 | 37.2801 | 94.4152 | 17.7952 | 379 | 71.6794 | 0 | 611.0298 | 0.20835
7526 | 1177.1685 | 5.335 | 102.6659 | 135.0211 | 38.384 | 21.8503 | 161.555 | 11.2365 | 24.6807 | 106.7979 | 182.3684 | 40.7721 | 438.5276 | 377.3253 | 604.2149 | 38.8998 | 92.1638 | 18.291 | 323 | 76.3195 | 0 | 627.0415 | 0.16551
7527 | 1198.2524 | 5.0118 | 104.4847 | 136.6217 | 41.9975 | 22.7997 | 157.9236 | 9.5407 | 25.886 | 109.3923 | 185.2499 | 40.8243 | 435.1288 | 378.7286 | 612.7285 | 39.342 | 96.1964 | 18.1925 | 312 | 78.3277 | 0 | 622.619 | 0.071181
7528 | 1185.6064 | 5.5202 | 105.6005 | 136.5202 | 42.6186 | 18.0513 | 155.1575 | 8.7146 | 23.055 | 101.8386 | 186.4701 | 40.183 | 425.0312 | 370.127 | 620.0178 | 38.1225 | 99.7627 | 18.1535 | 327 | 76.1718 | 0 | 620.4556 | 0.006452
7529 | 1135.3989 | 5.5922 | 99.9278 | 132.6617 | 43.2744 | 14.255 | 147.99 | 8.5797 | 21.4329 | 101.5629 | 185.6431 | 39.617 | 405.5806 | 338.4887 | 576.0026 | 33.3208 | 97.351 | 17.9757 | 286 | 72.8586 | 0 | 564.3071 | 0
7530 | 1064.5371 | 5.8352 | 93.4064 | 121.2219 | 56.4207 | 6.6482 | 126.7705 | 8.2106 | 22.2062 | 86.9438 | 163.2831 | 35.9929 | 365.0598 | 271.806 | 473.658 | 19.0288 | 90.3013 | 17.1408 | 268 | 59.9199 | 0 | 452.307 | 0
7531 | 1020.3747 | 5.7835 | 89.3287 | 109.6053 | 55.8017 | 7.5997 | 111.3926 | 7.3486 | 21.0868 | 67.4381 | 126.1145 | 27.1957 | 313.539 | 221.7246 | 405.1362 | 13.568 | 85.0309 | 15.765 | 242 | 63.4053 | 0 | 400.9739 | 0
7532 | 967.8515 | 5.3921 | 77.0905 | 104.7641 | 50.0312 | 6.6521 | 96.3437 | 6.8283 | 13.9096 | 69.5355 | 107.4036 | 16.1254 | 267.1281 | 193.7658 | 374.0215 | 12.7668 | 78.6656 | 14.6364 | 227 | 45.3692 | 0 | 331.5909 | 0
7533 | 917.1582 | 4.4088 | 39.6529 | 101.2493 | 53.9761 | 6.6482 | 80.0634 | 6.6318 | 9.986 | 66.5145 | 103.794 | 11.155 | 252.2964 | 148.4162 | 331.5497 | 11.5599 | 72.6785 | 13.8167 | 207 | 50.3669 | 0 | 302.2371 | 0
7534 | 894.4634 | 4.0542 | 26.4055 | 98.4385 | 60.5467 | 6.65 | 70.8336 | 6.4294 | 8.4882 | 48.3927 | 96.8521 | 12.66 | 229.7229 | 131.9469 | 270.2931 | 11.1488 | 69.933 | 13.0418 | 194 | 56.9775 | 0 | 298.994 | 0
7535 | 859.4518 | 4.0315 | 25.3378 | 97.1344 | 53.4062 | 6.65 | 66.5817 | 6.787 | 7.4958 | 37.6513 | 83.2767 | 13.7998 | 209.6105 | 116.6683 | 266.1066 | 10.6403 | 68.2067 | 12.7083 | 177 | 53.287 | 0 | 294.5491 | 0
7536 | 839.2901 | 3.0247 | 25.0648 | 97.1099 | 47.3074 | 5.7003 | 71.2389 | 6.9883 | 7.192 | 36.4477 | 76.119 | 11.2146 | 199.5538 | 101.6571 | 258.1961 | 10.8164 | 67.3098 | 12.1068 | 145 | 54.3132 | 0 | 284.2867 | 0
7537 | 829.9881 | 4.2747 | 25.1725 | 95.6983 | 56.002 | 5.7 | 71.6557 | 7.1718 | 7.178 | 36.1213 | 75.028 | 10.0852 | 197.1629 | 94.891 | 242.1026 | 10.5745 | 67.3554 | 11.3786 | 139 | 54.5704 | 0 | 282.4434 | 0
7538 | 828.8895 | 2.6317 | 25.0937 | 93.5794 | 61.6687 | 5.7 | 66.3853 | 6.9809 | 7.148 | 35.6114 | 75.4435 | 9.9026 | 193.6014 | 94.0507 | 230.8768 | 10.5624 | 67.508 | 11.2101 | 130 | 54.3572 | 0 | 281.942 | 0
7539 | 816.1587 | 1.5084 | 25.163 | 92.5262 | 56.9907 | 5.7 | 63.7832 | 6.3287 | 7.347 | 36.0592 | 76.0023 | 9.8352 | 194.1548 | 92.039 | 231.0719 | 10.5495 | 67.4349 | 11.2031 | 136 | 54.5824 | 0 | 284.4588 | 0
7540 | 864.037 | 4.8686 | 25.0992 | 92.4253 | 58.5847 | 4.7503 | 112.3123 | 9.4765 | 12.5002 | 74.2506 | 144.2328 | 22.5948 | 347.5324 | 88.1343 | 404.5283 | 10.0404 | 67.4825 | 18.3173 | 121 | 54.6155 | 0 | 281.0317 | 0
7541 | 887.4464 | 4.3365 | 62.0098 | 136.7316 | 55.7654 | 9.4158 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 202.657 | 322.4765 | 18.9706 | 78.1205 | 14.7206 | 116 | 47.9845 | 0 | 376.4442 | 0
7542 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 123 | 44.0063 | 0 | 346.8886 | 0
7543 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4766 | 15.8148 | 60.662 | 14.7206 | 185 | 44.0063 | 0 | 346.8886 | 0
7544 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 302 | 44.0063 | 0 | 346.8886 | 0
7545 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 294 | 44.0063 | 0 | 346.8886 | 0.057997
7546 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 368 | 44.0063 | 0 | 346.8886 | 0.098254
7547 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 373 | 44.0063 | 0 | 346.8886 | 0.085869
7548 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 366 | 44.0063 | 0 | 346.8886 | 0.11137
7549 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 376 | 44.0063 | 0 | 346.8886 | 0.10162
7550 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 325 | 44.0063 | 0 | 346.8886 | 0.042144
7551 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 279 | 44.0063 | 0 | 346.8886 | 0.027958
7552 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 265 | 44.0063 | 0 | 346.8886 | 0.004902
7553 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 258 | 44.0063 | 0 | 346.8886 | 0
7554 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 247 | 44.0063 | 0 | 346.8886 | 0
7555 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 227 | 44.0063 | 0 | 346.8886 | 0
7556 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 199 | 44.0063 | 0 | 346.8886 | 0
7557 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 185 | 44.0063 | 0 | 346.8886 | 0
7558 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 180 | 44.0063 | 0 | 346.8886 | 0
7559 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 164 | 44.0063 | 0 | 346.8886 | 0
7560 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 151 | 44.0063 | 0 | 346.8886 | 0
7561 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 141 | 44.0063 | 0 | 346.8886 | 0
7562 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 129 | 44.0063 | 0 | 346.8886 | 0
7563 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 130 | 44.0063 | 0 | 346.8886 | 0
7564 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 122 | 44.0063 | 0 | 346.8886 | 0
7565 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 113 | 44.0063 | 0 | 346.8886 | 0
7566 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 121 | 44.0063 | 0 | 346.8886 | 0
7567 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 196 | 44.0063 | 0 | 346.8886 | 0
7568 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 287 | 44.0063 | 0 | 346.8886 | 0
7569 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 318 | 44.0063 | 0 | 346.8886 | 0.036343
7570 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4766 | 15.8148 | 60.662 | 14.7206 | 352 | 44.0063 | 0 | 346.8886 | 0.033876
7571 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 347 | 44.0063 | 0 | 346.8886 | 0.020918
7572 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 330 | 44.0063 | 0 | 346.8886 | 0.021688
7573 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 399 | 44.0063 | 0 | 346.8886 | 0.030068
7574 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 294 | 44.0063 | 0 | 346.8886 | 0.025225
7575 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 289 | 44.0063 | 0 | 346.8886 | 0.027801
7576 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 270 | 44.0063 | 0 | 346.8886 | 0.001545
7577 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 267 | 44.0063 | 0 | 346.8886 | 0
7578 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 239 | 44.0063 | 0 | 346.8886 | 0
7579 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 214 | 44.0063 | 0 | 346.8886 | 0
7580 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 199 | 44.0063 | 0 | 346.8886 | 0
7581 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 182 | 44.0063 | 0 | 346.8886 | 0
7582 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 177 | 44.0063 | 0 | 346.8886 | 0
7583 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 156 | 44.0063 | 0 | 346.8886 | 0
7584 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 148 | 44.0063 | 0 | 346.8886 | 0
7585 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 141 | 44.0063 | 0 | 346.8886 | 0
7586 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 137 | 44.0063 | 0 | 346.8886 | 0
7587 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 133 | 44.0063 | 0 | 346.8886 | 0
7588 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 128 | 44.0063 | 0 | 346.8886 | 0
7589 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4766 | 15.8148 | 60.662 | 14.7206 | 127 | 44.0063 | 0 | 346.8886 | 0
7590 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 127 | 44.0063 | 0 | 346.8886 | 0
7591 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4766 | 15.8148 | 60.662 | 14.7206 | 128 | 44.0063 | 0 | 346.8886 | 0
7592 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 133 | 44.0063 | 0 | 346.8886 | 0
7593 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 133 | 44.0063 | 0 | 346.8886 | 0.080795
7594 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 140 | 44.0063 | 0 | 346.8886 | 0.13083
7595 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 150 | 44.0063 | 0 | 346.8886 | 0.16834
7596 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 160 | 44.0063 | 0 | 346.8886 | 0.19813
7597 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 157 | 44.0063 | 0 | 346.8886 | 0.21933
7598 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 157 | 44.0063 | 0 | 346.8886 | 0.18911
7599 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 181 | 44.0063 | 0 | 346.8886 | 0.12742
7600 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 184 | 44.0063 | 0 | 346.8886 | 0.015072
7601 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 192 | 44.0063 | 0 | 346.8886 | 0
7602 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 194 | 44.0063 | 0 | 346.8886 | 0
7603 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 191 | 44.0063 | 0 | 346.8886 | 0
7604 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 208 | 44.0063 | 0 | 346.8886 | 0
7605 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 237 | 44.0063 | 0 | 346.8886 | 0
7606 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 218 | 44.0063 | 0 | 346.8886 | 0
7607 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 217 | 44.0063 | 0 | 346.8886 | 0
7608 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 200 | 44.0063 | 0 | 346.8886 | 0
7609 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 206 | 44.0063 | 0 | 346.8886 | 0
7610 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4766 | 15.8148 | 60.662 | 14.7206 | 208 | 44.0063 | 0 | 346.8886 | 0
7611 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 208 | 44.0063 | 0 | 346.8886 | 0
7612 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 182 | 44.0063 | 0 | 346.8886 | 0
7613 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 151 | 44.0063 | 0 | 346.8886 | 0
7614 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 137 | 44.0063 | 0 | 346.8886 | 0
7615 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 132 | 44.0063 | 0 | 346.8886 | 0
7616 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 130 | 44.0063 | 0 | 346.8886 | 0
7617 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 124 | 44.0063 | 0 | 346.8886 | 0.014473
7618 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 199 | 44.0063 | 0 | 346.8886 | 0.044725
7619 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 189 | 44.0063 | 0 | 346.8886 | 0.093263
7620 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 178 | 44.0063 | 0 | 346.8886 | 0.11563
7621 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 207 | 44.0063 | 0 | 346.8886 | 0.09131
7622 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 199 | 44.0063 | 0 | 346.8886 | 0.048291
7623 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 200 | 44.0063 | 0 | 346.8886 | 0.026028
7624 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 179 | 44.0063 | 0 | 346.8886 | 0.0019365
7625 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 192 | 44.0063 | 0 | 346.8886 | 0
7626 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2683 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 181 | 44.0063 | 0 | 346.8886 | 0
7627 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 157 | 44.0063 | 0 | 346.8886 | 0
7628 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 133 | 44.0063 | 0 | 346.8886 | 0
7629 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 127 | 44.0063 | 0 | 346.8886 | 0
7630 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7465 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 121 | 44.0063 | 0 | 346.8886 | 0
7631 | 887.4464 | 4.3365 | 55.4213 | 113.2541 | 55.7668 | 9.4145 | 92.93 | 7.5356 | 10.2682 | 62.7503 | 118.7464 | 19.5102 | 252.9121 | 179.6459 | 322.4765 | 15.8148 | 60.662 | 14.7206 | 121 | 44.0063 | 0 | 346.8886 | 0
7632 | 887.4464 | 4.3365 | 5.9802 | 12.2356 | 55.7668 | 9.4145 | 92.93 | 0.80885 | 10.2683 | 62.7503 | 12.7908 | 2.0954 | 252.9121 | 19.3804 | 322.4765 | 17.1392 | 60.662 | 1.5796 | 120 | 44.0063 | 0 | 346.8886 | 0
7633 | 887.4464 | 4.3365 | 5.9818 | 12.239 | 55.7668 | 9.4145 | 92.93 | 0.80908 | 10.2682 | 62.7503 | 12.7938 | 2.096 | 252.9121 | 19.3858 | 322.4765 | 17.1392 | 60.662 | 1.5801 | 126 | 44.0063 | 0 | 346.8886 | 0
7634 | 887.4464 | 4.3365 | 5.9818 | 12.239 | 55.7668 | 9.4145 | 92.93 | 0.80908 | 10.2682 | 62.7503 | 12.7938 | 2.096 | 252.9121 | 19.3858 | 322.4765 | 17.1392 | 60.662 | 1.5801 | 115 | 44.0063 | 0 | 346.8886 | 0
7635 | 887.4464 | 4.3365 | 5.9818 | 12.239 | 55.7668 | 9.4145 | 92.93 | 0.80908 | 10.2682 | 62.7503 | 12.7938 | 2.096 | 252.9121 | 19.3858 | 322.4765 | 17.1392 | 60.662 | 1.5801 | 110 | 44.0063 | 0 | 346.8886 | 0
7636 | 887.4464 | 4.3365 | 5.9818 | 12.239 | 55.7668 | 9.4145 | 92.93 | 0.80908 | 10.2682 | 62.7503 | 12.7938 | 2.096 | 252.9121 | 19.3858 | 322.4765 | 17.1392 | 60.662 | 1.5801 | 104 | 44.0063 | 0 | 346.8886 | 0
7637 | 887.4464 | 4.3365 | 5.9818 | 12.239 | 55.7668 | 9.4145 | 92.93 | 0.80908 | 10.2682 | 62.7503 | 12.7938 | 2.096 | 252.9121 | 19.3858 | 322.4766 | 17.1392 | 60.662 | 1.5801 | 104 | 44.0063 | 0 | 346.8886 | 0
7638 | 887.4464 | 4.3365 | 5.9818 | 12.239 | 55.7668 | 9.4145 | 92.93 | 0.80908 | 10.2683 | 62.7503 | 12.7938 | 2.096 | 252.9121 | 19.3858 | 322.4765 | 17.1392 | 60.662 | 1.5801 | 107 | 44.0063 | 0 | 346.8886 | 0
7639 | 887.4464 | 4.3365 | 5.9818 | 12.239 | 55.7668 | 9.4145 | 92.93 | 0.80908 | 10.2682 | 62.7503 | 12.7938 | 2.096 | 252.9121 | 19.3858 | 322.4765 | 17.1392 | 60.662 | 1.5801 | 158 | 44.0063 | 0 | 346.8886 | 0
7640 | 887.4464 | 3.2355 | 5.9818 | 12.239 | 55.7778 | 9.4041 | 71.3294 | 0.80908 | 7.8986 | 47.7533 | 12.32 | 2.096 | 168.3626 | 19.3858 | 238.9237 | 13.4728 | 48.0385 | 1.5801 | 297 | 40.9256 | 0 | 314.8941 | 0
7641 | 982.4108 | 10.6587 | 72.8096 | 91.9346 | 53.8972 | 20.9046 | 114.9473 | 7.1681 | 19.0786 | 97.561 | 119.3585 | 29.3883 | 304.2565 | 231.7807 | 445.4228 | 32.612 | 59.6221 | 12.5429 | 305 | 59.0222 | 0 | 465.7465 | 0.0074994
7642 | 1078.6749 | 13.2829 | 101.447 | 124.96 | 60.2095 | 20.9 | 148.7344 | 11.7341 | 26.649 | 114.8855 | 178.0378 | 41.3693 | 394.6277 | 337.1815 | 588.7656 | 42.2166 | 72.1546 | 16.2978 | 367 | 66.6136 | 0 | 482.378 | 0.027345
7643 | 1147.2676 | 8.709 | 102.2684 | 132.2323 | 60.9102 | 19.9503 | 161.6621 | 12.2506 | 28.603 | 109.4994 | 182.7318 | 40.7565 | 420.9482 | 354.4521 | 621.7835 | 42.0734 | 76.9776 | 16.3202 | 336 | 72.2085 | 0 | 529.5393 | 0.011943
7644 | 1169.4974 | 4.9392 | 106.75 | 133.0907 | 59.6193 | 20.8997 | 168.0183 | 12.0524 | 25.038 | 112.7923 | 185.6714 | 36.9388 | 428.6088 | 377.8398 | 620.4863 | 40.6246 | 83.6822 | 17.1658 | 333 | 82.1419 | 0 | 560.9588 | 0.016169
7645 | 1170.5784 | 4.1929 | 108.2888 | 132.3129 | 57.563 | 22.7995 | 158.61 | 11.8958 | 19.289 | 113.0989 | 186.5726 | 38.8448 | 432.4879 | 382.6989 | 602.7563 | 42.6781 | 79.3104 | 17.9672 | 387 | 76.8313 | 0 | 573.8135 | 0.011803
7646 | 1163.5568 | 5.1688 | 105.7438 | 136.0105 | 56.3426 | 23.7497 | 160.4675 | 10.8049 | 22.825 | 108.8279 | 191.2584 | 41.632 | 442.9817 | 391.2413 | 601.0087 | 43.3377 | 79.3538 | 18.5858 | 303 | 79.5577 | 0 | 573.597 | 0.008161
7647 | 1179.5704 | 5.6457 | 101.7236 | 140.6178 | 57.302 | 22.8003 | 171.4782 | 10.0161 | 24.075 | 114.4284 | 195.0977 | 40.8358 | 464.2136 | 386.4188 | 605.1881 | 42.7574 | 79.983 | 18.4718 | 272 | 78.1098 | 0 | 580.2801 | 0.0023089
7648 | 1167.8706 | 5.8242 | 99.1368 | 143.4168 | 63.5979 | 17.1016 | 164.5715 | 8.9842 | 20.644 | 115.0472 | 194.863 | 42.7039 | 458.9987 | 370.4178 | 593.8874 | 40.8569 | 79.3302 | 18.5164 | 277 | 76.3475 | 0 | 557.055 | 0
7649 | 1118.7229 | 5.7762 | 95.3983 | 134.7713 | 69.7043 | 11.4016 | 141.835 | 8.2822 | 18.947 | 108.7004 | 191.1387 | 43.0451 | 416.133 | 346.2575 | 537.6767 | 34.3842 | 78.1377 | 18.4414 | 245 | 72.4487 | 0 | 509.3362 | 0
7650 | 1048.7965 | 5.3678 | 90.7057 | 121.8446 | 74.9359 | 6.6513 | 132.4972 | 6.5269 | 18.602 | 95.7772 | 168.6648 | 41.1696 | 405.6302 | 272.3817 | 453.7661 | 19.4848 | 74.2662 | 17.9012 | 240 | 62.594 | 0 | 402.6182 | 0
7651 | 996.9144 | 5.1161 | 87.2505 | 108.5895 | 75.4153 | 6.65 | 123.5623 | 5.2389 | 16.668 | 83.248 | 131.0001 | 34.1612 | 405.8865 | 195.5116 | 396.5526 | 13.1255 | 65.3845 | 16.829 | 226 | 51.846 | 0 | 356.8133 | 0
7652 | 953.7046 | 4.2901 | 76.0633 | 103.3217 | 76.6619 | 5.7003 | 101.4921 | 4.9689 | 11.782 | 83.5522 | 112.7475 | 19.9361 | 384.5672 | 163.5116 | 354.8721 | 12.2749 | 58.3501 | 15.4504 | 202 | 47.7261 | 0 | 314.6086 | 0
7653 | 907.5575 | 3.5615 | 38.3807 | 100.2148 | 76.669 | 5.7 | 89.4286 | 4.8318 | 9.057 | 76.4812 | 108.3252 | 14.311 | 358.3932 | 147.6208 | 303.388 | 12.325 | 53.2162 | 13.7037 | 178 | 40.9957 | 0 | 273.7772 | 0
7654 | 872.5601 | 3.2225 | 25.8789 | 97.6861 | 77.6679 | 4.7503 | 85.0075 | 4.9304 | 8.024 | 52.8188 | 100.5439 | 13.9383 | 335.0143 | 129.1628 | 272.1735 | 12.2595 | 48.6236 | 13.0237 | 161 | 38.9857 | 0 | 271.6119 | 0
7655 | 854.941 | 3.5437 | 25.4283 | 95.8076 | 76.6765 | 5.6997 | 72.7418 | 4.4958 | 6.934 | 39.8184 | 84.7108 | 13.8704 | 323.0428 | 114.7332 | 264.1425 | 12.3648 | 46.522 | 13.2779 | 152 | 36.9832 | 0 | 254.0983 | 0
7656 | 831.4607 | 2.2114 | 25.4339 | 93.5481 | 77.4012 | 4.7503 | 71.8028 | 4.237 | 6.615 | 38.088 | 76.3249 | 13.7906 | 309.7858 | 106.9505 | 241.7869 | 12.3639 | 45.7104 | 13.1315 | 139 | 37.4808 | 0 | 241.6865 | 0
7657 | 823.8148 | 1.533 | 25.419 | 92.8498 | 76.4036 | 5.6997 | 78.7911 | 4.1949 | 6.665 | 36.84 | 73.7135 | 13.5585 | 304.4269 | 101.9643 | 233.652 | 12.2938 | 45.9074 | 12.2737 | 130 | 38.0966 | 0 | 242.7016 | 0
7658 | 819.6154 | 1.434 | 25.4412 | 92.7454 | 77.5475 | 4.7503 | 80.9003 | 4.4458 | 6.778 | 35.7568 | 75.6247 | 13.451 | 306.4011 | 96.1444 | 238.4348 | 12.2865 | 45.9949 | 11.6684 | 126 | 35.8963 | 0 | 240.9781 | 0
7659 | 805.7679 | 1.3787 | 25.3938 | 93.9338 | 74.9164 | 7.5992 | 80.0905 | 4.3196 | 6.435 | 35.4565 | 78.1772 | 13.4867 | 304.0136 | 91.9813 | 246.416 | 12.1412 | 46.1485 | 11.4964 | 124 | 34.6568 | 0 | 242.8835 | 0
7660 | 816.6125 | 1.5796 | 25.2026 | 93.2962 | 76.9662 | 5.7005 | 69.5879 | 4.5166 | 6.613 | 38.2244 | 79.0971 | 13.4915 | 298.6687 | 88.4341 | 246.5002 | 11.999 | 46.1213 | 11.6099 | 111 | 34.5705 | 0 | 236.7569 | 0
7661 | 814.3096 | 1.9869 | 25.3203 | 93.0513 | 77.882 | 4.7503 | 72.1648 | 4.6279 | 6.872 | 48.9139 | 77.9422 | 13.3952 | 301.4258 | 86.7103 | 236.2235 | 12.1608 | 47.5957 | 11.3386 | 111 | 34.6758 | 0 | 265.3641 | 0
7662 | 820.6905 | 3.0412 | 32.6907 | 93.0469 | 77.7411 | 4.75 | 84.1403 | 4.5725 | 6.759 | 51.1896 | 75.0843 | 16.606 | 309.9036 | 94.8159 | 235.1412 | 11.3933 | 50.0668 | 11.1814 | 110 | 36.8647 | 0 | 309.9159 | 0
7663 | 864.8552 | 4.004 | 50.9759 | 100.9738 | 71.5639 | 10.4484 | 99.6428 | 4.7852 | 12.913 | 59.3378 | 97.7932 | 19.5409 | 339.2406 | 160.4318 | 259.1207 | 14.4538 | 47.5463 | 12.2737 | 174 | 43.9923 | 0 | 362.2564 | 0
7664 | 950.8063 | 11.6352 | 79.7899 | 107.0212 | 61.0772 | 19.9474 | 117.2208 | 5.4404 | 19.535 | 93.2305 | 142.247 | 33.302 | 398.4089 | 241.7865 | 367.8779 | 29.8916 | 51.4944 | 16.1733 | 268 | 54.0007 | 0 | 402.8829 | 0
7665 | 1030.8287 | 25.6935 | 93.4091 | 121.7225 | 58.5548 | 21.8495 | 130.5069 | 6.2675 | 23.33 | 99.7098 | 167.1142 | 40.2111 | 481.3334 | 305.517 | 512.0131 | 37.6231 | 60.8974 | 16.111 | 287 | 55.7042 | 0 | 482.6611 | 0.0040194
7666 | 1119.8451 | 29.1488 | 100.2034 | 132.6147 | 59.6137 | 20.9003 | 150.7533 | 8.3291 | 24.573 | 101.1258 | 176.5564 | 43.1655 | 535.4992 | 338.7689 | 594.3714 | 40.1536 | 72.311 | 16.9912 | 319 | 67.2375 | 0 | 537.2267 | 0.0056118
7667 | 1203.7951 | 21.3395 | 100.1963 | 138.1981 | 58.0732 | 22.7995 | 157.1304 | 8.8382 | 25.084 | 98.1447 | 181.5861 | 45.5037 | 555.7755 | 355.6797 | 635.4923 | 42.6882 | 82.4368 | 18.158 | 363 | 75.0791 | 0 | 545.242 | 0.0057794
7668 | 1225.2153 | 12.0173 | 105.4146 | 140.4489 | 56.4546 | 24.6995 | 162.8881 | 9.015 | 22.72 | 109.3639 | 185.349 | 44.4944 | 572.3035 | 377.6402 | 654.9364 | 42.7418 | 85.8529 | 18.23 | 376 | 81.088 | 0 | 569.7037 | 0.0096578
7669 | 1206.1587 | 7.1079 | 108.206 | 137.0671 | 56.7201 | 24.7 | 164.8699 | 8.9578 | 20.226 | 107.2184 | 186.8095 | 42.7413 | 583.483 | 384.064 | 636.4943 | 42.8039 | 82.0525 | 18.2674 | 382 | 78.453 | 0 | 584.341 | 0.027299
7670 | 1185.3967 | 5.3185 | 104.1886 | 140.2289 | 56.9362 | 24.7069 | 161.8703 | 9.2139 | 22.665 | 105.4548 | 186.7298 | 43.976 | 560.2726 | 386.9515 | 612.4105 | 44.3049 | 82.3397 | 18.5387 | 330 | 80.179 | 0 | 604.4241 | 0.019153
7671 | 1183.4608 | 4.2399 | 103.3108 | 146.3819 | 58.3301 | 23.7434 | 166.2843 | 7.3239 | 23.046 | 102.0816 | 189.3622 | 43.1369 | 496.6906 | 388.7305 | 615.191 | 45.2931 | 84.0113 | 18.3518 | 308 | 77.578 | 0 | 598.6603 | 0.014857
7672 | 1155.5769 | 5.1092 | 104.1915 | 143.7991 | 57.5294 | 24.7066 | 168.6824 | 4.9019 | 19.0675 | 94.392 | 201.0737 | 41.1254 | 475.2108 | 380.9241 | 615.605 | 44.4539 | 84.547 | 18.3169 | 290 | 72.9084 | 0 | 586.2301 | 0
7673 | 1123.7098 | 6.881 | 100.5788 | 140.0442 | 68.3158 | 14.246 | 158.1481 | 5.5743 | 17.846 | 94.2785 | 196.4853 | 38.7732 | 456.0104 | 363.1965 | 553.9308 | 35.0137 | 82.7337 | 17.8219 | 244 | 68.4965 | 0 | 530.2799 | 0
7674 | 1073.6567 | 6.214 | 94.2746 | 127.15 | 73.971 | 8.5516 | 140.2464 | 5.0869 | 18.314 | 91.0203 | 168.8163 | 33.6359 | 404.01 | 283.5741 | 445.2814 | 17.6855 | 75.8429 | 16.6526 | 234 | 61.3155 | 0 | 406.0424 | 0
7675 | 1019.9469 | 5.5386 | 90.9593 | 111.2142 | 76.1662 | 6.6505 | 122.1995 | 4.6518 | 18.2565 | 80.9985 | 125.7428 | 25.9815 | 351.0536 | 212.0287 | 389.4609 | 9.5964 | 67.8161 | 16.1715 | 226 | 57.1176 | 0 | 345.5655 | 0
7676 | 971.2466 | 5.5133 | 77.8095 | 104.5284 | 76.1909 | 6.65 | 98.9803 | 4.6026 | 16.5675 | 78.4592 | 105.0474 | 14.2209 | 301.9028 | 174.7195 | 364.1315 | 9.5888 | 58.5227 | 15.8422 | 205 | 50.9507 | 0 | 283.2406 | 0
7677 | 910.2261 | 5.4088 | 40.2199 | 102.8196 | 77.142 | 5.7003 | 86.1451 | 4.5518 | 13.5507 | 72.0001 | 100.6362 | 9.7952 | 272.6449 | 152.9336 | 316.6004 | 9.7154 | 54.1955 | 15.2407 | 187 | 44.6643 | 0 | 260.031 | 0
7678 | 876.1707 | 4.9506 | 22.6812 | 99.7392 | 78.2853 | 4.7503 | 81.0635 | 4.8454 | 9.0482 | 53.4235 | 96.1007 | 9.6716 | 236.4525 | 148.7592 | 275.5989 | 9.621 | 52.9879 | 14.6678 | 174 | 40.5941 | 0 | 247.4166 | 0
7679 | 846.5956 | 3.7881 | 20.1971 | 95.2141 | 77.4035 | 5.6997 | 78.6766 | 4.7983 | 6.9663 | 39.7698 | 80.6702 | 11.0245 | 212.4416 | 136.0014 | 257.3951 | 9.7058 | 50.8357 | 13.7119 | 159 | 37.7945 | 0 | 246.3454 | 0
7680 | 825.2563 | 3.9986 | 19.8385 | 95.1543 | 77.4265 | 5.7 | 71.5292 | 4.8505 | 6.7788 | 37.4532 | 73.1292 | 11.4175 | 200.2929 | 122.629 | 248.1163 | 9.4745 | 49.9064 | 13.2566 | 132 | 36.8036 | 0 | 240.5787 | 0
7681 | 827.209 | 2.6693 | 19.6849 | 94.2505 | 77.9447 | 4.7503 | 64.0869 | 4.8976 | 6.982 | 36.1563 | 72.7183 | 10.6602 | 192.09 | 113.4727 | 240.8907 | 9.78 | 49.2659 | 12.8799 | 123 | 35.7082 | 0 | 242.2486 | 0
7682 | 817.5235 | 1.6456 | 19.6998 | 93.3375 | 77.2128 | 5.6997 | 69.3824 | 4.9165 | 6.9855 | 35.6903 | 74.4036 | 9.5385 | 189.0836 | 107.6138 | 246.9949 | 9.7415 | 49.1147 | 12.1926 | 118 | 35.0359 | 0 | 254.5585 | 0
7683 | 808.2376 | 1.5863 | 19.6324 | 93.6152 | 76.8658 | 5.7 | 77.4273 | 4.7407 | 6.6447 | 35.8506 | 75.0487 | 9.1643 | 186.9916 | 107.2384 | 249.4057 | 9.5931 | 48.7089 | 11.966 | 113 | 34.93 | 0 | 247.071 | 0
7684 | 811.4228 | 1.6248 | 19.6295 | 93.0283 | 77.2031 | 4.7503 | 76.2579 | 4.5624 | 6.6132 | 38.3006 | 74.1004 | 9.1333 | 183.4853 | 105.3539 | 234.1209 | 9.7079 | 48.7679 | 11.9514 | 113 | 34.9954 | 0 | 248.3387 | 0
7685 | 807.1903 | 2.288 | 19.5804 | 92.9147 | 72.8911 | 8.5489 | 65.0428 | 4.4625 | 6.6428 | 49.1766 | 73.7302 | 9.0791 | 184.9732 | 104.27 | 219.0896 | 9.4571 | 49.8964 | 11.9365 | 111 | 35.3411 | 0 | 269.9306 | 0
7686 | 820.4806 | 3.9155 | 26.2561 | 95.1503 | 75.7396 | 5.7008 | 66.953 | 4.3144 | 7.801 | 53.1963 | 74.976 | 10.2834 | 195.0598 | 108.4896 | 223.66 | 9.7002 | 52.6095 | 11.9471 | 115 | 36.0224 | 0 | 318.1333 | 0
7687 | 855.0764 | 4.9888 | 42.5302 | 102.8785 | 70.8006 | 10.4487 | 93.185 | 4.7977 | 11.1983 | 60.1299 | 98.277 | 18.9172 | 224.1452 | 158.0497 | 255.5348 | 13.9682 | 49.5639 | 11.9095 | 176 | 39.6576 | 0 | 371.7562 | 0
7688 | 938.3129 | 7.4772 | 76.0153 | 103.9789 | 59.9969 | 20.8971 | 121.8131 | 5.5448 | 15.886 | 91.2325 | 145.7015 | 35.114 | 278.4604 | 237.0583 | 374.7956 | 29.0478 | 54.1879 | 14.6128 | 256 | 48.4469 | 0 | 432.6944 | 0
7689 | 1067.4785 | 9.1947 | 94.1483 | 111.9778 | 59.799 | 20.9 | 140.2919 | 7.4188 | 22.7768 | 104.1823 | 169.6853 | 40.5988 | 341.129 | 300.5225 | 504.8558 | 37.9107 | 64.7663 | 17.1682 | 302 | 59.4809 | 0 | 494.6642 | 0.011861
7690 | 1148.0605 | 13.8402 | 101.6912 | 121.117 | 58.6027 | 21.8497 | 149.6565 | 8.5792 | 25.3083 | 111.428 | 177.8768 | 41.6262 | 401.7497 | 335.0383 | 605.7707 | 42.372 | 76.3407 | 16.6556 | 370 | 66.4915 | 0 | 548.0314 | 0.019926
7691 | 1196.5786 | 13.5848 | 100.021 | 131.0088 | 57.8518 | 22.7997 | 161.2013 | 8.52 | 26.3028 | 108.4427 | 183.3929 | 43.1386 | 424.6464 | 350.5674 | 647.0382 | 43.801 | 80.3392 | 17.675 | 404 | 73.2977 | 0 | 595.5945 | 0.013031
7692 | 1218.0158 | 7.634 | 104.1868 | 131.9606 | 56.1223 | 24.6995 | 162.5375 | 8.3831 | 24.4542 | 114.0855 | 183.8305 | 42.3575 | 441.7852 | 369.1429 | 638.6917 | 44.6432 | 82.8388 | 18.1458 | 339 | 89.3874 | 0 | 612.6016 | 0.012563
7693 | 1187.5717 | 4.5066 | 104.8708 | 132.9484 | 58.4638 | 22.8005 | 158.6406 | 7.4915 | 21.5224 | 109.4025 | 183.0827 | 43.5283 | 442.5367 | 374.1485 | 621.7014 | 45.1842 | 79.9113 | 17.6691 | 329 | 80.6016 | 0 | 585.2061 | 0.012961
7694 | 1206.584 | 4.0612 | 104.3257 | 134.7471 | 57.2577 | 23.7497 | 163.3284 | 6.8888 | 20.8759 | 106.0864 | 193.3696 | 44.5538 | 443.0929 | 375.8147 | 607.299 | 45.7996 | 82.2412 | 18.1773 | 286 | 81.1781 | 0 | 616.7698 | 0.019965
7695 | 1209.8038 | 6.8517 | 106.8727 | 134.1848 | 60.0441 | 20.9066 | 167.7486 | 8.7518 | 20.7849 | 103.2658 | 201.2232 | 42.9115 | 448.8204 | 369.3049 | 601.3894 | 45.2865 | 83.7029 | 18.2281 | 280 | 80.9355 | 0 | 603.4963 | 0.0069972
7696 | 1171.2526 | 8.9434 | 105.1855 | 131.7266 | 64.0451 | 17.0953 | 165.6609 | 8.4685 | 19.9245 | 104.7247 | 198.9182 | 41.0628 | 436.2182 | 362.4765 | 594.5144 | 39.7197 | 82.6354 | 17.745 | 293 | 80.0216 | 0 | 593.9597 | 0
7697 | 1134.6229 | 8.2654 | 100.0754 | 137.1239 | 73.1213 | 8.5524 | 157.3824 | 7.7312 | 17.761 | 101.4716 | 187.3818 | 37.2614 | 412.2497 | 341.1339 | 574.9196 | 33.641 | 81.6909 | 16.961 | 273 | 76.5411 | 0 | 526.8199 | 0
7698 | 1074.6673 | 7.11 | 93.343 | 126.6805 | 74.4033 | 7.6003 | 144.4137 | 7.0706 | 19.5742 | 92.1558 | 162.2883 | 35.1691 | 366.8693 | 272.5446 | 492.338 | 17.6843 | 76.7594 | 16.131 | 232 | 69.7103 | 0 | 409.4166 | 0
7699 | 1013.0002 | 5.184 | 89.5197 | 112.6942 | 73.8856 | 8.5497 | 126.1331 | 4.8673 | 18.3512 | 83.053 | 122.9525 | 31.3388 | 308.6626 | 204.89 | 410.7716 | 10.7797 | 69.9346 | 15.3354 | 235 | 61.2397 | 0 | 356.7305 | 0
7700 | 946.5464 | 4.6296 | 77.1399 | 105.6092 | 76.9934 | 5.7008 | 102.3385 | 3.8793 | 11.2377 | 83.8649 | 108.5744 | 19.0526 | 271.7431 | 178.7109 | 352.9139 | 9.8646 | 61.7764 | 14.0553 | 212 | 49.9064 | 0 | 309.2993 | 0
7701 | 910.637 | 4.544 | 39.3955 | 102.2193 | 77.3895 | 4.7503 | 102.6461 | 4.0513 | 8.7826 | 73.7519 | 97.429 | 13.9232 | 254.2713 | 151.0004 | 301.6953 | 10.0688 | 56.6868 | 13.2848 | 187 | 43.3694 | 0 | 272.7227 | 0
7702 | 882.2372 | 3.754 | 26.1247 | 98.0405 | 75.7418 | 5.6997 | 102.4234 | 4.2541 | 8.0437 | 51.3308 | 98.1332 | 13.5133 | 232.6471 | 131.9284 | 271.3313 | 9.9967 | 53.2213 | 13.0386 | 176 | 40.0676 | 0 | 271.7797 | 0
7703 | 848.4834 | 3.2949 | 25.333 | 96.5491 | 76.4119 | 4.7503 | 89.8621 | 4.3722 | 7.105 | 37.6475 | 88.2834 | 13.5721 | 216.2733 | 111.3446 | 255.8926 | 9.8037 | 50.8293 | 12.7293 | 159 | 37.4381 | 0 | 266.7194 | 0
7704 | 830.051 | 2.1665 | 25.2107 | 94.815 | 75.6451 | 5.6997 | 83.9904 | 4.5017 | 6.7712 | 33.2269 | 79.7454 | 13.6188 | 206.3062 | 97.4726 | 245.7788 | 10.6318 | 49.9114 | 12.4474 | 136 | 36.0921 | 0 | 264.1685 | 0
7705 | 815.9928 | 1.6501 | 25.0844 | 93.9569 | 76.3317 | 4.7503 | 82.8444 | 4.8644 | 6.541 | 28.9137 | 76.152 | 13.2542 | 194.26 | 91.8224 | 239.3109 | 10.6656 | 49.4923 | 11.7696 | 127 | 34.6403 | 0 | 264.0901 | 0
7706 | 811.7231 | 1.5882 | 24.9374 | 93.7175 | 75.6532 | 5.6997 | 82.2235 | 4.7404 | 6.5587 | 28.1607 | 74.3916 | 13.1041 | 189.1975 | 89.7016 | 238.5641 | 10.9083 | 49.4286 | 11.0999 | 127 | 34.294 | 0 | 269.9901 | 0
7707 | 802.4728 | 1.5864 | 24.9808 | 93.365 | 77.1272 | 4.7516 | 72.4753 | 4.6074 | 6.643 | 28.548 | 74.1328 | 13.2986 | 188.6164 | 87.8471 | 236.154 | 10.842 | 49.2865 | 10.9398 | 126 | 34.5459 | 0 | 263.4052 | 0
7708 | 808.169 | 1.439 | 25.011 | 92.9349 | 76.2648 | 5.6984 | 71.5906 | 4.6333 | 6.3662 | 30.8226 | 74.3187 | 13.1773 | 187.9025 | 86.1828 | 225.4501 | 10.92 | 49.3037 | 10.935 | 124 | 33.7365 | 0 | 270.3131 | 0
7709 | 811.7033 | 1.8794 | 25.0702 | 94.3222 | 77.101 | 4.7503 | 80.3 | 4.2263 | 6.508 | 40.6479 | 74.5137 | 13.0918 | 189.6031 | 88.4776 | 219.3276 | 10.8271 | 51.0129 | 10.959 | 126 | 33.1516 | 0 | 282.5235 | 0
7710 | 829.0377 | 3.1637 | 32.1039 | 94.0911 | 75.4671 | 5.6997 | 89.5454 | 4.0984 | 7.04 | 44.0988 | 76.2299 | 15.7528 | 196.0125 | 97.6589 | 225.9916 | 10.605 | 53.699 | 11.0926 | 116 | 34.3681 | 0 | 327.7714 | 0
7711 | 863.1042 | 4.7792 | 48.5412 | 102.5638 | 70.6789 | 10.4487 | 103.1989 | 4.4128 | 11.8623 | 58.5012 | 97.6656 | 21.5113 | 220.9565 | 163.6239 | 267.5518 | 13.2759 | 50.4398 | 14.2569 | 194 | 42.627 | 0 | 378.8596 | 0
7712 | 937.8311 | 7.8415 | 77.1238 | 103.8761 | 61.1005 | 19.9474 | 111.5591 | 4.6765 | 15.3295 | 94.3294 | 140.3921 | 33.6855 | 285.4149 | 245.2632 | 378.4763 | 28.8276 | 56.3248 | 17.0665 | 302 | 49.7559 | 0 | 427.7026 | 0
7713 | 1034.991 | 12.8335 | 95.0057 | 114.4976 | 58.0872 | 22.7992 | 128.3458 | 5.534 | 19.8777 | 99.0773 | 171.0133 | 39.7955 | 362.1039 | 288.9359 | 501.1182 | 36.4344 | 67.1748 | 16.6403 | 327 | 64.2331 | 0 | 497.2804 | 0.020305
7714 | 1132.8444 | 10.3553 | 101.5134 | 127.74 | 60.1043 | 20.9005 | 155.0677 | 7.4836 | 22.7043 | 104.6135 | 180.402 | 41.1182 | 411.8269 | 298.3046 | 562.3936 | 41.3135 | 78.6822 | 16.2738 | 348 | 71.8717 | 0 | 545.0601 | 0.078646
7715 | 1193.4397 | 5.3331 | 101.0318 | 132.7042 | 60.62 | 20.9 | 164.3422 | 9.0182 | 23.0122 | 103.2065 | 181.2834 | 42.3587 | 433.3073 | 317.9959 | 581.7093 | 43.8143 | 97.9453 | 16.7583 | 361 | 70.3567 | 0 | 572.0364 | 0.12022
7716 | 1208.3655 | 3.2872 | 103.6226 | 137.5663 | 58.2009 | 23.7492 | 164.9068 | 9.7137 | 22.5573 | 101.2919 | 183.0161 | 43.5044 | 460.9302 | 344.6468 | 583.3668 | 42.9254 | 113.2588 | 17.2137 | 350 | 79.7071 | 0 | 596.7632 | 0.11741
7717 | 1198.6072 | 4.2337 | 103.4173 | 133.4874 | 59.385 | 22.8066 | 168.4702 | 8.5632 | 22.0158 | 98.1563 | 186.7745 | 42.8698 | 458.9993 | 356.4314 | 585.5774 | 43.7474 | 110.3094 | 17.5219 | 381 | 68.6511 | 0 | 603.4595 | 0.079209
7718 | 1203.1609 | 6.3856 | 103.3589 | 141.1334 | 58.0433 | 23.7434 | 172.6984 | 6.9054 | 22.7272 | 103.2575 | 189.855 | 42.928 | 479.01 | 368.291 | 599.5596 | 44.6237 | 107.5835 | 17.8352 | 322 | 78.3289 | 0 | 604.4371 | 0.023245
7719 | 1201.9723 | 7.5229 | 105.5233 | 144.9913 | 59.5013 | 21.8505 | 171.7997 | 7.3856 | 21.5507 | 108.5922 | 191.7116 | 41.6718 | 491.2334 | 371.6789 | 597.3693 | 44.7801 | 104.8667 | 18.9346 | 329 | 79.0965 | 0 | 596.6289 | 0.012127
7720 | 1187.5972 | 7.2226 | 101.3492 | 146.7686 | 67.4816 | 14.2521 | 168.8939 | 7.1184 | 17.338 | 105.0047 | 192.1535 | 39.9549 | 478.3756 | 364.8069 | 607.057 | 41.3945 | 102.3049 | 20.2868 | 342 | 78.5067 | 0 | 603.5181 | 0
7721 | 1137.3299 | 6.1058 | 96.4311 | 140.8018 | 70.7786 | 11.4008 | 159.116 | 7.0706 | 15.6233 | 105.5425 | 195.1953 | 39.1737 | 442.6674 | 340.8368 | 583.9494 | 33.7845 | 88.7801 | 18.2405 | 316 | 74.7572 | 0 | 544.7259 | 0
7722 | 1054.9826 | 5.644 | 91.8712 | 125.8271 | 74.2518 | 8.5508 | 145.2855 | 6.8146 | 13.2812 | 93.9468 | 169.8757 | 38.8466 | 390.991 | 269.9594 | 496.1178 | 17.8238 | 77.5671 | 16.5434 | 316 | 66.9466 | 0 | 408.1413 | 0
7723 | 978.2151 | 5.6024 | 88.8302 | 111.2168 | 76.7305 | 6.6505 | 127.5623 | 5.5451 | 12.3319 | 80.0922 | 125.9463 | 31.6982 | 328.3963 | 195.5977 | 410.7093 | 11.4646 | 67.4759 | 14.9113 | 288 | 59.5244 | 0 | 364.0136 | 0
7724 | 938.5117 | 4.7994 | 76.499 | 104.0162 | 77.6292 | 5.7003 | 104.0071 | 4.0874 | 9.8135 | 78.4502 | 106.6964 | 18.1504 | 281.7694 | 174.6427 | 350.5083 | 10.932 | 56.2648 | 14.1627 | 281 | 55.3938 | 0 | 310.9321 | 0
7725 | 893.4238 | 4.2692 | 37.8528 | 99.6557 | 78.0617 | 4.7503 | 91.2347 | 3.9066 | 8.7058 | 74.7719 | 101.785 | 13.3694 | 256.4863 | 179.3068 | 304.1995 | 10.7814 | 50.9366 | 13.638 | 249 | 47.4561 | 0 | 279.9915 | 0
7726 | 861.96 | 4.5934 | 25.2462 | 96.0326 | 76.7428 | 5.6997 | 84.28 | 3.7814 | 7.9733 | 51.8837 | 98.3629 | 12.5386 | 237.6339 | 148.8661 | 274.3424 | 10.8314 | 48.7742 | 12.8824 | 235 | 43.8051 | 0 | 268.0486 | 0
7727 | 828.6495 | 3.7499 | 24.9476 | 93.7608 | 75.8101 | 5.7 | 82.3902 | 4.1813 | 7.3603 | 37.6676 | 86.9934 | 12.2265 | 224.4299 | 119.2961 | 259.3346 | 10.7964 | 48.5287 | 12.644 | 211 | 40.4374 | 0 | 265.7484 | 0
7728 | 810.0939 | 2.2303 | 24.9924 | 93.3375 | 76.6514 | 4.7503 | 82.5102 | 4.4195 | 7.273 | 33.4034 | 81.4388 | 12.2616 | 215.3679 | 109.1959 | 244.2276 | 10.8687 | 48.4558 | 12.6611 | 180 | 37.6948 | 0 | 273.1348 | 0
7729 | 804.0912 | 1.4424 | 22.08 | 93.9764 | 76.3648 | 5.6997 | 82.5852 | 4.6604 | 7.1973 | 32.2369 | 80.1434 | 12.0788 | 209.3649 | 102.6635 | 241.1996 | 10.7485 | 48.3538 | 12.2003 | 147 | 36.1653 | 0 | 269.7196 | 0
7730 | 800.4436 | 1.3308 | 19.3164 | 92.6901 | 77.3741 | 4.7503 | 81.0145 | 4.5974 | 7.3002 | 31.3418 | 77.813 | 11.9665 | 208.7769 | 97.343 | 251.2031 | 10.6138 | 48.2366 | 11.8704 | 148 | 36.7478 | 0 | 272.5562 | 0
7731 | 793.409 | 1.5148 | 18.4725 | 92.4788 | 77.6441 | 4.75 | 79.225 | 4.4913 | 7.339 | 30.7311 | 77.0029 | 11.9835 | 205.4863 | 93.5909 | 249.7968 | 10.8553 | 48.2346 | 11.4962 | 140 | 34.5369 | 0 | 271.7094 | 0
7732 | 799.31 | 1.4834 | 18.525 | 92.5406 | 76.7794 | 5.6997 | 80.4051 | 4.378 | 7.3387 | 33.2636 | 77.1435 | 12.006 | 197.2689 | 91.1373 | 239.9461 | 10.2397 | 48.4348 | 11.379 | 135 | 34.7491 | 0 | 267.2416 | 0
7733 | 799.6863 | 2.6538 | 18.3352 | 94.3097 | 76.5954 | 4.7503 | 81.4094 | 3.7753 | 7.2332 | 43.3743 | 77.4989 | 12.0194 | 196.4465 | 88.2686 | 227.0876 | 9.7636 | 49.7441 | 11.4363 | 149 | 34.9981 | 0 | 293.4533 | 0
7734 | 813.1128 | 3.6238 | 24.2558 | 93.9139 | 75.6144 | 4.75 | 86.5916 | 3.7629 | 7.2258 | 45.5242 | 78.9947 | 13.1621 | 203.1323 | 94.4857 | 222.0994 | 9.9322 | 52.6079 | 11.433 | 139 | 35.1608 | 0 | 339.1114 | 0
7735 | 862.4137 | 4.7756 | 34.7287 | 98.6346 | 70.9755 | 9.4987 | 101.3003 | 3.7769 | 11.0742 | 56.9161 | 100.1868 | 21.2359 | 236.0039 | 151.9335 | 257.2033 | 13.9216 | 49.3938 | 11.3642 | 199 | 43.1453 | 0 | 377.8194 | 0
7736 | 940.0562 | 6.0213 | 67.2111 | 101.139 | 60.6107 | 19.9471 | 120.0553 | 4.4536 | 14.009 | 89.1624 | 144.3242 | 33.4383 | 294.128 | 236.5863 | 359.1766 | 28.6646 | 55.1035 | 13.8397 | 269 | 51.9448 | 0 | 428.1556 | 0
7737 | 1037.5892 | 9.6541 | 86.2214 | 112.1361 | 59.4496 | 20.8997 | 137.7529 | 5.591 | 19.0707 | 101.3 | 165.6961 | 38.8064 | 357.8005 | 307.44 | 481.5 | 37.4974 | 65.7151 | 18.1468 | 283 | 63.3832 | 0 | 514.2475 | 0.025758
7738 | 1117.5558 | 9.914 | 92.8477 | 124.5871 | 58.4728 | 21.8497 | 159.419 | 6.5957 | 21.366 | 100.3718 | 171.9265 | 40.0329 | 403.2555 | 341.7401 | 568.1348 | 40.8004 | 77.3067 | 17.8099 | 408 | 71.3772 | 0 | 581.3863 | 0.050259
7739 | 1164.06 | 7.6717 | 97.2741 | 134.7436 | 56.8588 | 23.7495 | 161.4056 | 8.1786 | 21.9017 | 98.6395 | 179.2688 | 40.4785 | 416.9656 | 356.8323 | 607.4735 | 40.5684 | 81.8056 | 17.2095 | 396 | 73.1662 | 0 | 594.6538 | 0.0623
7740 | 1180.3337 | 6.1208 | 102.6591 | 135.4657 | 59.9814 | 20.9008 | 158.9508 | 8.1618 | 20.0427 | 99.0317 | 183.7134 | 40.1331 | 419.9426 | 380.501 | 612.777 | 40.5272 | 83.9814 | 17.0744 | 343 | 75.996 | 0 | 601.0307 | 0.047502
7741 | 1155.3875 | 5.9516 | 101.4838 | 134.0384 | 63.2164 | 18.0508 | 158.4979 | 6.2354 | 13.8651 | 98.1427 | 183.2251 | 40.5005 | 420.5215 | 370.2659 | 608.747 | 42.1439 | 82.9217 | 17.1591 | 418 | 69.7402 | 0 | 601.4163 | 0.043434
7742 | 1156.0501 | 7.7321 | 104.7518 | 135.0287 | 66.9717 | 14.2511 | 161.3011 | 5.9348 | 16.8412 | 97.8236 | 186.3104 | 40.8333 | 423.7549 | 375.7838 | 618.8264 | 45.3884 | 85.7026 | 18.1741 | 335 | 69.9467 | 0 | 604.628 | 0.013813
7743 | 1182.4977 | 9.0486 | 106.4374 | 135.3181 | 66.0816 | 14.25 | 160.9471 | 6.3174 | 18.3913 | 96.0729 | 190.0453 | 40.615 | 426.1135 | 378.7904 | 617.318 | 44.9416 | 85.24 | 18.2692 | 304 | 69.998 | 0 | 605.4216 | 0.0050992
7744 | 1153.363 | 7.843 | 104.8913 | 132.9384 | 63.0993 | 17.0992 | 153.8592 | 6.3517 | 15.3935 | 103.1225 | 189.527 | 40.6562 | 415.6251 | 358.308 | 612.9324 | 41.459 | 84.3266 | 17.0766 | 305 | 68.9758 | 0 | 584.157 | 0
7745 | 1092.5219 | 6.2649 | 99.6561 | 132.0429 | 70.3416 | 10.4518 | 134.3388 | 6.4432 | 12.904 | 103.7145 | 186.8241 | 39.3934 | 391.2304 | 331.7837 | 550.0461 | 26.1393 | 78.2251 | 15.4912 | 282 | 64.6639 | 0 | 530.708 | 0
7746 | 1025.5088 | 4.9741 | 80.7146 | 119.5035 | 74.9063 | 6.6511 | 124.0456 | 6.1514 | 12.4675 | 74.5585 | 167.654 | 38.0245 | 364.8258 | 256.8251 | 437.6917 | 15.047 | 71.3248 | 14.4739 | 277 | 57.7832 | 0 | 401.9174 | 0
7747 | 964.8824 | 4.4005 | 40.1153 | 104.8158 | 76.4899 | 5.7003 | 117.9945 | 5.1641 | 12.0442 | 60.5956 | 146.3277 | 30.1311 | 333.5302 | 184.9362 | 366.9029 | 11.9293 | 64.4815 | 13.808 | 250 | 53.8013 | 0 | 335.8799 | 0
7748 | 911.2778 | 3.8832 | 26.5526 | 97.9229 | 76.9254 | 5.7 | 106.5304 | 4.7669 | 9.8892 | 70.5576 | 114.3961 | 14.4919 | 274.0805 | 157.7934 | 323.2993 | 10.7928 | 56.9144 | 12.8469 | 222 | 52.6414 | 0 | 289.4914 | 0
7749 | 875.6442 | 3.6295 | 25.7813 | 97.0238 | 76.6855 | 5.7 | 94.1459 | 4.5808 | 8.58 | 68.2427 | 92.8347 | 9.4862 | 242.3605 | 140.0019 | 307.8354 | 10.4492 | 51.3862 | 12.4404 | 214 | 43.5156 | 0 | 296.3424 | 0
7750 | 851.7584 | 3.4895 | 25.7416 | 95.7772 | 77.7899 | 4.7503 | 87.0782 | 4.0912 | 7.8644 | 48.0893 | 80.8435 | 10.0662 | 222.7627 | 140.693 | 297.6891 | 9.9784 | 49.717 | 12.4894 | 208 | 40.4159 | 0 | 295.2615 | 0
7751 | 827.2907 | 3.7413 | 25.5045 | 94.0657 | 77.4692 | 4.75 | 82.0165 | 3.982 | 7.1476 | 39.3668 | 75.083 | 9.3784 | 209.1497 | 129.4721 | 284.8991 | 10.2632 | 48.8251 | 12.4774 | 190 | 40.8887 | 0 | 275.4122 | 0
7752 | 809.4855 | 2.5979 | 25.5519 | 93.044 | 76.3295 | 5.6997 | 79.0449 | 4.0686 | 7.0288 | 38.5757 | 73.7063 | 8.9729 | 204.3105 | 123.2098 | 261.8487 | 10.123 | 48.2853 | 12.5237 | 160 | 37.6476 | 0 | 264.8612 | 0
7753 | 808.4114 | 1.906 | 25.8317 | 92.539 | 77.2567 | 4.7503 | 70.4856 | 4.4808 | 6.8808 | 34.8046 | 72.4928 | 9.1642 | 202.1472 | 115.4761 | 239.9424 | 10.2035 | 48.3048 | 12.4494 | 170 | 35.4047 | 0 | 255.5975 | 0
7754 | 803.2261 | 1.8038 | 25.8451 | 92.131 | 75.9104 | 5.6997 | 77.0693 | 4.8857 | 7.068 | 31.4689 | 72.259 | 8.9095 | 199.7638 | 110.9091 | 235.0238 | 10.0737 | 48.2977 | 12.2764 | 159 | 35.8181 | 0 | 251.2317 | 0
7755 | 794.8167 | 2.0202 | 25.4753 | 92.695 | 77.2076 | 4.7503 | 81.5517 | 4.862 | 6.8547 | 30.5707 | 72.6135 | 8.7518 | 197.8173 | 108.4517 | 234.5031 | 10.1 | 48.7765 | 12.2021 | 147 | 34.2408 | 0 | 248.0048 | 0
7756 | 789.8378 | 1.8694 | 25.3818 | 94.4842 | 77.018 | 4.75 | 81.3699 | 4.7621 | 6.6655 | 33.9372 | 73.5792 | 8.8642 | 195.6846 | 104.0216 | 229.4938 | 10.2487 | 48.51 | 11.629 | 136 | 33.544 | 0 | 248.0232 | 0
7757 | 787.8195 | 1.9976 | 21.9083 | 94.2013 | 75.2678 | 5.6997 | 80.5507 | 4.7208 | 6.6889 | 45.1422 | 73.5634 | 8.7836 | 193.3422 | 101.7593 | 221.0801 | 10.2242 | 49.8094 | 11.2508 | 134 | 34.5002 | 0 | 249.742 | 0
7758 | 788.7427 | 2.9252 | 19.9355 | 92.5072 | 76.1746 | 4.7503 | 71.2698 | 4.7412 | 6.6538 | 46.5349 | 73.2714 | 8.7047 | 190.0235 | 99.6616 | 218.3513 | 10.0651 | 52.3762 | 11.1312 | 133 | 33.3694 | 0 | 250.1757 | 0
7759 | 805.031 | 4.1294 | 37.2332 | 93.2473 | 76.2724 | 4.75 | 70.2247 | 4.5218 | 6.9311 | 36.3443 | 73.6991 | 8.7118 | 189.1829 | 98.7556 | 218.7444 | 10.1122 | 49.3783 | 11.1114 | 129 | 34.0217 | 0 | 254.0044 | 0
7760 | 819.3193 | 5.1592 | 46.9932 | 91.4297 | 76.0477 | 5.6997 | 80.8808 | 4.2944 | 6.7562 | 30.4388 | 78.2534 | 10.0776 | 194.2698 | 113.9617 | 218.5339 | 9.9448 | 48.0897 | 11.1392 | 135 | 38.9342 | 0 | 255.6479 | 0
7761 | 822.0769 | 3.9753 | 54.2858 | 89.5886 | 76.3656 | 5.7016 | 89.7984 | 4.0695 | 5.9592 | 37.879 | 109.1089 | 14.3697 | 207.1974 | 120.1835 | 213.4404 | 9.7135 | 47.0457 | 11.2016 | 145 | 41.8748 | 0 | 248.3693 | 0
7762 | 848.4837 | 2.3429 | 67.7536 | 89.4433 | 76.1142 | 5.6984 | 99.1237 | 3.8758 | 5.647 | 51.8741 | 134.9095 | 15.8901 | 222.6991 | 109.821 | 222.763 | 9.5546 | 46.6796 | 11.455 | 148 | 41.6201 | 0 | 260.7012 | 0.033838
7763 | 866.4961 | 1.919 | 75.7714 | 89.2183 | 75.6425 | 5.7016 | 101.3332 | 5.3296 | 8.0953 | 61.2786 | 140.9765 | 15.9129 | 232.699 | 121.0982 | 233.7633 | 8.9023 | 47.7868 | 11.5447 | 187 | 45.4848 | 0 | 261.2617 | 0.044017
7764 | 871.6256 | 2.5502 | 74.644 | 90.2019 | 76.694 | 4.7487 | 102.5329 | 7.0966 | 10.8473 | 59.3347 | 115.3995 | 15.8854 | 246.2878 | 135.6718 | 246.1845 | 9.2606 | 48.052 | 12.0871 | 221 | 48.1593 | 0 | 264.8676 | 0.02849
7765 | 868.0464 | 2.0846 | 74.532 | 89.6989 | 76.853 | 4.75 | 97.2407 | 7.0724 | 12.8185 | 61.689 | 99.4205 | 15.938 | 249.8072 | 140.3602 | 251.8614 | 9.3638 | 48.0561 | 12.3165 | 229 | 50.5684 | 0 | 269.5231 | 0.040479
7766 | 876.5876 | 1.9387 | 68.8999 | 89.8512 | 76.0213 | 5.6997 | 95.58 | 5.3547 | 13.7858 | 58.8309 | 96.6585 | 15.9689 | 248.0881 | 153.5241 | 268.338 | 9.0071 | 49.0306 | 12.6082 | 262 | 50.38 | 0 | 266.35 | 0.050686
7767 | 875.371 | 3.3309 | 31.8524 | 92.1543 | 77.0951 | 4.7503 | 92.4179 | 4.3559 | 14.6652 | 59.6978 | 95.6463 | 16.9993 | 243.8781 | 163.8047 | 285.0669 | 9.2042 | 50.3172 | 13.2205 | 284 | 51.8269 | 0 | 262.0982 | 0.01507
7768 | 876.3229 | 4.4222 | 18.9021 | 94.3896 | 77.0463 | 4.75 | 89.4843 | 4.636 | 14.3738 | 52.5727 | 95.2511 | 18.4443 | 247.7049 | 163.8263 | 297.0074 | 9.6099 | 51.1201 | 13.2661 | 269 | 53.01 | 0 | 264.0409 | 0
7769 | 876.4347 | 4.1548 | 19.0403 | 94.1796 | 76.1652 | 5.6997 | 95.6205 | 4.4056 | 12.5375 | 40.1163 | 97.8377 | 12.3851 | 255.3347 | 169.095 | 296.2742 | 9.9949 | 50.7965 | 12.9078 | 272 | 48.0682 | 0 | 274.1969 | 0
7770 | 869.9122 | 4.084 | 19.1843 | 94.2809 | 77.0356 | 4.7503 | 88.3269 | 4.0407 | 14.3725 | 36.7117 | 97.8399 | 9.2467 | 250.1891 | 180.7053 | 289.3591 | 10.0822 | 49.9267 | 12.7623 | 277 | 48.2177 | 0 | 271.6132 | 0
7771 | 848.8741 | 4.1127 | 18.8534 | 94.2096 | 77.029 | 4.75 | 78.1638 | 4.2314 | 15.2783 | 43.1323 | 86.8383 | 10.4402 | 241.4928 | 156.5812 | 269.8596 | 10.2562 | 49.2543 | 12.8716 | 264 | 46.8303 | 0 | 266.3274 | 0
7772 | 831.5014 | 3.6106 | 18.6813 | 92.8775 | 76.2 | 5.6997 | 90.1232 | 4.1728 | 10.3265 | 52.353 | 81.6675 | 9.7658 | 230.2818 | 141.5139 | 259.6714 | 10.2579 | 48.8191 | 12.5042 | 311 | 44.0374 | 0 | 264.4231 | 0
7773 | 821.973 | 3.5149 | 18.3421 | 93.3218 | 77.3252 | 4.7503 | 86.828 | 4.4986 | 9.2615 | 49.3922 | 79.9414 | 8.9945 | 218.7398 | 134.0505 | 258.3555 | 10.2274 | 48.8448 | 12.1279 | 269 | 41.9648 | 0 | 261.1692 | 0
7774 | 806.0329 | 3.4074 | 18.2464 | 93.5399 | 77.2344 | 4.75 | 81.0178 | 4.7781 | 8.8768 | 40.3905 | 80.0436 | 8.9488 | 214.3986 | 127.7275 | 255.2948 | 10.0926 | 47.5306 | 12.1991 | 263 | 42.8358 | 0 | 262.4869 | 0
7775 | 799.7293 | 2.9497 | 18.2625 | 93.0839 | 76.4252 | 5.6997 | 78.2678 | 4.8547 | 7.6161 | 35.9349 | 79.035 | 9.0373 | 210.4229 | 122.5191 | 251.4301 | 9.9934 | 47.4124 | 12.3127 | 241 | 41.9285 | 0 | 254.0432 | 0
7776 | 784.5026 | 2.2251 | 18.4106 | 92.3964 | 77.7461 | 4.7503 | 67.0199 | 4.9144 | 7.0379 | 32.8625 | 75.8678 | 9.2254 | 207.0799 | 116.6818 | 246.4067 | 10.1962 | 47.4333 | 12.1889 | 210 | 40.8205 | 0 | 258.3943 | 0
7777 | 811.1697 | 1.9304 | 18.4379 | 92.2384 | 76.9967 | 5.7013 | 70.6595 | 4.9299 | 6.826 | 31.5162 | 75.0794 | 9.0925 | 205.0917 | 113.2347 | 242.648 | 10.2047 | 47.153 | 11.7638 | 197 | 39.3003 | 0 | 252.0776 | 0
7778 | 802.823 | 1.714 | 18.4615 | 92.4538 | 77.9104 | 4.7487 | 77.1653 | 4.903 | 6.8826 | 30.9742 | 75.8863 | 9.2124 | 203.178 | 111.8237 | 247.3545 | 10.116 | 47.1776 | 11.288 | 169 | 37.8607 | 0 | 260.622 | 0
7779 | 780.8623 | 1.65 | 18.3272 | 92.3926 | 73.4783 | 8.5489 | 79.071 | 4.8516 | 6.9587 | 30.9901 | 76.4686 | 8.9474 | 198.9518 | 111.1888 | 248.8942 | 10.1969 | 47.5302 | 11.6486 | 157 | 36.2272 | 0 | 255.3294 | 0
7780 | 780.9662 | 1.5685 | 18.4146 | 92.0543 | 73.0768 | 8.55 | 73.3862 | 4.3991 | 7.5003 | 32.4237 | 77.3111 | 8.8657 | 196.0642 | 108.0121 | 238.1363 | 9.9596 | 47.7384 | 11.8482 | 141 | 36.3662 | 0 | 282.0898 | 0
7781 | 773.9612 | 2.1045 | 18.4033 | 92.0129 | 73.9243 | 7.6003 | 64.8973 | 4.544 | 8.097 | 35.4408 | 77.7316 | 8.8228 | 196.3785 | 103.0515 | 226.07 | 10.2181 | 49.1651 | 11.2915 | 146 | 36.797 | 0 | 285.3521 | 0
7782 | 771.5487 | 2.915 | 18.2957 | 91.9456 | 75.8671 | 5.7005 | 73.0366 | 4.4382 | 7.7053 | 35.1641 | 77.6768 | 8.748 | 190.9206 | 101.2341 | 218.8321 | 10.0756 | 51.6478 | 11.0316 | 142 | 33.4825 | 0 | 277.4522 | 0
7783 | 783.0454 | 3.5382 | 18.4415 | 91.8929 | 76.8077 | 4.7503 | 78.6368 | 4.3926 | 7.4757 | 31.9372 | 78.1223 | 8.7724 | 187.5896 | 101.9229 | 218.5717 | 10.0742 | 49.7978 | 11.0252 | 134 | 32.4092 | 0 | 264.3635 | 0
7784 | 793.4357 | 5.6066 | 18.3976 | 91.6464 | 76.1201 | 5.6997 | 78.716 | 4.8526 | 7.1833 | 29.5968 | 78.3341 | 8.4836 | 191.291 | 104.7656 | 217.3693 | 9.9399 | 48.5028 | 11.1313 | 127 | 33.274 | 0 | 262.381 | 0
7785 | 801.6972 | 4.3943 | 18.1986 | 89.2342 | 75.2221 | 6.6497 | 67.6368 | 4.8564 | 6.8765 | 35.6705 | 77.9803 | 6.5427 | 192.8868 | 112.9068 | 214.529 | 9.4875 | 47.274 | 11.4326 | 122 | 36.5268 | 0 | 248.9202 | 0
7786 | 808.4832 | 2.1318 | 18.0589 | 89.1682 | 75.3337 | 5.7003 | 69.8966 | 4.6309 | 8.2692 | 48.098 | 77.932 | 5.7787 | 199.2797 | 113.4852 | 216.742 | 9.6717 | 46.1784 | 11.4209 | 159 | 35.4957 | 0 | 248.5954 | 0.026147
7787 | 818.0269 | 1.7187 | 17.9713 | 88.6467 | 72.8963 | 8.5492 | 98.318 | 4.8906 | 10.6703 | 58.9505 | 79.8112 | 6.0001 | 217.5708 | 128.778 | 230.2385 | 9.5298 | 45.9028 | 11.4556 | 159 | 36.2342 | 0 | 265.3948 | 0.027002
7788 | 839.5862 | 1.6342 | 18.0051 | 88.2318 | 77.1988 | 4.7511 | 103.8548 | 4.5761 | 10.4798 | 62.5116 | 91.4493 | 6.7883 | 222.8436 | 134.8757 | 237.9941 | 9.313 | 46.4789 | 11.6553 | 174 | 36.7579 | 0 | 268.0295 | 0.047034
7789 | 850.3747 | 3.2006 | 17.9036 | 91.0748 | 76.1203 | 5.6997 | 103.0306 | 3.9489 | 10.034 | 62.678 | 101.4356 | 7.9016 | 228.9205 | 130.3053 | 249.4097 | 8.764 | 47.033 | 12.1318 | 182 | 35.2295 | 0 | 265.8509 | 0.11221
7790 | 856.7642 | 4.6624 | 18.6023 | 93.0914 | 77.2183 | 4.7503 | 104.6851 | 3.7791 | 12.0712 | 58.978 | 98.7862 | 9.7898 | 238.5684 | 135.0798 | 261.5838 | 8.5345 | 49.2246 | 13.0186 | 181 | 42.6168 | 0 | 259.4433 | 0.058234
7791 | 872.893 | 4.8318 | 18.8429 | 93.201 | 77.3809 | 4.75 | 95.0273 | 3.8944 | 11.4567 | 61.2125 | 98.9213 | 11.8092 | 238.922 | 143.7049 | 280.8973 | 9.0051 | 56.6341 | 13.2244 | 191 | 46.4998 | 0 | 260.5981 | 0.013877
7792 | 876.1133 | 4.1972 | 18.8299 | 94.2709 | 76.3066 | 5.6997 | 96.3943 | 4.3497 | 9.5566 | 52.6695 | 104.7057 | 11.0595 | 237.881 | 159.1201 | 301.1789 | 9.7135 | 54.3222 | 13.9063 | 201 | 45.8711 | 0 | 268.3589 | 0
7793 | 868.4773 | 4.1763 | 18.8331 | 93.6808 | 76.1413 | 5.7 | 92.4344 | 4.6413 | 10.8526 | 35.6874 | 105.9357 | 9.97 | 243.1979 | 168.8761 | 297.7777 | 9.9661 | 52.9301 | 14.5461 | 194 | 46.7327 | 0 | 283.7781 | 0
7794 | 860.5663 | 3.8336 | 18.6973 | 94.2395 | 76.5838 | 5.7 | 76.7211 | 5.1863 | 10.1548 | 29.4594 | 101.1669 | 9.5789 | 244.0072 | 169.5672 | 299.8347 | 10.2525 | 52.321 | 14.1336 | 193 | 45.7152 | 0 | 281.094 | 0
7795 | 857.7632 | 3.8582 | 18.4111 | 94.2056 | 76.7304 | 5.7 | 79.629 | 5.0838 | 9.054 | 29.4269 | 97.1851 | 9.1545 | 236.8903 | 160.0189 | 309.7038 | 10.1038 | 50.8459 | 13.2718 | 172 | 39.5898 | 0 | 292.2748 | 0
7796 | 845.764 | 4.8508 | 18.4121 | 92.853 | 76.9209 | 5.7 | 83.2684 | 4.9402 | 8.9293 | 31.6537 | 90.7863 | 9.2995 | 224.6999 | 137.0966 | 308.3403 | 10.4378 | 50.6171 | 13.1543 | 156 | 40.2496 | 0 | 293.6643 | 0
7797 | 829.1934 | 4.6161 | 18.3358 | 92.6485 | 78.1729 | 4.7503 | 80.4388 | 4.9656 | 8.8245 | 31.0593 | 80.4122 | 8.9834 | 217.5553 | 123.1793 | 270.7475 | 10.2769 | 49.4994 | 12.9243 | 143 | 38.8031 | 0 | 270.8146 | 0
7798 | 817.2535 | 3.7396 | 18.3657 | 92.3658 | 78.018 | 4.75 | 69.3787 | 4.7787 | 8.3962 | 27.4669 | 76.4858 | 8.6529 | 214.4995 | 118.9998 | 250.1893 | 9.783 | 49.1779 | 12.1308 | 137 | 38.2334 | 0 | 263.0557 | 0
7799 | 805.5039 | 2.9471 | 18.2723 | 93.624 | 77.7928 | 4.75 | 73.3798 | 4.3081 | 8.0852 | 25.9296 | 75.1355 | 8.5948 | 207.6176 | 113.0937 | 250.2304 | 9.3074 | 49.9112 | 11.1403 | 119 | 35.6511 | 0 | 252.0283 | 0
7800 | 785.9538 | 2.0481 | 18.5404 | 93.5225 | 77.2965 | 5.6997 | 77.8559 | 3.8211 | 7.8764 | 26.8751 | 71.8478 | 8.6617 | 202.2237 | 110.3655 | 242.9157 | 9.0364 | 48.478 | 10.8777 | 121 | 35.224 | 0 | 254.6971 | 0
7801 | 787.8809 | 2.0019 | 18.5393 | 94.1267 | 78.4368 | 4.7503 | 77.6548 | 3.7374 | 7.8771 | 26.3151 | 70.1463 | 8.4607 | 196.4214 | 103.2162 | 231.5378 | 9.3202 | 48.3716 | 10.862 | 115 | 33.3437 | 0 | 254.0287 | 0
7802 | 783.1268 | 1.811 | 18.5027 | 95.0497 | 79.0753 | 4.75 | 78.3707 | 4.1468 | 7.9578 | 25.6725 | 70.0381 | 8.3732 | 194.647 | 103.2022 | 224.1027 | 9.2066 | 48.0613 | 10.8502 | 114 | 34.1379 | 0 | 252.9453 | 0
7803 | 771.2799 | 1.7734 | 18.5633 | 93.9862 | 77.1754 | 5.6997 | 78.8989 | 4.3231 | 7.8797 | 25.5502 | 70.2585 | 8.4464 | 196.4334 | 106.4388 | 224.0468 | 9.2339 | 47.928 | 11.5411 | 111 | 33.4444 | 0 | 256.6886 | 0
7804 | 772.676 | 1.6789 | 19.5367 | 93.1606 | 77.4978 | 4.7516 | 78.7777 | 4.3218 | 7.7612 | 28.3506 | 70.158 | 8.426 | 192.3052 | 111.4821 | 221.2187 | 9.1726 | 47.9844 | 11.6818 | 108 | 33.1405 | 0 | 246.37 | 0
7805 | 778.2105 | 1.952 | 21.1237 | 95.5667 | 77.5625 | 4.7487 | 78.4996 | 4.3463 | 7.6942 | 38.8414 | 70.4354 | 8.4289 | 195.5808 | 104.9553 | 217.658 | 9.175 | 49.5172 | 11.1493 | 111 | 32.9573 | 0 | 278.6942 | 0
7806 | 789.5502 | 2.7823 | 24.0337 | 95.0419 | 77.685 | 4.7513 | 83.9779 | 4.3223 | 7.9452 | 41.0191 | 72.2744 | 9.3833 | 200.4907 | 107.6825 | 215.6355 | 9.2273 | 52.2153 | 10.9267 | 107 | 34.3443 | 0 | 300.3335 | 0
7807 | 838.1346 | 4.8802 | 37.3309 | 99.7282 | 71.8242 | 10.4471 | 98.4612 | 4.3853 | 11.6118 | 56.0612 | 103.2998 | 16.3685 | 227.7695 | 164.5349 | 252.8002 | 12.9948 | 48.997 | 12.4185 | 173 | 39.6506 | 0 | 348.9555 | 0
7808 | 922.1445 | 9.2107 | 70.4299 | 105.938 | 62.4672 | 18.9976 | 118.6145 | 4.2774 | 15.2632 | 93.1415 | 146.0081 | 32.1973 | 280.8082 | 240.8804 | 354.0915 | 28.068 | 53.5265 | 16.2456 | 327 | 46.4132 | 0 | 417.484 | 0
7809 | 1017.7413 | 9.564 | 88.5248 | 114.9152 | 60.711 | 19.9497 | 135.2173 | 4.9826 | 22.0983 | 95.5327 | 167.287 | 39.4728 | 342.3453 | 297.3985 | 472.6467 | 34.9049 | 63.1471 | 16.7991 | 326 | 60.0999 | 0 | 468.4651 | 0
7810 | 1096.1475 | 5.8458 | 94.9559 | 125.6304 | 57.8906 | 22.7992 | 155.7647 | 7.4174 | 26.8723 | 93.7523 | 180.8347 | 42.1711 | 392.7767 | 330.4914 | 573.3692 | 40.1339 | 75.5274 | 16.5814 | 375 | 67.4096 | 0 | 541.5636 | 0.029204
7811 | 1151.9682 | 3.4602 | 99.0767 | 129.9514 | 56.8504 | 23.7497 | 164.5522 | 8.8503 | 28.217 | 96.6695 | 187.9419 | 43.6687 | 416.229 | 348.0755 | 601.6227 | 41.1929 | 99.1554 | 16.8921 | 391 | 69.2828 | 0 | 565.1323 | 0.042813
7812 | 1191.5969 | 3.5564 | 105.761 | 132.6062 | 57.173 | 23.75 | 161.5785 | 9.194 | 25.1737 | 107.8704 | 189.3391 | 42.4533 | 434.245 | 360.1253 | 602.2212 | 40.7525 | 111.5992 | 16.7249 | 377 | 80.8968 | 0 | 582.1837 | 0.072698
7813 | 1184.8503 | 7.6048 | 103.6715 | 131.851 | 57.5755 | 23.75 | 161.6678 | 9.6274 | 20.5775 | 103.2186 | 191.7756 | 40.3323 | 441.4131 | 364.7208 | 591.1474 | 41.624 | 109.7059 | 16.5192 | 384 | 78.7764 | 0 | 601.2184 | 0.054872
7814 | 1209.0639 | 11.5562 | 98.8097 | 133.4468 | 59.4858 | 21.8505 | 169.6659 | 8.2667 | 21.6823 | 95.5211 | 192.5627 | 41.2142 | 451.7021 | 377.1654 | 581.0593 | 41.8899 | 113.9685 | 17.0537 | 337 | 78.9037 | 0 | 603.0712 | 0.01543
7815 | 1218.5018 | 11.4506 | 100.1956 | 136.0386 | 59.0752 | 21.85 | 169.7338 | 7.0745 | 22.2243 | 94.6513 | 194.1711 | 41.0692 | 492.8172 | 372.4129 | 592.8091 | 41.3075 | 115.8832 | 19.7969 | 353 | 78.8897 | 0 | 610.2334 | 0.0045785
7816 | 1203.9964 | 8.1111 | 102.356 | 143.1225 | 65.1236 | 16.1516 | 163.6717 | 8.4217 | 12.7003 | 99.0937 | 196.267 | 42.2673 | 504.603 | 369.0235 | 573.576 | 39.3482 | 113.6079 | 18.3659 | 299 | 78.2733 | 0 | 591.3754 | 0
7817 | 1164.6977 | 7.8842 | 98.3811 | 137.4762 | 66.514 | 15.2003 | 151.7668 | 7.4687 | 10.3975 | 91.4699 | 194.0718 | 40.6566 | 477.9143 | 349.0147 | 515.6229 | 32.3589 | 109.1518 | 16.7802 | 280 | 76.6343 | 0 | 560.7623 | 0
7818 | 1077.3677 | 9.5802 | 91.1819 | 122.7305 | 71.0466 | 11.4011 | 141.0734 | 5.1196 | 11.7097 | 78.4385 | 172.0311 | 35.4027 | 425.77 | 280.5756 | 448.6946 | 17.6177 | 101.3223 | 15.7029 | 254 | 69.5662 | 0 | 452.314 | 0
7819 | 1006.0886 | 9.8048 | 84.9799 | 114.0556 | 76.3818 | 6.6513 | 129.1127 | 4.4141 | 11.9097 | 66.4977 | 128.4261 | 28.2571 | 369.2733 | 226.3137 | 411.0924 | 11.2696 | 94.0723 | 15.0513 | 242 | 64.4017 | 0 | 380.7984 | 0
7820 | 966.3727 | 8.7874 | 70.5395 | 109.8828 | 76.7711 | 6.65 | 110.7677 | 3.6547 | 9.7057 | 70.0505 | 105.1908 | 14.9427 | 332.3692 | 200.7831 | 356.1924 | 10.1789 | 82.3454 | 14.6645 | 220 | 58.6258 | 0 | 315.2411 | 0
7821 | 913.1444 | 6.5643 | 38.0232 | 103.9088 | 78.049 | 5.7003 | 112.4035 | 3.1488 | 8.4782 | 65.9664 | 99.6085 | 10.157 | 312.7549 | 167.3317 | 291.6997 | 10.227 | 60.0987 | 13.9235 | 224 | 50.5682 | 0 | 276.9961 | 0
7822 | 880.9596 | 5.1501 | 27.3692 | 99.7915 | 79.0093 | 4.7503 | 114.5377 | 3.9376 | 8.0448 | 46.1064 | 96.9244 | 10.4117 | 264.0508 | 142.8598 | 252.1141 | 10.2118 | 52.3873 | 13.4559 | 223 | 47.0873 | 0 | 270.5757 | 0
7823 | 854.565 | 4.6626 | 26.9077 | 96.3588 | 77.7562 | 5.6997 | 98.9108 | 4.2431 | 7.3341 | 34.4163 | 83.6116 | 10.1833 | 224.994 | 126.5966 | 243.0186 | 10.1228 | 51.8851 | 12.951 | 197 | 40.9704 | 0 | 252.4907 | 0
7824 | 835.2207 | 4.0097 | 26.8082 | 95.6477 | 78.0456 | 5.7 | 84.1101 | 4.2036 | 7.1207 | 32.8028 | 77.7499 | 10.0097 | 209.5559 | 119.5959 | 242.7093 | 10.2001 | 50.9164 | 12.7545 | 174 | 38.8882 | 0 | 248.8713 | 0
7825 | 822.6779 | 3.8732 | 27.646 | 95.6058 | 79.3226 | 4.7503 | 79.6499 | 4.2258 | 7.273 | 32.6269 | 78.1221 | 9.6851 | 207.1858 | 112.2828 | 226.5995 | 10.033 | 50.4317 | 12.7165 | 135 | 37.3606 | 0 | 248.0228 | 0
7826 | 809.2687 | 3.1764 | 28.3117 | 96.5019 | 78.5867 | 5.6997 | 78.4529 | 4.3559 | 7.0863 | 32.4409 | 79.2993 | 9.758 | 204.8386 | 109.4754 | 223.9284 | 10.1582 | 50.5873 | 12.6142 | 135 | 35.9562 | 0 | 246.9637 | 0
7827 | 794.7009 | 2.5319 | 28.3334 | 95.6017 | 80.0197 | 4.7503 | 77.67 | 3.7033 | 7.2193 | 32.373 | 79.8252 | 9.6367 | 198.5812 | 108.5209 | 229.4165 | 10.157 | 50.5924 | 11.9714 | 142 | 35.0945 | 0 | 261.0925 | 0
7828 | 784.0863 | 2.5325 | 28.5408 | 94.7386 | 79.2746 | 5.6997 | 77.7601 | 3.1811 | 7.4074 | 34.9552 | 79.7659 | 9.6025 | 193.1251 | 105.3596 | 230.1862 | 10.0708 | 50.6161 | 11.4258 | 140 | 36.0871 | 0 | 247.6628 | 0
7829 | 792.2215 | 3.1002 | 28.4923 | 95.143 | 78.908 | 5.7 | 78.4913 | 3.7592 | 7.2878 | 45.1989 | 78.4583 | 9.605 | 195.0393 | 103.5354 | 217.162 | 10.2216 | 52.2313 | 11.3304 | 131 | 36.37 | 0 | 267.5836 | 0
7830 | 811.9303 | 4.4385 | 29.9455 | 96.1354 | 77.9144 | 5.7 | 83.7358 | 4.1813 | 8.4874 | 48.4319 | 75.7339 | 10.4657 | 203.4955 | 111.8332 | 216.7474 | 9.8214 | 54.7546 | 11.3122 | 124 | 38.1958 | 0 | 313.4348 | 0
7831 | 857.9984 | 5.7103 | 38.3023 | 103.9419 | 72.6879 | 10.4487 | 97.9479 | 4.2338 | 10.6498 | 59.9724 | 98.5922 | 20.9287 | 230.8257 | 177.515 | 236.2033 | 12.607 | 51.8559 | 11.2681 | 172 | 42.1559 | 0 | 372.7559 | 0
7832 | 929.9362 | 8.9577 | 74.899 | 108.7404 | 62.2697 | 19.9529 | 122.1197 | 4.8386 | 17.3817 | 95.7808 | 142.2561 | 35.4784 | 285.8858 | 256.6769 | 334.6956 | 27.7891 | 58.9829 | 13.1673 | 259 | 49.8365 | 0 | 430.4637 | 0
7833 | 1038.8731 | 12.7052 | 95.8051 | 122.0454 | 60.5968 | 20.8942 | 142.5366 | 5.8601 | 23.1082 | 103.9427 | 164.1252 | 39.3525 | 351.6359 | 306.9151 | 468.1405 | 36.0998 | 77.4948 | 16.3363 | 306 | 61.8009 | 0 | 520.4615 | 0
7834 | 1137.9357 | 13.2528 | 101.317 | 138.6355 | 63.0052 | 19.0005 | 153.4535 | 4.6548 | 22.8362 | 101.918 | 171.3488 | 39.5669 | 396.7587 | 340.781 | 575.7312 | 40.2749 | 101.6472 | 17.2322 | 365 | 73.9389 | 0 | 617.0639 | 0.016861
7835 | 1181.9703 | 11.4337 | 104.6854 | 145.5716 | 65.6376 | 17.1005 | 155.4012 | 6.3915 | 20.3968 | 94.7041 | 172.9717 | 42.0155 | 416.066 | 370.0512 | 615.8765 | 42.1163 | 110.8333 | 16.8964 | 399 | 78.0117 | 0 | 597.7459 | 0.029714
7836 | 1199.6228 | 6.6768 | 107.3186 | 148.6101 | 62.6396 | 19.9492 | 154.8554 | 7.6348 | 19.4558 | 94.5046 | 171.8968 | 43.5941 | 434.3389 | 386.3508 | 623.5567 | 42.7957 | 112.994 | 16.4933 | 372 | 81.9815 | 0 | 597.9228 | 0.04961
7837 | 1204.0022 | 5.2883 | 104.1697 | 144.0595 | 61.9509 | 20.8997 | 146.7589 | 7.6843 | 18.9072 | 94.5072 | 171.7714 | 43.5102 | 434.8613 | 379.8932 | 598.7798 | 43.9608 | 105.5404 | 16.7863 | 351 | 76.147 | 0 | 622.3926 | 0.034821
7838 | 1204.0022 | 7.192 | 102.0262 | 146.1201 | 62.7519 | 19.9503 | 149.9849 | 6.2058 | 21.202 | 96.3643 | 178.6011 | 43.2006 | 443.9841 | 377.4136 | 598.4958 | 46.0747 | 103.1564 | 17.3912 | 318 | 79.2866 | 0 | 641.8567 | 0.027518
7839 | 1207.7942 | 8.0274 | 104.6123 | 150.2551 | 58.8975 | 22.7992 | 162.6537 | 5.2513 | 21.556 | 99.7038 | 183.1435 | 41.445 | 457.9713 | 376.4804 | 618.0088 | 45.9845 | 101.8371 | 17.8297 | 291 | 77.5766 | 0 | 631.0019 | 0.010348
7840 | 1185.7593 | 10.1508 | 105.4934 | 144.5476 | 64.554 | 17.1016 | 162.9176 | 6.3107 | 21.131 | 99.2714 | 184.564 | 37.0753 | 457.2954 | 370.2403 | 622.495 | 42.1166 | 91.9331 | 17.8068 | 334 | 73.0056 | 0 | 632.8942 | 0
7841 | 1150.839 | 8.2905 | 102.9276 | 142.3247 | 71.4952 | 10.4518 | 152.072 | 6.6138 | 21.353 | 93.7007 | 184.2135 | 36.1901 | 434.9297 | 348.6488 | 565.1629 | 33.9679 | 86.1873 | 18.0426 | 304 | 67.4264 | 0 | 554.075 | 0
7842 | 1064.4904 | 6.8617 | 92.8818 | 126.1623 | 74.687 | 7.6008 | 137.8705 | 5.4433 | 17.83 | 87.4201 | 169.7551 | 35.7394 | 387.9944 | 286.2627 | 457.5214 | 18.413 | 77.3376 | 16.6648 | 282 | 66.6112 | 0 | 419.6075 | 0
7843 | 987.219 | 6.1838 | 83.505 | 109.9391 | 75.9076 | 6.6503 | 124.4735 | 4.9177 | 13.624 | 81.3324 | 130.5233 | 31.4038 | 336.8348 | 226.2871 | 393.0494 | 11.8897 | 70.2788 | 15.4022 | 271 | 61.0819 | 0 | 384.229 | 0
7844 | 953.5096 | 5.2391 | 69.3975 | 105.8585 | 77.929 | 4.7505 | 109.8707 | 4.1251 | 8.794 | 73.287 | 112.7825 | 17.916 | 299.3968 | 195.5993 | 352.0867 | 9.8956 | 62.6381 | 14.4815 | 270 | 55.1895 | 0 | 318.8652 | 0
7845 | 920.6414 | 5.1792 | 30.8386 | 102.591 | 77.2719 | 5.6997 | 103.7636 | 3.5718 | 7.3027 | 62.7683 | 106.0848 | 11.0545 | 263.6906 | 177.4804 | 316.3645 | 9.1914 | 57.1771 | 13.5461 | 233 | 50.6768 | 0 | 273.2308 | 0
7846 | 877.1767 | 5.6407 | 17.7455 | 98.1034 | 77.3335 | 5.7 | 95.1518 | 4.0277 | 7.2188 | 45.1826 | 98.7546 | 9.1549 | 231.5733 | 159.4263 | 285.2082 | 9.3731 | 54.6865 | 13.4256 | 232 | 47.452 | 0 | 269.2412 | 0
7847 | 849.9492 | 4.669 | 17.4146 | 95.3162 | 78.3475 | 4.7503 | 94.9642 | 4.6492 | 6.697 | 35.8159 | 83.8335 | 7.9199 | 221.5138 | 146.0854 | 268.9955 | 9.2445 | 53.6202 | 13.2209 | 216 | 43.8197 | 0 | 268.1302 | 0
7848 | 822.1348 | 3.3105 | 17.4274 | 94.9049 | 78.4574 | 4.75 | 88.2585 | 4.7454 | 6.5604 | 34.1901 | 77.8392 | 7.5531 | 210.7288 | 136.8956 | 254.2148 | 9.2965 | 53.5375 | 13.0338 | 179 | 42.935 | 0 | 253.0602 | 0
7849 | 816.5438 | 2.6952 | 17.3706 | 94.1151 | 77.695 | 5.6997 | 81.7593 | 4.666 | 6.6081 | 33.7712 | 79.8203 | 7.4126 | 202.427 | 130.6622 | 249.7028 | 9.2517 | 53.3968 | 12.9146 | 137 | 42.7996 | 0 | 258.1406 | 0
7850 | 807.592 | 2.5884 | 17.3096 | 94.5193 | 79.023 | 4.7503 | 79.9985 | 4.6324 | 6.364 | 33.6896 | 80.4995 | 7.2322 | 199.1455 | 125.3138 | 240.1979 | 9.0592 | 52.9793 | 12.7767 | 119 | 42.4828 | 0 | 257.0881 | 0
7851 | 785.3827 | 2.6331 | 17.2271 | 94.3621 | 77.2876 | 6.6495 | 80.1018 | 4.1515 | 6.1214 | 33.6971 | 77.7786 | 7.1329 | 195.1587 | 122.7537 | 228.4698 | 9.2109 | 52.872 | 12.1976 | 114 | 41.2118 | 0 | 252.7534 | 0
7852 | 780.8678 | 2.6365 | 17.1009 | 93.4584 | 78.4615 | 5.7003 | 79.4653 | 3.9225 | 6.1397 | 36.6331 | 76.2516 | 7.1183 | 192.4715 | 122.2314 | 225.929 | 9.2212 | 52.7533 | 11.5981 | 116 | 38.5097 | 0 | 259.9385 | 0
7853 | 787.5941 | 3.0858 | 17.1776 | 94.6232 | 79.8769 | 4.7503 | 79.6585 | 3.8128 | 6.17 | 46.7778 | 76.2269 | 7.1059 | 196.7143 | 121.78 | 219.2889 | 9.1523 | 54.4476 | 11.4436 | 113 | 34.4059 | 0 | 271.2869 | 0
7854 | 798.4596 | 4.5424 | 24.7115 | 95.563 | 77.2395 | 6.6495 | 85.0499 | 4.3714 | 6.779 | 49.2693 | 78.2569 | 12.3546 | 207.0615 | 129.662 | 234.3212 | 9.2518 | 57.1535 | 11.2894 | 116 | 34.0697 | 0 | 317.7724 | 0
7855 | 844.8631 | 5.5721 | 42.1152 | 102.6547 | 76.3715 | 6.65 | 99.3179 | 4.6777 | 10.218 | 60.9749 | 99.8069 | 20.4892 | 248.9127 | 182.5775 | 256.7012 | 13.1992 | 54.5593 | 11.0439 | 176 | 35.8423 | 0 | 361.1311 | 0
7856 | 907.3561 | 6.55 | 76.1437 | 104.4254 | 64.6913 | 17.0971 | 121.4362 | 5.3464 | 15.633 | 89.8369 | 133.1246 | 34.2517 | 306.647 | 256.0232 | 358.5551 | 28.9702 | 60.1991 | 13.8361 | 277 | 44.1059 | 0 | 421.8681 | 0
7857 | 1010.075 | 7.5974 | 91.7103 | 112.1121 | 62.4009 | 18.9995 | 140.1433 | 6.3488 | 23.2924 | 104.1621 | 150.396 | 39.5417 | 375.4194 | 318.5575 | 468.9082 | 36.3472 | 70.842 | 14.8664 | 333 | 57.5783 | 0 | 503.887 | 0
7858 | 1099.2043 | 8.0884 | 97.9861 | 141.5391 | 61.3711 | 19.9497 | 155.6548 | 8.4786 | 25.1531 | 109.1773 | 165.3668 | 40.1553 | 434.8339 | 346.5507 | 564.5486 | 40.9844 | 81.5549 | 15.3981 | 354 | 64.4101 | 0 | 555.4253 | 0.068014
7859 | 1133.6365 | 7.9719 | 101.6476 | 139.5795 | 59.7079 | 21.8495 | 158.9831 | 8.0809 | 24.6366 | 117.5651 | 174.6043 | 41.2341 | 458.0397 | 370.1983 | 609.9916 | 41.0529 | 88.2444 | 16.713 | 339 | 68.5526 | 0 | 577.5639 | 0.081801
7860 | 1160.3529 | 8.18 | 104.6048 | 134.014 | 62.2724 | 19.9505 | 158.5858 | 7.8706 | 24.432 | 109.3159 | 175.9626 | 39.729 | 471.3182 | 386.5168 | 619.3454 | 40.2254 | 88.3605 | 16.9033 | 322 | 82.1617 | 0 | 592.5696 | 0.099796
7861 | 1148.1193 | 8.0732 | 103.7125 | 133.2911 | 63.8016 | 19.0003 | 154.9506 | 7.9981 | 24.873 | 97.4787 | 178.9391 | 38.4286 | 463.5453 | 386.6134 | 595.977 | 40.506 | 84.7702 | 17.1851 | 367 | 76.0932 | 0 | 604.1344 | 0.10324
7862 | 1163.0963 | 6.5798 | 104.0035 | 134.421 | 62.4789 | 19.9497 | 155.6786 | 7.4878 | 24.947 | 95.8916 | 187.1959 | 39.0712 | 468.4431 | 381.6967 | 603.0595 | 41.9344 | 98.8531 | 17.7123 | 328 | 83.0311 | 0 | 617.606 | 0.029796
7863 | 1175.9052 | 6.032 | 103.7707 | 138.8924 | 64.3511 | 18.0505 | 161.2561 | 7.1829 | 24.12 | 107.935 | 191.9401 | 40.1285 | 475.9689 | 378.2903 | 598.3941 | 42.3962 | 111.4008 | 18.3975 | 277 | 88.2529 | 0 | 610.1799 | 0.0096138
7864 | 1157.0355 | 6.4793 | 104.3195 | 141.3701 | 69.4282 | 13.305 | 163.2835 | 6.3016 | 20.003 | 102.4924 | 191.9022 | 41.4073 | 465.199 | 380.2865 | 599.2205 | 41.8419 | 103.8134 | 18.8831 | 275 | 87.9434 | 0 | 600.6897 | 0
7865 | 1127.3502 | 6.7459 | 99.552 | 138.4131 | 76.2559 | 6.6482 | 155.6529 | 6.1344 | 18.2137 | 96.1183 | 186.8194 | 41.8225 | 438.5072 | 361.8331 | 563.7972 | 35.3405 | 91.4427 | 18.9198 | 255 | 82.6756 | 0 | 559.4046 | 0
7866 | 1051.8542 | 6.3162 | 93.0365 | 124.4457 | 74.292 | 8.5495 | 140.5759 | 5.8135 | 21.3442 | 78.75 | 162.4709 | 38.3575 | 382.2604 | 294.933 | 463.2703 | 19.9909 | 81.6851 | 17.9696 | 222 | 73.5516 | 0 | 430.1648 | 0
7867 | 982.7322 | 6.083 | 88.3565 | 110.875 | 76.5758 | 6.6505 | 123.768 | 6.1273 | 20.3212 | 65.48 | 121.7516 | 30.7094 | 320.8264 | 247.0977 | 383.9985 | 11.9526 | 74.5225 | 16.5844 | 210 | 65.5355 | 0 | 371.0112 | 0
7868 | 956.4614 | 5.4672 | 71.8964 | 105.1716 | 77.3186 | 5.7003 | 107.9986 | 5.7547 | 12.2859 | 58.327 | 100.4185 | 15.0388 | 284.5732 | 202.5714 | 331.6735 | 10.3281 | 65.2811 | 15.364 | 193 | 57.4625 | 0 | 312.5331 | 0
7869 | 915.8228 | 4.8956 | 33.1507 | 99.3951 | 77.3799 | 5.7 | 113.8078 | 4.9929 | 13.409 | 52.5893 | 94.6885 | 9.104 | 257.8373 | 161.6772 | 296.7831 | 9.7299 | 60.7268 | 14.7615 | 178 | 49.8616 | 0 | 290.6994 | 0
7870 | 884.4435 | 5.0598 | 19.4683 | 96.7183 | 77.6388 | 5.7 | 111.5924 | 4.4984 | 10.146 | 42.9095 | 87.4705 | 8.4605 | 229.4082 | 136.7033 | 265.3595 | 9.3831 | 59.3452 | 14.0989 | 160 | 41.3335 | 0 | 280.1191 | 0
7871 | 854.5826 | 4.7654 | 18.7349 | 93.7754 | 78.7558 | 4.7503 | 92.8347 | 4.6055 | 7.315 | 33.56 | 75.6085 | 8.2249 | 214.7979 | 126.4266 | 251.2916 | 9.9919 | 57.3681 | 13.626 | 138 | 36.3357 | 0 | 269.7744 | 0
7872 | 827.7142 | 3.3571 | 18.6302 | 93.4009 | 77.6782 | 5.6997 | 82.2691 | 4.873 | 7.002 | 30.0545 | 70.1079 | 7.8773 | 202.2699 | 119.5153 | 234.6623 | 9.9143 | 55.0771 | 13.2907 | 138 | 34.4741 | 0 | 258.5825 | 0
7873 | 823.0415 | 2.7848 | 18.4549 | 92.2668 | 78.5711 | 4.7516 | 80.4271 | 5.2977 | 7.0658 | 29.1362 | 68.3763 | 7.4832 | 197.0225 | 112.8842 | 220.7113 | 9.9253 | 54.6916 | 12.9212 | 116 | 34.6651 | 0 | 256.937 | 0
7874 | 811.2626 | 2.7398 | 18.5496 | 92.0802 | 77.464 | 5.6984 | 77.7792 | 5.4612 | 7.0373 | 28.9005 | 67.8863 | 7.1972 | 196.0651 | 112.0041 | 219.187 | 9.9017 | 54.5254 | 12.6999 | 115 | 34.0824 | 0 | 261.3814 | 0
7875 | 800.7997 | 2.7202 | 18.3831 | 91.7903 | 78.4765 | 4.7503 | 71.3626 | 5.7983 | 6.5489 | 28.2224 | 67.8687 | 7.9564 | 195.5371 | 110.4375 | 224.2116 | 9.793 | 54.2222 | 11.9348 | 115 | 32.2333 | 0 | 259.8333 | 0
7876 | 810.275 | 2.5704 | 18.45 | 91.5311 | 77.5407 | 5.6997 | 77.4151 | 5.8963 | 6.5321 | 28.1126 | 67.6787 | 7.6967 | 193.7606 | 108.5342 | 222.9767 | 10.0455 | 54.0974 | 11.4193 | 109 | 31.9135 | 0 | 266.8311 | 0
7877 | 814.8672 | 3.5206 | 18.6519 | 91.5786 | 77.5953 | 5.7 | 79.9114 | 6.1903 | 6.3844 | 28.2228 | 67.7564 | 7.1852 | 196.3052 | 106.6048 | 221.8169 | 9.8518 | 56.2785 | 11.3411 | 109 | 32.4405 | 0 | 285.4852 | 0
7878 | 824.7646 | 4.5901 | 19.4869 | 92.227 | 75.6511 | 7.5995 | 75.8028 | 5.7699 | 6.9985 | 30.3714 | 69.7699 | 8.7925 | 203.0225 | 111.8566 | 230.759 | 9.8396 | 58.1489 | 11.4281 | 110 | 34.2112 | 0 | 335.544 | 0
7879 | 867.7097 | 5.9322 | 37.9188 | 98.2193 | 74.4087 | 8.5497 | 91.0401 | 5.3809 | 11.857 | 45.4343 | 91.7834 | 17.1407 | 226.7241 | 165.9316 | 271.5116 | 13.7548 | 54.8972 | 12.7452 | 207 | 42.4089 | 0 | 373.313 | 0
7880 | 934.4004 | 6.844 | 73.193 | 102.1691 | 62.8756 | 19.0024 | 121.5937 | 6.0706 | 15.714 | 75.4173 | 132.0705 | 32.4666 | 296.7912 | 248.0064 | 363.9603 | 28.4126 | 59.3884 | 14.8787 | 280 | 49.1231 | 0 | 437.6267 | 0
7881 | 1024.1724 | 11.1207 | 91.1518 | 111.1025 | 62.5878 | 18.9947 | 134.5693 | 8.5962 | 20.457 | 83.2894 | 156.0261 | 34.7802 | 375.4345 | 303.3065 | 455.4528 | 35.1986 | 69.8576 | 16.8629 | 312 | 60.4468 | 0 | 489.3881 | 0
7882 | 1118.0878 | 8.808 | 97.9591 | 120.202 | 62.4842 | 19 | 148.1342 | 9.9386 | 22.791 | 96.6791 | 173.1745 | 35.4122 | 433.5145 | 333.7803 | 549.2231 | 39.7604 | 81.0994 | 16.3226 | 347 | 63.9711 | 0 | 542.287 | 0.027829
7883 | 1169.4831 | 8.8462 | 101.8497 | 124.2522 | 61.7718 | 19.9497 | 159.7016 | 9.2059 | 22.44 | 97.6034 | 178.6546 | 39.8752 | 438.9379 | 356.1075 | 594.5924 | 41.4949 | 85.7392 | 16.1226 | 354 | 67.2883 | 0 | 575.7529 | 0.057879
7884 | 1191.4904 | 11.1174 | 104.6343 | 126.7631 | 64.2988 | 18.0505 | 160.0001 | 7.9311 | 20.126 | 94.5373 | 178.7283 | 40.5452 | 430.7884 | 370.0325 | 604.2157 | 41.3644 | 87.7518 | 15.9444 | 316 | 73.289 | 0 | 571.8764 | 0.068462
7885 | 1201.8734 | 8.8482 | 102.4514 | 131.6554 | 63.3945 | 19.005 | 161.1438 | 7.5281 | 17.5777 | 93.7754 | 181.1045 | 41.2001 | 424.7749 | 378.7494 | 596.7159 | 42.1061 | 87.9887 | 15.8106 | 349 | 72.0608 | 0 | 599.2391 | 0.042383
7886 | 1210.2423 | 5.5803 | 103.8839 | 141.8747 | 63.5297 | 18.045 | 165.3943 | 6.9073 | 23.4178 | 90.5716 | 183.2501 | 42.2488 | 437.8346 | 389.2049 | 597.1785 | 43.9372 | 88.6081 | 16.4815 | 342 | 73.4943 | 0 | 615.0771 | 0.02356
7887 | 1196.6396 | 5.1987 | 105.1952 | 145.2205 | 63.1512 | 18.05 | 167.7534 | 6.8015 | 24.6412 | 93.8259 | 183.7283 | 41.4951 | 456.1042 | 384.3318 | 599.1348 | 41.6102 | 89.8751 | 17.1575 | 329 | 74.4763 | 0 | 595.1959 | 0.0095402
7888 | 1184.1187 | 6.5322 | 103.9079 | 143.286 | 68.178 | 13.3013 | 163.6987 | 7.4302 | 21.7278 | 97.8667 | 183.9811 | 40.5036 | 457.8778 | 373.0373 | 598.3859 | 40.83 | 89.686 | 18.349 | 307 | 74.7319 | 0 | 571.1891 | 0
7889 | 1140.2596 | 7.0532 | 101.2692 | 140.675 | 72.983 | 8.5513 | 152.3118 | 7.9698 | 18.1561 | 89.1397 | 183.7871 | 41.2415 | 418.1864 | 339.911 | 544.9459 | 34.1737 | 87.6481 | 18.4823 | 305 | 68.2349 | 0 | 534.7545 | 0
7890 | 1063.6718 | 7.1093 | 96.3733 | 124.7841 | 72.2054 | 9.4997 | 134.0264 | 7.5781 | 11.5626 | 71.1884 | 172.4905 | 37.2352 | 365.9707 | 260.1913 | 456.8931 | 19.4109 | 80.7609 | 18.0929 | 268 | 60.6488 | 0 | 423.5373 | 0
7891 | 995.4307 | 6.4746 | 89.3845 | 108.0585 | 74.6296 | 7.6005 | 123.5444 | 6.9768 | 15.4159 | 59.72 | 142.3052 | 33.8155 | 312.1656 | 188.6796 | 387.1779 | 14.1053 | 73.0634 | 16.9511 | 249 | 57.0641 | 0 | 365.5323 | 0
7892 | 938.0524 | 5.5891 | 75.5322 | 101.7861 | 76.851 | 5.7005 | 111.707 | 6.5903 | 11.6163 | 57.2531 | 132.7836 | 25.076 | 274.8797 | 163.1269 | 348.4252 | 11.4732 | 65.2972 | 15.4397 | 226 | 51.2854 | 0 | 298.8831 | 0
7893 | 889.465 | 5.632 | 36.9628 | 99.7216 | 76.8567 | 5.7 | 109.5816 | 5.6173 | 9.1543 | 53.5795 | 118.5017 | 19.4317 | 249.0108 | 152.2289 | 308.3455 | 10.0106 | 60.1681 | 14.4345 | 206 | 43.3864 | 0 | 278.7803 | 0
7894 | 855.4752 | 5.2751 | 24.3669 | 97.9945 | 78.0597 | 4.7503 | 96.4443 | 5.2734 | 8.5652 | 44.0253 | 99.0101 | 16.9456 | 226.7191 | 137.9325 | 274.6893 | 9.845 | 59.1271 | 13.7986 | 193 | 44.174 | 0 | 274.7853 | 0
7895 | 831.2978 | 5.1414 | 20.0288 | 94.3386 | 77.4819 | 5.6997 | 71.0663 | 5.727 | 6.8608 | 34.5124 | 79.2017 | 16.275 | 212.0702 | 126.462 | 251.6623 | 9.5953 | 57.985 | 13.563 | 170 | 38.3593 | 0 | 269.382 | 0
7896 | 806.8082 | 3.6722 | 17.8151 | 92.6855 | 78.1388 | 5.7 | 68.8529 | 5.6898 | 6.3049 | 32.6566 | 69.9394 | 15.6484 | 203.0458 | 116.9438 | 241.8212 | 9.9638 | 56.588 | 13.2525 | 151 | 37.6848 | 0 | 274.8741 | 0
7897 | 809.5673 | 3.1445 | 17.6238 | 92.2565 | 79.6861 | 4.7503 | 69.016 | 6.0829 | 6.429 | 33.0116 | 69.2068 | 12.7264 | 198.9838 | 109.4368 | 235.0162 | 9.9286 | 55.5892 | 12.8622 | 124 | 38.8961 | 0 | 277.5315 | 0
7898 | 804.1949 | 2.9688 | 17.5938 | 93.7597 | 79.0237 | 5.6997 | 63.6478 | 6.2911 | 6.4436 | 32.9134 | 70.1953 | 11.6984 | 198.0991 | 104.808 | 233.5505 | 9.8274 | 55.3516 | 11.7 | 123 | 37.4816 | 0 | 280.5421 | 0
7899 | 793.9896 | 2.8572 | 17.5532 | 92.8574 | 79.8181 | 4.7503 | 68.0299 | 5.9741 | 7.247 | 31.3757 | 69.7575 | 12.53 | 197.0549 | 101.0696 | 234.6602 | 9.9231 | 55.1656 | 11.2159 | 114 | 35.7242 | 0 | 281.4838 | 0
7900 | 792.9319 | 2.5425 | 17.6543 | 91.9646 | 79.6989 | 4.75 | 75.0661 | 5.8999 | 6.7602 | 30.3639 | 68.8384 | 12.1519 | 196.5977 | 94.4828 | 230.8162 | 9.5769 | 55.0774 | 11.207 | 113 | 34.9005 | 0 | 273.9909 | 0
7901 | 794.4067 | 3.3606 | 17.4753 | 92.3227 | 78.0518 | 5.7013 | 67.5244 | 5.5605 | 6.2107 | 30.0039 | 68.8354 | 11.3977 | 199.4518 | 90.7004 | 225.7969 | 9.9375 | 56.5409 | 11.1958 | 108 | 33.0169 | 0 | 287.5018 | 0
7902 | 808.028 | 4.1796 | 25.0608 | 92.9355 | 78.2408 | 4.75 | 70.8156 | 4.6462 | 6.3493 | 30.6369 | 71.927 | 12.0128 | 209.4748 | 97.6645 | 227.9457 | 9.8829 | 59.0994 | 11.1495 | 113 | 34.5603 | 0 | 322.0674 | 0
7903 | 855.939 | 5.9303 | 44.4478 | 100.6403 | 76.1513 | 6.6482 | 92.7232 | 4.2578 | 12.0658 | 48.5542 | 92.7752 | 18.38 | 233.7179 | 165.0736 | 251.6434 | 13.0942 | 56.1437 | 11.1284 | 201 | 41.5669 | 0 | 355.1275 | 0
7904 | 927.9652 | 10.5157 | 76.3008 | 104.2284 | 64.8339 | 17.0971 | 118.3439 | 5.115 | 18.0525 | 89.4293 | 129.6733 | 34.4114 | 284.963 | 242.0034 | 353.0649 | 27.3265 | 61.3922 | 13.7193 | 236 | 48.4176 | 0 | 418.018 | 0
7905 | 1001.1706 | 14.3779 | 92.2776 | 110.9629 | 62.5197 | 18.9995 | 138.7996 | 6.7926 | 22.0913 | 103.3636 | 156.1462 | 40.7635 | 349.5395 | 302.6089 | 496.0823 | 35.9555 | 71.2156 | 17.3714 | 327 | 66.8843 | 0 | 489.7124 | 0
7906 | 1089.2939 | 10.5544 | 97.8226 | 124.3809 | 62.3907 | 19 | 157.1718 | 7.5845 | 24.6193 | 95.8688 | 172.129 | 41.0287 | 390.7063 | 332.7703 | 562.5388 | 40.995 | 82.3418 | 16.3943 | 321 | 76.1379 | 0 | 538.5632 | 0.015056
7907 | 1140.6171 | 7.9958 | 98.3766 | 131.2485 | 62.2318 | 19 | 164.9209 | 8.466 | 26.3237 | 85.0873 | 178.5958 | 40.919 | 408.3164 | 352.453 | 586.1695 | 41.7819 | 88.0671 | 16.4647 | 367 | 75.2877 | 0 | 564.1673 | 0.041039
7908 | 1167.6085 | 7.6073 | 102.1185 | 135.5455 | 59.8098 | 17.1005 | 166.4354 | 7.9685 | 24.1513 | 85.5905 | 178.2756 | 39.1735 | 428.2886 | 365.5453 | 578.5741 | 40.9576 | 88.2298 | 16.8254 | 337 | 75.4666 | 0 | 567.5992 | 0.027263
7909 | 1153.1535 | 7.6961 | 99.1701 | 132.9742 | 15.7873 | 18.9995 | 162.663 | 6.332 | 16.4407 | 80.4845 | 177.6907 | 33.9566 | 401.8618 | 366.627 | 560.2428 | 41.9882 | 88.558 | 16.9864 | 369 | 66.4303 | 0 | 577.1658 | 0.047648
7910 | 1144.3718 | 9.39 | 97.0054 | 132.2188 | -4.1434 | 16.1508 | 160.2266 | 6.7405 | 18.3437 | 73.7736 | 179.5284 | 32.3975 | 427.8926 | 379.1705 | 556.5968 | 44.2142 | 86.5778 | 18.23 | 313 | 68.217 | 0 | 578.941 | 0.033961
7911 | 1154.4537 | 12.1907 | 101.1839 | 133.6388 | -1.151 | 13.3008 | 160.5944 | 7.6869 | 21.1147 | 78.153 | 186.7205 | 37.8688 | 442.8804 | 387.5675 | 559.172 | 42.557 | 85.9275 | 19.2248 | 287 | 70.4556 | 0 | 561.337 | 0.012233
7912 | 1150.9176 | 9.4893 | 100.0787 | 134.2692 | -5.1409 | 17.0989 | 154.5193 | 7.4079 | 21.0055 | 89.0962 | 199.3944 | 39.6164 | 424.7183 | 369.7716 | 531.0913 | 40.7164 | 85.8881 | 18.9134 | 296 | 69.674 | 0 | 543.4831 | 0
7913 | 1100.5178 | 7.5607 | 96.8602 | 130.8862 | -5.1431 | 17.1 | 143.7705 | 6.5139 | 18.6457 | 98.4909 | 186.4973 | 40.1317 | 388.8273 | 341.8471 | 477.7799 | 28.2047 | 84.1443 | 17.9845 | 290 | 66.6463 | 0 | 489.959 | 0
7914 | 1010.2136 | 6.7059 | 74.2093 | 122.3315 | 3.8608 | 8.5524 | 129.1063 | 4.7256 | 16.2993 | 83.8766 | 156.7106 | 38.4578 | 338.332 | 261.8331 | 393.7631 | 17.9836 | 78.0662 | 15.8971 | 257 | 61.134 | 0 | 383.203 | 0
7915 | 943.1693 | 5.8968 | 36.5054 | 110.4014 | 6.8655 | 5.7008 | 115.8575 | 3.9896 | 13.1372 | 65.9344 | 116.7207 | 29.9967 | 290.9124 | 181.439 | 360.0066 | 14.0447 | 70.5576 | 14.47 | 230 | 58.7326 | 0 | 331.1537 | 0
7916 | 895.7591 | 5.3569 | 20.5758 | 101.773 | 6.8663 | 5.7 | 98.0956 | 4.8666 | 10.0847 | 52.9718 | 93.0721 | 14.0743 | 255.4897 | 148.2635 | 329.7771 | 12.6492 | 61.4391 | 13.5849 | 226 | 52.3754 | 0 | 295.3768 | 0
7917 | 852.8681 | 4.8668 | 17.9785 | 98.5748 | 6.8624 | 5.7 | 94.7789 | 5.0525 | 8.0617 | 49.0757 | 82.3585 | 8.4734 | 233.7909 | 136.2314 | 285.5597 | 11.7111 | 55.6197 | 13.1078 | 216 | 44.6051 | 0 | 262.0491 | 0
7918 | 828.1216 | 4.6165 | 17.3373 | 98.1121 | 7.8628 | 4.7503 | 86.6081 | 4.9319 | 7.2718 | 39.3516 | 76.3676 | 7.9298 | 214.9887 | 130.9592 | 255.523 | 11.0398 | 54.7783 | 14.3356 | 211 | 38.8503 | 0 | 247.9224 | 0
7919 | 808.3966 | 4.1412 | 16.9488 | 96.0206 | 6.863 | 5.6997 | 80.6671 | 5.1399 | 6.6924 | 29.9525 | 73.3695 | 7.6718 | 207.6555 | 122.4927 | 244.8372 | 10.9718 | 53.9925 | 14.6211 | 181 | 35.5489 | 0 | 247.9089 | 0
7920 | 792.8357 | 3.0716 | 16.9808 | 95.3974 | 7.8611 | 4.7503 | 78.511 | 4.2674 | 6.9151 | 30.0481 | 70.9862 | 7.5493 | 204.4387 | 115.2751 | 237.5043 | 10.8488 | 54.0336 | 13.7053 | 164 | 36.06 | 0 | 243.0083 | 0
7921 | 795.0902 | 2.6767 | 17.221 | 95.1956 | 6.8666 | 5.6997 | 78.1951 | 3.7578 | 6.9568 | 29.3593 | 72.259 | 8.1482 | 201.4889 | 99.6655 | 233.0667 | 11.0506 | 54.0162 | 13.1889 | 144 | 34.8873 | 0 | 250.1903 | 0
7922 | 796.1102 | 2.6794 | 17.0366 | 95.3399 | 7.8652 | 4.7503 | 78.3057 | 4.5287 | 6.8979 | 27.7856 | 71.1895 | 8.2897 | 200.2331 | 95.188 | 238.4742 | 10.9934 | 53.6759 | 12.9791 | 146 | 37.6205 | 0 | 250.2182 | 0
7923 | 780.4387 | 2.6564 | 16.6671 | 94.8191 | 6.8643 | 5.6997 | 78.7144 | 4.9011 | 6.8341 | 26.3303 | 70.448 | 8.6308 | 197.7166 | 93.871 | 242.7106 | 10.9887 | 53.6782 | 12.7754 | 148 | 34.9773 | 0 | 242.7098 | 0
7924 | 781.2646 | 2.6725 | 16.7505 | 94.6922 | 7.8617 | 4.7503 | 78.2321 | 5.1881 | 6.681 | 25.8498 | 71.1743 | 9.1167 | 193.3217 | 90.633 | 232.7857 | 10.9631 | 53.3136 | 12.7514 | 141 | 34.0136 | 0 | 248.3699 | 0
7925 | 780.8923 | 3.0916 | 17.0319 | 95.007 | 6.8654 | 5.6997 | 78.344 | 5.0451 | 6.716 | 26.0758 | 71.3799 | 8.8857 | 190.6874 | 89.8208 | 221.6119 | 10.7742 | 54.373 | 12.7478 | 139 | 31.7855 | 0 | 244.9249 | 0
7926 | 786.7498 | 3.92 | 17.4174 | 95.4499 | 7.8633 | 4.7503 | 77.5332 | 4.0873 | 7.0223 | 26.1858 | 71.3543 | 7.9257 | 186.9034 | 88.7558 | 218.0215 | 10.9059 | 56.9498 | 12.7059 | 139 | 32.9028 | 0 | 250.6737 | 0
7927 | 803.6108 | 4.0684 | 31.7364 | 95.9222 | 6.8631 | 5.6997 | 78.14 | 3.6243 | 7.5313 | 26.0827 | 72.4222 | 7.2852 | 186.1701 | 87.48 | 218.2638 | 11.0307 | 54.1448 | 12.6678 | 135 | 32.5119 | 0 | 247.3409 | 0
7928 | 826.3612 | 4.2221 | 42.3458 | 95.5857 | 7.8652 | 4.7503 | 81.1202 | 4.439 | 7.3675 | 26.1676 | 80.381 | 9.0397 | 194.883 | 93.3264 | 220.0179 | 15.6237 | 52.9905 | 12.6904 | 142 | 42.8056 | 0 | 249.9322 | 0
7929 | 832.7288 | 4.4527 | 49.7382 | 95.3061 | 5.8643 | 6.6495 | 87.4496 | 5.0873 | 6.4875 | 35.0064 | 111.5373 | 13.9888 | 199.9366 | 104.4754 | 217.2932 | 30.7386 | 51.944 | 12.7014 | 197 | 51.7979 | 0 | 250.8554 | 0
7930 | 853.4142 | 3.9555 | 66.1407 | 92.9336 | 6.8605 | 5.7003 | 103.0619 | 6.0794 | 6.7992 | 49.4515 | 137.0292 | 16.5482 | 206.1514 | 105.0743 | 239.7008 | 39.6749 | 52.2114 | 12.6878 | 152 | 53.3613 | 0 | 240.2245 | 0.0047043
7931 | 875.3471 | 3.1919 | 74.386 | 94.1038 | 6.8584 | 5.7 | 112.1253 | 6.7827 | 6.2242 | 58.1489 | 141.4778 | 19.2142 | 217.4066 | 121.0023 | 255.3173 | 42.8554 | 55.3792 | 12.693 | 207 | 54.9211 | 0 | 250.5348 | 0.025776
7932 | 888.2257 | 2.7141 | 76.6757 | 95.9352 | 5.8643 | 6.6497 | 111.2394 | 6.3836 | 6.2125 | 60.4932 | 113.5704 | 19.9843 | 222.4633 | 125.7372 | 253.036 | 43.3243 | 57.1029 | 12.9255 | 189 | 55.2154 | 0 | 267.014 | 0.048348
7933 | 876.2309 | 2.8519 | 74.3341 | 96.8848 | 6.8615 | 5.7003 | 110.9018 | 4.9151 | 7.7757 | 63.7771 | 94.3977 | 20.1817 | 225.5766 | 129.4794 | 252.5766 | 42.7267 | 54.7547 | 13.0349 | 210 | 56.1127 | 0 | 254.9548 | 0.027445
7934 | 866.3399 | 3.3194 | 68.9576 | 98.524 | 7.8594 | 4.7503 | 108.8991 | 3.7998 | 9.8416 | 58.752 | 92.9435 | 17.943 | 225.9733 | 131.3942 | 268.8973 | 41.6595 | 54.6181 | 13.1947 | 240 | 53.4543 | 0 | 256.7607 | 0.02964
7935 | 864.9006 | 3.6153 | 36.1945 | 97.2944 | 6.8569 | 5.6997 | 107.0911 | 3.7665 | 11.3055 | 55.7101 | 93.4334 | 20.0699 | 221.4102 | 130.8298 | 288.131 | 33.8231 | 53.8579 | 13.3772 | 216 | 52.5162 | 0 | 252.6071 | 0.008093
7936 | 865.0073 | 5.0712 | 23.8402 | 96.7399 | 7.8571 | 4.7516 | 106.286 | 3.8076 | 10.168 | 64.2465 | 91.6432 | 19.1757 | 224.614 | 124.7839 | 299.6065 | 25.4429 | 54.3583 | 14.4415 | 247 | 52.5609 | 0 | 251.981 | 0
7937 | 866.9628 | 5.0274 | 23.977 | 97.8825 | 7.8628 | 4.7487 | 104.6169 | 3.2546 | 10.3927 | 50.1233 | 94.1819 | 15.1932 | 227.6657 | 129.795 | 293.6968 | 13.8668 | 55.786 | 15.0303 | 256 | 47.6205 | 0 | 265.3042 | 0
7938 | 854.7096 | 4.7434 | 24.0077 | 97.7442 | 6.8628 | 5.6997 | 109.4967 | 3.4472 | 11.6632 | 37.0664 | 94.2876 | 11.9747 | 226.3671 | 127.2999 | 282.7142 | 10.0621 | 56.2139 | 14.853 | 237 | 46.5357 | 0 | 268.712 | 0
7939 | 840.4337 | 4.916 | 24.1016 | 96.9802 | 4.8699 | 7.5995 | 101.3597 | 4.1278 | 11.3018 | 33.1238 | 81.7989 | 8.7713 | 223.7393 | 121.0404 | 273.4585 | 9.8833 | 55.4168 | 14.541 | 278 | 44.9107 | 0 | 268.5454 | 0
7940 | 826.7433 | 5.2392 | 23.8843 | 95.4755 | 6.8649 | 5.7021 | 87.4547 | 4.407 | 10.6015 | 33.0517 | 75.5379 | 7.7271 | 221.0102 | 116.0857 | 256.6895 | 9.8561 | 55.1289 | 14.0541 | 278 | 41.6695 | 0 | 274.7295 | 0
7941 | 812.1655 | 4.9143 | 24.0322 | 93.7381 | 7.8693 | 4.7487 | 82.8294 | 4.4992 | 9.3798 | 32.158 | 74.6579 | 7.7585 | 218.5881 | 112.5878 | 254.5852 | 9.9927 | 55.4828 | 13.9132 | 301 | 38.5886 | 0 | 268.5062 | 0
7942 | 809.8006 | 4.6606 | 23.9608 | 93.2871 | 5.867 | 6.6495 | 81.3219 | 4.8417 | 8.2123 | 27.9175 | 74.0853 | 7.6481 | 203.1837 | 113.6527 | 252.871 | 9.844 | 55.6365 | 13.521 | 269 | 37.2582 | 0 | 276.0859 | 0
7943 | 797.8067 | 4.1419 | 23.8441 | 92.3388 | 6.8644 | 5.7003 | 79.4757 | 4.8334 | 7.5823 | 26.7409 | 73.0901 | 7.6953 | 190.8725 | 105.9137 | 251.3306 | 9.8639 | 54.5277 | 13.3811 | 234 | 35.0663 | 0 | 283.8374 | 0
7944 | 776.1628 | 3.2426 | 23.966 | 92.0331 | 6.8631 | 5.7 | 78.765 | 4.2592 | 7.5979 | 29.154 | 72.1805 | 7.7718 | 188.7892 | 101.2184 | 236.0862 | 9.7856 | 53.1946 | 13.0723 | 204 | 35.022 | 0 | 300.9356 | 0
7945 | 796.1798 | 3.1131 | 23.8849 | 92.1734 | 6.8633 | 5.7 | 78.6819 | 3.9763 | 7.5877 | 29.1213 | 70.5059 | 7.6127 | 183.872 | 99.836 | 225.2164 | 10.3361 | 53.1488 | 13.0072 | 205 | 35.6419 | 0 | 293.7481 | 0
7946 | 799.3193 | 3.085 | 24.0248 | 92.4406 | 7.8658 | 4.7503 | 78.9933 | 4.0466 | 7.1514 | 27.6585 | 69.0538 | 7.4787 | 182.5423 | 96.0016 | 221.9282 | 10.6924 | 53.2329 | 13.0839 | 177 | 35.2692 | 0 | 297.0844 | 0
7947 | 779.6443 | 3.0851 | 23.9904 | 92.7075 | 1.8704 | 10.4484 | 77.7837 | 4.7799 | 6.6206 | 26.5934 | 69.0196 | 7.4298 | 179.5804 | 92.5913 | 224.6355 | 10.7737 | 53.5847 | 12.7744 | 161 | 33.1202 | 0 | 287.9911 | 0
7948 | 775.4459 | 3.0177 | 23.9999 | 91.936 | 4.8655 | 7.6008 | 76.7836 | 5.1194 | 6.6592 | 25.2869 | 69.7547 | 7.5752 | 178.4591 | 89.4732 | 223.5302 | 10.6891 | 53.3268 | 12.3171 | 156 | 32.2054 | 0 | 269.6518 | 0
7949 | 763.0681 | 3.2747 | 23.9873 | 91.9046 | 4.8647 | 7.6 | 68.5449 | 5.2364 | 6.6798 | 25.3134 | 69.0301 | 7.6628 | 177.2309 | 89.9813 | 222.9163 | 10.7197 | 54.7331 | 11.8615 | 160 | 32.6212 | 0 | 267.125 | 0
7950 | 761.5906 | 4.0657 | 24.0256 | 91.8241 | 7.8664 | 4.7508 | 68.8012 | 5.3266 | 6.7173 | 25.282 | 68.4398 | 7.4632 | 173.9667 | 89.9791 | 220.6709 | 10.4948 | 57.1296 | 11.6648 | 153 | 32.1796 | 0 | 271.4391 | 0
7951 | 777.7525 | 4.3438 | 24.1295 | 93.6925 | 6.8679 | 5.6997 | 75.6381 | 5.4901 | 7.0553 | 25.855 | 69.0822 | 7.3998 | 174.2447 | 89.1992 | 232.0186 | 10.758 | 54.1075 | 11.646 | 133 | 32.6592 | 0 | 273.09 | 0
7952 | 788.7318 | 4.4677 | 24.8824 | 93.0475 | 6.8665 | 5.7 | 73.5489 | 5.1755 | 7.094 | 25.5189 | 69.5734 | 7.3683 | 180.3957 | 91.8379 | 237.5526 | 10.5792 | 52.5619 | 11.6791 | 126 | 31.8524 | 0 | 268.6565 | 0
7953 | 786.4828 | 3.8729 | 24.5859 | 90.3198 | 6.8616 | 5.7 | 66.219 | 4.5564 | 6.2573 | 34.4032 | 68.0929 | 5.3434 | 187.1796 | 92.6623 | 237.6211 | 10.278 | 52.3067 | 11.7056 | 134 | 34.6794 | 0 | 259.4165 | 0
7954 | 798.226 | 2.8207 | 24.3204 | 89.4366 | 6.8662 | 5.7 | 85.7386 | 4.6774 | 5.8038 | 50.6626 | 69.691 | 4.4915 | 192.5393 | 93.7527 | 239.5061 | 11.7374 | 51.9835 | 11.6908 | 186 | 36.1406 | 0 | 257.3235 | 0.15264
7955 | 816.4459 | 2.5591 | 24.5771 | 91.2294 | 5.8636 | 6.6497 | 105.0762 | 4.4203 | 5.5278 | 56.1535 | 83.361 | 4.4749 | 205.9494 | 102.2355 | 240.3962 | 11.2636 | 52.7987 | 11.7134 | 171 | 35.6306 | 0 | 264.9977 | 0.16978
7956 | 829.3878 | 3.3845 | 22.5259 | 92.1142 | 5.8601 | 6.65 | 99.6137 | 4.6934 | 7.5542 | 60.8153 | 90.12 | 6.4485 | 215.6416 | 109.8496 | 239.1516 | 10.0616 | 53.8502 | 12.164 | 203 | 39.4443 | 0 | 269.3065 | 0.20135
7957 | 826.7263 | 3.6786 | 18.4586 | 90.1945 | 6.8586 | 5.7003 | 92.5786 | 5.0034 | 6.8635 | 65.485 | 91.234 | 9.0747 | 227.4318 | 114.827 | 241.7862 | 9.3531 | 53.8753 | 12.8761 | 210 | 39.1988 | 0 | 277.0757 | 0.22356
7958 | 830.374 | 4.2442 | 17.3338 | 91.5545 | 7.8634 | 4.7503 | 103.401 | 5.079 | 7.6073 | 58.9495 | 97.1553 | 9.7445 | 235.046 | 123.0851 | 251.1618 | 9.8693 | 53.5079 | 13.204 | 200 | 41.1235 | 0 | 281.4783 | 0.19146
7959 | 821.8111 | 6.9932 | 17.1359 | 95.1012 | 6.8603 | 5.6997 | 101.1684 | 5.1319 | 8.6058 | 58.854 | 111.3469 | 9.7143 | 234.8204 | 129.9434 | 264.152 | 10.0299 | 52.1964 | 13.4114 | 178 | 44.1178 | 0 | 276.9978 | 0.091676
7960 | 832.1827 | 10.3079 | 17.2239 | 100.5611 | 7.8576 | 4.7503 | 98.5651 | 5.0314 | 7.8831 | 53.54 | 111.5735 | 10.3094 | 225.8091 | 133.3316 | 283.893 | 9.983 | 51.681 | 13.8712 | 171 | 45.9402 | 0 | 279.1992 | 0
7961 | 849.3364 | 7.0803 | 18.2097 | 102.6958 | 6.8661 | 5.6997 | 99.6391 | 5.2941 | 8.9631 | 37.1165 | 114.1342 | 12.0682 | 227.6683 | 140.3385 | 302.6203 | 10.6149 | 53.8921 | 14.112 | 169 | 45.8463 | 0 | 287.3492 | 0
7962 | 847.9825 | 5.0103 | 18.0813 | 98.0445 | 5.8644 | 6.6497 | 110.8899 | 5.2571 | 8.1492 | 30.6473 | 119.8346 | 11.4075 | 223.9935 | 135.9528 | 308.3224 | 10.5939 | 54.784 | 13.7909 | 169 | 45.4227 | 0 | 287.9066 | 0
7963 | 848.1627 | 4.9838 | 17.5692 | 94.3175 | 5.8638 | 6.65 | 99.4593 | 5.3658 | 7.8419 | 29.7776 | 109.0546 | 10.7294 | 210.1953 | 128.5958 | 310.6134 | 10.6435 | 56.5531 | 13.4535 | 141 | 45.2058 | 0 | 283.4835 | 0
7964 | 837.453 | 5.0295 | 17.6753 | 93.5148 | 4.8664 | 7.5997 | 76.9559 | 6.0852 | 7.8002 | 30.1597 | 93.1896 | 11.8035 | 207.2861 | 121.6449 | 306.4004 | 10.5966 | 55.7268 | 12.8191 | 142 | 43.0253 | 0 | 284.4436 | 0
7965 | 807.1207 | 4.9921 | 17.5686 | 94.8067 | 4.868 | 7.6 | 74.0132 | 6.9718 | 7.9407 | 35.0148 | 79.2619 | 11.0759 | 207.8847 | 111.8547 | 276.27 | 10.5467 | 54.7112 | 12.5893 | 139 | 40.0292 | 0 | 276.482 | 0
7966 | 785.2332 | 4.7223 | 17.5839 | 94.517 | 6.867 | 5.7005 | 75.5383 | 6.8751 | 7.7978 | 35.2909 | 75.0082 | 9.0135 | 203.7768 | 104.1775 | 261.1765 | 10.3318 | 54.7325 | 12.5632 | 139 | 36.6121 | 0 | 277.5089 | 0
7967 | 767.0409 | 4.1009 | 17.6559 | 93.9995 | 6.8621 | 5.7 | 79.5979 | 6.2554 | 7.1438 | 30.465 | 72.9358 | 8.539 | 190.797 | 100.421 | 254.8731 | 9.8886 | 53.688 | 12.3586 | 125 | 35.2598 | 0 | 277.3288 | 0
7968 | 749.7495 | 3.1335 | 17.4715 | 93.7771 | 6.8617 | 5.7 | 79.2709 | 6.0287 | 6.6548 | 27.2681 | 71.0882 | 8.3687 | 179.6295 | 99.9184 | 243.0349 | 9.7467 | 53.2373 | 12.2875 | 114 | 32.802 | 0 | 281.4932 | 0
7969 | 751.9302 | 3.0272 | 17.6383 | 93.3296 | 6.8662 | 5.7 | 72.793 | 7.9775 | 6.9728 | 27.7708 | 70.6495 | 7.83 | 175.6823 | 96.2798 | 234.2031 | 9.7079 | 52.9413 | 12.0899 | 116 | 30.6723 | 0 | 276.7051 | 0
7970 | 744.6078 | 2.9844 | 17.5878 | 93.008 | 6.862 | 5.7 | 64.0414 | 7.2296 | 6.7745 | 29.4228 | 70.828 | 7.7097 | 175.6091 | 94.0176 | 232.9236 | 9.6661 | 52.9715 | 11.5511 | 118 | 30.5368 | 0 | 270.1796 | 0
7971 | 737.2963 | 3.0146 | 17.7732 | 92.9874 | 7.8621 | 4.7503 | 64.1842 | 6.3413 | 6.888 | 30.5743 | 70.3074 | 8.3385 | 175.3821 | 95.895 | 237.9695 | 9.731 | 53.2057 | 11.3622 | 110 | 31.4536 | 0 | 277.3227 | 0
7972 | 735.6334 | 3.0164 | 18.5033 | 92.7768 | 6.8673 | 5.6997 | 68.9472 | 8.0038 | 6.947 | 30.9615 | 70.0658 | 7.8781 | 175.0031 | 97.8456 | 236.2297 | 9.8237 | 52.8124 | 11.7022 | 111 | 30.1597 | 0 | 275.8037 | 0
7973 | 737.9488 | 3.5773 | 20.1509 | 94.0259 | 6.8647 | 5.7 | 64.5228 | 7.5885 | 6.9191 | 30.9442 | 71.6714 | 7.3799 | 176.9242 | 92.3962 | 233.3467 | 9.7111 | 53.8527 | 11.5395 | 106 | 29.3549 | 0 | 314.2922 | 0
7974 | 766.3337 | 4.7049 | 24.3142 | 93.7454 | 6.8627 | 5.7 | 79.7475 | 6.9033 | 7.8832 | 32.2251 | 73.6006 | 8.4145 | 186.0554 | 96.9558 | 238.582 | 9.6949 | 56.1985 | 11.8671 | 111 | 31.4868 | 0 | 335.3936 | 0
7975 | 814.8811 | 5.8669 | 44.0202 | 98.8102 | 2.8587 | 9.4989 | 99.0931 | 8.4843 | 10.0339 | 52.4448 | 100.8919 | 19.3902 | 220.1301 | 148.9732 | 297.9794 | 13.3439 | 54.147 | 15.6992 | 171 | 41.0771 | 0 | 395.4351 | 0
7976 | 879.708 | 6.8415 | 74.7752 | 107.4004 | -5.858 | 18.0476 | 108.8339 | 7.8903 | 13.167 | 101.4546 | 136.5952 | 36.8297 | 277.9811 | 220.7562 | 397.5356 | 27.9837 | 59.3899 | 17.9153 | 290 | 47.0246 | 0 | 464.8847 | 0
7977 | 990.1972 | 6.7134 | 87.8958 | 114.2615 | -5.9848 | 18.05 | 128.0204 | 9.7452 | 19.5525 | 116.1951 | 159.738 | 42.7253 | 340.8656 | 269.1483 | 488.1467 | 35.4249 | 70.7937 | 16.5514 | 328 | 59.3396 | 0 | 523.6573 | 0
7978 | 1082.0445 | 5.4323 | 91.2395 | 122.6886 | -8.1491 | 19.955 | 150.2329 | 13.3496 | 23.2286 | 116.2379 | 171.8632 | 42.7697 | 392.3665 | 312.4764 | 564.5434 | 40.1976 | 80.789 | 15.8391 | 339 | 65.7361 | 0 | 581.4932 | 0.15469
7979 | 1118.7552 | 4.9555 | 93.9284 | 128.8745 | -7.1367 | 18.9947 | 148.1058 | 12.3933 | 27.1895 | 109.9113 | 175.5727 | 43.9018 | 408.6453 | 329.7725 | 599.7798 | 40.9889 | 89.8711 | 16.172 | 334 | 69.7911 | 0 | 582.602 | 0.1675
7980 | 1162.7968 | 4.9136 | 99.5064 | 132.5238 | -8.1412 | 19.9497 | 149.9781 | 11.3517 | 24.8467 | 120.9366 | 176.1579 | 43.0866 | 422.0732 | 340.8996 | 598.0041 | 39.7868 | 95.1162 | 16.3522 | 333 | 79.1968 | 0 | 611.2904 | 0.1621
7981 | 1183.4311 | 5.0569 | 102.8642 | 132.1856 | -10.1353 | 21.8495 | 151.4948 | 12.1145 | 22.308 | 109.2312 | 179.2725 | 42.7836 | 425.5318 | 342.5845 | 597.0342 | 39.8611 | 111.9863 | 16.6278 | 377 | 69.5217 | 0 | 641.9211 | 0.095375
7982 | 1175.6164 | 5.0149 | 102.2192 | 133.325 | -8.1413 | 19.9505 | 154.7205 | 12.2139 | 25.9707 | 103.0187 | 181.8902 | 43.9217 | 438.9267 | 351.7483 | 596.3121 | 40.9277 | 113.2839 | 17.7355 | 310 | 73.0244 | 0 | 638.495 | 0.13916
7983 | 1174.8763 | 5.587 | 101.5532 | 139.4918 | -7.1443 | 19.0003 | 165.2569 | 10.3863 | 26.1825 | 100.9522 | 183.3554 | 43.6208 | 453.4715 | 358.6006 | 613.6007 | 41.2258 | 110.8847 | 18.7065 | 296 | 77.5994 | 0 | 617.105 | 0.048064
7984 | 1163.8551 | 6.7537 | 98.0557 | 140.4236 | -3.1442 | 15.2011 | 152.5754 | 8.6727 | 23.0357 | 102.8284 | 185.2111 | 43.913 | 436.8399 | 357.2639 | 629.6643 | 41.1866 | 107.1482 | 19.538 | 261 | 79.5182 | 0 | 588.4928 | 0
7985 | 1126.4043 | 7.1747 | 98.1724 | 134.5485 | -1.1434 | 13.3005 | 142.6312 | 8.9565 | 20.8418 | 106.2122 | 184.0794 | 43.4359 | 405.0604 | 337.8463 | 579.3773 | 34.9734 | 98.9776 | 19.2472 | 248 | 78.9724 | 0 | 548.7743 | 0
7986 | 1062.6839 | 7.1474 | 94.5246 | 121.6919 | 4.8591 | 7.6016 | 131.3962 | 8.818 | 14.9477 | 83.8597 | 165.1475 | 38.7175 | 358.5752 | 277.5462 | 482.7322 | 18.4273 | 84.1029 | 18.3343 | 235 | 67.4403 | 0 | 422.9873 | 0
7987 | 1002.6214 | 6.8953 | 90.6851 | 108.3348 | 5.8666 | 6.6503 | 117.4754 | 7.5862 | 10.8077 | 59.2984 | 126.7407 | 31.0441 | 316.7332 | 204.1549 | 414.8309 | 11.6811 | 77.3328 | 17.1001 | 231 | 58.9501 | 0 | 368.7901 | 0
7988 | 957.2113 | 6.1968 | 76.7827 | 103.9761 | 7.8667 | 4.7505 | 102.2444 | 5.9608 | 8.5795 | 51.885 | 107.9961 | 16.4251 | 281.3408 | 181.0176 | 370.6397 | 10.5774 | 68.4242 | 15.5468 | 197 | 52.3417 | 0 | 304.3704 | 0
7989 | 914.1134 | 5.3117 | 38.5532 | 100.3235 | 6.8647 | 5.6997 | 85.3487 | 5.5095 | 7.4152 | 48.0033 | 98.6477 | 10.2912 | 248.24 | 150.2354 | 330.0657 | 10.2727 | 61.4139 | 14.5703 | 198 | 44.7996 | 0 | 278.339 | 0
7990 | 885.4698 | 5.0969 | 26.074 | 96.453 | 6.8644 | 5.7 | 68.5284 | 5.7215 | 7.18 | 38.7104 | 91.8342 | 9.6827 | 226.041 | 120.6366 | 284.576 | 10.1641 | 58.4937 | 13.7804 | 177 | 40.4684 | 0 | 275.3779 | 0
7991 | 852.1113 | 4.5036 | 25.8037 | 94.0765 | 5.8669 | 6.6497 | 73.8911 | 5.754 | 6.7361 | 31.5442 | 79.8735 | 9.4352 | 212.1716 | 104.1159 | 257.9963 | 10.3131 | 58.0038 | 13.0084 | 157 | 39.857 | 0 | 270.697 | 0
7992 | 832.1726 | 3.2957 | 25.6681 | 92.8162 | 5.8701 | 6.65 | 88.6019 | 6.4032 | 6.7092 | 29.599 | 73.3547 | 9.0103 | 200.5219 | 97.3526 | 246.6398 | 10.1771 | 57.7058 | 12.6782 | 131 | 37.485 | 0 | 255.3537 | 0
7993 | 828.3759 | 2.8008 | 25.5703 | 92.3868 | 6.8626 | 5.7018 | 86.8484 | 7.179 | 6.5558 | 30.6149 | 71.4129 | 8.7037 | 195.2925 | 91.3871 | 242.7978 | 10.2434 | 57.525 | 12.3547 | 125 | 32.6681 | 0 | 253.2431 | 0
7994 | 823.4072 | 2.7978 | 25.6451 | 92.2629 | 6.8653 | 5.6984 | 70.9148 | 7.1019 | 6.6277 | 31.4209 | 72.9781 | 8.6637 | 196.0897 | 89.1326 | 230.2438 | 10.2383 | 57.6007 | 11.4978 | 121 | 29.7087 | 0 | 261.5202 | 0
7995 | 806.8118 | 2.7041 | 25.6622 | 93.1226 | 6.8673 | 5.7 | 72.5026 | 6.3992 | 6.7545 | 31.221 | 77.6252 | 8.6812 | 194.7738 | 88.6022 | 232.8576 | 10.059 | 57.6597 | 11.1904 | 111 | 29.1983 | 0 | 257.9801 | 0
7996 | 799.5171 | 2.7424 | 25.7291 | 93.252 | 6.865 | 5.7 | 69.2226 | 6.3108 | 6.3972 | 30.8099 | 79.465 | 8.3746 | 190.3398 | 87.2306 | 234.7065 | 10.2502 | 57.4971 | 11.379 | 114 | 29.4824 | 0 | 263.5188 | 0
7997 | 804.0946 | 3.083 | 25.7588 | 92.3929 | 6.8637 | 5.7 | 62.6451 | 7.8914 | 6.4238 | 31.2282 | 76.7782 | 8.2163 | 192.4903 | 84.7393 | 228.6218 | 10.0934 | 58.6821 | 11.3603 | 108 | 29.8608 | 0 | 291.5877 | 0
7998 | 824.2021 | 4.2607 | 34.1371 | 92.3854 | 6.864 | 5.7 | 76.0857 | 7.9177 | 7.0612 | 33.7126 | 73.727 | 11.4663 | 201.2706 | 92.5417 | 232.5034 | 9.9878 | 60.1286 | 11.2499 | 119 | 30.9218 | 0 | 332.064 | 0
7999 | 864.2226 | 5.9348 | 57.564 | 98.601 | -0.14095 | 12.3482 | 91.5221 | 6.9003 | 12.7272 | 54.2906 | 95.5117 | 18.4504 | 231.0867 | 161.3994 | 254.916 | 13.4183 | 57.8087 | 11.8625 | 180 | 41.5849 | 0 | 376.2638 | 0
8000 | 932.7143 | 6.9102 | 79.6364 | 102.9527 | -5.1432 | 17.0987 | 104.2294 | 7.3323 | 19.3752 | 100.824 | 132.5319 | 33.8806 | 296.4203 | 243.5163 | 344.4837 | 28.8599 | 62.7869 | 16.0533 | 279 | 49.4358 | 0 | 438.2164 | 0
8001 | 1046.0217 | 11.0155 | 93.5668 | 112.985 | -5.146 | 17.1 | 131.3884 | 9.9511 | 23.8356 | 112.8293 | 154.1863 | 40.5341 | 371.1658 | 291.8758 | 463.7487 | 36.3811 | 71.8404 | 18.2862 | 271 | 62.5572 | 0 | 510.9182 | 0
8002 | 1163.1886 | 15.2645 | 96.3125 | 127.6066 | -6.1498 | 18.0497 | 152.2063 | 9.4945 | 24.7918 | 106.924 | 171.7696 | 41.2353 | 414.8791 | 328.7861 | 552.6263 | 41.1599 | 80.8829 | 17.5294 | 349 | 67.1107 | 0 | 547.27 | 0.028698
8003 | 1218.8367 | 14.3912 | 98.9817 | 136.0892 | -6.145 | 18.05 | 148.4859 | 9.0102 | 23.6958 | 99.2097 | 187.3636 | 42.6861 | 423.8441 | 356.1815 | 589.8165 | 42.9343 | 87.655 | 17.2294 | 381 | 72.3794 | 0 | 554.7668 | 0.054522
8004 | 1209.7069 | 9.4556 | 105.2952 | 138.4457 | -7.1363 | 18.9997 | 153.2793 | 8.0246 | 23.2772 | 103.8367 | 191.3085 | 42.8036 | 431.6145 | 378.0718 | 602.8968 | 42.6889 | 89.3349 | 17.2039 | 364 | 76.1957 | 0 | 575.6409 | 0.076815
8005 | 1197.4403 | 7.4628 | 105.5931 | 135.489 | -8.1417 | 19.9497 | 158.738 | 9.4765 | 23.7387 | 102.8032 | 190.4192 | 41.2848 | 444.105 | 379.3953 | 593.4318 | 43.6292 | 88.8239 | 17.5412 | 337 | 77.4071 | 0 | 583.2552 | 0.043712
8006 | 1194.2971 | 8.8132 | 107.8089 | 141.2061 | -10.1441 | 21.8495 | 162.2461 | 10.3126 | 24.1063 | 110.6011 | 193.1885 | 41.3014 | 448.4076 | 375.935 | 588.1896 | 45.2208 | 91.1411 | 18.5069 | 306 | 77.4502 | 0 | 590.0888 | 0.019054
8007 | 1206.5295 | 10.4568 | 105.9644 | 145.5273 | -8.1439 | 19.9505 | 169.2618 | 9.1663 | 22.9043 | 111.9108 | 197.2663 | 43.4017 | 453.5076 | 380.6655 | 593.7568 | 44.6054 | 91.2997 | 18.5317 | 295 | 76.8335 | 0 | 597.1596 | 0.0075425
8008 | 1205.559 | 10.3204 | 104.5218 | 138.0861 | -1.1456 | 13.3018 | 161.4388 | 8.5909 | 20.4865 | 110.5165 | 196.7087 | 42.6116 | 449.4051 | 367.227 | 587.2384 | 43.0409 | 90.771 | 18.6605 | 291 | 75.3246 | 0 | 589.3087 | 0
8009 | 1156.556 | 8.1247 | 100.5278 | 135.0411 | 4.8542 | 7.6016 | 150.2654 | 9.0072 | 20.3033 | 105.2417 | 196.2955 | 41.6133 | 437.5996 | 340.0319 | 537.9418 | 35.0434 | 88.9056 | 18.4825 | 248 | 71.6391 | 0 | 529.8781 | 0
8010 | 1066.7741 | 6.9243 | 95.5583 | 124.4487 | 5.8586 | 6.6503 | 137.0384 | 6.7316 | 20.745 | 88.8468 | 175.5756 | 37.5735 | 399.4031 | 280.0679 | 442.0677 | 19.4405 | 80.2483 | 17.9483 | 214 | 65.7188 | 0 | 416.8948 | 0
8011 | 1009.9884 | 6.3391 | 90.7758 | 111.5698 | 6.8621 | 5.7003 | 127.6539 | 4.9767 | 20.4072 | 66.4639 | 127.0753 | 30.5739 | 338.1744 | 210.0931 | 385.0359 | 12.0138 | 70.9326 | 17.1946 | 193 | 60.7872 | 0 | 363.5219 | 0
8012 | 967.6582 | 5.4776 | 79.4309 | 104.8301 | 7.8633 | 4.7503 | 112.8348 | 5.061 | 18.8712 | 56.2337 | 102.3583 | 19.6096 | 298.6785 | 169.3109 | 346.565 | 10.4198 | 60.9783 | 15.8273 | 177 | 53.7233 | 0 | 315.9215 | 0
8013 | 924.693 | 4.977 | 44.1906 | 98.5402 | 6.8649 | 5.6997 | 99.2661 | 5.4277 | 12.7973 | 51.2303 | 96.2103 | 15.0019 | 277.3371 | 149.8796 | 308.7469 | 10.0223 | 56.0121 | 14.94 | 169 | 47.1508 | 0 | 283.5126 | 0
8014 | 879.6969 | 4.774 | 28.2778 | 96.3911 | 7.8651 | 4.7503 | 87.6412 | 5.5346 | 8.9975 | 40.6276 | 89.9991 | 13.5526 | 241.9876 | 135.9367 | 276.2599 | 9.9979 | 55.6698 | 14.1104 | 158 | 41.5097 | 0 | 279.2923 | 0
8015 | 850.2822 | 4.4051 | 26.1676 | 94.6297 | 7.8687 | 4.75 | 82.9919 | 5.4078 | 7.6218 | 30.9576 | 76.9571 | 12.1163 | 217.9203 | 129.5525 | 254.2903 | 9.9303 | 54.7458 | 13.2484 | 131 | 38.2459 | 0 | 273.7734 | 0
8016 | 819.0786 | 3.3642 | 25.8959 | 93.9939 | 6.8692 | 5.6997 | 82.6165 | 5.3034 | 6.8212 | 29.5859 | 70.2561 | 8.8932 | 200.4752 | 129.8703 | 238.5563 | 10.0309 | 53.4635 | 12.8359 | 121 | 35.7672 | 0 | 274.0982 | 0
8017 | 809.5648 | 2.827 | 25.8708 | 94.2133 | 7.8628 | 4.7503 | 81.8621 | 4.7065 | 6.5555 | 30.4006 | 68.6369 | 7.9717 | 191.8001 | 139.7298 | 232.7197 | 9.8313 | 53.26 | 12.3198 | 110 | 35.0697 | 0 | 269.7189 | 0
8018 | 810.2774 | 2.7893 | 25.8743 | 93.0572 | 6.8645 | 5.6997 | 81.8585 | 4.748 | 6.8167 | 28.6415 | 68.0503 | 7.8728 | 191.4627 | 127.7506 | 234.6838 | 9.899 | 53.4156 | 11.8228 | 109 | 34.2433 | 0 | 270.3619 | 0
8019 | 800.9095 | 3.1237 | 25.8681 | 92.4027 | 4.8653 | 7.5995 | 81.2591 | 4.7635 | 6.6218 | 27.5217 | 68.0468 | 7.9529 | 190.8911 | 127.4734 | 244.8973 | 9.744 | 53.2408 | 12.5022 | 105 | 34.8397 | 0 | 268.0227 | 0
8020 | 806.9491 | 2.9699 | 25.8247 | 92.8705 | 7.8611 | 4.7508 | 80.6168 | 5.1518 | 6.7365 | 26.932 | 67.6559 | 7.659 | 190.3636 | 129.6148 | 244.4806 | 10.1923 | 52.8243 | 12.9523 | 103 | 32.5515 | 0 | 270.9161 | 0
8021 | 805.79 | 3.1196 | 25.8308 | 92.4176 | 7.8685 | 4.75 | 81.5692 | 5.6464 | 6.6938 | 27.0147 | 67.7261 | 7.5075 | 192.6484 | 127.676 | 229.6271 | 10.5664 | 54.2781 | 12.6316 | 103 | 31.8601 | 0 | 285.3007 | 0
8022 | 813.5417 | 4.5691 | 35.1836 | 93.561 | 6.8627 | 5.6997 | 86.4308 | 5.673 | 7.6194 | 31.452 | 70.683 | 9.0802 | 201.3746 | 128.2527 | 228.9886 | 10.7365 | 57.0152 | 12.4622 | 116 | 32.6304 | 0 | 328.7293 | 0
8023 | 872.0342 | 5.8185 | 58.4827 | 100.5665 | 0.85682 | 11.3984 | 99.0337 | 5.9501 | 11.7416 | 52.7026 | 94.103 | 20.5864 | 232.7227 | 174.3041 | 254.3968 | 14.36 | 54.3463 | 13.6131 | 163 | 41.0209 | 0 | 392.3877 | 0
8024 | 939.7906 | 6.6645 | 82.832 | 103.4032 | -5.1417 | 17.0984 | 119.4732 | 6.2949 | 14.7771 | 97.1625 | 135.9707 | 36.5148 | 287.1288 | 246.6533 | 348.1166 | 29.8424 | 56.953 | 15.9046 | 287 | 46.3748 | 0 | 429.1529 | 0
8025 | 1045.0159 | 9.8299 | 93.5838 | 114.7865 | -5.1403 | 17.1 | 135.8519 | 6.2243 | 20.1006 | 113.7492 | 158.841 | 40.8306 | 351.5462 | 298.9871 | 465.8808 | 37.6976 | 69.8829 | 16.1034 | 300 | 63.601 | 0 | 500.4158 | 0
8026 | 1111.2038 | 11.864 | 98.3864 | 128.2367 | -6.1375 | 18.0497 | 155.0744 | 7.4263 | 23.7053 | 112.6805 | 178.8629 | 41.5312 | 405.7362 | 330.395 | 537.6506 | 40.461 | 84.0006 | 16.2945 | 358 | 71.9942 | 0 | 550.1366 | 0.033453
8027 | 1157.9107 | 10.9567 | 99.4278 | 133.1945 | -8.142 | 19.9495 | 160.0308 | 9.3336 | 26.8238 | 117.151 | 180.8941 | 43.1349 | 427.4177 | 360.4123 | 587.4917 | 42.5921 | 90.0897 | 17.2318 | 334 | 78.2474 | 0 | 591.5294 | 0.070697
8028 | 1182.05 | 6.6169 | 105.0634 | 133.6259 | -6.1455 | 18.0505 | 159.8473 | 10.0065 | 23.8781 | 112.396 | 177.8932 | 42.9447 | 455.793 | 384.356 | 593.6681 | 42.5898 | 105.7281 | 17.8899 | 310 | 88.2287 | 0 | 588.7026 | 0.098295
8029 | 1167.425 | 4.8517 | 106.4895 | 132.4861 | -7.1408 | 18.9997 | 165.5883 | 9.9825 | 19.8605 | 106.0368 | 179.5683 | 42.0586 | 457.5195 | 380.5423 | 568.3556 | 41.6809 | 117.789 | 18.009 | 358 | 77.1452 | 0 | 572.2652 | 0.08595
8030 | 1176.6571 | 6.3649 | 105.2028 | 138.9254 | -10.1431 | 21.8492 | 175.348 | 8.5577 | 22.1814 | 107.2759 | 184.927 | 42.461 | 460.63 | 390.0969 | 573.6934 | 43.8307 | 118.922 | 17.7998 | 266 | 81.8511 | 0 | 576.6407 | 0.039731
8031 | 1196.8613 | 6.3141 | 107.78 | 136.3178 | -5.1459 | 17.1013 | 178.529 | 7.3199 | 22.6186 | 105.3453 | 182.7315 | 41.6006 | 468.1022 | 382.9937 | 582.578 | 44.0738 | 113.0018 | 18.0531 | 257 | 84.9136 | 0 | 593.7177 | 0.038776
8032 | 1178.2388 | 6.9655 | 97.8493 | 133.657 | -2.1444 | 14.2508 | 172.4018 | 6.8415 | 20.2075 | 104.7638 | 178.1602 | 39.5396 | 458.9166 | 376.88 | 589.4576 | 40.3838 | 112.6222 | 18.3862 | 254 | 86.284 | 0 | 574.5819 | 0
8033 | 1138.2614 | 7.2097 | 96.6069 | 134.3316 | -3.1389 | 15.1997 | 162.9458 | 7.1246 | 16.636 | 111.8459 | 179.8578 | 39.3546 | 427.1838 | 347.2088 | 569.443 | 33.6078 | 94.4827 | 18.5197 | 248 | 83.1801 | 0 | 511.2813 | 0
8034 | 1068.3462 | 6.9902 | 98.5341 | 120.828 | 5.8553 | 6.6524 | 147.1597 | 7.5975 | 18.15 | 98.7014 | 160.2101 | 34.9058 | 379.159 | 265.8691 | 477.9408 | 18.2276 | 78.6513 | 18.7077 | 219 | 74.6378 | 0 | 417.3 | 0
8035 | 996.025 | 6.0301 | 94.9928 | 109.3491 | 6.861 | 5.7003 | 134.2867 | 7.6769 | 17.119 | 77.323 | 119.8394 | 27.5059 | 331.3781 | 208.2702 | 402.0692 | 12.6472 | 70.359 | 17.2415 | 203 | 66.4551 | 0 | 366.488 | 0
8036 | 957.4079 | 5.9145 | 82.3985 | 104.6006 | 6.8629 | 5.7 | 121.9063 | 6.9237 | 11.8545 | 64.4199 | 98.6644 | 16.2884 | 301.343 | 180.0606 | 340.3007 | 11.7207 | 65.9859 | 15.4992 | 177 | 55.2695 | 0 | 312.5906 | 0
8037 | 912.3652 | 5.328 | 59.7035 | 98.3897 | 7.8594 | 4.7503 | 99.7671 | 6.3328 | 8.0138 | 60.4331 | 93.0049 | 9.3831 | 280.0503 | 151.808 | 299.3584 | 11.2745 | 59.4884 | 14.5068 | 162 | 48.4887 | 0 | 289.7666 | 0
8038 | 882.247 | 4.8624 | 51.5109 | 95.3688 | 6.8579 | 5.6997 | 95.2485 | 5.2968 | 7.6012 | 49.6228 | 87.1017 | 7.9692 | 260.5923 | 131.5393 | 270.874 | 11.1047 | 55.836 | 13.6772 | 147 | 44.7765 | 0 | 278.8168 | 0
8039 | 851.2959 | 4.2384 | 47.985 | 93.112 | 6.8617 | 5.7 | 84.7473 | 5.1228 | 7.0018 | 36.8641 | 74.9362 | 7.5823 | 249.6907 | 112.9629 | 254.1038 | 10.8773 | 54.8701 | 13.0779 | 137 | 40.7787 | 0 | 269.0658 | 0
8040 | 825.2595 | 3.4188 | 44.2546 | 92.5836 | 5.8643 | 6.6497 | 72.4052 | 5.2641 | 6.7817 | 36.6737 | 68.837 | 7.4133 | 231.6168 | 97.0058 | 234.1481 | 11.0526 | 54.7696 | 12.8635 | 115 | 35.8526 | 0 | 267.5348 | 0
8041 | 816.4156 | 3.3018 | 43.258 | 92.4512 | 57.9905 | 5.7003 | 75.6901 | 6.0133 | 6.4302 | 37.5958 | 67.4706 | 7.3821 | 214.5379 | 88.9974 | 227.8734 | 10.8785 | 54.872 | 12.7794 | 108 | 35.1658 | 0 | 270.6761 | 0
8042 | 821.3559 | 3.1013 | 43.5923 | 92.3642 | 57.9903 | 5.7 | 72.4082 | 6.406 | 6.178 | 37.4085 | 69.8477 | 7.2613 | 204.9145 | 86.2878 | 232.908 | 10.8887 | 55.017 | 12.2541 | 104 | 33.8491 | 0 | 269.5194 | 0
8043 | 813.0684 | 3.2974 | 43.9013 | 92.2092 | 58.99 | 4.7503 | 66.1604 | 6.6179 | 6.2406 | 37.3191 | 71.582 | 7.5879 | 200.2909 | 84.7417 | 236.1111 | 10.8816 | 55.031 | 11.4207 | 104 | 32.9851 | 0 | 273.531 | 0
8044 | 799.635 | 2.906 | 43.882 | 93.2763 | 57.9935 | 5.7013 | 74.7637 | 5.6151 | 6.1653 | 37.1642 | 71.0607 | 8.0551 | 197.5916 | 84.3578 | 233.3084 | 10.8637 | 55.0354 | 11.0941 | 101 | 31.2173 | 0 | 273.0562 | 0
8045 | 802.8825 | 3.1513 | 43.9405 | 92.5266 | 58.9925 | 4.7487 | 76.1069 | 5.1458 | 6.1684 | 37.417 | 71.1481 | 7.4107 | 201.0469 | 94.4866 | 225.675 | 10.8461 | 56.4987 | 11.0855 | 101 | 30.3235 | 0 | 291.0707 | 0
8046 | 821.7953 | 4.2331 | 44.9346 | 92.5677 | 57.9894 | 5.6997 | 72.7543 | 5.1591 | 6.477 | 35.1821 | 73.8172 | 12.0696 | 211.2059 | 105.4679 | 233.578 | 10.8263 | 58.4931 | 11.1959 | 113 | 32.3544 | 0 | 341.9396 | 0
8047 | 863.7247 | 5.6873 | 59.0454 | 101.3819 | 56.9888 | 6.6497 | 94.6381 | 5.9206 | 10.9645 | 49.2885 | 93.5897 | 20.2511 | 242.7757 | 161.1793 | 259.0106 | 13.52 | 55.8744 | 11.976 | 173 | 41.014 | 0 | 383.8043 | 0
8048 | 919.9816 | 6.9503 | 75.122 | 105.6087 | 48.985 | 14.2479 | 120.3078 | 6.4522 | 16.0655 | 87.185 | 129.5642 | 34.41 | 310.7185 | 242.0648 | 339.3219 | 28.7169 | 61.2686 | 12.1617 | 283 | 49.122 | 0 | 432.9819 | 0
8049 | 1012.2934 | 10.1947 | 89.2665 | 116.7676 | 49.9874 | 13.3003 | 133.2331 | 6.7934 | 21.9867 | 93.0674 | 154.5568 | 42.7749 | 384.3792 | 298.1081 | 462.8923 | 36.1393 | 73.1993 | 16.029 | 352 | 64.053 | 0 | 527.0527 | 0
8050 | 1122.2977 | 20.1328 | 98.1186 | 130.3341 | 48.9907 | 14.2497 | 148.9272 | 7.0507 | 24.8607 | 102.4044 | 179.4129 | 43.0762 | 432.0324 | 336.5134 | 553.4884 | 40.6306 | 83.2862 | 16.5224 | 332 | 69.8936 | 0 | 570.1449 | 0.01635
8051 | 1188.6834 | 20.6317 | 101.6813 | 134.2008 | 47.9863 | 15.1997 | 156.2855 | 6.5525 | 25.1367 | 107.7886 | 202.1497 | 42.6254 | 451.3812 | 354.3573 | 609.0115 | 42.8318 | 107.6528 | 16.7595 | 385 | 71.157 | 0 | 581.0615 | 0.04369
8052 | 1168.2424 | 14.5449 | 106.6642 | 137.0577 | 48.9859 | 14.2503 | 159.2659 | 7.3236 | 23.231 | 105.9189 | 204.2649 | 41.1609 | 463.9472 | 366.5776 | 618.28 | 42.8306 | 118.6929 | 17.2125 | 374 | 81.0013 | 0 | 585.2862 | 0.064519
8053 | 1147.3176 | 9.7441 | 103.3623 | 133.565 | 50.9876 | 12.3505 | 157.6978 | 7.7083 | 20.0275 | 105.5692 | 192.9083 | 39.7402 | 453.3017 | 373.6437 | 605.6314 | 42.0998 | 118.0038 | 17.1556 | 368 | 70.7325 | 0 | 565.9463 | 0.03811
8054 | 1170.2706 | 8.1574 | 101.214 | 137.9581 | 47.9884 | 15.1992 | 159.6439 | 8.1358 | 22.1675 | 104.2985 | 190.2897 | 40.6283 | 464.3705 | 380.1445 | 578.8453 | 42.6034 | 121.3683 | 17.9623 | 338 | 82.8392 | 0 | 587.4173 | 0.019539
8055 | 1182.5872 | 8.2761 | 107.8736 | 142.723 | 48.9856 | 14.2503 | 161.3251 | 8.0456 | 22.2175 | 116.8417 | 190.9761 | 39.3208 | 465.0501 | 377.2806 | 569.1692 | 41.6765 | 106.0147 | 18.0484 | 283 | 85.4175 | 0 | 582.8711 | 0.0049401
8056 | 1164.04 | 8.3682 | 110.1344 | 143.9774 | 49.9852 | 13.3003 | 159.1662 | 6.7213 | 17.7295 | 107.8016 | 189.6713 | 40.3627 | 455.4487 | 369.0381 | 589.5601 | 40.8752 | 93.0646 | 18.2579 | 261 | 81.7582 | 0 | 556.5679 | 0
8057 | 1146.645 | 7.5533 | 106.4529 | 140.086 | 50.9884 | 12.3503 | 149.1935 | 6.0454 | 15.5308 | 95.9236 | 187.8851 | 41.5692 | 443.9107 | 344.1685 | 552.1475 | 34.0948 | 87.2094 | 18.4597 | 246 | 74.1444 | 0 | 509.7145 | 0
8058 | 1072.369 | 7.2444 | 99.3638 | 124.9843 | 56.9864 | 6.6516 | 133.9949 | 5.7124 | 11.4845 | 83.7483 | 168.6135 | 38.8556 | 401.5523 | 269.7705 | 439.4235 | 17.5448 | 77.4231 | 17.4344 | 235 | 62.1808 | 0 | 399.5004 | 0
8059 | 1002.7003 | 6.6834 | 93.9472 | 109.1626 | 56.9874 | 6.65 | 119.9732 | 5.5501 | 10.8185 | 64.0655 | 129.0705 | 34.2401 | 348.6659 | 196.0553 | 363.4411 | 11.3412 | 68.5669 | 15.997 | 207 | 56.0469 | 0 | 353.163 | 0
8060 | 949.3974 | 5.9828 | 81.8092 | 104.7952 | 57.991 | 5.7003 | 109.4089 | 5.664 | 9.0143 | 55.1431 | 105.3096 | 20.5142 | 299.1404 | 162.3178 | 328.0263 | 11.4257 | 61.0728 | 14.6374 | 182 | 52.472 | 0 | 294.895 | 0
8061 | 932.9611 | 4.9831 | 49.5602 | 99.2066 | 56.9958 | 6.6497 | 102.2386 | 5.8787 | 7.0305 | 50.7844 | 96.9354 | 13.1143 | 261.6573 | 154.4446 | 313.8795 | 11.5065 | 59.1991 | 13.5343 | 160 | 45.9945 | 0 | 278.0696 | 0
8062 | 901.4176 | 5.1698 | 38.2608 | 95.8322 | 58.9966 | 4.7505 | 95.558 | 5.7191 | 6.8452 | 41.9523 | 90.4338 | 13.252 | 227.9966 | 140.6792 | 284.0784 | 11.6051 | 56.2766 | 12.9427 | 158 | 44.6501 | 0 | 269.4344 | 0
8063 | 876.2725 | 4.9022 | 37.5719 | 92.8431 | 57.9909 | 5.6997 | 79.9298 | 5.3137 | 6.4483 | 34.0129 | 77.18 | 12.9931 | 206.8807 | 126.6031 | 263.4797 | 11.3812 | 54.3941 | 12.5848 | 132 | 40.3948 | 0 | 262.2943 | 0
8064 | 859.7505 | 8.5899 | 37.6288 | 92.1568 | 57.992 | 5.7 | 71.2583 | 5.4242 | 6.3073 | 30.9032 | 72.4017 | 9.8575 | 199.0159 | 111.1109 | 238.887 | 11.2846 | 54.176 | 12.4802 | 125 | 35.0713 | 0 | 249.0374 | 0
8065 | 866.6432 | 10.3696 | 35.1933 | 92.2958 | 83.5567 | 5.7 | 73.0137 | 6.244 | 6.2153 | 28.1937 | 71.9838 | 8.6618 | 197.9606 | 97.0918 | 228.4852 | 11.3776 | 54.1379 | 12.4792 | 117 | 32.5724 | 0 | 254.7918 | 0
8066 | 861.2842 | 6.7228 | 31.9539 | 92.2417 | 84.5523 | 4.7503 | 67.2733 | 7.0439 | 6.0123 | 26.8741 | 70.0883 | 8.4359 | 197.5413 | 89.1026 | 233.8286 | 11.2819 | 54.0627 | 12.3656 | 113 | 34.0587 | 0 | 258.9685 | 0
8067 | 839.3971 | 3.6274 | 31.6953 | 92.1836 | 82.5524 | 6.6495 | 60.352 | 7.1595 | 5.95 | 26.3768 | 70.3843 | 8.8326 | 197.029 | 89.9569 | 240.8814 | 11.3292 | 54.101 | 11.5024 | 103 | 33.0799 | 0 | 261.6785 | 0
8068 | 826.7923 | 2.9233 | 31.1201 | 93.7216 | 81.5596 | 7.5997 | 67.5499 | 6.1624 | 5.9142 | 26.3768 | 71.5358 | 8.5633 | 197.0908 | 92.2889 | 240.1956 | 11.1762 | 54.1797 | 11.1608 | 105 | 34.3721 | 0 | 250.7156 | 0
8069 | 825.4277 | 3.2833 | 29.9553 | 94.2654 | 84.5535 | 4.7508 | 66.2091 | 5.9469 | 5.9072 | 27.0511 | 72.762 | 8.3487 | 198.5947 | 91.6794 | 226.8516 | 11.0039 | 55.4716 | 11.1834 | 104 | 30.889 | 0 | 280.6246 | 0
8070 | 837.8244 | 4.0985 | 31.3799 | 96.8348 | 83.5528 | 5.6997 | 64.3471 | 6.8651 | 6.555 | 28.0564 | 75.6054 | 9.4697 | 207.1031 | 96.7947 | 227.7239 | 11.2655 | 57.6025 | 11.21 | 105 | 30.7947 | 0 | 326.3294 | 0
8071 | 886.3824 | 5.4937 | 53.9005 | 103.3991 | 81.5537 | 7.5995 | 85.7967 | 8.0859 | 10.6442 | 48.7079 | 95.4561 | 18.7125 | 249.4024 | 151.5532 | 258.6081 | 14.5341 | 55.1445 | 11.3148 | 173 | 39.3825 | 0 | 379.6331 | 0
8072 | 945.6346 | 6.7077 | 82.5963 | 104.7012 | 77.5502 | 11.3989 | 112.3425 | 7.6841 | 14.5823 | 103.161 | 134.2657 | 35.5021 | 298.3576 | 242.9643 | 380.4707 | 29.2503 | 60.1364 | 14.0349 | 264 | 48.0802 | 0 | 430.9903 | 0
8073 | 1009.0669 | 8.6574 | 94.6719 | 111.5548 | 75.5495 | 13.2995 | 128.2303 | 7.2871 | 17.9163 | 119.8011 | 164.7299 | 42.0973 | 358.1074 | 297.2589 | 500.5551 | 36.2154 | 69.1306 | 18.0715 | 322 | 60.9812 | 0 | 517.3858 | 0
8074 | 1083.7091 | 7.4831 | 101.7754 | 126.2174 | 76.5476 | 12.3503 | 149.8926 | 8.2743 | 22.5635 | 114.0345 | 176.1679 | 40.473 | 417.7498 | 326.1245 | 568.3134 | 39.3725 | 79.6396 | 17.5165 | 393 | 69.2902 | 0 | 557.7632 | 0.14435
8075 | 1169.199 | 5.0802 | 99.0248 | 131.2313 | 73.5521 | 15.1992 | 160.8804 | 8.9508 | 25.0036 | 107.2441 | 171.7034 | 43.0813 | 433.7325 | 344.0609 | 593.6851 | 40.4405 | 92.4905 | 17.8593 | 394 | 71.0452 | 0 | 589.6518 | 0.16287
8076 | 1198.2539 | 4.8226 | 98.2898 | 134.8831 | 76.5515 | 12.3508 | 157.134 | 9.0675 | 23.4982 | 111.7135 | 170.4998 | 45.0203 | 430.8532 | 365.2085 | 587.8992 | 39.5122 | 95.4843 | 18.9247 | 362 | 76.1568 | 0 | 589.2888 | 0.19518
8077 | 1158.1389 | 5.0318 | 102.5161 | 131.4764 | 75.552 | 13.2997 | 152.6103 | 8.3087 | 15.1948 | 103.1562 | 177.2186 | 43.8901 | 411.453 | 366.575 | 567.5655 | 39.3325 | 90.9397 | 18.6224 | 390 | 71.4577 | 0 | 576.0035 | 0.21522
8078 | 1171.9003 | 4.7321 | 103.9585 | 137.4309 | 77.5496 | 11.4005 | 157.6338 | 7.764 | 17.5033 | 94.7115 | 182.961 | 43.1061 | 415.179 | 378.9672 | 571.7341 | 40.5443 | 88.4921 | 17.9172 | 313 | 71.2082 | 0 | 598.8139 | 0.17978
8079 | 1198.4587 | 5.4854 | 105.6327 | 142.2771 | 72.5498 | 16.1487 | 161.1807 | 7.1746 | 17.9087 | 84.879 | 185.4052 | 39.5351 | 431.1644 | 375.9821 | 582.9435 | 40.0519 | 84.9122 | 18.7895 | 274 | 75.8957 | 0 | 592.479 | 0.094621
8080 | 1163.1008 | 6.7434 | 99.2006 | 140.3685 | 64.556 | 23.7479 | 153.9369 | 7.2196 | 13.5205 | 89.0098 | 185.5635 | 39.8913 | 422.7351 | 358.059 | 570.9276 | 39.1425 | 83.4708 | 18.9053 | 271 | 70.9332 | 0 | 568.79 | 0
8081 | 1108.4057 | 6.8384 | 96.1232 | 134.8828 | 81.546 | 7.6045 | 142.7677 | 7.4917 | 11.3692 | 96.7936 | 183.0565 | 40.3362 | 397.4149 | 329.3699 | 510.9727 | 25.8049 | 78.5167 | 18.747 | 245 | 64.1681 | 0 | 508.9956 | 0
8082 | 1036.3021 | 6.7262 | 79.4542 | 122.1058 | 83.5523 | 5.7005 | 130.033 | 7.9541 | 10.2185 | 89.5292 | 161.494 | 39.0138 | 344.4223 | 249.2885 | 425.5018 | 15.3022 | 70.8096 | 17.2867 | 254 | 55.6744 | 0 | 399.451 | 0
8083 | 1002.3687 | 5.9661 | 41.9423 | 106.4597 | 83.5598 | 5.7 | 107.6925 | 7.0626 | 8.5585 | 65.3573 | 119.4551 | 30.2716 | 289.8061 | 175.3812 | 367.019 | 12.1189 | 64.0288 | 16.0812 | 215 | 50.2773 | 0 | 353.6007 | 0
8084 | 953.1047 | 5.6777 | 23.7918 | 98.6399 | 83.5594 | 5.7 | 96.2815 | 6.3066 | 7.5455 | 52.8407 | 94.1693 | 15.6234 | 254.6408 | 144.1009 | 326.7519 | 11.4726 | 56.6268 | 15.3426 | 193 | 44.3939 | 0 | 308.7738 | 0
8085 | 893.8681 | 5.1472 | 20.4357 | 96.0429 | 83.5526 | 5.7 | 89.7237 | 6.3322 | 7.0733 | 45.454 | 87.385 | 12.0281 | 236.9645 | 131.3748 | 295.8466 | 11.4749 | 53.7718 | 14.4986 | 181 | 39.7601 | 0 | 289.7711 | 0
8086 | 871.1648 | 5.0039 | 20.0437 | 95.3653 | 84.556 | 4.7503 | 69.1243 | 8.6901 | 7.0438 | 35.2842 | 96.0207 | 10.0639 | 218.4989 | 128.8378 | 271.0648 | 11.4275 | 51.7652 | 13.3917 | 171 | 37.475 | 0 | 286.7894 | 0
8087 | 862.5826 | 4.3436 | 19.9951 | 93.2701 | 82.5537 | 6.6495 | 67.7976 | 7.4729 | 6.5563 | 32.6126 | 85.1869 | 8.2629 | 205.1259 | 117.4823 | 262.7637 | 11.4032 | 50.7291 | 12.8806 | 155 | 37.8194 | 0 | 290.9103 | 0
8088 | 843.5736 | 3.3475 | 20.1124 | 92.726 | 83.5531 | 5.7003 | 72.2901 | 6.9114 | 6.6008 | 34.7463 | 69.8157 | 7.6119 | 200.2226 | 104.2036 | 257.151 | 11.208 | 50.5557 | 12.8253 | 148 | 36.9434 | 0 | 317.4545 | 0
8089 | 841.0067 | 3.2018 | 20.118 | 92.9347 | 83.5563 | 5.7 | 63.9503 | 8.7334 | 6.6857 | 32.6027 | 66.2634 | 7.4479 | 204.9018 | 103.2861 | 254.8444 | 11.1282 | 49.7549 | 12.2321 | 147 | 32.898 | 0 | 320.6862 | 0
8090 | 842.2569 | 3.112 | 20.0974 | 93.2327 | 83.5571 | 5.7 | 64.939 | 7.4478 | 6.3575 | 31.6968 | 65.7335 | 7.8095 | 210.1525 | 108.2685 | 255.6311 | 11.3095 | 49.3753 | 11.7491 | 149 | 31.302 | 0 | 301.0582 | 0
8091 | 828.8875 | 2.9093 | 19.8453 | 93.0822 | 83.5577 | 5.7 | 70.7318 | 8.2584 | 6.574 | 31.6342 | 65.9682 | 7.646 | 204.5518 | 108.708 | 256.2356 | 11.1717 | 49.1429 | 11.6089 | 137 | 28.6447 | 0 | 297.7868 | 0
8092 | 818.4681 | 2.8384 | 19.807 | 92.8094 | 84.5589 | 4.7503 | 64.5358 | 8.4841 | 6.3732 | 30.7436 | 67.1005 | 8.3632 | 198.3195 | 93.4637 | 244.2334 | 11.2684 | 49.185 | 11.5994 | 130 | 27.6501 | 0 | 302.2108 | 0
8093 | 817.0768 | 3.242 | 19.9095 | 92.8513 | 80.5559 | 8.5489 | 64.9314 | 7.2736 | 6.3332 | 31.3379 | 66.7196 | 7.6499 | 193.6233 | 88.039 | 229.4899 | 11.1449 | 50.4698 | 11.5778 | 123 | 26.8481 | 0 | 292.5278 | 0
8094 | 816.5327 | 4.3457 | 21.0972 | 92.5767 | 84.5523 | 4.7524 | 70.9463 | 9.1445 | 6.4058 | 31.1272 | 66.2769 | 6.9964 | 188.4277 | 87.5517 | 223.4639 | 11.0083 | 52.4928 | 11.6086 | 118 | 27.171 | 0 | 295.3853 | 0
8095 | 822.5155 | 4.5556 | 38.3878 | 92.7449 | 83.5559 | 5.6984 | 65.752 | 7.7858 | 6.7323 | 31.7967 | 67.0461 | 7.3072 | 189.0575 | 88.2218 | 223.0319 | 11.2326 | 49.9094 | 11.6049 | 123 | 30.3924 | 0 | 296.1158 | 0
8096 | 839.7299 | 4.4505 | 46.839 | 92.65 | 82.5521 | 6.6497 | 69.4049 | 9.1928 | 6.9259 | 31.7449 | 75.1304 | 9.0277 | 199.5364 | 91.1525 | 225.0579 | 15.7205 | 48.8944 | 11.836 | 121 | 36.9775 | 0 | 304.5666 | 0
8097 | 850.1112 | 4.0854 | 54.3048 | 90.5618 | 83.5553 | 5.7003 | 81.7963 | 7.9384 | 6.6038 | 39.5771 | 104.3633 | 13.3888 | 207.5348 | 91.0958 | 224.0516 | 28.9389 | 48.3779 | 12.7561 | 116 | 41.7069 | 0 | 303.3067 | 0
8098 | 860.1274 | 3.1864 | 67.1144 | 89.8307 | 82.5537 | 6.6516 | 83.5027 | 8.8266 | 7.2729 | 60.4151 | 130.415 | 14.5838 | 212.8682 | 97.1676 | 221.2871 | 31.638 | 47.4954 | 13.1231 | 137 | 42.2796 | 0 | 293.1761 | 0.072475
8099 | 881.3314 | 2.9779 | 77.6534 | 89.9644 | 83.5564 | 5.6984 | 94.3663 | 8.3716 | 7.5722 | 73.114 | 133.2967 | 14.689 | 226.3773 | 105.8992 | 226.6869 | 30.5306 | 47.6738 | 12.9815 | 173 | 42.0967 | 0 | 306.4707 | 0.049517
8100 | 894.1256 | 3.2781 | 78.1338 | 91.3414 | 83.5544 | 5.7 | 101.822 | 7.498 | 6.9176 | 75.0157 | 105.1639 | 14.7689 | 238.3094 | 110.572 | 238.2658 | 30.3258 | 48.8588 | 13.213 | 187 | 44.4002 | 0 | 313.8906 | 0.043009
8101 | 891.1057 | 4.0223 | 77.0335 | 91.8443 | 84.5537 | 4.7503 | 98.5356 | 6.4396 | 6.0928 | 70.5677 | 89.7602 | 14.9248 | 245.8588 | 115.6155 | 261.1682 | 30.2777 | 51.0387 | 14.2443 | 197 | 48.9133 | 0 | 312.2043 | 0.039088
8102 | 900.9185 | 4.5169 | 73.2108 | 92.1575 | 83.5578 | 5.6997 | 100.1456 | 5.9899 | 5.8477 | 68.9226 | 88.7929 | 14.782 | 247.3299 | 125.0413 | 278.8212 | 30.2818 | 52.564 | 14.6874 | 198 | 51.7123 | 0 | 324.7911 | 0.024623
8103 | 896.8011 | 5.2652 | 36.3426 | 91.5727 | 83.5547 | 5.7 | 96.9902 | 6.1291 | 5.8894 | 74.5943 | 90.6337 | 15.4496 | 242.6221 | 137.6635 | 258.6824 | 30.3626 | 52.7055 | 14.7419 | 199 | 49.7469 | 0 | 327.7167 | 0.0050299
8104 | 891.9566 | 6.06 | 20.7802 | 92.8911 | 84.5522 | 4.7503 | 83.1136 | 6.1855 | 6.1823 | 66.9607 | 93.4061 | 17.1124 | 243.8309 | 155.2862 | 259.448 | 26.8027 | 54.0955 | 14.9984 | 226 | 46.5788 | 0 | 313.5918 | 0
8105 | 879.288 | 5.9962 | 19.2955 | 93.7519 | 83.5497 | 5.6997 | 80.1888 | 5.5825 | 7.3722 | 50.7752 | 108.3876 | 12.9593 | 248.5659 | 154.7744 | 285.478 | 15.2762 | 52.7343 | 15.2795 | 223 | 46.2697 | 0 | 310.1539 | 0
8106 | 875.2848 | 5.5854 | 19.2019 | 93.7473 | 82.55 | 6.6497 | 83.1549 | 5.2205 | 7.6853 | 44.3113 | 111.3285 | 8.7739 | 242.2711 | 152.7972 | 287.2213 | 11.1532 | 50.1468 | 15.2113 | 205 | 45.1016 | 0 | 307.8744 | 0
8107 | 873.8241 | 5.8011 | 19.2172 | 94.162 | 81.5527 | 7.5997 | 79.053 | 5.1219 | 8.027 | 40.3718 | 88.6143 | 7.3734 | 233.7066 | 143.8855 | 274.8263 | 10.8259 | 49.4714 | 14.1881 | 221 | 43.2892 | 0 | 303.5143 | 0
8108 | 862.6117 | 5.8402 | 19.1888 | 94.4333 | 83.5495 | 5.7005 | 66.6213 | 6.1141 | 8.7892 | 40.514 | 78.521 | 7.3626 | 227.1018 | 127.7012 | 262.3584 | 10.8029 | 49.8276 | 13.5121 | 235 | 39.8712 | 0 | 314.2041 | 0
8109 | 854.4532 | 5.5417 | 18.9571 | 93.2958 | 84.554 | 4.7503 | 72.4886 | 7.4727 | 8.342 | 38.1589 | 75.634 | 7.2042 | 223.1883 | 123.0341 | 250.8508 | 10.8725 | 50.901 | 13.1687 | 205 | 36.3269 | 0 | 323.4702 | 0
8110 | 846.2972 | 5.784 | 19.1362 | 93.021 | 83.5538 | 5.6997 | 74.1748 | 6.3129 | 7.4465 | 36.1929 | 73.0381 | 8.5714 | 207.8511 | 116.2986 | 246.4679 | 10.8454 | 49.7237 | 12.4997 | 215 | 34.159 | 0 | 319.1297 | 0
8111 | 854.7247 | 4.626 | 19.1943 | 93.7916 | 83.5499 | 5.7016 | 64.316 | 5.6912 | 7.2645 | 36.3159 | 70.6342 | 7.7555 | 194.9978 | 118.3361 | 241.2501 | 10.9473 | 48.513 | 12.1529 | 189 | 34.8916 | 0 | 301.0288 | 0
8112 | 845.0764 | 3.4398 | 19.1752 | 92.7677 | 81.5528 | 7.5979 | 67.5613 | 6.8871 | 6.9224 | 37.2056 | 66.2108 | 7.1476 | 189.8018 | 120.7251 | 239.1746 | 10.7106 | 48.4248 | 11.9138 | 168 | 37.9264 | 0 | 296.3964 | 0
8113 | 865.9357 | 3.1635 | 19.229 | 92.2932 | 82.5518 | 6.6503 | 71.9465 | 7.7865 | 6.6175 | 35.9097 | 65.9224 | 7.148 | 188.2618 | 106.621 | 243.2377 | 10.6899 | 48.7962 | 11.4826 | 167 | 36.891 | 0 | 298.3036 | 0
8114 | 861.4978 | 3.3302 | 19.4148 | 92.2598 | 84.5543 | 4.7505 | 65.0046 | 6.4649 | 6.5569 | 35.2173 | 65.5334 | 7.1116 | 188.3405 | 99.2513 | 251.7852 | 10.7518 | 48.7229 | 11.3075 | 145 | 36.261 | 0 | 300.3809 | 0
8115 | 841.9044 | 3.0251 | 19.4194 | 92.4523 | 78.5607 | 10.4484 | 65.7777 | 5.748 | 6.5252 | 36.6811 | 64.76 | 7.0138 | 184.9956 | 97.2218 | 246.3406 | 10.9535 | 48.7277 | 11.3094 | 129 | 33.3826 | 0 | 293.4536 | 0
8116 | 825.954 | 2.7852 | 19.3744 | 92.7273 | 80.5587 | 8.5505 | 71.9231 | 6.9032 | 6.4524 | 37.0518 | 64.9675 | 6.9843 | 181.2426 | 92.5907 | 247.7731 | 10.8931 | 48.7257 | 11.2973 | 122 | 30.602 | 0 | 293.9133 | 0
8117 | 804.5885 | 3.203 | 19.4327 | 93.4763 | 79.5574 | 9.4997 | 65.9857 | 7.3862 | 6.5224 | 37.7881 | 64.9428 | 6.9671 | 179.0155 | 88.8238 | 243.1416 | 10.7174 | 49.8796 | 11.3075 | 117 | 31.2314 | 0 | 283.947 | 0
8118 | 796.9548 | 4.0356 | 19.2252 | 92.6787 | 83.5523 | 5.7011 | 63.0828 | 6.0413 | 6.0512 | 36.5132 | 64.9207 | 7.178 | 175.4518 | 88.6119 | 237.5597 | 10.6925 | 51.9187 | 11.3087 | 103 | 37.0227 | 0 | 289.2399 | 0
8119 | 804.2135 | 4.1815 | 19.4106 | 92.2584 | 83.5545 | 5.7 | 71.7686 | 5.8664 | 6.2585 | 36.1771 | 66.0786 | 7.4085 | 175.1402 | 89.0852 | 225.7888 | 10.6049 | 49.3623 | 11.2706 | 100 | 32.7387 | 0 | 289.2156 | 0
8120 | 812.3406 | 4.0941 | 19.3122 | 92.4937 | 82.5541 | 6.6497 | 69.4051 | 6.7764 | 6.3412 | 36.5494 | 69.8347 | 7.1136 | 180.9805 | 99.0853 | 221.461 | 12.2018 | 48.3269 | 11.5121 | 102 | 33.7267 | 0 | 288.0584 | 0
8121 | 816.7965 | 4.0532 | 19.198 | 91.4959 | 83.5546 | 5.7003 | 65.7814 | 7.2743 | 5.7295 | 42.0072 | 70.9041 | 5.3281 | 188.8016 | 97.4815 | 216.5501 | 15.6076 | 47.447 | 12.219 | 100 | 37.6795 | 0 | 281.6814 | 0
8122 | 828.38 | 3.0926 | 18.9411 | 90.5341 | 84.5536 | 4.7503 | 89.5113 | 5.708 | 6.8545 | 58.7738 | 73.8807 | 4.4685 | 195.407 | 98.4123 | 213.7937 | 20.8717 | 46.8265 | 12.5392 | 188 | 36.8326 | 0 | 280.9641 | 0.021689
8123 | 864.0242 | 2.8709 | 18.8756 | 90.8269 | 83.5511 | 5.6997 | 103.034 | 4.4371 | 6.3078 | 68.7559 | 82.4615 | 8.4198 | 211.595 | 104.0914 | 213.1937 | 15.6524 | 46.6776 | 12.8017 | 160 | 37.6706 | 0 | 296.9068 | 0.031048
8124 | 908.4509 | 2.9335 | 18.8617 | 91.2403 | 83.562 | 5.7 | 95.2576 | 4.1638 | 6.1953 | 67.3401 | 86.4048 | 10.026 | 221.5569 | 111.0628 | 211.628 | 12.9106 | 46.6861 | 13.6421 | 151 | 40.7257 | 0 | 299.9509 | 0.036323
8125 | 916.8803 | 2.9835 | 18.9312 | 91.5967 | 83.5611 | 5.7 | 99.8949 | 4.9739 | 6.7357 | 66.7061 | 87.7004 | 10.2304 | 229.9725 | 117.3219 | 219.9965 | 12.4789 | 46.4529 | 14.2407 | 156 | 41.4287 | 0 | 294.7257 | 0.04337
8126 | 903.89 | 2.7904 | 18.5298 | 91.9341 | 84.556 | 4.7503 | 106.0362 | 5.3404 | 6.1547 | 69.8784 | 91.5189 | 10.6557 | 240.8971 | 123.3073 | 237.6936 | 12.0015 | 48.3317 | 14.5839 | 162 | 45.13 | 0 | 287.7813 | 0.02838
8127 | 890.2602 | 4.0612 | 19.2571 | 93.5254 | 83.5519 | 5.6997 | 106.0841 | 5.2338 | 5.7382 | 68.7094 | 103.6634 | 9.8501 | 242.2896 | 131.2088 | 260.7231 | 12.5725 | 50.8891 | 14.9615 | 156 | 50.4492 | 0 | 291.6783 | 0.021632
8128 | 885.2686 | 4.9954 | 19.5817 | 94.7031 | 83.5537 | 5.7 | 109.2411 | 5.2587 | 5.9193 | 60.2479 | 111.2682 | 10.8749 | 240.4011 | 145.8944 | 268.5811 | 12.9812 | 51.449 | 15.4065 | 149 | 56.5987 | 0 | 288.2836 | 0
8129 | 899.7669 | 5.5922 | 19.6397 | 95.0758 | 83.5543 | 5.7 | 112.6009 | 4.8192 | 7.1567 | 45.6851 | 103.5871 | 16.0694 | 234.7696 | 155.4803 | 280.5813 | 11.7383 | 49.6639 | 15.1594 | 160 | 51.6377 | 0 | 290.8567 | 0
8130 | 905.5429 | 5.5579 | 19.2865 | 94.6718 | 82.5501 | 6.6497 | 108.9303 | 4.6728 | 8.1905 | 42.0159 | 95.4426 | 13.6737 | 237.6565 | 168.0378 | 285.7791 | 11.2265 | 49.055 | 14.9069 | 147 | 52.3778 | 0 | 284.5579 | 0
8131 | 893.5254 | 5.656 | 19.1488 | 94.572 | 83.551 | 5.7003 | 90.3617 | 4.7239 | 8.3563 | 42.794 | 93.6076 | 11.0425 | 251.7561 | 160.0475 | 289.8359 | 11.0236 | 49.7064 | 14.961 | 134 | 50.8967 | 0 | 292.9748 | 0
8132 | 906.0637 | 5.3049 | 19.3054 | 94.581 | 83.5541 | 5.7 | 91.5891 | 5.5853 | 7.8739 | 41.1192 | 88.2045 | 9.9274 | 240.8217 | 140.8524 | 273.7776 | 10.8432 | 49.3124 | 14.7218 | 126 | 47.3305 | 0 | 289.6067 | 0
8133 | 890.6476 | 4.9981 | 19.1137 | 93.299 | 83.5532 | 5.7 | 86.6804 | 5.8371 | 7.4573 | 37.4537 | 79.0625 | 8.8607 | 228.7434 | 120.2302 | 252.1729 | 10.891 | 48.9823 | 14.1458 | 121 | 45.7505 | 0 | 283.9245 | 0
8134 | 884.5247 | 5.0742 | 19.0753 | 93.3255 | 83.5523 | 5.7 | 81.0329 | 5.814 | 6.9973 | 36.0098 | 73.1589 | 7.6021 | 224.9701 | 109.9598 | 246.6582 | 10.7336 | 48.632 | 13.0213 | 114 | 46.165 | 0 | 279.4886 | 0
8135 | 871.3247 | 4.384 | 19.1164 | 93.4683 | 84.5574 | 4.7503 | 77.7339 | 5.5609 | 6.4272 | 35.8717 | 68.8436 | 7.4509 | 207.6946 | 102.9815 | 255.556 | 10.8739 | 48.5925 | 11.9997 | 120 | 42.0206 | 0 | 274.6823 | 0
8136 | 844.9273 | 3.1801 | 18.9887 | 93.2779 | 81.5573 | 7.5992 | 76.6602 | 4.7528 | 6.264 | 35.4552 | 66.4895 | 7.2806 | 191.9909 | 94.8698 | 245.3072 | 10.7342 | 48.5824 | 11.4629 | 118 | 40.9108 | 0 | 276.1955 | 0
8137 | 836.6247 | 2.75 | 19.1624 | 93.355 | 83.5568 | 5.7005 | 75.6881 | 4.4264 | 6.2932 | 34.8721 | 65.5267 | 7.0428 | 184.4894 | 89.6106 | 230.2563 | 10.6827 | 48.6696 | 11.3441 | 107 | 38.2797 | 0 | 276.0035 | 0
8138 | 825.4396 | 2.5258 | 19.1855 | 93.2669 | 83.557 | 5.7 | 74.5716 | 4.4487 | 6.3659 | 34.6356 | 66.4217 | 7.3173 | 182.1851 | 92.193 | 223.451 | 10.668 | 48.6419 | 11.333 | 101 | 35.9772 | 0 | 270.9183 | 0
8139 | 794.646 | 2.5415 | 19.2583 | 94.6463 | 83.5578 | 5.7 | 74.6641 | 5.2367 | 6.3828 | 34.4732 | 67.491 | 7.144 | 181.8243 | 105.4118 | 225.7981 | 9.8299 | 48.8134 | 11.3205 | 106 | 35.0255 | 0 | 275.384 | 0
8140 | 798.2969 | 2.5543 | 20.1145 | 94.4325 | 83.5567 | 5.7 | 74.1151 | 5.2812 | 6.3728 | 34.4729 | 67.9274 | 7.0025 | 182.3319 | 114.3666 | 223.7252 | 9.8314 | 48.8502 | 11.312 | 102 | 35.7179 | 0 | 274.3907 | 0
8141 | 796.379 | 3.2744 | 21.8467 | 94.8522 | 84.5591 | 4.7503 | 73.8806 | 5.1666 | 6.0905 | 34.3801 | 68.9291 | 7.7708 | 185.8272 | 108.0568 | 218.1051 | 9.7658 | 50.2677 | 11.3329 | 102 | 34.5673 | 0 | 319.3919 | 0
8142 | 810.8143 | 4.3312 | 27.2602 | 95.1425 | 83.5561 | 5.6997 | 80.1523 | 5.1974 | 6.6465 | 35.4254 | 70.6533 | 9.27 | 191.8892 | 110.6071 | 226.3365 | 9.8044 | 52.5452 | 11.3471 | 103 | 35.6797 | 0 | 342.1713 | 0
8143 | 862.5591 | 5.4307 | 46.338 | 101.2221 | 81.551 | 7.5995 | 96.2913 | 4.7125 | 10.9735 | 53.1675 | 100.0521 | 16.4367 | 221.9057 | 163.3593 | 248.7269 | 13.7769 | 49.5958 | 12.0441 | 172 | 43.9745 | 0 | 373.2273 | 0
8144 | 912.8091 | 11.2027 | 75.4309 | 106.1373 | 77.7075 | 11.4021 | 120.1336 | 4.7708 | 12.9957 | 88.3524 | 132.9304 | 33.9324 | 279.9513 | 224.2388 | 351.0779 | 29.1488 | 53.8487 | 13.4495 | 274 | 47.6435 | 0 | 442.305 | 0
8145 | 1023.3571 | 14.8308 | 95.7399 | 116.3965 | 74.6374 | 14.246 | 142.1274 | 5.9408 | 18.3272 | 101.062 | 161.1724 | 41.6252 | 352.9629 | 271.8158 | 467.2793 | 36.9322 | 66.6725 | 15.9474 | 327 | 57.2906 | 0 | 501.7169 | 0
8146 | 1107.4476 | 10.4515 | 100.3243 | 126.3048 | 75.5473 | 13.3003 | 160.7347 | 8.5346 | 23.5918 | 99.0922 | 180.9961 | 42.4257 | 404.821 | 303.5572 | 538.4141 | 42.0706 | 77.9708 | 18.5708 | 346 | 65.5089 | 0 | 548.7311 | 0.015554
8147 | 1144.7332 | 6.9994 | 102.2673 | 128.5944 | 74.546 | 14.2497 | 163.255 | 9.9735 | 27.1142 | 96.9278 | 185.8145 | 44.4582 | 423.9512 | 319.8704 | 565.4995 | 43.4053 | 85.7971 | 17.9614 | 381 | 67.423 | 0 | 577.1613 | 0.036747
8148 | 1191.6709 | 5.8044 | 107.9771 | 129.3792 | 75.5485 | 13.3003 | 162.85 | 11.5639 | 23.0054 | 106.1718 | 181.5542 | 46.2893 | 457.6644 | 330.4784 | 585.0356 | 43.0349 | 88.4134 | 17.5804 | 375 | 79.1239 | 0 | 571.6004 | 0.030868
8149 | 1187.5159 | 5.2417 | 105.9577 | 128.6649 | 73.5467 | 15.1995 | 167.3517 | 11.5461 | 16.2915 | 104.5805 | 178.728 | 40.5508 | 467.0305 | 328.0572 | 586.1903 | 43.785 | 87.5052 | 18.2876 | 354 | 78.4846 | 0 | 560.0076 | 0.033179
8150 | 1163.6702 | 4.8892 | 107.3354 | 130.0101 | 72.5484 | 16.1497 | 176.5229 | 10.3973 | 19.9842 | 100.2634 | 187.5376 | 42.9496 | 469.657 | 341.1363 | 582.0892 | 44.0456 | 87.8777 | 19.6545 | 315 | 72.1627 | 0 | 583.7984 | 0.021478
8151 | 1170.5141 | 4.9631 | 105.7608 | 135.9311 | 74.5466 | 14.2505 | 179.9816 | 7.0587 | 21.0548 | 104.6898 | 193.5655 | 42.4745 | 462.7912 | 346.3726 | 581.9145 | 42.6767 | 89.1005 | 19.9026 | 284 | 78.6828 | 0 | 595.9849 | 0.0082264
8152 | 1146.5059 | 6.5287 | 107.5026 | 138.1406 | 75.5492 | 13.3003 | 172.203 | 6.7343 | 12.3038 | 107.2349 | 193.0697 | 42.1407 | 442.9332 | 346.8248 | 566.4805 | 40.0846 | 87.2656 | 19.6591 | 275 | 80.0068 | 0 | 585.6845 | 0
8153 | 1104.2547 | 6.9201 | 104.3461 | 134.4184 | 76.5454 | 12.3503 | 162.2308 | 8.1761 | 9.6793 | 103.2395 | 190.1625 | 39.3139 | 436.4757 | 316.0345 | 514.5841 | 34.9085 | 84.3704 | 18.9379 | 248 | 77.2683 | 0 | 551.3823 | 0
8154 | 1038.6557 | 6.8532 | 100.0685 | 120.2467 | 82.5474 | 6.6516 | 147.7812 | 7.2898 | 8.779 | 82.7902 | 177.9138 | 35.3885 | 385.7229 | 253.0004 | 419.7471 | 19.5268 | 80.2227 | 17.9971 | 236 | 71.906 | 0 | 429.8496 | 0
8155 | 995.361 | 6.4672 | 96.3826 | 107.2908 | 81.5509 | 7.5997 | 136.4578 | 6.2413 | 7.8613 | 63.2338 | 165.21 | 28.421 | 324.3586 | 211.8926 | 355.5646 | 13.0174 | 72.9211 | 17.4396 | 214 | 67.2474 | 0 | 374.2757 | 0
8156 | 944.0099 | 6.2555 | 81.1866 | 102.6945 | 82.5547 | 6.6503 | 119.9593 | 6.1162 | 7.4937 | 58.3733 | 137.3653 | 13.5743 | 282.7984 | 180.6482 | 336.4863 | 11.8707 | 64.9564 | 16.3245 | 200 | 57.4025 | 0 | 309.5525 | 0
8157 | 922.6992 | 10.5308 | 39.2816 | 98.4271 | 83.5541 | 5.7003 | 102.58 | 5.3685 | 7.076 | 54.9028 | 114.8057 | 8.5023 | 254.2968 | 150.0878 | 320.5986 | 11.1253 | 60.9263 | 14.9237 | 174 | 52.4938 | 0 | 279.1257 | 0
8158 | 887.6884 | 8.1423 | 25.3061 | 96.1381 | 83.554 | 5.7 | 90.9162 | 5.0429 | 6.6605 | 43.5134 | 93.6004 | 8.5493 | 231.2992 | 131.2442 | 278.9469 | 10.9556 | 56.7426 | 13.9822 | 151 | 46.7291 | 0 | 264.8213 | 0
8159 | 860.6522 | 4.8658 | 24.9136 | 93.4988 | 83.5513 | 5.7 | 87.8278 | 5.3401 | 6.4589 | 33.0956 | 74.3075 | 8.3311 | 216.543 | 113.5567 | 243.2668 | 10.5603 | 55.0697 | 13.7111 | 142 | 44.3491 | 0 | 262.1756 | 0
8160 | 837.3872 | 3.4262 | 24.5437 | 92.9242 | 83.5524 | 5.7 | 93.0552 | 5.9285 | 6.5682 | 30.3169 | 68.041 | 8.2468 | 205.6901 | 101.6781 | 233.8869 | 10.8059 | 54.8177 | 13.5876 | 129 | 39.879 | 0 | 265.6375 | 0
8161 | 834.4583 | 2.885 | 24.5674 | 92.5297 | 80.557 | 8.5492 | 84.5823 | 6.2124 | 6.4366 | 29.5526 | 68.6125 | 8.3815 | 205.2038 | 97.5812 | 234.1433 | 10.8221 | 55.1858 | 13.1499 | 115 | 36.9234 | 0 | 265.2351 | 0
8162 | 826.6591 | 5.9909 | 24.6081 | 92.429 | 82.5584 | 6.6505 | 71.307 | 6.1795 | 6.5678 | 29.163 | 73.7244 | 8.3805 | 206.5442 | 95.9224 | 226.8539 | 10.6661 | 55.2611 | 12.3871 | 105 | 33.7062 | 0 | 264.0561 | 0
8163 | 801.2828 | 9.7428 | 24.6056 | 92.2925 | 82.5565 | 6.65 | 75.6578 | 6.3254 | 6.5282 | 29.0167 | 76.9237 | 8.7287 | 201.9055 | 103.5962 | 231.4565 | 10.7525 | 55.1035 | 11.8107 | 108 | 30.5732 | 0 | 259.4712 | 0
8164 | 805.8519 | 7.7708 | 24.6071 | 92.2162 | 81.5553 | 7.5997 | 77.3636 | 6.1266 | 6.4083 | 29.2359 | 76.8807 | 8.4905 | 197.0174 | 103.3329 | 232.346 | 10.4618 | 55.0997 | 11.7098 | 98 | 30.6594 | 0 | 268.419 | 0
8165 | 800.3672 | 4.8206 | 24.5326 | 92.2662 | 82.5539 | 6.6503 | 67.6858 | 6.043 | 6.2698 | 29.81 | 75.8019 | 8.0809 | 201.0085 | 102.6453 | 226.1725 | 10.7308 | 56.6201 | 11.7435 | 99 | 30.0514 | 0 | 294.1909 | 0
8166 | 805.4034 | 4.5292 | 33.0343 | 93.2603 | 83.5516 | 5.7003 | 76.49 | 7.2457 | 7.0409 | 31.4872 | 74.3212 | 9.3535 | 205.6858 | 112.3402 | 226.6801 | 10.6857 | 59.2322 | 11.7074 | 103 | 30.3518 | 0 | 346.5293 | 0
8167 | 840.2257 | 5.7302 | 50.7129 | 102.153 | 80.5468 | 8.5492 | 97.2103 | 8.0456 | 10.1614 | 50.5923 | 91.7652 | 19.5955 | 232.4739 | 151.9646 | 248.0115 | 13.8054 | 56.1036 | 12.5234 | 192 | 37.2703 | 0 | 401.9413 | 0
8168 | 906.8016 | 6.9188 | 80.9711 | 105.2131 | 76.5479 | 12.3489 | 110.1447 | 7.3141 | 16.1228 | 97.6894 | 134.2534 | 36.9221 | 291.4389 | 222.1734 | 367.9239 | 29.8522 | 61.2964 | 15.9622 | 249 | 43.0944 | 0 | 444.19 | 0
8169 | 982.2876 | 10.6069 | 94.4994 | 106.052 | 75.5446 | 13.2997 | 130.4395 | 8.8889 | 21.5217 | 104.1348 | 162.9939 | 41.506 | 363.2384 | 273.8014 | 476.7038 | 38.3756 | 72.0406 | 19.4425 | 275 | 55.7117 | 0 | 520.8173 | 0
8170 | 1072.1033 | 11.9849 | 102.4414 | 118.8792 | 74.5479 | 14.2497 | 155.8129 | 12.321 | 24.6157 | 103.0053 | 180.3899 | 41.6042 | 409.5667 | 305.6995 | 566.1864 | 40.5138 | 81.6164 | 19.4409 | 365 | 61.0375 | 0 | 583.3093 | 0.04434
8171 | 1122.7952 | 10.6683 | 102.2674 | 124.7691 | 74.5453 | 14.25 | 154.1133 | 11.7448 | 25.585 | 110.1175 | 185.4794 | 43.4523 | 430.8886 | 351.4345 | 611.3298 | 42.014 | 87.5369 | 19.1229 | 364 | 71.0963 | 0 | 608.6 | 0.040536
8172 | 1170.7526 | 6.4428 | 106.7889 | 137.6258 | 75.5457 | 13.3003 | 161.1468 | 10.3473 | 24.3895 | 111.3217 | 186.5554 | 43.088 | 462.4243 | 378.7093 | 606.4308 | 43.4263 | 88.1706 | 19.4275 | 341 | 79.961 | 0 | 628.7119 | 0.039535
8173 | 1144.1082 | 5.0914 | 110.193 | 135.5235 | 74.5472 | 14.2497 | 163.3305 | 10.1543 | 21.0629 | 100.9736 | 186.2329 | 43.9717 | 467.5942 | 370.9848 | 588.68 | 43.8167 | 86.843 | 19.8623 | 371 | 70.3478 | 0 | 617.2071 | 0.046156
8174 | 1152.5601 | 5.2569 | 109.8026 | 139.3656 | 72.5436 | 16.1495 | 154.398 | 10.6027 | 20.658 | 104.6564 | 189.4992 | 45.317 | 468.664 | 368.418 | 609.7237 | 44.0342 | 88.6862 | 19.9287 | 293 | 69.5025 | 0 | 644.0672 | 0.026479
8175 | 1163.1228 | 5.4655 | 111.1455 | 141.139 | 75.5475 | 13.3008 | 161.3231 | 9.978 | 21.5033 | 108.3313 | 191.6538 | 43.0833 | 477.3512 | 370.033 | 599.2745 | 44.4327 | 89.606 | 20.1532 | 282 | 71.3669 | 0 | 621.1621 | 0.0095743
8176 | 1140.9212 | 6.6689 | 108.9279 | 135.4777 | 72.5444 | 16.1492 | 156.803 | 10.0529 | 21.9893 | 115.3854 | 191.9472 | 40.0275 | 471.0109 | 367.263 | 576.4385 | 43.4766 | 90.8658 | 20.9052 | 278 | 73.2024 | 0 | 607.7659 | 0
8177 | 1116.7694 | 7.2672 | 102.4384 | 135.0068 | 80.5407 | 8.5521 | 146.8563 | 8.52 | 22.196 | 114.8549 | 186.8956 | 35.078 | 449.06 | 353.2872 | 538.9866 | 36.4567 | 89.2691 | 20.5042 | 261 | 70.409 | 0 | 553.6049 | 0
8178 | 1063.9181 | 7.3773 | 97.2906 | 125.0889 | 82.5442 | 6.6505 | 141.1987 | 7.1542 | 20.7137 | 90.3466 | 175.4605 | 30.4856 | 399.7492 | 294.3797 | 455.5928 | 19.7426 | 83.7656 | 19.56 | 213 | 64.8503 | 0 | 425.5668 | 0
8179 | 994.5599 | 8.3747 | 92.7016 | 112.3802 | 83.5468 | 5.7003 | 124.7629 | 8.3159 | 16.3188 | 73.284 | 144.5765 | 25.767 | 350.6021 | 227.3035 | 376.6084 | 12.5208 | 77.5975 | 18.0717 | 198 | 57.3517 | 0 | 365.5722 | 0
8180 | 953.2997 | 7.4148 | 79.7987 | 109.1941 | 83.5484 | 5.7 | 121.122 | 8.12 | 10.0112 | 66.483 | 125.4532 | 16.6057 | 303.8573 | 198.0113 | 325.6551 | 12.1169 | 67.3161 | 16.2443 | 173 | 51.7838 | 0 | 318.7692 | 0
8181 | 923.7699 | 5.5849 | 39.7069 | 104.1625 | 83.5554 | 5.7 | 116.3451 | 6.8754 | 7.336 | 59.2479 | 113.4338 | 12.9668 | 273.3067 | 176.7553 | 296.9026 | 12.0009 | 62.3082 | 15.2252 | 158 | 44.4875 | 0 | 289.7739 | 0
8182 | 885.4207 | 4.999 | 26.0202 | 102.1536 | 83.5521 | 5.7 | 98.3871 | 7.0993 | 6.8938 | 45.415 | 96.0375 | 10.3079 | 231.4875 | 153.3851 | 264.4515 | 12.0805 | 59.5485 | 14.4627 | 147 | 39.9923 | 0 | 285.899 | 0
8183 | 866.2481 | 4.434 | 25.653 | 101.9561 | 83.5489 | 5.7 | 85.3808 | 8.9048 | 6.4673 | 37.057 | 77.9376 | 8.7658 | 206.0119 | 133.0629 | 249.3374 | 11.9303 | 58.4856 | 14.3066 | 134 | 36.3532 | 0 | 282.1868 | 0
8184 | 835.7137 | 10.4146 | 25.4833 | 102.813 | 83.5486 | 5.7 | 74.7955 | 7.3222 | 6.4777 | 34.6215 | 70.552 | 8.2751 | 199.7717 | 123.0512 | 240.0256 | 11.8494 | 57.5375 | 14.1174 | 121 | 36.2672 | 0 | 271.6012 | 0
8185 | 828.3338 | 11.9792 | 25.3522 | 101.929 | 83.5541 | 5.7 | 73.3766 | 6.4966 | 6.5113 | 35.3058 | 70.1484 | 7.8711 | 197.0467 | 116.539 | 239.484 | 12.0735 | 57.553 | 14.0235 | 112 | 35.6502 | 0 | 278.6548 | 0
8186 | 834.4243 | 6.8786 | 25.7075 | 98.9302 | 82.5556 | 6.6497 | 89.0923 | 8.6585 | 6.7222 | 36.0112 | 69.6923 | 7.6121 | 194.7498 | 112.9141 | 236.0884 | 12.0152 | 57.5919 | 13.8976 | 106 | 33.8759 | 0 | 286.51 | 0
8187 | 809.4801 | 3.2492 | 25.6459 | 98.7649 | 82.5521 | 6.65 | 84.4806 | 7.6905 | 6.423 | 36.2432 | 68.2414 | 8.2474 | 193.58 | 113.6731 | 232.6053 | 12.0068 | 57.6273 | 12.9 | 106 | 32.018 | 0 | 293.2131 | 0
8188 | 810.0033 | 2.5896 | 25.5682 | 99.2336 | 83.5518 | 5.7003 | 71.6434 | 6.2161 | 6.3632 | 35.4862 | 67.4908 | 7.8421 | 192.8244 | 113.0462 | 228.8837 | 11.9997 | 57.6153 | 12.3404 | 103 | 31.0241 | 0 | 295.0124 | 0
8189 | 802.6553 | 3.0421 | 25.4329 | 99.8456 | 83.5527 | 5.7016 | 76.8019 | 6.1079 | 6.2543 | 35.41 | 67.0796 | 7.5389 | 195.2169 | 110.8373 | 226.5139 | 11.887 | 58.9276 | 12.1161 | 104 | 30.4578 | 0 | 306.6389 | 0
8190 | 815.0455 | 3.9654 | 32.1877 | 103.3506 | 83.5516 | 5.6984 | 80.091 | 6.6898 | 6.3011 | 35.5548 | 68.756 | 11.8457 | 204.7213 | 117.903 | 234.1008 | 11.9653 | 60.4106 | 12.0066 | 105 | 32.2032 | 0 | 351.2882 | 0
8191 | 859.8279 | 6.4535 | 47.2568 | 102.8708 | 81.5472 | 7.5995 | 86.299 | 6.7727 | 11.3708 | 58.3266 | 88.8086 | 18.8073 | 231.201 | 174.3962 | 253.6013 | 14.8388 | 57.6848 | 12.052 | 169 | 40.4264 | 0 | 384.9802 | 0
8192 | 921.6713 | 9.0568 | 78.1152 | 103.4569 | 76.5444 | 12.3521 | 117.6861 | 7.516 | 15.9523 | 105.0876 | 138.8857 | 32.4085 | 283.5601 | 246.5058 | 338.6672 | 30.4629 | 62.0033 | 16.1665 | 277 | 46.8091 | 0 | 440.3494 | 0
8193 | 989.1987 | 8.0983 | 95.5401 | 114.4345 | 72.5555 | 16.1455 | 145.0187 | 9.2836 | 22.7731 | 120.0739 | 165.4165 | 38.0044 | 350.6712 | 303.3891 | 468.5133 | 38.5527 | 71.0129 | 17.9265 | 296 | 65.0727 | 0 | 520.1514 | 0
8194 | 1078.2213 | 6.5369 | 104.5429 | 123.8601 | 74.5484 | 14.2505 | 161.9037 | 9.8062 | 25.2307 | 116.8297 | 174.1622 | 41.3236 | 401.5954 | 348.0378 | 564.7839 | 42.3609 | 80.8378 | 18.6358 | 374 | 73.907 | 0 | 590.0558 | 0.015221
8195 | 1121.809 | 7.4428 | 106.4369 | 127.6188 | 73.5496 | 15.1997 | 165.549 | 10.1398 | 24.6937 | 117.0372 | 177.3147 | 41.9769 | 435.5834 | 371.5623 | 612.5346 | 44.2645 | 104.8225 | 19.7406 | 342 | 74.095 | 0 | 603.889 | 0.022938
8196 | 1176.1745 | 8.7156 | 108.8362 | 133.9426 | 73.5476 | 15.2 | 170.6589 | 12.015 | 22.9665 | 125.1845 | 180.3709 | 40.9716 | 475.1689 | 383.3076 | 632.6435 | 44.6051 | 114.0006 | 20.1644 | 313 | 85.8401 | 0 | 608.9388 | 0.0096589
8197 | 1174.5735 | 12.1578 | 107.2124 | 137.2441 | 74.5465 | 14.2503 | 166.367 | 12.6189 | 19.456 | 120.2064 | 179.9661 | 40.6898 | 469.0909 | 384.538 | 616.3746 | 46.0289 | 112.8674 | 20.233 | 354 | 79.2918 | 0 | 589.8445 | 0.006284
8198 | 1203.1206 | 19.637 | 107.8592 | 142.4181 | 72.5498 | 16.1495 | 162.882 | 10.9025 | 19.5757 | 118.2547 | 183.1099 | 41.2385 | 470.6992 | 385.8868 | 613.3419 | 47.0955 | 116.1585 | 20.3031 | 292 | 81.0097 | 0 | 630.9125 | 0.0024256
8199 | 1197.9824 | 16.0379 | 109.0765 | 142.9043 | 71.5398 | 17.1045 | 163.1308 | 8.4399 | 19.3275 | 123.0383 | 187.6472 | 41.0779 | 483.3373 | 381.5213 | 604.7205 | 45.0012 | 117.5161 | 20.2692 | 253 | 84.7552 | 0 | 604.0818 | 0.00069639
8200 | 1169.3335 | 13.7609 | 108.9389 | 136.6662 | 72.5459 | 16.15 | 165.5255 | 7.1275 | 13.7195 | 128.7394 | 195.1398 | 43.4743 | 463.5194 | 368.8452 | 592.0963 | 42.5899 | 102.1305 | 20.2119 | 275 | 82.4223 | 0 | 609.421 | 0
8201 | 1122.1143 | 11.7151 | 102.711 | 135.5012 | 81.5525 | 7.5979 | 157.7002 | 6.6999 | 13.9277 | 122.5709 | 197.9214 | 40.1311 | 427.4557 | 340.7177 | 550.0944 | 35.6658 | 91.4048 | 19.9285 | 232 | 78.157 | 0 | 537.2529 | 0
8202 | 1071.6294 | 8.9098 | 98.1171 | 121.5159 | 83.5509 | 5.7005 | 144.4832 | 6.4981 | 21.0535 | 94.7528 | 186.7189 | 35.9502 | 375.5852 | 269.6994 | 473.2677 | 20.6148 | 82.9671 | 18.501 | 235 | 71.0419 | 0 | 407.9361 | 0
8203 | 1011.4656 | 6.8269 | 92.8906 | 108.9856 | 82.5507 | 6.6497 | 135.2193 | 6.6026 | 22.6572 | 70.116 | 153.2109 | 30.0324 | 323.5855 | 210.1227 | 408.4787 | 13.1418 | 76.9421 | 17.2044 | 212 | 62.5867 | 0 | 357.6707 | 0
8204 | 966.4372 | 5.2617 | 84.7123 | 103.3584 | 82.553 | 6.65 | 121.8397 | 6.2174 | 19.9192 | 62.3303 | 132.9967 | 16.3031 | 275.5253 | 180.7826 | 357.1052 | 11.0718 | 69.9868 | 15.5383 | 188 | 57.6506 | 0 | 308.9809 | 0
8205 | 928.1177 | 4.9353 | 44.847 | 98.0608 | 83.5506 | 5.7018 | 109.2911 | 5.6033 | 18.9987 | 56.6994 | 121.396 | 10.7458 | 252.0237 | 148.7179 | 307.8867 | 10.8745 | 65.0684 | 14.5422 | 170 | 49.0374 | 0 | 286.1882 | 0
8206 | 893.2839 | 4.6456 | 30.6005 | 95.4807 | 84.5599 | 4.7487 | 94.393 | 4.3413 | 18.8237 | 44.6932 | 102.3936 | 9.4617 | 228.7896 | 122.3473 | 267.1309 | 10.815 | 62.8734 | 14.1121 | 151 | 44.1028 | 0 | 274.7189 | 0
8207 | 862.7473 | 3.9555 | 29.7633 | 95.3485 | 83.5604 | 5.6997 | 85.9911 | 3.6229 | 17.5102 | 33.4255 | 83.5031 | 8.7787 | 223.29 | 109.1206 | 250.8366 | 10.8317 | 61.9543 | 14.0317 | 144 | 41.7642 | 0 | 266.1197 | 0
8208 | 841.2691 | 2.9211 | 29.5542 | 95.3747 | 83.5563 | 5.7 | 82.9196 | 4.6501 | 10.9928 | 30.3651 | 76.1053 | 8.6121 | 211.7836 | 104.6026 | 236.9729 | 10.7042 | 60.5826 | 13.9297 | 123 | 41.9488 | 0 | 258.8546 | 0
8209 | 834.798 | 2.7974 | 29.5425 | 95.0109 | 84.5586 | 4.7503 | 80.261 | 4.7858 | 7.492 | 31.6409 | 75.1754 | 8.1221 | 196.8051 | 99.0851 | 222.187 | 10.5567 | 60.1988 | 13.4471 | 112 | 38.5485 | 0 | 259.7868 | 0
8210 | 817.8543 | 2.9033 | 29.5238 | 94.7418 | 81.5587 | 7.5992 | 79.401 | 4.6435 | 6.8191 | 32.6349 | 75.3934 | 7.7799 | 193.9202 | 95.101 | 222.8831 | 10.8086 | 60.8429 | 12.8534 | 106 | 35.668 | 0 | 258.9664 | 0
8211 | 794.562 | 3.0751 | 29.2136 | 95.2424 | 83.5601 | 5.7005 | 78.7582 | 4.3636 | 6.7594 | 30.4996 | 75.2799 | 7.6297 | 192.4642 | 91.9358 | 229.6279 | 10.5498 | 60.3834 | 12.3126 | 108 | 33.8355 | 0 | 256.1271 | 0
8212 | 786.1414 | 3.1384 | 29.2231 | 95.3322 | 83.5649 | 5.7 | 78.373 | 3.5678 | 6.7063 | 26.9939 | 74.4123 | 7.6041 | 190.1934 | 89.9337 | 223.7122 | 10.5898 | 60.0258 | 11.8751 | 103 | 32.5699 | 0 | 255.1656 | 0
8213 | 795.561 | 3.3787 | 29.3822 | 96.2808 | 84.5656 | 4.7503 | 78.476 | 4.0202 | 6.5099 | 26.0192 | 75.1407 | 7.6145 | 195.2944 | 88.4941 | 217.4975 | 10.5138 | 61.655 | 11.6158 | 103 | 29.9125 | 0 | 269.3289 | 0
8214 | 815.7514 | 4.2145 | 43.6201 | 97.5669 | 83.5603 | 5.6997 | 94.9272 | 4.5123 | 7.3358 | 33.3503 | 77.8081 | 9.0364 | 206.9128 | 95.1834 | 226.3383 | 10.2887 | 64.1148 | 11.7743 | 104 | 32.558 | 0 | 322.0641 | 0
8215 | 843.0326 | 5.5213 | 64.002 | 100.3135 | 83.5527 | 5.7 | 111.5683 | 4.5593 | 10.9209 | 53.4221 | 93.3237 | 16.6252 | 240.6478 | 167.7274 | 246.1363 | 15.0627 | 61.5534 | 13.2604 | 178 | 38.9521 | 0 | 359.666 | 0
8216 | 893.449 | 10.0676 | 87.2671 | 104.4496 | 76.548 | 12.3482 | 123.3929 | 5.5187 | 15.7862 | 93.6398 | 142.5222 | 33.7537 | 298.2697 | 243.8984 | 351.2735 | 30.647 | 66.227 | 15.814 | 271 | 44.7429 | 0 | 406.0117 | 0
8217 | 992.8025 | 13.0428 | 97.3232 | 117.3685 | 97.2549 | 15.1992 | 141.7903 | 7.8233 | 21.6727 | 98.2131 | 179.073 | 38.7103 | 366.2572 | 305.7989 | 484.0034 | 39.3691 | 76.0601 | 17.9737 | 317 | 63.5369 | 0 | 493.1943 | 0
8218 | 1107.5331 | 8.0407 | 100.9022 | 130.0397 | 119.9237 | 14.2503 | 162.8082 | 10.0138 | 24.3217 | 103.6067 | 189.8212 | 37.3961 | 423.1366 | 346.8866 | 560.8845 | 42.1148 | 82.0633 | 21.0736 | 385 | 70.3574 | 0 | 544.2683 | 0.035545
8219 | 1138.7878 | 4.9926 | 105.3873 | 138.3092 | 93.2573 | 14.25 | 167.4724 | 9.3077 | 25.5285 | 106.1536 | 189.0597 | 42.6271 | 426.5531 | 365.3724 | 587.2061 | 42.3904 | 86.1569 | 20.7999 | 382 | 69.6662 | 0 | 562.2917 | 0.10347
8220 | 1157.8641 | 6.1845 | 109.8461 | 143.3648 | 71.5446 | 17.0992 | 165.1763 | 8.3966 | 24.183 | 108.8743 | 190.3348 | 42.3841 | 461.0847 | 369.3699 | 604.9768 | 43.8734 | 88.1043 | 20.1854 | 376 | 77.9292 | 0 | 572.1226 | 0.10927
8221 | 1144.7233 | 7.6745 | 109.1507 | 138.8644 | 74.5401 | 14.2508 | 162.2971 | 6.5283 | 20.9543 | 108.6608 | 193.9029 | 40.6668 | 460.7642 | 352.3528 | 595.2017 | 43.8105 | 85.6018 | 20.0442 | 405 | 71.212 | 0 | 574.4677 | 0.13338
8222 | 1166.2541 | 7.6844 | 111.8996 | 142.2122 | 74.5388 | 14.25 | 159.1934 | 7.2196 | 22.8425 | 112.6595 | 193.6138 | 43.2371 | 469.4048 | 352.599 | 611.5136 | 44.5016 | 84.5769 | 20.6846 | 335 | 75.1265 | 0 | 600.3705 | 0.10875
8223 | 1203.7439 | 7.5805 | 110.8549 | 143.2161 | 76.5383 | 12.3505 | 162.3475 | 8.0327 | 21.6537 | 117.8737 | 193.7142 | 42.5274 | 478.0361 | 357.7393 | 615.9456 | 43.7773 | 86.6846 | 21.0521 | 293 | 79.2568 | 0 | 601.197 | 0.040758
8224 | 1173.8112 | 7.0269 | 108.4315 | 145.2963 | 76.5419 | 12.35 | 164.8574 | 7.8149 | 19.6837 | 103.9115 | 193.4858 | 40.7604 | 459.6901 | 346.8573 | 600.0985 | 42.147 | 86.5151 | 20.9433 | 268 | 74.6323 | 0 | 585.5737 | 0
8225 | 1133.3839 | 7.9598 | 100.9321 | 141.1425 | 81.5443 | 7.6013 | 156.6506 | 6.8173 | 21.0115 | 101.706 | 196.3092 | 40.1252 | 439.3583 | 328.6174 | 556.1552 | 35.3922 | 88.1759 | 20.714 | 232 | 72.4342 | 0 | 545.4055 | 0
8226 | 1082.695 | 11.7856 | 92.5917 | 124.2214 | 83.5491 | 5.7005 | 140.9785 | 5.2582 | 20.8758 | 93.2857 | 190.5431 | 37.0821 | 399.825 | 250.6559 | 449.1741 | 19.6803 | 83.4942 | 19.0819 | 216 | 65.1354 | 0 | 404.1334 | 0
8227 | 1037.4596 | 12.9647 | 88.2233 | 109.7071 | 84.5515 | 4.7503 | 127.4603 | 5.1574 | 17.5973 | 84.3358 | 160.6421 | 30.1097 | 352.2349 | 170.9538 | 385.1173 | 12.8373 | 75.3449 | 17.9218 | 209 | 56.6572 | 0 | 361.7676 | 0
8228 | 978.4745 | 9.6157 | 75.6964 | 104.1896 | 82.5537 | 6.6495 | 122.4294 | 5.0482 | 11.6198 | 80.2928 | 140.6602 | 17.0533 | 293.8013 | 143.0962 | 354.3217 | 10.8862 | 66.9098 | 17.1569 | 182 | 48.2867 | 0 | 299.5866 | 0
8229 | 937.5684 | 5.9756 | 34.0549 | 100.0893 | 82.5573 | 6.65 | 119.9312 | 4.9756 | 9.8561 | 77.1198 | 129.487 | 11.9587 | 260.4783 | 140.6449 | 310.7842 | 10.3711 | 62.4374 | 15.8359 | 176 | 43.6976 | 0 | 270.4585 | 0
8230 | 916.1293 | 4.5284 | 19.3546 | 98.9057 | 83.553 | 5.7003 | 104.6976 | 4.4365 | 10.7715 | 69.5317 | 111.7521 | 11.5029 | 240.1247 | 131.172 | 269.7494 | 10.4089 | 58.6053 | 14.6943 | 161 | 40.4072 | 0 | 257.9191 | 0
8231 | 883.6955 | 3.7841 | 18.9092 | 97.4625 | 83.5576 | 5.7 | 92.6718 | 3.8011 | 9.9573 | 62.5218 | 104.0516 | 11.3393 | 225.4712 | 119.6379 | 251.9461 | 10.4622 | 58.9158 | 14.1216 | 144 | 36.9248 | 0 | 254.3414 | 0
8232 | 844.8543 | 3.2943 | 18.9589 | 97.491 | 83.5564 | 5.7 | 83.7739 | 4.3246 | 9.8695 | 59.4587 | 98.1295 | 11.4465 | 211.8778 | 110.7974 | 247.5872 | 10.2234 | 58.4519 | 13.7147 | 119 | 33.2346 | 0 | 252.1386 | 0
8233 | 852.1882 | 3.058 | 19.0877 | 96.8433 | 84.556 | 4.7503 | 79.6071 | 4.8149 | 11.5127 | 54.0359 | 84.2439 | 11.7276 | 202.1949 | 102.4848 | 233.9353 | 10.2094 | 58.0764 | 13.1776 | 107 | 32.6086 | 0 | 251.6841 | 0
8234 | 842.3757 | 2.6667 | 18.9488 | 96.3251 | 83.5562 | 5.6997 | 78.9519 | 5.1323 | 10.3083 | 41.7556 | 79.0612 | 11.5444 | 199.4423 | 103.2108 | 232.933 | 10.0578 | 58.1949 | 12.5269 | 105 | 32.1882 | 0 | 258.0645 | 0
8235 | 828.923 | 2.8352 | 18.9845 | 95.7065 | 83.5592 | 5.7 | 78.7676 | 5.0472 | 9.3778 | 33.9252 | 78.8792 | 11.3232 | 194.9412 | 102.1876 | 236.8538 | 10.0828 | 58.2637 | 12.2777 | 105 | 30.53 | 0 | 255.979 | 0
8236 | 825.4671 | 2.732 | 18.8963 | 96.0845 | 84.5601 | 4.7503 | 77.8626 | 4.3072 | 7.193 | 27.6095 | 77.8049 | 11.2985 | 190.1163 | 95.0882 | 245.5962 | 10.1635 | 58.5621 | 12.2081 | 103 | 30.1084 | 0 | 258.6995 | 0
8237 | 832.1875 | 2.9682 | 18.8289 | 95.7178 | 83.5559 | 5.6997 | 77.1033 | 3.8094 | 6.5434 | 25.7159 | 77.85 | 10.8752 | 192.0508 | 90.2438 | 249.0441 | 10.0383 | 59.7289 | 12.3593 | 114 | 28.92 | 0 | 274.0301 | 0
8238 | 835.855 | 4.0811 | 33.2764 | 96.4488 | 83.5531 | 5.7 | 83.6304 | 4.2392 | 6.6273 | 25.7255 | 79.2358 | 16.2478 | 201.1388 | 104.0351 | 250.1795 | 9.9716 | 61.7289 | 12.0383 | 122 | 31.2957 | 0 | 328.3216 | 0
8239 | 882.7875 | 5.4824 | 55.8325 | 102.415 | 81.5456 | 7.5995 | 99.0722 | 5.0694 | 12.5067 | 40.4333 | 96.1091 | 21.53 | 231.0223 | 158.5295 | 266.6346 | 12.2301 | 58.8257 | 11.8737 | 195 | 39.9749 | 0 | 360.8615 | 0
8240 | 966.5848 | 10.1994 | 83.9712 | 104.1841 | 77.5421 | 11.3989 | 119.8599 | 5.5801 | 16.5357 | 78.5947 | 147.0386 | 35.9886 | 295.6773 | 236.3052 | 372.6273 | 28.5044 | 62.9834 | 13.0367 | 280 | 46.855 | 0 | 415.3549 | 0
8241 | 1033.8899 | 16.1376 | 96.8526 | 117.2095 | 73.5408 | 15.1989 | 144.5532 | 6.9817 | 20.0408 | 94.827 | 170.1614 | 41.6294 | 365.2153 | 291.7662 | 490.2392 | 37.5475 | 74.1279 | 16.6819 | 301 | 63.0151 | 0 | 488.5695 | 0
8242 | 1131.9946 | 14.5073 | 102.79 | 133.1348 | 75.5376 | 13.3005 | 162.8545 | 6.7881 | 22.9768 | 95.8471 | 176.1148 | 40.674 | 416.2336 | 318.8887 | 570.9613 | 41.2127 | 82.7026 | 18.2401 | 329 | 68.2907 | 0 | 553.3964 | 0.026527
8243 | 1155.1004 | 7.2815 | 102.8804 | 137.3555 | 69.5443 | 18.9984 | 167.8855 | 5.938 | 25.0262 | 100.9145 | 180.0421 | 41.0796 | 437.0055 | 337.0831 | 645.759 | 40.8926 | 88.8708 | 19.4297 | 325 | 69.5686 | 0 | 599.5343 | 0.039928
8244 | 1176.226 | 4.9178 | 106.3456 | 137.2812 | 73.5441 | 15.2011 | 169.7012 | 6.4795 | 23.3845 | 103.7903 | 182.8072 | 40.6553 | 454.1604 | 351.7415 | 661.2619 | 40.1618 | 93.5887 | 20.2202 | 326 | 77.2741 | 0 | 604.002 | 0.058045
8245 | 1170.7885 | 4.8022 | 104.7608 | 135.6502 | 69.5466 | 18.9989 | 163.9432 | 7.3365 | 17.1852 | 91.0499 | 184.5359 | 39.7422 | 451.6247 | 351.3052 | 643.7176 | 43.1528 | 100.6544 | 20.9375 | 358 | 74.432 | 0 | 594.3593 | 0.04988
8246 | 1171.1108 | 6.2601 | 104.4856 | 137.6425 | 68.5467 | 19.9497 | 162.9457 | 6.633 | 19.2008 | 84.7482 | 189.796 | 36.3427 | 478.8813 | 369.3514 | 619.6607 | 43.7225 | 115.2345 | 20.9243 | 294 | 74.6944 | 0 | 592.9991 | 0.021939
8247 | 1162.1078 | 6.8952 | 104.1849 | 140.4182 | 67.5439 | 20.8997 | 164.6842 | 5.4997 | 19.2318 | 87.1572 | 193.1576 | 35.7596 | 491.4377 | 370.7336 | 592.238 | 41.7855 | 116.972 | 20.9021 | 273 | 76.3327 | 0 | 590.076 | 0.0045233
8248 | 1115.9564 | 6.8822 | 100.4732 | 144.3727 | 68.5396 | 19.9503 | 161.4393 | 6.18 | 16.0773 | 97.1862 | 196.2206 | 40.1678 | 466.3539 | 359.1695 | 584.5805 | 39.5583 | 112.1482 | 20.8147 | 267 | 72.7816 | 0 | 587.1279 | 0
8249 | 1092.3121 | 6.8956 | 94.6865 | 142.5598 | 70.5413 | 18.0505 | 154.5781 | 6.0858 | 15.8263 | 107.6412 | 192.7428 | 41.3769 | 424.36 | 328.8311 | 529.2212 | 27.3165 | 106.8433 | 20.2518 | 246 | 64.7912 | 0 | 465.2025 | 0
8250 | 1042.9723 | 6.0878 | 79.2176 | 121.3147 | 77.5449 | 11.4018 | 141.0567 | 5.6693 | 16.7957 | 80.219 | 177.64 | 36.5567 | 363.5541 | 255.1376 | 405.5078 | 19.7456 | 100.2545 | 18.6634 | 249 | 57.1678 | 0 | 370.0906 | 0
8251 | 983.8468 | 5.2952 | 42.7043 | 103.0553 | 76.5468 | 12.3497 | 124.2615 | 4.6473 | 12.3585 | 64.2882 | 148.9943 | 28.262 | 314.8945 | 171.4207 | 339.0316 | 20.0443 | 91.3993 | 16.9212 | 248 | 55.685 | 0 | 326.0247 | 0
8252 | 918.3672 | 5.0358 | 23.2992 | 99.2434 | 77.5481 | 11.4003 | 109.8776 | 3.859 | 9.4938 | 60.0616 | 124.5396 | 14.7679 | 287.4739 | 136.6188 | 323.5921 | 18.8852 | 84.1868 | 16.1758 | 227 | 48.0923 | 0 | 278.0092 | 0
8253 | 891.6006 | 4.7211 | 19.4012 | 97.9264 | 78.5497 | 10.4503 | 103.9657 | 4.529 | 10.0675 | 55.487 | 96.0648 | 9.9122 | 273.5942 | 128.1817 | 300.5313 | 20.6554 | 82.122 | 15.2726 | 242 | 40.9704 | 0 | 278.5225 | 0
8254 | 868.4697 | 4.458 | 18.6852 | 98.3105 | 78.5506 | 10.45 | 99.34 | 5.098 | 10.8083 | 44.6432 | 82.3283 | 9.7911 | 251.5746 | 120.0061 | 281.9761 | 23.3194 | 80.861 | 13.936 | 213 | 35.7997 | 0 | 273.1353 | 0
8255 | 845.814 | 3.9305 | 18.6985 | 97.9006 | 78.5513 | 10.45 | 87.8671 | 4.977 | 8.1693 | 35.1706 | 77.1377 | 9.7757 | 234.4255 | 115.4244 | 272.3502 | 24.7721 | 80.2209 | 13.5926 | 192 | 33.6458 | 0 | 274.3489 | 0
8256 | 834.3475 | 3.0453 | 18.6639 | 97.6068 | 78.5512 | 10.45 | 81.8765 | 4.3303 | 7.0772 | 30.2108 | 73.6471 | 10.0056 | 225.9842 | 101.8579 | 272.7102 | 25.9152 | 78.9353 | 13.3175 | 161 | 32.8609 | 0 | 268.9187 | 0
8257 | 833.7622 | 2.5285 | 18.6992 | 97.3847 | 78.5434 | 10.4529 | 78.8076 | 3.675 | 7.2305 | 27.7176 | 72.5501 | 9.2906 | 225.2279 | 94.9854 | 264.0413 | 25.0789 | 79.0268 | 13.4238 | 139 | 34.1581 | 0 | 251.3285 | 0
8258 | 828.8338 | 2.4135 | 18.605 | 97.5359 | 78.5498 | 10.4471 | 76.6443 | 4.3999 | 6.8801 | 25.739 | 71.8857 | 8.9671 | 221.8846 | 94.8151 | 250.6838 | 25.3684 | 78.5727 | 13.111 | 126 | 34.2356 | 0 | 250.3496 | 0
8259 | 819.409 | 2.5362 | 18.6608 | 98.0462 | 79.5481 | 9.5003 | 76.0826 | 4.8513 | 6.8063 | 24.6106 | 71.9982 | 9.0527 | 214.2031 | 93.9011 | 245.9728 | 24.1577 | 78.2675 | 11.9876 | 127 | 34.0912 | 0 | 241.524 | 0
8260 | 811.4986 | 2.4142 | 18.3801 | 98.064 | 78.5482 | 10.4497 | 75.8507 | 4.8459 | 6.5115 | 24.2667 | 72.8324 | 8.9991 | 210.7781 | 88.1891 | 238.9959 | 22.9106 | 78.4556 | 11.5168 | 113 | 35.1876 | 0 | 236.2856 | 0
8261 | 824.2521 | 2.7722 | 18.3228 | 98.7576 | 78.5487 | 10.45 | 76.0978 | 4.641 | 6.3298 | 24.7494 | 72.6891 | 8.9241 | 209.4852 | 87.0816 | 226.7315 | 22.3192 | 79.9314 | 11.4957 | 114 | 33.8135 | 0 | 238.3764 | 0
8262 | 832.2966 | 3.7126 | 18.363 | 97.4385 | 78.5479 | 10.45 | 76.3101 | 3.7508 | 6.3768 | 24.8158 | 72.2607 | 8.9356 | 207.7683 | 88.0763 | 222.6018 | 20.0553 | 82.1011 | 11.5152 | 107 | 30.0174 | 0 | 231.7222 | 0
8263 | 838.8196 | 3.9222 | 32.7125 | 97.9901 | 79.5456 | 9.5003 | 76.2118 | 3.9068 | 6.8328 | 24.7844 | 72.5295 | 8.9612 | 207.2836 | 95.9115 | 221.5296 | 19.4178 | 80.1614 | 11.5084 | 102 | 30.2393 | 0 | 236.569 | 0
8264 | 852.3505 | 3.9847 | 40.9275 | 97.9237 | 78.5487 | 10.4497 | 79.505 | 4.8055 | 7.0908 | 26.031 | 81.6411 | 11.0996 | 214.0345 | 93.514 | 223.747 | 21.476 | 79.1614 | 11.6973 | 103 | 39.9641 | 0 | 241.5562 | 0
8265 | 851.2789 | 4.2561 | 49.4878 | 96.8128 | 74.5461 | 14.2489 | 87.9863 | 4.9788 | 6.7187 | 36.3742 | 107.6762 | 16.9923 | 220.9182 | 91.7302 | 229.5255 | 32.151 | 77.7737 | 12.8117 | 121 | 51.2649 | 0 | 239.8684 | 0
8266 | 857.5232 | 5.8194 | 67.4159 | 95.1367 | 74.5415 | 14.25 | 98.0272 | 4.5509 | 7.0545 | 45.7024 | 127.4836 | 22.2343 | 226.9196 | 101.6556 | 234.0143 | 36.3823 | 76.7225 | 14.2951 | 146 | 53.716 | 0 | 242.1967 | 0.012694
8267 | 866.44 | 7.5217 | 79.5525 | 95.1455 | 72.5453 | 16.1495 | 112.3684 | 3.624 | 8.9628 | 55.3882 | 138.6528 | 25.2914 | 241.9922 | 114.9649 | 238.8187 | 37.2048 | 76.6164 | 14.9228 | 196 | 56.565 | 0 | 261.7747 | 0.0078392
8268 | 874.199 | 5.7974 | 79.0283 | 95.2122 | 74.5439 | 14.2505 | 113.3212 | 2.9762 | 7.4685 | 60.1198 | 125.78 | 25.7037 | 253.482 | 122.5747 | 252.4417 | 38.9769 | 76.1572 | 15.4477 | 172 | 55.0169 | 0 | 266.6504 | 0.016721
8269 | 866.7467 | 4.4438 | 77.2711 | 95.0547 | 79.5401 | 9.5013 | 107.0331 | 3.8533 | 6.4452 | 60.4249 | 116.9753 | 25.8042 | 257.5882 | 129.7371 | 263.8441 | 38.4731 | 77.069 | 15.7185 | 174 | 54.4697 | 0 | 270.687 | 0.010156
8270 | 876.6169 | 4.0996 | 74.806 | 94.8849 | 78.537 | 10.4497 | 113.9051 | 4.6062 | 6.1937 | 61.9065 | 116.7431 | 23.0627 | 257.9386 | 136.9782 | 273.8496 | 39.0038 | 80.4532 | 16.4073 | 181 | 55.2028 | 0 | 262.0406 | 0.0089837
8271 | 884.461 | 4.5537 | 43.8111 | 95.0524 | 78.5399 | 10.45 | 120.3577 | 4.441 | 5.7402 | 59.7704 | 120.4886 | 21.6117 | 259.699 | 137.7704 | 297.4131 | 39.3781 | 81.228 | 16.9954 | 183 | 53.4785 | 0 | 279.6729 | 0.0018203
8272 | 896.2635 | 4.5617 | 23.115 | 98.3155 | 77.5481 | 11.3997 | 121.8795 | 4.4261 | 6.364 | 56.6382 | 127.1101 | 21.1237 | 260.9012 | 154.4116 | 322.0683 | 35.8521 | 78.9461 | 17.5224 | 189 | 52.4683 | 0 | 274.2691 | 0
8273 | 892.9197 | 4.7636 | 19.5192 | 100.5052 | 76.5503 | 12.3497 | 114.8342 | 4.0314 | 7.3867 | 39.6134 | 130.3099 | 17.3626 | 263.3163 | 165.0784 | 325.8708 | 24.9231 | 78.1022 | 17.7118 | 222 | 47.0837 | 0 | 280.7219 | 0
8274 | 884.6115 | 4.9971 | 19.543 | 100.2266 | 78.5464 | 10.4505 | 106.9603 | 4.0449 | 7.4908 | 32.2766 | 118.401 | 16.386 | 264.0964 | 147.751 | 291.3887 | 20.9804 | 78.4081 | 17.0313 | 242 | 47.17 | 0 | 284.0763 | 0
8275 | 866.7108 | 5.4328 | 19.0923 | 98.4515 | 79.5487 | 9.5003 | 105.9655 | 4.5736 | 7.2695 | 31.0822 | 91.0835 | 15.5338 | 257.1417 | 135.7274 | 260.0925 | 22.3273 | 78.6765 | 15.8512 | 196 | 46.3093 | 0 | 277.7877 | 0
8276 | 838.752 | 5.6535 | 18.5457 | 97.8175 | 77.5462 | 11.3995 | 109.1195 | 5.0779 | 6.9735 | 29.5244 | 78.438 | 11.9811 | 247.3525 | 123.5977 | 254.0883 | 22.3294 | 78.3509 | 15.6397 | 192 | 42.2812 | 0 | 270.3695 | 0
8277 | 835.8741 | 4.7568 | 18.6921 | 98.0333 | 78.5437 | 10.4503 | 113.6709 | 5.4094 | 6.923 | 29.0798 | 80.254 | 10.5415 | 236.8882 | 118.0233 | 257.1379 | 22.0319 | 78.6647 | 15.4641 | 187 | 38.8396 | 0 | 261.2176 | 0
8278 | 848.6951 | 5.1315 | 18.4778 | 98.2359 | 77.5438 | 11.3997 | 106.7871 | 5.2308 | 7.026 | 29.267 | 93.7048 | 10.7945 | 228.4054 | 109.7011 | 249.8392 | 21.2964 | 77.3076 | 14.5553 | 192 | 40.2382 | 0 | 259.4567 | 0
8279 | 850.9184 | 4.6423 | 18.5518 | 97.2189 | 79.5403 | 9.5005 | 102.7376 | 4.6471 | 6.888 | 28.4788 | 94.8371 | 10.6459 | 227.4999 | 107.5471 | 249.6208 | 20.0595 | 76.8023 | 14.1057 | 198 | 39.9272 | 0 | 254.2323 | 0
8280 | 830.578 | 3.1695 | 18.6808 | 97.8796 | 78.5417 | 10.4497 | 101.3125 | 4.1503 | 6.9418 | 27.3812 | 78.639 | 10.4452 | 217.9877 | 107.0661 | 248.501 | 19.982 | 76.8244 | 13.8556 | 179 | 37.9979 | 0 | 254.2546 | 0
8281 | 843.1698 | 2.7715 | 18.7696 | 99.185 | 79.547 | 9.5003 | 97.1994 | 4.1043 | 6.7739 | 26.9415 | 72.6814 | 10.7168 | 211.3678 | 102.3415 | 250.3645 | 19.3226 | 77.1748 | 13.4041 | 173 | 38.2494 | 0 | 261.3361 | 0
8282 | 831.5125 | 3.0841 | 18.7294 | 96.9364 | 78.5493 | 10.4497 | 87.5307 | 4.87 | 6.7666 | 27.2316 | 73.4064 | 10.6399 | 212.1116 | 110.6287 | 248.5245 | 17.0104 | 77.5487 | 13.132 | 175 | 36.8938 | 0 | 251.4493 | 0
8283 | 822.0317 | 7.9153 | 18.6342 | 97.1776 | 73.5488 | 15.1987 | 80.2354 | 5.3952 | 6.6742 | 27.0476 | 72.9799 | 10.6239 | 211.2247 | 114.8867 | 257.1162 | 16.2775 | 77.5694 | 12.9482 | 172 | 38.7971 | 0 | 246.98 | 0
8284 | 813.1907 | 9.048 | 18.8375 | 96.9756 | 75.5473 | 13.3005 | 78.3201 | 5.3359 | 6.5269 | 26.7835 | 73.2396 | 10.7087 | 207.5747 | 100.7152 | 256.6512 | 14.5067 | 77.261 | 12.7631 | 157 | 38.9153 | 0 | 241.6797 | 0
8285 | 803.4698 | 5.0653 | 18.8167 | 96.9882 | 73.5502 | 15.1995 | 77.7406 | 5.1988 | 6.6835 | 27.3614 | 73.622 | 10.4291 | 204.7276 | 91.6929 | 235.8768 | 12.6982 | 78.7553 | 12.6747 | 148 | 38.7102 | 0 | 244.05 | 0
8286 | 800.4438 | 3.9238 | 18.6333 | 97.9894 | 78.5464 | 10.4513 | 77.5677 | 4.4989 | 6.932 | 27.3193 | 73.7087 | 10.3145 | 200.9859 | 91.3805 | 220.4729 | 12.061 | 81.1904 | 11.6623 | 132 | 48.1741 | 0 | 243.8424 | 0
8287 | 803.577 | 4.3951 | 18.6372 | 96.9225 | 78.547 | 10.45 | 77.2418 | 4.1362 | 6.9785 | 27.0017 | 74.2756 | 10.3289 | 200.1935 | 91.275 | 217.3541 | 11.3629 | 78.4498 | 11.0677 | 131 | 38.8949 | 0 | 246.5641 | 0
8288 | 798.6003 | 4.2013 | 18.8598 | 95.9152 | 79.542 | 9.5003 | 77.1421 | 4.2991 | 7.0784 | 26.8868 | 75.8841 | 10.4903 | 207.5787 | 91.6065 | 216.4271 | 11.4183 | 77.3145 | 11.2572 | 129 | 34.9628 | 0 | 245.2422 | 0
8289 | 791.4154 | 4.0957 | 18.5742 | 94.8392 | 77.5459 | 11.3995 | 92.3334 | 4.9327 | 6.7635 | 33.2836 | 78.1052 | 9.8275 | 219.59 | 96.3656 | 212.9938 | 12.2948 | 76.5569 | 11.9871 | 125 | 37.077 | 0 | 240.2293 | 0
8290 | 817.9106 | 3.6222 | 18.1904 | 92.6701 | 78.5461 | 10.4503 | 106.9978 | 5.1027 | 6.046 | 43.4523 | 78.6373 | 8.0539 | 232.679 | 98.1968 | 218.2693 | 14.3113 | 75.8939 | 12.9427 | 158 | 38.7918 | 0 | 240.4626 | 0.029743
8291 | 829.8416 | 3.2464 | 18.21 | 93.4109 | 79.5406 | 9.5003 | 114.1971 | 5.0063 | 5.9469 | 51.9454 | 89.5386 | 10.3392 | 244.9904 | 115.6355 | 223.3977 | 14.2508 | 75.4604 | 13.8022 | 150 | 41.5616 | 0 | 244.7997 | 0.066431
8292 | 839.02 | 3.1789 | 18.3088 | 92.3651 | 79.5405 | 9.5 | 114.5735 | 5.5564 | 7.1395 | 55.5352 | 101.8182 | 11.402 | 258.5799 | 119.0706 | 223.2973 | 14.0162 | 75.9363 | 14.7797 | 172 | 40.4725 | 0 | 255.956 | 0.11393
8293 | 846.5089 | 2.8145 | 18.1246 | 91.512 | 79.5398 | 9.5 | 104.6645 | 4.6464 | 6.4003 | 55.5097 | 116.2443 | 11.1608 | 273.2233 | 120.0497 | 223.4865 | 13.4921 | 76.3193 | 15.7389 | 161 | 42.9534 | 0 | 256.6131 | 0.18295
8294 | 854.2684 | 3.0756 | 18.1013 | 93.5999 | 78.5427 | 10.4497 | 103.2266 | 3.8692 | 5.973 | 62.6902 | 120.7342 | 10.9382 | 280.5898 | 127.3074 | 240.6281 | 12.0642 | 78.2576 | 16.0529 | 161 | 47.2234 | 0 | 266.4666 | 0.12634
8295 | 844.1668 | 3.6403 | 18.2632 | 92.4985 | 79.5425 | 9.5003 | 113.8524 | 4.1708 | 5.8753 | 61.7125 | 119.7697 | 9.4838 | 282.4161 | 134.7143 | 263.9849 | 9.5843 | 78.2276 | 16.4679 | 169 | 49.0536 | 0 | 267.3508 | 0.008559
8296 | 875.2759 | 4.5973 | 18.4338 | 94.2127 | 78.5399 | 10.4497 | 121.8751 | 5.0511 | 6.4535 | 54.0991 | 120.0662 | 12.1057 | 282.4531 | 139.2517 | 286.9161 | 9.3621 | 79.1832 | 17.0575 | 169 | 53.2051 | 0 | 275.8631 | 0
8297 | 892.1008 | 4.6523 | 18.5591 | 96.163 | 78.5454 | 10.45 | 121.638 | 5.8955 | 7.345 | 39.9455 | 122.233 | 13.4465 | 279.1142 | 146.3689 | 289.4919 | 9.9291 | 79.9984 | 17.2725 | 161 | 50.6983 | 0 | 286.5749 | 0
8298 | 892.8913 | 4.7037 | 18.7217 | 98.273 | 77.5491 | 11.3997 | 121.836 | 6.0469 | 7.5953 | 34.7407 | 120.4337 | 13.9642 | 266.7236 | 141.4069 | 303.3765 | 9.7803 | 80.7732 | 17.0195 | 147 | 50.2323 | 0 | 289.7372 | 0
8299 | 885.555 | 4.9376 | 18.8953 | 97.9746 | 75.5518 | 13.2995 | 117.8188 | 5.8725 | 7.675 | 32.1312 | 127.6079 | 14.5613 | 259.9793 | 133.5179 | 312.932 | 9.6126 | 82.0278 | 16.2027 | 125 | 46.5868 | 0 | 294.3629 | 0
8300 | 855.5171 | 5.202 | 18.6772 | 95.8898 | 73.5488 | 15.1995 | 105.13 | 5.4919 | 7.9011 | 31.0107 | 137.4296 | 12.0181 | 245.1831 | 124.7387 | 298.8927 | 9.9449 | 81.2622 | 15.4112 | 116 | 42.9828 | 0 | 285.1392 | 0
8301 | 842.0439 | 5.2702 | 18.614 | 93.6851 | 75.5473 | 13.3005 | 100.9799 | 5.6376 | 8.0239 | 30.8254 | 102.7216 | 14.6715 | 235.5777 | 110.2719 | 265.849 | 9.8562 | 78.7197 | 14.9979 | 117 | 44.3086 | 0 | 280.5272 | 0
8302 | 829.3585 | 5.2215 | 18.7099 | 94.5526 | 78.549 | 10.4508 | 95.8618 | 5.6789 | 7.7247 | 30.7399 | 79.0935 | 14.5531 | 230.8037 | 100.5383 | 244.986 | 9.8603 | 77.5725 | 14.5555 | 117 | 41.8521 | 0 | 290.8726 | 0
8303 | 816.4232 | 4.3176 | 19.1264 | 95.4769 | 78.5481 | 10.45 | 95.348 | 6.5231 | 6.9407 | 28.6067 | 72.1201 | 11.0509 | 220.2552 | 97.8161 | 246.0081 | 9.9043 | 76.9668 | 13.7153 | 114 | 37.8986 | 0 | 301.1208 | 0
8304 | 792.2333 | 3.2721 | 18.6375 | 94.0429 | 78.5453 | 10.45 | 102.1886 | 7.2061 | 6.7302 | 26.387 | 69.4376 | 9.9317 | 212.2167 | 92.0979 | 243.6447 | 9.6427 | 76.9678 | 13.1399 | 122 | 35.8669 | 0 | 280.2242 | 0
8305 | 802.7425 | 3.1196 | 18.5192 | 93.5172 | 79.5447 | 9.5003 | 101.2477 | 6.7682 | 6.6989 | 25.9921 | 69.0925 | 9.7719 | 208.891 | 89.3438 | 236.1429 | 9.8078 | 77.7038 | 12.5953 | 116 | 35.1195 | 0 | 285.8122 | 0
8306 | 793.7521 | 3.1388 | 18.8421 | 95.0889 | 78.5483 | 10.4497 | 93.8709 | 6.2091 | 6.5453 | 26.1854 | 69.1968 | 9.5697 | 203.255 | 89.8176 | 233.8264 | 9.8746 | 77.3889 | 11.786 | 118 | 34.7349 | 0 | 267.5066 | 0
8307 | 786.3958 | 3.487 | 18.8789 | 97.5738 | 78.548 | 10.45 | 84.7019 | 6.2021 | 6.8263 | 26.9516 | 69.444 | 9.5614 | 198.1702 | 94.7958 | 237.2871 | 9.7877 | 77.5707 | 11.5065 | 110 | 32.6574 | 0 | 265.491 | 0
8308 | 789.261 | 3.5205 | 19.6485 | 98.9985 | 78.5496 | 10.45 | 78.0038 | 8.1018 | 6.9313 | 27.6863 | 69.4496 | 9.5636 | 195.9732 | 97.363 | 233.2388 | 9.9012 | 77.4603 | 11.5489 | 104 | 33.4536 | 0 | 259.2734 | 0
8309 | 797.7731 | 3.6449 | 21.6505 | 100.4693 | 78.5505 | 10.45 | 67.5147 | 7.7823 | 6.6405 | 28.362 | 70.9022 | 9.5082 | 198.4664 | 93.5814 | 228.1512 | 9.6737 | 78.8579 | 11.5898 | 99 | 33.2483 | 0 | 300.0382 | 0
8310 | 818.8438 | 4.2883 | 27.3715 | 99.3359 | 78.5413 | 10.45 | 74.9345 | 7.0645 | 7.1033 | 30.3641 | 74.3245 | 10.8667 | 209.217 | 95.2399 | 228.6254 | 9.8902 | 80.5148 | 11.703 | 103 | 35.1863 | 0 | 324.3985 | 0
8311 | 858.0145 | 5.4654 | 50.3196 | 102.3449 | 74.5405 | 14.2489 | 93.8174 | 9.1541 | 9.2458 | 53.1629 | 95.7524 | 19.1421 | 251.522 | 151.6783 | 261.539 | 12.2595 | 77.7902 | 14.6262 | 184 | 45.5353 | 0 | 377.4162 | 0
8312 | 902.3664 | 7.2179 | 71.9606 | 107.4482 | 70.6992 | 18.0489 | 108.4941 | 8.6091 | 14.8322 | 98.3716 | 141.9629 | 38.0552 | 307.2196 | 232.8128 | 372.0669 | 26.2187 | 83.445 | 14.6255 | 283 | 55.3127 | 0 | 448.353 | 0
8313 | 1000.2098 | 13.1068 | 83.1034 | 111.9836 | 70.6298 | 18.05 | 132.2022 | 10.5299 | 19.7385 | 110.8789 | 169.8299 | 43.872 | 359.2626 | 300.5856 | 485.8544 | 36.1889 | 95.0453 | 15.3734 | 342 | 71.57 | 0 | 511.6922 | 0
8314 | 1070.4009 | 18.6251 | 88.4071 | 120.8861 | 68.5464 | 19.9495 | 157.6436 | 11.4077 | 21.72 | 113.3513 | 177.5208 | 42.1801 | 408.3516 | 338.3601 | 563.336 | 41.6168 | 105.6748 | 19.5008 | 363 | 80.3634 | 0 | 551.9465 | 0.10975
8315 | 1133.1873 | 19.5542 | 88.6773 | 130.7766 | 67.5446 | 20.8997 | 154.6212 | 10.242 | 24.4823 | 115.4212 | 172.4826 | 44.9579 | 443.6199 | 351.9603 | 604.1973 | 43.4145 | 115.5828 | 20.272 | 360 | 85.0926 | 0 | 596.5692 | 0.15784
8316 | 1169.8854 | 15.5695 | 93.3347 | 133.7686 | 67.5451 | 20.9 | 158.8552 | 12.0411 | 20.6312 | 117.1632 | 174.0775 | 44.1025 | 452.8408 | 367.328 | 602.0761 | 42.8914 | 119.758 | 19.6172 | 341 | 92.8218 | 0 | 608.4961 | 0.18234
8317 | 1147.5759 | 13.518 | 92.5353 | 128.5156 | 67.5464 | 20.9 | 158.2607 | 12.238 | 16.8595 | 112.1443 | 181.7096 | 41.8621 | 462.2091 | 357.5425 | 581.7077 | 43.3511 | 116.7825 | 19.3459 | 339 | 82.0447 | 0 | 611.0424 | 0.10804
8318 | 1161.4189 | 9.8965 | 92.8726 | 130.4346 | 65.5428 | 22.7995 | 157.5953 | 10.7379 | 23.4873 | 112.7074 | 186.7353 | 42.9719 | 471.4473 | 368.6592 | 591.5162 | 43.7705 | 116.74 | 19.9966 | 289 | 83.3756 | 0 | 639.0047 | 0.036437
8319 | 1163.5692 | 7.2316 | 97.327 | 137.4533 | 65.543 | 22.8 | 162.1547 | 9.1456 | 24.078 | 111.3701 | 191.4161 | 42.7596 | 466.6892 | 377.9298 | 596.9053 | 43.1775 | 104.8586 | 21.1716 | 240 | 88.8666 | 0 | 620.7691 | 0.028064
8320 | 1148.3515 | 6.9935 | 96.7912 | 143.7648 | 67.5462 | 20.9005 | 152.6297 | 9.9097 | 15.9575 | 112.2337 | 193.829 | 43.144 | 445.1926 | 377.5922 | 591.0532 | 41.808 | 93.5045 | 21.641 | 249 | 84.6993 | 0 | 620.3346 | 0
8321 | 1139.8963 | 7.0055 | 93.2707 | 136.8046 | 69.55 | 19.0005 | 152.6477 | 9.9312 | 13.1817 | 112.1864 | 193.2975 | 43.5576 | 419.6857 | 352.2857 | 550.4501 | 34.9953 | 92.4715 | 21.1461 | 230 | 74.2611 | 0 | 550.2258 | 0
8322 | 1075.4217 | 7.0125 | 89.579 | 120.084 | 77.545 | 11.4021 | 136.7719 | 8.299 | 10.1498 | 94.857 | 180.3444 | 36.7281 | 377.6067 | 272.6921 | 465.2877 | 19.475 | 85.9521 | 20.0583 | 223 | 77.44 | 0 | 415.7322 | 0
8323 | 1025.5649 | 6.4742 | 86.7618 | 106.9325 | 77.5441 | 11.4 | 124.0944 | 7.412 | 8.0513 | 79.8245 | 145.0554 | 28.2749 | 384.0607 | 199.0355 | 401.2628 | 12.8814 | 77.5373 | 18.532 | 200 | 63.3659 | 0 | 370.1591 | 0
8324 | 978.4384 | 5.8115 | 71.9115 | 101.8263 | 78.5482 | 10.4503 | 116.8121 | 7.4072 | 7.2413 | 71.8545 | 124.4064 | 16.2597 | 413.2766 | 155.9313 | 361.4728 | 11.2647 | 69.6891 | 17.7921 | 180 | 57.118 | 0 | 330.343 | 0
8325 | 941.1719 | 5.3386 | 32.1817 | 98.51 | 78.5487 | 10.45 | 110.9549 | 7.3147 | 6.6658 | 64.228 | 112.1346 | 11.1135 | 396.184 | 129.9851 | 338.5766 | 10.9904 | 63.6673 | 17.0986 | 175 | 48.537 | 0 | 298.733 | 0
8326 | 908.0715 | 5.0178 | 19.2903 | 95.5479 | 78.5498 | 10.45 | 102.3668 | 6.3805 | 6.2592 | 50.6245 | 95.3478 | 9.4249 | 368.118 | 116.1902 | 316.0968 | 10.9362 | 60.6482 | 15.5071 | 163 | 44.3263 | 0 | 284.8529 | 0
8327 | 878.0361 | 4.5773 | 19.162 | 94.4754 | 79.5507 | 9.5003 | 98.4624 | 5.7001 | 6.4467 | 37.2505 | 78.387 | 8.8877 | 348.6129 | 102.3094 | 297.2058 | 10.8256 | 58.3026 | 14.3408 | 138 | 40.8871 | 0 | 284.8488 | 0
8328 | 849.2346 | 3.5133 | 19.1559 | 94.6036 | 78.5514 | 10.4497 | 96.3847 | 5.6458 | 7.3555 | 31.5466 | 72.4872 | 8.8579 | 335.3347 | 96.0751 | 273.6012 | 10.9012 | 57.8001 | 13.917 | 114 | 39.9224 | 0 | 283.135 | 0
8329 | 842.1055 | 3.5405 | 19.0004 | 93.628 | 76.5529 | 12.3495 | 84.0607 | 6.4507 | 7.1612 | 30.231 | 71.8146 | 9.1397 | 335.1212 | 94.6745 | 245.1192 | 10.8159 | 57.9481 | 13.6217 | 110 | 36.6419 | 0 | 285.0021 | 0
8330 | 836.7621 | 3.1058 | 19.0162 | 93.077 | 78.5544 | 10.4505 | 82.5856 | 7.2414 | 6.401 | 30.7023 | 74.2564 | 8.8825 | 338.3885 | 91.7433 | 234.3289 | 10.906 | 57.8341 | 13.2828 | 111 | 34.2149 | 0 | 284.2458 | 0
8331 | 827.0238 | 2.6868 | 19.1084 | 93.5931 | 78.5502 | 10.45 | 79.9938 | 7.0246 | 6.2373 | 31.4205 | 77.5857 | 8.7376 | 335.452 | 89.8222 | 240.1353 | 10.8892 | 57.9657 | 12.5868 | 116 | 34.5638 | 0 | 286.0768 | 0
8332 | 817.0294 | 2.4886 | 19.0834 | 93.2826 | 79.552 | 9.5003 | 68.6931 | 5.8513 | 6.1955 | 31.5104 | 79.2063 | 8.6706 | 328.819 | 88.6402 | 249.5641 | 10.7763 | 58.1733 | 11.8096 | 111 | 34.3889 | 0 | 276.0558 | 0
8333 | 811.2424 | 3.4579 | 19.0886 | 92.9621 | 78.5535 | 10.4497 | 66.3453 | 5.3313 | 6.1127 | 31.7168 | 77.5508 | 8.59 | 331.7751 | 87.6169 | 247.4256 | 10.6334 | 58.863 | 11.5487 | 110 | 34.9 | 0 | 294.8747 | 0
8334 | 817.9662 | 4.2399 | 28.7188 | 92.8177 | 78.5488 | 10.45 | 79.1711 | 5.3331 | 6.176 | 32.4639 | 74.0639 | 11.3767 | 342.1259 | 95.3372 | 246.497 | 10.6607 | 60.9078 | 11.4862 | 133 | 36.4699 | 0 | 340.5791 | 0
8335 | 860.2126 | 5.6558 | 47.8703 | 97.2504 | 73.548 | 15.1987 | 95.3272 | 6.0332 | 11.8287 | 57.727 | 85.424 | 18.1246 | 369.1834 | 180.2601 | 263.6881 | 13.5296 | 58.3577 | 11.4825 | 189 | 41.4405 | 0 | 380.2543 | 0
8336 | 918.7822 | 6.963 | 76.6671 | 103.4017 | 71.5462 | 17.0995 | 109.4044 | 7.1924 | 17.533 | 105.0266 | 127.6746 | 34.8469 | 422.158 | 253.5247 | 381.1261 | 28.2936 | 63.345 | 14.4226 | 275 | 50.117 | 0 | 428.9852 | 0
8337 | 1005.0372 | 7.1473 | 93.2344 | 116.3029 | 68.5417 | 19.9492 | 134.8348 | 7.7316 | 21.6907 | 120.3079 | 161.347 | 42.7363 | 491.4432 | 297.7041 | 492.7802 | 38.2838 | 71.3132 | 18.1358 | 308 | 69.5465 | 0 | 523.0608 | 0
8338 | 1105.4229 | 6.9366 | 101.9841 | 130.3876 | 67.5452 | 20.8997 | 155.6236 | 7.3056 | 22.3954 | 120.3142 | 177.3307 | 42.2115 | 569.3051 | 335.141 | 567.874 | 42.6209 | 83.2436 | 19.1659 | 377 | 78.1707 | 0 | 574.9704 | 0.0064342
8339 | 1138.1662 | 7.6684 | 103.4076 | 138.6421 | 69.5505 | 19.0005 | 160.3876 | 7.2468 | 22.8768 | 122.6586 | 183.8773 | 43.1165 | 604.7286 | 361.0258 | 619.0041 | 41.8929 | 108.8615 | 20.0979 | 384 | 82.2769 | 0 | 604.9002 | 0.022668
8340 | 1167.4066 | 6.8691 | 108.2901 | 140.5169 | 67.5419 | 20.8995 | 156.2832 | 7.9242 | 21.519 | 121.2821 | 186.4847 | 42.435 | 619.1924 | 389.1641 | 617.4429 | 40.9612 | 117.9102 | 20.5244 | 308 | 91.1265 | 0 | 606.8966 | 0.033992
8341 | 1157.3706 | 5.5105 | 107.5202 | 137.7412 | 66.5409 | 21.8497 | 159.5608 | 9.3639 | 18.4687 | 116.228 | 185.3124 | 43.4071 | 609.554 | 378.4652 | 614.9489 | 43.4964 | 117.3685 | 20.4727 | 367 | 85.7395 | 0 | 606.1917 | 0.014131
8342 | 1186.0566 | 5.0331 | 106.4038 | 139.4855 | 69.5443 | 19.0008 | 167.5968 | 10.6059 | 21.0938 | 111.7018 | 191.1979 | 43.8721 | 552.9752 | 383.8464 | 625.3535 | 45.343 | 117.3397 | 20.8347 | 328 | 88.3204 | 0 | 620.0444 | 0.010826
8343 | 1185.5765 | 4.8577 | 106.5266 | 144.4252 | 68.5464 | 19.9497 | 171.9829 | 9.9971 | 21.2902 | 116.3355 | 199.7682 | 41.8176 | 521.27 | 389.3593 | 623.0758 | 45.5521 | 117.9972 | 21.1346 | 305 | 84.4712 | 0 | 608.3104 | 0.0030073
8344 | 1153.6911 | 6.0969 | 105.1226 | 138.3507 | 69.5389 | 19.0055 | 162.6648 | 8.8378 | 21.5453 | 121.7983 | 197.6155 | 39.2345 | 495.4807 | 373.3006 | 608.5878 | 42.8393 | 103.3683 | 21.0694 | 257 | 84.5416 | 0 | 617.0193 | 0
8345 | 1120.6033 | 6.8929 | 101.4317 | 138.0069 | 72.5465 | 16.1455 | 152.8391 | 7.6317 | 21.6107 | 122.0047 | 198.4503 | 38.2008 | 465.3325 | 342.066 | 549.1294 | 36.4386 | 95.3958 | 20.7135 | 246 | 77.8092 | 0 | 539.6668 | 0
8346 | 1032.5615 | 6.6487 | 94.6358 | 124.3626 | 76.5405 | 12.3511 | 143.8527 | 6.4586 | 20.4665 | 102.7466 | 181.8182 | 38.5086 | 435.6637 | 266.29 | 451.1428 | 20.7315 | 85.4413 | 20.1511 | 216 | 67.8252 | 0 | 409.4553 | 0
8347 | 989.5801 | 6.2161 | 91.2087 | 107.6938 | 78.5465 | 10.4505 | 134.7566 | 5.5776 | 15.3946 | 77.4773 | 148.0574 | 29.4992 | 382.0797 | 189.9192 | 404.4337 | 12.8935 | 77.79 | 19.2745 | 196 | 59.5843 | 0 | 368.3553 | 0
8348 | 942.0477 | 5.7454 | 75.1489 | 100.4177 | 77.549 | 11.3997 | 115.9023 | 5.7294 | 9.3127 | 67.3461 | 129.6836 | 14.7286 | 322.6234 | 160.3064 | 362.3345 | 11.8246 | 69.3423 | 18.3063 | 159 | 55.2441 | 0 | 319.7828 | 0
8349 | 894.7913 | 5.0124 | 37.2805 | 96.0254 | 77.5483 | 11.4 | 114.229 | 6.0033 | 7.4175 | 57.7678 | 118.7269 | 9.3303 | 282.6865 | 144.3348 | 316.8257 | 11.5987 | 61.4181 | 16.6738 | 149 | 52.2272 | 0 | 295.5298 | 0
8350 | 871.0165 | 4.6132 | 20.3112 | 94.6773 | 78.5517 | 10.4503 | 102.4561 | 6.7334 | 6.7661 | 42.763 | 99.9151 | 7.9574 | 251.0865 | 135.0952 | 289.2963 | 11.9048 | 58.5434 | 14.5908 | 144 | 49.7608 | 0 | 291.8812 | 0
8351 | 840.2321 | 4.5473 | 18.4584 | 93.6563 | 77.5539 | 11.3997 | 84.4526 | 6.429 | 6.0005 | 30.2617 | 81.4626 | 7.6743 | 229.3746 | 130.5601 | 272.1714 | 11.806 | 56.4726 | 13.9954 | 126 | 46.4816 | 0 | 275.9204 | 0
8352 | 820.9322 | 3.8747 | 18.4115 | 93.162 | 75.5562 | 13.2995 | 95.9537 | 5.8196 | 5.9753 | 27.2526 | 75.1085 | 7.8657 | 220.7627 | 128.0895 | 261.0673 | 11.8107 | 55.0311 | 14.4713 | 111 | 45.3635 | 0 | 275.4271 | 0
8353 | 820.1262 | 3.1566 | 18.3537 | 93.0321 | 77.5545 | 11.4005 | 102.0305 | 5.982 | 6.0988 | 27.3644 | 74.4613 | 7.7504 | 219.2637 | 122.404 | 254.7901 | 11.7533 | 54.7262 | 13.816 | 112 | 45.6098 | 0 | 277.7675 | 0
8354 | 810.7646 | 3.2069 | 18.2907 | 93.8111 | 77.5504 | 11.4 | 82.1921 | 7.3062 | 6.3059 | 28.0239 | 73.7112 | 7.347 | 216.2337 | 113.2212 | 259.2812 | 11.6311 | 55.0098 | 13.2933 | 105 | 39.4343 | 0 | 292.7708 | 0
8355 | 796.7902 | 2.8972 | 18.3721 | 94.6991 | 78.5524 | 10.4503 | 76.1917 | 8.1265 | 5.9192 | 28.027 | 72.6219 | 7.1777 | 212.4071 | 109.8638 | 252.2171 | 11.6917 | 55.0391 | 12.279 | 107 | 37.868 | 0 | 290.956 | 0
8356 | 789.6359 | 2.6923 | 18.3218 | 95.034 | 77.5528 | 11.3997 | 78.986 | 7.0997 | 6.0113 | 28.4733 | 72.4341 | 7.1695 | 211.2 | 109.645 | 239.9883 | 11.6353 | 55.0723 | 11.839 | 106 | 36.2068 | 0 | 286.8172 | 0
8357 | 797.2394 | 3.6188 | 18.5618 | 94.9984 | 76.5533 | 12.3497 | 71.9809 | 6.4175 | 6.3736 | 28.9308 | 73.1444 | 7.3291 | 214.5112 | 108.3051 | 230.0391 | 11.6558 | 56.4319 | 11.8249 | 105 | 35.3518 | 0 | 309.7841 | 0
8358 | 799.251 | 4.6217 | 28.3979 | 94.9087 | 78.5531 | 10.4505 | 76.447 | 7.8016 | 6.9453 | 31.8211 | 76.1765 | 8.601 | 225.2798 | 112.186 | 227.8861 | 11.407 | 58.4734 | 11.8664 | 108 | 36.4239 | 0 | 355.033 | 0
8359 | 842.422 | 6.2797 | 46.7541 | 101.0683 | 73.5517 | 15.1987 | 98.9094 | 7.9656 | 9.3517 | 55.7585 | 92.1645 | 16.3842 | 257.9919 | 163.8525 | 262.0899 | 13.8634 | 55.9137 | 11.8892 | 166 | 40.7284 | 0 | 400.5019 | 0
8360 | 916.676 | 9.3591 | 77.9202 | 104.0338 | 69.5494 | 18.9989 | 118.4619 | 7.5811 | 13.4837 | 102.1662 | 135.762 | 36.7102 | 308.723 | 246.3681 | 399.6041 | 28.6626 | 61.1753 | 14.5915 | 280 | 50.2688 | 0 | 453.2337 | 0
8361 | 974.3262 | 7.6648 | 95.593 | 116.3127 | 67.5447 | 20.8995 | 136.2677 | 9.1647 | 20.833 | 118.1189 | 163.012 | 43.7328 | 373.0239 | 300.9039 | 520.157 | 37.3174 | 69.9379 | 17.7993 | 276 | 69.3341 | 0 | 526.4582 | 0
8362 | 1050.6444 | 5.4488 | 95.543 | 127.4164 | 66.5426 | 21.8497 | 154.7227 | 11.1841 | 23.9323 | 115.2472 | 179.5864 | 43.5413 | 412.7999 | 334.2282 | 574.871 | 43.119 | 78.5295 | 19.4733 | 392 | 76.8303 | 0 | 580.8805 | 0.11337
8363 | 1098.4545 | 5.3919 | 98.888 | 136.357 | 67.5445 | 20.9003 | 152.2338 | 10.3627 | 26.2453 | 120.0379 | 186.0211 | 45.6726 | 444.9619 | 356.6876 | 608.05 | 44.1328 | 89.1783 | 20.5577 | 351 | 76.1437 | 0 | 615.2978 | 0.13775
8364 | 1128.9951 | 13.103 | 108.8062 | 135.3881 | 65.5384 | 22.8058 | 156.0716 | 10.1326 | 24.9072 | 112.5124 | 187.6871 | 44.1066 | 490.4685 | 368.9794 | 613.2395 | 43.94 | 104.9663 | 20.8485 | 318 | 84.6797 | 0 | 616.9186 | 0.16901
8365 | 1147.1066 | 14.5157 | 105.518 | 134.0394 | 68.5523 | 19.9445 | 157.6549 | 11.3964 | 21.4872 | 105.0675 | 186.0652 | 42.6268 | 494.6644 | 365.1048 | 589.7488 | 43.6244 | 103.8878 | 19.7948 | 343 | 76.9324 | 0 | 593.9349 | 0.17705
8366 | 1126.2875 | 15.7356 | 108.0152 | 133.1811 | 69.5414 | 19.0003 | 154.4591 | 11.3103 | 20.685 | 110.0201 | 187.1936 | 43.0362 | 520.1382 | 368.7405 | 598.8455 | 44.6958 | 101.1895 | 19.9388 | 315 | 83.3897 | 0 | 633.8973 | 0.15523
8367 | 1143.2693 | 11.9942 | 106.7424 | 136.4892 | 69.5417 | 19 | 163.6337 | 8.9283 | 19.2219 | 117.6977 | 187.6906 | 43.1796 | 545.7901 | 365.8983 | 598.4352 | 43.0909 | 103.9265 | 20.3037 | 289 | 82.3934 | 0 | 597.7274 | 0.076129
8368 | 1138.633 | 11.1418 | 105.1169 | 140.0554 | 68.538 | 19.9497 | 154.2614 | 8.1564 | 16.9016 | 117.4995 | 186.6456 | 44.7696 | 537.9266 | 354.2549 | 583.8913 | 40.517 | 106.541 | 20.3881 | 271 | 83.3267 | 0 | 597.5102 | 0
8369 | 1108.1871 | 9.1185 | 101.196 | 134.3761 | 68.5382 | 19.95 | 144.2192 | 9.537 | 18.0475 | 107.9105 | 187.7744 | 44.5322 | 487.6045 | 322.1893 | 548.8044 | 34.2334 | 106.0837 | 20.0155 | 235 | 78.2665 | 0 | 533.1167 | 0
8370 | 1043.3576 | 7.3844 | 96.9644 | 121.0887 | 77.5439 | 11.4024 | 137.5225 | 9.5838 | 18.059 | 86.8872 | 184.0729 | 42.3871 | 491.7563 | 256.7818 | 454.2808 | 20.3907 | 102.7772 | 18.8756 | 205 | 69.6154 | 0 | 416.5706 | 0
8371 | 976.2015 | 6.2813 | 88.3713 | 108.6642 | 78.5446 | 10.4503 | 122.8733 | 7.8431 | 14.7063 | 68.0841 | 154.5888 | 33.7782 | 503.7248 | 209.3524 | 385.877 | 13.6659 | 80.1089 | 17.4956 | 193 | 63.4908 | 0 | 385.6618 | 0
8372 | 935.0812 | 5.6452 | 74.6229 | 103.211 | 76.548 | 12.3495 | 112.7758 | 8.0076 | 9.9712 | 61.719 | 133.5192 | 19.0596 | 377.6063 | 187.1969 | 364.0107 | 12.6868 | 62.663 | 16.8518 | 188 | 56.7145 | 0 | 329.3116 | 0
8373 | 911.8905 | 5.1505 | 35.0672 | 100.3338 | 78.5489 | 10.4505 | 101.6421 | 8.9467 | 7.8393 | 58.0851 | 120.588 | 14.377 | 285.8345 | 158.0325 | 322.3881 | 11.3641 | 57.4417 | 15.8796 | 170 | 49.3569 | 0 | 308.112 | 0
8374 | 876.8671 | 4.8835 | 20.2049 | 102.0308 | 79.5512 | 9.5003 | 88.247 | 7.4417 | 7.3963 | 48.2109 | 100.1493 | 12.3884 | 247.8659 | 136.3654 | 295.65 | 10.8681 | 56.2127 | 14.6071 | 160 | 43.2879 | 0 | 309.6675 | 0
8375 | 857.4936 | 5.3784 | 19.315 | 101.7104 | 77.5539 | 11.3995 | 84.2486 | 8.7182 | 6.7444 | 39.3547 | 80.9036 | 10.0482 | 230.6075 | 120.2779 | 282.4047 | 10.9742 | 56.2471 | 13.9476 | 134 | 40.4048 | 0 | 319.4068 | 0
8376 | 842.9731 | 3.8811 | 19.1027 | 97.5069 | 78.5499 | 10.4503 | 84.9956 | 8.2969 | 6.1967 | 36.0436 | 74.9127 | 9.4548 | 221.8993 | 108.2945 | 256.4756 | 10.8859 | 56.2811 | 13.7778 | 125 | 38.2543 | 0 | 310.3312 | 0
8377 | 831.3548 | 6.0211 | 19.2389 | 97.4229 | 78.5549 | 10.45 | 91.0442 | 7.6581 | 6.1915 | 37.037 | 72.7568 | 8.8116 | 219.5654 | 103.4935 | 251.0208 | 10.9996 | 56.449 | 13.4319 | 118 | 35.4625 | 0 | 306.369 | 0
8378 | 831.2262 | 8.9633 | 19.2068 | 97.642 | 79.5523 | 9.5003 | 81.7581 | 9.2757 | 6.4216 | 37.1545 | 71.3336 | 8.3405 | 215.8697 | 100.8973 | 251.2146 | 10.7701 | 56.5709 | 12.8648 | 115 | 36.9041 | 0 | 300.9661 | 0
8379 | 817.7731 | 9.6668 | 19.1718 | 95.9175 | 78.5542 | 10.4497 | 69.1466 | 7.8982 | 6.653 | 37.568 | 71.6745 | 8.8021 | 213.8176 | 97.3016 | 246.5315 | 10.7273 | 56.1375 | 11.9846 | 113 | 36.1588 | 0 | 298.2251 | 0
8380 | 842.8021 | 6.8405 | 18.9993 | 94.7112 | 78.5524 | 10.45 | 82.8619 | 9.3953 | 9.2131 | 52.7547 | 89.2094 | 15.1551 | 242.0669 | 92.1405 | 271.3908 | 10.6458 | 55.3334 | 12.5343 | 102 | 34.1664 | 0 | 300.0836 | 0
8381 | 855.4522 | 5.4922 | 34.2284 | 97.1418 | 76.8028 | 12.1095 | 89.7996 | 10.4573 | 10.198 | 59.1547 | 97.3413 | 17.7472 | 253.9394 | 137.0223 | 283.4131 | 14.6688 | 57.2835 | 12.9192 | 104 | 40.7136 | 0 | 394.5741 | 0
8382 | 855.4522 | 5.4922 | 43.1823 | 98.4579 | 76.7988 | 12.1133 | 89.7996 | 10.4573 | 10.198 | 59.1547 | 97.3413 | 17.7472 | 253.9394 | 164.4028 | 283.4131 | 17.0889 | 58.5473 | 12.9192 | 106 | 41.2877 | 0 | 416.7602 | 0
8383 | 855.4522 | 5.4922 | 43.1823 | 98.4579 | 76.7988 | 12.1133 | 89.7996 | 10.4573 | 10.198 | 59.1547 | 97.3413 | 17.7472 | 253.9394 | 164.4028 | 283.4131 | 17.0889 | 58.5473 | 12.9192 | 159 | 41.2877 | 0 | 416.7602 | 0
8384 | 855.4522 | 5.4922 | 43.1823 | 98.4579 | 76.7988 | 12.1133 | 89.7996 | 10.4573 | 10.198 | 59.1547 | 97.3413 | 17.7472 | 253.9394 | 164.4028 | 283.4131 | 17.0889 | 58.5473 | 12.9192 | 259 | 41.2877 | 0 | 416.7602 | 0
8385 | 955.4284 | 7.7177 | 78.2114 | 113.3362 | 66.541 | 21.8574 | 117.4685 | 15.068 | 18.8699 | 84.9381 | 154.0114 | 32.2601 | 353.5014 | 267.2587 | 437.3288 | 31.4166 | 71.0346 | 16.9773 | 278 | 70.4909 | 0 | 565.0742 | 0
8386 | 1072.6746 | 10.9368 | 94.4473 | 121.1355 | 69.5468 | 19.0008 | 144.7945 | 17.725 | 21.9727 | 97.4747 | 186.9467 | 39.9462 | 449.3425 | 329.2955 | 571.191 | 40.7809 | 82.4372 | 17.9275 | 315 | 76.2189 | 0 | 603.7282 | 0.048184
8387 | 1113.8832 | 16.1692 | 102.1189 | 137.524 | 69.546 | 19 | 148.1466 | 18.3711 | 20.664 | 99.3926 | 195.2582 | 42.7094 | 480.3513 | 350.9971 | 594.6687 | 42.8975 | 87.7008 | 18.6918 | 332 | 78.3202 | 0 | 598.6728 | 0.073394
8388 | 1144.2829 | 14.1231 | 105.0346 | 142.7373 | 68.5357 | 19.9553 | 145.0744 | 18.7082 | 19.0287 | 100.5654 | 194.9443 | 42.2513 | 474.3181 | 359.4053 | 610.1397 | 43.3484 | 90.8377 | 19.425 | 336 | 76.7625 | 0 | 611.8973 | 0.039386
8389 | 1163.1427 | 11.5239 | 107.34 | 137.7876 | 69.5524 | 18.9947 | 151.4071 | 18.588 | 16.6426 | 103.8762 | 199.7077 | 42.1358 | 468.0833 | 361.1908 | 616.5848 | 44.3389 | 90.4672 | 19.5524 | 341 | 69.3721 | 0 | 603.7583 | 0.018563
8390 | 1173.7812 | 11.1992 | 107.0436 | 139.3167 | 68.552 | 19.9497 | 148.8831 | 18.9851 | 20.9522 | 115.6412 | 203.3417 | 45.2931 | 472.4365 | 366.4833 | 615.6837 | 44.4665 | 91.5969 | 19.3044 | 296 | 71.4569 | 0 | 625.4791 | 0.015063
8391 | 1174.8252 | 10.3102 | 105.8578 | 143.7585 | 68.5484 | 19.95 | 158.809 | 18.8242 | 22.5597 | 122.6255 | 205.6513 | 44.2214 | 480.1652 | 372.6414 | 619.2783 | 42.7733 | 92.7931 | 19.7352 | 237 | 72.3203 | 0 | 619.6088 | 0.002041
8392 | 1149.545 | 9.1023 | 104.718 | 142.9709 | 69.543 | 19.0003 | 151.0901 | 18.2004 | 15.1447 | 114.6149 | 208.7157 | 39.9414 | 464.821 | 370.1281 | 599.6943 | 40.9106 | 93.4636 | 20.545 | 237 | 73.8281 | 0 | 605.6019 | 0
8393 | 1131.1163 | 8.9848 | 103.1641 | 141.479 | 76.5465 | 12.3518 | 142.6644 | 18.8611 | 10.0497 | 102.4775 | 208.2942 | 36.565 | 440.0249 | 339.8424 | 539.4244 | 35.1877 | 90.8695 | 20.9766 | 245 | 67.0078 | 0 | 529.5091 | 0
8394 | 1086.5302 | 8.9473 | 96.9435 | 130.0106 | 74.5487 | 14.2495 | 134.1003 | 17.2173 | 8.2699 | 93.2559 | 196.3914 | 34.1879 | 399.2882 | 272.0162 | 467.0332 | 22.6451 | 83.4904 | 20.7897 | 219 | 58.7381 | 0 | 411.6633 | 0
8395 | 1008.3726 | 8.4447 | 93.55 | 114.8298 | 78.5485 | 10.4511 | 108.488 | 14.875 | 9.6863 | 72.7254 | 163.0143 | 27.8289 | 346.2091 | 194.3506 | 414.222 | 15.2308 | 75.1003 | 19.1861 | 199 | 54.439 | 0 | 378.7329 | 0
8396 | 969.7718 | 6.0414 | 79.788 | 105.8566 | 78.5565 | 10.45 | 96.2458 | 9.2489 | 7.9077 | 65.3795 | 141.3294 | 13.4197 | 303.1973 | 165.8728 | 359.7976 | 11.6736 | 66.167 | 17.0135 | 176 | 50.1767 | 0 | 326.4554 | 0
8397 | 935.3332 | 4.7875 | 39.7253 | 100.2059 | 79.5517 | 9.5003 | 99.9386 | 11.8638 | 7.1255 | 62.2335 | 129.8008 | 7.9631 | 283.4454 | 153.5588 | 312.2379 | 10.5873 | 62.2606 | 15.3572 | 163 | 46.3927 | 0 | 318.9735 | 0
8398 | 899.4519 | 4.6392 | 26.1159 | 98.6335 | 78.5514 | 10.4497 | 87.2382 | 14.0522 | 7.1491 | 51.9693 | 111.2076 | 7.7546 | 258.4286 | 135.7502 | 281.305 | 10.5296 | 60.6441 | 14.6488 | 149 | 41.985 | 0 | 337.5236 | 0
8399 | 868.0007 | 4.0885 | 25.9701 | 98.0683 | 79.5522 | 9.5003 | 89.8934 | 14.1079 | 6.5319 | 49.6427 | 91.5968 | 7.8495 | 243.5343 | 110.8072 | 265.9392 | 10.2969 | 60.2372 | 14.3471 | 139 | 40.9433 | 0 | 318.4751 | 0
8400 | 852.4285 | 5.2633 | 26.0593 | 97.0985 | 78.5551 | 10.4497 | 98.8175 | 14.3787 | 6.8375 | 47.1101 | 84.5749 | 8.2804 | 234.3619 | 101.8231 | 249.1165 | 10.572 | 60.1341 | 14.0185 | 124 | 40.8409 | 0 | 305.9222 | 0
8401 | 846.0215 | 8.7742 | 26.3047 | 96.448 | 78.5542 | 10.45 | 78.8596 | 10.4346 | 7.1575 | 40.3678 | 84.9663 | 8.1253 | 222.0895 | 96.4527 | 232.6669 | 10.5774 | 60.0135 | 13.4707 | 112 | 38.712 | 0 | 298.9695 | 0
8402 | 839.6282 | 9.9836 | 26.6261 | 96.1983 | 79.5559 | 9.5003 | 73.1553 | 11.1486 | 7.5384 | 36.6531 | 84.718 | 7.7447 | 215.8654 | 96.7087 | 240.4964 | 10.3496 | 59.4293 | 12.425 | 105 | 41.0178 | 0 | 293.228 | 0
8403 | 822.7046 | 10.2764 | 26.2625 | 94.5469 | 78.5567 | 10.4497 | 78.9278 | 13.6454 | 7.2064 | 35.2519 | 82.7011 | 9.3272 | 212.4365 | 93.4269 | 250.06 | 10.4105 | 58.7901 | 11.8994 | 104 | 38.422 | 0 | 285.4827 | 0
8404 | 807.1199 | 5.9754 | 25.9535 | 93.6007 | 79.5568 | 9.5003 | 74.6193 | 14.5105 | 6.532 | 34.6923 | 81.7929 | 8.3612 | 209.5073 | 88.9619 | 245.1779 | 10.192 | 58.6473 | 11.8806 | 104 | 35.6193 | 0 | 289.6333 | 0
8405 | 796.4428 | 3.6889 | 25.8695 | 94.2789 | 78.5582 | 10.4497 | 67.0089 | 10.4708 | 6.5518 | 34.7783 | 82.4195 | 7.6107 | 212.4187 | 86.4835 | 230.4762 | 10.405 | 60.3528 | 11.8733 | 102 | 34.4141 | 0 | 319.9392 | 0
8406 | 817.8391 | 4.4513 | 32.1711 | 95.076 | 79.5538 | 9.5003 | 80.6877 | 11.0766 | 7.1634 | 36.8006 | 84.9972 | 10.9537 | 222.6371 | 94.0988 | 227.4876 | 10.4104 | 62.6851 | 11.853 | 103 | 35.6153 | 0 | 352.341 | 0
8407 | 842.3574 | 6.0145 | 40.6286 | 101.9273 | 77.5499 | 11.3995 | 97.2874 | 13.3877 | 9.8855 | 57.6102 | 100.0077 | 20.9288 | 251.8398 | 152.5719 | 264.3315 | 12.9383 | 59.7509 | 11.8406 | 152 | 40.0614 | 0 | 396.9882 | 0
8408 | 899.2222 | 8.1074 | 71.9286 | 101.9041 | 69.5485 | 18.9979 | 108.6268 | 14.4949 | 12.729 | 98.0078 | 152.7187 | 36.8281 | 304.7884 | 231.6563 | 366.4305 | 28.1695 | 63.5205 | 13.9331 | 252 | 49.0311 | 0 | 451.6163 | 0
8409 | 971.6533 | 13.5779 | 97.6762 | 114.9021 | 70.5381 | 18.0553 | 128.5825 | 16.1526 | 18.8637 | 111.8397 | 185.2156 | 42.6352 | 362.6284 | 288.119 | 470.0106 | 37.2017 | 74.0016 | 17.8815 | 282 | 58.4098 | 0 | 519.746 | 0
8410 | 1062.1549 | 15.1719 | 105.0363 | 124.2376 | 69.5465 | 18.9947 | 142.6317 | 17.1055 | 20.3585 | 109.213 | 192.1542 | 37.6429 | 411.8394 | 327.7392 | 568.5607 | 41.3925 | 83.5224 | 18.6728 | 356 | 63.7926 | 0 | 558.0747 | 0.0085748
8411 | 1120.7111 | 8.7952 | 104.1343 | 128.7837 | 67.5501 | 20.8995 | 140.5211 | 13.0594 | 20.4935 | 104.4213 | 193.5315 | 33.5515 | 419.3499 | 358.3034 | 612.5094 | 42.1273 | 90.7193 | 18.986 | 345 | 67.3391 | 0 | 593.726 | 0.013853
8412 | 1143.7043 | 4.9221 | 112.0082 | 131.8229 | 70.5449 | 18.0558 | 145.9059 | 16.9483 | 19.0472 | 102.6267 | 192.2415 | 32.2569 | 420.561 | 375.5865 | 583.7092 | 40.6618 | 97.5577 | 19.3532 | 309 | 67.7741 | 0 | 605.5677 | 0.016951
8413 | 1132.314 | 5.2294 | 111.522 | 130.7625 | 69.5558 | 18.9947 | 151.3985 | 18.3589 | 10.325 | 94.2877 | 189.9008 | 30.7443 | 415.2031 | 368.8347 | 560.2128 | 41.4665 | 108.1315 | 19.6414 | 384 | 65.3269 | 0 | 591.7862 | 0.013625
8414 | 1134.3003 | 5.1078 | 110.3309 | 135.3609 | 69.5512 | 19 | 148.1105 | 13.4781 | 7.3057 | 93.8605 | 192.4982 | 33.6217 | 418.8221 | 368.6758 | 560.3542 | 42.6436 | 101.6176 | 20.0223 | 299 | 69.8726 | 0 | 605.5698 | 0.0088836
8415 | 1137.8445 | 5.1853 | 106.7817 | 139.1822 | 68.5493 | 19.9497 | 152.6727 | 9.8482 | 7.2432 | 91.3658 | 196.9962 | 34.2638 | 428.3104 | 366.8504 | 561.0099 | 41.9657 | 98.9715 | 20.4195 | 261 | 68.3345 | 0 | 590.6164 | 0.0022104
8416 | 1097.1978 | 6.3232 | 101.3763 | 137.2392 | 70.5473 | 18.0505 | 145.3228 | 8.721 | 8.6777 | 91.1686 | 203.7453 | 36.1422 | 421.1798 | 356.0011 | 564.2871 | 40.8948 | 107.8043 | 20.945 | 258 | 64.784 | 0 | 591.0692 | 0
8417 | 1063.8308 | 6.7842 | 96.7335 | 136.6397 | 77.5477 | 11.4018 | 130.6921 | 8.1885 | 9.5982 | 87.4228 | 199.5765 | 32.695 | 396.4439 | 319.94 | 522.8785 | 27.4944 | 106.1836 | 20.794 | 260 | 62.1973 | 0 | 481.7088 | 0
8418 | 1023.6576 | 6.542 | 84.1192 | 122.1835 | 77.5517 | 11.4 | 125.4124 | 7.6195 | 8.3764 | 86.0797 | 186.7111 | 31.7951 | 345.6585 | 252.4657 | 429.7277 | 17.5807 | 99.5328 | 20.1493 | 234 | 57.4344 | 0 | 387.2606 | 0
8419 | 972.305 | 5.8436 | 45.2463 | 103.75 | 77.5519 | 11.4 | 106.411 | 6.9233 | 7.6608 | 66.4646 | 154.7335 | 26.9021 | 291.1018 | 189.3917 | 349.7614 | 13.3467 | 93.0241 | 19.404 | 204 | 53.411 | 0 | 348.4182 | 0
8420 | 921.4058 | 5.0253 | 28.2134 | 96.0846 | 77.5486 | 11.4 | 90.0763 | 6.5883 | 7.7554 | 57.1589 | 128.3675 | 13.3431 | 256.1446 | 154.0664 | 307.7072 | 12.8464 | 81.8972 | 18.0821 | 186 | 46.5773 | 0 | 319.2951 | 0
8421 | 897.2639 | 5.1368 | 26.6133 | 94.2517 | 79.5525 | 9.5005 | 81.7943 | 5.8683 | 8.167 | 55.9786 | 106.443 | 8.4854 | 241.982 | 132.7092 | 288.9041 | 12.5214 | 61.4592 | 17.108 | 174 | 43.5313 | 0 | 296.4704 | 0
8422 | 863.1398 | 4.8725 | 26.3229 | 93.8612 | 78.5535 | 10.4497 | 76.0589 | 5.7647 | 7.7768 | 49.0359 | 91.4244 | 8.333 | 227.7832 | 119.0407 | 264.6001 | 11.3382 | 55.7269 | 16.1523 | 177 | 40.1022 | 0 | 289.1474 | 0
8423 | 857.3335 | 4.6506 | 26.0501 | 93.7188 | 78.5481 | 10.45 | 83.5971 | 5.7555 | 7.044 | 41.5019 | 85.6598 | 8.2512 | 217.559 | 113.9711 | 253.5441 | 10.7401 | 55.1489 | 15.7209 | 160 | 37.1322 | 0 | 291.9024 | 0
8424 | 833.3983 | 3.6533 | 26.1929 | 93.353 | 79.5501 | 9.5029 | 82.7045 | 6.3213 | 6.8274 | 39.2227 | 83.6796 | 8.2409 | 218.1708 | 104.9886 | 256.2999 | 10.7184 | 55.2756 | 15.1622 | 150 | 36.3346 | 0 | 297.6001 | 0
8425 | 842.4133 | 3.0454 | 26.509 | 93.2478 | 78.5591 | 10.4471 | 71.5101 | 6.8436 | 6.6845 | 38.2434 | 82.2885 | 8.1456 | 214.1707 | 99.6384 | 256.4259 | 10.915 | 55.1261 | 14.0324 | 126 | 37.3837 | 0 | 301.1241 | 0
8426 | 838.0364 | 2.9821 | 26.46 | 93.7031 | 79.5547 | 9.5003 | 68.9346 | 7.2534 | 6.6943 | 34.321 | 83.1506 | 8.0188 | 207.253 | 94.5946 | 255.6516 | 10.7603 | 55.1325 | 12.7382 | 125 | 36.5159 | 0 | 297.8149 | 0
8427 | 830.1118 | 2.8385 | 26.2262 | 93.3619 | 77.5587 | 11.3995 | 75.7609 | 6.3591 | 6.3121 | 32.4001 | 83.4007 | 8.3989 | 204.1201 | 94.3 | 264.94 | 10.8207 | 54.849 | 12.0001 | 130 | 35.0388 | 0 | 290.9768 | 0
8428 | 834.018 | 2.869 | 26.2355 | 93.0755 | 78.5582 | 10.4503 | 71.7649 | 5.7144 | 6.1643 | 31.8167 | 83.3188 | 8.4904 | 201.5484 | 92.0573 | 260.671 | 10.837 | 54.7571 | 11.6938 | 126 | 37.9952 | 0 | 289.3154 | 0
8429 | 831.8092 | 3.2738 | 26.3204 | 93.2582 | 78.556 | 10.45 | 65.2396 | 5.6823 | 6.3348 | 33.0615 | 84.0672 | 8.1413 | 199.6936 | 88.9093 | 247.8195 | 10.683 | 56.6204 | 11.588 | 127 | 36.2178 | 0 | 294.3507 | 0
8430 | 836.0598 | 3.9921 | 26.3123 | 93.2276 | 78.5541 | 10.45 | 75.2719 | 6.1848 | 6.5075 | 34.134 | 84.5674 | 7.9534 | 194.9953 | 85.681 | 233.3333 | 10.8198 | 58.8563 | 11.594 | 115 | 34.0163 | 0 | 291.8894 | 0
8431 | 845.4092 | 4.1015 | 41.7631 | 93.5603 | 79.5523 | 9.5003 | 75.9814 | 6.8753 | 6.8008 | 33.2905 | 84.1308 | 7.9176 | 193.8648 | 88.6315 | 234.0605 | 10.7163 | 55.2538 | 11.5947 | 107 | 35.9524 | 0 | 295.8093 | 0
8432 | 864.7106 | 4.2673 | 53.62 | 93.0161 | 78.5518 | 10.4497 | 79.5053 | 7.3652 | 6.728 | 32.4928 | 92.3406 | 9.7825 | 201.4858 | 87.706 | 235.9596 | 13.8079 | 53.8272 | 11.8674 | 107 | 44.5826 | 0 | 297.9849 | 0
8433 | 867.4634 | 4.2337 | 61.0042 | 92.5604 | 77.5539 | 11.3997 | 99.0814 | 6.4226 | 6.4378 | 41.6285 | 108.6772 | 15.505 | 210.2474 | 101.3349 | 227.6904 | 24.1325 | 53.8647 | 13.042 | 108 | 50.821 | 0 | 297.5906 | 0
8434 | 879.2615 | 3.3984 | 74.6681 | 90.204 | 76.5508 | 12.3497 | 95.4119 | 6.9405 | 5.5545 | 60.2518 | 123.7324 | 16.6259 | 217.4709 | 110.4508 | 224.1135 | 27.1643 | 52.9161 | 13.3705 | 113 | 51.9066 | 0 | 286.5734 | 0.0047045
8435 | 897.5012 | 2.764 | 84.0694 | 89.8267 | 78.5473 | 10.4505 | 91.2851 | 7.2637 | 6.0427 | 68.3925 | 143.7131 | 17.4538 | 229.8373 | 112.6206 | 240.7208 | 27.2588 | 52.6837 | 13.4202 | 120 | 54.0131 | 0 | 292.576 | 0.0087587
8436 | 902.7659 | 2.7634 | 85.2046 | 91.4298 | 79.5492 | 9.5003 | 92.8274 | 7.1382 | 6.2812 | 70.1459 | 135.1876 | 17.9585 | 243.0651 | 119.0683 | 245.5583 | 27.1992 | 53.0725 | 13.7744 | 130 | 56.5658 | 0 | 299.9165 | 0.016691
8437 | 906.6405 | 2.8786 | 87.0313 | 93.3577 | 78.5466 | 10.4497 | 92.9978 | 6.4702 | 5.4364 | 69.8845 | 130.1652 | 17.9417 | 245.6914 | 137.4363 | 246.5733 | 27.238 | 53.4957 | 14.4491 | 126 | 56.9026 | 0 | 291.0416 | 0.013717
8438 | 895.7156 | 3.0849 | 77.3938 | 92.8137 | 79.5441 | 9.5029 | 92.1251 | 6.3384 | 5.0012 | 67.478 | 131.7373 | 18.1492 | 246.671 | 141.2711 | 249.976 | 27.2178 | 53.5262 | 15.5857 | 130 | 54.3276 | 0 | 297.3202 | 0.0093943
8439 | 917.3345 | 3.6719 | 38.6791 | 93.0918 | 78.5509 | 10.4471 | 96.1057 | 5.6949 | 5.3578 | 64.1474 | 131.2293 | 19.0277 | 250.8267 | 144.6902 | 270.204 | 27.0811 | 56.0363 | 16.1562 | 143 | 53.7446 | 0 | 305.0122 | 0.0030459
8440 | 915.3759 | 4.3702 | 25.6821 | 97.4156 | 79.5497 | 9.5003 | 103.2931 | 5.3939 | 6.4035 | 61.7447 | 136.5657 | 20.3606 | 262.9034 | 140.8004 | 296.8132 | 24.1447 | 58.5156 | 16.5483 | 149 | 47.645 | 0 | 310.6925 | 0
8441 | 925.8305 | 4.9353 | 25.6592 | 99.1833 | 78.5505 | 10.4497 | 99.5328 | 5.2717 | 6.6096 | 42.9672 | 138.3615 | 12.3289 | 265.902 | 139.2519 | 300.2564 | 13.9618 | 56.2263 | 16.4447 | 153 | 45.0972 | 0 | 313.8227 | 0
8442 | 902.7559 | 4.9652 | 25.6375 | 99.7122 | 79.549 | 9.5029 | 95.0391 | 5.3863 | 7.0237 | 34.6536 | 127.9544 | 8.6244 | 258.7126 | 142.1573 | 288.1663 | 10.7171 | 54.8908 | 16.1277 | 139 | 44.2913 | 0 | 308.6882 | 0
8443 | 882.4469 | 4.4993 | 25.6769 | 98.7909 | 77.5585 | 11.3968 | 88.3869 | 6.1193 | 8.5273 | 33.9364 | 106.2664 | 8.4045 | 249.7435 | 141.9029 | 284.6642 | 10.673 | 55.0968 | 15.0953 | 138 | 41.5094 | 0 | 299.1305 | 0
8444 | 873.106 | 4.4988 | 25.3986 | 97.5404 | 74.5512 | 14.2492 | 89.1877 | 5.9928 | 8.2803 | 32.4631 | 95.4803 | 8.4771 | 242.983 | 137.2171 | 271.306 | 10.5749 | 55.0517 | 14.3469 | 136 | 41.2171 | 0 | 293.0054 | 0
8445 | 865.2919 | 4.5066 | 25.2944 | 96.1958 | 79.5503 | 9.5013 | 80.9742 | 5.7639 | 8.0517 | 33.1203 | 98.2404 | 9.3359 | 236.3216 | 119.7658 | 256.671 | 10.6644 | 56.7796 | 13.6091 | 139 | 39.8246 | 0 | 282.3371 | 0
8446 | 838.237 | 4.7805 | 25.4101 | 94.3392 | 78.5504 | 10.4526 | 76.864 | 5.556 | 7.4565 | 32.1096 | 96.2479 | 8.9089 | 222.0824 | 114.4388 | 244.3855 | 9.7792 | 57.3298 | 12.5042 | 140 | 38.1195 | 0 | 278.9927 | 0
8447 | 825.4662 | 4.1774 | 25.3298 | 93.1273 | 79.5558 | 9.4974 | 78.7815 | 4.896 | 7.038 | 32.3704 | 86.8334 | 8.3221 | 211.4455 | 106.4893 | 243.2223 | 9.5602 | 55.3245 | 12.4032 | 138 | 36.5324 | 0 | 286.9185 | 0
8448 | 821.414 | 3.1598 | 25.3224 | 93.3965 | 78.5553 | 10.4497 | 87.9922 | 4.9617 | 6.8881 | 32.8804 | 83.635 | 8.2376 | 207.7706 | 103.3906 | 243.2142 | 9.5185 | 54.1249 | 12.3899 | 118 | 38.426 | 0 | 274.817 | 0
8449 | 819.4242 | 2.8433 | 25.3691 | 93.4659 | 79.5534 | 9.5029 | 87.8622 | 4.9504 | 6.6625 | 32.434 | 81.9852 | 8.1759 | 207.5185 | 98.9316 | 236.6873 | 10.1396 | 53.9868 | 12.8378 | 118 | 34.7375 | 0 | 282.7826 | 0
8450 | 820.0213 | 2.9755 | 25.3485 | 93.9444 | 79.56 | 9.4974 | 77.8461 | 5.477 | 6.2789 | 31.3572 | 81.4411 | 8.0226 | 206.7629 | 93.4068 | 240.7699 | 10.4705 | 54.5667 | 13.0095 | 114 | 33.8979 | 0 | 277.6425 | 0
8451 | 817.8166 | 3.526 | 25.3988 | 93.5233 | 73.5549 | 15.1984 | 74.2383 | 5.7691 | 6.1793 | 30.9216 | 81.4908 | 7.9886 | 206.2434 | 90.1711 | 243.8894 | 9.9574 | 54.9377 | 12.6429 | 109 | 33.8367 | 0 | 277.7999 | 0
8452 | 808.9895 | 3.0856 | 25.5523 | 93.329 | 75.5552 | 13.3005 | 74.0052 | 5.7509 | 6.1842 | 31.0424 | 81.5408 | 8.5803 | 207.6193 | 86.8743 | 240.2175 | 10.3746 | 55.2263 | 12.4818 | 105 | 35.5785 | 0 | 272.1798 | 0
8453 | 811.6597 | 3.2317 | 25.4745 | 94.5128 | 76.5584 | 12.3503 | 73.8059 | 6.2504 | 6.0589 | 31.0932 | 81.6268 | 8.272 | 207.001 | 84.7826 | 233.7518 | 10.4971 | 55.6704 | 12.4667 | 106 | 40.085 | 0 | 275.9508 | 0
8454 | 803.3457 | 3.9129 | 25.4398 | 93.1438 | 78.5586 | 10.4505 | 73.5907 | 5.5581 | 6.2236 | 30.9158 | 81.6813 | 8.5555 | 205.0317 | 84.5636 | 234.4723 | 10.3893 | 59.0648 | 12.0956 | 102 | 45.2724 | 0 | 280.0033 | 0
8455 | 817.5812 | 4.1538 | 25.4219 | 91.7526 | 78.5534 | 10.45 | 70.9929 | 5.0474 | 6.5405 | 30.8599 | 83.923 | 8.1293 | 204.7253 | 85.9593 | 227.6266 | 10.601 | 55.9252 | 11.9208 | 105 | 41.2687 | 0 | 271.5636 | 0
8456 | 816.9006 | 3.9878 | 25.3566 | 93.373 | 74.5542 | 14.2489 | 74.2489 | 5.0685 | 6.6579 | 30.8013 | 86.4312 | 7.7984 | 211.045 | 90.2909 | 222.315 | 10.3519 | 53.8922 | 12.1547 | 101 | 40.9254 | 0 | 276.0841 | 0
8457 | 807.9361 | 3.6481 | 25.2697 | 92.5323 | 76.5535 | 12.3505 | 85.6389 | 5.4812 | 6.1298 | 40.1931 | 86.8419 | 7.1903 | 215.894 | 96.1161 | 226.1958 | 10.1698 | 53.0859 | 12.9107 | 105 | 42.0212 | 0 | 275.4155 | 0
8458 | 821.5855 | 2.99 | 25.0821 | 90.0774 | 76.5514 | 12.35 | 82.9778 | 5.7832 | 5.3477 | 51.6577 | 85.3586 | 5.7615 | 224.828 | 98.3913 | 232.8449 | 9.9718 | 53.1204 | 13.6341 | 116 | 44.3652 | 0 | 275.811 | 0.005424
8459 | 857.9452 | 2.5155 | 24.9353 | 89.6424 | 77.5487 | 11.4003 | 78.9352 | 5.8347 | 5.3235 | 62.5454 | 86.395 | 5.5491 | 241.6094 | 114.573 | 232.0435 | 9.7274 | 53.0136 | 14.4635 | 119 | 46.6387 | 0 | 275.5498 | 0.0093128
8460 | 868.8174 | 2.5869 | 25.0582 | 90.2488 | 78.5484 | 10.4503 | 98.1807 | 5.9827 | 5.589 | 67.2886 | 101.3017 | 5.4158 | 256.8685 | 135.5773 | 234.1078 | 9.8948 | 53.3049 | 15.3197 | 124 | 45.1572 | 0 | 281.0396 | 0.010927
8461 | 866.8117 | 3.0013 | 25.0933 | 90.6986 | 79.5508 | 9.5003 | 99.9742 | 5.2418 | 5.9366 | 68.4183 | 120.7762 | 5.2705 | 269.3423 | 146.3443 | 236.08 | 9.8201 | 53.3508 | 16.0348 | 141 | 50.6694 | 0 | 288.7347 | 0.012102
8462 | 875.3678 | 3.0789 | 25.0189 | 92.7991 | 78.5536 | 10.4497 | 83.322 | 4.6968 | 5.6561 | 64.4511 | 128.2905 | 5.4602 | 275.1741 | 151.8773 | 243.0463 | 9.9608 | 53.8432 | 16.1769 | 142 | 51.2721 | 0 | 276.6686 | 0.0086153
8463 | 881.1215 | 3.1678 | 25.0279 | 95.9172 | 78.5527 | 10.45 | 73.0289 | 4.6915 | 5.3997 | 66.4416 | 130.675 | 6.3242 | 270.4543 | 155.7251 | 257.9906 | 9.8476 | 53.9082 | 16.3459 | 141 | 51.3021 | 0 | 292.2707 | 0.0024271
8464 | 890.9899 | 4.2402 | 25.1808 | 96.4844 | 78.5454 | 10.4529 | 83.8825 | 5.4723 | 6.4108 | 60.707 | 133.8194 | 10.3221 | 264.5168 | 145.2759 | 275.7616 | 9.9487 | 55.1479 | 16.5137 | 139 | 52.6473 | 0 | 297.0729 | 0
8465 | 905.6035 | 5.0314 | 25.3417 | 95.3007 | 78.5485 | 10.4471 | 92.984 | 6.2858 | 7.6199 | 44.0622 | 134.9642 | 9.3788 | 257.6761 | 140.4371 | 268.9463 | 10.2621 | 56.4649 | 16.6229 | 139 | 50.1659 | 0 | 288.142 | 0
8466 | 889.5222 | 5.1016 | 25.3279 | 95.2463 | 78.5445 | 10.45 | 93.3591 | 6.9052 | 7.0294 | 39.5411 | 132.2461 | 7.7034 | 251.9303 | 132.8426 | 274.146 | 10.3005 | 56.1761 | 16.9207 | 130 | 50.289 | 0 | 289.3741 | 0
8467 | 884.2083 | 8.3065 | 25.4129 | 95.6465 | 79.5451 | 9.5003 | 90.1069 | 6.6341 | 6.7305 | 38.4924 | 129.7478 | 7.5891 | 241.5449 | 128.1799 | 262.5948 | 10.1067 | 56.9276 | 16.7387 | 121 | 46.956 | 0 | 283.6494 | 0
8468 | 893.4902 | 10.9318 | 25.4742 | 94.9174 | 78.5491 | 10.4526 | 79.8838 | 5.7068 | 6.6411 | 37.3355 | 120.073 | 7.8326 | 235.9612 | 117.191 | 258.839 | 10.3076 | 57.6695 | 16.0717 | 122 | 45.8249 | 0 | 275.8487 | 0
8469 | 870.6361 | 11.3483 | 25.3617 | 93.7949 | 78.5568 | 10.4471 | 66.7528 | 5.2292 | 6.7821 | 36.0393 | 96.1976 | 7.6315 | 228.5248 | 105.8884 | 243.9288 | 10.2645 | 56.1681 | 15.3879 | 121 | 43.7336 | 0 | 279.0829 | 0
8470 | 857.044 | 11.4193 | 25.4101 | 93.5931 | 77.5489 | 11.4029 | 65.2417 | 5.2221 | 7.2052 | 33.6044 | 86.9882 | 7.499 | 224.8816 | 102.7394 | 231.3014 | 10.3951 | 55.1454 | 14.2503 | 116 | 42.2228 | 0 | 271.2961 | 0
8471 | 851.1526 | 9.3598 | 25.5379 | 93.5933 | 78.5568 | 10.4471 | 72.6905 | 5.933 | 6.6828 | 31.5238 | 85.9654 | 8.6997 | 217.6865 | 98.8916 | 229.7935 | 10.3709 | 54.3191 | 13.6382 | 121 | 40.6887 | 0 | 270.648 | 0
8472 | 823.9573 | 5.2923 | 25.6329 | 93.3802 | 78.5489 | 10.4529 | 70.6132 | 6.4064 | 6.2906 | 30.9435 | 84.8603 | 9.3539 | 206.3662 | 94.1525 | 227.7712 | 10.304 | 54.7787 | 13.1939 | 117 | 41.256 | 0 | 266.7477 | 0
8473 | 823.3416 | 3.258 | 25.5361 | 93.0708 | 79.5555 | 9.4974 | 61.8902 | 6.7607 | 6.024 | 30.9804 | 83.8492 | 8.7811 | 198.0259 | 88.0542 | 225.1885 | 10.3541 | 54.0716 | 12.9656 | 109 | 39.2824 | 0 | 274.1732 | 0
8474 | 830.4018 | 2.7392 | 25.5394 | 93.2032 | 78.5558 | 10.4497 | 69.5076 | 6.106 | 6.1223 | 30.617 | 82.8639 | 8.0658 | 194.8717 | 86.723 | 227.3759 | 10.1507 | 53.6988 | 11.9937 | 105 | 37.0351 | 0 | 275.0945 | 0
8475 | 817.3827 | 2.4791 | 25.6103 | 92.8896 | 79.5562 | 9.5003 | 73.7896 | 5.392 | 6.256 | 30.3114 | 83.2595 | 7.476 | 193.4215 | 93.2596 | 229.9553 | 10.2885 | 53.5314 | 11.559 | 104 | 37.8604 | 0 | 279.2185 | 0
8476 | 812.2482 | 2.4149 | 26.6547 | 93.1731 | 78.5561 | 10.4497 | 67.8056 | 5.1847 | 6.182 | 30.3597 | 82.7892 | 7.3134 | 193.4341 | 94.9814 | 229.9317 | 10.3682 | 53.5758 | 11.5411 | 104 | 38.6529 | 0 | 279.5721 | 0
8477 | 818.0494 | 2.8326 | 28.2039 | 94.8267 | 78.5548 | 10.45 | 65.5607 | 5.2755 | 6.0135 | 30.3268 | 81.2718 | 7.3115 | 197.3239 | 90.3669 | 225.5917 | 10.236 | 55.1848 | 11.5248 | 103 | 39.2376 | 0 | 316.5917 | 0
8478 | 834.9174 | 3.7969 | 32.1005 | 93.6473 | 79.5529 | 9.5029 | 76.8257 | 5.7055 | 6.0171 | 33.0885 | 81.8895 | 8.4089 | 210.7764 | 93.2241 | 224.7086 | 10.3912 | 58.0246 | 11.7158 | 99 | 39.7027 | 0 | 336.1942 | 0
8479 | 880.2009 | 4.956 | 57.3293 | 95.6405 | 77.5563 | 11.3968 | 92.4912 | 6.0407 | 6.6035 | 48.3741 | 102.6594 | 14.3034 | 242.1308 | 153.1504 | 256.4491 | 12.859 | 55.1843 | 13.2143 | 131 | 44.9943 | 0 | 381.9573 | 0
8480 | 917.6151 | 9.3492 | 79.0841 | 103.1479 | 72.7105 | 16.1487 | 110.956 | 6.5603 | 8.775 | 75.0535 | 136.7881 | 25.3497 | 279.2304 | 213.0128 | 350.4108 | 25.139 | 58.2494 | 13.3056 | 199 | 48.3067 | 0 | 459.6135 | 0
8481 | 1014.0218 | 14.7539 | 91.4023 | 115.2214 | 68.6337 | 19.9489 | 127.8223 | 7.6799 | 7.89 | 78.647 | 163.9867 | 32.8289 | 337.1535 | 263.6678 | 440.0278 | 29.5612 | 68.1708 | 15.9068 | 229 | 55.0896 | 0 | 520.323 | 0
8482 | 1111.0156 | 12.076 | 94.5037 | 126.1032 | 68.5401 | 19.9555 | 143.084 | 7.9233 | 7.6687 | 81.5608 | 183.0362 | 35.2774 | 390.5841 | 300.5146 | 527.2552 | 30.0003 | 78.1739 | 15.7024 | 237 | 62.2264 | 0 | 554.393 | 0.018801
8483 | 1162.6458 | 11.1414 | 96.5516 | 130.0584 | 66.5826 | 21.8136 | 153.0704 | 9.0701 | 7.1515 | 81.6358 | 192.123 | 33.0011 | 494.16 | 329.833 | 586.9619 | 30.0657 | 98.6615 | 16.3615 | 237 | 67.7957 | 0 | 574.3937 | 0.024987
8484 | 1182.5846 | 11.0121 | 102.9187 | 131.6181 | 65.5084 | 22.8364 | 154.5633 | 10.6449 | 6.2766 | 75.8309 | 194.3546 | 29.6917 | 551.9919 | 348.1624 | 586.8641 | 29.8869 | 105.6573 | 17.8768 | 225 | 71.9397 | 0 | 567.9475 | 0.026687
8485 | 1169.8693 | 6.9355 | 101.9833 | 130.2772 | 67.5643 | 20.8826 | 160.2282 | 11.1205 | 6.398 | 75.3541 | 189.4145 | 32.0344 | 464.5223 | 347.4326 | 566.3928 | 30.0709 | 103.9062 | 17.8131 | 237 | 66.9584 | 0 | 575.4422 | 0.010542
8486 | 1152.8663 | 5.0495 | 101.4068 | 133.896 | 65.5256 | 22.8174 | 166.2327 | 11.0425 | 6.3104 | 67.9286 | 189.1009 | 34.575 | 428.7704 | 351.8939 | 558.6194 | 29.9248 | 106.0144 | 18.0646 | 214 | 68.3167 | 0 | 578.4332 | 0.0093687
8487 | 1154.1589 | 5.3071 | 103.9512 | 136.0767 | 69.5523 | 18.9947 | 163.9676 | 11.1288 | 6.2368 | 68.4574 | 189.6721 | 33.9542 | 436.1646 | 353.239 | 546.5475 | 29.5821 | 107.0775 | 18.6361 | 222 | 68.4496 | 0 | 562.7904 | 0.0012136
8488 | 1155.2249 | 8.6531 | 101.8467 | 139.4879 | 70.5435 | 18.0503 | 154.0878 | 10.4438 | 6.4444 | 69.2824 | 191.9578 | 35.904 | 429.4784 | 348.3253 | 521.9275 | 30.8921 | 106.9075 | 19.0247 | 219 | 70.5425 | 0 | 553.7508 | 0
8489 | 1096.3191 | 12.6457 | 97.5081 | 135.5234 | 76.541 | 12.3516 | 142.6117 | 8.2833 | 7.2028 | 67.112 | 190.8812 | 35.9236 | 402.2531 | 321.0307 | 491.1193 | 27.4166 | 104.7053 | 18.9427 | 170 | 68.9382 | 0 | 489.7937 | 0
8490 | 1036.5001 | 9.854 | 86.9078 | 118.6344 | 76.5439 | 12.35 | 131.6052 | 5.6898 | 7.6501 | 67.896 | 181.4519 | 33.9733 | 355.8065 | 243.1638 | 443.4802 | 16.0112 | 97.4693 | 17.8427 | 155 | 61.0461 | 0 | 394.8087 | 0
8491 | 980.584 | 6.8452 | 42.7805 | 105.7564 | 76.5518 | 12.35 | 116.2972 | 5.3089 | 7.5914 | 56.9569 | 151.088 | 27.6752 | 312.3651 | 171.0206 | 396.7291 | 10.7714 | 90.9417 | 17.2701 | 181 | 64.3895 | 0 | 382.0073 | 0
8492 | 939.2753 | 5.3066 | 26.7511 | 99.1598 | 78.5467 | 10.4505 | 100.2286 | 5.6129 | 7.064 | 46.8515 | 130.7719 | 14.1702 | 278.0124 | 139.1972 | 358.4547 | 10.2251 | 83.6494 | 16.1394 | 148 | 57.0357 | 0 | 323.9067 | 0
8493 | 899.2334 | 5.0064 | 26.2082 | 96.9492 | 79.5505 | 9.5003 | 86.1438 | 5.4817 | 6.643 | 40.9947 | 120.9523 | 9.1985 | 256.3914 | 127.188 | 321.6964 | 10.2705 | 75.8365 | 15.1018 | 126 | 49.7786 | 0 | 295.6415 | 0
8494 | 893.803 | 4.6032 | 25.5059 | 97.1275 | 78.5514 | 10.4526 | 86.7145 | 5.2417 | 6.557 | 33.2717 | 105.5675 | 8.8954 | 235.477 | 114.1336 | 290.4381 | 10.146 | 63.3102 | 14.1784 | 120 | 44.8457 | 0 | 284.9336 | 0
8495 | 865.7908 | 4.1 | 25.1369 | 96.8774 | 79.5582 | 9.4974 | 92.4989 | 4.7698 | 6.623 | 27.5741 | 88.9496 | 8.9907 | 221.9475 | 103.5596 | 276.9222 | 10.4254 | 58.523 | 14.2465 | 114 | 40.8037 | 0 | 284.1895 | 0
8496 | 844.5048 | 3.0277 | 22.401 | 95.9711 | 78.5624 | 10.4497 | 88.297 | 4.461 | 6.398 | 26.3117 | 82.7756 | 9.0488 | 216.5858 | 102.9347 | 263.8288 | 10.5321 | 57.3769 | 13.777 | 107 | 40.8096 | 0 | 275.9077 | 0
8497 | 840.3212 | 2.581 | 19.3907 | 95.6699 | 78.5704 | 10.45 | 79.3507 | 4.6666 | 6.164 | 26.2883 | 80.5452 | 7.8944 | 214.0138 | 99.5405 | 256.0135 | 11.2012 | 56.8329 | 13.2222 | 107 | 40.4507 | 0 | 270.2965 | 0
8498 | 831.2767 | 2.9915 | 18.6415 | 95.1423 | 79.5697 | 9.5003 | 75.4991 | 5.2214 | 6.131 | 26.2107 | 83.3296 | 7.0666 | 212.9339 | 92.239 | 250.4959 | 11.301 | 56.6892 | 12.8689 | 104 | 39.6272 | 0 | 277.1988 | 0
8499 | 819.6454 | 2.6638 | 18.4904 | 95.4717 | 79.5663 | 9.5 | 74.9724 | 5.4131 | 6.042 | 26.1474 | 86.2401 | 7.1555 | 208.9073 | 89.2776 | 238.6719 | 11.0272 | 56.4088 | 12.5369 | 108 | 38.5953 | 0 | 274.6159 | 0
8500 | 829.464 | 2.4612 | 18.5743 | 95.4335 | 78.5666 | 10.4497 | 74.429 | 5.7029 | 6.2492 | 26.1002 | 86.6604 | 7.0024 | 203.895 | 87.0699 | 232.737 | 11.2785 | 56.3067 | 12.2867 | 102 | 38.5042 | 0 | 273.2301 | 0
8501 | 844.0282 | 3.029 | 18.6737 | 95.2971 | 79.5684 | 9.5003 | 79.8577 | 5.5188 | 6.1079 | 26.3637 | 84.5809 | 6.9081 | 208.102 | 86.7112 | 227.3883 | 11.0944 | 57.0794 | 12.2693 | 103 | 38.1646 | 0 | 299.758 | 0
8502 | 852.9635 | 4.2471 | 24.5811 | 94.7364 | 78.567 | 10.4497 | 88.158 | 4.6715 | 5.982 | 26.612 | 82.6623 | 7.8544 | 218.6699 | 93.2576 | 230.0884 | 11.0885 | 58.1984 | 12.2482 | 101 | 39.2796 | 0 | 332.2701 | 0
8503 | 872.6808 | 6.1009 | 37.3738 | 98.7252 | 77.5499 | 11.3997 | 96.1762 | 4.4281 | 7.6283 | 48.5852 | 96.8926 | 14.9016 | 244.6602 | 166.1263 | 248.9823 | 13.8774 | 55.6741 | 12.2054 | 140 | 44.0956 | 0 | 378.3146 | 0
8504 | 935.375 | 7.0758 | 67.8074 | 104.0331 | 72.5509 | 16.1487 | 115.2459 | 5.5837 | 12.2316 | 71.5459 | 135.2642 | 29.9647 | 297.6654 | 228.8661 | 327.2854 | 28.1886 | 59.5711 | 14.8535 | 195 | 57.8878 | 0 | 446.4452 | 0
8505 | 1018.7707 | 9.9663 | 87.7815 | 116.8489 | 69.5471 | 18.9992 | 129.4166 | 7.1588 | 13.4411 | 76.4647 | 166.0762 | 34.5236 | 354.202 | 269.3226 | 439.1063 | 35.5245 | 68.1756 | 16.4697 | 234 | 67.602 | 0 | 497.3017 | 0
8506 | 1088.4137 | 16.0113 | 95.4436 | 124.9804 | 69.5458 | 19 | 137.878 | 8.1946 | 12.6107 | 75.8477 | 182.1937 | 33.1865 | 408.5568 | 298.2002 | 513.6873 | 39.2918 | 87.435 | 16.927 | 226 | 72.7233 | 0 | 528.9556 | 0.0083562
8507 | 1129.0494 | 15.7566 | 95.4411 | 134.3899 | 67.5466 | 20.8995 | 141.2803 | 8.986 | 12.3783 | 71.1375 | 188.9503 | 36.0928 | 443.9512 | 317.8848 | 540.7916 | 40.1878 | 112.6618 | 17.6235 | 219 | 76.4963 | 0 | 542.6315 | 0.012664
8508 | 1134.7311 | 14.3406 | 100.5885 | 130.799 | 69.5429 | 19.0005 | 140.7113 | 9.2592 | 12.919 | 68.2518 | 191.7696 | 38.3066 | 440.1679 | 323.6027 | 542.3152 | 41.1178 | 116.0523 | 18.1265 | 230 | 76.2612 | 0 | 551.5657 | 0.014615
8509 | 1106.0452 | 14.3199 | 100.2685 | 132.2949 | 69.5445 | 19 | 145.3291 | 8.3793 | 13.175 | 71.3524 | 190.2061 | 35.468 | 428.0522 | 332.0857 | 545.0715 | 41.6308 | 110.3796 | 18.3088 | 219 | 76.2678 | 0 | 550.8993 | 0.020506
8510 | 1092.6033 | 11.4264 | 98.1164 | 141.165 | 70.5417 | 18.0503 | 156.0379 | 7.8929 | 14.9197 | 73.817 | 190.7109 | 33.9064 | 450.1232 | 335.5108 | 552.1357 | 42.1574 | 93.8243 | 17.9179 | 213 | 77.4421 | 0 | 542.1187 | 0.01194
8511 | 1103.9241 | 17.0485 | 99.2933 | 143.1079 | 69.5444 | 18.9997 | 156.4322 | 7.5899 | 15.0296 | 81.1515 | 193.0248 | 32.6353 | 456.0856 | 331.5723 | 543.4529 | 42.7379 | 88.4658 | 17.9002 | 226 | 76.6899 | 0 | 550.255 | 0.003931
8512 | 1094.9772 | 13.8715 | 97.4763 | 135.7651 | 70.5453 | 18.0503 | 145.4757 | 8.504 | 14.6152 | 87.8751 | 199.3886 | 34.4573 | 440.0177 | 324.3577 | 522.256 | 41.2848 | 87.1904 | 17.8962 | 232 | 77.6196 | 0 | 541.1357 | 0
8513 | 1080.3141 | 8.1674 | 94.6051 | 130.2049 | 76.5477 | 12.3516 | 136.7376 | 9.0891 | 14.3368 | 88.0161 | 197.2655 | 30.5642 | 427.1068 | 300.8006 | 471.758 | 34.5665 | 85.2673 | 17.6914 | 184 | 77.2552 | 0 | 473.2885 | 0
8514 | 1022.5939 | 6.2318 | 82.3445 | 115.9531 | 68.5502 | 19.9479 | 129.6036 | 7.7103 | 14.3059 | 72.3178 | 186.1263 | 26.9955 | 404.0111 | 240.1249 | 374.0173 | 18.8334 | 78.4527 | 17.8078 | 159 | 72.525 | 0 | 379.0365 | 0
8515 | 976.3733 | 5.4284 | 40.3301 | 102.0918 | 75.5443 | 13.3018 | 112.5651 | 6.0881 | 13.0827 | 56.929 | 155.4895 | 22.294 | 348.5015 | 178.4206 | 322.781 | 12.382 | 71.9221 | 17.1552 | 154 | 59.7945 | 0 | 346.8027 | 0
8516 | 944.5024 | 4.7969 | 25.6766 | 96.8361 | 78.5456 | 10.4537 | 83.6907 | 5.5727 | 8.995 | 52.6526 | 138.8012 | 11.5857 | 293.3955 | 157.8693 | 298.9557 | 11.786 | 63.8163 | 16.3042 | 133 | 54.3421 | 0 | 304.6838 | 0
8517 | 907.4215 | 4.809 | 25.3502 | 96.0289 | 78.5548 | 10.4471 | 80.6352 | 5.2693 | 6.8711 | 49.4563 | 127.2775 | 7.4591 | 253.9519 | 145.4977 | 273.929 | 11.2986 | 59.2214 | 15.8016 | 131 | 51.3696 | 0 | 282.8752 | 0
8518 | 887.5496 | 5.1376 | 25.1937 | 96.1599 | 78.5457 | 10.4529 | 78.4893 | 5.3965 | 6.493 | 40.3412 | 108.9515 | 7.2783 | 219.7759 | 131.831 | 246.4508 | 11.1317 | 57.6137 | 14.9578 | 122 | 49.3441 | 0 | 278.9189 | 0
8519 | 857.8984 | 4.508 | 25.2394 | 94.7317 | 78.5509 | 10.4471 | 68.9543 | 6.0805 | 6.138 | 34.395 | 90.5098 | 7.2612 | 206.1249 | 123.2273 | 242.6598 | 10.8041 | 57.31 | 14.2464 | 127 | 47.1065 | 0 | 277.1979 | 0
8520 | 827.7458 | 3.275 | 25.3182 | 93.6499 | 79.5501 | 9.5003 | 75.635 | 6.7056 | 6.0641 | 33.2333 | 82.9474 | 7.2004 | 201.085 | 113.5305 | 235.1306 | 11.023 | 56.4865 | 13.0927 | 121 | 42.828 | 0 | 279.0877 | 0
8521 | 825.527 | 2.8086 | 25.2939 | 93.1841 | 78.5523 | 10.4497 | 78.6556 | 6.763 | 6.0188 | 33.1774 | 81.9135 | 7.081 | 198.0637 | 110.4502 | 229.166 | 10.9722 | 56.5642 | 12.3085 | 117 | 40.5878 | 0 | 282.0338 | 0
8522 | 822.9431 | 2.7135 | 25.4301 | 94.6667 | 78.5547 | 10.45 | 67.8938 | 6.0144 | 6.1477 | 33.7376 | 84.292 | 7.0477 | 198.0036 | 106.047 | 235.2683 | 10.9261 | 55.8446 | 12.1174 | 107 | 42.1992 | 0 | 291.793 | 0
8523 | 824.579 | 2.5106 | 25.3325 | 95.1276 | 78.5522 | 10.45 | 68.2948 | 5.6375 | 6.3485 | 34.3888 | 85.2309 | 7.0366 | 198.4001 | 107.2244 | 240.2155 | 11.0234 | 55.2623 | 11.893 | 107 | 42.457 | 0 | 292.2931 | 0
8524 | 813.3137 | 2.5145 | 25.2838 | 93.8604 | 79.5523 | 9.5003 | 73.841 | 5.6729 | 6.541 | 33.5649 | 84.0818 | 7.0364 | 199.195 | 105.7936 | 236.8672 | 10.7245 | 54.4637 | 11.776 | 106 | 41.6889 | 0 | 291.8419 | 0
8525 | 815.5056 | 2.9141 | 25.3513 | 93.0943 | 78.5491 | 10.4526 | 66.9996 | 6.3454 | 6.514 | 32.8873 | 82.8314 | 7.0091 | 201.9742 | 105.987 | 228.1592 | 10.8937 | 55.4468 | 11.7577 | 105 | 41.4915 | 0 | 314.6035 | 0
8526 | 838.507 | 4.1027 | 31.8955 | 93.141 | 77.5489 | 11.3968 | 71.1497 | 6.8575 | 6.3152 | 32.6882 | 84.7398 | 9.1476 | 213.2135 | 111.4852 | 234.5414 | 10.9146 | 57.0761 | 11.735 | 107 | 42.0857 | 0 | 355.94 | 0
8527 | 869.2433 | 5.5736 | 47.3932 | 97.0649 | 74.548 | 14.2492 | 93.7709 | 6.9577 | 7.2903 | 55.4959 | 96.8011 | 15.4387 | 249.1646 | 168.7176 | 257.8784 | 13.5372 | 55.1003 | 12.8989 | 139 | 47.342 | 0 | 394.6903 | 0
8528 | 915.5241 | 8.5492 | 76.0809 | 102.1438 | 70.546 | 18.0489 | 112.8981 | 7.1987 | 8.0766 | 80.8734 | 134.2284 | 24.6282 | 295.6867 | 226.7266 | 341.9685 | 26.9355 | 58.7982 | 18.0617 | 180 | 59.8783 | 0 | 446.79 | 0
8529 | 957.2562 | 14.1234 | 89.17 | 113.9766 | 68.5466 | 19.9495 | 117.9034 | 9.8102 | 8.1031 | 83.3105 | 158.7302 | 29.3445 | 343.9092 | 266.9695 | 429.0603 | 33.2814 | 66.6825 | 16.3178 | 208 | 73.6245 | 0 | 498.321 | 0
8530 | 1022.9778 | 13.6768 | 94.8435 | 122.519 | 65.5409 | 22.7992 | 132.4866 | 10.3806 | 6.2918 | 76.6668 | 174.0865 | 30.8135 | 389.1723 | 300.7479 | 497.3573 | 34.8034 | 72.4228 | 14.7514 | 203 | 67.7931 | 0 | 530.7832 | 0.0056372
8531 | 1089.0662 | 7.5285 | 97.1762 | 124.0894 | 66.5389 | 21.8503 | 135.4821 | 9.9368 | 5.438 | 71.351 | 180.5809 | 29.179 | 415.1445 | 325.079 | 522.5951 | 34.5523 | 78.4081 | 15.0791 | 190 | 68.9774 | 0 | 551.2236 | 0.017495
8532 | 1086.6042 | 4.8119 | 97.0804 | 125.0091 | 68.5368 | 19.9505 | 126.019 | 9.2395 | 5.531 | 69.728 | 181.1869 | 27.772 | 418.4148 | 338.4274 | 515.6248 | 35.1387 | 81.8285 | 14.154 | 180 | 71.3193 | 0 | 554.8981 | 0.01181
8533 | 1071.8884 | 4.8028 | 96.8262 | 128.4872 | 69.5399 | 19.0003 | 131.2589 | 10.0263 | 6.048 | 71.0394 | 182.8272 | 30.0338 | 410.9414 | 337.2582 | 499.2884 | 35.9965 | 80.4402 | 9.5959 | 203 | 70.0066 | 0 | 543.2132 | 0.011424
8534 | 1074.8633 | 8.5896 | 95.1957 | 128.6247 | 68.545 | 19.9497 | 136.7245 | 10.3535 | 6.009 | 67.5612 | 182.7723 | 29.4763 | 414.2946 | 336.7864 | 499.8214 | 37.9675 | 83.715 | 7.5665 | 201 | 66.9197 | 0 | 560.1538 | 0.0073313
8535 | 1092.3768 | 11.4366 | 94.1516 | 129.2753 | 69.5434 | 19.0003 | 137.0719 | 9.1236 | 5.735 | 68.8963 | 182.1672 | 27.7403 | 417.9556 | 329.8766 | 493.846 | 37.9312 | 84.7415 | 6.7345 | 209 | 67.3596 | 0 | 550.7808 | 0.0023732
8536 | 1062.7127 | 8.6548 | 92.8891 | 130.5456 | 69.547 | 19 | 137.1956 | 8.7107 | 6.2468 | 69.7505 | 182.2364 | 29.2947 | 404.3507 | 311.4548 | 463.1016 | 37.9019 | 85.7605 | 6.908 | 179 | 64.6407 | 0 | 541.1115 | 0
8537 | 1045.5179 | 6.7402 | 90.4925 | 125.7247 | 73.5453 | 15.2011 | 131.3606 | 8.4192 | 6.5641 | 78.1158 | 163.8483 | 28.3598 | 385.505 | 284.1768 | 414.9168 | 30.6744 | 83.9516 | 7.3862 | 162 | 60.532 | 0 | 478.9729 | 0
8538 | 991.5143 | 6.571 | 86.963 | 116.5182 | 77.5499 | 11.4011 | 120.3381 | 8.267 | 6.828 | 69.8026 | 144.746 | 27.4541 | 349.0031 | 221.7199 | 373.9535 | 16.0085 | 75.2007 | 7.8801 | 151 | 58.8161 | 0 | 369.2991 | 0
8539 | 928.3232 | 5.9067 | 46.7948 | 104.6099 | 78.5481 | 10.4503 | 111.1254 | 8.1554 | 6.9197 | 58.171 | 137.041 | 24.0194 | 299.2474 | 162.5997 | 335.332 | 10.6843 | 67.5932 | 7.8892 | 149 | 51.7371 | 0 | 341.3847 | 0
8540 | 885.4266 | 5.1261 | 27.2161 | 97.4826 | 79.5494 | 9.5003 | 101.289 | 7.1128 | 6.4958 | 52.7113 | 132.2975 | 13.5999 | 269.7245 | 128.2801 | 300.7231 | 10.5915 | 60.7643 | 7.5492 | 130 | 46.1816 | 0 | 295.1056 | 0
8541 | 860.204 | 4.8985 | 25.0081 | 96.3901 | 78.5482 | 10.4497 | 89.5422 | 6.0562 | 6.5522 | 47.0658 | 123.7147 | 10.5013 | 253.384 | 108.2921 | 262.1483 | 10.1641 | 57.9938 | 6.9615 | 122 | 43.1406 | 0 | 271.6523 | 0
8542 | 834.6113 | 7.3435 | 24.7663 | 94.8856 | 79.5493 | 9.5003 | 79.2999 | 4.8909 | 6.4967 | 37.6228 | 107.1152 | 10.1053 | 234.7638 | 98.2986 | 228.986 | 9.7367 | 55.6688 | 6.07 | 118 | 41.6044 | 0 | 267.6406 | 0
8543 | 806.9404 | 6.062 | 24.7581 | 94.8817 | 79.5458 | 9.5 | 85.2381 | 4.4445 | 6.0888 | 31.4019 | 87.9782 | 9.5542 | 218.4753 | 88.9838 | 220.6857 | 9.7172 | 55.0584 | 5.8765 | 113 | 38.1404 | 0 | 258.014 | 0
8544 | 791.0792 | 3.4844 | 24.7655 | 94.1404 | 78.5489 | 10.4497 | 90.1146 | 4.8378 | 5.9999 | 30.0946 | 82.4379 | 9.4092 | 207.4734 | 86.793 | 218.1667 | 9.5916 | 54.815 | 5.4068 | 106 | 37.1305 | 0 | 252.4277 | 0
8545 | 772.6513 | 2.6869 | 24.899 | 94.0814 | 79.5535 | 9.5003 | 85.1045 | 5.2316 | 6.0689 | 30.1427 | 82.4607 | 9.3547 | 202.8337 | 87.9364 | 214.7613 | 9.6834 | 54.7964 | 4.4343 | 104 | 34.397 | 0 | 257.2096 | 0
8546 | 771.972 | 2.5171 | 24.869 | 94.1101 | 79.5514 | 9.5 | 87.6773 | 5.5722 | 6.349 | 30.1428 | 79.4469 | 9.5204 | 201.6512 | 83.3819 | 220.0444 | 9.7053 | 54.8663 | 3.6007 | 103 | 34.4352 | 0 | 250.1724 | 0
8547 | 762.4384 | 2.431 | 24.7753 | 93.8809 | 78.5557 | 10.4497 | 85.1945 | 5.4233 | 6.3729 | 30.1361 | 78.2334 | 9.4002 | 200.3132 | 83.2663 | 222.802 | 9.6861 | 55.0649 | 3.3695 | 102 | 34.7849 | 0 | 254.7386 | 0
8548 | 770.7682 | 2.6352 | 24.782 | 93.4161 | 79.5541 | 9.5003 | 77.1624 | 4.9458 | 6.2671 | 30.2535 | 78.5804 | 9.3876 | 200.5071 | 82.1255 | 220.2757 | 9.8408 | 54.451 | 3.2915 | 102 | 35.5837 | 0 | 259.6108 | 0
8549 | 776.5908 | 2.9858 | 24.68 | 94.0943 | 79.5536 | 9.5026 | 74.3804 | 4.3429 | 6.4335 | 30.3692 | 78.8166 | 9.3895 | 206.5388 | 80.2923 | 216.9828 | 9.6525 | 55.4141 | 3.4074 | 100 | 36.979 | 0 | 290.2435 | 0
8550 | 799.7298 | 3.7014 | 33.9584 | 93.6784 | 77.5549 | 11.3968 | 79.2104 | 4.3694 | 6.6943 | 30.5885 | 80.0388 | 10.1221 | 217.4316 | 89.3777 | 219.0244 | 9.9453 | 57.4787 | 3.273 | 102 | 36.7642 | 0 | 337.7171 | 0
8551 | 812.8806 | 5.6842 | 50.0021 | 99.2138 | 72.5528 | 16.1487 | 93.6377 | 4.8641 | 7.7282 | 45.4013 | 89.5751 | 16.4661 | 239.089 | 156.3092 | 238.3236 | 13.0318 | 54.7963 | 5.0141 | 143 | 41.6255 | 0 | 380.2938 | 0
8552 | 839.4639 | 6.8641 | 74.5748 | 101.4629 | 69.5469 | 18.9992 | 111.3805 | 6.7925 | 7.3396 | 86.6348 | 125.1669 | 30.3178 | 281.8176 | 222.5089 | 312.0105 | 27.2158 | 56.9822 | 7.758 | 188 | 56.6157 | 0 | 441.5906 | 0
8553 | 885.3025 | 7.8906 | 84.6457 | 109.5186 | 68.5449 | 19.9497 | 121.451 | 8.4749 | 6.5905 | 100.6362 | 149.7417 | 32.2852 | 316.1712 | 248.8762 | 380.3672 | 33.1066 | 62.6392 | 6.0331 | 207 | 63.7526 | 0 | 489.56 | 0
8554 | 944.1801 | 7.5319 | 88.9875 | 114.6766 | 70.544 | 18.0505 | 125.3139 | 8.6667 | 5.5557 | 95.1565 | 165.7301 | 26.5369 | 338.4537 | 266.8058 | 436.3916 | 34.0369 | 68.989 | 4.4495 | 201 | 63.9749 | 0 | 511.1854 | 0.072637
8555 | 996.9716 | 5.2024 | 92.329 | 117.3529 | 68.5451 | 19.9495 | 123.5378 | 8.3837 | 5.5683 | 88.7826 | 176.4325 | 25.4647 | 345.8775 | 281.9793 | 461.3805 | 33.8231 | 74.1543 | 4.5046 | 207 | 64.3342 | 0 | 529.9602 | 0.10458
8556 | 1014.472 | 4.6383 | 93.4473 | 117.4674 | 67.5493 | 20.8997 | 127.2373 | 7.9342 | 6.4625 | 90.956 | 178.8076 | 26.6298 | 352.4076 | 288.1628 | 458.5169 | 35.165 | 76.1588 | 4.7479 | 194 | 63.8903 | 0 | 521.5865 | 0.14162
8557 | 1002.7719 | 7.2624 | 92.32 | 121.3035 | 69.5455 | 19.0005 | 128.1188 | 6.7379 | 7.2187 | 85.1856 | 179.1714 | 27.6257 | 355.0073 | 288.337 | 439.8437 | 36.1237 | 74.5234 | 5.7482 | 196 | 62.5038 | 0 | 525.1911 | 0.15898
8558 | 1011.973 | 10.1657 | 95.9727 | 121.3076 | 71.5459 | 17.1005 | 129.7884 | 7.1757 | 7.142 | 75.6879 | 183.1728 | 27.8121 | 356.6415 | 281.1933 | 412.7975 | 33.4425 | 72.9578 | 5.7905 | 180 | 63.2751 | 0 | 517.3579 | 0.15257
8559 | 1019.9081 | 11.4616 | 93.3965 | 123.4081 | 69.5503 | 18.9995 | 133.4428 | 7.6832 | 5.9077 | 67.1104 | 183.0386 | 26.0706 | 365.9787 | 281.8061 | 410.6742 | 31.4918 | 72.5951 | 5.6861 | 179 | 65.4933 | 0 | 501.744 | 0.060751
8560 | 1001.0871 | 12.5113 | 92.7229 | 128.3681 | 66.5469 | 21.8492 | 130.3239 | 8.2553 | 5.9175 | 67.3067 | 174.1605 | 26.7603 | 356.7461 | 278.3426 | 403.942 | 27.9282 | 72.5637 | 5.8214 | 169 | 65.3102 | 0 | 489.8122 | 0
8561 | 966.949 | 9.9868 | 89.6316 | 123.8823 | 76.5479 | 12.3526 | 121.2877 | 7.7617 | 6.9478 | 68.5217 | 158.5843 | 27.1554 | 343.2186 | 256.8708 | 385.6415 | 17.8207 | 71.8201 | 5.7296 | 151 | 65.3626 | 0 | 424.9393 | 0
8562 | 933.6894 | 7.0147 | 77.1413 | 110.3028 | 77.5498 | 11.4003 | 112.7414 | 6.4554 | 6.7157 | 63.8476 | 142.6602 | 26.8309 | 321.7228 | 186.6086 | 342.6831 | 12.8495 | 67.3736 | 5.6465 | 140 | 64.4653 | 0 | 327.3971 | 0
8563 | 896.8604 | 5.2352 | 38.6608 | 98.0462 | 78.5464 | 10.4503 | 100.8646 | 4.7549 | 6.7595 | 47.5145 | 133.5064 | 23.1348 | 278.6096 | 124.3878 | 307.9132 | 10.3244 | 62.6562 | 5.356 | 138 | 50.7847 | 0 | 304.1726 | 0
8564 | 879.641 | 7.0484 | 25.423 | 94.5527 | 78.5465 | 10.45 | 82.6274 | 4.3861 | 7.1853 | 41.5624 | 128.5509 | 13.0741 | 245.5708 | 108.3599 | 279.711 | 9.4484 | 57.8252 | 4.9367 | 121 | 43.9148 | 0 | 264.4247 | 0
8565 | 858.2351 | 9.3093 | 25.0798 | 95.0394 | 79.552 | 9.5003 | 75.2837 | 5.0773 | 6.9947 | 39.6592 | 121.5801 | 9.2645 | 232.9091 | 94.9388 | 243.0905 | 9.6417 | 55.3934 | 4.2991 | 114 | 40.3527 | 0 | 244.7912 | 0
8566 | 842.2004 | 7.0208 | 24.9268 | 94.6005 | 78.5512 | 10.4497 | 74.3241 | 5.52 | 6.8413 | 31.1677 | 103.5001 | 9.1812 | 214.2196 | 87.5998 | 228.2611 | 9.6366 | 54.2366 | 3.6087 | 114 | 37.5355 | 0 | 243.2818 | 0
8567 | 812.683 | 4.3836 | 24.9203 | 94.2674 | 79.5492 | 9.5003 | 74.5429 | 5.6451 | 6.4 | 27.9872 | 85.3613 | 9.1695 | 203.5181 | 88.8661 | 228.7856 | 9.6307 | 53.6031 | 3.2274 | 122 | 34.75 | 0 | 243.2766 | 0
8568 | 785.7279 | 3.4513 | 24.888 | 94.3053 | 78.5487 | 10.4497 | 73.9511 | 5.6731 | 6.2085 | 27.1916 | 79.8898 | 9.0692 | 198.4557 | 88.4216 | 226.6186 | 9.7042 | 54.2642 | 2.7578 | 121 | 36.8129 | 0 | 244.0281 | 0
8569 | 782.4318 | 3.0562 | 24.9438 | 95.713 | 79.5508 | 9.5003 | 69.8353 | 5.0383 | 6.63 | 26.822 | 79.2953 | 8.95 | 194.6673 | 83.5407 | 220.2946 | 9.4127 | 53.8835 | 2.5054 | 121 | 35.2621 | 0 | 240.5185 | 0
8570 | 776.0852 | 2.6848 | 24.9853 | 95.6447 | 78.5548 | 10.4497 | 71.9555 | 4.8439 | 6.6495 | 26.9046 | 79.2574 | 8.9439 | 193.5493 | 83.5566 | 219.4935 | 9.6747 | 51.9401 | 2.5009 | 117 | 34.1323 | 0 | 253.0602 | 0
8571 | 765.8198 | 2.9817 | 25.243 | 94.583 | 79.5522 | 9.5003 | 73.7201 | 4.6881 | 6.4108 | 26.9802 | 78.3632 | 9.0096 | 193.2273 | 84.7037 | 222.3949 | 9.6114 | 50.1013 | 2.5271 | 115 | 33.6883 | 0 | 241.8545 | 0
8572 | 764.7764 | 2.7541 | 25.1582 | 94.3754 | 78.5552 | 10.4497 | 73.8979 | 5.1735 | 6.3687 | 27.0587 | 77.7316 | 8.9991 | 192.5924 | 80.3845 | 222.1035 | 9.587 | 49.5699 | 2.5304 | 114 | 34.6949 | 0 | 243.7867 | 0
8573 | 758.5202 | 2.84 | 25.0399 | 94.8059 | 79.552 | 9.5003 | 73.3484 | 5.6112 | 6.5306 | 27.1063 | 78.1406 | 8.9991 | 195.662 | 80.2259 | 217.3321 | 9.826 | 52.0497 | 2.4879 | 106 | 35.2533 | 0 | 268.115 | 0
8574 | 774.8435 | 3.6139 | 36.1891 | 94.0703 | 76.5563 | 12.3492 | 70.3829 | 5.9494 | 6.4689 | 27.3753 | 78.9473 | 9.7317 | 205.0833 | 90.4466 | 221.2241 | 9.5421 | 53.9825 | 2.468 | 102 | 36.6026 | 0 | 316.7942 | 0
8575 | 802.9154 | 5.1986 | 50.8062 | 99.7223 | 76.5509 | 12.35 | 86.5268 | 6.9516 | 7.4296 | 46.9531 | 88.1247 | 15.9804 | 235.6591 | 138.2203 | 230.6591 | 9.6464 | 51.0342 | 2.4792 | 125 | 42.0852 | 0 | 343.0922 | 0
8576 | 835.9588 | 6.078 | 77.5945 | 100.1185 | 71.5479 | 17.0987 | 107.3122 | 6.8495 | 7.7225 | 72.494 | 124.6488 | 25.957 | 250.546 | 184.7361 | 262.7757 | 13.4938 | 52.0653 | 3.1234 | 149 | 44.1075 | 0 | 379.6133 | 0
8577 | 856.0647 | 5.3155 | 87.3636 | 106.3963 | 66.5474 | 21.8487 | 105.6944 | 6.5998 | 6.6337 | 76.2629 | 153.4353 | 27.9977 | 264.4704 | 211.1986 | 299.0927 | 23.3797 | 56.5446 | 4.1314 | 139 | 46.5936 | 0 | 414.0687 | 0
8578 | 876.3464 | 4.0609 | 87.5407 | 110.7688 | 67.5491 | 20.9003 | 96.0533 | 6.6971 | 5.6968 | 68.1534 | 154.416 | 25.8881 | 275.6805 | 226.2983 | 305.1668 | 26.6819 | 60.0855 | 5.5971 | 142 | 46.8461 | 0 | 411.8323 | 0.072829
8579 | 900.4499 | 3.6069 | 86.9747 | 110.7637 | 68.5431 | 19.9503 | 100.8739 | 6.9393 | 5.963 | 64.7106 | 160.5225 | 24.9226 | 281.9287 | 230.4573 | 312.4905 | 27.5993 | 60.326 | 8.6619 | 141 | 44.9512 | 0 | 410.9238 | 0.10407
8580 | 900.3254 | 4.3335 | 76.8274 | 109.3393 | 70.5411 | 18.0505 | 104.5381 | 7.1856 | 5.8028 | 60.5596 | 161.5337 | 24.276 | 279.842 | 224.1126 | 322.1067 | 25.2841 | 61.1249 | 5.7147 | 141 | 42.1119 | 0 | 415.4699 | 0.13378
8581 | 893.6042 | 9.407 | 48.851 | 111.1786 | 71.546 | 17.1003 | 104.3737 | 7.5653 | 5.4726 | 64.6025 | 150.2849 | 22.7064 | 275.3623 | 216.9562 | 316.1023 | 16.4489 | 60.2835 | 3.8884 | 141 | 40.3016 | 0 | 402.2772 | 0.13631
8582 | 892.6799 | 10.7466 | 37.4872 | 116.3103 | 71.5452 | 17.1 | 102.4062 | 6.6525 | 5.4903 | 62.064 | 146.2433 | 21.8524 | 272.6626 | 207.6515 | 307.4379 | 11.9571 | 62.0505 | 3.8649 | 144 | 40.5595 | 0 | 388.119 | 0.058092
8583 | 875.8709 | 6.2736 | 36.227 | 112.2476 | 69.5456 | 18.9995 | 104.3447 | 5.0783 | 5.229 | 62.9452 | 146.8098 | 22.3888 | 272.9584 | 204.6113 | 300.702 | 11.4466 | 61.2073 | 3.9557 | 140 | 42.9315 | 0 | 392.2376 | 0.015152
8584 | 869.8523 | 4.5215 | 36.6803 | 110.7002 | 72.5429 | 16.1508 | 106.5004 | 4.8065 | 5.6332 | 61.2189 | 142.0387 | 24.3113 | 270.2088 | 185.6496 | 302.4469 | 12.476 | 61.4124 | 4.5145 | 144 | 42.8834 | 0 | 385.0783 | 0
8585 | 857.3076 | 4.727 | 35.8009 | 107.6158 | 78.5423 | 10.4516 | 104.0532 | 4.9537 | 6.2578 | 70.9137 | 125.0233 | 25.9293 | 260.7936 | 161.956 | 280.5265 | 10.9559 | 62.965 | 4.3829 | 143 | 43.1229 | 0 | 337.9982 | 0
8586 | 848.3711 | 4.8035 | 29.2748 | 102.6996 | 79.5434 | 9.5003 | 99.9229 | 5.7719 | 6.2977 | 63.5305 | 112.5616 | 26.521 | 242.9088 | 130.2141 | 249.9356 | 10.2372 | 60.2043 | 4.0246 | 135 | 42.5462 | 0 | 283.7795 | 0
8587 | 834.3675 | 4.5848 | 25.879 | 96.3916 | 78.5459 | 10.4497 | 90.6798 | 5.9265 | 6.2985 | 48.2519 | 108.1634 | 22.9006 | 225.6882 | 103.4622 | 226.5481 | 9.2051 | 56.9972 | 3.9312 | 147 | 42.2568 | 0 | 259.036 | 0
8588 | 800.8928 | 4.5536 | 25.429 | 94.7271 | 79.5456 | 9.5003 | 73.6915 | 5.7683 | 6.7357 | 42.4872 | 102.0281 | 12.5326 | 211.4183 | 89.0733 | 220.1691 | 8.7165 | 52.5394 | 3.8962 | 120 | 40.5031 | 0 | 246.9571 | 0
8589 | 785.0903 | 5.1669 | 25.3638 | 94.233 | 79.5462 | 9.5026 | 67.692 | 5.6472 | 7.0577 | 40.0027 | 90.2863 | 8.838 | 203.0833 | 86.1338 | 217.7817 | 8.6415 | 50.2129 | 3.6963 | 111 | 36.9077 | 0 | 238.6554 | 0
8590 | 778.4593 | 5.5888 | 25.5924 | 93.8584 | 77.5549 | 11.3968 | 67.3942 | 4.9242 | 6.948 | 31.7923 | 84.4055 | 8.9868 | 190.2179 | 83.1723 | 212.4161 | 8.8458 | 49.3721 | 3.1494 | 112 | 34.7603 | 0 | 241.2598 | 0
8591 | 777.8827 | 4.3201 | 25.6235 | 93.6274 | 78.5495 | 10.4503 | 68.3881 | 4.6298 | 7.1595 | 26.9822 | 81.6749 | 8.9518 | 184.3777 | 80.1599 | 213.5882 | 8.8342 | 48.3844 | 2.9557 | 110 | 34.4635 | 0 | 237.8951 | 0
8592 | 780.1353 | 3.1791 | 25.5975 | 93.8424 | 79.5506 | 9.5003 | 67.6981 | 4.8329 | 6.7683 | 26.3191 | 80.2176 | 8.9266 | 184.3542 | 77.9686 | 217.2307 | 8.9232 | 47.5402 | 2.9389 | 104 | 36.5076 | 0 | 242.6337 | 0
8593 | 773.1305 | 2.8294 | 25.9001 | 94.0942 | 78.5515 | 10.4497 | 67.4838 | 5.6474 | 6.5987 | 26.6344 | 80.0151 | 8.8008 | 188.5259 | 75.5598 | 223.5305 | 9.0644 | 45.4107 | 3.3092 | 101 | 37.5252 | 0 | 246.2401 | 0
8594 | 766.1778 | 2.6702 | 25.8655 | 94.2835 | 79.5509 | 9.5003 | 67.1878 | 5.7306 | 6.4882 | 26.9424 | 78.6059 | 8.7276 | 191.2637 | 75.4499 | 230.0991 | 8.9107 | 44.5566 | 3.1041 | 100 | 39.407 | 0 | 244.8746 | 0
8595 | 757.6211 | 2.4803 | 25.589 | 94.3621 | 79.5536 | 9.5 | 66.6393 | 5.5528 | 6.2895 | 26.6953 | 77.7686 | 8.7291 | 189.2781 | 74.9526 | 230.0492 | 9.0786 | 44.2876 | 2.9568 | 99 | 36.6004 | 0 | 246.3493 | 0
8596 | 761.9828 | 2.5874 | 25.4153 | 94.403 | 78.5541 | 10.4497 | 66.4246 | 5.2816 | 6.359 | 26.4064 | 77.9141 | 8.7022 | 187.3815 | 74.3931 | 228.1532 | 8.7712 | 44.139 | 2.9683 | 99 | 37.1724 | 0 | 247.3601 | 0
8597 | 766.0145 | 3.0425 | 25.4161 | 94.0906 | 79.5526 | 9.5003 | 66.4776 | 4.6104 | 6.1878 | 26.6834 | 78.1034 | 8.7238 | 187.2687 | 74.3345 | 224.4872 | 8.0889 | 44.1982 | 2.9423 | 98 | 37.0545 | 0 | 241.1525 | 0
8598 | 757.3823 | 3.7008 | 25.4087 | 93.8727 | 79.5517 | 9.5 | 66.9009 | 4.6316 | 6.3867 | 26.7839 | 78.1382 | 8.6948 | 186.0222 | 74.1899 | 223.9024 | 8.6033 | 45.8658 | 2.9171 | 96 | 36.6407 | 0 | 244.171 | 0
8599 | 749.7557 | 3.9263 | 25.691 | 93.7086 | 78.5497 | 10.4526 | 67.1629 | 5.1102 | 6.6075 | 27.0441 | 78.6869 | 8.6818 | 186.0763 | 79.4811 | 223.8959 | 8.7853 | 44.5807 | 2.9375 | 99 | 35.9423 | 0 | 246.177 | 0
8600 | 741.3086 | 4.0367 | 25.4748 | 93.7347 | 78.5545 | 10.4471 | 67.1186 | 5.6295 | 6.4923 | 27.0712 | 80.2822 | 8.68 | 187.9511 | 80.5353 | 226.3495 | 8.9955 | 43.8767 | 3.1885 | 100 | 37.8123 | 0 | 244.4269 | 0
8601 | 739.4558 | 3.6056 | 25.1361 | 93.4228 | 76.5486 | 12.3495 | 66.4386 | 5.6911 | 6.1505 | 36.3365 | 79.9085 | 7.9416 | 189.3566 | 77.8442 | 224.6864 | 8.6233 | 43.6995 | 3.7402 | 100 | 37.4951 | 0 | 248.2266 | 0
8602 | 740.0326 | 2.9106 | 24.7005 | 91.1543 | 76.5517 | 12.35 | 64.6387 | 5.4681 | 6.2693 | 50.3027 | 76.751 | 6.3486 | 188.7473 | 77.5442 | 218.8917 | 8.3004 | 42.9681 | 3.968 | 104 | 36.2084 | 0 | 233.3172 | 0.10207
8603 | 743.5305 | 2.5832 | 24.6079 | 90.326 | 77.5511 | 11.4003 | 63.0192 | 5.2369 | 5.7652 | 51.6127 | 77.4385 | 5.1057 | 186.508 | 77.8398 | 215.1945 | 8.2651 | 42.6368 | 3.9621 | 104 | 35.6503 | 0 | 242.3904 | 0.050107
8604 | 749.8072 | 2.8011 | 24.5628 | 90.5529 | 78.547 | 10.4532 | 64.9189 | 4.4675 | 5.3795 | 48.1977 | 77.638 | 4.2641 | 186.4817 | 79.9523 | 215.3719 | 8.1701 | 42.7029 | 3.9611 | 115 | 37.643 | 0 | 242.7505 | 0.017381
8605 | 745.3373 | 3.0319 | 24.7921 | 91.237 | 78.5473 | 10.4471 | 66.2858 | 4.473 | 5.1695 | 46.9547 | 75.6834 | 4.0514 | 184.7929 | 82.437 | 218.4343 | 8.4027 | 43.7854 | 3.9876 | 121 | 37.586 | 0 | 235.9466 | 0.042209
8606 | 743.9283 | 2.7234 | 24.6872 | 91.1963 | 79.5474 | 9.5003 | 66.2638 | 4.4253 | 5.3537 | 41.4411 | 75.0478 | 4.0336 | 186.216 | 84.0927 | 224.3946 | 8.2158 | 43.9419 | 3.9746 | 120 | 38.4199 | 0 | 232.2543 | 0.013851
8607 | 744.6932 | 2.5325 | 24.5711 | 90.9313 | 79.549 | 9.5 | 65.0671 | 5.0446 | 5.192 | 43.6946 | 75.2811 | 4.0335 | 188.6807 | 84.6327 | 229.179 | 8.3594 | 43.8513 | 3.9744 | 126 | 42.3283 | 0 | 238.4224 | 0.0093934
8608 | 740.9044 | 4.0913 | 24.6606 | 91.4722 | 79.5462 | 9.5 | 63.5611 | 5.8302 | 5.3265 | 41.5117 | 78.2508 | 5.0537 | 189.9485 | 84.4257 | 237.3343 | 8.4695 | 43.4579 | 4.0043 | 124 | 40.9828 | 0 | 243.3883 | 0
8609 | 745.7811 | 4.9073 | 24.8355 | 93.6078 | 78.5465 | 10.4526 | 67.2313 | 6.0993 | 6.2375 | 31.7761 | 82.1503 | 6.4757 | 189.8992 | 80.4431 | 243.3489 | 8.6966 | 44.0535 | 3.9803 | 126 | 38.6769 | 0 | 251.4524 | 0
8610 | 747.1316 | 4.6239 | 24.8395 | 94.7934 | 79.5523 | 9.4974 | 67.886 | 6.3338 | 6.7519 | 28.2099 | 81.0319 | 6.8855 | 189.8832 | 80.6695 | 246.087 | 8.9914 | 44.1755 | 3.9375 | 124 | 36.7418 | 0 | 250.2493 | 0
8611 | 746.3299 | 4.4178 | 24.872 | 94.4839 | 78.5514 | 10.4497 | 57.0031 | 5.8524 | 6.6878 | 28.0499 | 80.9015 | 6.9098 | 191.1745 | 80.9368 | 244.2627 | 8.7629 | 44.0712 | 3.9106 | 134 | 37.0008 | 0 | 253.6158 | 0
8612 | 742.2558 | 4.421 | 24.9549 | 93.4406 | 77.547 | 11.4029 | 52.8789 | 5.7279 | 6.7072 | 27.2679 | 81.4207 | 6.9416 | 188.5094 | 82.1672 | 238.3684 | 8.8524 | 44.3492 | 3.9332 | 134 | 36.4988 | 0 | 252.6861 | 0
8613 | 742.7975 | 4.6264 | 24.8561 | 93.7725 | 78.5535 | 10.4471 | 60.9802 | 5.3726 | 7.8515 | 26.7304 | 80.8328 | 6.9007 | 187.971 | 83.1346 | 233.4163 | 8.9111 | 44.177 | 3.9119 | 130 | 35.7199 | 0 | 239.668 | 0
8614 | 737.3704 | 4.519 | 24.8758 | 93.767 | 79.5488 | 9.5003 | 66.2212 | 5.6665 | 7.0253 | 26.5135 | 80.134 | 6.8502 | 187.8973 | 82.5649 | 227.5374 | 8.6421 | 44.1523 | 3.4591 | 131 | 36.3101 | 0 | 245.1297 | 0
8615 | 733.2657 | 4.0687 | 24.9212 | 94.0824 | 79.5502 | 9.5 | 62.6764 | 6.2404 | 6.8182 | 26.5862 | 78.1213 | 6.8546 | 186.8456 | 80.8853 | 229.929 | 8.8631 | 44.3829 | 3.3926 | 132 | 35.3182 | 0 | 239.1384 | 0
8616 | 722.2024 | 3.4427 | 25.1379 | 93.6895 | 78.5553 | 10.4497 | 62.3344 | 6.4164 | 7.284 | 26.6974 | 75.9045 | 6.96 | 185.0603 | 81.2369 | 229.883 | 8.6879 | 44.361 | 3.3821 | 101 | 36.1397 | 0 | 243.908 | 0
8617 | 724.5683 | 3.146 | 24.9615 | 93.0345 | 79.5564 | 9.5003 | 66.0636 | 6.2332 | 6.9398 | 28.1116 | 74.8529 | 7.9132 | 184.731 | 77.8897 | 221.1952 | 8.7215 | 44.4086 | 3.1705 | 104 | 34.765 | 0 | 246.7686 | 0
8618 | 723.8283 | 3.6098 | 24.8774 | 93.4074 | 78.5513 | 10.4497 | 66.3825 | 5.7738 | 6.9578 | 29.484 | 74.7329 | 7.3722 | 185.5919 | 77.0994 | 222.6004 | 8.7192 | 44.371 | 3.0525 | 104 | 34.9108 | 0 | 241.6044 | 0
8619 | 713.4027 | 3.0163 | 24.9146 | 94.1782 | 74.5514 | 14.2489 | 62.3553 | 5.2621 | 6.5885 | 29.5118 | 75.1576 | 6.9281 | 185.0914 | 77.1065 | 225.6784 | 8.6069 | 45.1517 | 3.0457 | 99 | 35.6608 | 0 | 242.5213 | 0
8620 | 712.8164 | 2.6205 | 24.9717 | 93.7671 | 74.555 | 14.25 | 63.2814 | 5.1553 | 6.1448 | 30.1734 | 76.0223 | 6.9192 | 185.1371 | 76.6182 | 222.9255 | 8.8759 | 44.6978 | 2.9197 | 101 | 36.3283 | 0 | 239.1673 | 0
8621 | 711.8172 | 2.9552 | 25.1508 | 92.8416 | 76.5522 | 12.3505 | 65.7327 | 5.6303 | 6.1762 | 29.925 | 76.5661 | 6.9398 | 185.4585 | 78.2768 | 219.965 | 8.6529 | 45.2931 | 2.773 | 101 | 36.986 | 0 | 240.6366 | 0
8622 | 714.1202 | 3.9567 | 24.9639 | 92.7929 | 78.5543 | 10.4505 | 66.0275 | 6.1216 | 6.2515 | 27.6748 | 76.5546 | 6.9055 | 184.5971 | 77.4057 | 217.5859 | 8.6985 | 46.7927 | 2.7104 | 97 | 42.5713 | 0 | 238.568 | 0
8623 | 723.5261 | 4.0511 | 25.0585 | 92.8058 | 79.5501 | 9.5003 | 66.6281 | 6.1131 | 6.346 | 26.5959 | 77.0199 | 6.9145 | 184.6864 | 76.2452 | 218.0909 | 8.7924 | 44.9715 | 2.7293 | 100 | 41.3108 | 0 | 241.2986 | 0
8624 | 725.5116 | 4.0875 | 25.1335 | 92.6013 | 78.55 | 10.4497 | 66.76 | 6.0777 | 6.5735 | 26.6022 | 78.6172 | 6.912 | 186.7688 | 76.2877 | 219.8676 | 8.6091 | 44.2108 | 3.0379 | 104 | 40.4274 | 0 | 239.8587 | 0
8625 | 724.004 | 3.6586 | 24.7558 | 91.9881 | 79.552 | 9.5003 | 63.2746 | 5.8189 | 6.3777 | 35.6075 | 79.4344 | 6.2014 | 189.1773 | 77.0217 | 217.4689 | 8.6234 | 43.8464 | 3.6695 | 103 | 40.8153 | 0 | 235.3293 | 0
8626 | 721.1061 | 2.7858 | 24.4795 | 90.5654 | 77.5509 | 11.3995 | 63.3784 | 4.7416 | 5.5963 | 50.0226 | 78.0329 | 4.6542 | 190.4142 | 77.8629 | 214.6856 | 8.2333 | 42.92 | 3.7681 | 105 | 41.6572 | 0 | 225.5225 | 0.012321
8627 | 723.5218 | 2.474 | 24.4918 | 92.9174 | 79.5506 | 9.5005 | 64.7526 | 4.337 | 5.287 | 51.2797 | 77.9714 | 4.0901 | 185.538 | 78.8117 | 213.5202 | 8.1593 | 42.6363 | 3.7076 | 107 | 42.4317 | 0 | 232.9877 | 0.019996
8628 | 723.525 | 2.5723 | 24.5099 | 93.7797 | 79.5484 | 9.5 | 64.8012 | 4.6854 | 5.2081 | 47.995 | 81.8064 | 4.1536 | 184.1836 | 81.2028 | 209.3737 | 8.3323 | 43.7745 | 3.7158 | 104 | 39.3572 | 0 | 234.7042 | 0.023019
8629 | 723.4953 | 2.5844 | 24.448 | 91.5442 | 79.5501 | 9.5 | 64.7041 | 5.0621 | 5.0361 | 47.5407 | 92.1815 | 4.1344 | 187.4285 | 84.9915 | 206.7111 | 8.0204 | 44.4479 | 3.7191 | 109 | 39.5421 | 0 | 223.2328 | 0.028569
8630 | 725.9219 | 2.6582 | 24.5324 | 91.267 | 76.5497 | 12.3492 | 65.5275 | 5.1778 | 5.1786 | 46.5014 | 96.7492 | 4.091 | 192.4901 | 91.3427 | 207.0419 | 8.004 | 45.5924 | 3.6946 | 121 | 41.4791 | 0 | 226.4889 | 0.010338
8631 | 732.3366 | 2.3563 | 25.0439 | 91.3544 | 79.5435 | 9.5034 | 65.4117 | 5.2731 | 5.3245 | 42.8733 | 98.9813 | 4.0996 | 193.7073 | 92.0528 | 209.8293 | 7.4031 | 47.8005 | 3.6773 | 121 | 41.3415 | 0 | 227.4618 | 0.0065667
8632 | 747.4258 | 3.5972 | 24.7466 | 94.208 | 79.5476 | 9.5 | 65.5347 | 4.946 | 5.7585 | 42.6162 | 102.3701 | 5.4393 | 193.1075 | 91.1294 | 214.4466 | 7.5028 | 47.4166 | 3.787 | 120 | 44.8429 | 0 | 229.941 | 0
8633 | 763.7967 | 4.6903 | 24.6074 | 95.2683 | 79.5492 | 9.4974 | 65.7864 | 4.1211 | 6.2138 | 32.6666 | 104.484 | 6.7022 | 192.7527 | 90.9443 | 219.3202 | 7.718 | 45.2285 | 3.8989 | 116 | 45.4415 | 0 | 236.5361 | 0
8634 | 781.6365 | 4.626 | 24.4613 | 96.3211 | 78.5471 | 10.4497 | 65.7645 | 4.2965 | 6.5808 | 27.8803 | 103.5861 | 6.88 | 191.6562 | 93.4343 | 220.3318 | 7.7085 | 44.8854 | 3.9263 | 110 | 42.0554 | 0 | 229.4339 | 0
8635 | 789.5258 | 4.689 | 24.3877 | 95.4022 | 80.5483 | 8.5505 | 66.248 | 4.8248 | 6.7803 | 26.5818 | 102.3232 | 9.8163 | 193.2637 | 89.2885 | 233.4877 | 7.9181 | 45.0411 | 3.9091 | 103 | 42.7317 | 0 | 233.4295 | 0
8636 | 782.8131 | 4.4442 | 24.4847 | 96.3748 | 79.5498 | 9.4997 | 65.785 | 4.9659 | 6.5835 | 25.9671 | 96.9024 | 11.0211 | 195.6135 | 88.2374 | 243.4544 | 7.7741 | 44.6858 | 3.9279 | 112 | 41.8975 | 0 | 233.5806 | 0
8637 | 750.4594 | 4.6027 | 24.4673 | 95.6006 | 79.5463 | 9.5 | 63.5722 | 4.9427 | 6.4278 | 26.1001 | 84.9898 | 8.094 | 196.8456 | 82.4003 | 225.9123 | 7.7833 | 44.7131 | 3.7318 | 105 | 41.6344 | 0 | 229.309 | 0
8638 | 740.4813 | 4.4648 | 24.5347 | 96.6046 | 79.5499 | 9.5 | 62.8504 | 4.9528 | 6.6193 | 26.222 | 81.1966 | 6.8719 | 193.9446 | 76.4 | 214.9204 | 7.8904 | 44.3888 | 3.5932 | 109 | 40.797 | 0 | 229.3988 | 0
8639 | 733.0893 | 3.7797 | 24.558 | 96.1273 | 80.5513 | 8.5503 | 63.2328 | 4.0875 | 6.3092 | 26.2551 | 80.0405 | 6.9091 | 190.0332 | 79.6172 | 213.6394 | 7.7964 | 44.3359 | 3.3149 | 109 | 40.513 | 0 | 228.1072 | 0
8640 | 722.4602 | 2.7353 | 24.6498 | 95.3793 | 79.5499 | 9.5024 | 67.1562 | 3.9003 | 6.279 | 26.2891 | 78.0693 | 7.1137 | 186.3989 | 80.7351 | 211.8266 | 7.9241 | 44.2206 | 3.1798 | 106 | 41.0306 | 0 | 225.9706 | 0
8641 | 725.1178 | 2.4561 | 24.5195 | 96.3752 | 80.5514 | 8.55 | 68.0304 | 4.6 | 6.1222 | 26.0739 | 77.1752 | 6.9657 | 183.9238 | 78.2662 | 213.5402 | 7.8068 | 44.1903 | 3.1738 | 104 | 40.5046 | 0 | 230.2112 | 0
8642 | 717.1766 | 2.6823 | 24.5752 | 95.726 | 79.5573 | 9.4974 | 67.7453 | 4.839 | 6.3267 | 26.3207 | 75.814 | 6.8959 | 183.8915 | 82.8165 | 218.8511 | 7.9715 | 44.1915 | 3.1941 | 103 | 40.7126 | 0 | 226.9574 | 0
8643 | 703.1626 | 2.5912 | 24.5492 | 94.7953 | 79.5531 | 9.5 | 66.3894 | 4.8307 | 6.3253 | 26.3111 | 75.6709 | 6.9136 | 183.8355 | 84.9402 | 221.9246 | 7.8538 | 44.2077 | 3.2258 | 108 | 39.9542 | 0 | 235.9779 | 0
8644 | 701.0303 | 2.5407 | 25.7856 | 94.9366 | 80.5501 | 8.5503 | 66.0344 | 5.052 | 6.3445 | 26.2446 | 76.2819 | 6.9163 | 183.8064 | 86.8288 | 221.5116 | 7.7865 | 44.3127 | 3.2238 | 105 | 40.9681 | 0 | 232.3003 | 0
8645 | 707.1787 | 2.9439 | 27.5024 | 93.6464 | 78.5555 | 10.4495 | 66.1537 | 4.962 | 6.4703 | 26.1908 | 76.8319 | 7.0028 | 182.5831 | 80.5604 | 223.92 | 7.9632 | 44.6521 | 3.1849 | 102 | 41.3927 | 0 | 269.4505 | 0
8646 | 713.5885 | 3.738 | 25.7464 | 93.4871 | 79.5542 | 9.5003 | 66.0816 | 4.5621 | 6.4885 | 26.1939 | 77.0643 | 7.0467 | 185.5265 | 80.4633 | 223.3175 | 7.812 | 46.343 | 3.1831 | 102 | 41.8933 | 0 | 277.5954 | 0
8647 | 723.5819 | 4.0775 | 26.1479 | 93.1696 | 78.5549 | 10.4497 | 66.8911 | 5.4465 | 6.7667 | 36.4469 | 83.8837 | 7.0562 | 187.6991 | 97.2215 | 230.1414 | 8.2966 | 45.0102 | 3.2051 | 122 | 42.678 | 0 | 268.1824 | 0
8648 | 727.5632 | 4.1178 | 29.4211 | 94.5061 | 73.7173 | 15.1987 | 67.1428 | 8.7879 | 6.6077 | 52.3406 | 103.3038 | 6.9865 | 189.5431 | 104.7724 | 259.6102 | 8.6799 | 44.7801 | 3.4333 | 144 | 42.4971 | 0 | 265.9775 | 0
8649 | 730.1196 | 3.5271 | 29.6067 | 92.9714 | 72.6368 | 16.1497 | 66.25 | 8.6601 | 5.8335 | 49.8809 | 108.9837 | 5.8689 | 194.0685 | 137.2185 | 275.0125 | 8.6482 | 44.672 | 3.9149 | 141 | 41.6495 | 0 | 257.8045 | 0
8650 | 735.4681 | 2.6546 | 29.1338 | 90.846 | 73.55 | 15.2003 | 65.5741 | 7.3065 | 5.0898 | 44.9184 | 106.3839 | 4.6777 | 198.5838 | 158.4917 | 275.7875 | 8.5849 | 44.2141 | 5.7261 | 139 | 40.798 | 0 | 252.0649 | 0.060103
8651 | 760.7474 | 2.8767 | 28.8892 | 90.4472 | 72.5502 | 16.1497 | 65.856 | 5.3544 | 5.1173 | 45.0778 | 115.0313 | 4.2369 | 194.8368 | 162.9057 | 271.5544 | 8.1488 | 44.868 | 8.886 | 140 | 39.797 | 0 | 258.9346 | 0.025054
8652 | 771.2893 | 3.3065 | 29.827 | 90.5334 | 73.5503 | 15.2003 | 65.5815 | 4.3302 | 5.2556 | 41.7792 | 123.8735 | 4.1196 | 200.7918 | 161.9742 | 272.309 | 8.1773 | 45.247 | 5.8341 | 141 | 41.1612 | 0 | 248.0801 | 0.024178
8653 | 774.419 | 3.1062 | 29.314 | 90.0578 | 74.543 | 14.2503 | 64.0881 | 4.5958 | 5.3869 | 40.384 | 128.3449 | 4.0451 | 210.3523 | 166.0208 | 277.2504 | 8.2105 | 47.2106 | 3.9496 | 150 | 41.486 | 0 | 254.686 | 0.056931
8654 | 773.3845 | 2.633 | 28.9583 | 90.7496 | 74.5406 | 14.254 | 59.6203 | 4.9078 | 5.5805 | 42.0326 | 126.1153 | 4.0256 | 217.9513 | 167.2606 | 293.797 | 8.1307 | 48.0905 | 3.8967 | 150 | 41.7396 | 0 | 255.0142 | 0.041028
8655 | 775.0592 | 2.5123 | 28.9865 | 91.4769 | 73.552 | 15.1958 | 65.0111 | 5.2266 | 5.5325 | 46.4074 | 126.0428 | 4.0327 | 220.4696 | 168.607 | 293.8633 | 8.2015 | 47.7564 | 4.0631 | 142 | 43.7899 | 0 | 266.1105 | 0.020743
8656 | 758.9714 | 3.5569 | 29.0577 | 91.9462 | 71.55 | 17.0995 | 67.3954 | 5.8681 | 5.7122 | 41.8898 | 129.8228 | 4.7836 | 215.9896 | 150.2146 | 285.1467 | 8.3054 | 48.1224 | 4.2173 | 141 | 43.9347 | 0 | 256.2377 | 0
8657 | 746.4394 | 4.7033 | 29.3306 | 94.8991 | 77.5442 | 11.4016 | 74.4273 | 5.8191 | 6.4307 | 47.5536 | 134.4971 | 6.4984 | 213.4912 | 121.2508 | 272.5489 | 8.4505 | 48.1026 | 4.3935 | 143 | 44.2067 | 0 | 266.2856 | 0
8658 | 740.9409 | 4.807 | 28.1848 | 95.3985 | 79.545 | 9.5005 | 77.0842 | 5.4264 | 6.4363 | 40.3534 | 130.4337 | 7.1342 | 205.0428 | 99.6354 | 238.79 | 8.6833 | 48.693 | 4.6945 | 134 | 43.1887 | 0 | 232.0882 | 0
8659 | 737.6789 | 4.7316 | 25.5971 | 94.1639 | 78.5494 | 10.4497 | 67.607 | 5.1426 | 6.4547 | 29.0663 | 118.3164 | 7.1492 | 187.5891 | 89.8848 | 220.6348 | 8.4569 | 48.7754 | 4.4673 | 133 | 43.9725 | 0 | 238.552 | 0
8660 | 731.2373 | 4.7651 | 24.9916 | 94.3393 | 79.5515 | 9.5003 | 65.6124 | 5.1584 | 6.4212 | 26.0225 | 110.5729 | 6.9985 | 178.7128 | 86.5616 | 222.6021 | 8.7862 | 46.7738 | 4.1626 | 118 | 43.3138 | 0 | 234.9859 | 0
8661 | 724.0003 | 4.4771 | 25.0867 | 94.2835 | 79.5533 | 9.5 | 66.7026 | 5.8495 | 6.6695 | 26.0628 | 103.6769 | 6.9158 | 174.9987 | 83.0139 | 219.7276 | 8.8302 | 44.7735 | 3.8908 | 111 | 42.7813 | 0 | 230.2412 | 0
8662 | 717.7048 | 4.4773 | 25.1512 | 94.6905 | 78.552 | 10.4497 | 63.0995 | 5.6936 | 6.6725 | 26.0698 | 90.6601 | 7.1249 | 168.9318 | 80.1811 | 218.9995 | 8.1853 | 44.4612 | 3.3945 | 112 | 41.9771 | 0 | 226.1508 | 0
8663 | 709.8921 | 3.9915 | 25.1213 | 94.3814 | 79.5527 | 9.5003 | 61.8508 | 5.4852 | 6.3577 | 25.753 | 84.6392 | 7.0095 | 164.8761 | 81.0409 | 211.5785 | 7.7991 | 45.085 | 3.2082 | 111 | 41.4599 | 0 | 225.7161 | 0
8664 | 705.5202 | 3.2439 | 25.1136 | 93.9009 | 79.5548 | 9.5 | 64.6349 | 5.2062 | 6.2189 | 25.6598 | 81.8238 | 6.9441 | 163.3765 | 78.9606 | 208.4277 | 7.586 | 45.5145 | 3.1756 | 102 | 42.0546 | 0 | 225.0261 | 0
8665 | 709.3761 | 2.861 | 24.978 | 93.8063 | 79.5562 | 9.5 | 65.5988 | 4.5344 | 6.3894 | 25.7578 | 79.2968 | 6.9703 | 167.2303 | 79.6945 | 209.6815 | 7.7892 | 48.1982 | 3.1635 | 105 | 41.6755 | 0 | 233.3025 | 0
8666 | 710.3687 | 2.9125 | 25.0808 | 93.3731 | 79.5513 | 9.5 | 65.6071 | 4.4326 | 6.2974 | 25.778 | 81.6937 | 6.9554 | 170.2766 | 80.6208 | 210.7989 | 7.7131 | 49.1471 | 3.1796 | 102 | 41.12 | 0 | 230.5011 | 0
8667 | 703.6638 | 2.7856 | 24.9598 | 92.9015 | 78.553 | 10.4497 | 66.1895 | 5.1214 | 6.2414 | 25.6718 | 84.6075 | 6.948 | 168.3801 | 80.307 | 216.2587 | 7.7008 | 49.2041 | 3.2029 | 107 | 40.0032 | 0 | 234.0686 | 0
8668 | 711.4088 | 2.6341 | 24.9187 | 92.6699 | 77.5543 | 11.3997 | 65.9294 | 5.4585 | 6.3799 | 25.8407 | 84.7929 | 6.9471 | 164.9684 | 78.7778 | 218.7445 | 7.6595 | 49.0885 | 3.1839 | 102 | 40.0179 | 0 | 232.8905 | 0
8669 | 710.2137 | 3.0748 | 25.0616 | 92.3948 | 79.5532 | 9.5005 | 66.0728 | 5.4876 | 6.3676 | 26.1532 | 83.6681 | 6.9779 | 168.8938 | 78.7079 | 213.9593 | 7.5293 | 50.8592 | 3.1647 | 102 | 40.8211 | 0 | 263.4257 | 0
8670 | 722.1701 | 4.1916 | 35.1563 | 92.3417 | 79.5511 | 9.5 | 71.7714 | 5.8526 | 6.4833 | 26.6 | 81.2101 | 7.7582 | 181.5099 | 86.4425 | 213.9904 | 7.7523 | 53.2425 | 3.1729 | 100 | 41.3337 | 0 | 310.6354 | 0
8671 | 758.7567 | 5.4677 | 46.6354 | 98.1368 | 78.5505 | 10.4497 | 83.5203 | 5.4321 | 9.1057 | 42.9777 | 88.8308 | 14.4729 | 202.6748 | 121.1256 | 224.4362 | 7.7219 | 50.4046 | 5.0715 | 129 | 44.3261 | 0 | 348.993 | 0
8672 | 785.5235 | 6.1523 | 76.3624 | 99.0701 | 72.5524 | 16.1484 | 99.7447 | 5.0081 | 12.4965 | 70.4777 | 124.9629 | 25.9003 | 228.6441 | 148.7754 | 260.6425 | 12.9271 | 51.7754 | 4.7493 | 145 | 46.3872 | 0 | 391.8839 | 0
8673 | 803.6414 | 5.5819 | 85.8666 | 107.3662 | 71.5499 | 17.0997 | 112.0822 | 6.6083 | 13.0818 | 72.2825 | 142.0054 | 28.0662 | 245.3163 | 190.3911 | 291.5785 | 22.9842 | 54.3383 | 3.8026 | 148 | 48.9381 | 0 | 422.7199 | 0
8674 | 806.594 | 4.6156 | 85.8784 | 107.8125 | 72.5429 | 16.1503 | 115.1719 | 8.6924 | 12.521 | 65.6067 | 149.4643 | 24.9886 | 255.6501 | 207.9517 | 307.6361 | 24.9029 | 54.8785 | 5.2642 | 149 | 47.7361 | 0 | 426.7823 | 0.026662
8675 | 832.6185 | 4.2697 | 86.5232 | 109.9024 | 70.5477 | 18.0495 | 114.1989 | 9.5201 | 12.2341 | 67.4765 | 158.7568 | 25.1782 | 263.2723 | 213.6785 | 318.5918 | 24.2009 | 56.1516 | 8.5365 | 148 | 44.4063 | 0 | 430.917 | 0.028479
8676 | 848.3781 | 4.5234 | 88.4009 | 112.1511 | 69.5495 | 18.9997 | 113.8582 | 9.6989 | 12.0682 | 68.2167 | 160.9949 | 25.151 | 269.2187 | 220.3663 | 330.4515 | 24.4924 | 58.9145 | 5.418 | 162 | 45.7941 | 0 | 434.9623 | 0.043549
8677 | 852.3654 | 4.2547 | 88.885 | 113.6944 | 70.5494 | 18.0503 | 113.4451 | 9.7675 | 11.8999 | 63.2841 | 161.6348 | 24.3549 | 268.1338 | 224.217 | 326.5654 | 23.2792 | 60.8465 | 3.8575 | 163 | 45.9879 | 0 | 435.3055 | 0.034493
8678 | 854.7057 | 3.862 | 86.9493 | 113.4574 | 69.546 | 18.9997 | 112.6036 | 9.1116 | 12.0625 | 62.4546 | 164.8687 | 24.4291 | 266.5741 | 223.2989 | 324.0185 | 22.7363 | 62.0139 | 4.0261 | 150 | 45.7755 | 0 | 446.0607 | 0.03627
8679 | 866.9902 | 3.5662 | 86.4559 | 115.4977 | 67.5452 | 20.8995 | 113.0889 | 8.5041 | 12.2582 | 59.5221 | 166.234 | 24.4075 | 268.7436 | 222.5909 | 331.583 | 23.2756 | 61.374 | 3.845 | 158 | 49.3848 | 0 | 442.7086 | 0.01789
8680 | 879.22 | 4.8317 | 77.87 | 112.7026 | 68.5445 | 19.9503 | 109.7815 | 8.5801 | 12.4577 | 65.0925 | 160.7335 | 24.9199 | 282.9038 | 199.8028 | 328.1567 | 21.6515 | 61.8947 | 4.1489 | 154 | 50.5049 | 0 | 433.405 | 0
8681 | 877.6173 | 5.3975 | 46.3743 | 110.7151 | 76.5453 | 12.3521 | 98.4453 | 7.8227 | 13.294 | 68.5059 | 148.0338 | 25.061 | 285.2988 | 171.7524 | 298.9435 | 13.7035 | 60.7576 | 4.7655 | 145 | 48.8172 | 0 | 355.1684 | 0
8682 | 886.5092 | 4.8726 | 29.5693 | 103.3097 | 78.549 | 10.4505 | 89.6035 | 6.5781 | 13.6 | 61.2433 | 139.9704 | 25.0482 | 263.7517 | 149.7507 | 277.0861 | 10.8256 | 56.8761 | 5.1961 | 141 | 49.6718 | 0 | 292.7502 | 0
8683 | 869.3349 | 4.5343 | 26.2421 | 95.5194 | 77.555 | 11.3997 | 81.5819 | 6.0415 | 12.3335 | 45.8247 | 135.4716 | 21.6063 | 245.5079 | 128.7687 | 255.9562 | 10.3105 | 55.6236 | 4.7999 | 148 | 47.4339 | 0 | 268.6058 | 0
8684 | 852.1813 | 4.6972 | 25.2755 | 93.6119 | 78.5581 | 10.4503 | 71.3976 | 6.0917 | 8.6112 | 40.5906 | 128.2232 | 11.2104 | 224.3552 | 116.6525 | 239.8954 | 9.9236 | 50.9998 | 4.3215 | 131 | 44.4997 | 0 | 245.6815 | 0
8685 | 832.0019 | 4.887 | 24.7651 | 94.1699 | 79.5546 | 9.5003 | 68.5537 | 5.6986 | 6.8718 | 37.6908 | 107.2183 | 7.2377 | 202.0008 | 113.3387 | 235.3161 | 10.1131 | 49.0496 | 3.8572 | 119 | 43.0797 | 0 | 234.743 | 0
8686 | 813.622 | 4.8044 | 24.677 | 93.5295 | 78.5486 | 10.4497 | 68.2767 | 5.4879 | 6.6082 | 30.1731 | 86.9534 | 7.1766 | 180.1829 | 109.6607 | 232.5359 | 10.0549 | 48.7716 | 3.2608 | 112 | 40.8943 | 0 | 226.9938 | 0
8687 | 785.5217 | 4.149 | 24.6938 | 93.0217 | 79.5525 | 9.5003 | 60.5507 | 5.4163 | 6.4668 | 27.3262 | 79.9038 | 7.167 | 168.3538 | 107.5924 | 232.9381 | 9.9882 | 48.6423 | 3.1444 | 112 | 42.4144 | 0 | 229.5061 | 0
8688 | 766.4644 | 3.1599 | 24.7214 | 94.4306 | 78.5551 | 10.4497 | 62.2594 | 6.0509 | 6.4228 | 27.1223 | 78.9617 | 7.2023 | 164.0545 | 105.1583 | 231.0143 | 9.9773 | 48.8862 | 2.9709 | 106 | 41.6068 | 0 | 228.4608 | 0
8689 | 766.9516 | 2.8663 | 24.7611 | 93.688 | 79.5536 | 9.5029 | 66.1956 | 7.6353 | 6.2337 | 28.6614 | 79.226 | 7.2076 | 164.4972 | 101.2711 | 228.3163 | 9.8974 | 48.8211 | 2.766 | 108 | 41.9511 | 0 | 234.3538 | 0
8690 | 761.8697 | 2.8311 | 24.9433 | 93.7625 | 78.5575 | 10.4471 | 59.0742 | 7.2388 | 6.4542 | 30.0314 | 78.6794 | 7.2248 | 165.9852 | 96.3287 | 231.6618 | 10.1432 | 48.9377 | 3.7048 | 104 | 42.2526 | 0 | 242.2595 | 0
8691 | 738.0883 | 2.7716 | 24.982 | 94.5293 | 79.5477 | 9.5029 | 57.3723 | 6.5796 | 6.5128 | 30.1412 | 77.0678 | 7.2006 | 165.5952 | 96.0033 | 233.3758 | 10.0402 | 48.9066 | 4.0418 | 105 | 42.6159 | 0 | 245.6839 | 0
8692 | 746.5586 | 2.6551 | 25.0044 | 93.3147 | 78.5554 | 10.45 | 64.0035 | 7.1146 | 6.4895 | 30.0926 | 75.9467 | 7.1733 | 164.3658 | 96.5768 | 231.0946 | 10.0202 | 48.9041 | 3.9432 | 102 | 42.2767 | 0 | 248.746 | 0
8693 | 755.8113 | 3.1578 | 24.8638 | 92.8142 | 79.5566 | 9.5 | 60.2175 | 8.4095 | 6.3292 | 31.0748 | 75.8599 | 7.1806 | 167.3785 | 96.2852 | 223.5482 | 9.9207 | 50.4824 | 3.9255 | 103 | 42.7077 | 0 | 275.2136 | 0
8694 | 765.6965 | 3.9421 | 31.8892 | 93.677 | 78.5538 | 10.4471 | 61.84 | 6.9749 | 6.2861 | 31.7525 | 77.1281 | 7.9585 | 178.3905 | 101.1232 | 223.4616 | 9.9246 | 52.1881 | 3.9184 | 101 | 41.1589 | 0 | 309.7592 | 0
8695 | 785.9386 | 5.3421 | 44.198 | 96.0872 | 78.5468 | 10.4529 | 79.1162 | 6.3902 | 6.7357 | 47.6889 | 87.8025 | 13.4161 | 195.2848 | 127.7087 | 231.8104 | 10.1015 | 49.8265 | 3.9407 | 129 | 42.5306 | 0 | 350.5454 | 0
8696 | 821.468 | 5.8252 | 73.6582 | 98.6164 | 72.5551 | 16.1455 | 95.894 | 8.9526 | 6.7523 | 73.957 | 122.1285 | 25.9884 | 228.55 | 150.5142 | 257.2212 | 13.1886 | 51.7038 | 4.1794 | 159 | 49.6539 | 0 | 401.2132 | 0
8697 | 845.7445 | 5.3811 | 83.6142 | 105.1775 | 70.5517 | 18.0495 | 97.4887 | 8.9532 | 6.1462 | 77.9429 | 150.1107 | 29.6185 | 254.583 | 191.2071 | 293.4055 | 22.3812 | 55.5692 | 4.6263 | 163 | 50.5714 | 0 | 448.8193 | 0
8698 | 865.4459 | 8.3733 | 85.1824 | 108.7393 | 67.5499 | 20.8992 | 108.7601 | 8.4007 | 5.5807 | 73.5617 | 159.4166 | 29.6444 | 265.8169 | 207.8722 | 311.9836 | 25.1369 | 58.0717 | 5.0592 | 155 | 50.5217 | 0 | 448.213 | 0.017091
8699 | 901.8331 | 10.7756 | 87.7682 | 110.5963 | 69.5482 | 19.0005 | 117.6344 | 8.3714 | 5.7311 | 69.5002 | 162.5257 | 26.0583 | 278.5906 | 213.7877 | 320.6822 | 24.8754 | 59.6555 | 4.7952 | 162 | 50.8866 | 0 | 456.0001 | 0.025948
8700 | 914.9132 | 8.7793 | 89.6163 | 111.002 | 69.5494 | 19 | 114.3753 | 9.4624 | 5.3698 | 64.304 | 163.4762 | 23.9601 | 278.0896 | 218.2331 | 327.6576 | 25.0541 | 60.8107 | 3.8623 | 158 | 52.422 | 0 | 462.1768 | 0.065605
8701 | 917.2859 | 5.5127 | 88.4159 | 111.0899 | 68.551 | 19.9497 | 117.9135 | 9.2037 | 5.2373 | 59.662 | 163.7599 | 24.2338 | 271.6036 | 221.33 | 330.1738 | 25.2143 | 61.3162 | 3.3074 | 153 | 50.9798 | 0 | 453.2897 | 0.060846
8702 | 932.0161 | 4.3307 | 88.1363 | 112.174 | 70.5483 | 18.0505 | 120.7012 | 8.8659 | 5.2528 | 61.8378 | 164.4141 | 24.3091 | 267.6113 | 224.9378 | 328.65 | 25.2638 | 62.9706 | 3.6457 | 154 | 50.5993 | 0 | 451.5165 | 0.023944
8703 | 941.109 | 3.6694 | 89.0554 | 112.743 | 70.5506 | 18.05 | 114.4763 | 8.2137 | 5.3503 | 63.2932 | 164.6421 | 23.9684 | 270.3849 | 228.8699 | 328.1315 | 25.4627 | 61.2398 | 3.9393 | 152 | 52.9301 | 0 | 428.9962 | 0.013543
8704 | 931.1744 | 4.7594 | 78.8408 | 113.5476 | 70.5484 | 18.05 | 105.8453 | 7.6196 | 5.4258 | 63.0508 | 159.2094 | 25.1364 | 278.1469 | 210.417 | 323.6741 | 22.9565 | 61.8344 | 4.0356 | 150 | 55.1617 | 0 | 434.9416 | 0
8705 | 927.3661 | 5.6869 | 47.1462 | 113.3208 | 73.5486 | 15.2008 | 98.6832 | 7.7685 | 6.1997 | 65.5658 | 144.2007 | 26.205 | 272.996 | 191.7414 | 307.0534 | 14.3112 | 61.0583 | 3.8208 | 145 | 53.7501 | 0 | 382.0987 | 0
8706 | 895.3047 | 5.9216 | 30.2518 | 106.1165 | 78.5496 | 10.4513 | 92.1959 | 7.378 | 6.4283 | 61.583 | 133.0363 | 25.5395 | 252.2378 | 170.0229 | 277.908 | 10.4495 | 58.1377 | 3.6269 | 135 | 52.0694 | 0 | 313.8383 | 0
8707 | 872.9605 | 5.5138 | 27.3706 | 96.689 | 79.5522 | 9.5003 | 82.4863 | 6.9834 | 6.3283 | 48.9174 | 127.0981 | 21.2777 | 223.4276 | 133.6953 | 261.8965 | 9.5497 | 54.5513 | 3.4809 | 136 | 50.7405 | 0 | 281.5351 | 0
8708 | 843.5211 | 4.9257 | 26.4862 | 94.264 | 79.5528 | 9.5 | 67.2853 | 6.3228 | 6.522 | 45.1199 | 121.3291 | 10.8202 | 205.3153 | 106.6016 | 247.0611 | 9.1348 | 50.1234 | 3.3362 | 118 | 50.7701 | 0 | 258.6925 | 0
8709 | 825.5792 | 4.5991 | 25.8448 | 94.7475 | 78.5578 | 10.4497 | 67.7375 | 5.9588 | 6.6385 | 40.2339 | 108.4986 | 7.5342 | 192.0354 | 96.6724 | 235.355 | 9.1039 | 48.7128 | 3.1228 | 114 | 47.9956 | 0 | 262.2116 | 0
8710 | 813.7076 | 4.5776 | 25.3316 | 95.2243 | 79.5526 | 9.5003 | 69.4991 | 5.1425 | 6.5298 | 32.1574 | 89.5359 | 7.3059 | 176.8709 | 91.7875 | 219.025 | 9.2853 | 48.755 | 2.5656 | 122 | 46.162 | 0 | 247.7615 | 0
8711 | 800.2089 | 4.0872 | 25.3911 | 93.627 | 78.553 | 10.4497 | 68.5241 | 4.7079 | 6.472 | 28.5095 | 80.8639 | 7.1407 | 170.086 | 92.7711 | 212.7091 | 9.129 | 48.2101 | 2.3381 | 114 | 45.5625 | 0 | 246.6468 | 0
8712 | 782.1247 | 5.522 | 25.3636 | 93.1428 | 78.5552 | 10.45 | 68.3794 | 4.8802 | 6.2759 | 27.3182 | 79.6117 | 7.1475 | 169.1881 | 87.5551 | 213.5506 | 9.1543 | 47.9309 | 2.3185 | 110 | 44.504 | 0 | 238.1236 | 0
8713 | 779.9834 | 4.0349 | 25.4639 | 93.1936 | 79.5567 | 9.5003 | 68.3803 | 5.8234 | 6.3003 | 27.0559 | 79.7845 | 7.1781 | 167.1112 | 81.4415 | 214.7973 | 9.0938 | 48.1885 | 2.3252 | 104 | 42.7548 | 0 | 240.3601 | 0
8714 | 769.0728 | 3.2911 | 25.5235 | 93.0876 | 79.5539 | 9.5 | 68.3365 | 5.8895 | 6.3185 | 27.0293 | 79.2455 | 7.1745 | 165.0205 | 80.4097 | 220.0436 | 9.0666 | 48.1283 | 2.3779 | 102 | 42.8937 | 0 | 246.5819 | 0
8715 | 761.0923 | 2.9274 | 25.4418 | 92.9963 | 78.554 | 10.4497 | 68.6718 | 5.7836 | 6.257 | 27.1725 | 78.734 | 7.1667 | 163.4241 | 79.3357 | 221.3001 | 9.2338 | 48.1912 | 2.3627 | 101 | 42.954 | 0 | 244.6425 | 0
8716 | 775.7742 | 2.8907 | 25.5782 | 92.8921 | 78.5561 | 10.45 | 68.7797 | 5.7946 | 6.2738 | 27.2303 | 77.9615 | 7.3669 | 163.9322 | 78.6303 | 219.0558 | 9.2262 | 48.1731 | 2.3387 | 102 | 43.8007 | 0 | 250.877 | 0
8717 | 777.8465 | 3.2074 | 25.5699 | 93.5816 | 77.5581 | 11.3997 | 68.4854 | 5.025 | 6.2863 | 27.3073 | 78.1629 | 7.3026 | 169.2462 | 78.6863 | 218.1269 | 9.2018 | 49.7876 | 2.3393 | 101 | 45.3112 | 0 | 268.8766 | 0
8718 | 786.2065 | 3.7477 | 32.8453 | 93.2301 | 79.5548 | 9.5005 | 73.6208 | 4.7027 | 6.2146 | 27.4416 | 79.1773 | 7.9827 | 178.8816 | 88.4331 | 218.2341 | 9.0438 | 51.9504 | 2.3599 | 99 | 44.1186 | 0 | 309.4529 | 0
8719 | 806.6227 | 5.1658 | 43.3286 | 95.6068 | 76.5509 | 12.3492 | 82.0613 | 5.0248 | 6.3764 | 42.3043 | 89.0868 | 13.442 | 196.0823 | 121.5846 | 223.4186 | 9.1887 | 49.1734 | 2.4699 | 126 | 45.3283 | 0 | 346.7295 | 0
8720 | 840.1142 | 5.927 | 64.4892 | 99.2114 | 71.5522 | 17.0987 | 97.4717 | 6.5092 | 6.3375 | 69.5771 | 123.5891 | 24.0892 | 218.2722 | 159.4726 | 247.7544 | 13.5492 | 51.6404 | 3.5119 | 146 | 48.7643 | 0 | 374.7295 | 0
8721 | 881.2649 | 5.2389 | 81.9479 | 110.3785 | 69.5453 | 19.0048 | 107.5862 | 8.1269 | 5.9603 | 74.1496 | 147.1542 | 26.5824 | 240.9028 | 197.8517 | 282.3325 | 23.1982 | 58.0842 | 3.945 | 150 | 49.9918 | 0 | 430.9369 | 0
8722 | 900.9666 | 4.0755 | 87.7144 | 112.3763 | 70.5521 | 18.045 | 111.2819 | 8.8179 | 5.4573 | 68.8517 | 148.4059 | 24.7251 | 248.6579 | 173.5261 | 298.7641 | 27.0728 | 59.8118 | 5.6633 | 154 | 52.2577 | 0 | 437.8862 | 0.0090481
8723 | 910.5542 | 3.8753 | 88.6638 | 112.3068 | 71.5483 | 17.1003 | 110.4018 | 9.8477 | 5.3458 | 68.5509 | 147.7462 | 23.938 | 265.2543 | 193.6721 | 315.0327 | 27.3182 | 60.5424 | 9.7559 | 149 | 55.6333 | 0 | 443.4881 | 0.017841
8724 | 913.9682 | 4.2008 | 88.3021 | 113.0793 | 70.5537 | 18.0497 | 116.0682 | 9.1328 | 5.317 | 64.9417 | 152.5656 | 23.9786 | 277.4112 | 223.4229 | 334.983 | 26.624 | 62.7211 | 6.7106 | 152 | 54.3143 | 0 | 452.3482 | 0.021021
8725 | 924.5029 | 3.7208 | 88.7222 | 113.4051 | 71.5505 | 17.1003 | 117.4482 | 8.7205 | 5.2355 | 65.4317 | 159.7597 | 23.9541 | 278.8887 | 232.2784 | 339.2033 | 25.8819 | 61.9323 | 4.6695 | 152 | 54.6534 | 0 | 449.2273 | 0.019806
8726 | 919.1978 | 3.4535 | 89.8966 | 115.3972 | 71.5472 | 17.1 | 117.5006 | 9.4562 | 5.1168 | 66.3065 | 165.5817 | 23.7794 | 286.1585 | 237.8617 | 338.5792 | 25.8807 | 64.7832 | 4.7604 | 151 | 54.6406 | 0 | 447.9091 | 0.01251
8727 | 909.154 | 3.2852 | 88.8223 | 116.0355 | 71.5447 | 17.1 | 120.3425 | 8.8004 | 5.2448 | 66.6971 | 163.5441 | 23.8181 | 290.5425 | 239.602 | 345.1336 | 25.8844 | 66.0769 | 4.9555 | 160 | 54.6677 | 0 | 432.5899 | 0.0036406
8728 | 908.2953 | 5.4175 | 78.1604 | 118.972 | 69.5413 | 19.0048 | 116.5873 | 7.641 | 5.8188 | 66.428 | 157.6448 | 26.1906 | 281.6996 | 220.6509 | 351.8176 | 22.6428 | 65.5912 | 5.4703 | 160 | 55.2865 | 0 | 436.0949 | 0
8729 | 919.1878 | 6.3879 | 47.0129 | 117.646 | 78.5487 | 10.4471 | 101.268 | 7.2835 | 6.7438 | 68.3157 | 142.2027 | 29.2067 | 265.7309 | 187.2698 | 325.6298 | 13.7779 | 63.0315 | 5.4976 | 150 | 53.9239 | 0 | 359.0692 | 0
8730 | 918.5172 | 5.6811 | 29.5239 | 108.7938 | 78.5491 | 10.45 | 90.9622 | 5.9335 | 6.729 | 60.9734 | 133.8726 | 30.0653 | 250.0876 | 151.1349 | 299.1346 | 9.6657 | 58.6622 | 5.325 | 145 | 52.9665 | 0 | 299.6784 | 0
8731 | 898.7512 | 5.2472 | 25.632 | 97.4635 | 79.5465 | 9.5003 | 85.6884 | 4.7887 | 6.4971 | 47.5653 | 130.9421 | 25.2206 | 230.0453 | 118.8169 | 290.9938 | 8.9796 | 56.6063 | 5.0395 | 146 | 52.3611 | 0 | 265.3634 | 0
8732 | 869.3978 | 4.9859 | 25.2007 | 94.7981 | 76.5512 | 12.3492 | 75.8703 | 4.7211 | 6.4846 | 42.0351 | 124.7232 | 12.1538 | 211.0139 | 106.6773 | 272.5837 | 8.6602 | 52.3932 | 4.5356 | 129 | 49.4066 | 0 | 243.9403 | 0
8733 | 844.4562 | 4.9526 | 25.1213 | 94.6183 | 79.5522 | 9.5008 | 72.0069 | 5.1867 | 6.564 | 38.3632 | 116.584 | 7.5308 | 198.7034 | 96.7299 | 243.9443 | 8.642 | 50.637 | 3.8688 | 118 | 47.8706 | 0 | 234.8143 | 0
8734 | 818.434 | 9.6836 | 25.0921 | 94.7314 | 79.5547 | 9.5 | 71.4619 | 5.3807 | 6.8982 | 31.936 | 93.3903 | 7.437 | 183.52 | 92.9656 | 228.4246 | 8.4744 | 50.329 | 3.0056 | 115 | 46.3932 | 0 | 227.9553 | 0
8735 | 803.7939 | 10.9237 | 25.0351 | 94.5005 | 78.5515 | 10.4497 | 71.1463 | 5.3826 | 6.9483 | 28.4047 | 80.3111 | 7.3693 | 172.5456 | 89.0971 | 225.1173 | 8.5439 | 50.3546 | 2.6613 | 111 | 42.9502 | 0 | 227.5819 | 0
8736 | 785.1849 | 6.3385 | 24.9403 | 94.2702 | 79.5529 | 9.5003 | 71.0322 | 5.5674 | 6.8842 | 27.3017 | 78.8005 | 7.4182 | 162.4631 | 84.0206 | 222.127 | 8.4351 | 50.3176 | 2.6374 | 106 | 43.4158 | 0 | 227.4938 | 0
8737 | 780.6805 | 3.1375 | 25.0463 | 94.3619 | 78.5576 | 10.4497 | 71.3056 | 4.7687 | 7.5999 | 27.1143 | 79.3878 | 7.4211 | 160.1299 | 79.6648 | 216.4982 | 8.3455 | 50.42 | 2.6722 | 104 | 43.0507 | 0 | 226.1305 | 0
8738 | 774.5695 | 2.4756 | 25.0939 | 93.9697 | 79.5586 | 9.5003 | 70.8511 | 4.2924 | 7.5347 | 26.9967 | 79.8738 | 7.4024 | 161.1867 | 79.34 | 218.5549 | 8.4046 | 50.2719 | 2.6594 | 102 | 42.5987 | 0 | 229.4088 | 0
8739 | 761.1409 | 3.2121 | 25.1662 | 93.563 | 79.5551 | 9.5 | 70.4373 | 4.4798 | 6.743 | 27.1781 | 80.4728 | 7.6853 | 160.6727 | 80.5092 | 219.1633 | 8.246 | 50.4559 | 2.6323 | 100 | 42.6188 | 0 | 229.426 | 0
8740 | 775.0354 | 3.3342 | 25.2038 | 93.611 | 78.5558 | 10.4497 | 70.3195 | 5.1177 | 6.3825 | 27.3257 | 79.9605 | 7.5259 | 160.6184 | 79.4399 | 216.2792 | 8.4876 | 50.5083 | 2.6352 | 100 | 43.1849 | 0 | 231.7334 | 0
8741 | 784.629 | 3.2327 | 25.1608 | 94.3981 | 79.5563 | 9.5003 | 70.5209 | 5.6573 | 6.0605 | 27.2292 | 80.3686 | 7.3263 | 164.2134 | 79.3847 | 213.358 | 8.3719 | 51.9439 | 2.6528 | 98 | 44.2699 | 0 | 249.9142 | 0
8742 | 792.862 | 3.8465 | 32.1764 | 93.7882 | 79.5551 | 9.5 | 76.182 | 5.4925 | 6.0288 | 27.4822 | 81.1717 | 8.0886 | 175.9178 | 85.8541 | 214.5879 | 8.4118 | 54.1912 | 2.6588 | 97 | 44.2088 | 0 | 282.4566 | 0
8743 | 823.1803 | 4.8719 | 48.9854 | 96.1816 | 76.5519 | 12.3492 | 84.4949 | 5.3739 | 7.7227 | 42.0456 | 90.9884 | 13.562 | 203.3493 | 115.6062 | 221.1137 | 8.3577 | 51.4237 | 2.645 | 120 | 44.4633 | 0 | 315.5224 | 0
8744 | 862.0831 | 5.292 | 78.6466 | 99.2305 | 71.5517 | 17.0987 | 99.5768 | 4.9151 | 8.0145 | 67.9455 | 124.8128 | 24.1566 | 240.5046 | 139.3607 | 249.1126 | 10.6883 | 55.1344 | 3.0679 | 142 | 48.8959 | 0 | 355.522 | 0
8745 | 870.2735 | 5.8013 | 86.8643 | 108.742 | 70.5502 | 18.0497 | 110.5051 | 5.5606 | 6.6445 | 71.3873 | 150.7805 | 26.5703 | 259.378 | 188.6161 | 282.2325 | 19.4659 | 58.1801 | 3.7553 | 147 | 49.9368 | 0 | 414.3291 | 0
8746 | 890.5161 | 4.1806 | 88.055 | 110.9566 | 71.5492 | 17.1003 | 113.8472 | 6.5295 | 5.5331 | 69.6509 | 154.7798 | 24.4433 | 264.7229 | 208.9001 | 303.5849 | 22.9646 | 60.3492 | 6.2029 | 144 | 51.106 | 0 | 413.0075 | 0.0056921
8747 | 906.9599 | 3.0784 | 86.9991 | 112.4457 | 71.5461 | 17.1 | 115.4005 | 8.521 | 5.287 | 70.1773 | 153.1067 | 23.7223 | 269.9086 | 210.3707 | 315.628 | 23.0824 | 63.062 | 8.4605 | 142 | 52.0866 | 0 | 434.6711 | 0.013745
8748 | 911.3974 | 3.2027 | 87.6149 | 113.8066 | 71.5451 | 17.1 | 115.3772 | 9.9036 | 5.2413 | 67.3837 | 157.8671 | 23.9968 | 262.3631 | 215.601 | 328.5304 | 22.0615 | 64.7947 | 6.338 | 149 | 52.5517 | 0 | 437.665 | 0.021967
8749 | 926.3422 | 3.8465 | 87.628 | 115.6185 | 68.5509 | 19.9492 | 114.8372 | 10.4832 | 5.162 | 66.7463 | 162.5345 | 24.3529 | 256.986 | 219.6566 | 331.04 | 15.3965 | 63.527 | 4.3016 | 144 | 54.1409 | 0 | 424.52 | 0.028848
8750 | 930.785 | 3.6135 | 87.0918 | 116.9702 | 70.5432 | 18.0555 | 114.6149 | 10.2276 | 5.508 | 64.5243 | 162.2054 | 24.056 | 262.4542 | 224.0935 | 326.9109 | 11.6015 | 61.9169 | 4.5111 | 147 | 57.2612 | 0 | 409.3687 | 0.043714
8751 | 927.8589 | 3.0705 | 87.1641 | 120.3823 | 72.5522 | 16.1455 | 113.8619 | 8.5415 | 5.688 | 61.5052 | 162.9116 | 23.6777 | 261.9709 | 222.028 | 322.0054 | 11.9784 | 60.9579 | 4.7938 | 149 | 58.2711 | 0 | 397.3211 | 0.0064533
8752 | 909.1531 | 3.9667 | 76.485 | 123.4084 | 69.5495 | 18.9992 | 109.0006 | 7.1222 | 5.8501 | 66.7431 | 159.9329 | 24.6511 | 257.4744 | 198.5679 | 309.9678 | 12.0783 | 62.0982 | 5.1206 | 144 | 57.9058 | 0 | 385.8216 | 0
8753 | 891.3412 | 5.194 | 48.0698 | 119.9463 | 77.5455 | 11.4021 | 97.785 | 6.0524 | 6.5034 | 67.1995 | 146.8286 | 25.1258 | 254.671 | 170.3687 | 291.1719 | 10.7686 | 60.5395 | 5.2399 | 154 | 57.8395 | 0 | 324.3696 | 0
8754 | 877.9395 | 5.104 | 29.0408 | 112.6528 | 79.5481 | 9.5005 | 89.6097 | 5.5495 | 6.7883 | 55.3916 | 132.0027 | 24.9589 | 237.0853 | 138.0025 | 283.0095 | 9.548 | 57.3093 | 5.0114 | 144 | 55.369 | 0 | 275.6925 | 0
8755 | 874.8905 | 4.8612 | 25.4208 | 102.9853 | 79.5478 | 9.5 | 83.7581 | 5.3634 | 6.583 | 44.4617 | 116.212 | 20.6729 | 213.1532 | 110.9715 | 262.6843 | 8.7943 | 55.1411 | 5.0003 | 140 | 53.5554 | 0 | 244.5055 | 0
8756 | 854.9689 | 4.6036 | 25.1712 | 97.6322 | 79.5504 | 9.5 | 74.2405 | 5.1754 | 6.5452 | 41.2977 | 102.4135 | 11.6858 | 197.335 | 97.8343 | 239.9694 | 8.5767 | 52.7048 | 5.0275 | 121 | 51.3874 | 0 | 234.4453 | 0
8757 | 819.2214 | 4.3764 | 25.1463 | 96.5136 | 79.5554 | 9.5 | 69.6209 | 5.0281 | 6.452 | 39.3664 | 89.8362 | 7.4174 | 186.0914 | 95.3791 | 238.3478 | 8.4395 | 50.0556 | 4.3441 | 122 | 47.4771 | 0 | 222.9441 | 0
8758 | 801.4621 | 4.2612 | 25.0583 | 95.885 | 79.5551 | 9.5 | 69.3012 | 4.1946 | 6.504 | 33.5303 | 83.4938 | 7.2679 | 171.5471 | 90.3972 | 235.2083 | 8.4147 | 48.7512 | 3.3951 | 120 | 45.1747 | 0 | 221.6638 | 0
8759 | 790.19 | 3.6206 | 24.9328 | 95.5761 | 78.5488 | 10.4497 | 69.4703 | 3.9229 | 6.288 | 28.661 | 83.4108 | 7.2479 | 161.8229 | 85.043 | 228.7738 | 8.3919 | 48.6795 | 3.0316 | 117 | 45.0397 | 0 | 220.3344 | 0
8760 | 779.5218 | 3.3741 | 24.9395 | 95.8596 | 78.5512 | 10.45 | 69.8149 | 4.6314 | 6.086 | 27.3458 | 81.9466 | 7.2858 | 161.2945 | 81.3156 | 227.7679 | 8.4862 | 47.772 | 3.04 | 115 | 47.0935 | 0 | 217.0766 | 0
8761 | 774.3387 | 2.9628 | 25.0514 | 95.1067 | 79.5536 | 9.5029 | 69.9005 | 5.1948 | 6.278 | 26.7427 | 80.7627 | 7.3225 | 161.7024 | 77.8332 | 231.198 | 8.6059 | 45.3619 | 3.0296 | 106 | 45.5282 | 0 | 225.1372 | 0
8762 | 766.9695 | 2.5026 | 25.2264 | 95.9912 | 79.5543 | 9.5 | 69.7809 | 5.1263 | 6.2985 | 26.4121 | 80.4226 | 7.359 | 162.4069 | 75.3329 | 233.2804 | 8.5027 | 44.1287 | 3.0227 | 99 | 44.5422 | 0 | 227.0974 | 0
8763 | 749.8741 | 2.4207 | 25.2284 | 94.909 | 79.5567 | 9.4974 | 69.9808 | 4.8396 | 6.001 | 26.1569 | 80.5999 | 7.3675 | 161.5446 | 74.3734 | 228.548 | 8.4837 | 43.794 | 3.033 | 101 | 42.8172 | 0 | 222.3888 | 0
8764 | 754.8421 | 2.4744 | 25.2362 | 94.54 | 80.5524 | 8.5526 | 70.162 | 4.1401 | 6.0669 | 26.3559 | 80.7156 | 7.3527 | 160.6444 | 74.1896 | 220.0128 | 8.4227 | 43.7932 | 3.0612 | 98 | 42.8176 | 0 | 219.8453 | 0
8765 | 764.1012 | 2.871 | 25.1664 | 94.1713 | 79.5574 | 9.5 | 70.3746 | 3.7985 | 6.2637 | 26.818 | 80.8643 | 7.31 | 160.0657 | 74.2812 | 214.2782 | 8.6006 | 45.0386 | 3.2277 | 95 | 43.7594 | 0 | 217.2752 | 0
8766 | 765.1015 | 3.5565 | 25.2138 | 94.7638 | 79.5551 | 9.4974 | 69.8545 | 4.7564 | 6.295 | 27.0572 | 81.4801 | 7.2598 | 159.2338 | 74.1439 | 213.3893 | 8.5217 | 45.872 | 3.3014 | 95 | 43.1361 | 0 | 221.6768 | 0
8767 | 773.6105 | 3.8704 | 25.4766 | 95.0569 | 79.5475 | 9.5026 | 69.8797 | 5.1604 | 6.473 | 27.3865 | 82.0001 | 7.2441 | 159.6752 | 74.1782 | 214.4533 | 8.4716 | 44.8063 | 3.1274 | 94 | 43.8456 | 0 | 223.889 | 0
8768 | 778.0912 | 4.4185 | 25.5176 | 94.9544 | 79.5587 | 9.4974 | 70.052 | 5.0178 | 6.438 | 27.1761 | 84.0185 | 7.2594 | 165.7542 | 75.9655 | 216.5837 | 8.531 | 44.0837 | 3.277 | 98 | 45.9551 | 0 | 227.1815 | 0
8769 | 773.2674 | 4.3542 | 25.1171 | 94.4668 | 79.5553 | 9.5 | 69.5928 | 4.8765 | 6.36 | 37.8523 | 85.324 | 6.4297 | 170.0851 | 79.3842 | 215.9421 | 8.3419 | 43.9556 | 3.9171 | 100 | 45.7022 | 0 | 229.2069 | 0
8770 | 772.4107 | 3.9071 | 24.5751 | 92.0677 | 73.5513 | 15.1984 | 68.2527 | 5.4869 | 5.6209 | 49.1356 | 81.7924 | 5.0266 | 172.9926 | 85.1917 | 212.1445 | 8.2225 | 43.119 | 4.2713 | 103 | 45.9316 | 0 | 214.8067 | 0.0064175
8771 | 776.2225 | 3.245 | 24.4534 | 91.5616 | 73.5515 | 15.2 | 67.8295 | 5.5367 | 5.3803 | 47.902 | 80.8941 | 4.4021 | 176.9436 | 87.9108 | 212.9768 | 8.0118 | 42.8013 | 4.2113 | 105 | 46.3074 | 0 | 217.7051 | 0.014244
8772 | 778.2354 | 2.5996 | 24.4341 | 91.5444 | 79.5504 | 9.5042 | 67.8354 | 4.7509 | 5.3581 | 45.1953 | 82.008 | 4.3611 | 179.1379 | 90.6199 | 217.3291 | 7.9343 | 44.3882 | 4.1125 | 121 | 47.3309 | 0 | 214.99 | 0.012664
8773 | 777.0155 | 2.4908 | 24.4031 | 91.8265 | 80.5501 | 8.55 | 67.4641 | 4.5719 | 5.1307 | 42.3739 | 85.9445 | 4.3464 | 179.4205 | 93.1239 | 221.6281 | 7.924 | 44.8294 | 4.0706 | 119 | 47.9667 | 0 | 211.1754 | 0.012107
8774 | 780.0793 | 2.974 | 24.3977 | 92.4065 | 79.5477 | 9.5 | 67.2239 | 4.4564 | 5.0831 | 40.7019 | 87.3026 | 4.3838 | 179.0979 | 95.5888 | 225.6233 | 7.9171 | 43.7705 | 4.0506 | 127 | 47.7496 | 0 | 213.6833 | 0.014602
8775 | 779.9206 | 3.2604 | 24.4441 | 92.3034 | 79.5529 | 9.4974 | 67.9433 | 4.0325 | 5.3044 | 42.6027 | 83.395 | 4.4545 | 177.7089 | 99.6659 | 237.8539 | 8.1226 | 44.186 | 4.0601 | 136 | 48.7159 | 0 | 212.8895 | 0.0055995
8776 | 777.696 | 4.0445 | 24.6976 | 95.3266 | 80.5479 | 8.5526 | 68.5512 | 3.8767 | 5.8384 | 39.9516 | 84.1946 | 6.0253 | 179.2201 | 97.0045 | 249.7767 | 8.2144 | 44.3494 | 4.359 | 143 | 49.4402 | 0 | 221.8833 | 0
8777 | 780.261 | 4.6354 | 24.7732 | 96.5301 | 79.55 | 9.5 | 68.6064 | 4.095 | 6.2898 | 31.8594 | 84.1108 | 7.1373 | 175.7546 | 87.3982 | 254.4136 | 8.3617 | 43.6676 | 4.7976 | 147 | 47.7746 | 0 | 228.7109 | 0
8778 | 789.8392 | 4.6373 | 24.5643 | 95.1212 | 80.5526 | 8.5476 | 68.7806 | 4.5596 | 6.5381 | 26.6678 | 81.4927 | 7.1712 | 172.9742 | 85.5042 | 244.121 | 8.4373 | 43.3566 | 4.7984 | 142 | 46.72 | 0 | 229.2235 | 0
8779 | 782.9607 | 4.4807 | 24.7468 | 95.2488 | 79.55 | 9.4997 | 69.2857 | 4.9218 | 6.7461 | 25.9104 | 81.461 | 7.1733 | 172.5594 | 84.4276 | 234.7662 | 8.3858 | 43.3646 | 4.5093 | 138 | 45.966 | 0 | 229.7761 | 0
8780 | 775.489 | 4.2964 | 24.6783 | 94.9648 | 78.5509 | 10.4497 | 70.3164 | 4.9734 | 6.908 | 25.9615 | 81.9425 | 7.2074 | 170.363 | 80.3968 | 231.0524 | 8.4943 | 43.4585 | 4.1696 | 134 | 44.4308 | 0 | 229.5916 | 0
8781 | 773.162 | 4.1647 | 24.5914 | 94.185 | 77.5513 | 11.3997 | 70.4446 | 4.5758 | 6.9447 | 25.8713 | 81.7876 | 7.3681 | 165.933 | 77.0333 | 222.5495 | 8.5251 | 43.9306 | 3.7304 | 131 | 44.2762 | 0 | 226.5771 | 0
8782 | 773.2797 | 4.1126 | 24.6316 | 95.0385 | 79.5518 | 9.5005 | 69.8803 | 3.899 | 7.0004 | 25.8795 | 82.3166 | 7.3217 | 160.1429 | 75.8135 | 220.4137 | 8.4388 | 44.4884 | 3.2365 | 145 | 43.6759 | 0 | 221.333 | 0
8783 | 764.8213 | 4.0369 | 24.8283 | 94.4203 | 78.5524 | 10.4497 | 69.2516 | 3.8824 | 6.755 | 25.9566 | 81.6854 | 7.2574 | 157.0919 | 79.4282 | 224.0986 | 8.5474 | 44.0545 | 3.3579 | 137 | 43.7428 | 0 | 222.6105 | 0
8784 | 757.0266 | 3.4916 | 24.8179 | 94.3959 | 79.5522 | 9.5003 | 70.5103 | 4.621 | 6.632 | 26.4707 | 79.9684 | 7.3463 | 156.6692 | 80.2409 | 224.7454 | 8.4342 | 43.7237 | 3.3054 | 114 | 44.2202 | 0 | 220.5002 | 0
8785 | 759.4484 | 2.7331 | 24.9026 | 94.9045 | 79.5518 | 9.5026 | 70.8836 | 5.0373 | 6.614 | 26.8663 | 79.858 | 7.3774 | 157.7821 | 76.316 | 225.7992 | 8.4931 | 43.7841 | 2.9006 | 123 | 44.0308 | 0 | 219.5022 | 0
8786 | 744.25 | 2.7185 | 24.82 | 94.6642 | 77.5587 | 11.3968 | 69.8586 | 4.9327 | 6.504 | 26.2151 | 80.3706 | 7.3725 | 159.0172 | 74.782 | 228.5854 | 8.5648 | 43.8256 | 2.784 | 125 | 43.8948 | 0 | 218.899 | 0
8787 | 732.9612 | 3.1298 | 24.7933 | 94.5077 | 74.5546 | 14.2492 | 69.4131 | 4.6918 | 6.424 | 25.6002 | 79.7608 | 7.3664 | 159.3832 | 74.0579 | 231.7319 | 8.4638 | 43.8838 | 2.8184 | 121 | 44.0656 | 0 | 218.5546 | 0
8788 | 742.7762 | 2.9699 | 24.9182 | 95.2849 | 74.5539 | 14.25 | 69.5235 | 4.1946 | 6.316 | 25.5914 | 78.7135 | 7.3586 | 159.3545 | 73.4351 | 235.247 | 8.5382 | 43.777 | 2.9781 | 115 | 43.0061 | 0 | 216.7305 | 0
8789 | 744.3813 | 3.2628 | 25.0449 | 94.3843 | 75.5578 | 13.3003 | 70.1667 | 4.0338 | 6.2338 | 25.6863 | 78.3857 | 7.3691 | 159.6022 | 73.3178 | 235.4465 | 8.372 | 44.1758 | 2.8742 | 123 | 44.6465 | 0 | 218.4559 | 0
8790 | 747.0219 | 3.7831 | 25.0657 | 94.2739 | 79.5557 | 9.5011 | 70.0478 | 4.4811 | 6.4046 | 25.4942 | 78.7156 | 7.3749 | 159.7673 | 75.2387 | 228.1812 | 8.5354 | 45.5608 | 2.6062 | 122 | 43.7311 | 0 | 224.1703 | 0
8791 | 760.6686 | 3.9398 | 25.1662 | 93.8519 | 79.5534 | 9.5 | 69.9286 | 5.2959 | 6.4676 | 25.4314 | 80.2702 | 7.374 | 160.0437 | 75.8409 | 221.926 | 8.5178 | 44.7244 | 2.5128 | 109 | 44.1726 | 0 | 229.2733 | 0
8792 | 768.6246 | 3.995 | 25.124 | 93.0027 | 79.5522 | 9.5 | 69.84 | 5.5334 | 6.4749 | 25.4108 | 82.8441 | 7.3448 | 165.175 | 74.7971 | 221.999 | 8.8467 | 43.7589 | 2.8407 | 105 | 43.0712 | 0 | 220.5366 | 0
8793 | 766.048 | 3.7453 | 24.9326 | 91.645 | 78.5496 | 10.4526 | 68.9344 | 5.4357 | 6.0498 | 35.1411 | 83.1966 | 6.4762 | 170.2808 | 75.186 | 218.3337 | 9.0556 | 43.2181 | 3.3945 | 105 | 42.3176 | 0 | 214.7861 | 0
8794 | 768.9404 | 2.9002 | 24.8077 | 90.1578 | 76.5603 | 12.3466 | 68.2214 | 5.1285 | 5.5215 | 43.6478 | 81.333 | 5.04 | 171.1547 | 79.1286 | 212.4626 | 8.8116 | 42.6394 | 3.5324 | 101 | 43.5014 | 0 | 212.0664 | 0.025242
8795 | 773.3684 | 2.3581 | 24.6913 | 89.2736 | 77.5545 | 11.4003 | 67.9672 | 4.2883 | 6.1239 | 44.1033 | 79.928 | 4.866 | 168.0963 | 84.0716 | 206.7308 | 8.7688 | 42.4403 | 3.4822 | 102 | 41.7356 | 0 | 215.5808 | 0.031895
8796 | 773.2058 | 2.4675 | 24.7302 | 88.9294 | 77.5502 | 11.4 | 67.5223 | 3.8829 | 6.794 | 41.411 | 84.0766 | 4.7995 | 166.0746 | 85.0631 | 205.5452 | 8.257 | 42.3933 | 3.5143 | 102 | 40.2487 | 0 | 216.62 | 0.083597
8797 | 764.8332 | 2.6148 | 24.639 | 88.6625 | 79.5487 | 9.5032 | 67.7219 | 4.5621 | 6.082 | 41.8212 | 96.9943 | 4.5479 | 167.5459 | 85.3782 | 208.4234 | 8.4071 | 42.218 | 3.5183 | 112 | 42.0137 | 0 | 207.7396 | 0.066922
8798 | 762.2764 | 2.6184 | 25.1142 | 88.7476 | 79.5549 | 9.4974 | 69.1291 | 5.2342 | 5.2986 | 41.8863 | 103.0895 | 4.5138 | 173.0865 | 91.7009 | 209.5213 | 8.6853 | 42.6002 | 3.4858 | 113 | 42.5999 | 0 | 213.35 | 0.035725
8799 | 779.5388 | 2.6428 | 24.9884 | 89.1567 | 79.5506 | 9.5 | 67.7341 | 5.5757 | 5.2697 | 39.7632 | 100.8843 | 4.695 | 182.6852 | 96.0583 | 222.2123 | 8.6448 | 43.3084 | 3.4617 | 113 | 44.5593 | 0 | 217.6685 | 0.017006
8800 | 797.3595 | 3.4894 | 24.7211 | 90.2139 | 79.5499 | 9.5 | 65.3417 | 6.2245 | 5.3177 | 39.6869 | 101.6193 | 5.4047 | 187.0291 | 97.5463 | 237.3277 | 8.8663 | 43.0239 | 3.4817 | 121 | 45.3175 | 0 | 223.8929 | 0
8801 | 806.0709 | 4.7699 | 25.0383 | 92.1468 | 78.5513 | 10.4497 | 68.4833 | 5.9876 | 5.902 | 33.713 | 107.9787 | 6.9968 | 189.7972 | 96.7849 | 255.7618 | 9.1339 | 45.2591 | 3.6243 | 126 | 45.4049 | 0 | 232.8518 | 0
8802 | 802.1803 | 4.8993 | 25.2047 | 92.7593 | 75.5535 | 13.2992 | 69.2215 | 5.525 | 6.568 | 29.6772 | 117.5208 | 7.62 | 190.7773 | 94.5666 | 252.0825 | 9.1846 | 46.7095 | 3.7479 | 115 | 44.4496 | 0 | 240.0009 | 0
8803 | 806.9247 | 4.9399 | 25.0346 | 92.3877 | 76.5518 | 12.3503 | 60.452 | 5.7454 | 6.7976 | 29.3106 | 121.9038 | 7.4117 | 190.3164 | 91.3855 | 232.8283 | 9.3826 | 46.2288 | 3.7201 | 112 | 44.518 | 0 | 241.445 | 0
8804 | 805.1923 | 5.2546 | 24.9847 | 92.3871 | 77.5529 | 11.4003 | 61.1501 | 6.873 | 6.7518 | 27.3356 | 110.7935 | 7.3578 | 188.858 | 87.6736 | 226.9657 | 9.2146 | 45.3813 | 3.6815 | 117 | 44.9779 | 0 | 241.1748 | 0
8805 | 783.3434 | 4.9354 | 25.0425 | 92.9468 | 77.5521 | 11.4 | 67.949 | 7.8669 | 6.7386 | 26.4771 | 94.6782 | 7.3705 | 187.0411 | 84.7457 | 226.4784 | 9.263 | 44.1073 | 3.4542 | 116 | 44.9211 | 0 | 243.2822 | 0
8806 | 771.7098 | 4.7495 | 25.0444 | 94.9404 | 78.5495 | 10.4503 | 63.5857 | 6.9148 | 6.704 | 26.5178 | 84.8894 | 7.6608 | 185.4227 | 84.637 | 225.7415 | 9.2297 | 43.7947 | 2.9917 | 114 | 43.8488 | 0 | 246.9296 | 0
8807 | 757.8173 | 4.1534 | 25.0585 | 95.868 | 77.5492 | 11.4029 | 58.5878 | 6.1645 | 6.414 | 26.0448 | 80.3085 | 7.5218 | 173.651 | 82.6953 | 226.147 | 9.1869 | 44.0136 | 2.7537 | 105 | 44.7459 | 0 | 245.8799 | 0
8808 | 745.865 | 3.1852 | 25.164 | 96.1164 | 78.5581 | 10.4471 | 64.2297 | 7.351 | 6.2416 | 25.9079 | 78.1086 | 7.2061 | 164.6609 | 79.952 | 227.6711 | 9.2957 | 44.9966 | 2.7381 | 103 | 43.8673 | 0 | 248.4372 | 0
8809 | 750.5343 | 2.6907 | 25.1501 | 96.7 | 78.8165 | 10.45 | 63.8713 | 8.0836 | 6.1102 | 26.5324 | 76.8529 | 7.1362 | 163.3417 | 79.2813 | 228.0872 | 9.1115 | 47.1254 | 2.7243 | 103 | 43.2565 | 0 | 240.7184 | 0
8810 | 741.7862 | 2.5795 | 25.0439 | 97.2152 | 79.8164 | 9.5003 | 56.8545 | 7.3109 | 6.1941 | 28.0987 | 76.5872 | 7.1912 | 163.0934 | 81.1208 | 230.1743 | 9.233 | 48.105 | 2.7417 | 99 | 43.0685 | 0 | 241.7113 | 0
8811 | 734.0072 | 2.6397 | 25.0834 | 98.6745 | 78.8112 | 10.4497 | 62.2191 | 6.9953 | 6.388 | 29.4403 | 76.5642 | 7.479 | 163.2001 | 85.0058 | 231.9196 | 9.1877 | 48.1911 | 2.7753 | 102 | 44.2575 | 0 | 247.829 | 0
8812 | 733.8253 | 2.6494 | 25.9854 | 97.2491 | 79.8103 | 9.5003 | 65.2331 | 8.4796 | 6.338 | 30.0243 | 76.5603 | 7.3368 | 163.1956 | 88.9837 | 229.3838 | 9.1714 | 48.0583 | 2.7552 | 98 | 44.7569 | 0 | 254.78 | 0
8813 | 738.7542 | 3.0761 | 27.4405 | 97.1708 | 78.8174 | 10.4497 | 57.382 | 7.7461 | 6.408 | 29.6522 | 77.2198 | 7.1395 | 166.803 | 84.8549 | 227.4083 | 9.358 | 49.9925 | 2.7402 | 99 | 43.9546 | 0 | 288.4248 | 0
8814 | 751.9472 | 4.2386 | 34.2628 | 96.1932 | 79.8176 | 9.5003 | 67.1662 | 7.906 | 6.5482 | 30.8063 | 78.7758 | 8.4009 | 178.145 | 87.791 | 231.5945 | 9.116 | 51.8551 | 2.9927 | 96 | 45.3161 | 0 | 302.6292 | 0
8815 | 788.8152 | 5.5146 | 51.9598 | 97.9223 | 76.8112 | 12.3492 | 83.1268 | 8.4129 | 7.0782 | 49.8905 | 97.6643 | 17.8293 | 206.0245 | 118.467 | 243.3574 | 9.2146 | 49.5941 | 3.7769 | 123 | 48.7809 | 0 | 333.2644 | 0
8816 | 828.4493 | 6.8252 | 77.3022 | 103.9578 | 70.9419 | 18.0484 | 91.1578 | 8.2118 | 7.0236 | 78.7198 | 131.5746 | 32.0268 | 239.3368 | 164.4861 | 285.334 | 12.0967 | 52.3342 | 5.9865 | 155 | 57.6702 | 0 | 387.584 | 0
8817 | 867.6563 | 8.031 | 88.1254 | 110.0114 | 69.9238 | 18.9997 | 104.2804 | 10.5986 | 6.084 | 82.2058 | 153.005 | 36.5163 | 273.9113 | 217.4744 | 332.5085 | 19.739 | 58.4051 | 5.8198 | 159 | 64.5681 | 0 | 455.0058 | 0
8818 | 904.2207 | 8.0231 | 91.9006 | 117.0248 | 70.8065 | 18.0503 | 114.0297 | 10.4073 | 5.49 | 69.549 | 161.1689 | 32.8534 | 307.4966 | 252.8871 | 363.1854 | 17.1602 | 65.327 | 5.2264 | 161 | 63.0269 | 0 | 476.449 | 0.11851
8819 | 937.5894 | 8.6701 | 92.1241 | 120.08 | 69.8059 | 19.005 | 117.7655 | 9.803 | 5.492 | 64.6861 | 172.025 | 30.679 | 325.0311 | 271.3372 | 386.3899 | 11.5506 | 71.6935 | 5.8002 | 163 | 63.2752 | 0 | 476.8904 | 0.1445
8820 | 958.9592 | 12.2971 | 92.808 | 121.3768 | 70.819 | 18.045 | 124.193 | 10.2992 | 5.704 | 65.0973 | 181.4059 | 30.3399 | 330.6765 | 283.1817 | 416.8502 | 10.623 | 72.9334 | 6.1818 | 163 | 62.6542 | 0 | 479.7764 | 0.18663
8821 | 962.5843 | 15.7151 | 91.5931 | 121.6166 | 70.8127 | 18.05 | 124.7979 | 9.3028 | 5.536 | 64.9208 | 179.8047 | 30.4869 | 335.5604 | 276.8134 | 411.6151 | 10.476 | 71.1781 | 6.5479 | 172 | 60.0064 | 0 | 477.3188 | 0.19579
8822 | 961.0858 | 15.4424 | 91.2298 | 130.2183 | 67.81 | 20.8992 | 120.4168 | 8.4663 | 5.567 | 64.1413 | 182.5364 | 29.2962 | 329.2296 | 270.3829 | 391.1943 | 10.1636 | 73.838 | 6.9462 | 167 | 59.1465 | 0 | 482.1221 | 0.17225
8823 | 972.6977 | 10.3478 | 93.2469 | 129.6587 | 67.8043 | 20.9058 | 123.2273 | 8.8663 | 6.0194 | 62.3995 | 185.7642 | 26.7265 | 325.5184 | 265.6522 | 397.2149 | 10.1799 | 74.6529 | 7.5764 | 166 | 62.5139 | 0 | 479.3157 | 0.10718
8824 | 973.5557 | 6.3814 | 93.3072 | 121.6134 | 69.8189 | 18.9947 | 123.608 | 10.8009 | 6.3376 | 61.7194 | 183.3982 | 24.7365 | 319.2035 | 248.6581 | 392.3024 | 10.7643 | 73.9998 | 7.9351 | 160 | 61.6123 | 0 | 472.5513 | 0
8825 | 961.9008 | 6.2149 | 91.482 | 117.6772 | 76.8119 | 12.3518 | 113.506 | 10.364 | 6.982 | 64.2575 | 182.4234 | 24.7538 | 302.2807 | 230.8947 | 365.3272 | 11.1975 | 70.413 | 7.5465 | 159 | 58.8062 | 0 | 415.5333 | 0
8826 | 941.6789 | 6.4377 | 76.8657 | 111.7688 | 78.8105 | 10.4534 | 106.654 | 9.0864 | 7.322 | 69.9461 | 174.5952 | 25.0024 | 273.2063 | 196.2845 | 344.0315 | 10.204 | 64.3847 | 7.1674 | 151 | 55.7156 | 0 | 338.9359 | 0
8827 | 920.4518 | 5.7881 | 42.2559 | 104.02 | 78.8181 | 10.4471 | 92.5468 | 9.2029 | 7.914 | 59.6396 | 147.8514 | 20.8574 | 238.26 | 148.7688 | 344.5388 | 9.0883 | 59.7199 | 5.8671 | 158 | 52.6897 | 0 | 297.4349 | 0
8828 | 893.8168 | 5.2166 | 25.5832 | 98.8917 | 77.8176 | 11.3997 | 70.9619 | 8.0066 | 8.2245 | 47.0853 | 129.2173 | 11.5671 | 219.2839 | 117.7143 | 342.8285 | 8.7934 | 54.787 | 4.7028 | 133 | 51.0802 | 0 | 281.4485 | 0
8829 | 869.0366 | 5.0541 | 25.249 | 96.8068 | 78.817 | 10.4503 | 65.2969 | 8.9751 | 8.3628 | 43.4381 | 120.9934 | 7.0417 | 206.0736 | 108.7183 | 302.9814 | 8.7497 | 51.0142 | 4.4291 | 125 | 49.8098 | 0 | 263.2254 | 0
8830 | 842.9706 | 4.8371 | 25.3884 | 94.7783 | 78.8164 | 10.45 | 63.1513 | 7.2624 | 7.7487 | 40.0796 | 103.3193 | 7.3206 | 189.0268 | 104.512 | 267.1994 | 8.895 | 49.8893 | 3.8266 | 116 | 46.6112 | 0 | 257.2308 | 0
8831 | 812.945 | 4.3159 | 25.4774 | 93.5838 | 78.8128 | 10.45 | 59.7309 | 6.8263 | 6.622 | 34.565 | 85.0921 | 7.1378 | 175.6 | 96.2132 | 255.837 | 8.8135 | 49.5306 | 3.179 | 114 | 47.5364 | 0 | 257.5193 | 0
8832 | 795.1951 | 3.8744 | 25.5519 | 93.6161 | 78.8129 | 10.45 | 61.976 | 11.8914 | 6.192 | 32.1072 | 77.9602 | 6.9136 | 169.9256 | 90.6183 | 243.4018 | 8.7305 | 49.2524 | 2.9866 | 114 | 46.1136 | 0 | 261.8087 | 0
8833 | 790.1436 | 3.6482 | 25.5336 | 94.3645 | 77.9446 | 11.3997 | 60.7941 | 14.3466 | 6.036 | 31.3524 | 76.9736 | 6.9216 | 171.3994 | 87.3525 | 237.4176 | 8.7558 | 49.875 | 2.8851 | 109 | 44.1395 | 0 | 265.8628 | 0
8834 | 788.0097 | 2.997 | 25.6321 | 94.3696 | 78.9432 | 10.4503 | 58.8685 | 14.1951 | 6.012 | 29.9246 | 80.2291 | 6.9134 | 174.2753 | 84.802 | 249.0459 | 8.726 | 50.0189 | 2.6116 | 109 | 42.9206 | 0 | 266.4339 | 0
8835 | 778.8875 | 2.565 | 25.7466 | 94.4602 | 78.9426 | 10.45 | 61.4821 | 14.2051 | 5.994 | 29.9601 | 83.3277 | 6.9113 | 173.3865 | 84.1418 | 250.7137 | 8.8223 | 49.825 | 2.4281 | 111 | 43.081 | 0 | 269.049 | 0
8836 | 776.4564 | 2.5851 | 25.6634 | 94.6811 | 78.9449 | 10.45 | 59.8216 | 14.158 | 6.064 | 29.9274 | 83.0681 | 6.9001 | 170.2403 | 83.6303 | 241.7706 | 8.8397 | 49.9587 | 2.409 | 106 | 42.1472 | 0 | 271.0322 | 0
8837 | 778.0632 | 3.1949 | 25.3609 | 94.9481 | 78.9415 | 10.45 | 60.0137 | 14.1112 | 5.912 | 30.2184 | 81.3131 | 6.8726 | 173.3852 | 83.4805 | 234.906 | 8.8131 | 51.3938 | 2.4138 | 107 | 42.7569 | 0 | 290.6834 | 0
8838 | 795.1969 | 4.2171 | 29.6308 | 96.3197 | 76.9406 | 12.3495 | 68.0362 | 14.2549 | 5.874 | 31.2357 | 79.2929 | 8.4559 | 184.9676 | 92.9442 | 234.8957 | 8.8115 | 52.7843 | 2.5054 | 101 | 41.7137 | 0 | 314.6442 | 0
8839 | 817.7972 | 5.9515 | 45.4947 | 101.0691 | 77.9406 | 11.4003 | 78.0177 | 14.1703 | 8.188 | 55.3538 | 95.8206 | 15.3168 | 208.9396 | 126.6854 | 248.4408 | 8.7616 | 51.1835 | 2.9358 | 131 | 46.2285 | 0 | 363.5204 | 0
8840 | 853.7005 | 8.5819 | 73.7604 | 104.8279 | 69.9403 | 18.9979 | 96.7859 | 14.7086 | 12.4058 | 87.3159 | 132.8911 | 25.9765 | 246.675 | 170.5545 | 298.4289 | 9.7281 | 54.5147 | 4.0205 | 167 | 54.7162 | 0 | 406.4588 | 0
8841 | 920.7574 | 12.0091 | 87.433 | 112.2117 | 69.9337 | 19.0053 | 115.455 | 16.5384 | 13.4779 | 89.3895 | 156.2964 | 29.124 | 284.8638 | 228.627 | 349.7425 | 10.3388 | 60.7396 | 5.3907 | 158 | 60.3605 | 0 | 483.9138 | 0
8842 | 960.1747 | 13.0497 | 90.4255 | 121.1977 | 64.9394 | 23.75 | 121.9228 | 13.7515 | 12.8523 | 78.7525 | 168.8925 | 27.742 | 317.651 | 271.4415 | 382.1527 | 10.2972 | 65.6907 | 8.3797 | 166 | 62.363 | 0 | 512.5868 | 0.0090522
8843 | 992.1283 | 9.9416 | 91.8627 | 125.4881 | 66.9434 | 21.8439 | 131.4922 | 10.2024 | 13.882 | 74.737 | 178.6265 | 26.7369 | 332.1855 | 290.3395 | 408.7665 | 10.2981 | 86.5816 | 11.6526 | 161 | 66.4243 | 0 | 508.9653 | 0.016238
8844 | 1023.9257 | 7.7275 | 93.5706 | 126.5669 | 69.936 | 19.0008 | 142.3659 | 10.6024 | 14.244 | 81.1027 | 181.3756 | 28.896 | 339.6101 | 306.9668 | 422.7399 | 11.559 | 102.4784 | 10.2141 | 159 | 70.4733 | 0 | 509.3954 | 0.021299
8845 | 1030.3669 | 8.5582 | 94.6594 | 127.5987 | 69.9341 | 19 | 136.238 | 11.3982 | 13.982 | 79.7747 | 181.6411 | 30.6788 | 349.3344 | 316.0462 | 424.9608 | 12.3054 | 102.3244 | 8.7068 | 164 | 70.5267 | 0 | 505.913 | 0.0080009
8846 | 1030.2423 | 8.1506 | 96.3504 | 128.8309 | 68.935 | 19.9497 | 132.3633 | 11.1207 | 14.006 | 83.6023 | 182.3729 | 30.9862 | 354.4346 | 317.7307 | 435.7324 | 11.8263 | 104.4874 | 8.9839 | 169 | 69.6826 | 0 | 510.0973 | 0.0051044
8847 | 1033.4445 | 5.5497 | 97.7729 | 130.289 | 70.9312 | 18.0505 | 137.7946 | 9.8373 | 14.072 | 87.7254 | 184.9644 | 32.8163 | 370.7243 | 314.1406 | 439.1342 | 11.4278 | 107.1989 | 8.7739 | 171 | 70.2953 | 0 | 502.8961 | 0.0048806
8848 | 1030.3314 | 5.4709 | 93.6174 | 130.5302 | 69.9308 | 18.9997 | 135.0611 | 8.895 | 14.232 | 82.828 | 188.1916 | 34.2853 | 374.2777 | 293.2967 | 424.7379 | 11.5285 | 106.7442 | 8.8085 | 176 | 66.3407 | 0 | 499.8865 | 0
8849 | 999.7673 | 6.2909 | 85.019 | 125.4677 | 75.9342 | 13.3016 | 121.6603 | 8.5581 | 14.14 | 81.8327 | 189.723 | 31.431 | 357.2563 | 277.1757 | 407.7534 | 10.6925 | 101.8566 | 8.8937 | 171 | 60.6146 | 0 | 424.0642 | 0
8850 | 955.3753 | 6.2151 | 64.5456 | 113.6853 | 77.9347 | 11.4037 | 118.2552 | 7.3619 | 13.684 | 74.6938 | 178.0044 | 27.5696 | 327.111 | 240.4505 | 373.8908 | 9.4139 | 94.2182 | 8.5274 | 149 | 56.5915 | 0 | 363.4272 | 0
8851 | 928.6036 | 5.7079 | 36.4276 | 102.0639 | 78.9369 | 10.45 | 111.1159 | 5.6392 | 11.84 | 65.6109 | 148.8876 | 22.4251 | 288.8093 | 182.6819 | 336.9724 | 8.8519 | 89.198 | 7.728 | 146 | 54.0402 | 0 | 307.1925 | 0
8852 | 902.894 | 4.9855 | 25.2242 | 97.511 | 77.9416 | 11.3968 | 93.3827 | 4.9777 | 8.402 | 61.3056 | 130.8542 | 13.4459 | 260.7803 | 147.8277 | 288.8623 | 8.9066 | 84.816 | 6.6172 | 133 | 49.9116 | 0 | 278.2145 | 0
8853 | 871.2435 | 4.9691 | 25.0887 | 96.5271 | 78.9404 | 10.4503 | 77.6153 | 5.145 | 6.842 | 56.6195 | 123.2418 | 8.9948 | 239.3411 | 135.049 | 249.9245 | 9.022 | 82.0618 | 5.3823 | 123 | 45.8288 | 0 | 264.6198 | 0
8854 | 821.7476 | 5.4241 | 24.9073 | 94.9201 | 77.9444 | 11.3997 | 69.5716 | 5.8992 | 6.8416 | 45.8483 | 107.459 | 8.6591 | 214.2881 | 126.2352 | 243.9813 | 8.8893 | 80.005 | 4.3544 | 116 | 42.4567 | 0 | 270.1136 | 0
8855 | 774.1821 | 4.5812 | 24.8883 | 99.489 | 78.9428 | 10.4532 | 73.0917 | 6.4245 | 6.8229 | 35.9981 | 93.3421 | 8.5683 | 187.492 | 122.6868 | 239.4482 | 8.9928 | 78.9472 | 3.6902 | 106 | 41.9998 | 0 | 278.2243 | 0
8856 | 745.7663 | 3.237 | 25.0025 | 103.7454 | 77.9506 | 11.3968 | 74.4723 | 6.4845 | 6.5025 | 32.5454 | 87.4047 | 8.6011 | 171.7513 | 118.0126 | 231.2166 | 8.9132 | 78.6584 | 2.9034 | 99 | 39.9141 | 0 | 270.9264 | 0
8857 | 744.3463 | 2.761 | 25.0602 | 101.9804 | 78.9458 | 10.4532 | 68.8436 | 6.2631 | 6.2921 | 32.3049 | 85.4431 | 8.5982 | 168.0444 | 113.8861 | 228.9167 | 8.8441 | 78.4999 | 2.5026 | 96 | 38.6935 | 0 | 263.4937 | 0
8858 | 740.8145 | 2.7385 | 25.0274 | 100.624 | 77.9536 | 11.3968 | 70.3047 | 5.6393 | 6.37 | 32.6329 | 84.8201 | 8.6075 | 167.3906 | 110.629 | 231.4958 | 9.0766 | 78.5022 | 2.4794 | 99 | 40.3698 | 0 | 263.8917 | 0
8859 | 723.0792 | 2.8729 | 25.0104 | 100.8411 | 78.9476 | 10.4503 | 78.2699 | 5.6958 | 6.3148 | 32.7524 | 84.9605 | 8.9923 | 167.9133 | 109.4143 | 234.2494 | 8.8418 | 78.4218 | 2.4638 | 98 | 39.4875 | 0 | 265.7896 | 0
8860 | 721.6077 | 2.7539 | 24.9943 | 100.6572 | 78.9449 | 10.4529 | 74.7429 | 5.8904 | 6.24 | 32.6376 | 84.981 | 9.3248 | 168.1652 | 106.5283 | 231.8567 | 8.9385 | 78.3491 | 2.4575 | 97 | 38.8174 | 0 | 262.4012 | 0
8861 | 718.7534 | 3.1052 | 25.0498 | 100.7567 | 77.9528 | 11.3968 | 65.9746 | 6.8872 | 6.252 | 33.0919 | 84.8451 | 8.8915 | 171.8134 | 105.6866 | 227.9268 | 8.8778 | 79.9823 | 2.4701 | 100 | 38.4763 | 0 | 284.2304 | 0
8862 | 726.776 | 3.9618 | 33.7525 | 106.2023 | 78.9454 | 10.4503 | 71.2404 | 7.9853 | 6.338 | 34.2061 | 85.8219 | 9.8308 | 185.3466 | 112.044 | 229.7653 | 8.8033 | 81.2313 | 2.4814 | 92 | 37.6383 | 0 | 311.6767 | 0
8863 | 761.5455 | 5.3043 | 52.0026 | 113.6386 | 75.9436 | 13.2992 | 78.6719 | 7.0096 | 7.278 | 50.8912 | 107.93 | 16.4734 | 209.7427 | 132.4882 | 246.6732 | 8.899 | 79.573 | 2.5395 | 128 | 41.8432 | 0 | 350.8394 | 0
8864 | 815.2348 | 7.0557 | 74.9457 | 117.7403 | 71.94 | 17.0989 | 89.0626 | 7.6392 | 7.186 | 76.1546 | 151.0894 | 31.3534 | 240.9055 | 165.3592 | 287.2731 | 8.7575 | 82.6451 | 5.0093 | 149 | 49.5196 | 0 | 396.8257 | 0
8865 | 870.6342 | 11.8541 | 85.3444 | 126.0473 | 69.9379 | 18.9995 | 104.7608 | 10.0852 | 6.154 | 82.1925 | 174.049 | 38.5098 | 281.5092 | 223.2598 | 336.2112 | 9.5358 | 91.5859 | 7.275 | 155 | 57.3005 | 0 | 469.1857 | 0
8866 | 924.7745 | 12.6288 | 91.1242 | 135.1151 | 70.9377 | 18.0503 | 113.4998 | 10.0003 | 5.65 | 76.8029 | 176.3985 | 34.7287 | 318.2044 | 275.6459 | 382.1882 | 9.7117 | 97.2109 | 8.1324 | 169 | 60.5497 | 0 | 498.6757 | 0.023357
8867 | 976.9527 | 10.4985 | 92.3615 | 138.4556 | 69.9319 | 19.005 | 115.8087 | 9.0163 | 5.588 | 75.1864 | 180.1899 | 32.1259 | 335.4164 | 298.0893 | 413.8097 | 9.8826 | 100.3849 | 8.5429 | 162 | 58.4446 | 0 | 502.3874 | 0.038343
8868 | 994.1052 | 10.815 | 95.404 | 141.5506 | 68.9427 | 19.9445 | 123.9669 | 9.9118 | 6.134 | 77.5728 | 183.2595 | 32.3778 | 349.7804 | 316.4274 | 446.8425 | 10.9073 | 105.1873 | 8.7222 | 167 | 63.5867 | 0 | 515.9059 | 0.034797
8869 | 989.594 | 9.4855 | 97.4128 | 139.9249 | 67.9344 | 20.8997 | 128.3403 | 10.7037 | 7.03 | 81.1239 | 186.2416 | 34.4088 | 356.9408 | 324.6319 | 476.7744 | 12.0028 | 105.3146 | 9.0619 | 164 | 66.4634 | 0 | 528.8771 | 0.024203
8870 | 998.1021 | 6.8363 | 97.8189 | 142.8894 | 67.9349 | 20.9 | 125.2008 | 9.4656 | 7.144 | 81.1412 | 187.7486 | 35.8143 | 359.0972 | 324.6312 | 493.4157 | 12.7791 | 107.075 | 8.9435 | 167 | 63.4934 | 0 | 527.7233 | 0.024129
8871 | 1003.8138 | 5.2548 | 96.6671 | 150.6645 | 68.9332 | 19.9503 | 125.4294 | 8.4423 | 6.7697 | 81.2591 | 187.0383 | 36.771 | 369.9099 | 324.4016 | 485.7516 | 13.2932 | 109.1843 | 8.9321 | 175 | 60.2349 | 0 | 540.4377 | 0.0067437
8872 | 976.4434 | 5.4233 | 92.1764 | 147.0007 | 69.9331 | 19.0003 | 125.935 | 9.7106 | 6.8981 | 83.7199 | 190.1888 | 37.2185 | 366.2412 | 303.7242 | 456.4287 | 12.8348 | 108.703 | 9.577 | 168 | 62.4163 | 0 | 532.6736 | 0
8873 | 948.0283 | 6.1653 | 84.0619 | 137.8705 | 75.932 | 13.3016 | 122.6496 | 9.833 | 7.0177 | 82.5161 | 185.7516 | 36.556 | 345.4094 | 263.3287 | 407.8544 | 11.8356 | 92.1076 | 10.0556 | 163 | 58.759 | 0 | 455.0602 | 0
8874 | 920.9541 | 6.6813 | 65.3638 | 126.1274 | 78.9317 | 10.4537 | 118.8729 | 8.2214 | 6.9058 | 75.6666 | 169.9936 | 34.5227 | 307.7578 | 205.8972 | 364.449 | 10.383 | 74.5205 | 9.7369 | 156 | 55.1088 | 0 | 381.5626 | 0
8875 | 899.7567 | 6.6277 | 38.1632 | 112.7285 | 78.9418 | 10.4471 | 102.1226 | 9.5073 | 6.9361 | 62.9152 | 144.9191 | 29.5338 | 262.1252 | 155.6518 | 339.7074 | 9.2238 | 65.4049 | 8.7544 | 147 | 54.4536 | 0 | 343.1385 | 0
8876 | 870.7393 | 8.9597 | 26.4798 | 105.053 | 78.9411 | 10.45 | 81.4613 | 8.785 | 6.6466 | 54.6354 | 130.2316 | 19.3938 | 237.6943 | 131.2443 | 331.5209 | 8.7227 | 57.5824 | 7.5493 | 130 | 50.5083 | 0 | 299.515 | 0
8877 | 827.4624 | 9.6629 | 25.801 | 103.5587 | 78.942 | 10.45 | 72.4718 | 9.1668 | 6.5457 | 49.6352 | 122.2469 | 13.7713 | 220.6203 | 122.6247 | 321.531 | 8.6795 | 53.839 | 6.2804 | 122 | 45.9549 | 0 | 283.7199 | 0
8878 | 799.856 | 7.1725 | 25.8177 | 103.1225 | 77.9426 | 11.3997 | 84.3085 | 8.441 | 7.4309 | 41.1316 | 107.3067 | 13.3687 | 198.0459 | 109.2593 | 301.7372 | 8.8481 | 52.7972 | 5.3029 | 121 | 41.5698 | 0 | 287.2128 | 0
8879 | 789.3895 | 5.4347 | 25.7937 | 102.1418 | 78.9412 | 10.4532 | 94.7801 | 6.0811 | 7.9594 | 36.4391 | 91.0023 | 12.7569 | 185.5704 | 100.2087 | 276.0432 | 8.6737 | 52.6963 | 4.7819 | 110 | 39.5729 | 0 | 294.5951 | 0
8880 | 778.0367 | 4.0682 | 25.8255 | 100.9193 | 77.9445 | 11.4 | 77.2391 | 10.6077 | 7.378 | 35.983 | 84.1273 | 12.4201 | 178.6581 | 96.655 | 255.403 | 8.8211 | 52.8386 | 4.6312 | 107 | 37.3211 | 0 | 297.9767 | 0
8881 | 768.6966 | 3.3995 | 25.9801 | 98.8036 | 76.9474 | 12.3466 | 62.2514 | 14.4771 | 6.5 | 35.6406 | 82.9628 | 12.4832 | 173.834 | 88.2332 | 236.8762 | 8.804 | 52.7069 | 4.3649 | 103 | 36.7668 | 0 | 307.9753 | 0
8882 | 758.1222 | 3.5205 | 26.09 | 96.7858 | 77.9467 | 11.4003 | 64.4981 | 14.4331 | 6.244 | 36.8016 | 82.0339 | 12.4285 | 171.5353 | 82.6201 | 229.6026 | 8.7184 | 52.7559 | 3.7468 | 101 | 37.242 | 0 | 331.3386 | 0
8883 | 744.6335 | 3.8553 | 26.1455 | 95.9755 | 77.9488 | 11.4 | 65.1703 | 14.2926 | 6.2026 | 37.7237 | 82.0288 | 12.7877 | 171.4607 | 82.2204 | 238.0802 | 8.8196 | 52.7596 | 2.984 | 98 | 35.568 | 0 | 320.9691 | 0
8884 | 747.3543 | 4.0629 | 26.1225 | 94.4679 | 77.9473 | 11.4 | 62.2755 | 14.2597 | 6.1523 | 36.9591 | 81.8885 | 12.5319 | 171.2963 | 81.8282 | 244.0935 | 8.6957 | 52.8395 | 2.6801 | 99 | 33.3245 | 0 | 318.5992 | 0
8885 | 765.1202 | 4.1988 | 26.2158 | 94.477 | 78.9452 | 10.4503 | 63.9716 | 14.2908 | 6.1551 | 36.6163 | 82.2522 | 12.1808 | 175.5034 | 80.7845 | 244.4138 | 8.8469 | 54.5812 | 2.7036 | 99 | 32.9949 | 0 | 337.3822 | 0
8886 | 781.0947 | 4.8316 | 36.8692 | 95.6337 | 77.9458 | 11.3997 | 65.0473 | 14.442 | 6.162 | 36.5244 | 83.3803 | 14.5343 | 186.9146 | 89.3168 | 251.1145 | 8.8167 | 55.8823 | 2.6744 | 98 | 33.7292 | 0 | 361.5448 | 0
8887 | 797.6797 | 5.6326 | 49.4342 | 100.4976 | 76.9443 | 12.3497 | 67.1664 | 14.2528 | 7.334 | 49.2413 | 106.3871 | 21.1965 | 204.7678 | 117.2731 | 263.2128 | 8.6833 | 53.8078 | 2.7166 | 133 | 38.4487 | 0 | 396.5291 | 0
8888 | 827.8047 | 6.1179 | 66.7937 | 104.5494 | 71.9445 | 17.0987 | 76.0233 | 14.3557 | 7.1125 | 68.9887 | 149.8005 | 33.1868 | 234.9543 | 167.3449 | 297.0563 | 8.9217 | 54.5897 | 4.8719 | 159 | 47.973 | 0 | 434.3284 | 0
8889 | 871.4938 | 7.2053 | 78.1148 | 109.1825 | 69.9377 | 19.0048 | 98.1385 | 15.8799 | 6.3263 | 74.1674 | 174.2777 | 39.9941 | 286.9507 | 232.8079 | 357.3551 | 10.2298 | 60.5926 | 7.4927 | 173 | 56.8251 | 0 | 514.1035 | 0
8890 | 939.5223 | 7.9609 | 88.4416 | 116.359 | 69.9424 | 18.9947 | 124.9769 | 17.4376 | 6.0895 | 74.0412 | 176.4245 | 38.5932 | 331.8341 | 258.762 | 420.3346 | 11.4025 | 69.0415 | 10.4302 | 188 | 60.5169 | 0 | 538.4691 | 0.12046
8891 | 988.0364 | 7.7345 | 95.4289 | 120.9556 | 69.9362 | 19 | 135.8453 | 18.1352 | 6.6508 | 77.214 | 174.9656 | 33.4884 | 345.0872 | 284.3246 | 445.8476 | 11.5038 | 74.5006 | 10.4859 | 185 | 64.8257 | 0 | 539.435 | 0.14154
8892 | 1010.1717 | 7.4961 | 92.4999 | 119.3163 | 67.9356 | 20.8995 | 132.7308 | 17.4556 | 6.599 | 77.98 | 173.3987 | 33.3958 | 353.0581 | 287.3594 | 444.4826 | 11.1373 | 82.8862 | 10.0475 | 192 | 71.7709 | 0 | 540.9959 | 0.11724
8893 | 997.439 | 6.1092 | 86.3694 | 122.32 | 67.9356 | 20.9 | 131.2069 | 15.6032 | 5.6228 | 73.379 | 172.0442 | 36.7722 | 359.2226 | 283.0204 | 442.0942 | 10.9862 | 83.5779 | 10.245 | 187 | 67.0589 | 0 | 542.5814 | 0.13099
8894 | 995.959 | 4.8439 | 84.7766 | 123.6986 | 68.9354 | 19.9503 | 124.5079 | 15.2869 | 5.1158 | 69.715 | 174.389 | 40.9646 | 359.514 | 277.4832 | 446.0207 | 10.6745 | 85.427 | 9.9725 | 178 | 65.3018 | 0 | 548.0918 | 0.13306
8895 | 994.0854 | 6.1467 | 81.1227 | 121.6755 | 69.4405 | 19.4697 | 119.5775 | 15.5118 | 11.0773 | 73.9526 | 174.3685 | 40.955 | 357.4938 | 276.3386 | 452.4383 | 11.0582 | 79.9871 | 9.8958 | 177 | 65.5946 | 0 | 518.3881 | 0.097227
8896 | 992.7442 | 6.9015 | 79.8927 | 121.0865 | 69.4349 | 19.475 | 118.9177 | 15.5452 | 13.465 | 76.0731 | 173.7597 | 40.3619 | 356.9935 | 276.6956 | 454.4319 | 11.2485 | 77.8605 | 9.9423 | 189 | 65.643 | 0 | 514.3775 | 0
8897 | 975.5887 | 8.4961 | 75.9191 | 119.1128 | 73.9202 | 15.2162 | 107.4153 | 14.8452 | 14.9879 | 76.2519 | 172.495 | 39.8819 | 333.7877 | 238.0914 | 422.4307 | 10.551 | 79.1762 | 10.1071 | 168 | 66.564 | 0 | 424.9586 | 0
8898 | 934.5997 | 7.1964 | 65.1435 | 111.2515 | 75.9425 | 13.2963 | 101.8698 | 14.9454 | 15.6617 | 69.3145 | 165.0596 | 35.8029 | 319.1249 | 193.4489 | 403.9253 | 9.3971 | 78.3783 | 9.1709 | 145 | 62.5353 | 0 | 342.1383 | 0
8899 | 888.9902 | 6.3225 | 37.0643 | 100.7372 | 75.9434 | 13.3 | 91.2586 | 14.6463 | 14.7297 | 47.4892 | 141.9827 | 30.988 | 300.374 | 165.5394 | 387.5071 | 8.4421 | 74.1874 | 7.4471 | 138 | 54.9806 | 0 | 314.9812 | 0
8900 | 853.5943 | 5.2966 | 27.6471 | 96.0596 | 73.9426 | 15.1995 | 75.0106 | 14.3701 | 9.9067 | 39.4573 | 129.3569 | 22.848 | 270.2929 | 149.6274 | 334.6662 | 8.4719 | 62.0702 | 6.2294 | 121 | 46.7383 | 0 | 300.1711 | 0
8901 | 820.4762 | 5.1076 | 27.63 | 95.8874 | 77.945 | 11.4011 | 70.2135 | 14.4829 | 8.0067 | 40.2256 | 120.428 | 20.4845 | 252.9297 | 127.6884 | 291.0687 | 8.3955 | 55.207 | 5.5102 | 116 | 43.4203 | 0 | 295.193 | 0
8902 | 799.026 | 5.0269 | 27.1424 | 96.1891 | 77.9387 | 11.4032 | 67.522 | 14.2364 | 8.6953 | 39.8805 | 101.987 | 20.1423 | 232.2406 | 113.8391 | 284.873 | 8.2206 | 52.9465 | 4.5155 | 112 | 39.1954 | 0 | 295.3275 | 0
8903 | 793.4004 | 4.3833 | 26.865 | 96.6323 | 78.9425 | 10.4471 | 64.3088 | 13.9956 | 8.259 | 39.9244 | 89.0447 | 19.497 | 213.8892 | 106.5425 | 283.56 | 8.2536 | 51.6456 | 3.9607 | 111 | 35.4721 | 0 | 294.5579 | 0
8904 | 792.1989 | 3.438 | 26.79 | 96.4162 | 77.9317 | 11.4029 | 65.4542 | 13.9528 | 7.2278 | 39.7121 | 83.1635 | 18.2722 | 200.1978 | 97.4501 | 271.5734 | 8.1609 | 51.2332 | 3.0659 | 106 | 33.5684 | 0 | 298.5971 | 0
8905 | 790.9603 | 3.1855 | 26.748 | 95.847 | 78.9429 | 10.4471 | 63.7915 | 14.2856 | 7.64 | 38.0813 | 79.992 | 11.2487 | 196.0328 | 89.5555 | 265.2081 | 8.4193 | 48.3341 | 2.5153 | 104 | 33.5795 | 0 | 305.8186 | 0
8906 | 772.7901 | 3.7948 | 26.8542 | 95.113 | 78.9426 | 10.45 | 61.6914 | 14.2278 | 7.4318 | 37.1284 | 78.6731 | 8.172 | 183.9157 | 84.8264 | 270.2427 | 8.3924 | 47.3751 | 2.4242 | 104 | 31.9834 | 0 | 309.9338 | 0
8907 | 764.4427 | 3.2237 | 27.0293 | 95.1135 | 77.9471 | 11.3997 | 64.7131 | 14.186 | 6.456 | 37.9761 | 78.7772 | 8.0829 | 175.7512 | 82.9515 | 272.6302 | 8.2785 | 47.3867 | 2.4439 | 102 | 31.7587 | 0 | 303.0796 | 0
8908 | 746.6842 | 2.9426 | 27.0441 | 97.5131 | 78.9419 | 10.4503 | 63.2975 | 14.2338 | 6.254 | 38.1006 | 79.5054 | 8.0917 | 173.7825 | 84.4741 | 258.7618 | 8.3822 | 47.5471 | 2.4774 | 104 | 31.9021 | 0 | 304.8504 | 0
8909 | 743.5791 | 3.3711 | 26.9793 | 101.5308 | 77.9458 | 11.3997 | 63.9024 | 14.3786 | 6.4801 | 37.6275 | 79.8383 | 8.1128 | 172.5624 | 82.6298 | 249.825 | 8.2477 | 47.2724 | 2.4436 | 104 | 32.5307 | 0 | 315.8293 | 0
8910 | 738.3335 | 4.2383 | 27.3037 | 100.9523 | 78.9432 | 10.4503 | 65.6888 | 14.3017 | 6.3488 | 38.001 | 79.8195 | 8.0513 | 172.8416 | 88.2688 | 248.5306 | 8.5302 | 48.7884 | 2.4302 | 98 | 32.3513 | 0 | 342.5554 | 0
8911 | 748.9842 | 5.4416 | 46.8161 | 99.6689 | 77.9397 | 11.3997 | 63.2793 | 14.0697 | 7.8949 | 49.2088 | 88.3648 | 8.0152 | 177.0598 | 103.6506 | 252.312 | 8.3201 | 47.8953 | 2.4287 | 119 | 32.6992 | 0 | 349.3496 | 0
8912 | 760.7173 | 5.4894 | 60.0654 | 99.5287 | 73.9395 | 15.1989 | 64.9996 | 13.9428 | 7.4227 | 72.1877 | 108.4586 | 9.4649 | 186.8579 | 117.4998 | 267.0017 | 8.2933 | 47.69 | 3.175 | 140 | 34.3472 | 0 | 366.5483 | 0
8913 | 772.7807 | 4.1853 | 68.089 | 96.866 | 72.94 | 16.1497 | 68.5856 | 13.8275 | 6.3938 | 76.7155 | 115.7852 | 15.0722 | 208.955 | 143.9842 | 274.8729 | 8.0769 | 47.9583 | 5.5992 | 142 | 42.3978 | 0 | 380.1049 | 0
8914 | 816.192 | 3.0448 | 74.1767 | 95.6547 | 72.9388 | 16.15 | 82.2566 | 13.6455 | 7.03 | 71.2181 | 118.2534 | 20.5959 | 233.9582 | 163.8497 | 288.1284 | 9.5458 | 48.0134 | 7.4582 | 144 | 46.556 | 0 | 376.2409 | 0.020808
8915 | 845.9902 | 2.9208 | 76.2009 | 97.7872 | 72.9435 | 16.15 | 100.5595 | 13.8464 | 6.9098 | 74.8747 | 128.0073 | 18.9884 | 243.4703 | 191.2041 | 319.9521 | 9.9416 | 48.9168 | 8.8997 | 146 | 49.9537 | 0 | 382.7204 | 0.047556
8916 | 881.7192 | 2.8362 | 79.4153 | 99.2217 | 71.9449 | 17.0997 | 98.1668 | 13.8155 | 6.254 | 79.4383 | 134.6834 | 13.8858 | 247.8906 | 208.5915 | 349.3195 | 9.4389 | 50.7009 | 9.2347 | 146 | 58.2023 | 0 | 380.8365 | 0.084731
8917 | 895.3635 | 2.9326 | 79.8776 | 100.63 | 73.9461 | 15.2005 | 97.9848 | 13.6946 | 6.3727 | 78.8957 | 132.4621 | 12.9027 | 250.4086 | 206.6468 | 370.9645 | 8.5831 | 50.7053 | 9.5538 | 147 | 59.0596 | 0 | 377.0665 | 0.13288
8918 | 877.7075 | 3.431 | 79.0312 | 103.367 | 73.9436 | 15.2 | 102.0814 | 13.7289 | 8.4852 | 76.1757 | 132.4277 | 12.4845 | 258.1172 | 210.5281 | 381.862 | 8.0731 | 50.7143 | 10.3433 | 148 | 56.8448 | 0 | 383.9117 | 0.037973
8919 | 858.7151 | 3.5528 | 79.1118 | 107.5728 | 73.9403 | 15.2042 | 95.4288 | 13.7268 | 11.1835 | 72.1684 | 132.9278 | 12.4406 | 265.1283 | 216.4601 | 380.0356 | 7.8162 | 52.0794 | 10.4867 | 157 | 59.5065 | 0 | 377.2681 | 0.016436
8920 | 862.5671 | 3.998 | 69.4399 | 110.4902 | 72.9495 | 16.1455 | 99.6206 | 14.0774 | 12.198 | 72.928 | 133.325 | 13.0631 | 264.1142 | 226.929 | 383.5742 | 8.1339 | 53.4363 | 10.1883 | 159 | 62.2419 | 0 | 374.2449 | 0
8921 | 897.0711 | 4.582 | 37.0554 | 109.1059 | 77.9414 | 11.4013 | 107.3182 | 14.0638 | 12.4362 | 72.1773 | 136.5053 | 15.5381 | 264.8999 | 216.3016 | 364.2654 | 8.2078 | 54.4603 | 9.681 | 163 | 63.5707 | 0 | 343.0148 | 0
8922 | 900.1133 | 4.9137 | 26.6874 | 106.1944 | 78.9407 | 10.4503 | 100.453 | 14.0265 | 10.7854 | 69.3437 | 150.0327 | 21.9132 | 256.4431 | 191.4284 | 341.3266 | 8.2852 | 54.5803 | 9.2118 | 150 | 61.5735 | 0 | 298.8277 | 0
8923 | 870.3596 | 5.3846 | 26.721 | 104.8326 | 77.9422 | 11.3997 | 79.1796 | 14.1113 | 9.1341 | 49.4447 | 153.4269 | 21.8361 | 244.0264 | 167.9568 | 311.3392 | 8.4227 | 54.0782 | 8.2769 | 146 | 54.7633 | 0 | 279.0687 | 0
8924 | 851.0505 | 5.2338 | 26.7444 | 105.3818 | 78.942 | 10.4503 | 72.7561 | 14.188 | 8.5034 | 39.1942 | 126.1596 | 20.7416 | 228.8314 | 159.3038 | 304.9219 | 8.2743 | 52.2294 | 6.7381 | 132 | 46.4792 | 0 | 267.6132 | 0
8925 | 825.1243 | 4.8053 | 26.5817 | 104.6819 | 78.9468 | 10.45 | 72.4132 | 14.2507 | 7.9645 | 39.9205 | 94.8358 | 20.2303 | 215.4905 | 148.7302 | 306.7775 | 8.3836 | 50.4469 | 5.6486 | 125 | 47.795 | 0 | 271.0125 | 0
8926 | 799.2681 | 4.5978 | 26.6862 | 104.3638 | 78.9441 | 10.45 | 67.6657 | 14.4204 | 7.3972 | 38.4476 | 86.0047 | 16.3432 | 202.0851 | 136.0205 | 288.8992 | 8.3519 | 49.2884 | 4.7796 | 123 | 43.267 | 0 | 271.4474 | 0
8927 | 782.7906 | 4.8461 | 26.5937 | 104.2989 | 75.9478 | 13.2992 | 68.1118 | 14.315 | 6.9322 | 38.4432 | 86.3051 | 15.8431 | 185.6645 | 107.145 | 268.8452 | 8.3615 | 48.9312 | 3.9224 | 120 | 38.2726 | 0 | 272.5327 | 0
8928 | 794.5661 | 4.8549 | 26.4857 | 104.3257 | 78.9433 | 10.4508 | 69.796 | 14.1537 | 7.341 | 38.347 | 84.8569 | 15.1443 | 171.9789 | 93.715 | 255.4485 | 8.3944 | 49.4274 | 3.1094 | 105 | 34.9423 | 0 | 274.4573 | 0
8929 | 806.5491 | 3.4829 | 26.7349 | 104.1827 | 77.9427 | 11.3997 | 66.653 | 14.1011 | 7.7524 | 36.7491 | 83.7498 | 14.9512 | 168.5435 | 88.7429 | 250.5038 | 8.2072 | 51.7721 | 2.5638 | 103 | 32.1818 | 0 | 279.2972 | 0
8930 | 780.5917 | 3.0924 | 26.4248 | 104.69 | 78.9417 | 10.4503 | 66.9409 | 14.1139 | 6.9056 | 37.5374 | 82.6572 | 12.2233 | 169.2351 | 84.8943 | 254.6772 | 8.3744 | 52.6979 | 2.4328 | 103 | 33.1805 | 0 | 279.7311 | 0
8931 | 757.3187 | 3.6722 | 26.2015 | 104.3365 | 78.9467 | 10.45 | 70.0239 | 14.4208 | 6.4827 | 36.8658 | 82.7541 | 10.1952 | 168.7064 | 82.828 | 257.2565 | 8.4015 | 52.7636 | 2.4341 | 97 | 32.6929 | 0 | 279.7139 | 0
8932 | 760.5939 | 3.1053 | 26.1605 | 104.1822 | 78.9426 | 10.45 | 65.8182 | 14.2495 | 6.3668 | 38.3497 | 83.2043 | 9.232 | 168.2477 | 82.5953 | 254.1874 | 8.2646 | 52.5963 | 2.4298 | 97 | 33.8546 | 0 | 278.3816 | 0
8933 | 764.6035 | 3.1699 | 26.2519 | 104.5992 | 77.9388 | 11.4029 | 65.6221 | 14.0965 | 6.3085 | 37.5301 | 82.7534 | 8.3783 | 168.5924 | 82.2952 | 250.3996 | 8.303 | 54.1052 | 2.4008 | 97 | 32.8922 | 0 | 272.8529 | 0
8934 | 773.9095 | 4.028 | 26.3027 | 103.7181 | 77.9415 | 11.4 | 71.7726 | 14.0612 | 6.601 | 38.0231 | 83.5515 | 8.4052 | 166.9906 | 82.0624 | 248.4159 | 8.1844 | 56.7411 | 2.3887 | 97 | 33.3835 | 0 | 278.8327 | 0
8935 | 771.9068 | 4.8491 | 37.5944 | 104.8277 | 77.9465 | 11.3968 | 68.2861 | 13.9752 | 6.7679 | 37.8242 | 84.8598 | 8.4441 | 166.8845 | 82.4372 | 240.0054 | 8.4155 | 53.611 | 2.4213 | 99 | 33.1267 | 0 | 272.7516 | 0
8936 | 785.604 | 4.5098 | 50.9561 | 106.0507 | 77.9409 | 11.4 | 67.5553 | 13.9232 | 9.5178 | 39.8757 | 91.4402 | 10.2103 | 180.3844 | 91.1451 | 237.7545 | 8.5823 | 52.483 | 2.6577 | 102 | 35.7288 | 0 | 277.5906 | 0
8937 | 798.3727 | 4.5199 | 63.5341 | 105.6919 | 76.9398 | 12.3497 | 81.5895 | 14.192 | 7.8945 | 49.0711 | 105.6029 | 16.8166 | 197.5584 | 121.1502 | 248.2627 | 8.2408 | 52.2492 | 3.8837 | 105 | 47.0272 | 0 | 277.7088 | 0
8938 | 816.4095 | 3.7874 | 68.0962 | 106.0331 | 77.9365 | 11.4003 | 84.1834 | 15.4094 | 10.1855 | 72.307 | 121.6342 | 20.6144 | 213.0966 | 133.3839 | 262.5243 | 7.9891 | 51.3564 | 6.4991 | 119 | 53.6735 | 0 | 275.0908 | 0.0061276
8939 | 849.0657 | 3.0348 | 69.819 | 106.3749 | 78.9372 | 10.4503 | 86.9337 | 15.5376 | 8.8614 | 84.6985 | 136.4014 | 21.573 | 226.7599 | 145.7096 | 282.1819 | 7.6957 | 51.1201 | 8.5945 | 150 | 55.5063 | 0 | 275.8607 | 0.006653
8940 | 863.8987 | 3.0236 | 69.8703 | 107.096 | 78.938 | 10.45 | 101.0577 | 14.1481 | 12.6503 | 89.364 | 130.966 | 21.6934 | 240.0406 | 172.6061 | 302.1715 | 7.944 | 52.7881 | 9.7016 | 152 | 61.3345 | 0 | 278.112 | 0.023374
8941 | 862.7936 | 3.2631 | 70.0466 | 105.1798 | 77.9406 | 11.3997 | 98.9873 | 13.5233 | 14.7003 | 87.3852 | 126.4678 | 21.4813 | 246.1602 | 186.4417 | 316.3606 | 7.9248 | 52.971 | 10.1252 | 167 | 60.981 | 0 | 276.9241 | 0.02387
8942 | 864.2372 | 2.9171 | 70.0223 | 105.1535 | 78.9351 | 10.4503 | 88.3574 | 13.453 | 14.912 | 81.2036 | 123.2691 | 22.4951 | 242.3621 | 189.6948 | 314.0978 | 7.7548 | 53.0263 | 10.2532 | 169 | 60.9647 | 0 | 276.9572 | 0.020524
8943 | 882.7219 | 2.8089 | 70.4984 | 104.7296 | 79.9356 | 9.5029 | 90.963 | 13.367 | 13.1525 | 81.5124 | 122.1074 | 21.1425 | 236.4995 | 187.2282 | 324.9661 | 7.7397 | 53.0152 | 10.3354 | 171 | 60.9078 | 0 | 280.016 | 0.0097997
8944 | 868.7425 | 3.4014 | 66.7691 | 104.2641 | 78.9448 | 10.4471 | 106.4592 | 13.969 | 9.2035 | 70.1424 | 124.9885 | 19.6735 | 243.4293 | 177.7715 | 336.1064 | 7.8282 | 52.8261 | 10.3169 | 174 | 58.6808 | 0 | 286.0172 | 0
8945 | 867.7512 | 4.5243 | 37.4371 | 107.2972 | 76.9439 | 12.3495 | 99.7882 | 14.1799 | 8.5929 | 45.9139 | 128.6887 | 16.4638 | 248.0535 | 173.8152 | 319.1278 | 8.1814 | 52.8573 | 10.2021 | 167 | 59.1413 | 0 | 293.9327 | 0
8946 | 882.6711 | 5.4383 | 26.0357 | 108.292 | 76.9419 | 12.35 | 88.6041 | 14.0981 | 8.5498 | 38.785 | 121.5746 | 12.3265 | 246.833 | 167.0771 | 302.8412 | 8.3236 | 52.9546 | 9.631 | 156 | 56.9741 | 0 | 281.3049 | 0
8947 | 873.7482 | 5.4712 | 25.4401 | 106.9181 | 78.9434 | 10.4534 | 94.3772 | 14.3311 | 9.026 | 39.343 | 111.8549 | 11.3212 | 236.4021 | 161.7842 | 283.6816 | 8.2294 | 53.1739 | 8.86 | 171 | 52.77 | 0 | 275.0919 | 0
8948 | 860.0428 | 5.4945 | 25.5628 | 105.7962 | 78.9467 | 10.4471 | 92.9765 | 14.2362 | 9.4142 | 39.3815 | 108.6827 | 10.2219 | 225.4308 | 144.1454 | 267.6291 | 8.266 | 53.1844 | 7.9533 | 172 | 46.6112 | 0 | 276.1206 | 0
8949 | 845.5134 | 5.1723 | 25.5697 | 104.6053 | 78.9447 | 10.45 | 84.2 | 14.1534 | 9.0638 | 38.7669 | 106.8802 | 8.9119 | 213.4092 | 129.9694 | 250.2168 | 8.109 | 54.7298 | 6.5577 | 162 | 44.6345 | 0 | 275.0918 | 0
8950 | 829.8397 | 5.132 | 25.6268 | 103.6169 | 78.9452 | 10.45 | 81.7197 | 14.1932 | 7.9683 | 37.6705 | 104.9769 | 8.5643 | 191.8299 | 131.1343 | 245.5461 | 8.2666 | 54.7073 | 5.9653 | 152 | 42.05 | 0 | 284.2648 | 0
8951 | 788.6996 | 5.3528 | 25.4485 | 102.5699 | 78.9465 | 10.45 | 73.7573 | 14.2213 | 7.5928 | 39.2117 | 100.1418 | 8.6393 | 178.3148 | 115.4425 | 245.0722 | 8.2209 | 53.3293 | 5.7315 | 147 | 39.7948 | 0 | 285.0625 | 0
8952 | 762.8575 | 3.6908 | 25.4727 | 102.9601 | 78.9417 | 10.45 | 71.9623 | 14.217 | 7.8744 | 39.6644 | 87.8465 | 8.3768 | 172.3986 | 105.238 | 247.025 | 8.0576 | 52.945 | 5.0314 | 124 | 36.6123 | 0 | 275.4032 | 0
8953 | 775.4369 | 3.2101 | 25.5035 | 101.0491 | 77.9455 | 11.3997 | 76.5154 | 14.1127 | 7.9201 | 40.7128 | 82.7264 | 8.1297 | 170.9117 | 96.7845 | 249.2024 | 8.1203 | 52.9217 | 4.542 | 116 | 34.7299 | 0 | 278.5706 | 0
8954 | 761.9614 | 2.9954 | 25.5284 | 101.281 | 78.9409 | 10.4503 | 72.0199 | 14.0422 | 6.8584 | 41.6212 | 82.3103 | 8.0268 | 169.3602 | 92.0113 | 252.9521 | 8.012 | 52.743 | 3.387 | 113 | 33.8281 | 0 | 278.4437 | 0
8955 | 747.062 | 2.5496 | 25.6043 | 100.1404 | 73.941 | 15.2029 | 69.7865 | 14.0508 | 6.5575 | 40.4314 | 80.5813 | 7.8902 | 167.2923 | 89.61 | 246.121 | 8.1429 | 52.7284 | 2.8261 | 107 | 34.2655 | 0 | 278.427 | 0
8956 | 747.9348 | 2.8922 | 25.5589 | 99.6469 | 72.9417 | 16.15 | 74.6765 | 14.1697 | 6.385 | 39.7975 | 80.2563 | 8.7634 | 166.4421 | 86.3023 | 236.5596 | 8.2406 | 52.7607 | 2.7708 | 104 | 33.7008 | 0 | 275.6972 | 0
8957 | 744.2539 | 3.191 | 25.7922 | 98.758 | 73.9481 | 15.1958 | 72.3616 | 14.2836 | 9.1022 | 39.82 | 80.2887 | 8.151 | 166.0978 | 84.6491 | 229.4322 | 8.0592 | 54.138 | 2.7397 | 106 | 36.5816 | 0 | 272.6791 | 0
8958 | 744.8227 | 3.858 | 26.413 | 100.0661 | 76.936 | 12.3542 | 70.7936 | 14.0966 | 7.544 | 39.4745 | 80.3511 | 7.7058 | 166.6581 | 84.7129 | 226.0634 | 8.143 | 56.4925 | 2.7441 | 100 | 44.1849 | 0 | 277.1694 | 0
8959 | 757.3025 | 4.3256 | 42.2783 | 100.6821 | 77.9435 | 11.3968 | 74.6726 | 13.9728 | 6.748 | 39.7968 | 81.4056 | 7.6909 | 168.3073 | 85.1273 | 235.5896 | 7.9255 | 53.965 | 2.7806 | 101 | 34.7982 | 0 | 275.4294 | 0
8960 | 770.3459 | 4.6409 | 52.2306 | 99.4845 | 78.9395 | 10.4503 | 73.7508 | 13.9896 | 8.1257 | 40.4511 | 84.3518 | 7.9562 | 187.8259 | 93.2499 | 236.8619 | 8.2106 | 52.7251 | 3.3393 | 108 | 35.6929 | 0 | 274.259 | 0
8961 | 772.5123 | 4.0446 | 63.7156 | 97.6963 | 78.9433 | 10.45 | 70.1493 | 13.8831 | 9.0027 | 50.4759 | 84.1988 | 8.6333 | 208.3042 | 107.011 | 232.7634 | 7.9575 | 52.0959 | 4.7395 | 107 | 43.0655 | 0 | 281.454 | 0
8962 | 788.164 | 3.1183 | 66.6423 | 97.3063 | 77.9372 | 11.4029 | 77.4373 | 13.8604 | 10.1892 | 73.2512 | 83.5419 | 10.1023 | 220.8052 | 130.15 | 247.1649 | 7.6284 | 51.342 | 6.4178 | 137 | 50.1433 | 0 | 277.4521 | 0.010107
8963 | 823.8709 | 2.9638 | 67.9971 | 97.4018 | 78.9431 | 10.4471 | 92.1581 | 13.5636 | 10.0195 | 81.8561 | 94.8432 | 10.3901 | 236.7099 | 149.1193 | 273.57 | 7.6018 | 51.3554 | 8.1052 | 141 | 54.9339 | 0 | 282.1286 | 0.018363
8964 | 848.0067 | 2.9092 | 69.1769 | 96.756 | 79.9332 | 9.5003 | 99.9161 | 13.3412 | 12.5778 | 81.5732 | 108.1926 | 10.3468 | 244.3304 | 155.9433 | 308.6039 | 7.5634 | 51.2865 | 9.3848 | 149 | 61.424 | 0 | 289.1074 | 0.011091
8965 | 853.9275 | 2.638 | 69.886 | 99.6231 | 78.9359 | 10.4497 | 106.7538 | 13.3009 | 14.2735 | 81.0272 | 120.233 | 10.1794 | 251.5791 | 162.6208 | 320.1665 | 7.604 | 51.3856 | 9.7886 | 174 | 65.8171 | 0 | 287.4278 | 0.012385
8966 | 856.5733 | 2.8107 | 70.3294 | 102.6061 | 78.9368 | 10.45 | 111.9841 | 13.3114 | 14.6745 | 79.6431 | 123.7976 | 12.9051 | 256.8548 | 178.6402 | 311.4539 | 7.7364 | 51.7691 | 10.3174 | 161 | 62.1567 | 0 | 295.3345 | 0.009846
8967 | 860.8918 | 3.4311 | 70.4876 | 104.0316 | 78.9403 | 10.45 | 106.8995 | 13.3355 | 14.498 | 78.9758 | 125.7332 | 20.1666 | 256.9718 | 187.0706 | 324.8927 | 7.6827 | 52.5214 | 10.5221 | 159 | 60.2864 | 0 | 292.3315 | 0.010167
8968 | 857.9497 | 4.7832 | 68.7237 | 110.6621 | 79.9342 | 9.5003 | 100.1074 | 13.677 | 12.6872 | 71.1605 | 127.0473 | 20.2811 | 246.9144 | 181.8618 | 335.9499 | 7.7699 | 51.6929 | 10.5065 | 172 | 62.4579 | 0 | 289.3647 | 0
8969 | 855.3954 | 5.2767 | 46.7195 | 109.2079 | 76.9413 | 12.3492 | 89.1061 | 14.0005 | 9.9304 | 56.2695 | 129.9837 | 21.9527 | 243.6593 | 196.3651 | 340.7403 | 8.057 | 52.9071 | 10.4938 | 161 | 65.8204 | 0 | 282.3889 | 0
8970 | 851.5902 | 5.4224 | 29.7639 | 107.9032 | 77.9447 | 11.4003 | 81.8619 | 14.0661 | 9.5664 | 47.2458 | 129.9758 | 20.7128 | 243.2584 | 185.1079 | 316.0329 | 8.3153 | 52.9529 | 10.206 | 144 | 63.2077 | 0 | 289.746 | 0
8971 | 850.9656 | 5.4513 | 26.2927 | 105.1139 | 78.9445 | 10.4503 | 86.7856 | 14.0596 | 11.3872 | 40.4738 | 129.3621 | 17.0033 | 234.9565 | 162.3996 | 304.0896 | 8.3075 | 53.3455 | 9.2431 | 128 | 59.6536 | 0 | 287.4731 | 0
8972 | 842.4989 | 4.8523 | 26.2613 | 101.3897 | 79.9438 | 9.5003 | 109.4775 | 14.0654 | 8.72 | 37.7674 | 119.38 | 12.7085 | 217.2563 | 151.4082 | 308.1642 | 8.2061 | 53.8928 | 8.4596 | 119 | 55.5241 | 0 | 280.905 | 0
8973 | 806.4748 | 4.9941 | 26.2381 | 96.7187 | 78.9446 | 10.4497 | 102.8254 | 14.0381 | 7.0496 | 37.7572 | 95.788 | 8.916 | 208.0773 | 147.3357 | 310.9771 | 8.2397 | 53.4985 | 7.0816 | 119 | 51.9989 | 0 | 271.5144 | 0
8974 | 783.2996 | 4.7117 | 26.2103 | 93.9648 | 78.9427 | 10.45 | 83.2267 | 14.2542 | 6.3193 | 37.1115 | 86.4716 | 7.7877 | 202.2632 | 135.6215 | 306.1647 | 8.0767 | 54.3934 | 5.243 | 118 | 46.9559 | 0 | 273.6323 | 0
8975 | 771.3022 | 4.6309 | 26.1635 | 93.4225 | 78.9412 | 10.45 | 83.1752 | 14.0843 | 6.048 | 36.5942 | 85.5047 | 7.7661 | 193.6169 | 116.1797 | 278.0279 | 8.2905 | 53.7465 | 4.0072 | 116 | 44.5585 | 0 | 272.999 | 0
8976 | 755.5114 | 4.3119 | 26.1465 | 94.2402 | 78.941 | 10.45 | 76.8434 | 13.9698 | 6.9428 | 34.9473 | 83.3351 | 7.7796 | 179.6889 | 104.7225 | 255.2793 | 8.3169 | 52.9745 | 3.2525 | 109 | 42.8258 | 0 | 278.061 | 0
8977 | 754.2186 | 4.1085 | 26.218 | 93.3691 | 78.946 | 10.45 | 71.4177 | 13.9986 | 6.7976 | 33.6319 | 81.6545 | 7.791 | 172.2059 | 96.1032 | 245.6725 | 8.218 | 52.8578 | 2.9783 | 99 | 42.0507 | 0 | 271.7177 | 0
8978 | 742.7893 | 2.9672 | 26.33 | 92.4954 | 78.9422 | 10.45 | 80.3337 | 13.9883 | 6.3907 | 33.2315 | 81.2592 | 7.7948 | 170.5547 | 90.9372 | 244.2579 | 8.316 | 52.928 | 2.8677 | 99 | 43.224 | 0 | 269.7219 | 0
8979 | 725.365 | 2.4218 | 26.248 | 92.2559 | 78.9462 | 10.45 | 80.9889 | 14.0178 | 6.2627 | 32.8709 | 81.2803 | 8.2407 | 170.4274 | 94.5405 | 244.8303 | 8.1089 | 52.9823 | 2.9227 | 100 | 41.0999 | 0 | 268.1517 | 0
8980 | 732.8632 | 2.4139 | 26.8066 | 93.0259 | 79.945 | 9.5003 | 72.28 | 11.5239 | 6.1827 | 32.5859 | 81.2006 | 8.0007 | 170.4012 | 95.7077 | 236.8199 | 8.3574 | 52.9532 | 2.7531 | 99 | 39.9468 | 0 | 271.1948 | 0
8981 | 744.2889 | 2.9173 | 28.3996 | 94.0867 | 78.9431 | 10.4526 | 74.9484 | 10.6015 | 6.4753 | 32.737 | 81.8779 | 7.8096 | 173.3366 | 87.9347 | 227.9463 | 8.3527 | 54.8115 | 2.4986 | 97 | 39.3488 | 0 | 313.3439 | 0
8982 | 755.2713 | 3.8979 | 31.0345 | 92.9457 | 78.9432 | 10.4471 | 88.6086 | 12.9167 | 6.452 | 32.8807 | 86.0256 | 9.1007 | 180.1537 | 92.7482 | 229.1961 | 8.1572 | 57.8651 | 2.4596 | 114 | 37.907 | 0 | 331.3265 | 0
8983 | 792.2243 | 5.416 | 45.9334 | 96.3263 | 75.9391 | 13.2992 | 95.6958 | 13.7575 | 8.5455 | 50.482 | 106.1771 | 16.1929 | 208.9066 | 142.5947 | 257.9821 | 11.1195 | 54.5574 | 3.949 | 165 | 43.9242 | 0 | 383.774 | 0
8984 | 856.7852 | 10.7692 | 69.1306 | 103.4055 | 72.1011 | 17.0989 | 113.9648 | 13.8399 | 11.9275 | 99.4136 | 143.2538 | 29.5825 | 270.4015 | 196.8102 | 362.224 | 25.505 | 60.6498 | 9.923 | 256 | 57.2341 | 0 | 440.1388 | 0
8985 | 919.194 | 11.5345 | 90.7028 | 116.6749 | 70.0317 | 18.9995 | 144.9421 | 12.6974 | 8.2417 | 113.1199 | 165.8185 | 37.4759 | 328.6618 | 241.5694 | 464.7556 | 31.1963 | 71.4782 | 16.8179 | 334 | 65.9528 | 0 | 501.2852 | 0
8986 | 986.508 | 8.7042 | 102.9313 | 127.0055 | 68.9404 | 19.9497 | 150.8598 | 12.8883 | 6.4869 | 111.8081 | 175.3731 | 41.565 | 362.2086 | 267.9292 | 538.507 | 31.9557 | 79.7959 | 20.3735 | 349 | 67.3232 | 0 | 546.3259 | 0.017459
8987 | 1048.585 | 7.8876 | 102.7216 | 131.4144 | 70.9343 | 18.0505 | 143.1919 | 16.6467 | 8.1496 | 107.3697 | 182.5838 | 42.2558 | 381.9524 | 289.5536 | 580.19 | 32.9962 | 90.5293 | 19.2243 | 316 | 67.0541 | 0 | 569.8804 | 0.017751
8988 | 1119.1348 | 7.6576 | 104.4816 | 131.6286 | 69.9362 | 18.9997 | 156.0236 | 14.3915 | 7.6883 | 108.2122 | 188.9554 | 41.2167 | 388.3987 | 331.1601 | 593.008 | 33.8267 | 93.8354 | 18.7421 | 333 | 69.5733 | 0 | 566.6038 | 0.01886
8989 | 1113.5823 | 7.7062 | 103.4588 | 131.524 | 68.9377 | 19.9497 | 163.9715 | 15.6278 | 15.0488 | 107.8038 | 187.7464 | 42.6162 | 394.3885 | 358.9602 | 580.4423 | 35.1055 | 92.0102 | 18.9883 | 322 | 72.2438 | 0 | 565.6538 | 0.018686
8990 | 1110.1028 | 8.0323 | 105.1297 | 138.8452 | 66.9377 | 21.8495 | 155.6229 | 17.6359 | 21.3507 | 113.1359 | 190.3263 | 43.4525 | 398.865 | 367.4082 | 577.6552 | 34.9568 | 97.0771 | 19.5058 | 285 | 76.2099 | 0 | 567.1713 | 0.022734
8991 | 1119.549 | 7.4679 | 103.4492 | 139.8336 | 68.9314 | 19.9561 | 163.2433 | 12.8708 | 23.3008 | 116.1464 | 192.5976 | 42.3957 | 399.5603 | 362.1778 | 582.2487 | 34.7779 | 99.2283 | 19.9778 | 266 | 75.7872 | 0 | 569.7427 | 0.0061847
8992 | 1092.8215 | 7.0055 | 103.6831 | 134.7852 | 69.9453 | 18.9947 | 163.4155 | 16.5162 | 24.1792 | 115.1894 | 191.9995 | 42.9327 | 392.8737 | 355.5466 | 572.0357 | 35.6402 | 97.5822 | 20.318 | 257 | 75.5904 | 0 | 548.8038 | 0
8993 | 1072.2625 | 6.6372 | 99.35 | 128.5378 | 70.9394 | 18.0503 | 144.4034 | 14.6829 | 24.42 | 113.1213 | 191.2224 | 43.4933 | 369.8464 | 333.6507 | 520.0653 | 30.9187 | 93.4656 | 19.783 | 224 | 75.1959 | 0 | 486.4456 | 0
8994 | 1035.1786 | 6.7758 | 94.135 | 116.224 | 77.932 | 11.4018 | 138.9105 | 13.2755 | 23.1873 | 98.707 | 181.9166 | 42.4569 | 336.3656 | 270.4149 | 433.9411 | 16.2231 | 85.6337 | 19.0286 | 200 | 70.0307 | 0 | 384.4618 | 0
8995 | 979.8435 | 6.377 | 87.8055 | 100.1927 | 77.9384 | 11.4 | 126.8924 | 14.81 | 14.7665 | 70.9605 | 153.649 | 30.8687 | 278.4347 | 191.4534 | 367.6454 | 10.4504 | 78.4718 | 16.0871 | 187 | 60.9442 | 0 | 344.1727 | 0
8996 | 941.2748 | 6.25 | 68.1865 | 95.3764 | 78.9445 | 10.4503 | 95.1765 | 9.6019 | 8.6525 | 59.1935 | 137.8268 | 15.0943 | 239.7485 | 160.1553 | 349.4822 | 9.9661 | 68.3323 | 9.7759 | 173 | 54.131 | 0 | 309.5229 | 0
8997 | 897.1569 | 5.9924 | 35.5141 | 95.3274 | 78.9437 | 10.45 | 90.7757 | 11.9523 | 7.6256 | 51.5578 | 128.6355 | 10.1573 | 216.9329 | 147.0245 | 339.8032 | 9.9993 | 64.2118 | 6.7152 | 150 | 50.7343 | 0 | 286.647 | 0
8998 | 858.999 | 5.641 | 25.6761 | 94.2413 | 79.9396 | 9.5029 | 94.4809 | 14.0054 | 7.2616 | 42.413 | 112.0682 | 9.2847 | 198.6996 | 133.8762 | 298.1826 | 9.9348 | 57.1763 | 5.5622 | 145 | 45.7611 | 0 | 272.3551 | 0
8999 | 828.1916 | 4.4135 | 25.7532 | 94.0495 | 78.9431 | 10.4471 | 94.6353 | 9.1442 | 6.7426 | 36.6268 | 96.2598 | 8.8593 | 188.3012 | 117.2818 | 262.3862 | 9.8587 | 53.1481 | 4.7539 | 135 | 43.2555 | 0 | 272.0058 | 0
9000 | 808.0769 | 3.1458 | 25.9791 | 93.1465 | 78.9441 | 10.45 | 96.9831 | 11.8056 | 7.6778 | 34.6765 | 90.9171 | 8.963 | 183.0083 | 105.6661 | 242.9141 | 9.9754 | 53.1281 | 4.191 | 115 | 41.0167 | 0 | 270.0437 | 0
9001 | 804.2938 | 2.6962 | 25.8278 | 92.6145 | 79.9434 | 9.5003 | 104.2682 | 13.9958 | 7.3977 | 33.7908 | 89.3476 | 8.6498 | 185.453 | 100.6509 | 232.7241 | 10.0281 | 52.6607 | 3.9207 | 108 | 39.4485 | 0 | 272.2122 | 0
9002 | 790.2843 | 2.8518 | 25.8613 | 92.3419 | 78.9444 | 10.4497 | 94.0789 | 14.0433 | 6.4893 | 33.3981 | 91.6671 | 8.5056 | 190.6114 | 94.2373 | 232.3576 | 9.9388 | 52.4587 | 3.2204 | 102 | 39.1547 | 0 | 276.6093 | 0
9003 | 784.9367 | 2.6051 | 25.8572 | 93.0796 | 78.9413 | 10.45 | 82.3333 | 9.2711 | 6.1898 | 33.6728 | 93.8021 | 8.5229 | 188.3735 | 89.258 | 237.2985 | 9.8651 | 52.5676 | 2.746 | 108 | 39.3034 | 0 | 278.4088 | 0
9004 | 788.6665 | 2.4266 | 25.886 | 93.4408 | 78.9455 | 10.45 | 87.3245 | 11.8103 | 6.1413 | 34.0519 | 93.5145 | 8.5214 | 183.0363 | 87.3043 | 237.6065 | 9.8545 | 52.5288 | 2.6796 | 104 | 38.7179 | 0 | 276.8178 | 0
9005 | 793.1254 | 2.9518 | 25.9751 | 94.0101 | 78.9444 | 10.45 | 83.7193 | 14.0913 | 6.1443 | 34.5027 | 91.8805 | 8.4973 | 186.4362 | 87.4712 | 236.0176 | 9.9106 | 53.9717 | 2.68 | 103 | 37.9817 | 0 | 305.8184 | 0
9006 | 803.3907 | 3.8696 | 35.1704 | 94.9745 | 79.943 | 9.5003 | 82.1522 | 14.0883 | 6.5007 | 34.3218 | 91.5154 | 10.8614 | 197.2843 | 95.711 | 246.9498 | 9.9925 | 56.279 | 2.7105 | 100 | 36.5429 | 0 | 347.2508 | 0
9007 | 838.4391 | 5.5961 | 56.1011 | 100.3215 | 77.9416 | 11.3995 | 100.3979 | 13.9263 | 8.6477 | 52.3982 | 104.0558 | 16.8092 | 223.9745 | 153.2852 | 265.3123 | 12.6228 | 53.5031 | 3.5902 | 192 | 44.644 | 0 | 398.5538 | 0
9008 | 888.3073 | 6.6385 | 81.1407 | 102.2769 | 70.9399 | 18.0482 | 121.9099 | 14.7361 | 15.6299 | 95.9506 | 140.7525 | 28.6884 | 280.7016 | 227.1851 | 338.8078 | 27.4969 | 58.2633 | 5.4281 | 234 | 60.046 | 0 | 437.4133 | 0
9009 | 959.9406 | 7.0679 | 99.5652 | 115.8059 | 69.9376 | 18.9997 | 134.5693 | 16.1308 | 21.5115 | 110.8445 | 169.5944 | 36.7605 | 337.7166 | 290.6723 | 470.14 | 37.4682 | 69.0661 | 13.725 | 296 | 73.0509 | 0 | 522.7269 | 0
9010 | 1046.4733 | 5.7593 | 103.3011 | 127.3393 | 69.938 | 19 | 149.0499 | 16.5789 | 22.2135 | 106.1352 | 183.1117 | 39.6368 | 378.3102 | 340.9529 | 566.1451 | 41.4892 | 81.3453 | 18.5516 | 345 | 75.6528 | 0 | 564.8833 | 0.01364
9011 | 1128.8019 | 4.791 | 102.3464 | 133.862 | 70.9352 | 18.0503 | 155.691 | 15.7799 | 21.8049 | 105.2937 | 190.1518 | 41.7613 | 400.2745 | 362.6468 | 593.8529 | 41.9656 | 94.8609 | 19.5529 | 335 | 74.2831 | 0 | 561.6587 | 0.013969
9012 | 1178.3742 | 6.3642 | 107.0569 | 136.1228 | 67.9393 | 20.8992 | 151.1642 | 13.4836 | 22.5924 | 106.3924 | 193.1039 | 41.1945 | 411.0036 | 374.4341 | 604.6177 | 42.685 | 98.0705 | 19.4733 | 298 | 79.5588 | 0 | 561.7293 | 0.015508
9013 | 1163.5235 | 9.9209 | 107.6579 | 131.9108 | 65.9437 | 22.7995 | 153.0781 | 12.527 | 21.1458 | 104.3866 | 194.6522 | 39.8441 | 417.4933 | 374.144 | 614.1587 | 43.7093 | 97.388 | 19.75 | 331 | 75.0566 | 0 | 563.5851 | 0.016116
9014 | 1146.7084 | 11.4086 | 108.712 | 137.1336 | 64.9457 | 23.7497 | 149.8367 | 14.4792 | 22.598 | 106.8554 | 195.2632 | 41.5947 | 425.9216 | 373.6623 | 615.3895 | 43.9738 | 97.8513 | 20.3051 | 286 | 73.7893 | 0 | 570.6423 | 0.012514
9015 | 1138.6352 | 7.4932 | 106.0574 | 142.2187 | 67.9446 | 20.9008 | 146.9583 | 15.8952 | 24.182 | 107.7414 | 192.4864 | 43.2314 | 430.1791 | 375.6939 | 610.091 | 44.9637 | 95.5704 | 20.4326 | 256 | 74.0742 | 0 | 583.6113 | 0.0054608
9016 | 1124.3541 | 7.3582 | 100.3164 | 140.4734 | 66.9363 | 21.8558 | 154.8719 | 15.2979 | 24.7685 | 105.9746 | 192.6541 | 45.6069 | 414.6555 | 360.2676 | 576.1061 | 42.3421 | 93.6657 | 20.1563 | 272 | 73.6015 | 0 | 586.7667 | 0
9017 | 1090.8452 | 7.3089 | 93.4964 | 133.4975 | 68.9492 | 19.9445 | 141.0652 | 11.1671 | 24.7347 | 106.5969 | 193.1238 | 44.2378 | 389.0632 | 330.3744 | 528.5167 | 35.4277 | 95.7886 | 19.7293 | 235 | 71.9917 | 0 | 528.6418 | 0
9018 | 1035.4749 | 6.4766 | 90.567 | 118.911 | 77.9356 | 11.4055 | 125.3912 | 13.1359 | 18.8507 | 92.3992 | 182.3917 | 39.9039 | 347.4299 | 288.4646 | 457.5765 | 21.0017 | 89.0158 | 18.609 | 201 | 67.2969 | 0 | 431.2992 | 0
9019 | 985.5822 | 5.8168 | 88.7068 | 108.1005 | 78.9456 | 10.4471 | 111.5472 | 14.2976 | 14.4898 | 63.1287 | 153.6928 | 28.7241 | 306.827 | 221.3253 | 407.5586 | 13.1639 | 80.2534 | 14.6843 | 195 | 59.0321 | 0 | 397.3489 | 0
9020 | 935.5553 | 5.9125 | 73.0902 | 101.6867 | 78.9444 | 10.45 | 87.4438 | 14.2172 | 9.0688 | 50.7947 | 137.4463 | 12.8818 | 272.6067 | 190.8677 | 367.6319 | 10.3595 | 65.5417 | 8.08 | 169 | 56.3135 | 0 | 333.0632 | 0
9021 | 915.9657 | 6.0111 | 37.8585 | 97.0841 | 78.9429 | 10.45 | 87.9163 | 9.009 | 6.8321 | 48.28 | 129.9527 | 7.7097 | 243.7491 | 167.0835 | 330.2062 | 9.3313 | 58.0382 | 5.5953 | 159 | 54.606 | 0 | 305.8166 | 0
9022 | 884.811 | 5.365 | 26.5084 | 94.5299 | 79.94 | 9.5003 | 88.5868 | 11.5977 | 6.393 | 39.432 | 116.7169 | 7.3596 | 218.5419 | 145.6481 | 288.86 | 9.162 | 54.9047 | 4.7431 | 150 | 49.1096 | 0 | 295.9391 | 0
9023 | 855.2133 | 4.4471 | 26.4107 | 93.3884 | 78.9439 | 10.4497 | 79.4548 | 14.1553 | 6.1384 | 32.0535 | 100.3228 | 7.3277 | 205.8937 | 133.0881 | 269.2907 | 9.246 | 54.4235 | 4.1296 | 135 | 47.4345 | 0 | 294.608 | 0
9024 | 835.7456 | 3.106 | 26.0912 | 93.8054 | 78.9456 | 10.45 | 78.9422 | 11.8527 | 6.2137 | 30.3036 | 91.3293 | 7.4394 | 199.0482 | 126.2649 | 261.9498 | 9.1067 | 54.456 | 3.716 | 124 | 45.5462 | 0 | 290.3021 | 0
9025 | 832.8468 | 2.5297 | 26.0648 | 93.1416 | 78.9454 | 10.45 | 85.5764 | 10.1507 | 6.2557 | 28.1422 | 90.3271 | 7.4216 | 193.1799 | 119.2057 | 247.6862 | 9.3394 | 54.5273 | 3.6834 | 112 | 42.997 | 0 | 298.5738 | 0
9026 | 823.8892 | 2.5245 | 26.016 | 92.5624 | 78.9435 | 10.45 | 78.4246 | 12.7855 | 6.3145 | 28.0612 | 90.5125 | 7.1005 | 193.24 | 113.53 | 247.2733 | 9.2654 | 54.4412 | 3.8323 | 103 | 43.8656 | 0 | 302.4432 | 0
9027 | 812.099 | 2.5121 | 26.0403 | 92.3585 | 76.9491 | 12.3495 | 73.4989 | 13.536 | 6.4045 | 28.5142 | 89.5159 | 7.7751 | 193.0388 | 112.124 | 251.9989 | 9.2256 | 54.4306 | 3.229 | 105 | 43.3024 | 0 | 305.5322 | 0
9028 | 814.2148 | 2.5438 | 26.0604 | 92.4146 | 78.9497 | 10.4505 | 81.3717 | 9.3986 | 6.4587 | 28.2557 | 88.5896 | 7.3504 | 192.0799 | 109.3096 | 250.431 | 9.317 | 54.5932 | 2.5154 | 101 | 42.8773 | 0 | 301.306 | 0
9029 | 806.4462 | 2.9081 | 26.1207 | 92.6936 | 78.9464 | 10.45 | 81.8068 | 12.1724 | 6.3305 | 28.3017 | 88.9392 | 6.9659 | 195.6551 | 108.0265 | 244.3055 | 9.0203 | 56.0545 | 2.6499 | 101 | 42.7328 | 0 | 326.7417 | 0
9030 | 825.2452 | 3.7618 | 36.4535 | 93.9157 | 78.9415 | 10.45 | 78.6147 | 13.9853 | 6.9582 | 31.589 | 92.2037 | 10.1088 | 207.0961 | 115.6903 | 249.9979 | 9.3032 | 58.5791 | 3 | 103 | 42.5589 | 0 | 374.7212 | 0
9031 | 857.178 | 5.4168 | 53.2393 | 99.0467 | 77.9432 | 11.3997 | 94.0811 | 8.9748 | 7.7924 | 51.516 | 107.4462 | 16.5221 | 235.628 | 168.2569 | 275.6943 | 11.4904 | 55.8429 | 3.2239 | 177 | 47.8048 | 0 | 419.4562 | 0
9032 | 905.7038 | 10.1877 | 81.825 | 100.5373 | 68.9459 | 19.9476 | 122.9858 | 12.6475 | 14.9129 | 102.6197 | 146.3306 | 37.0125 | 290.4226 | 234.9056 | 376.4633 | 28.8533 | 62.0475 | 6.646 | 297 | 58.2778 | 0 | 455.847 | 0
9033 | 965.987 | 15.1901 | 96.3451 | 110.5593 | 67.9399 | 20.8997 | 132.7852 | 15.9076 | 20.9558 | 118.5801 | 173.452 | 46.9826 | 341.6919 | 286.0619 | 479.0761 | 39.8107 | 71.6382 | 13.5864 | 310 | 65.3708 | 0 | 516.7423 | 0
9034 | 1036.9758 | 21.1329 | 104.6795 | 127.1306 | 65.9361 | 22.7995 | 141.6217 | 16.1168 | 22.5928 | 110.8567 | 179.2705 | 45.2639 | 383.3795 | 330.3099 | 553.0697 | 43.615 | 83.5211 | 17.9214 | 297 | 68.089 | 0 | 571.0783 | 0.0038189
9035 | 1102.3823 | 21.9101 | 102.7536 | 133.8432 | 64.9265 | 23.7563 | 151.4679 | 15.6277 | 22.4827 | 108.3437 | 181.1639 | 43.9179 | 401.1362 | 359.1438 | 574.8108 | 44.4093 | 88.7721 | 18.7254 | 300 | 67.8214 | 0 | 556.7446 | 0.0050781
9036 | 1135.5368 | 19.6003 | 105.1113 | 133.086 | 66.94 | 21.8439 | 146.581 | 16.2652 | 22.0872 | 108.5587 | 186.3101 | 43.1184 | 408.5526 | 374.1933 | 597.4851 | 44.104 | 99.3714 | 19.4703 | 292 | 70.2679 | 0 | 559.2134 | 0.0078381
9037 | 1116.2569 | 18.7179 | 105.0301 | 134.2218 | 66.9395 | 21.85 | 153.4998 | 11.9187 | 21.1532 | 109.3243 | 192.8569 | 40.8013 | 412.5268 | 383.6075 | 611.0323 | 44.2311 | 99.4637 | 19.8734 | 302 | 69.8786 | 0 | 559.5982 | 0.0073978
9038 | 1119.9664 | 19.1973 | 105.7449 | 133.1882 | 63.9407 | 24.6992 | 160.7647 | 16.0458 | 21.7387 | 112.6604 | 194.8475 | 39.2546 | 424.71 | 391.6808 | 594.9554 | 45.2343 | 99.7283 | 19.8234 | 276 | 72.0689 | 0 | 565.263 | 0.013395
9039 | 1122.1615 | 14.5092 | 103.3214 | 132.3035 | 66.9391 | 21.8508 | 147.9187 | 13.1076 | 22.3337 | 111.6412 | 196.3927 | 41.7569 | 430.9974 | 383.0064 | 576.2345 | 43.9902 | 101.6105 | 19.7811 | 260 | 71.732 | 0 | 546.0985 | 0.0069347
9040 | 1095.5577 | 10.3098 | 99.9395 | 132.7654 | 68.943 | 19.9505 | 143.2674 | 13.8822 | 22.5518 | 109.5519 | 197.064 | 43.1155 | 410.2634 | 374.5184 | 570.3772 | 40.5213 | 103.1871 | 19.9394 | 264 | 69.0706 | 0 | 546.2049 | 0
9041 | 1067.1195 | 7.53 | 93.0992 | 131.0368 | 70.9388 | 18.0555 | 140.7591 | 12.4712 | 23.1447 | 111.8984 | 195.524 | 41.6346 | 385.3218 | 353.62 | 533.4838 | 33.7264 | 99.8512 | 19.7354 | 249 | 69.314 | 0 | 509.4761 | 0
9042 | 1006.3649 | 6.9778 | 81.5908 | 117.5357 | 77.9426 | 11.4 | 124.9093 | 11.1792 | 22.5932 | 96.5502 | 186.0783 | 42.0633 | 348.592 | 309.229 | 455.3871 | 18.9394 | 90.7608 | 19.3727 | 206 | 67.7946 | 0 | 400.156 | 0
9043 | 963.5708 | 6.4671 | 74.1491 | 103.01 | 78.9493 | 10.4471 | 102.4263 | 11.9448 | 17.1873 | 61.7013 | 155.3637 | 33.6325 | 294.5835 | 261.9502 | 387.4096 | 12.4544 | 82.0392 | 17.679 | 184 | 57.9727 | 0 | 368.6238 | 0
9044 | 928.122 | 5.7021 | 64.1353 | 98.0597 | 79.9468 | 9.5003 | 88.6406 | 9.6025 | 10.9417 | 48.4053 | 154.6829 | 16.0429 | 265.3673 | 227.6127 | 329.5522 | 10.7711 | 69.056 | 11.8319 | 171 | 53.8214 | 0 | 313.5564 | 0
9045 | 904.9353 | 5.0304 | 34.1579 | 95.053 | 79.9459 | 9.5 | 93.9821 | 11.5956 | 8.9117 | 44.479 | 147.8161 | 9.8917 | 246.7733 | 175.1433 | 294.376 | 10.3238 | 58.8413 | 8.0705 | 160 | 51.3736 | 0 | 290.9058 | 0
9046 | 865.6009 | 4.8582 | 24.4129 | 91.998 | 78.9365 | 10.4526 | 99.3212 | 8.3758 | 8.1465 | 37.7504 | 114.2837 | 9.2208 | 223.3789 | 142.5416 | 263.2741 | 10.1943 | 56.5793 | 6.3867 | 150 | 47.5575 | 0 | 285.8916 | 0
9047 | 835.3134 | 5.2536 | 24.3476 | 92.8698 | 79.9465 | 9.4974 | 80.1087 | 11.8937 | 7.7567 | 32.6527 | 91.1037 | 9.2358 | 204.7214 | 126.6715 | 240.2367 | 10.3382 | 56.864 | 4.9061 | 136 | 45.4643 | 0 | 286.749 | 0
9048 | 822.2338 | 4.0395 | 24.2524 | 91.5497 | 79.95 | 9.5 | 78.5463 | 8.3281 | 7.7143 | 30.6534 | 84.8073 | 8.7309 | 196.9951 | 120.487 | 237.0433 | 10.0934 | 56.1684 | 4.1524 | 120 | 42.6835 | 0 | 276.2623 | 0
9049 | 817.3647 | 3.3529 | 23.9392 | 91.5732 | 78.9515 | 10.4497 | 82.1702 | 11.6743 | 7.6011 | 30.0167 | 83.1045 | 8.6602 | 192.7676 | 117.5847 | 240.1344 | 10.136 | 55.5578 | 4.2012 | 108 | 41.6666 | 0 | 280.524 | 0
9050 | 808.8967 | 3.044 | 23.9404 | 90.7701 | 79.9508 | 9.5003 | 79.585 | 8.8351 | 7.6072 | 30.4391 | 82.623 | 8.5477 | 188.2841 | 112.5984 | 241.5942 | 9.7949 | 55.4801 | 4.063 | 107 | 41.1 | 0 | 276.974 | 0
9051 | 807.5393 | 2.8791 | 23.9103 | 90.4275 | 78.9449 | 10.4497 | 69.6484 | 11.2565 | 7.6636 | 30.6389 | 82.8797 | 8.956 | 186.4024 | 103.5514 | 238.0964 | 9.742 | 55.3509 | 4.0382 | 101 | 41.0454 | 0 | 278.3745 | 0
9052 | 812.3055 | 2.931 | 23.7021 | 90.1882 | 79.9477 | 9.5003 | 75.0675 | 12.977 | 7.8443 | 28.8701 | 82.3986 | 8.9308 | 186.3265 | 91.3494 | 232.7758 | 10.0022 | 55.3445 | 3.9401 | 102 | 39.9145 | 0 | 279.0978 | 0
9053 | 808.1474 | 3.2686 | 23.6365 | 90.2305 | 79.9468 | 9.5 | 80.3368 | 9.1822 | 7.6408 | 27.189 | 82.2598 | 8.511 | 191.2278 | 87.0199 | 227.6765 | 9.7861 | 56.7605 | 3.1248 | 104 | 39.0345 | 0 | 301.5448 | 0
9054 | 831.3604 | 4.1396 | 32.1946 | 92.0189 | 78.9456 | 10.4497 | 79.4245 | 11.9339 | 7.6349 | 27.0105 | 83.872 | 9.8806 | 202.4701 | 95.5194 | 230.4946 | 9.8069 | 58.5658 | 3.7127 | 103 | 41.2525 | 0 | 356.0831 | 0
9055 | 857.9103 | 5.8724 | 56.5544 | 95.8677 | 77.9418 | 11.3997 | 87.3614 | 10.8147 | 9.6264 | 49.5354 | 98.1968 | 18.0278 | 232.7597 | 165.5841 | 254.3079 | 12.6161 | 56.4714 | 4.9347 | 183 | 47.802 | 0 | 402.7973 | 0
9056 | 914.7699 | 9.3292 | 82.195 | 98.9025 | 70.9405 | 18.0482 | 115.7947 | 11.1788 | 16.342 | 92.743 | 139.5756 | 33.2082 | 284.9695 | 240.5884 | 344.0126 | 28.0818 | 60.9464 | 8.6243 | 323 | 59.0176 | 0 | 459.1972 | 0
9057 | 1001.557 | 16.6423 | 94.6749 | 110.3482 | 65.9409 | 22.7987 | 134.289 | 15.4276 | 21.494 | 101.7517 | 173.6969 | 34.6767 | 336.8131 | 290.8238 | 440.373 | 36.1392 | 73.3096 | 14.7238 | 318 | 65.3556 | 0 | 527.1866 | 0
9058 | 1088.653 | 20.4264 | 102.5098 | 121.9462 | 64.939 | 23.7497 | 134.8585 | 13.2219 | 22.6718 | 97.4938 | 186.2473 | 30.7166 | 377.7565 | 322.4965 | 517.366 | 41.3092 | 97.4103 | 19.3601 | 338 | 66.1851 | 0 | 552.4902 | 0.018764
9059 | 1131.8308 | 18.5539 | 101.2321 | 130.838 | 65.9329 | 22.8003 | 143.979 | 12.4646 | 22.592 | 109.4582 | 190.4672 | 31.625 | 393.2857 | 351.899 | 541.8389 | 43.3941 | 115.5072 | 18.8027 | 344 | 67.9685 | 0 | 561.1203 | 0.027255
9060 | 1141.2644 | 12.8258 | 105.4284 | 132.257 | 65.9358 | 22.8 | 148.6762 | 15.7662 | 21.9838 | 104.3921 | 189.3758 | 32.3105 | 399.2614 | 371.8181 | 561.7975 | 43.8146 | 117.9259 | 17.9087 | 320 | 71.0896 | 0 | 595.9206 | 0.017385
9061 | 1136.2223 | 8.372 | 104.0947 | 134.2293 | 68.94 | 19.9508 | 136.9253 | 10.8001 | 20.814 | 98.4873 | 196.7446 | 34.3872 | 403.6298 | 370.1376 | 561.5243 | 45.0573 | 101.057 | 18.5714 | 324 | 72.5102 | 0 | 590.2495 | 0.040652
9062 | 1148.2966 | 6.1867 | 100.9993 | 138.1334 | 67.9395 | 20.8997 | 143.5597 | 13.7728 | 21.3645 | 99.3811 | 195.5649 | 38.1692 | 402.843 | 370.5294 | 543.366 | 44.5256 | 94.7438 | 18.8712 | 287 | 75.431 | 0 | 595.7896 | 0.036496
9063 | 1171.1322 | 5.0012 | 103.854 | 135.4074 | 67.9348 | 20.9 | 156.6981 | 11.3533 | 21.6082 | 104.2601 | 198.0292 | 37.9264 | 409.4285 | 369.4668 | 532.0299 | 43.1275 | 92.8541 | 19.2031 | 262 | 73.6277 | 0 | 597.6237 | 0.034391
9064 | 1141.2428 | 5.4757 | 100.1148 | 130.3959 | 68.9355 | 19.9503 | 152.7095 | 13.093 | 21.0798 | 106.0381 | 201.9788 | 35.5063 | 402.82 | 366.6141 | 517.5338 | 41.8108 | 94.4568 | 19.278 | 262 | 74.2439 | 0 | 552.8346 | 0
9065 | 1108.0356 | 6.6971 | 93.2873 | 127.03 | 76.9338 | 12.3521 | 134.7307 | 13.7807 | 22.0008 | 102.9269 | 195.2322 | 32.4756 | 385.5896 | 334.8297 | 470.8378 | 37.3449 | 91.1763 | 19.0733 | 252 | 75.0085 | 0 | 499.2453 | 0
9066 | 1061.4424 | 6.8192 | 85.0362 | 117.2841 | 76.9356 | 12.35 | 126.9714 | 10.1211 | 22.3468 | 89.7979 | 174.4162 | 31.0161 | 353.4136 | 264.3211 | 404.1577 | 20.0557 | 82.1543 | 17.957 | 211 | 72.8646 | 0 | 375.8476 | 0
9067 | 1001.1163 | 6.4547 | 78.3041 | 103.9084 | 79.9378 | 9.5008 | 111.5498 | 12.4239 | 16.849 | 63.9798 | 145.2001 | 26.6152 | 300.5391 | 190.8714 | 348.4264 | 12.1019 | 72.9912 | 16.3266 | 189 | 65.7288 | 0 | 340.0128 | 0
9068 | 963.2728 | 6.0373 | 66.1245 | 97.0286 | 78.9424 | 10.4497 | 81.2647 | 8.9753 | 10.089 | 49.5541 | 133.5545 | 15.9337 | 264.6134 | 152.7511 | 319.5637 | 11.0502 | 63.8326 | 10.4596 | 172 | 56.8454 | 0 | 280.8163 | 0
9069 | 928.1394 | 5.6079 | 35.8963 | 92.845 | 79.943 | 9.5003 | 77.7661 | 11.5877 | 8.3847 | 42.683 | 126.9716 | 12.3553 | 241.4837 | 139.2594 | 299.4477 | 11.0145 | 59.9279 | 6.803 | 148 | 51.2944 | 0 | 262.9142 | 0
9070 | 905.6717 | 4.9633 | 25.6595 | 90.9925 | 78.945 | 10.4497 | 78.3465 | 13.9526 | 9.0893 | 35.1191 | 113.0495 | 10.6788 | 219.6578 | 127.9251 | 281.0938 | 10.7848 | 56.9206 | 5.509 | 141 | 47.982 | 0 | 258.1479 | 0
9071 | 878.0214 | 4.2235 | 25.5989 | 90.6409 | 79.9448 | 9.5003 | 67.7302 | 8.9647 | 9.1135 | 30.8127 | 97.3186 | 8.6182 | 204.342 | 119.1392 | 265.8093 | 10.6562 | 56.0936 | 4.9909 | 127 | 45.0396 | 0 | 256.058 | 0
9072 | 861.2953 | 3.7386 | 25.3491 | 90.2251 | 78.9435 | 10.4497 | 65.8104 | 11.7531 | 8.6832 | 30.2519 | 87.8154 | 8.094 | 195.5227 | 114.6828 | 239.7414 | 10.9438 | 56.3719 | 5.1147 | 108 | 43.2516 | 0 | 261.796 | 0
9073 | 859.1683 | 2.9174 | 25.4174 | 90.0801 | 79.9483 | 9.5003 | 74.4939 | 14.1341 | 7.8835 | 29.8229 | 83.0023 | 7.9525 | 190.1807 | 107.9759 | 230.7789 | 10.9607 | 56.4237 | 5.0913 | 108 | 44.5754 | 0 | 264.8413 | 0
9074 | 847.305 | 2.9127 | 25.7019 | 90.7042 | 78.9474 | 10.4497 | 71.2554 | 14.4717 | 7.6343 | 30.2964 | 81.4827 | 7.8244 | 185.6694 | 93.713 | 232.7619 | 10.8121 | 56.4637 | 4.3467 | 103 | 45.9946 | 0 | 271.8082 | 0
9075 | 836.5303 | 2.7149 | 25.3524 | 90.3174 | 79.949 | 9.5003 | 65.187 | 14.3368 | 7.5502 | 30.228 | 81.3843 | 7.7827 | 183.2583 | 87.8304 | 239.5672 | 10.8564 | 56.3355 | 3.7036 | 105 | 41.6712 | 0 | 272.3847 | 0
9076 | 841.3976 | 2.758 | 25.175 | 89.9445 | 78.9441 | 10.4497 | 71.213 | 14.1962 | 7.4904 | 29.6869 | 81.3292 | 7.7623 | 182.8126 | 86.0967 | 233.1157 | 10.7143 | 56.2706 | 2.9539 | 100 | 40.9551 | 0 | 270.5192 | 0
9077 | 849.9375 | 3.2312 | 25.1599 | 89.785 | 79.9434 | 9.5003 | 71.8492 | 14.1831 | 7.431 | 29.3586 | 81.6084 | 7.7375 | 187.5088 | 84.7967 | 224.9271 | 10.7442 | 57.6282 | 2.4658 | 100 | 38.7416 | 0 | 297.8133 | 0
9078 | 874.7344 | 4.1045 | 32.9414 | 90.428 | 78.9483 | 10.4497 | 71.476 | 14.1293 | 7.4694 | 30.2701 | 83.708 | 10.1299 | 198.3312 | 95.6499 | 227.2899 | 10.6726 | 59.5897 | 2.5094 | 99 | 47.9135 | 0 | 350.0816 | 0
9079 | 907.0618 | 5.7219 | 53.6146 | 97.6491 | 79.9422 | 9.5003 | 88.8082 | 14.3261 | 11.7556 | 53.683 | 99.472 | 15.7427 | 224.9421 | 153.7254 | 259.6221 | 13.3292 | 57.2085 | 3.7756 | 177 | 39.821 | 0 | 390.7243 | 0
9080 | 943.992 | 10.4673 | 83.0614 | 99.9085 | 70.9324 | 18.0526 | 116.55 | 14.8183 | 17.267 | 100.6855 | 147.7139 | 32.249 | 279.3558 | 218.0351 | 368.2289 | 28.6192 | 62.7701 | 9.6954 | 237 | 61.4086 | 0 | 411.626 | 0
9081 | 1009.3491 | 14.2653 | 95.2116 | 110.6887 | 67.9416 | 20.8942 | 124.3323 | 16.0483 | 19.3103 | 107.6104 | 178.7968 | 41.7201 | 333.6107 | 251.2062 | 465.1704 | 36.6333 | 72.9731 | 14.7992 | 327 | 74.28 | 0 | 489.8416 | 0
9082 | 1077.8726 | 18.5137 | 95.6599 | 120.4949 | 67.937 | 20.9 | 133.0094 | 16.4058 | 19.6275 | 100.5548 | 184.6223 | 41.5543 | 369.7172 | 281.6622 | 497.6952 | 41.5479 | 84.7353 | 16.5379 | 343 | 74.1531 | 0 | 533.0121 | 0.070849
9083 | 1124.2471 | 18.281 | 95.2329 | 125.2022 | 66.9373 | 21.8497 | 143.9527 | 16.7959 | 19.7202 | 97.2791 | 189.5144 | 41.7129 | 382.7858 | 305.8643 | 529.1742 | 43.9065 | 95.5577 | 16.7567 | 317 | 74.2905 | 0 | 548.0092 | 0.10342
9084 | 1127.8604 | 13.3686 | 97.6959 | 125.113 | 69.9365 | 19.0008 | 135.6611 | 11.2002 | 20.0123 | 99.0582 | 199.2946 | 38.3355 | 384.3438 | 309.7951 | 546.1995 | 42.5827 | 99.4391 | 16.3032 | 329 | 75.4152 | 0 | 562.2391 | 0.18643
9085 | 1125.673 | 11.6952 | 100.1714 | 124.3746 | 67.9432 | 20.8995 | 132.362 | 13.8872 | 19.7043 | 100.4662 | 199.9747 | 35.9643 | 382.7446 | 308.543 | 539.6989 | 45.1843 | 98.9786 | 16.9198 | 332 | 74.5156 | 0 | 550.2471 | 0.11123
9086 | 1134.7782 | 9.3539 | 99.7639 | 125.1244 | 70.9451 | 18.0508 | 142.8167 | 16.9871 | 20.5577 | 101.4191 | 199.3087 | 34.2557 | 393.2494 | 314.5361 | 522.1681 | 44.7628 | 98.7278 | 17.7943 | 324 | 70.0827 | 0 | 587.629 | 0.097103
9087 | 1136.1573 | 5.8672 | 100.9068 | 127.711 | 69.9386 | 19.005 | 138.4034 | 11.985 | 21.031 | 102.4103 | 195.6312 | 32.6559 | 394.3166 | 315.5824 | 516.1736 | 41.5647 | 101.3599 | 18.0938 | 260 | 73.6734 | 0 | 571.5999 | 0.025964
9088 | 1099.5451 | 5.3778 | 101.5108 | 127.3389 | 62.9403 | 25.65 | 135.4058 | 14.6146 | 21.4733 | 103.3621 | 188.5078 | 31.1226 | 386.9774 | 306.6655 | 515.3693 | 39.1418 | 102.9325 | 18.5878 | 249 | 72.0237 | 0 | 533.8641 | 0
9089 | 1047.6972 | 6.4664 | 97.3992 | 120.7853 | 81.9431 | 7.5979 | 132.0279 | 16.0328 | 22.1149 | 105.7101 | 183.2034 | 30.3586 | 365.6155 | 286.563 | 469.4299 | 31.9453 | 98.7891 | 19.0188 | 245 | 75.3573 | 0 | 456.7835 | 0
9090 | 1010.777 | 6.5631 | 89.5881 | 107.5337 | 76.9419 | 12.3487 | 115.8812 | 15.2818 | 22.2651 | 92.6476 | 168.01 | 28.598 | 321.711 | 237.5967 | 382.0627 | 16.8067 | 84.8693 | 19.1067 | 212 | 69.7117 | 0 | 360.2534 | 0
9091 | 966.4119 | 6.1722 | 84.7385 | 99.8849 | 83.938 | 5.7018 | 111.7633 | 15.2863 | 16.9684 | 64.3376 | 141.5506 | 25.0814 | 283.0109 | 162.3208 | 326.5249 | 10.4406 | 76.5646 | 18.2472 | 201 | 57.7957 | 0 | 315.5797 | 0
9092 | 924.2383 | 5.7031 | 72.4576 | 95.9047 | 83.9414 | 5.7 | 95.9062 | 14.6094 | 10.3699 | 49.0112 | 122.7431 | 12.9732 | 250.7 | 125.3122 | 304.2971 | 9.616 | 63.2418 | 11.9969 | 169 | 52.2507 | 0 | 285.4726 | 0
9093 | 891.3545 | 5.8779 | 37.2441 | 93.0911 | 84.9412 | 4.7516 | 75.4433 | 8.8975 | 7.5662 | 43.5802 | 99.36 | 8.1472 | 226.4797 | 105.4483 | 308.657 | 9.446 | 59.2464 | 7.0254 | 156 | 50.1449 | 0 | 276.8862 | 0
9094 | 863.402 | 5.6066 | 25.021 | 92.9437 | 82.9478 | 6.6482 | 76.0578 | 11.9514 | 6.7785 | 37.0652 | 89.2243 | 7.926 | 199.5697 | 95.9044 | 293.0907 | 9.2669 | 56.116 | 5.2545 | 156 | 47.8 | 0 | 264.058 | 0
9095 | 832.3909 | 4.5706 | 24.8389 | 92.7811 | 84.9448 | 4.7505 | 74.6654 | 14.1198 | 6.3646 | 32.3585 | 86.3379 | 7.8374 | 186.7148 | 93.8681 | 275.5528 | 9.4398 | 53.8891 | 4.717 | 144 | 45.0676 | 0 | 266.8069 | 0
9096 | 826.6653 | 3.7092 | 25.0947 | 92.6951 | 83.949 | 5.6997 | 70.2261 | 14.1022 | 6.511 | 31.6048 | 84.2787 | 7.822 | 184.8235 | 90.2587 | 260.6942 | 9.2183 | 53.6016 | 4.5794 | 133 | 45.4901 | 0 | 268.1114 | 0
9097 | 825.0769 | 3.9398 | 25.0527 | 92.7516 | 83.9442 | 5.7 | 72.0429 | 14.1079 | 6.5054 | 31.826 | 83.8704 | 7.7555 | 184.9382 | 88.7089 | 260.3587 | 9.4319 | 54.2397 | 4.5448 | 115 | 46.3956 | 0 | 274.6879 | 0
9098 | 812.0882 | 3.2882 | 24.9631 | 92.5823 | 84.9457 | 4.7503 | 75.2462 | 14.259 | 6.3883 | 33.4009 | 83.7098 | 7.9611 | 184.5087 | 88.087 | 246.4183 | 9.2996 | 53.5907 | 3.3726 | 109 | 45.4174 | 0 | 277.3869 | 0
9099 | 797.974 | 2.5557 | 25.0375 | 92.6228 | 83.951 | 5.6997 | 69.3787 | 14.2964 | 6.3457 | 33.9648 | 83.2809 | 8.2766 | 182.0179 | 87.0546 | 246.8677 | 9.3843 | 53.5046 | 2.8511 | 114 | 41.1753 | 0 | 273.0361 | 0
9100 | 794.8233 | 2.7014 | 24.8879 | 92.5595 | 83.9497 | 5.7 | 70.0344 | 12.6886 | 6.3472 | 33.7386 | 83.8958 | 7.7995 | 179.4652 | 86.4256 | 249.5292 | 9.3999 | 53.8322 | 2.7383 | 113 | 41.3444 | 0 | 273.8724 | 0
9101 | 789.5785 | 3.2725 | 24.9126 | 92.6613 | 84.9449 | 4.7503 | 76.2117 | 9.8914 | 6.3177 | 34.5624 | 84.0638 | 7.746 | 179.3362 | 85.8739 | 245.4029 | 9.1666 | 54.5731 | 2.7149 | 113 | 41.5112 | 0 | 273.3667 | 0
9102 | 795.0166 | 4.1416 | 25.1291 | 92.7861 | 83.948 | 5.6997 | 71.5113 | 12.5384 | 6.5328 | 36.1784 | 84.3873 | 7.6077 | 178.1005 | 85.4703 | 234.5337 | 9.4049 | 56.2541 | 2.7377 | 114 | 39.6544 | 0 | 280.1558 | 0
9103 | 804.7007 | 4.5249 | 45.3891 | 93.2563 | 84.9481 | 4.7503 | 68.1664 | 14.1423 | 6.6875 | 35.9028 | 85.3145 | 7.4643 | 180.3143 | 86.1566 | 227.8909 | 9.4415 | 53.6966 | 2.7029 | 107 | 41.3214 | 0 | 281.8444 | 0
9104 | 813.0223 | 4.9946 | 52.5354 | 92.3767 | 83.9473 | 5.6997 | 77.5103 | 14.2146 | 14.2278 | 43.6229 | 91.2479 | 19.2135 | 204.8776 | 92.3004 | 231.739 | 9.2639 | 52.6073 | 2.9034 | 104 | 57.4088 | 0 | 278.8642 | 0
9105 | 821.1358 | 4.1134 | 58.1758 | 90.7891 | 82.939 | 6.6497 | 83.1994 | 13.8542 | 18.8483 | 60.7274 | 103.7779 | 28.2138 | 220.2641 | 107.7167 | 235.3262 | 9.0218 | 52.2512 | 3.3505 | 106 | 70.9394 | 0 | 276.884 | 0
9106 | 833.8042 | 4.0915 | 71.4562 | 89.7938 | 80.9426 | 8.5495 | 80.1918 | 14.9991 | 21.5407 | 72.1739 | 121.8369 | 27.5597 | 225.6741 | 110.6716 | 241.4808 | 8.9186 | 51.3362 | 5.3076 | 119 | 69.4935 | 0 | 270.158 | 0.008953
9107 | 855.3129 | 3.4329 | 79.3905 | 90.5512 | 84.9432 | 4.7511 | 84.4253 | 15.2759 | 22.7568 | 73.8666 | 137.7548 | 25.6649 | 240.856 | 115.381 | 265.8036 | 8.9403 | 53.2898 | 10.6349 | 149 | 66.4993 | 0 | 269.5234 | 0.04789
9108 | 862.6895 | 3.2264 | 81.2458 | 89.9679 | 83.945 | 5.6997 | 87.5973 | 8.9007 | 22.4003 | 70.8963 | 129.8858 | 24.6716 | 252.3097 | 120.0617 | 282.9831 | 8.8016 | 57.1893 | 12.6989 | 224 | 66.0168 | 0 | 277.7561 | 0.024516
9109 | 862.7266 | 3.0876 | 82.2947 | 88.3107 | 84.9425 | 4.7503 | 81.1188 | 10.987 | 20.3983 | 70.2548 | 124.5052 | 26.839 | 260.3143 | 125.2301 | 274.1108 | 8.8525 | 57.7016 | 13.4671 | 201 | 67.0541 | 0 | 275.0226 | 0.017883
9110 | 866.4844 | 3.2107 | 81.3929 | 87.6021 | 83.9381 | 5.7013 | 79.5281 | 13.4656 | 21.0517 | 70.9491 | 126.1204 | 28.155 | 263.93 | 130.9495 | 271.8711 | 8.8332 | 54.7303 | 14.1122 | 214 | 71.327 | 0 | 297.2325 | 0.013286
9111 | 866.0427 | 3.3875 | 80.4493 | 87.9286 | 84.9439 | 4.7487 | 90.4654 | 9.4371 | 21.1528 | 68.4744 | 128.5472 | 28.0518 | 255.4146 | 130.0651 | 279.4302 | 8.7382 | 54.1462 | 12.3828 | 224 | 72.5264 | 0 | 286.1086 | 0.0074922
9112 | 869.3311 | 3.7414 | 73.6948 | 89.3282 | 82.9406 | 6.6495 | 86.5273 | 10.4357 | 19.5774 | 66.9393 | 127.5982 | 26.7252 | 247.0946 | 117.7856 | 269.6981 | 8.773 | 53.3443 | 7.6891 | 220 | 72.7213 | 0 | 287.0526 | 0.00090027
9113 | 876.7201 | 5.5121 | 37.8495 | 95.2234 | 82.9384 | 6.65 | 79.6089 | 13.049 | 20.1221 | 63.8893 | 129.72 | 25.2778 | 255.1546 | 123.2372 | 263.7338 | 9.2618 | 55.5814 | 5.9727 | 191 | 73.3449 | 0 | 288.9975 | 0
9114 | 856.7537 | 9.3597 | 24.8456 | 98.416 | 83.9341 | 5.7003 | 80.1403 | 13.9094 | 20.3616 | 61.3259 | 123.0063 | 17.8252 | 254.6976 | 117.9538 | 273.2489 | 9.1023 | 54.7553 | 6.2042 | 196 | 72.3606 | 0 | 287.4416 | 0
9115 | 829.8996 | 11.3615 | 24.5156 | 98.4139 | 84.9358 | 4.7503 | 75.547 | 13.8754 | 15.4612 | 46.1625 | 96.5952 | 14.2634 | 232.4874 | 120.4399 | 272.5031 | 9.2623 | 53.5112 | 6.1544 | 209 | 60.8553 | 0 | 303.1799 | 0
9116 | 810.4179 | 11.5827 | 24.6628 | 98.0614 | 83.942 | 5.6997 | 71.8281 | 13.9285 | 9.7187 | 40.6564 | 86.3127 | 11.2608 | 219.2872 | 112.2848 | 259.563 | 9.0552 | 53.9763 | 5.9878 | 206 | 52.2113 | 0 | 296.2625 | 0
9117 | 814.7685 | 11.341 | 24.7151 | 98.9315 | 83.9443 | 5.7 | 74.416 | 13.9808 | 8.146 | 42.0844 | 85.7354 | 10.829 | 206.711 | 104.2903 | 257.706 | 9.4257 | 54.247 | 5.5149 | 194 | 46.5099 | 0 | 296.9194 | 0
9118 | 815.8363 | 11.0627 | 24.7422 | 98.0315 | 83.944 | 5.7 | 72.7864 | 14.0527 | 7.4774 | 41.4396 | 86.4108 | 13.3953 | 198.3675 | 98.9344 | 269.9084 | 9.2671 | 52.8048 | 5.0388 | 192 | 47.3021 | 0 | 298.7273 | 0
9119 | 799.5016 | 8.2015 | 24.9726 | 97.4202 | 83.9459 | 5.7 | 68.4203 | 14.3938 | 7.5082 | 42.3681 | 87.3452 | 12.2347 | 193.6152 | 96.6932 | 263.4454 | 9.4446 | 52.0855 | 4.8435 | 182 | 46.2236 | 0 | 296.5588 | 0
9120 | 799.4676 | 4.8834 | 25.0491 | 95.8925 | 83.9485 | 5.7 | 71.6715 | 14.2746 | 7.3648 | 40.403 | 85.8563 | 9.3608 | 195.1976 | 102.3874 | 258.2096 | 9.1696 | 52.0736 | 4.6168 | 143 | 49.2236 | 0 | 295.3225 | 0
9121 | 810.5409 | 3.3434 | 24.7751 | 94.8941 | 83.9475 | 5.7 | 72.1748 | 14.2114 | 11.7463 | 38.8151 | 84.3494 | 8.0268 | 194.1409 | 96.6888 | 257.7265 | 9.0951 | 51.9976 | 4.4202 | 146 | 51.7404 | 0 | 293.375 | 0
9122 | 801.5577 | 3.0861 | 24.7869 | 94.1887 | 84.9469 | 4.7503 | 68.1353 | 14.1978 | 8.7398 | 39.2916 | 84.0838 | 7.7985 | 191.8351 | 100.0594 | 257.4897 | 9.2131 | 51.8266 | 4.1166 | 144 | 51.7083 | 0 | 308.7785 | 0
9123 | 790.2166 | 3.2749 | 25.0795 | 90.9511 | 77.9477 | 11.3982 | 69.6189 | 14.1759 | 6.592 | 37.9541 | 84.2932 | 8.045 | 185.2556 | 98.6446 | 265.1162 | 9.3933 | 51.7235 | 3.8045 | 133 | 51.2846 | 0 | 307.2408 | 0
9124 | 779.6894 | 3.3473 | 25.2079 | 91.1033 | 79.9444 | 9.5005 | 71.3085 | 14.1626 | 6.7451 | 35.8885 | 85.4134 | 8.9436 | 183.9539 | 92.3561 | 277.7205 | 9.2129 | 51.7924 | 3.8552 | 138 | 52.0866 | 0 | 296.8327 | 0
9125 | 778.3787 | 3.5585 | 25.203 | 91.1733 | 79.9481 | 9.5 | 66.9769 | 14.4611 | 6.6667 | 36.7605 | 86.3072 | 8.5467 | 186.582 | 87.9944 | 272.3009 | 9.2107 | 53.3273 | 3.2088 | 128 | 55.3538 | 0 | 296.3273 | 0
9126 | 775.7622 | 4.3352 | 26.6315 | 90.6483 | 83.9485 | 5.7011 | 68.6169 | 14.3328 | 6.5255 | 37.8648 | 86.3084 | 7.8982 | 183.6195 | 88.2695 | 246.4617 | 9.1709 | 56.2656 | 2.5963 | 121 | 58.5221 | 0 | 298.3431 | 0
9127 | 778.1938 | 4.4928 | 56.3327 | 91.4243 | 83.943 | 5.7 | 70.8761 | 14.2043 | 6.6774 | 37.1318 | 87.6567 | 7.7944 | 181.5791 | 88.9094 | 235.6963 | 9.2001 | 53.3589 | 2.4556 | 113 | 50.9513 | 0 | 296.5748 | 0
9128 | 787.7884 | 4.487 | 65.8912 | 91.3587 | 83.946 | 5.7 | 69.0993 | 14.1527 | 6.8293 | 38.1191 | 89.869 | 7.9329 | 187.3663 | 96.2057 | 239.8492 | 9.1268 | 51.9405 | 2.7148 | 113 | 42.5149 | 0 | 297.5405 | 0
9129 | 786.9274 | 3.5053 | 65.6653 | 89.103 | 83.9475 | 5.7 | 69.0414 | 13.9878 | 6.7107 | 43.8959 | 89.3315 | 6.447 | 192.4919 | 94.738 | 240.6635 | 8.9169 | 51.1038 | 3.3301 | 114 | 42.5512 | 0 | 292.2192 | 0
9130 | 799.1948 | 2.6354 | 71.2022 | 87.5239 | 83.9438 | 5.7 | 75.149 | 13.6638 | 9.0078 | 59.1988 | 88.4584 | 5.1746 | 194.0801 | 90.8221 | 237.1159 | 8.6453 | 50.383 | 3.4714 | 131 | 40.0714 | 0 | 283.214 | 0.1449
9131 | 823.2678 | 2.483 | 78.0978 | 87.4661 | 82.939 | 6.6497 | 81.4892 | 13.7594 | 9.4097 | 67.3942 | 97.3533 | 4.9203 | 200.5395 | 98.6045 | 246.7248 | 8.4453 | 50.1033 | 3.4444 | 144 | 38.4492 | 0 | 294.8404 | 0.16889
9132 | 838.3235 | 2.5953 | 77.9636 | 87.8022 | 74.9434 | 14.2479 | 91.7817 | 13.6524 | 10.2893 | 68.791 | 107.189 | 4.9231 | 207.8607 | 99.8109 | 270.179 | 8.8182 | 51.1074 | 3.5714 | 152 | 37.6916 | 0 | 304.0653 | 0.20718
9133 | 835.8882 | 2.8507 | 77.8062 | 88.5258 | 82.9416 | 6.6521 | 103.4164 | 13.6603 | 7.968 | 64.2096 | 120.8666 | 4.918 | 212.3215 | 104.8701 | 275.0411 | 8.7394 | 51.8476 | 3.5463 | 148 | 39.633 | 0 | 306.4614 | 0.22358
9134 | 861.4028 | 5.1823 | 77.7571 | 89.0409 | 83.9426 | 5.7003 | 89.5675 | 14.3863 | 5.891 | 64.77 | 128.2464 | 4.909 | 215.6921 | 110.5083 | 267.7218 | 8.6924 | 52.9314 | 3.8298 | 170 | 41.6101 | 0 | 299.1487 | 0.21564
9135 | 870.0505 | 4.4035 | 79.4723 | 90.5371 | 83.9359 | 5.7016 | 73.4354 | 14.054 | 6.9548 | 63.3288 | 132.5495 | 5.8536 | 218.4944 | 114.3066 | 267.2865 | 8.6217 | 53.1465 | 4.0928 | 163 | 44.451 | 0 | 304.023 | 0.15794
9136 | 872.6402 | 3.2537 | 74.3884 | 90.3184 | 84.941 | 4.7487 | 71.134 | 13.5806 | 7.2362 | 56.6027 | 134.1247 | 7.8333 | 216.36 | 111.552 | 266.9363 | 8.5684 | 52.682 | 4.1914 | 159 | 48.5434 | 0 | 306.088 | 0.03266
9137 | 875.0376 | 5.1571 | 39.6343 | 91.515 | 83.9407 | 5.7013 | 69.1433 | 14.0782 | 6.6183 | 45.8505 | 136.9101 | 7.848 | 224.4848 | 109.6556 | 273.3761 | 9.0091 | 54.603 | 4.3014 | 155 | 49.7902 | 0 | 316.1493 | 0
9138 | 873.7778 | 5.19 | 26.0834 | 92.3712 | 83.9427 | 5.7 | 67.0979 | 14.2213 | 6.5562 | 42.6871 | 139.2009 | 7.9542 | 227.9846 | 110.0794 | 274.911 | 9.0416 | 56.9505 | 4.7142 | 138 | 49.7474 | 0 | 332.9278 | 0
9139 | 879.4653 | 5.0992 | 25.3313 | 92.0699 | 83.9482 | 5.6984 | 69.9046 | 14.2403 | 8.029 | 40.4098 | 138.2197 | 8.4295 | 221.3086 | 112.2394 | 277.059 | 9.2603 | 57.8385 | 4.7713 | 131 | 47.9622 | 0 | 335.2843 | 0
9140 | 885.4679 | 5.895 | 25.5303 | 92.2851 | 83.9481 | 5.7 | 66.3584 | 14.2914 | 7.3 | 37.843 | 129.8354 | 8.3318 | 210.3254 | 117.1139 | 282.0454 | 9.1104 | 55.3342 | 4.7445 | 128 | 48.2218 | 0 | 316.945 | 0
9141 | 877.3613 | 9.5873 | 25.725 | 92.9352 | 83.9513 | 5.7 | 65.3368 | 14.3695 | 6.8089 | 38.3359 | 102.4611 | 8.4542 | 198.7261 | 108.6927 | 267.2594 | 9.1091 | 53.8424 | 4.4805 | 126 | 46.0544 | 0 | 308.7355 | 0
9142 | 868.8773 | 11.527 | 25.2732 | 92.0104 | 83.9491 | 5.7 | 68.5263 | 14.3157 | 6.6507 | 39.2667 | 89.886 | 8.2488 | 186.654 | 103.6431 | 255.9182 | 9.2064 | 52.6193 | 3.9828 | 116 | 45.9469 | 0 | 298.9614 | 0
9143 | 862.9011 | 11.0561 | 25.5916 | 91.2312 | 83.9453 | 5.7 | 65.4092 | 14.5349 | 6.2932 | 38.1367 | 87.75 | 8.1499 | 180.4929 | 97.798 | 252.5067 | 9.4017 | 52.624 | 4.1084 | 116 | 43.4944 | 0 | 318.0705 | 0
9144 | 848.0213 | 9.8338 | 25.8935 | 91.0956 | 83.9476 | 5.7 | 63.724 | 14.4209 | 6.2445 | 37.8527 | 85.9614 | 8.1377 | 179.8031 | 92.8868 | 243.662 | 9.1554 | 52.4365 | 4.2078 | 111 | 42.287 | 0 | 315.8139 | 0
9145 | 842.62 | 9.3231 | 25.8743 | 91.1716 | 83.9507 | 5.7 | 66.7451 | 14.3291 | 6.2342 | 37.4732 | 84.8238 | 7.9626 | 176.5403 | 88.2669 | 226.1234 | 9.301 | 52.1316 | 3.7717 | 106 | 42.9434 | 0 | 307.9375 | 0
9146 | 823.3731 | 7.713 | 25.8293 | 91.0329 | 83.9502 | 5.7 | 64.7778 | 14.3324 | 6.3174 | 38.222 | 84.8535 | 7.8965 | 176.3036 | 87.8535 | 218.8955 | 9.0823 | 52.6947 | 3.009 | 108 | 42.2213 | 0 | 303.6493 | 0
9147 | 809.1233 | 4.9998 | 26.0217 | 91.0351 | 83.949 | 5.7 | 62.3945 | 14.3234 | 6.2464 | 37.984 | 84.8117 | 7.7721 | 173.4038 | 92.8606 | 240.8105 | 9.3185 | 51.9459 | 2.7412 | 104 | 41.6008 | 0 | 309.4384 | 0
9148 | 791.2263 | 3.1672 | 26.5634 | 91.0413 | 83.9444 | 5.7 | 65.6707 | 14.524 | 6.0021 | 37.4549 | 84.4543 | 7.818 | 171.1522 | 96.3047 | 240.2014 | 9.1219 | 52.0057 | 2.7757 | 103 | 41.7659 | 0 | 314.2136 | 0
9149 | 790.05 | 3.1729 | 28.6337 | 92.625 | 83.9456 | 5.7 | 64.245 | 14.3725 | 6.3964 | 38.2193 | 84.9073 | 7.9836 | 174.7882 | 90.1683 | 223.5471 | 9.2951 | 53.6218 | 2.7681 | 100 | 41.46 | 0 | 350.5183 | 0
9150 | 802.2321 | 4.2091 | 35.442 | 92.2002 | 82.9483 | 6.6497 | 67.3191 | 14.1481 | 6.5212 | 38.1043 | 87.6551 | 9.5209 | 184.4719 | 94.8486 | 233.6463 | 9.2271 | 55.4171 | 2.8112 | 104 | 41.3213 | 0 | 376.7369 | 0
9151 | 841.9801 | 6.0373 | 51.7673 | 96.9763 | 80.9444 | 8.5495 | 88.011 | 14.0079 | 11.7575 | 57.3831 | 113.6355 | 18.6883 | 214.2576 | 165.1727 | 275.3842 | 11.4832 | 54.9008 | 6.0691 | 167 | 51.2476 | 0 | 416.8577 | 0
9152 | 893.1971 | 12.0159 | 78.4546 | 103.0295 | 77.097 | 12.3489 | 109.7668 | 15.134 | 19.1792 | 92.6882 | 157.2448 | 37.7782 | 272.4858 | 241.3895 | 345.2312 | 25.1392 | 59.5 | 8.8229 | 274 | 54.2497 | 0 | 479.8384 | 0
9153 | 985.8318 | 20.5081 | 97.171 | 109.5615 | 72.0261 | 17.0987 | 130.3873 | 17.1418 | 25.6617 | 103.012 | 181.0629 | 43.3512 | 312.4545 | 286.4576 | 443.6225 | 34.1745 | 71.2695 | 12.1115 | 316 | 59.273 | 0 | 525.4877 | 0
9154 | 1060.5875 | 21.9644 | 97.3806 | 117.8917 | 74.9322 | 14.2508 | 147.4814 | 18.2842 | 26.6518 | 101.3295 | 189.8619 | 41.5831 | 350.5678 | 325.1154 | 530.9748 | 40.9391 | 88.6824 | 15.3161 | 365 | 62.1823 | 0 | 557.321 | 0.08618
9155 | 1150.9117 | 14.7132 | 95.3905 | 121.1723 | 73.9361 | 15.1997 | 150.4151 | 18.8561 | 27.8408 | 96.6266 | 192.4318 | 41.8748 | 373.181 | 348.3477 | 568.77 | 41.9222 | 100.1993 | 15.2903 | 395 | 64.3264 | 0 | 590.7989 | 0.11812
9156 | 1207.6022 | 10.3946 | 99.0632 | 121.7302 | 72.9392 | 16.1497 | 154.2101 | 18.9318 | 24.5021 | 101.6693 | 192.1894 | 42.4193 | 394.8443 | 353.6772 | 581.6095 | 40.7595 | 101.8098 | 16.0257 | 385 | 67.0103 | 0 | 602.0069 | 0.12554
9157 | 1190.2299 | 10.598 | 98.4347 | 125.2709 | 73.9406 | 15.2045 | 162.2757 | 18.9753 | 18.2334 | 104.6608 | 190.0786 | 40.9621 | 399.5073 | 345.4046 | 564.9002 | 40.9102 | 97.0773 | 17.3452 | 393 | 58.8681 | 0 | 590.0864 | 0.18111
9158 | 1203.8394 | 13.7162 | 98.2869 | 126.4386 | 71.9517 | 17.0953 | 157.5469 | 18.0932 | 26.6182 | 96.74 | 189.2945 | 41.4313 | 393.5739 | 348.275 | 543.1018 | 40.9067 | 96.4924 | 18.1762 | 280 | 59.0985 | 0 | 607.2331 | 0.20807
9159 | 1201.2678 | 13.1487 | 98.0733 | 128.376 | 75.9386 | 13.3011 | 161.5932 | 17.5818 | 29.1092 | 95.528 | 194.5798 | 40.9171 | 391.5594 | 348.8418 | 538.3275 | 41.5764 | 98.3111 | 17.886 | 258 | 60.5532 | 0 | 596.9805 | 0.15307
9160 | 1171.9714 | 7.9095 | 99.8237 | 127.1655 | 72.9411 | 16.1492 | 154.3615 | 17.0436 | 21.1972 | 94.5182 | 198.4019 | 34.9788 | 383.2713 | 342.0205 | 531.433 | 40.9608 | 98.786 | 17.344 | 286 | 61.5999 | 0 | 576.2129 | 0.020958
9161 | 1123.828 | 6.617 | 96.3667 | 124.083 | 76.9434 | 12.3511 | 137.6203 | 17.8036 | 16.848 | 90.4144 | 199.7492 | 34.5092 | 365.1734 | 319.7019 | 510.3103 | 33.6469 | 98.3105 | 17.2723 | 249 | 60.529 | 0 | 539.3112 | 0
9162 | 1053.4819 | 7.1337 | 89.8625 | 115.5066 | 76.9381 | 12.3534 | 126.1595 | 16.5751 | 16.485 | 75.3423 | 181.2349 | 32.8064 | 328.4784 | 267.8619 | 428.8143 | 17.8443 | 92.0305 | 16.2832 | 218 | 59.6614 | 0 | 409.7715 | 0
9163 | 983.5471 | 6.6218 | 75.7322 | 104.3582 | 82.9416 | 6.6516 | 110.3854 | 14.8024 | 13.4955 | 54.0647 | 152.0857 | 26.2079 | 286.379 | 190.9873 | 368.2742 | 11.1621 | 82.3059 | 15.279 | 206 | 56.0279 | 0 | 379.2311 | 0
9164 | 932.8833 | 5.9369 | 65.0932 | 98.7337 | 83.9512 | 5.7003 | 88.8381 | 14.3339 | 8.5462 | 49.0596 | 138.9645 | 12.6112 | 260.832 | 157.0414 | 317.0674 | 10.4274 | 70.6496 | 9.974 | 189 | 51.1877 | 0 | 329.7747 | 0
9165 | 911.0151 | 5.6706 | 51.2516 | 93.8532 | 83.946 | 5.7 | 78.0552 | 14.381 | 7.0127 | 49.9504 | 130.774 | 8.1744 | 246.4743 | 131.2399 | 274.3847 | 10.0747 | 58.5063 | 6.1831 | 170 | 50.1735 | 0 | 304.3432 | 0
9166 | 870.3167 | 5.4432 | 47.7184 | 91.5389 | 83.9426 | 5.7 | 72.6435 | 14.1832 | 6.4883 | 42.5894 | 114.2475 | 7.8565 | 219.9953 | 118.0374 | 260.0176 | 10.0566 | 53.9333 | 5.0774 | 161 | 45.7693 | 0 | 293.3146 | 0
9167 | 861.4104 | 4.3604 | 47.5146 | 91.178 | 83.9424 | 5.7 | 75.1517 | 14.154 | 6.3115 | 39.0855 | 97.3517 | 7.6618 | 201.91 | 106.4941 | 251.7244 | 10.178 | 53.5301 | 4.2451 | 140 | 42.5266 | 0 | 289.5911 | 0
9168 | 846.9917 | 3.1434 | 47.4512 | 91.3146 | 83.9486 | 5.7 | 74.858 | 14.2339 | 6.2125 | 38.3014 | 90.8943 | 7.7154 | 195.9327 | 98.2993 | 240.1128 | 10.2354 | 53.9795 | 3.6734 | 124 | 42.6107 | 0 | 289.0377 | 0
9169 | 834.5535 | 3.7572 | 46.8118 | 91.6492 | 83.9487 | 5.7 | 70.9442 | 14.48 | 6.1055 | 39.0335 | 89.1228 | 7.7131 | 198.0278 | 93.0065 | 232.5554 | 10.0009 | 54.0364 | 3.0125 | 111 | 42.0959 | 0 | 293.6615 | 0
9170 | 824.0358 | 3.2993 | 48.2398 | 91.1858 | 84.9466 | 4.7503 | 73.3107 | 14.3372 | 6.295 | 40.1757 | 94.4623 | 7.6698 | 202.5662 | 92.5718 | 235.1072 | 10.081 | 53.9421 | 2.7151 | 109 | 42.9984 | 0 | 288.3726 | 0
9171 | 805.2847 | 2.5763 | 48.4301 | 91.0156 | 83.9469 | 5.7013 | 73.0031 | 14.2443 | 6.3657 | 40.3767 | 97.1896 | 8.3784 | 200.6085 | 90.9245 | 239.9787 | 10.0172 | 53.418 | 2.9171 | 117 | 42.4903 | 0 | 289.2207 | 0
9172 | 817.0422 | 2.5751 | 48.2794 | 91.241 | 83.951 | 5.6984 | 70.319 | 14.2294 | 6.3457 | 41.7984 | 95.7576 | 7.9204 | 196.1412 | 88.062 | 241.4583 | 10.0833 | 53.6728 | 3.0385 | 106 | 42.4665 | 0 | 294.8127 | 0
9173 | 817.9679 | 3.016 | 48.3358 | 92.5817 | 83.9454 | 5.7 | 74.4091 | 14.188 | 6.383 | 42.6091 | 93.7648 | 7.5844 | 200.2359 | 86.6329 | 239.2878 | 10.0312 | 55.269 | 2.7889 | 107 | 43.9725 | 0 | 319.9657 | 0
9174 | 824.0211 | 4.0605 | 50.0777 | 93.1175 | 83.946 | 5.7 | 79.5351 | 14.4022 | 6.7798 | 42.3264 | 92.5125 | 8.8502 | 211.6755 | 95.7476 | 247.7317 | 10.1386 | 57.1833 | 2.6776 | 105 | 42.7249 | 0 | 370.9049 | 0
9175 | 859.7972 | 5.9932 | 52.4493 | 98.4948 | 82.9426 | 6.6497 | 91.6451 | 14.1031 | 11.0508 | 63.1419 | 104.524 | 16.7262 | 241.6501 | 162.5097 | 255.7223 | 12.5427 | 56.9793 | 2.7132 | 187 | 49.5863 | 0 | 414.9083 | 0
9176 | 908.0267 | 10.6347 | 76.5323 | 103.4822 | 75.9378 | 13.2982 | 113.116 | 14.5252 | 17.832 | 92.8729 | 145.0801 | 34.9496 | 280.2316 | 237.9584 | 331.135 | 27.6015 | 63.3373 | 8.135 | 264 | 53.4192 | 0 | 452.866 | 0
9177 | 995.3228 | 15.2962 | 92.4018 | 110.1564 | 74.9324 | 14.2537 | 131.1449 | 16.2694 | 26.2887 | 105.7473 | 183.5593 | 39.7419 | 332.9386 | 294.5862 | 440.5366 | 36.552 | 69.6117 | 16.0392 | 317 | 57.3675 | 0 | 516.3501 | 0
9178 | 1083.5574 | 13.8144 | 98.3129 | 119.5164 | 73.9373 | 15.1958 | 141.9238 | 17.0139 | 28.63 | 107.8931 | 199.0939 | 39.1378 | 397.8257 | 317.3692 | 547.6243 | 40.8937 | 76.495 | 17.4212 | 380 | 62.6008 | 0 | 576.8974 | 0.016142
9179 | 1143.0867 | 9.6958 | 98.5852 | 125.035 | 70.9341 | 18.0492 | 154.9783 | 17.1595 | 24.0724 | 102.8863 | 198.1112 | 42.7553 | 422.2772 | 327.3527 | 611.9323 | 42.5242 | 89.5349 | 16.5777 | 369 | 67.5145 | 0 | 610.2325 | 0.028675
9180 | 1197.2348 | 10.8941 | 101.0958 | 128.533 | 73.9315 | 15.205 | 154.6594 | 16.4521 | 21.1432 | 103.0465 | 179.7506 | 42.9723 | 431.6229 | 350.2382 | 628.9688 | 42.7976 | 93.2721 | 16.333 | 381 | 77.6376 | 0 | 625.2052 | 0.02694
9181 | 1179.2009 | 12.0642 | 100.7571 | 133.1101 | 74.9359 | 14.246 | 151.8029 | 16.8775 | 18.4125 | 96.4691 | 183.3828 | 43.991 | 426.3159 | 359.511 | 624.6451 | 43.9965 | 90.5469 | 17.6546 | 377 | 71.9041 | 0 | 619.2669 | 0.02607
9182 | 1182.2325 | 8.6863 | 101.5444 | 141.8259 | 71.9336 | 17.0992 | 160.3098 | 18.0588 | 21.6408 | 93.8068 | 192.3941 | 45.7365 | 442.8905 | 361.1114 | 621.6885 | 44.7335 | 94.5131 | 18.8851 | 324 | 73.1707 | 0 | 627.5222 | 0.015941
9183 | 1177.7602 | 5.4054 | 100.9383 | 151.7539 | 73.934 | 15.2005 | 156.9698 | 17.4536 | 21.5787 | 94.8382 | 195.6627 | 43.4874 | 447.35 | 362.0001 | 604.8662 | 44.6409 | 98.4983 | 18.3786 | 291 | 73.7733 | 0 | 608.6122 | 0.0078036
9184 | 1145.3658 | 5.6678 | 98.7704 | 142.8418 | 74.9325 | 14.2503 | 155.7715 | 16.3013 | 22.3218 | 99.4844 | 192.8566 | 41.6526 | 437.0412 | 349.7368 | 573.7506 | 43.5504 | 100.2163 | 18.0736 | 306 | 70.4004 | 0 | 616.7375 | 0.0010274
9185 | 1094.6365 | 6.7165 | 95.1649 | 135.3433 | 76.9351 | 12.3505 | 149.0776 | 16.738 | 22.4572 | 104.7238 | 194.5121 | 36.9269 | 414.5484 | 321.9851 | 521.5562 | 36.734 | 99.016 | 18.4208 | 263 | 63.827 | 0 | 563.2304 | 0
9186 | 1037.7716 | 6.7841 | 91.3488 | 123.2468 | 82.94 | 6.6516 | 123.8084 | 15.3254 | 19.4735 | 94.2089 | 183.4775 | 32.5424 | 363.4767 | 261.3898 | 427.3606 | 20.0081 | 92.1082 | 18.081 | 212 | 57.6031 | 0 | 433.6584 | 0
9187 | 999.2284 | 6.2423 | 85.415 | 111.2934 | 82.9449 | 6.65 | 108.939 | 14.285 | 15.9807 | 71.0497 | 153.4094 | 23.6989 | 312.6651 | 191.7098 | 375.931 | 12.8626 | 82.0932 | 16.9713 | 191 | 56.0894 | 0 | 395.1885 | 0
9188 | 944.1296 | 5.603 | 70.7827 | 104.2968 | 83.9429 | 5.7003 | 87.9856 | 13.989 | 10.3602 | 54.5889 | 135.9872 | 11.4832 | 274.4885 | 155.0767 | 333.087 | 11.7886 | 65.826 | 10.4022 | 163 | 54.2738 | 0 | 343.5885 | 0
9189 | 902.5059 | 5.6995 | 39.1283 | 99.1434 | 83.9368 | 5.7016 | 73.0801 | 14.0666 | 7.7826 | 47.4702 | 126.9412 | 7.3833 | 249.617 | 136.269 | 302.2103 | 11.7157 | 59.6744 | 5.6799 | 154 | 53.2752 | 0 | 306.6401 | 0
9190 | 872.6114 | 5.0393 | 29.1733 | 94.0967 | 83.9449 | 5.6984 | 72.792 | 14.1067 | 7.5545 | 40.816 | 111.611 | 7.1473 | 219.3888 | 123.5844 | 272.759 | 11.6995 | 58.5491 | 4.242 | 148 | 47.7229 | 0 | 301.076 | 0
9191 | 839.0362 | 4.6069 | 29.0714 | 91.6714 | 81.9439 | 7.5995 | 76.842 | 9.0147 | 7.2926 | 33.9795 | 93.5134 | 7.1098 | 202.1468 | 114.7885 | 254.5474 | 11.4545 | 57.5699 | 4.1528 | 139 | 48.0572 | 0 | 295.8188 | 0
9192 | 835.8699 | 3.5056 | 29.0788 | 91.3137 | 84.9417 | 4.7508 | 69.7891 | 12.1524 | 7.0856 | 30.3127 | 85.1907 | 7.1143 | 195.5869 | 110.9728 | 247.3966 | 11.663 | 57.6234 | 3.9249 | 121 | 46.8128 | 0 | 294.78 | 0
9193 | 838.1452 | 3.2458 | 28.8616 | 90.8959 | 83.9465 | 5.6997 | 66.3945 | 14.2323 | 7.1629 | 28.9428 | 84.9605 | 7.0902 | 193.3738 | 108.3018 | 246.7092 | 11.5707 | 57.2948 | 3.4363 | 117 | 44.0804 | 0 | 292.4897 | 0
9194 | 823.2065 | 4.1535 | 29.0257 | 90.9034 | 84.946 | 4.7516 | 76.1339 | 11.5691 | 6.9234 | 28.9722 | 85.5282 | 7.2215 | 193.7234 | 107.9603 | 249.4399 | 11.6439 | 57.2349 | 3.1191 | 108 | 43.8835 | 0 | 297.204 | 0
9195 | 806.7534 | 3.1078 | 28.9936 | 90.937 | 83.9469 | 5.6984 | 75.6038 | 10.5668 | 6.8673 | 29.2531 | 85.343 | 7.5171 | 191.1561 | 105.0157 | 250.0081 | 11.5843 | 57.4366 | 3.0961 | 104 | 44.6632 | 0 | 293.5096 | 0
9196 | 820.7263 | 2.4256 | 28.9837 | 90.7284 | 83.9467 | 5.7 | 67.3462 | 13.1246 | 6.933 | 29.062 | 84.984 | 7.2576 | 188.1569 | 103.8702 | 238.9467 | 11.4202 | 57.1257 | 2.921 | 102 | 43.7917 | 0 | 294.7797 | 0
9197 | 825.6781 | 2.9805 | 29.1193 | 90.7369 | 84.9484 | 4.7503 | 71.1098 | 14.087 | 6.8998 | 29.12 | 85.575 | 7.0992 | 190.8859 | 103.9631 | 230.1952 | 11.6852 | 58.278 | 2.9004 | 98 | 44.2451 | 0 | 316.2826 | 0
9198 | 837.9211 | 3.9712 | 40.1521 | 92.9622 | 83.9449 | 5.6997 | 84.1801 | 8.7921 | 7.0952 | 29.5637 | 88.0643 | 10.728 | 201.9606 | 113.6365 | 234.6506 | 11.7817 | 60.5038 | 2.9178 | 113 | 44.9739 | 0 | 365.185 | 0
9199 | 881.5741 | 6.015 | 52.3052 | 98.7208 | 82.9406 | 6.6497 | 89.8746 | 11.5684 | 12.4833 | 55.1924 | 104.3365 | 19.565 | 239.7806 | 174.323 | 253.6642 | 14.1225 | 57.8168 | 2.6376 | 159 | 50.8096 | 0 | 407.3196 | 0
9200 | 923.8637 | 16.9213 | 76.5657 | 100.2691 | 77.9382 | 11.3987 | 107.427 | 15.7541 | 19.2731 | 93.7822 | 150.2361 | 33.6529 | 285.9275 | 239.5414 | 328.842 | 30.9272 | 65.0074 | 8.1453 | 261 | 52.1881 | 0 | 437.625 | 0
9201 | 1002.2259 | 23.6109 | 88.4081 | 115.3254 | 75.9383 | 13.2995 | 138.2354 | 12.5517 | 23.616 | 99.9595 | 176.3027 | 37.7931 | 338.9256 | 298.1208 | 442.8308 | 41.4023 | 73.5154 | 15.5286 | 307 | 59.5 | 0 | 518.9615 | 0
9202 | 1098.9971 | 19.8702 | 96.0996 | 128.155 | 73.9403 | 15.1995 | 150.137 | 12.65 | 25.0546 | 105.0329 | 178.7697 | 38.4757 | 392.0227 | 336.9487 | 540.1902 | 44.072 | 81.52 | 16.947 | 349 | 62.003 | 0 | 570.8523 | 0.0062483
9203 | 1184.9414 | 18.0061 | 98.2803 | 130.3335 | 73.9331 | 15.2 | 143.6165 | 15.7065 | 27.8452 | 107.0523 | 180.2565 | 41.4 | 422.2002 | 350.9465 | 594.0006 | 45.6753 | 95.2938 | 17.7588 | 357 | 69.1149 | 0 | 594.3237 | 0.033593
9204 | 1196.5255 | 17.5795 | 102.075 | 131.0329 | 72.9318 | 16.1497 | 152.6165 | 13.3578 | 25.6842 | 112.5771 | 182.357 | 42.903 | 433.4031 | 365.9387 | 599.4505 | 43.6144 | 103.3849 | 18.6886 | 346 | 77.9914 | 0 | 593.2098 | 0.04436
9205 | 1149.9364 | 15.097 | 98.518 | 130.7002 | 72.9343 | 16.15 | 159.9331 | 15.0453 | 19.3705 | 104.8349 | 189.2136 | 42.4658 | 423.2533 | 368.2474 | 598.0128 | 43.436 | 100.7359 | 19.0468 | 336 | 75.4146 | 0 | 585.5332 | 0.046589
9206 | 1172.4777 | 12.0744 | 101.2959 | 132.6216 | 72.9291 | 16.1545 | 153.7867 | 16.8617 | 19.4612 | 99.6918 | 191.9508 | 43.2037 | 432.5272 | 369.1384 | 594.1976 | 45.4996 | 102.2696 | 18.8742 | 318 | 75.8136 | 0 | 628.5544 | 0.045266
9207 | 1179.2051 | 9.6633 | 106.2386 | 138.2359 | 74.9393 | 14.246 | 161.9505 | 10.8976 | 18.9112 | 97.6305 | 192.2848 | 41.93 | 425.1507 | 370.312 | 605.1835 | 45.1181 | 103.9472 | 18.8032 | 264 | 75.1196 | 0 | 604.292 | 0.011871
9208 | 1140.5285 | 8.5584 | 100.5474 | 136.8111 | 74.9326 | 14.25 | 159.9591 | 13.497 | 19.1583 | 92.5098 | 187.6905 | 40.8685 | 414.9489 | 358.9868 | 588.8499 | 42.4665 | 101.8795 | 18.6248 | 272 | 73.2867 | 0 | 601.5833 | 0.0031798
9209 | 1103.4681 | 7.3922 | 92.2735 | 133.409 | 80.9285 | 8.5516 | 142.0151 | 11.7121 | 18.917 | 89.632 | 185.1454 | 38.2758 | 391.8852 | 333.4633 | 516.0514 | 35.9643 | 98.6641 | 18.56 | 283 | 62.3929 | 0 | 552.0396 | 0
9210 | 1033.0235 | 6.8141 | 84.7952 | 118.3464 | 81.9327 | 7.6003 | 134.7776 | 13.1304 | 18.9285 | 76.089 | 168.7436 | 34.3213 | 352.5083 | 262.1579 | 426.5505 | 21.6308 | 89.1664 | 17.1387 | 236 | 55.7079 | 0 | 434.3406 | 0
9211 | 989.0841 | 5.9586 | 84.9111 | 102.0153 | 82.9356 | 6.6503 | 123.5145 | 11.7778 | 16.0622 | 52.1977 | 143.3535 | 29.1937 | 302.4908 | 205.662 | 367.9854 | 13.622 | 80.1793 | 16.1774 | 205 | 51.0192 | 0 | 387.0936 | 0
9212 | 937.2559 | 5.2426 | 69.6353 | 97.957 | 81.9409 | 7.5997 | 107.5148 | 10.4655 | 10.7333 | 46.4489 | 134.1278 | 17.9482 | 264.1273 | 180.2389 | 341.4934 | 12.4994 | 67.2642 | 10.43 | 175 | 45.6288 | 0 | 322.0113 | 0
9213 | 911.477 | 4.7489 | 35.2912 | 97.7246 | 83.9394 | 5.7021 | 88.4718 | 10.4894 | 8.3805 | 46.4388 | 125.7999 | 14.4426 | 239.3489 | 136.1707 | 309.4198 | 12.0489 | 57.6376 | 6.2275 | 164 | 42.8266 | 0 | 297.111 | 0
9214 | 884.6986 | 4.74 | 25.3736 | 95.5677 | 84.9427 | 4.7487 | 81.1751 | 9.4461 | 7.7488 | 42.1828 | 107.383 | 11.0392 | 218.6289 | 111.7111 | 274.624 | 11.7318 | 56.0887 | 4.7985 | 160 | 35.3083 | 0 | 301.8218 | 0
9215 | 844.0639 | 4.0723 | 25.392 | 92.7222 | 84.9456 | 4.75 | 84.5696 | 11.0103 | 7.3018 | 34.4594 | 97.329 | 9.4347 | 203.3925 | 100.1306 | 258.2087 | 11.6079 | 55.2463 | 3.7999 | 144 | 33.3227 | 0 | 287.2771 | 0
9216 | 830.0272 | 3.0069 | 25.4137 | 91.9456 | 81.9471 | 7.5992 | 86.2876 | 8.8524 | 6.8348 | 31.3404 | 105.0618 | 9.3119 | 193.4447 | 96.7234 | 250.6575 | 11.358 | 54.548 | 3.4273 | 124 | 32.1667 | 0 | 287.6388 | 0
9217 | 829.0423 | 2.6636 | 25.3362 | 92.6051 | 83.9464 | 5.7005 | 77.2508 | 11.4406 | 6.9 | 31.1486 | 96.0452 | 9.2965 | 187.8376 | 92.1329 | 241.0104 | 11.5338 | 54.1452 | 3.2074 | 118 | 32.2117 | 0 | 282.8506 | 0
9218 | 812.5393 | 2.7349 | 25.0913 | 91.8703 | 84.948 | 4.7503 | 78.2049 | 8.5976 | 6.946 | 31.0278 | 84.0568 | 9.254 | 187.3578 | 88.4034 | 231.9115 | 11.5297 | 53.7162 | 3.1318 | 105 | 31.0552 | 0 | 281.0406 | 0
9219 | 807.1521 | 2.6854 | 25.2669 | 92.0222 | 84.948 | 4.75 | 82.7608 | 11.7534 | 6.7795 | 30.9348 | 81.4162 | 9.6131 | 187.2125 | 86.0182 | 230.5767 | 11.493 | 53.6772 | 3.108 | 103 | 31.0126 | 0 | 279.1865 | 0
9220 | 809.698 | 2.4907 | 25.2086 | 91.9452 | 83.9506 | 5.6997 | 83.5856 | 8.0945 | 6.7773 | 31.1077 | 81.4122 | 9.3834 | 186.6502 | 85.6412 | 228.4948 | 11.4789 | 53.8384 | 3.0817 | 102 | 32.614 | 0 | 279.7172 | 0
9221 | 810.2841 | 2.8804 | 25.2883 | 92.4824 | 84.9521 | 4.7503 | 75.0962 | 11.4216 | 7.0078 | 31.0767 | 81.597 | 9.1824 | 191.1044 | 85.2878 | 221.0647 | 11.2372 | 55.0371 | 3.0862 | 103 | 31.2919 | 0 | 299.3802 | 0
9222 | 813.6208 | 3.897 | 34.167 | 92.4282 | 83.9445 | 5.6997 | 81.7826 | 7.9055 | 7.5415 | 32.1044 | 83.3386 | 10.3675 | 202.9302 | 97.0388 | 225.1945 | 11.0437 | 56.6791 | 3.125 | 107 | 31.1047 | 0 | 341.4812 | 0
9223 | 854.0944 | 5.3006 | 50.5397 | 98.2802 | 81.9411 | 7.5995 | 100.8482 | 11.4293 | 8.7592 | 49.1782 | 94.6483 | 20.2184 | 239.5247 | 165.8962 | 248.3029 | 12.8057 | 53.508 | 4.2246 | 174 | 43.7696 | 0 | 377.4569 | 0
9224 | 931.9145 | 10.0952 | 78.5292 | 103.8893 | 74.9435 | 14.2482 | 121.1808 | 10.1356 | 10.7108 | 95.828 | 137.2351 | 38.5909 | 283.9019 | 251.088 | 343.0014 | 26.9792 | 60.4656 | 8.0946 | 265 | 50.8501 | 0 | 422.7453 | 0
9225 | 1022.9023 | 14.1439 | 96.0413 | 114.35 | 75.9356 | 13.3003 | 139.1557 | 14.001 | 14.717 | 110.4233 | 164.0743 | 43.1148 | 335.218 | 306.7096 | 454.9942 | 35.6383 | 70.3713 | 13.0099 | 293 | 56.6472 | 0 | 511.0303 | 0
9226 | 1096.7709 | 14.345 | 105.0311 | 128.2614 | 73.936 | 15.1995 | 151.0447 | 12.4581 | 20.9978 | 106.3618 | 172.3041 | 41.8241 | 385.9339 | 335.3768 | 539.6039 | 40.7984 | 80.709 | 15.6059 | 339 | 65.124 | 0 | 589.1489 | 0.023086
9227 | 1168.4143 | 9.9568 | 102.081 | 133.0035 | 73.934 | 15.2 | 149.1732 | 14.0898 | 27.8377 | 100.6216 | 186.5012 | 42.8586 | 408.4627 | 349.1145 | 581.81 | 42.601 | 91.8637 | 17.2134 | 357 | 66.9434 | 0 | 610.5976 | 0.033729
9228 | 1187.6089 | 6.202 | 100.8701 | 130.9961 | 74.9343 | 14.2503 | 156.2188 | 10.6778 | 26.8473 | 102.1768 | 188.1688 | 42.8843 | 423.0563 | 368.1936 | 596.7368 | 43.2444 | 96.0463 | 18.0231 | 350 | 76.8641 | 0 | 624.1576 | 0.040439
9229 | 1166.7314 | 9.9877 | 102.0646 | 131.402 | 73.9365 | 15.1997 | 157.2696 | 14.2466 | 22.5499 | 96.3539 | 183.9097 | 41.6953 | 423.3355 | 362.7943 | 579.1364 | 44.8815 | 95.2798 | 18.3991 | 340 | 66.4359 | 0 | 596.3546 | 0.046351
9230 | 1181.2031 | 11.9946 | 100.4023 | 136.7041 | 70.9362 | 18.0492 | 153.7365 | 10.6795 | 25.4293 | 87.4918 | 187.3474 | 41.9126 | 421.8019 | 364.7617 | 568.6354 | 45.827 | 96.9731 | 19.2413 | 291 | 64.7348 | 0 | 614.7925 | 0.030073
9231 | 1175.7195 | 8.9778 | 102.4517 | 143.8675 | 74.9355 | 14.2511 | 155.5083 | 12.6176 | 26.025 | 87.898 | 191.6532 | 41.1938 | 423.8613 | 359.8756 | 564.35 | 44.6424 | 97.5098 | 19.5674 | 277 | 65.0451 | 0 | 594.8136 | 0.01311
9232 | 1140.466 | 6.5797 | 99.6437 | 136.6549 | 73.9321 | 15.204 | 153.1406 | 10.8944 | 19.6588 | 82.2886 | 185.1296 | 40.2417 | 420.2432 | 351.7459 | 533.107 | 44.0434 | 98.3183 | 18.4365 | 244 | 68.1107 | 0 | 587.3115 | 0.0020415
9233 | 1116.0298 | 6.4522 | 90.1496 | 130.5403 | 79.9352 | 9.4974 | 141.2268 | 11.9695 | 17.2742 | 85.1941 | 182.4436 | 38.5771 | 392.7558 | 319.0894 | 480.9129 | 34.9121 | 97.8173 | 17.4565 | 236 | 61.1736 | 0 | 554.6266 | 0
9234 | 1065.9204 | 6.7091 | 78.5708 | 118.7526 | 76.9377 | 12.3492 | 126.8228 | 10.1484 | 17.3675 | 84.9932 | 171.2846 | 34.4172 | 351.6795 | 256.1838 | 424.7226 | 17.506 | 89.714 | 17.209 | 239 | 54.5986 | 0 | 409.8763 | 0
9235 | 1016.765 | 5.9786 | 74.5711 | 106.1511 | 76.9355 | 12.35 | 111.171 | 9.578 | 16.4927 | 63.5065 | 145.9125 | 25.202 | 314.9971 | 194.6247 | 397.0829 | 11.067 | 79.9626 | 15.8259 | 221 | 49.1603 | 0 | 349.948 | 0
9236 | 972.1914 | 5.3235 | 61.4816 | 101.2901 | 81.9382 | 7.6013 | 90.3501 | 9.5118 | 12.2608 | 57.8204 | 132.7198 | 12.7012 | 283.4231 | 162.2595 | 363.145 | 9.9165 | 71.9697 | 9.6107 | 195 | 45.5993 | 0 | 302.9948 | 0
9237 | 931.9131 | 5.3178 | 34.798 | 97.9655 | 83.9445 | 5.7005 | 83.6039 | 9.128 | 10.7651 | 59.3036 | 126.156 | 8.3242 | 258.9505 | 136.4263 | 319.243 | 10.0344 | 60.3687 | 5.7033 | 177 | 46.086 | 0 | 291.8394 | 0
9238 | 923.3362 | 8.6966 | 26.2112 | 97.7178 | 84.9413 | 4.7503 | 81.1039 | 9.8425 | 10.0682 | 56.9941 | 109.7538 | 9.7333 | 233.9008 | 108.0903 | 290.7487 | 9.6857 | 55.5377 | 4.3731 | 168 | 43.3032 | 0 | 268.7944 | 0
9239 | 884.6298 | 9.3101 | 25.9163 | 94.8342 | 83.9464 | 5.6997 | 71.4928 | 8.6947 | 9.471 | 49.8569 | 94.2302 | 9.3842 | 219.09 | 97.8377 | 280.9262 | 9.8042 | 55.2086 | 4.1705 | 164 | 42.4726 | 0 | 267.7884 | 0
9240 | 855.2271 | 5.671 | 25.9429 | 93.343 | 83.9501 | 5.7 | 74.526 | 10.1583 | 9.2713 | 46.9969 | 85.918 | 8.6045 | 216.8874 | 100.7031 | 272.1539 | 9.9962 | 54.9414 | 4.1358 | 157 | 41.702 | 0 | 268.2511 | 0
9241 | 841.922 | 3.3536 | 25.7859 | 95.2625 | 84.9435 | 4.7503 | 79.768 | 8.9158 | 9.1236 | 44.3702 | 82.9737 | 8.3697 | 213.1131 | 95.3373 | 253.8279 | 9.6512 | 53.9925 | 3.5929 | 149 | 41.2778 | 0 | 275.3113 | 0
9242 | 830.0829 | 3.1411 | 25.8288 | 95.2883 | 83.9499 | 5.6997 | 81.0771 | 10.8913 | 8.2871 | 37.3146 | 82.4855 | 8.7198 | 207.2879 | 92.1971 | 250.4696 | 9.8368 | 53.8434 | 3.7156 | 143 | 40.7861 | 0 | 275.5349 | 0
9243 | 816.5577 | 3.1022 | 25.7096 | 92.9416 | 84.9484 | 4.7503 | 73.8549 | 9.3314 | 7.8951 | 34.0921 | 82.4033 | 9.2378 | 203.4772 | 99.702 | 265.3763 | 9.9423 | 53.6607 | 3.6077 | 125 | 40.357 | 0 | 276.7571 | 0
9244 | 824.3008 | 2.773 | 25.6936 | 91.9465 | 81.9473 | 7.5992 | 71.8312 | 10.5822 | 7.503 | 32.3702 | 82.3164 | 9.25 | 205.3133 | 97.298 | 261.7772 | 9.6342 | 53.7368 | 3.5185 | 116 | 41.1484 | 0 | 270.764 | 0
9245 | 824.6047 | 3.5912 | 25.7869 | 91.8538 | 84.9472 | 4.7508 | 77.8686 | 10.1279 | 7.105 | 31.9195 | 82.5597 | 8.9072 | 201.0933 | 92.9219 | 243.5109 | 9.7976 | 55.1826 | 3.825 | 124 | 38.5513 | 0 | 288.3108 | 0
9246 | 843.0073 | 4.3942 | 36.3434 | 92.4893 | 83.9436 | 5.6997 | 85.8841 | 10.1543 | 7.084 | 35.0993 | 83.9722 | 10.0596 | 207.0676 | 99.8292 | 237.7039 | 9.5741 | 57.299 | 3.4887 | 109 | 44.0649 | 0 | 321.4575 | 0
9247 | 880.6684 | 6.2644 | 55.0509 | 97.645 | 81.9413 | 7.5995 | 92.1641 | 11.4067 | 12.6502 | 55.4355 | 98.3748 | 16.959 | 239.2437 | 147.8948 | 259.0591 | 12.258 | 55.1548 | 3.0616 | 188 | 37.27 | 0 | 374.762 | 0
9248 | 931.6674 | 12.1657 | 79.2015 | 101.8522 | 75.9403 | 13.2984 | 108.5595 | 9.3533 | 15.9374 | 78.2832 | 139.0769 | 31.5977 | 284.8806 | 220.4925 | 326.5662 | 28.0423 | 60.2901 | 10.03 | 208 | 51.2418 | 0 | 408.2467 | 0
9249 | 1003.5609 | 11.1028 | 92.2439 | 113.1151 | 76.9367 | 12.3503 | 138.0746 | 14.3085 | 16.0707 | 73.8129 | 165.4564 | 32.809 | 337.5405 | 271.0417 | 448.6307 | 38.5997 | 68.5719 | 15.6572 | 271 | 60.8903 | 0 | 471.4053 | 0
9250 | 1065.6611 | 7.4659 | 97.8265 | 122.9432 | 73.9359 | 15.1992 | 159.914 | 11.2924 | 18.904 | 75.6096 | 182.1118 | 37.3506 | 372.8078 | 305.0304 | 540.7619 | 42.4876 | 80.3408 | 16.1006 | 338 | 61.7526 | 0 | 516.3941 | 0.043567
9251 | 1124.361 | 5.6388 | 97.2291 | 129.4338 | 73.9351 | 15.2 | 160.264 | 13.7442 | 24.6467 | 79.7763 | 189.1978 | 42.9847 | 379.0079 | 313.4832 | 583.0833 | 42.9555 | 94.6737 | 15.2629 | 318 | 59.5165 | 0 | 549.8537 | 0.07953
9252 | 1155.0558 | 5.1021 | 99.5142 | 132.4346 | 72.935 | 16.1497 | 159.5514 | 9.6257 | 23.6937 | 85.5389 | 186.3451 | 42.7013 | 386.0891 | 314.0549 | 582.8203 | 42.8371 | 100.6223 | 15.4651 | 306 | 61.2006 | 0 | 569.4275 | 0.15284
9253 | 1152.2069 | 4.9116 | 99.9611 | 131.4706 | 74.9351 | 14.2505 | 159.3835 | 12.607 | 20.4715 | 77.6207 | 183.2543 | 39.2061 | 389.0758 | 309.3681 | 550.3435 | 43.585 | 98.4099 | 16.3551 | 318 | 59.1082 | 0 | 555.1641 | 0.19313
9254 | 1149.3859 | 4.9532 | 98.3887 | 137.6124 | 73.9371 | 15.1997 | 160.8287 | 10.2194 | 21.0275 | 72.9568 | 185.5958 | 38.6526 | 397.0957 | 327.5422 | 541.8492 | 43.0534 | 98.9955 | 17.0736 | 279 | 60.0882 | 0 | 567.9885 | 0.17677
9255 | 1138.8165 | 4.879 | 99.4399 | 137.8443 | 73.9343 | 15.2042 | 158.2028 | 11.0303 | 21.2217 | 73.084 | 186.7944 | 41.0159 | 405.2722 | 339.1676 | 543.4224 | 43.1566 | 99.5429 | 16.8581 | 281 | 62.3797 | 0 | 557.1607 | 0.13561
9256 | 1114.6367 | 4.4354 | 96.9333 | 135.8277 | 74.938 | 14.25 | 152.6911 | 10.9453 | 19.4747 | 72.941 | 185.7439 | 36.698 | 465.7428 | 318.887 | 506.2124 | 40.1594 | 100.067 | 16.2247 | 272 | 58.2298 | 0 | 544.5808 | 0.021333
9257 | 1065.6255 | 5.7608 | 94.9006 | 128.7548 | 75.935 | 13.2963 | 143.6101 | 11.5018 | 17.851 | 72.1833 | 184.5436 | 30.7382 | 417.6798 | 296.8952 | 442.2649 | 36.1311 | 97.732 | 15.7127 | 245 | 53.3537 | 0 | 450.3087 | 0
9258 | 996.8367 | 6.2865 | 80.7979 | 114.2212 | 80.9353 | 8.5513 | 132.4956 | 10.5127 | 16.2775 | 65.7062 | 169.1783 | 26.9874 | 330.219 | 249.3783 | 365.0199 | 29.3368 | 90.6003 | 15.3633 | 221 | 48.1906 | 0 | 348.9001 | 0
9259 | 947.1885 | 6.1487 | 49.5146 | 102.234 | 83.9375 | 5.7024 | 119.1398 | 10.8717 | 11.9042 | 46.5376 | 141.891 | 22.2873 | 273.0326 | 176.5464 | 328.7103 | 21.5515 | 81.3329 | 15.1398 | 228 | 47.4375 | 0 | 291.6121 | 0
9260 | 892.0829 | 5.292 | 38.3706 | 98.1708 | 83.9443 | 5.6984 | 100.0828 | 8.909 | 8.9123 | 39.8069 | 121.5611 | 12.5665 | 245.9144 | 144.941 | 293.6537 | 28.4714 | 65.1985 | 9.5847 | 239 | 42.5919 | 0 | 265.5958 | 0
9261 | 860.4231 | 4.7389 | 28.4669 | 93.6862 | 83.9468 | 5.7 | 87.67 | 10.226 | 7.6448 | 36.9114 | 99.6212 | 15.4362 | 230.7083 | 123.9564 | 270.9963 | 21.2925 | 57.602 | 5.9426 | 209 | 39.2751 | 0 | 249.8909 | 0
9262 | 833.9139 | 4.6669 | 24.7471 | 93.159 | 84.944 | 4.7503 | 85.6846 | 8.8822 | 7.542 | 30.8594 | 90.9021 | 15.6423 | 209.9485 | 108.2005 | 270.6447 | 14.2286 | 55.957 | 4.0104 | 185 | 39.1867 | 0 | 249.299 | 0
9263 | 817.0706 | 4.2912 | 24.8306 | 93.8389 | 83.9445 | 5.6997 | 83.2957 | 12.0751 | 7.4595 | 26.9585 | 89.3886 | 14.7093 | 197.6775 | 104.2433 | 258.9555 | 11.5809 | 55.9731 | 3.6111 | 166 | 36.7164 | 0 | 251.6843 | 0
9264 | 818.4272 | 3.7269 | 24.6639 | 92.2055 | 81.9489 | 7.5995 | 72.6951 | 8.3197 | 8.1382 | 26.4676 | 86.6929 | 17.531 | 191.8529 | 98.7501 | 256.4978 | 10.8372 | 55.9591 | 3.3155 | 135 | 36.3718 | 0 | 248.892 | 0
9265 | 820.7001 | 3.6546 | 24.8259 | 91.8142 | 84.9447 | 4.7508 | 76.9816 | 11.5609 | 8.2938 | 26.5612 | 85.3577 | 11.0579 | 187.8493 | 94.7934 | 251.6378 | 10.5237 | 55.9888 | 2.739 | 124 | 36.2457 | 0 | 257.5793 | 0
9266 | 812.869 | 4.1475 | 25.0532 | 92.7867 | 83.9462 | 5.6997 | 78.251 | 13.9519 | 7.4875 | 26.5904 | 86.0864 | 7.956 | 185.2381 | 92.0711 | 240.9869 | 10.4644 | 55.9218 | 2.5015 | 121 | 38.5036 | 0 | 256.332 | 0
9267 | 800.5103 | 3.3509 | 24.9177 | 91.3958 | 83.9477 | 5.7 | 71.5742 | 8.8121 | 6.7958 | 26.9737 | 87.2692 | 8.431 | 184.1016 | 93.1536 | 235.9641 | 10.6691 | 55.4379 | 2.4716 | 114 | 37.2056 | 0 | 256.2875 | 0
9268 | 796.2879 | 2.9189 | 24.9071 | 90.7527 | 84.9502 | 4.7503 | 73.784 | 11.7613 | 6.5182 | 27.2813 | 88.6687 | 9.5238 | 182.6246 | 89.0254 | 228.8869 | 10.6261 | 55.298 | 2.4934 | 107 | 37.2946 | 0 | 257.3615 | 0
9269 | 787.1325 | 3.1358 | 24.7554 | 91.5894 | 83.9529 | 5.6997 | 76.0977 | 14.2781 | 6.5345 | 27.736 | 88.4468 | 8.5453 | 182.0199 | 86.508 | 223.2934 | 10.527 | 56.6406 | 2.5138 | 105 | 34.6262 | 0 | 258.3935 | 0
9270 | 779.6171 | 3.8474 | 25.5991 | 91.5377 | 83.9445 | 5.7 | 71.0171 | 14.0936 | 6.4812 | 30.3319 | 87.9248 | 7.9169 | 180.8682 | 86.5346 | 222.0948 | 10.4554 | 58.8404 | 2.4813 | 106 | 31.6232 | 0 | 257.4656 | 0
9271 | 794.1312 | 4.3844 | 40.9456 | 92.6141 | 84.9459 | 4.7503 | 72.842 | 13.8707 | 6.6865 | 31.4059 | 88.3387 | 7.8521 | 181.4883 | 86.912 | 221.3664 | 10.3391 | 56.0405 | 2.4698 | 104 | 33.9848 | 0 | 259.837 | 0
9272 | 807.0554 | 4.4481 | 49.0255 | 94.1354 | 83.9452 | 5.6997 | 79.2978 | 13.8583 | 6.78 | 32.7877 | 95.102 | 9.7866 | 188.3888 | 95.6362 | 224.9084 | 10.5481 | 55.1412 | 2.6875 | 103 | 40.1942 | 0 | 267.5549 | 0
9273 | 823.2295 | 3.6007 | 58.4164 | 93.3379 | 81.9456 | 7.5995 | 81.7121 | 13.6541 | 9.6467 | 39.1879 | 110.9799 | 14.4013 | 194.1463 | 95.1015 | 220.5061 | 10.1442 | 54.0475 | 3.1292 | 145 | 46.1893 | 0 | 262.4144 | 0
9274 | 831.3827 | 3.2115 | 74.6467 | 93.8379 | 82.945 | 6.6503 | 83.5204 | 13.4917 | 9.2965 | 54.6034 | 128.2193 | 15.706 | 207.8914 | 91.1184 | 217.9773 | 9.8875 | 53.9034 | 5.078 | 118 | 47.8542 | 0 | 259.1121 | 0.038909
9275 | 865.3822 | 3.0361 | 80.8199 | 94.2004 | 83.9397 | 5.7003 | 88.5969 | 13.7707 | 6.3808 | 58.9557 | 141.2447 | 15.5524 | 228.6946 | 93.0707 | 220.2138 | 9.9375 | 53.6476 | 10.3953 | 151 | 47.2518 | 0 | 263.7968 | 0.020402
9276 | 864.5609 | 2.8803 | 81.8628 | 93.8607 | 83.9405 | 5.7 | 82.9516 | 9.1708 | 5.5102 | 59.0564 | 131.3781 | 16.4184 | 233.9729 | 101.3748 | 224.3854 | 9.7762 | 54.389 | 12.3874 | 152 | 45.3588 | 0 | 261.567 | 0.02506
9277 | 861.489 | 2.6715 | 81.1623 | 91.1901 | 81.9395 | 7.5995 | 80.4692 | 11.1403 | 5.2218 | 60.7167 | 124.5416 | 19.1115 | 233.2123 | 108.3161 | 237.0877 | 9.9262 | 56.8383 | 12.3856 | 160 | 45.0356 | 0 | 279.2514 | 0.038911
9278 | 863.5586 | 2.6162 | 75.2705 | 90.6078 | 81.9416 | 7.6 | 86.9231 | 13.1728 | 5.4942 | 63.3011 | 125.1225 | 19.9523 | 229.715 | 113.7162 | 242.7354 | 9.9325 | 54.5726 | 12.5156 | 149 | 45.6875 | 0 | 268.2547 | 0.035085
9279 | 863.8419 | 2.6847 | 48.7565 | 90.6244 | 83.9429 | 5.7005 | 83.5365 | 12.6539 | 6.8666 | 62.2407 | 125.7266 | 20.046 | 223.5983 | 120.9882 | 249.699 | 9.8143 | 53.8393 | 10.6302 | 170 | 46.0541 | 0 | 272.7692 | 0.017796
9280 | 859.8351 | 3.0903 | 38.3487 | 90.808 | 81.9416 | 7.5995 | 72.5729 | 8.499 | 6.6961 | 64.3854 | 125.417 | 17.7674 | 223.0242 | 126.0501 | 256.0139 | 9.8597 | 55.8335 | 5.8104 | 177 | 41.4578 | 0 | 279.7698 | 0.004276
9281 | 864.4818 | 4.792 | 28.8224 | 92.2725 | 81.9381 | 7.6 | 75.5458 | 11.4776 | 7.186 | 54.8387 | 126.7619 | 12.8939 | 225.7984 | 123.3317 | 263.3568 | 9.9303 | 53.9633 | 4.2721 | 174 | 40.047 | 0 | 290.6526 | 0
9282 | 857.1756 | 5.1504 | 25.3778 | 94.2172 | 82.9365 | 6.6503 | 75.8701 | 13.8246 | 7.791 | 43.5676 | 118.8258 | 12.8297 | 227.1936 | 128.5066 | 259.3263 | 10.3045 | 53.0216 | 4.4471 | 180 | 37.0289 | 0 | 302.6732 | 0
9283 | 845.9779 | 4.7864 | 25.1322 | 97.5956 | 82.9418 | 6.65 | 79.6985 | 13.8174 | 7.9673 | 38.718 | 97.7059 | 10.7825 | 229.3647 | 127.1813 | 242.6606 | 10.3794 | 53.0592 | 5.0511 | 178 | 36.6816 | 0 | 301.7532 | 0
9284 | 815.0695 | 4.4048 | 25.2191 | 99.2138 | 82.9455 | 6.65 | 79.6718 | 13.7903 | 7.56 | 35.7529 | 89.1985 | 8.8213 | 220.1271 | 117.8692 | 233.0573 | 10.3798 | 53.464 | 5.1221 | 174 | 37.518 | 0 | 292.6614 | 0
9285 | 813.6005 | 4.4497 | 25.2277 | 99.6675 | 82.9416 | 6.65 | 73.0357 | 13.8575 | 6.993 | 34.7806 | 88.8688 | 8.409 | 209.7262 | 102.7377 | 229.771 | 10.4154 | 54.2182 | 4.7155 | 176 | 37.1519 | 0 | 293.4472 | 0
9286 | 793.8232 | 4.6321 | 25.1983 | 95.6305 | 83.9456 | 5.7003 | 66.548 | 10.2009 | 6.6068 | 33.5274 | 89.0397 | 8.4927 | 206.6161 | 95.5926 | 226.7785 | 10.3482 | 54.2614 | 3.7172 | 179 | 35.3858 | 0 | 299.1706 | 0
9287 | 784.5999 | 3.9375 | 25.4574 | 95.4916 | 84.9447 | 4.7516 | 70.9611 | 11.1375 | 6.3017 | 32.7441 | 88.3716 | 8.4657 | 205.382 | 96.4549 | 227.7675 | 10.4485 | 53.113 | 3.3032 | 171 | 36.5107 | 0 | 316.6514 | 0
9288 | 787.6676 | 2.9853 | 25.4605 | 94.4439 | 83.9492 | 5.6984 | 72.5347 | 13.4756 | 7.9615 | 34.884 | 86.837 | 7.9788 | 197.7896 | 93.0814 | 225.9875 | 10.5469 | 52.6395 | 2.6752 | 141 | 34.6611 | 0 | 314.8648 | 0
9289 | 807.9063 | 2.9749 | 25.4344 | 93.6065 | 83.9504 | 5.7 | 66.6061 | 13.9874 | 7.1808 | 33.7306 | 83.4872 | 7.6105 | 190.0864 | 92.0247 | 223.7171 | 10.4204 | 52.7709 | 2.5175 | 131 | 33.3926 | 0 | 300.9757 | 0
9290 | 781.1705 | 2.8163 | 25.3853 | 93.5174 | 83.9474 | 5.7 | 68.5533 | 14.0424 | 6.8222 | 32.6111 | 82.3397 | 7.5171 | 185.1377 | 90.913 | 234.7684 | 10.5187 | 52.929 | 2.4898 | 135 | 33.4811 | 0 | 290.5208 | 0
9291 | 767.7622 | 2.72 | 25.5649 | 93.408 | 78.9497 | 10.4487 | 73.3332 | 10.8845 | 8.718 | 32.8308 | 83.4838 | 7.5321 | 183.6974 | 89.1507 | 252.9135 | 10.409 | 52.7044 | 2.5633 | 133 | 33.2651 | 0 | 286.5343 | 0
9292 | 767.3751 | 2.7462 | 25.6279 | 93.2108 | 76.9518 | 12.3495 | 66.4522 | 10.9442 | 8.0763 | 33.3802 | 85.2937 | 8.0394 | 183.6032 | 90.6465 | 259.4159 | 10.5365 | 53.2508 | 2.6086 | 131 | 32.7554 | 0 | 285.5543 | 0
9293 | 756.6773 | 3.1196 | 25.6518 | 93.5239 | 79.9495 | 9.5008 | 64.5405 | 13.3279 | 6.6672 | 34.0811 | 84.5678 | 7.7491 | 183.077 | 89.4308 | 238.653 | 10.6228 | 54.2391 | 2.5719 | 126 | 38.7917 | 0 | 283.1697 | 0
9294 | 772.0814 | 4.056 | 25.5352 | 93.4611 | 83.9498 | 5.7011 | 72.8577 | 14.0598 | 6.4762 | 32.9315 | 85.6593 | 7.5291 | 181.9499 | 89.6698 | 223.7575 | 10.3732 | 55.921 | 2.4257 | 119 | 44.9165 | 0 | 280.6252 | 0
9295 | 781.1997 | 4.44 | 25.5027 | 93.2157 | 83.9461 | 5.7 | 69.5727 | 14.0022 | 6.6375 | 34.1108 | 87.3095 | 7.5658 | 182.4098 | 91.441 | 222.1797 | 10.5168 | 53.6756 | 2.2728 | 117 | 36.0153 | 0 | 280.3497 | 0
9296 | 783.9836 | 4.453 | 25.546 | 93.0671 | 83.9454 | 5.7 | 63.6306 | 9.5206 | 6.7517 | 32.9848 | 88.6522 | 7.8187 | 188.518 | 90.642 | 222.1594 | 10.315 | 52.3347 | 2.5193 | 111 | 35.9578 | 0 | 278.5904 | 0
9297 | 784.7164 | 4.0473 | 25.683 | 89.6953 | 82.947 | 6.6497 | 69.1042 | 10.9926 | 6.2138 | 38.3513 | 86.7546 | 6.8314 | 192.1196 | 90.7137 | 219.1862 | 10.2315 | 51.5144 | 3.1986 | 116 | 35.7731 | 0 | 270.1398 | 0
9298 | 809.8516 | 3.0136 | 32.1655 | 88.2709 | 82.941 | 6.65 | 74.7807 | 13.3702 | 6.3555 | 53.7225 | 83.8094 | 5.1207 | 198.4451 | 91.1323 | 213.4989 | 10.0038 | 50.7452 | 3.6417 | 161 | 35.8871 | 0 | 267.1595 | 0.013981
9299 | 817.2601 | 2.6857 | 38.6404 | 88.1779 | 84.944 | 4.7505 | 75.6458 | 7.9145 | 8.2846 | 62.8521 | 91.2056 | 4.5659 | 210.4386 | 99.1562 | 213.1761 | 9.8749 | 50.7588 | 4.3038 | 166 | 36.3039 | 0 | 264.9169 | 0.015025
9300 | 829.6159 | 2.9944 | 40.927 | 88.1311 | 83.9422 | 5.6997 | 82.6813 | 10.7852 | 6.722 | 62.0936 | 103.6787 | 4.6544 | 217.0119 | 117.6855 | 209.0129 | 9.944 | 51.3562 | 4.8117 | 180 | 38.1033 | 0 | 270.0116 | 0.018595
9301 | 832.6534 | 2.7112 | 40.2333 | 88.3081 | 84.9382 | 4.7503 | 92.1559 | 13.1578 | 5.8681 | 66.7511 | 118.2157 | 4.7426 | 225.635 | 125.0478 | 212.9748 | 9.6621 | 53.9008 | 5.0229 | 172 | 40.0149 | 0 | 269.5332 | 0.032897
9302 | 838.8663 | 2.4844 | 39.8112 | 89.3799 | 83.9418 | 5.6997 | 90.3128 | 7.7499 | 6.0271 | 68.7368 | 123.7538 | 4.7622 | 231.5309 | 133.7714 | 233.6138 | 9.8648 | 55.3351 | 5.877 | 165 | 40.3299 | 0 | 274.0312 | 0.018362
9303 | 857.5662 | 2.7097 | 39.7298 | 88.8831 | 82.9438 | 6.6497 | 82.0419 | 10.88 | 7.6693 | 65.8761 | 125.4903 | 5.4849 | 234.0192 | 137.6066 | 258.6925 | 9.954 | 53.5207 | 6.4325 | 160 | 41.1748 | 0 | 277.8326 | 0.012743
9304 | 871.1071 | 3.0943 | 38.6969 | 91.2331 | 83.9417 | 5.7003 | 81.8655 | 11.9135 | 8.9542 | 53.1741 | 124.7164 | 7.8069 | 227.9674 | 134.3332 | 276.8553 | 9.8001 | 52.1487 | 6.1896 | 163 | 41.1981 | 0 | 285.7094 | 0.0025598
9305 | 864.9695 | 4.3876 | 29.2476 | 94.4926 | 83.9409 | 5.7 | 77.9578 | 9.1338 | 8.9444 | 38.3644 | 125.1728 | 10.9036 | 228.9002 | 139.294 | 282.4314 | 10.2268 | 51.8284 | 5.8509 | 157 | 40.077 | 0 | 294.2963 | 0
9306 | 849.7004 | 5.1496 | 25.7372 | 94.0677 | 83.9383 | 5.7 | 66.6239 | 11.9539 | 9.0294 | 35.3843 | 126.1036 | 12.0794 | 226.3235 | 130.232 | 265.5279 | 10.1901 | 53.0347 | 5.4555 | 146 | 37.9457 | 0 | 298.8133 | 0
9307 | 838.3532 | 4.7813 | 26.1411 | 92.5927 | 77.9422 | 11.3984 | 68.0944 | 13.6008 | 8.4914 | 35.079 | 125.0413 | 10.2733 | 218.4164 | 121.4435 | 256.6963 | 10.4353 | 54.3016 | 5.585 | 139 | 35.6081 | 0 | 301.8628 | 0
9308 | 836.0072 | 4.9592 | 25.5756 | 92.1233 | 82.9394 | 6.6513 | 76.7292 | 8.3427 | 8.3654 | 34.2236 | 119.3502 | 9.4457 | 211.7727 | 111.9946 | 250.3311 | 10.3382 | 54.1617 | 5.1397 | 122 | 37.2435 | 0 | 294.3256 | 0
9309 | 823.6141 | 5.5 | 25.3363 | 92.2589 | 84.9436 | 4.7505 | 69.8373 | 11.4718 | 7.8467 | 33.5957 | 98.2141 | 8.9957 | 212.0867 | 103.0706 | 242.9636 | 10.4513 | 52.9925 | 4.0237 | 116 | 38.2269 | 0 | 286.0975 | 0
9310 | 797.6699 | 4.8733 | 25.4045 | 91.4322 | 83.9497 | 5.6997 | 64.0631 | 13.4963 | 6.9454 | 33.0168 | 89.1249 | 8.1018 | 205.6727 | 101.5427 | 230.3344 | 10.4361 | 53.2809 | 3.3446 | 113 | 37.9065 | 0 | 282.2499 | 0
9311 | 779.3778 | 3.8916 | 25.2354 | 90.7979 | 83.9476 | 5.7 | 72.865 | 8.9668 | 6.645 | 30.1528 | 87.0691 | 8.0931 | 196.6153 | 98.038 | 224.0204 | 10.3712 | 52.9226 | 2.7193 | 114 | 32.4482 | 0 | 281.3817 | 0
9312 | 778.7159 | 2.8022 | 25.4367 | 90.6194 | 83.949 | 5.7 | 72.902 | 11.9603 | 6.58 | 27.9 | 85.7091 | 8.765 | 193.6213 | 92.8486 | 227.088 | 10.5849 | 52.6923 | 2.4924 | 106 | 31.2557 | 0 | 291.8449 | 0
9313 | 782.096 | 2.4434 | 25.4581 | 90.5498 | 82.9477 | 6.6497 | 63.9067 | 12.1383 | 6.4336 | 27.4628 | 84.7729 | 7.9471 | 187.8245 | 90.0966 | 222.5259 | 10.6269 | 52.6973 | 2.4887 | 107 | 31.2334 | 0 | 280.971 | 0
9314 | 770.8225 | 3.1918 | 25.3964 | 90.4394 | 83.9494 | 5.7003 | 65.3045 | 9.59 | 6.3856 | 27.6183 | 84.4429 | 7.72 | 181.0663 | 89.168 | 218.5486 | 10.5112 | 52.3404 | 2.5179 | 104 | 32.2348 | 0 | 282.5838 | 0
9315 | 751.324 | 2.7877 | 25.4034 | 90.3456 | 84.9508 | 4.7503 | 72.6734 | 12.4578 | 6.131 | 27.6019 | 84.3416 | 7.8609 | 176.8266 | 93.8124 | 227.2172 | 10.5186 | 52.5386 | 2.5372 | 106 | 32.3256 | 0 | 281.4264 | 0
9316 | 760.5347 | 2.491 | 26.1753 | 91.0956 | 83.9485 | 5.6997 | 66.453 | 11.0946 | 6.1733 | 27.6596 | 84.2786 | 7.5654 | 175.3409 | 100.6363 | 227.8491 | 10.398 | 52.9304 | 2.4943 | 104 | 31.2314 | 0 | 278.4581 | 0
9317 | 773.549 | 3.1941 | 28.1775 | 92.237 | 83.9482 | 5.7 | 63.6526 | 10.4381 | 6.3894 | 27.5689 | 84.4562 | 7.4229 | 178.7588 | 92.178 | 222.6914 | 10.5942 | 54.4259 | 2.4858 | 103 | 30.9001 | 0 | 322.1932 | 0
9318 | 795.6667 | 4.1741 | 34.6444 | 90.9105 | 84.9427 | 4.7503 | 78.247 | 12.9156 | 6.7693 | 28.5746 | 85.3702 | 8.5556 | 187.5989 | 100.7324 | 228.1478 | 10.4657 | 57.2861 | 2.5016 | 105 | 32.6029 | 0 | 343.2689 | 0
9319 | 826.0442 | 6.2014 | 53.9016 | 94.8745 | 82.9446 | 6.6495 | 91.2593 | 11.9891 | 8.8149 | 46.793 | 103.6074 | 19.4319 | 222.1746 | 165.4886 | 264.5113 | 13.4689 | 53.7693 | 3.6161 | 181 | 44.3127 | 0 | 382.8166 | 0
9320 | 891.4052 | 10.8428 | 79.0532 | 102.9345 | 76.1047 | 13.2982 | 101.4807 | 10.227 | 15.203 | 83.3379 | 139.2052 | 35.5973 | 277.9846 | 236.2904 | 378.1998 | 27.9014 | 58.5467 | 9.03 | 259 | 51.7689 | 0 | 456.2891 | 0
9321 | 989.1248 | 16.1596 | 94.5621 | 113.3705 | 75.0259 | 14.2497 | 127.3932 | 14.8306 | 22.6187 | 91.2958 | 157.1722 | 42.0546 | 330.937 | 292.4176 | 481.3162 | 35.4995 | 70.6682 | 16.7092 | 297 | 58.4903 | 0 | 529.649 | 0
9322 | 1075.7174 | 16.6089 | 100.6888 | 127.96 | 73.9374 | 15.1997 | 151.6212 | 17.1012 | 25.4655 | 89.551 | 163.1331 | 42.3916 | 376.4008 | 337.2757 | 550.7349 | 42.2763 | 79.3969 | 17.0837 | 324 | 63.9059 | 0 | 572.6686 | 0.079637
9323 | 1124.2237 | 18.5315 | 100.5514 | 131.3335 | 69.9371 | 18.9989 | 148.3958 | 11.2692 | 24.6524 | 94.1702 | 173.9173 | 43.2739 | 397.8523 | 350.8713 | 564.2303 | 44.6208 | 95.9253 | 16.6063 | 351 | 66.8273 | 0 | 575.2856 | 0.15421
9324 | 1185.5155 | 18.9068 | 106.1035 | 134.3553 | 70.934 | 18.0503 | 148.0281 | 13.8605 | 23.706 | 97.8664 | 183.7777 | 43.8875 | 408.262 | 364.6652 | 563.8804 | 43.0972 | 100.946 | 17.4834 | 358 | 72.9615 | 0 | 583.4798 | 0.12442
9325 | 1180.1961 | 16.3689 | 106.8058 | 132.3377 | 72.9344 | 16.1505 | 155.5012 | 12.1487 | 21.5579 | 88.1795 | 185.3527 | 44.0078 | 405.0659 | 361.2957 | 568.3915 | 43.3039 | 94.2234 | 18.4642 | 365 | 67.5146 | 0 | 571.0309 | 0.10826
9326 | 1190.9168 | 14.7826 | 100.3916 | 131.8426 | 72.9377 | 16.15 | 154.1156 | 13.4919 | 26.8109 | 91.3116 | 184.1607 | 44.4662 | 411.1988 | 366.9751 | 570.7813 | 44.2696 | 93.6586 | 18.8465 | 315 | 65.1908 | 0 | 632.9939 | 0.12014
9327 | 1183.9559 | 13.5405 | 102.5314 | 138.4695 | 72.9388 | 16.15 | 153.983 | 15.351 | 24.9466 | 91.5779 | 190.6021 | 42.8054 | 411.4332 | 369.7779 | 577.4997 | 44.7722 | 94.2957 | 19.075 | 255 | 65.3961 | 0 | 589.9463 | 0.14219
9328 | 1166.8835 | 9.597 | 102.9025 | 134.54 | 73.9369 | 15.2003 | 156.3972 | 12.3208 | 18.116 | 88.1039 | 189.3964 | 40.5409 | 415.8594 | 366.7525 | 581.14 | 46.0482 | 94.5887 | 19.0532 | 257 | 62.6938 | 0 | 590.3487 | 0.054307
9329 | 1134.2654 | 7.1228 | 98.9661 | 129.0415 | 73.9371 | 15.2 | 140.1243 | 14.8356 | 16.4325 | 81.3258 | 185.091 | 40.0771 | 404.6801 | 346.7238 | 526.5496 | 37.2421 | 93.5076 | 18.9976 | 235 | 53.2998 | 0 | 544.979 | 0
9330 | 1066.3011 | 6.8132 | 95.006 | 116.3191 | 81.9352 | 7.6021 | 123.3886 | 15.9476 | 15.8147 | 71.2783 | 173.0528 | 39.3674 | 358.9954 | 267.8645 | 434.8516 | 21.7154 | 82.9511 | 18.6143 | 217 | 50.413 | 0 | 438.6067 | 0
9331 | 1005.1463 | 6.4408 | 79.5412 | 105.3948 | 82.9369 | 6.6503 | 112.6387 | 12.9644 | 12.9328 | 55.355 | 147.839 | 31.9122 | 304.057 | 190.3924 | 370.7412 | 17.0413 | 74.0696 | 16.8744 | 220 | 47.3896 | 0 | 397.4991 | 0
9332 | 961.2927 | 5.2662 | 62.5826 | 99.8139 | 83.9405 | 5.7003 | 81.2325 | 11.2645 | 8.3553 | 49.5754 | 136.7521 | 16.3046 | 272.5951 | 154.7063 | 334.9499 | 14.9316 | 63.6697 | 10.0357 | 189 | 42.3562 | 0 | 349.4922 | 0
9333 | 933.0726 | 4.8699 | 35.09 | 93.6182 | 83.9458 | 5.7 | 78.7344 | 11.5171 | 6.52 | 46.0859 | 128.4982 | 10.9467 | 251.0688 | 130.6568 | 295.9632 | 19.8606 | 57.6618 | 5.5636 | 168 | 39.0938 | 0 | 320.436 | 0
9334 | 891.6086 | 4.8533 | 26.3613 | 91.0639 | 83.9446 | 5.7 | 86.2052 | 13.3333 | 6.4002 | 37.8018 | 113.4571 | 10.4362 | 229.1135 | 112.5694 | 263.9882 | 15.8262 | 56.3588 | 4.1155 | 159 | 34.7139 | 0 | 299.2311 | 0
9335 | 870.876 | 4.0561 | 26.2292 | 90.6873 | 84.941 | 4.7503 | 79.3323 | 13.986 | 6.1907 | 30.7918 | 96.4182 | 10.1361 | 218.2152 | 100.1911 | 249.3494 | 11.0914 | 55.1124 | 3.1055 | 134 | 32.3995 | 0 | 291.4765 | 0
9336 | 849.5171 | 3.087 | 26.0513 | 90.3102 | 83.9424 | 5.6997 | 76.4156 | 14.0497 | 5.8563 | 29.0173 | 88.6801 | 9.9305 | 204.5762 | 97.9086 | 246.6731 | 9.9939 | 54.023 | 2.782 | 117 | 31.723 | 0 | 291.5214 | 0
9337 | 840.1744 | 2.8751 | 25.969 | 90.2409 | 84.9433 | 4.7503 | 76.4959 | 13.9835 | 5.9822 | 29.3841 | 86.7255 | 9.7557 | 198.4482 | 94.8313 | 232.171 | 10.0901 | 54.1807 | 2.7872 | 106 | 30.356 | 0 | 295.71 | 0
9338 | 840.4373 | 2.6629 | 26.1814 | 91.0352 | 83.9472 | 5.6997 | 73.5996 | 8.7814 | 5.9338 | 29.4647 | 90.0867 | 9.7764 | 202.6825 | 90.7966 | 223.9346 | 10.1105 | 54.5637 | 2.8696 | 103 | 30.2665 | 0 | 296.3299 | 0
9339 | 828.2496 | 2.4553 | 26.2931 | 90.5381 | 84.9441 | 4.7503 | 67.4678 | 11.7415 | 5.9942 | 29.221 | 93.2226 | 9.7711 | 200.4432 | 88.9628 | 232.0397 | 9.7764 | 54.6363 | 2.9983 | 107 | 30.0353 | 0 | 300.3357 | 0
9340 | 841.4393 | 2.4748 | 26.3024 | 90.0907 | 83.9471 | 5.6997 | 69.2099 | 14.2792 | 6.0688 | 29.552 | 93.4189 | 9.7534 | 195.1244 | 87.2729 | 236.0078 | 9.9577 | 54.8117 | 2.8442 | 105 | 29.7371 | 0 | 300.8353 | 0
9341 | 840.6895 | 2.8827 | 26.2849 | 90.1538 | 84.9466 | 4.7503 | 73.1596 | 9.2416 | 6.0446 | 30.0956 | 91.7577 | 9.7072 | 197.7676 | 85.7798 | 230.545 | 9.9345 | 56.0213 | 2.7607 | 101 | 29.7974 | 0 | 327.0184 | 0
9342 | 863.9741 | 3.8679 | 35.5721 | 90.2291 | 83.9413 | 5.6997 | 72.1122 | 11.2694 | 5.938 | 30.4692 | 89.7001 | 11.6329 | 209.7907 | 90.5821 | 232.952 | 9.9616 | 57.8031 | 2.8819 | 101 | 31.407 | 0 | 370.1609 | 0
9343 | 900.8518 | 9.6751 | 54.3535 | 95.6211 | 82.9385 | 6.6497 | 85.3538 | 13.5543 | 10.7329 | 51.1215 | 100.8556 | 18.0543 | 247.5308 | 165.0191 | 253.1001 | 12.6055 | 55.6699 | 3.5743 | 160 | 41.5579 | 0 | 409.877 | 0
9344 | 960.3295 | 18.1467 | 81.6715 | 100.0915 | 73.9439 | 15.1976 | 114.6259 | 14.533 | 19.2653 | 79.0919 | 141.8631 | 31.9664 | 292.6635 | 242.048 | 353.843 | 28.4658 | 58.8571 | 7.3879 | 257 | 48.8056 | 0 | 463.7452 | 0
9345 | 1035.8889 | 16.0329 | 95.0677 | 108.5845 | 75.9393 | 13.3005 | 132.4812 | 12.7286 | 24.5003 | 78.347 | 165.6167 | 37.0773 | 353.1775 | 296.6332 | 495.7385 | 38.0414 | 72.1697 | 15.1899 | 291 | 59.2032 | 0 | 536.3222 | 0
9346 | 1137.3775 | 13.6159 | 103.7182 | 120.5143 | 76.9326 | 12.3503 | 147.761 | 12.0225 | 24.4205 | 82.8035 | 180.8147 | 38.8341 | 399.5958 | 340.2571 | 571.9458 | 42.7185 | 88.4842 | 18.7164 | 323 | 65.1237 | 0 | 575.7305 | 0.015362
9347 | 1169.5152 | 14.3488 | 103.0681 | 129.4318 | 74.9346 | 14.2495 | 158.9181 | 14.7917 | 21.1893 | 83.0132 | 188.66 | 42.3447 | 421.4522 | 359.4937 | 600.3622 | 44.7181 | 114.4749 | 19.4 | 323 | 67.9541 | 0 | 575.1598 | 0.01497
9348 | 1180.8861 | 12.105 | 106.2047 | 130.685 | 73.9355 | 15.1997 | 159.0841 | 10.2378 | 19.0652 | 88.4549 | 191.3255 | 41.3432 | 433.5178 | 376.0139 | 612.5217 | 44.1782 | 120.4123 | 18.8793 | 326 | 79.6372 | 0 | 612.9873 | 0.023862
9349 | 1184.4703 | 12.0968 | 103.8119 | 131.1946 | 73.9318 | 15.2 | 154.2497 | 14.3332 | 19.2333 | 86.3037 | 191.7703 | 38.8169 | 428.6708 | 371.9652 | 599.0468 | 44.1258 | 111.8702 | 18.9547 | 361 | 73.3653 | 0 | 617.7231 | 0.01638
9350 | 1178.7552 | 12.0988 | 102.9505 | 132.9344 | 74.9342 | 14.2503 | 165.5867 | 13.9158 | 25.4206 | 90.8904 | 195.5391 | 41.503 | 436.3933 | 370.7856 | 583.3522 | 46.0027 | 118.2207 | 19.1669 | 282 | 70.7061 | 0 | 659.9496 | 0.027322
9351 | 1172.5368 | 7.4374 | 103.7303 | 136.3657 | 76.9297 | 12.354 | 160.7956 | 12.1744 | 27.3661 | 95.8032 | 196.3863 | 42.3501 | 444.245 | 371.7771 | 585.1614 | 45.5473 | 122.5767 | 19.4583 | 256 | 71.8433 | 0 | 625.4973 | 0.014833
9352 | 1150.6278 | 7.8882 | 99.2722 | 135.6984 | 74.9363 | 14.246 | 149.4445 | 14.815 | 23.494 | 86.3154 | 192.3425 | 41.3709 | 437.6861 | 365.2959 | 572.1642 | 43.8381 | 124.7589 | 19.3386 | 241 | 67.7899 | 0 | 598.9986 | 0.0026131
9353 | 1104.6765 | 11.9527 | 91.5722 | 128.3111 | 75.9343 | 13.3003 | 145.7228 | 10.8603 | 18.9452 | 83.8595 | 188.3088 | 37.3995 | 428.1789 | 353.1766 | 509.2511 | 35.9392 | 121.9936 | 18.2749 | 221 | 56.1527 | 0 | 539.1687 | 0
9354 | 1069.0747 | 13.5041 | 87.6176 | 118.0143 | 82.9311 | 6.6518 | 123.8852 | 13.0318 | 17.1051 | 77.3167 | 172.1168 | 32.7023 | 387.441 | 290.1038 | 427.3938 | 21.4151 | 111.2051 | 17.5401 | 223 | 55.3421 | 0 | 427.5003 | 0
9355 | 1001.8804 | 12.8265 | 83.7896 | 105.7221 | 83.9309 | 5.7018 | 108.0064 | 14.2445 | 14.0277 | 61.8528 | 147.518 | 26.4264 | 390.9067 | 211.3333 | 365.7452 | 14.8703 | 104.3336 | 17.3376 | 205 | 52.9443 | 0 | 371.4944 | 0
9356 | 958.2463 | 16.4453 | 66.4126 | 99.1873 | 83.9366 | 5.6984 | 89.6219 | 8.5247 | 9.1518 | 53.3464 | 131.477 | 13.7616 | 332.8648 | 175.5527 | 323.0723 | 12.9055 | 73.8891 | 11.7334 | 180 | 49.3371 | 0 | 312.7017 | 0
9357 | 920.723 | 14.4327 | 35.3062 | 93.9579 | 83.9374 | 5.7016 | 72.7175 | 11.4928 | 7.3332 | 46.6257 | 121.9638 | 9.6616 | 257.2635 | 155.2532 | 281.4637 | 12.3932 | 59.707 | 7.5259 | 157 | 44.7781 | 0 | 295.9276 | 0
9358 | 888.3239 | 7.3258 | 25.7242 | 92.1347 | 84.9418 | 4.7487 | 70.9654 | 12.0934 | 7.1427 | 38.5168 | 106.2005 | 9.5222 | 220.391 | 130.1742 | 242.8809 | 12.3645 | 57.9433 | 6.0991 | 150 | 36.4055 | 0 | 291.1906 | 0
9359 | 842.1467 | 4.4288 | 25.3821 | 91.6801 | 83.9411 | 5.6997 | 79.5082 | 9.3152 | 6.8548 | 30.5226 | 88.5728 | 9.0793 | 201.7004 | 118.4214 | 238.7964 | 12.0927 | 57.0793 | 4.2576 | 146 | 35.4888 | 0 | 282.5466 | 0
9360 | 816.9175 | 3.8449 | 25.5522 | 91.5822 | 84.9396 | 4.7503 | 75.9949 | 12.2239 | 6.6783 | 27.5284 | 82.1246 | 8.9523 | 189.0128 | 111.242 | 244.5735 | 12.3074 | 55.5253 | 3.4618 | 126 | 36.004 | 0 | 291.1077 | 0
9361 | 813.2287 | 5.477 | 25.2861 | 92.8439 | 83.9403 | 5.6997 | 67.6841 | 8.6852 | 6.6142 | 27.2512 | 81.9198 | 8.7768 | 182.5766 | 109.6879 | 233.1505 | 12.31 | 54.7643 | 3.0736 | 118 | 35.2769 | 0 | 284.2775 | 0
9362 | 802.3396 | 8.1577 | 25.1201 | 91.8821 | 84.9422 | 4.7503 | 75.3568 | 11.3031 | 6.7863 | 27.6152 | 83.5777 | 8.8542 | 181.9189 | 107.0071 | 223.4819 | 12.3313 | 54.7806 | 3.1036 | 106 | 31.5676 | 0 | 287.0866 | 0
9363 | 804.8171 | 9.2779 | 25.5095 | 91.977 | 83.9441 | 5.6997 | 80.3975 | 11.7511 | 6.7865 | 27.9717 | 84.4908 | 8.803 | 182.5112 | 106.8204 | 223.9735 | 12.4227 | 55.3529 | 2.9237 | 103 | 31.2687 | 0 | 290.9539 | 0
9364 | 807.1052 | 8.9947 | 25.4203 | 91.5143 | 84.9445 | 4.7503 | 71.3454 | 9.3458 | 6.875 | 27.7932 | 84.4122 | 8.7488 | 180.768 | 107.047 | 219.6344 | 12.0853 | 55.1565 | 2.7587 | 99 | 30.9142 | 0 | 288.1658 | 0
9365 | 819.0713 | 6.5869 | 25.3643 | 91.7481 | 83.9406 | 5.7013 | 70.7788 | 12.2672 | 6.8857 | 28.0701 | 85.6892 | 8.7282 | 183.2605 | 106.6545 | 213.5663 | 12.2876 | 56.286 | 2.7757 | 104 | 31.4585 | 0 | 315.2592 | 0
9366 | 833.6447 | 4.8515 | 34.8541 | 91.6137 | 83.9394 | 5.6984 | 85.0609 | 8.6588 | 7.2475 | 29.5419 | 88.1356 | 9.7954 | 193.438 | 106.7743 | 218.1148 | 12.199 | 58.4888 | 2.8102 | 101 | 30.824 | 0 | 356.4831 | 0
9367 | 863.0852 | 5.7442 | 50.6759 | 95.961 | 81.9393 | 7.5995 | 95.966 | 11.1841 | 9.9285 | 50.6653 | 97.3748 | 20.3276 | 224.7115 | 164.3746 | 236.5875 | 14.8397 | 55.8831 | 3.0181 | 188 | 41.723 | 0 | 398.4492 | 0
9368 | 938.8073 | 9.6353 | 77.3132 | 100.7302 | 75.9361 | 13.2984 | 108.2086 | 14.4662 | 15.0028 | 84.3086 | 138.1153 | 35.6177 | 275.4914 | 240.9183 | 359.1644 | 31.0894 | 61.2113 | 6.9202 | 308 | 52.8949 | 0 | 447.9089 | 0
9369 | 1026.8528 | 13.2576 | 93.3305 | 113.0195 | 72.9304 | 16.1492 | 136.6619 | 10.1312 | 21.376 | 96.2903 | 167.3927 | 40.7101 | 339.3621 | 297.4178 | 490.8417 | 40.7422 | 71.3502 | 15.4745 | 314 | 59.5473 | 0 | 513.8142 | 0
9370 | 1117.1729 | 12.6981 | 100.2676 | 125.5944 | 73.9315 | 15.2045 | 157.2743 | 13.6737 | 25.4047 | 102.1366 | 183.0036 | 40.9309 | 398.5579 | 334.6764 | 562.1123 | 44.6055 | 80.959 | 18.1882 | 319 | 64.9908 | 0 | 584.7686 | 0.011362
9371 | 1176.0784 | 9.2862 | 101.1607 | 130.4806 | 72.9396 | 16.1455 | 156.5001 | 14.555 | 26.0879 | 103.3138 | 190.5946 | 41.9545 | 422.6977 | 356.3474 | 571.5514 | 44.8217 | 92.8685 | 18.4836 | 355 | 74.6048 | 0 | 577.2841 | 0.014916
9372 | 1193.7163 | 5.5014 | 106.2986 | 135.4131 | 74.935 | 14.2505 | 161.8333 | 11.6964 | 23.0614 | 101.1108 | 189.6822 | 42.6997 | 436.227 | 376.4378 | 594.8789 | 42.1025 | 99.1403 | 18.5889 | 374 | 80.1862 | 0 | 584.4893 | 0.019398
9373 | 1166.3442 | 7.6717 | 101.3579 | 133.7179 | 73.939 | 15.1997 | 166.7973 | 15.3343 | 17.3146 | 91.1447 | 192.5583 | 43.5168 | 425.9637 | 383.9401 | 586.8216 | 42.4817 | 104.7973 | 19.0699 | 377 | 74.11 | 0 | 581.093 | 0.02023
9374 | 1183.5032 | 13.1781 | 99.725 | 138.3009 | 73.9338 | 15.2042 | 163.1114 | 10.9226 | 19.668 | 84.7221 | 191.9668 | 41.9855 | 434.3805 | 381.0818 | 567.272 | 45.7229 | 124.5724 | 19.511 | 328 | 75.789 | 0 | 610.7221 | 0.018031
9375 | 1202.8305 | 12.6322 | 100.2958 | 140.892 | 76.9361 | 12.35 | 162.545 | 13.6332 | 19.7316 | 87.7892 | 190.1534 | 43.4415 | 430.1007 | 371.6683 | 586.4965 | 46.32 | 130.5799 | 19.2797 | 284 | 76.1061 | 0 | 578.4889 | 0.014009
9376 | 1177.0393 | 7.5317 | 100.7241 | 137.4545 | 76.9405 | 12.3466 | 156.9431 | 10.7188 | 17.4792 | 95.9606 | 189.7781 | 43.0754 | 422.7728 | 360.2844 | 588.0356 | 43.2573 | 131.0052 | 19.4697 | 250 | 76.4972 | 0 | 568.7867 | 0.0017892
9377 | 1129.2564 | 6.5939 | 90.7549 | 132.2084 | 81.9352 | 7.6013 | 137.0562 | 13.1731 | 19.917 | 110.1962 | 188.777 | 43.1009 | 403.7595 | 345.4465 | 547.6516 | 38.5761 | 126.934 | 19.2197 | 223 | 69.2461 | 0 | 521.2955 | 0
9378 | 1060.2233 | 6.9101 | 78.4504 | 119.1679 | 81.9384 | 7.6 | 127.0495 | 13.5125 | 24.9411 | 93.6394 | 174.5493 | 40.0764 | 355.129 | 279.8187 | 446.6111 | 24.5988 | 118.6425 | 17.4015 | 212 | 59.3894 | 0 | 416.4888 | 0
9379 | 996.0117 | 6.2591 | 71.6889 | 105.1473 | 81.9397 | 7.6 | 111.0064 | 9.5507 | 22.6406 | 73.4855 | 148.6726 | 31.5423 | 306.8485 | 190.722 | 382.103 | 16.4944 | 100.7908 | 16.5362 | 206 | 48.2811 | 0 | 367.8208 | 0
9380 | 938.6441 | 5.9811 | 62.2437 | 98.6644 | 84.9438 | 4.7508 | 78.492 | 12.2434 | 12.8696 | 65.2864 | 135.3322 | 16.5034 | 279.091 | 154.6291 | 341.8281 | 14.7099 | 76.4144 | 10.2645 | 177 | 47.9409 | 0 | 319.4582 | 0
9381 | 886.8482 | 5.3847 | 41.5453 | 95.2647 | 83.9517 | 5.6997 | 74.6157 | 8.3195 | 8.894 | 57.8441 | 127.2196 | 11.1018 | 263.0901 | 142.7866 | 313.9418 | 13.1186 | 69.4888 | 5.9802 | 164 | 41.439 | 0 | 299.4498 | 0
9382 | 862.6816 | 4.661 | 34.6435 | 92.8407 | 84.9434 | 4.7503 | 79.6707 | 11.5406 | 7.3195 | 47.3356 | 108.3023 | 13.5382 | 239.6543 | 118.2299 | 299.3588 | 11.9024 | 62.051 | 4.4248 | 152 | 34.8859 | 0 | 300.416 | 0
9383 | 836.6889 | 4.1655 | 34.3242 | 90.9152 | 83.9409 | 5.6997 | 72.9872 | 10.5094 | 6.4975 | 41.7937 | 92.7869 | 14.9682 | 218.2636 | 103.5413 | 291.2171 | 11.5016 | 57.1472 | 3.5588 | 135 | 34.4654 | 0 | 288.6283 | 0
9384 | 813.3803 | 3.1368 | 34.2217 | 90.2998 | 83.9391 | 5.7 | 72.4199 | 10.0671 | 6.3413 | 39.1198 | 87.0682 | 14.8972 | 200.8229 | 95.3263 | 267.5396 | 11.2202 | 57.0357 | 3.8745 | 119 | 33.7094 | 0 | 286.4246 | 0
9385 | 818.7309 | 2.5227 | 34.2423 | 90.2334 | 84.9423 | 4.7503 | 81.5352 | 13.0856 | 6.416 | 38.5508 | 86.5641 | 14.4842 | 192.5676 | 90.121 | 235.9045 | 11.2705 | 56.3009 | 4.2348 | 112 | 32.9803 | 0 | 282.4118 | 0
9386 | 798.5765 | 2.4246 | 34.863 | 90.9065 | 83.9476 | 5.6997 | 75.8036 | 8.717 | 6.3783 | 39.0449 | 85.4204 | 14.3577 | 193.6594 | 86.187 | 219.0638 | 11.4681 | 56.4399 | 3.7859 | 107 | 30.4238 | 0 | 287.4466 | 0
9387 | 791.8922 | 2.5667 | 35.4591 | 91.1168 | 83.9448 | 5.7 | 68.5811 | 11.3622 | 6.3572 | 39.0702 | 84.6295 | 14.3732 | 191.9631 | 85.8398 | 225.5417 | 11.3582 | 56.7148 | 2.999 | 111 | 30.5061 | 0 | 284.4786 | 0
9388 | 796.1331 | 2.6807 | 35.6266 | 90.1864 | 84.9416 | 4.7503 | 75.5836 | 13.811 | 6.4245 | 39.0762 | 84.5668 | 14.4047 | 190.0474 | 86.1821 | 222.7146 | 11.4311 | 56.7622 | 2.7976 | 109 | 30.2171 | 0 | 285.6643 | 0
9389 | 807.5905 | 3.3513 | 35.6648 | 90.8588 | 83.9436 | 5.6997 | 74.4317 | 9.191 | 6.5152 | 39.5595 | 84.7006 | 14.3561 | 191.411 | 85.8957 | 215.8048 | 11.131 | 58.0722 | 2.7673 | 108 | 29.9423 | 0 | 310.3715 | 0
9390 | 833.3903 | 4.1393 | 36.9278 | 91.3442 | 83.9416 | 5.7 | 73.9885 | 11.5108 | 6.4257 | 39.7606 | 86.5142 | 14.9105 | 201.4696 | 89.5302 | 220.4506 | 11.2728 | 59.8994 | 3.4211 | 107 | 30.7898 | 0 | 356.8414 | 0
9391 | 853.4003 | 5.4311 | 47.3813 | 96.5058 | 81.9389 | 7.5995 | 91.9372 | 13.6601 | 12.1696 | 60.9042 | 99.3718 | 17.9085 | 237.644 | 157.6412 | 240.4148 | 13.714 | 57.315 | 5.4946 | 162 | 41.8207 | 0 | 402.5062 | 0
9392 | 916.0622 | 10.7338 | 76.7792 | 100.5343 | 76.938 | 12.3487 | 114.3465 | 14.3017 | 14.1914 | 92.6791 | 151.8061 | 29.6665 | 287.4185 | 236.1195 | 335.501 | 29.8803 | 60.583 | 7.3929 | 256 | 50.943 | 0 | 444.42 | 0
9393 | 981.2521 | 12.2926 | 91.8111 | 114.8882 | 71.9367 | 17.0987 | 125.7449 | 12.5239 | 18.3703 | 101.3588 | 182.3503 | 35.0806 | 338.3313 | 291.3207 | 439.3892 | 38.4461 | 71.6619 | 13.4869 | 306 | 58.2828 | 0 | 522.337 | 0
9394 | 1094.9999 | 9.5074 | 97.2688 | 128.2367 | 70.9352 | 18.0497 | 139.4449 | 12.2162 | 23.1649 | 104.6969 | 192.6025 | 38.366 | 391.1206 | 331.0835 | 530.529 | 42.7146 | 83.2605 | 16.4987 | 376 | 62.6504 | 0 | 564.0809 | 0.016863
9395 | 1139.3856 | 8.2731 | 96.7381 | 133.4998 | 73.9363 | 15.2008 | 144.3265 | 14.5312 | 28.4427 | 107.2308 | 196.1635 | 42.3365 | 418.1298 | 354.6083 | 577.0158 | 44.0552 | 97.9676 | 16.9358 | 371 | 65.2548 | 0 | 579.9339 | 0.024251
9396 | 1147.85 | 7.459 | 101.4497 | 137.348 | 73.9346 | 15.2 | 144.2043 | 15.7306 | 26.5101 | 104.9777 | 193.6465 | 42.6639 | 439.4606 | 377.2188 | 595.7401 | 44.1486 | 100.7614 | 16.7912 | 342 | 74.9254 | 0 | 570.6337 | 0.036495
9397 | 1122.7255 | 6.1176 | 101.6836 | 133.7476 | 74.9303 | 14.2503 | 156.0016 | 10.9504 | 22.1123 | 98.0616 | 190.7079 | 40.5769 | 434.2697 | 365.4203 | 598.8716 | 45.0318 | 110.4019 | 18.667 | 340 | 69.5454 | 0 | 577.8209 | 0.079171
9398 | 1131.4712 | 5.2135 | 99.909 | 142.0752 | 71.9336 | 17.0992 | 165.3026 | 13.1871 | 23.6942 | 100.7132 | 194.605 | 41.0026 | 431.5786 | 368.2326 | 590.7274 | 45.7908 | 114.3178 | 20.0051 | 285 | 70.6389 | 0 | 616.1286 | 0.044026
9399 | 1144.6985 | 4.8622 | 100.2361 | 142.9196 | 70.9339 | 18.0497 | 154.1036 | 15.3759 | 23.6119 | 102.3875 | 193.4124 | 40.9208 | 431.0555 | 370.3921 | 581.4003 | 45.8291 | 118.3617 | 20.4189 | 258 | 72.7193 | 0 | 617.7557 | 0.024529
9400 | 1112.8176 | 4.9281 | 98.2534 | 137.0395 | 71.932 | 17.1003 | 149.4426 | 15.4542 | 19.2431 | 92.2145 | 193.1266 | 40.1315 | 422.0801 | 363.7477 | 569.9611 | 42.9642 | 120.7918 | 20.2314 | 240 | 69.1223 | 0 | 591.7612 | 0.0087681
9401 | 1067.8335 | 5.9089 | 91.4997 | 128.9178 | 79.928 | 9.5021 | 136.6941 | 15.5912 | 16.9921 | 80.6659 | 190.3585 | 39.6254 | 443.4924 | 342.0501 | 513.1936 | 33.2397 | 117.0327 | 19.726 | 235 | 59.4162 | 0 | 503.1921 | 0
9402 | 1014.4046 | 6.6533 | 82.108 | 114.6958 | 80.9309 | 8.5503 | 120.7249 | 14.8373 | 18.6148 | 71.3624 | 172.2526 | 37.112 | 471.1381 | 270.3135 | 430.0388 | 19.0271 | 115.8263 | 18.4864 | 214 | 57.509 | 0 | 396.0205 | 0
9403 | 952.3092 | 5.9102 | 74.3016 | 104.5154 | 83.9314 | 5.7008 | 110.6456 | 14.0831 | 17.5942 | 58.9368 | 143.0808 | 27.4046 | 453.719 | 193.8465 | 373.9838 | 12.5031 | 114.3983 | 17.0344 | 200 | 47.2552 | 0 | 338.2377 | 0
9404 | 919.0036 | 5.4913 | 60.2931 | 102.3789 | 83.9352 | 5.7 | 94.9556 | 13.8922 | 13.1318 | 51.3569 | 128.3933 | 15.3402 | 424.7038 | 158.6103 | 338.0998 | 11.7893 | 108.9139 | 10.5577 | 182 | 39.8743 | 0 | 288.4275 | 0
9405 | 874.5338 | 5.5534 | 35.7119 | 98.3045 | 84.9395 | 4.7503 | 82.4439 | 13.8709 | 10.2612 | 47.1923 | 122.3558 | 10.8081 | 364.6824 | 142.94 | 290.1793 | 11.156 | 98.4843 | 5.0866 | 168 | 37.3604 | 0 | 269.1039 | 0
9406 | 836.9885 | 5.0349 | 24.7727 | 93.5203 | 83.9379 | 5.6997 | 78.4884 | 14.0206 | 8.214 | 41.0035 | 106.0764 | 10.7625 | 264.9676 | 123.5092 | 243.8653 | 10.9112 | 79.6768 | 4.0815 | 157 | 35.2597 | 0 | 265.23 | 0
9407 | 824.2783 | 4.337 | 24.6974 | 91.6123 | 83.9405 | 5.7 | 72.7596 | 14.034 | 6.708 | 34.7332 | 91.3997 | 10.7679 | 211.1039 | 102.7207 | 234.2493 | 10.8775 | 63.341 | 3.6305 | 133 | 33.8688 | 0 | 269.8307 | 0
9408 | 801.0803 | 3.3388 | 24.6074 | 92.0374 | 83.942 | 5.7 | 73.8376 | 13.944 | 6.2131 | 31.9952 | 86.2714 | 10.7518 | 200.6337 | 94.5223 | 245.0686 | 10.8934 | 57.7722 | 3.2896 | 116 | 33.1754 | 0 | 266.3025 | 0
9409 | 791.5843 | 2.7917 | 24.5061 | 92.0902 | 84.94 | 4.7503 | 76.1176 | 13.9038 | 6.2564 | 32.8692 | 82.7914 | 10.5778 | 196.6995 | 92.4589 | 240.261 | 10.7129 | 57.1647 | 3.42 | 111 | 32.3033 | 0 | 269.3463 | 0
9410 | 783.704 | 2.7606 | 24.5994 | 91.7345 | 83.9422 | 5.6997 | 71.2081 | 13.8752 | 6.3276 | 34.3651 | 79.9849 | 10.5361 | 196.0372 | 92.1965 | 225.071 | 10.7069 | 57.2731 | 3.6957 | 108 | 31.4722 | 0 | 271.3384 | 0
9411 | 766.0477 | 2.8353 | 24.6884 | 91.6508 | 83.9406 | 5.7 | 71.1784 | 14.0814 | 6.3424 | 34.9829 | 79.3722 | 10.5206 | 195.127 | 89.8828 | 221.0876 | 10.8797 | 57.2891 | 3.8881 | 106 | 31.0251 | 0 | 263.8821 | 0
9412 | 766.424 | 2.7099 | 24.6153 | 91.5074 | 84.9403 | 4.7503 | 74.8616 | 14.0427 | 6.3005 | 35.7935 | 79.1918 | 10.4742 | 193.5168 | 88.192 | 227.5025 | 10.8126 | 57.3039 | 3.7368 | 106 | 30.2731 | 0 | 263.0893 | 0
9413 | 772.5492 | 3.2013 | 24.5586 | 91.2568 | 83.9426 | 5.6997 | 71.2269 | 13.851 | 6.274 | 36.2399 | 79.4058 | 10.4553 | 195.976 | 88.799 | 229.3067 | 10.8029 | 58.9873 | 3.5895 | 108 | 30.032 | 0 | 292.0704 | 0
9414 | 794.7338 | 4.1534 | 32.4246 | 91.7256 | 83.9411 | 5.7 | 75.3865 | 13.817 | 7.4439 | 39.6123 | 80.3979 | 11.9853 | 207.5591 | 93.3385 | 232.434 | 10.5712 | 60.0925 | 3.7416 | 107 | 31.7318 | 0 | 327.6653 | 0
9415 | 841.2204 | 5.5179 | 49.3681 | 93.5927 | 81.9377 | 7.5995 | 93.3901 | 13.7066 | 9.2654 | 57.5557 | 94.2625 | 20.8111 | 238.2903 | 149.9077 | 253.5648 | 14.5453 | 58.2171 | 3.4106 | 173 | 39.7529 | 0 | 375.6252 | 0
9416 | 894.8745 | 9.8845 | 77.714 | 99.749 | 76.937 | 12.3487 | 112.4845 | 14.9165 | 8.0966 | 90.706 | 131.4172 | 33.8809 | 285.6674 | 224.9509 | 361.1129 | 27.0616 | 63.3489 | 5.7598 | 250 | 49.4099 | 0 | 431.3082 | 0
9417 | 963.5942 | 10.2341 | 92.828 | 109.1469 | 74.9346 | 14.2495 | 131.4662 | 16.0402 | 7.3249 | 101.8831 | 164.7484 | 36.4389 | 340.6856 | 286.9755 | 470.5207 | 36.7823 | 73.7406 | 12.5523 | 290 | 56.534 | 0 | 511.6982 | 0
9418 | 1027.1826 | 6.4087 | 96.9283 | 120.2333 | 72.9338 | 16.1495 | 147.4648 | 16.3258 | 13.8753 | 91.3076 | 185.2696 | 34.0792 | 389.0566 | 331.6008 | 518.0572 | 41.9874 | 83.8298 | 17.3375 | 343 | 59.6725 | 0 | 550.2624 | 0.015919
9419 | 1072.1656 | 4.9138 | 101.1107 | 128.4317 | 71.9381 | 17.0997 | 149.9225 | 16.6673 | 23.154 | 86.8162 | 197.2071 | 35.4657 | 410.6372 | 350.2584 | 554.2031 | 43.8783 | 93.7103 | 18.5558 | 374 | 66.1775 | 0 | 580.2509 | 0.024176
9420 | 1098.4368 | 4.8461 | 101.1423 | 128.5062 | 73.938 | 15.2005 | 151.0006 | 16.5698 | 23.8026 | 88.5363 | 196.6698 | 34.4678 | 417.1696 | 347.8445 | 573.5554 | 43.3678 | 98.3967 | 18.6251 | 340 | 68.7301 | 0 | 594.9871 | 0.024779
9421 | 1101.0122 | 4.6908 | 96.9929 | 127.7418 | 72.9355 | 16.1497 | 150.2192 | 16.6417 | 18.2138 | 79.6023 | 192.0607 | 34.6956 | 419.3629 | 351.0571 | 560.8978 | 44.3627 | 94.926 | 18.8237 | 361 | 60.3757 | 0 | 576.5548 | 0.16484
9422 | 1117.8709 | 4.8317 | 95.5113 | 128.4148 | 71.9334 | 17.0997 | 147.5048 | 16.6396 | 15.5257 | 78.927 | 191.8467 | 37.4251 | 438.3512 | 353.877 | 559.6334 | 44.2221 | 93.8724 | 19.547 | 313 | 60.6496 | 0 | 576.465 | 0.20095
9423 | 1114.6502 | 5.0406 | 97.3637 | 133.8384 | 73.9249 | 15.2048 | 151.8634 | 13.0315 | 16.512 | 84.8509 | 193.8538 | 39.6092 | 491.0605 | 348.0692 | 566.0678 | 42.0688 | 102.8691 | 20.0615 | 284 | 63.2943 | 0 | 550.4064 | 0.18417
9424 | 1087.591 | 4.8994 | 96.5366 | 135.8865 | 73.9337 | 15.1958 | 145.2154 | 12.4551 | 14.066 | 82.4585 | 194.0215 | 37.1522 | 524.9099 | 326.3432 | 562.1573 | 39.7407 | 113.8899 | 20.0097 | 268 | 59.8252 | 0 | 562.6787 | 0.086559
9425 | 1057.3321 | 5.8009 | 94.6653 | 131.8707 | 79.9301 | 9.5016 | 131.8837 | 14.3023 | 10.34 | 81.8757 | 191.9902 | 31.514 | 507.1822 | 302.9697 | 503.3488 | 34.5843 | 112.5101 | 19.3088 | 253 | 55.3747 | 0 | 472.7584 | 0
9426 | 983.1154 | 6.2099 | 78.2842 | 119.8482 | 81.9345 | 7.6005 | 120.8179 | 14.1465 | 8.496 | 72.6604 | 178.2203 | 30.0481 | 402.9124 | 243.5125 | 435.1119 | 23.9352 | 103.7346 | 17.5281 | 235 | 52.7612 | 0 | 369.1131 | 0
9427 | 931.2908 | 6.0599 | 51.4978 | 107.3483 | 84.9367 | 4.7508 | 99.237 | 13.963 | 7.796 | 64.2804 | 154.5253 | 23.5081 | 301.9973 | 162.1761 | 376.6025 | 19.7362 | 97.2489 | 15.4529 | 199 | 47.8663 | 0 | 317.358 | 0
9428 | 911.916 | 5.5647 | 38.7295 | 101.6725 | 83.9364 | 5.6997 | 86.4409 | 13.8916 | 7.996 | 60.3746 | 136.1573 | 12.6532 | 259.1328 | 124.2653 | 328.2624 | 18.9034 | 87.3216 | 9.5106 | 193 | 41.918 | 0 | 286.9691 | 0
9429 | 870.8373 | 5.0174 | 30.4508 | 100.7131 | 83.9368 | 5.7 | 83.6944 | 13.7514 | 8.1569 | 50.8111 | 113.8541 | 8.4566 | 237.2533 | 116.5077 | 295.7691 | 21.6124 | 78.2781 | 4.8193 | 182 | 37.0578 | 0 | 277.8675 | 0
9430 | 833.1381 | 4.9602 | 26.2031 | 101.1492 | 84.9376 | 4.7503 | 71.7779 | 13.9319 | 7.8362 | 41.8663 | 102.803 | 8.509 | 220.9279 | 109.4557 | 278.8081 | 17.1656 | 74.9312 | 3.6253 | 181 | 35.7739 | 0 | 278.674 | 0
9431 | 830.7644 | 4.3488 | 26.2163 | 100.5138 | 83.9401 | 5.6997 | 69.554 | 14.023 | 7.4529 | 36.1417 | 96.4649 | 8.4177 | 212.973 | 100.7686 | 268.037 | 11.6889 | 72.3707 | 3.3349 | 162 | 35.966 | 0 | 282.1777 | 0
9432 | 813.4545 | 3.3097 | 26.2202 | 99.3879 | 83.9424 | 5.7 | 70.7942 | 13.9526 | 7.348 | 33.7185 | 90.208 | 8.0863 | 208.1543 | 93.126 | 260.1786 | 10.9742 | 61.0786 | 2.9105 | 146 | 38.7348 | 0 | 291.3699 | 0
9433 | 803.7744 | 2.8519 | 26.3807 | 100.7401 | 84.9425 | 4.7503 | 65.7859 | 13.9352 | 7.39 | 33.3311 | 89.969 | 8.1157 | 201.3451 | 89.5894 | 261.6777 | 11.0794 | 55.2627 | 2.6691 | 135 | 36.2566 | 0 | 291.0442 | 0
9434 | 808.319 | 2.8164 | 26.5592 | 100.6048 | 83.9449 | 5.6997 | 67.9579 | 14.0985 | 7.225 | 34.9453 | 90.0306 | 8.1175 | 197.404 | 89.5105 | 265.7809 | 10.8472 | 54.9467 | 2.7365 | 133 | 35.884 | 0 | 286.8352 | 0
9435 | 798.6847 | 2.7521 | 26.4663 | 98.7047 | 83.9467 | 5.7 | 68.0219 | 14.2238 | 7.4082 | 35.086 | 90.4135 | 8.4083 | 195.1879 | 90.2949 | 260.5297 | 10.9311 | 54.4336 | 2.6726 | 133 | 35.0425 | 0 | 281.1889 | 0
9436 | 791.9412 | 2.8097 | 26.4294 | 96.6942 | 83.9484 | 5.7 | 63.733 | 14.1256 | 7.4848 | 33.5481 | 91.1555 | 8.8136 | 194.7141 | 92.3462 | 250.1891 | 11.026 | 54.5929 | 2.6096 | 139 | 34.4487 | 0 | 278.13 | 0
9437 | 796.0655 | 3.3344 | 26.4888 | 96.0307 | 84.948 | 4.7503 | 67.466 | 14.0628 | 7.402 | 33.4048 | 91.5531 | 8.3225 | 193.4703 | 91.7405 | 238.8833 | 10.8724 | 56.6032 | 2.6633 | 136 | 33.8095 | 0 | 277.5249 | 0
9438 | 799.8305 | 4.016 | 29.019 | 96.6455 | 83.9446 | 5.6997 | 69.139 | 14.0145 | 7.47 | 35.4188 | 91.612 | 7.7216 | 191.5992 | 90.0486 | 229.3842 | 10.8316 | 57.4943 | 2.8645 | 115 | 33.4221 | 0 | 282.8959 | 0
9439 | 806.0153 | 4.8142 | 43.6146 | 97.7961 | 83.9425 | 5.7 | 65.1921 | 13.9614 | 7.588 | 36.5373 | 91.2398 | 7.5917 | 191.1266 | 89.9259 | 224.0905 | 10.8967 | 55.4935 | 2.9077 | 117 | 34.6183 | 0 | 283.6587 | 0
9440 | 815.6582 | 4.887 | 53.2424 | 98.9746 | 83.9435 | 5.7 | 70.8572 | 14.1006 | 7.4409 | 35.9637 | 97.5899 | 9.9849 | 196.8881 | 95.1291 | 222.5094 | 12.0954 | 54.4032 | 2.9421 | 117 | 38.7507 | 0 | 281.8068 | 0
9441 | 823.9115 | 3.5992 | 60.6503 | 97.0449 | 80.9442 | 8.5492 | 78.8984 | 13.7769 | 6.7959 | 46.6618 | 108.5229 | 13.7666 | 202.3191 | 95.7503 | 219.4613 | 14.312 | 54.3466 | 3.1736 | 117 | 41.3538 | 0 | 275.9514 | 0
9442 | 823.0739 | 2.6701 | 72.7144 | 93.9823 | 83.9382 | 5.7008 | 78.1737 | 13.3662 | 7.2826 | 63.0995 | 128.2722 | 15.2192 | 210.1759 | 95.9656 | 218.0557 | 27.4153 | 54.3525 | 5.5906 | 155 | 42.5678 | 0 | 276.4065 | 0.033323
9443 | 818.8816 | 2.5305 | 79.2046 | 95.6898 | 83.9375 | 5.7 | 79.946 | 13.3438 | 8.5626 | 69.5968 | 143.0944 | 16.0417 | 222.1449 | 108.2345 | 217.0808 | 37.4947 | 54.9203 | 10.4837 | 164 | 41.6282 | 0 | 294.2733 | 0.057675
9444 | 843.1955 | 2.675 | 80.074 | 98.8566 | 84.9392 | 4.7503 | 82.1292 | 14.6175 | 9.514 | 69.1876 | 134.8422 | 18.3251 | 232.688 | 121.0587 | 228.3772 | 36.2637 | 56.6918 | 12.8043 | 160 | 38.6584 | 0 | 297.6575 | 0.1235
9445 | 849.0653 | 2.8272 | 80.539 | 98.0751 | 83.9377 | 5.6997 | 79.0474 | 14.8647 | 9.754 | 65.4502 | 128.8366 | 18.5178 | 237.7956 | 125.7816 | 238.123 | 34.6872 | 58.2984 | 12.9324 | 215 | 37.7397 | 0 | 289.6962 | 0.17009
9446 | 855.0901 | 3.0214 | 71.541 | 94.9555 | 83.9399 | 5.7 | 82.1691 | 13.9839 | 8.862 | 60.7356 | 133.4554 | 17.8704 | 237.5123 | 141.8933 | 236.7861 | 32.1869 | 57.5819 | 13.1132 | 192 | 38.9164 | 0 | 290.9489 | 0.21247
9447 | 868.8544 | 3.7648 | 49.7471 | 93.7599 | 84.9401 | 4.7503 | 83.7221 | 9.3355 | 7.362 | 58.6511 | 131.47 | 18.9713 | 234.2946 | 150.0101 | 238.6514 | 19.7581 | 55.9167 | 11.031 | 201 | 43.3149 | 0 | 290.0972 | 0.10661
9448 | 884.4847 | 3.8486 | 37.5223 | 93.8537 | 84.9373 | 4.75 | 70.9987 | 10.25 | 6.592 | 58.0651 | 126.703 | 16.2703 | 234.1808 | 137.5483 | 244.7913 | 11.5618 | 56.2009 | 6.7886 | 201 | 41.8284 | 0 | 293.0925 | 0.015271
9449 | 890.9493 | 3.9463 | 29.2941 | 95.5948 | 83.9376 | 5.6997 | 66.342 | 13.5709 | 7.01 | 44.5547 | 127.0708 | 9.6435 | 241.7129 | 122.7879 | 245.4706 | 10.1988 | 56.1497 | 5.5711 | 209 | 42.764 | 0 | 290.5249 | 0
9450 | 869.0649 | 4.6025 | 25.1559 | 101.3046 | 83.9349 | 5.7 | 70.5793 | 13.7113 | 7.698 | 36.5532 | 124.1655 | 7.4325 | 240.6009 | 123.2092 | 240.5776 | 10.184 | 56.4208 | 5.9283 | 205 | 42.6863 | 0 | 298.3832 | 0
9451 | 854.9372 | 4.8414 | 25.2257 | 102.9334 | 81.9357 | 7.5995 | 67.2895 | 13.721 | 8.488 | 37.1078 | 112.1945 | 8.0226 | 234.8217 | 123.986 | 241.6427 | 10.3059 | 56.0943 | 5.6867 | 195 | 41.5587 | 0 | 293.4978 | 0
9452 | 846.346 | 4.9975 | 25.3316 | 102.2048 | 83.9372 | 5.7005 | 65.3558 | 14.0278 | 8.866 | 37.0189 | 98.8187 | 8.2071 | 229.5148 | 118.5779 | 237.0118 | 10.2835 | 55.2954 | 5.4959 | 197 | 39.9043 | 0 | 297.8419 | 0
9453 | 830.8873 | 4.9917 | 25.5015 | 99.9478 | 84.9402 | 4.7503 | 68.8943 | 14.0092 | 8.132 | 36.1545 | 90.9161 | 7.9989 | 218.5875 | 117.6569 | 235.518 | 10.1374 | 56.2691 | 5.0134 | 190 | 37.2161 | 0 | 305.0092 | 0
9454 | 831.618 | 4.7521 | 25.5428 | 98.0651 | 83.9395 | 5.6997 | 66.4832 | 13.8737 | 7.694 | 37.7379 | 89.3041 | 7.9214 | 202.6296 | 112.1328 | 239.8286 | 9.9091 | 55.7431 | 4.6617 | 188 | 36.3906 | 0 | 296.7886 | 0
9455 | 831.3829 | 4.2395 | 25.4223 | 97.2742 | 83.9382 | 5.7 | 64.6671 | 13.8928 | 7.4946 | 38.2775 | 87.9497 | 7.8705 | 193.8842 | 111.6288 | 231.6739 | 10.0795 | 54.6662 | 4.4139 | 174 | 38.1364 | 0 | 294.9719 | 0
9456 | 813.6602 | 3.3544 | 25.4874 | 98.2193 | 83.9425 | 5.7 | 67.5395 | 14.1548 | 7.5777 | 38.3283 | 85.1213 | 7.7855 | 193.9178 | 106.0468 | 226.7474 | 10.2424 | 54.3193 | 3.981 | 150 | 38.5258 | 0 | 302.673 | 0
9457 | 820.9142 | 2.9138 | 25.5817 | 99.113 | 84.9424 | 4.7503 | 64.5337 | 14.1551 | 7.5937 | 37.2816 | 83.834 | 8.0595 | 195.6417 | 99.4564 | 223.6329 | 10.1957 | 54.3425 | 3.6831 | 147 | 36.9296 | 0 | 307.9334 | 0
9458 | 820.4949 | 2.9675 | 25.8466 | 99.7475 | 83.9428 | 5.6997 | 63.5092 | 14.0547 | 7.292 | 35.8681 | 83.7305 | 8.1361 | 193.9881 | 92.9802 | 229.5044 | 10.2032 | 54.4927 | 3.4439 | 146 | 34.5349 | 0 | 315.7985 | 0
9459 | 809.9335 | 3.0668 | 25.9219 | 101.429 | 76.9472 | 12.3482 | 66.5202 | 14.0397 | 7.202 | 37.0338 | 83.9346 | 8.0069 | 188.6914 | 90.6727 | 237.2159 | 10.0268 | 54.5742 | 2.6567 | 135 | 33.9201 | 0 | 322.4186 | 0
9460 | 815.3172 | 2.9363 | 25.731 | 99.1114 | 79.9448 | 9.5008 | 64.1958 | 14.0312 | 7.284 | 36.9187 | 84.5189 | 8.8456 | 185.803 | 90.3668 | 237.0854 | 9.9655 | 54.8824 | 2.1703 | 131 | 35.8718 | 0 | 323.1205 | 0
9461 | 804.5276 | 3.4014 | 25.7634 | 96.4472 | 78.9449 | 10.4497 | 64.3921 | 14.0581 | 7.152 | 38.1514 | 84.8939 | 8.6634 | 185.0052 | 88.1892 | 227.9123 | 10.0689 | 56.809 | 2.1745 | 121 | 41.8663 | 0 | 318.0288 | 0
9462 | 803.9661 | 4.3564 | 25.7039 | 96.569 | 84.942 | 4.7516 | 69.2413 | 14.2658 | 7.094 | 38.9167 | 85.1614 | 7.9131 | 183.436 | 87.859 | 219.6454 | 10.1424 | 57.9937 | 2.1919 | 115 | 42.48 | 0 | 310.2222 | 0
9463 | 819.4294 | 4.7116 | 25.5412 | 98.2952 | 83.9422 | 5.6997 | 66.5045 | 14.1359 | 7.22 | 37.6112 | 85.7984 | 7.7645 | 182.9035 | 88.5481 | 217.2517 | 9.8982 | 55.4493 | 2.2112 | 113 | 37.5869 | 0 | 308.893 | 0
9464 | 819.6543 | 4.6619 | 25.4972 | 99.2501 | 82.9391 | 6.6497 | 63.9425 | 13.8441 | 7.43 | 35.9638 | 86.5939 | 7.695 | 188.3977 | 88.1755 | 217.4518 | 9.7194 | 53.7233 | 2.4764 | 113 | 35.2681 | 0 | 304.6688 | 0
9465 | 809.692 | 3.405 | 26.0861 | 96.6554 | 82.9374 | 6.65 | 69.009 | 13.5486 | 7.464 | 43.0923 | 85.1613 | 6.1785 | 192.543 | 89.1097 | 216.636 | 9.6006 | 53.1848 | 2.9367 | 112 | 37.3402 | 0 | 291.0695 | 0
9466 | 835.4095 | 2.5922 | 32.1938 | 97.5294 | 82.937 | 6.65 | 70.0789 | 13.3437 | 12.124 | 60.1008 | 86.9949 | 5.1224 | 204.133 | 91.4303 | 213.9627 | 9.5965 | 53.0798 | 3.2789 | 135 | 37.995 | 0 | 279.8221 | 0.013927
9467 | 864.5836 | 2.8096 | 38.6913 | 99.5915 | 82.9341 | 6.65 | 72.4445 | 13.3019 | 17.942 | 68.2427 | 100.1185 | 4.7583 | 217.0162 | 101.023 | 224.2009 | 9.6459 | 53.5342 | 3.8939 | 164 | 38.7703 | 0 | 282.1508 | 0.020487
9468 | 871.6572 | 2.9024 | 40.2048 | 99.4346 | 83.9347 | 5.7003 | 81.3101 | 13.357 | 16.172 | 68.4341 | 113.7792 | 4.4297 | 221.4143 | 107.0512 | 248.762 | 9.5289 | 54.0583 | 4.2745 | 187 | 40.7881 | 0 | 297.3828 | 0.022209
9469 | 864.957 | 2.6446 | 39.7641 | 102.6691 | 84.9352 | 4.7503 | 82.5307 | 13.2843 | 18.084 | 67.7014 | 123.2791 | 6.8059 | 225.7212 | 114.4012 | 270.1538 | 9.3585 | 56.0968 | 4.3402 | 197 | 40.9441 | 0 | 296.8012 | 0.016601
9470 | 865.0532 | 2.5655 | 39.6871 | 108.844 | 83.9372 | 5.6997 | 75.7642 | 13.2653 | 19.4534 | 65.6896 | 129.2574 | 9.9335 | 234.4308 | 130.0684 | 287.4107 | 9.514 | 56.6974 | 4.8343 | 192 | 43.2401 | 0 | 294.9719 | 0.060187
9471 | 882.06 | 2.7695 | 39.7417 | 109.5489 | 83.9409 | 5.7 | 79.3917 | 10.1582 | 17.8543 | 64.2054 | 131.4237 | 9.1766 | 239.0665 | 150.4386 | 293.8802 | 9.5479 | 54.765 | 5.2067 | 191 | 44.6761 | 0 | 298.587 | 0.031638
9472 | 902.2516 | 2.9789 | 38.0829 | 103.1368 | 84.94 | 4.7503 | 86.4211 | 10.0386 | 18.5177 | 59.5453 | 130.3517 | 7.821 | 237.877 | 159.9084 | 282.71 | 9.5857 | 54.638 | 5.1496 | 175 | 42.5663 | 0 | 295.2118 | 0.0066413
9473 | 889.7776 | 3.873 | 29.8358 | 99.1063 | 83.9384 | 5.6997 | 74.1166 | 12.7994 | 17.783 | 50.8814 | 129.9161 | 7.4241 | 269.1805 | 164.2059 | 285.6371 | 9.5126 | 56.1836 | 4.9963 | 162 | 43.1118 | 0 | 286.0151 | 0
9474 | 877.2119 | 4.579 | 25.7473 | 97.734 | 84.9409 | 4.7503 | 69.67 | 14.0978 | 19.4809 | 44.6467 | 132.4972 | 8.1586 | 330.7756 | 158.7964 | 310.5191 | 9.6646 | 56.4061 | 5.0111 | 165 | 40.9736 | 0 | 286.7904 | 0
9475 | 880.8152 | 4.7929 | 25.857 | 97.1675 | 83.9442 | 5.6997 | 79.454 | 10.3702 | 19.1148 | 40.1394 | 134.041 | 8.4561 | 359.4068 | 140.4366 | 315.689 | 10.0023 | 55.6442 | 5.0929 | 152 | 38.2954 | 0 | 287.4823 | 0
9476 | 864.8851 | 4.944 | 25.6036 | 97.1912 | 83.9417 | 5.7 | 74.7327 | 10.6663 | 12.768 | 37.598 | 124.4015 | 8.0555 | 354.1391 | 118.4764 | 285.7864 | 9.9578 | 56.6112 | 4.8627 | 133 | 36.4911 | 0 | 285.4833 | 0
9477 | 838.2309 | 4.9292 | 25.3022 | 97.347 | 84.939 | 4.7503 | 66.6841 | 13.5188 | 15.242 | 38.5635 | 101.0989 | 7.9847 | 321.8585 | 105.5277 | 259.9079 | 9.932 | 55.1154 | 4.425 | 128 | 37.0025 | 0 | 284.2036 | 0
9478 | 828.5849 | 4.9648 | 25.1809 | 96.6386 | 83.94 | 5.6997 | 72.4216 | 13.8738 | 18.202 | 38.0502 | 88.4546 | 9.1255 | 247.7733 | 102.9459 | 256.1092 | 9.9282 | 53.7668 | 3.8995 | 118 | 35.0972 | 0 | 280.8852 | 0
9479 | 805.7343 | 4.3723 | 25.0583 | 95.9335 | 84.9374 | 4.7516 | 74.2179 | 13.7669 | 12.058 | 36.0822 | 86.5689 | 10.2438 | 207.8824 | 100.5752 | 256.0593 | 9.7643 | 53.7011 | 3.6133 | 114 | 32.1124 | 0 | 272.3048 | 0
9480 | 786.7966 | 3.1147 | 24.9692 | 95.7638 | 83.9386 | 5.6984 | 66.5551 | 10.6802 | 7.19 | 35.1669 | 84.8449 | 10.1511 | 203.1229 | 94.1534 | 245.7853 | 9.8922 | 53.4721 | 3.6117 | 111 | 31.5994 | 0 | 270.7968 | 0
9481 | 787.4493 | 2.6919 | 24.9324 | 96.195 | 84.9399 | 4.7503 | 66.9441 | 10.5654 | 6.496 | 32.9534 | 84.1939 | 8.7449 | 196.575 | 87.8954 | 236.8144 | 9.9701 | 53.5226 | 3.7034 | 109 | 31.6883 | 0 | 272.9516 | 0
9482 | 780.2477 | 2.6637 | 25.0072 | 96.4307 | 84.9394 | 4.75 | 74.8554 | 13.0297 | 6.354 | 31.4528 | 83.8681 | 8.1501 | 191.0843 | 86.3522 | 230.4403 | 9.9369 | 53.4083 | 3.0359 | 109 | 31.8313 | 0 | 270.3525 | 0
9483 | 763.6153 | 2.4636 | 25.0316 | 96.3889 | 83.9374 | 5.6997 | 70.6671 | 13.7463 | 6.2395 | 31.45 | 83.9635 | 7.9326 | 188.6108 | 91.6304 | 229.6371 | 9.9971 | 53.5445 | 2.4724 | 107 | 31.7281 | 0 | 271.3266 | 0
9484 | 767.129 | 2.4092 | 25.9534 | 96.5173 | 83.9415 | 5.7 | 64.3343 | 10.4283 | 6.3635 | 31.476 | 84.2325 | 7.6802 | 183.8911 | 97.3006 | 229.0047 | 9.7495 | 53.6514 | 2.4645 | 107 | 31.1493 | 0 | 277.1635 | 0
9485 | 774.1163 | 2.9516 | 27.3319 | 97.3786 | 84.9398 | 4.7503 | 72.0127 | 10.4273 | 6.389 | 31.4549 | 84.4775 | 7.6754 | 185.3201 | 92.2875 | 225.2303 | 9.8718 | 55.1979 | 2.4623 | 108 | 30.893 | 0 | 310.3588 | 0
9486 | 797.2231 | 4.0371 | 34.2496 | 98.3077 | 83.9386 | 5.6997 | 82.7592 | 13.2592 | 6.4882 | 32.0156 | 85.1267 | 12.8431 | 193.7045 | 94.5997 | 228.1065 | 9.9547 | 56.722 | 2.7495 | 107 | 33.7503 | 0 | 330.9469 | 0
9487 | 833.0956 | 5.7151 | 54.8697 | 102.3803 | 82.9375 | 6.6497 | 89.8069 | 13.7738 | 10.2757 | 55.5869 | 103.5278 | 19.1432 | 230.591 | 169.5707 | 255.4323 | 14.2165 | 55.1319 | 4.2644 | 171 | 40.8124 | 0 | 371.6991 | 0
9488 | 905.679 | 11.6723 | 78.3376 | 109.0024 | 78.0662 | 11.3987 | 110.8344 | 14.49 | 14.7541 | 86.3048 | 144.106 | 32.7062 | 284.3047 | 247.162 | 357.4964 | 28.0554 | 61.5408 | 10.787 | 292 | 51.4818 | 0 | 432.0956 | 0
9489 | 996.1404 | 18.4163 | 91.7855 | 117.8504 | 77.0534 | 12.3532 | 137.1875 | 12.2247 | 18.7913 | 95.6611 | 175.3777 | 42.4553 | 329.2083 | 302.968 | 491.926 | 36.8582 | 72.0757 | 16.1293 | 293 | 60.1008 | 0 | 495.7191 | 0
9490 | 1071.8998 | 17.504 | 97.8143 | 127.1204 | 73.9448 | 15.1958 | 146.7833 | 12.4357 | 21.5013 | 97.8783 | 187.0435 | 44.8686 | 378.0898 | 353.3407 | 579.5514 | 41.7662 | 84.3691 | 19.2776 | 318 | 63.6546 | 0 | 547.3759 | 0.05018
9491 | 1099.925 | 13.5614 | 98.589 | 135.7211 | 75.9349 | 13.3005 | 151.7709 | 15.5058 | 21.3744 | 95.1375 | 192.6116 | 45.9578 | 396.2081 | 380.1343 | 622.3827 | 43.1527 | 97.5865 | 19.1904 | 316 | 66.2621 | 0 | 546.5463 | 0.045495
9492 | 1110.3338 | 10.0697 | 103.3432 | 139.1701 | 74.9382 | 14.2497 | 159.3689 | 12.1712 | 21.3346 | 96.5901 | 195.6266 | 44.1056 | 404.8483 | 392.9026 | 630.997 | 41.8107 | 103.4268 | 18.0564 | 308 | 76.0542 | 0 | 592.7024 | 0.082506
9493 | 1114.42 | 7.9093 | 103.1936 | 132.3435 | 73.9412 | 15.1997 | 155.6803 | 13.188 | 21.9563 | 100.6656 | 196.5109 | 43.3919 | 399.8443 | 388.4366 | 610.1559 | 43.8863 | 99.5927 | 18.9226 | 338 | 72.0348 | 0 | 600.889 | 0.046818
9494 | 1142.6462 | 6.6261 | 102.2577 | 137.6175 | 72.9422 | 16.1497 | 159.7195 | 14.0059 | 25.634 | 98.1842 | 197.7536 | 43.6708 | 407.4719 | 385.6529 | 593.8905 | 45.2 | 98.8622 | 19.2641 | 315 | 69.033 | 0 | 595.2212 | 0.018793
9495 | 1163.1168 | 12.7043 | 102.5678 | 142.8415 | 71.9395 | 17.0997 | 168.1761 | 12.9271 | 26.108 | 97.418 | 201.4628 | 42.199 | 422.8548 | 376.931 | 573.4012 | 43.4944 | 100.9489 | 18.832 | 267 | 72.773 | 0 | 568.1025 | 0.058405
9496 | 1130.7377 | 22.7019 | 100.784 | 140.97 | 71.9375 | 17.1 | 155.9322 | 14.9719 | 21.8592 | 101.4608 | 199.6747 | 41.1551 | 425.8829 | 358.7161 | 555.2736 | 43.1912 | 105.3148 | 19.1609 | 259 | 69.4521 | 0 | 560.4944 | 0.029571
9497 | 1110.0232 | 22.8287 | 96.5719 | 134.8805 | 81.9315 | 7.6026 | 145.5542 | 14.8552 | 18.8095 | 102.5541 | 193.0342 | 41.1291 | 405.4197 | 329.9312 | 529.4566 | 36.5468 | 101.3874 | 19.6416 | 232 | 62.3868 | 0 | 531.0937 | 0
9498 | 1027.6855 | 21.3411 | 91.2236 | 114.6132 | 82.9371 | 6.6503 | 134.1729 | 11.4481 | 18.0146 | 90.2379 | 177.1475 | 35.9049 | 364.9759 | 288.3196 | 451.8873 | 22.2601 | 90.8524 | 19.3306 | 225 | 57.3657 | 0 | 415.1717 | 0
9499 | 959.8032 | 20.9161 | 83.5281 | 100.7685 | 82.9403 | 6.65 | 118.2918 | 10.9617 | 15.8089 | 66.0403 | 149.7193 | 27.3268 | 320.2557 | 217.7756 | 373.6136 | 18.0498 | 82.4578 | 18.1 | 219 | 50.2168 | 0 | 358.5679 | 0
9500 | 928.031 | 16.7771 | 65.8424 | 98.6792 | 83.9387 | 5.7018 | 110.2115 | 13.1983 | 10.1352 | 56.2617 | 136.5725 | 14.0248 | 282.5405 | 170.0009 | 331.1673 | 14.6684 | 69.7558 | 11.4292 | 196 | 45.6238 | 0 | 308.9783 | 0
9501 | 882.702 | 8.0944 | 42.0313 | 95.1415 | 80.946 | 8.5476 | 88.274 | 13.9106 | 7.8602 | 55.4693 | 128.5058 | 9.6043 | 257.1721 | 137.6961 | 308.4424 | 12.2891 | 64.3109 | 6.5432 | 183 | 42.4243 | 0 | 287.249 | 0
9502 | 857.06 | 5.313 | 35.0483 | 94.9405 | 84.9463 | 4.7511 | 69.6453 | 13.9672 | 7.237 | 45.6676 | 112.2533 | 9.6343 | 231.3465 | 117.3964 | 273.506 | 11.7911 | 62.948 | 4.4234 | 165 | 38.181 | 0 | 283.3342 | 0
9503 | 835.5738 | 4.7635 | 35.0972 | 96.4068 | 83.9486 | 5.6997 | 71.3411 | 14.3024 | 6.8685 | 39.3088 | 95.0192 | 9.0535 | 217.1898 | 104.2103 | 251.3739 | 11.8053 | 59.6598 | 3.8028 | 145 | 36.9803 | 0 | 288.1745 | 0
9504 | 816.4605 | 3.5748 | 35.8067 | 95.1674 | 83.9449 | 5.7 | 68.2928 | 14.0294 | 6.603 | 38.9859 | 86.8817 | 8.1107 | 208.0389 | 98.5985 | 236.4114 | 11.4714 | 58.3232 | 3.6968 | 126 | 35.4235 | 0 | 297.6099 | 0
9505 | 797.7655 | 2.9343 | 36.0402 | 92.6121 | 82.9438 | 6.6497 | 64.9788 | 13.857 | 6.6899 | 38.3855 | 83.5598 | 7.6326 | 203.8958 | 94.1122 | 231.4208 | 11.503 | 58.1727 | 3.2544 | 112 | 35.3589 | 0 | 301.5376 | 0
9506 | 787.4716 | 2.7237 | 36.7634 | 91.462 | 82.9455 | 6.65 | 70.7033 | 13.9126 | 6.9829 | 37.7705 | 85.6196 | 7.9417 | 206.0274 | 90.714 | 233.2635 | 11.5834 | 57.8306 | 2.9311 | 105 | 32.212 | 0 | 303.8198 | 0
9507 | 777.0818 | 3.0643 | 36.3554 | 91.9827 | 83.9434 | 5.7003 | 67.2849 | 14.0899 | 7.0843 | 38.0483 | 87.6235 | 8.1474 | 200.6733 | 88.2821 | 231.1219 | 11.6074 | 57.5331 | 2.645 | 106 | 32.2901 | 0 | 302.7543 | 0
9508 | 779.7808 | 2.8778 | 36.3558 | 92.7571 | 83.9382 | 5.7 | 62.8609 | 13.9367 | 7.0542 | 37.8557 | 87.2509 | 7.7114 | 194.095 | 86.889 | 233.3143 | 11.5602 | 57.0647 | 2.5512 | 105 | 31.9943 | 0 | 300.007 | 0
9509 | 787.2608 | 3.2318 | 36.3288 | 93.4412 | 83.9398 | 5.7 | 68.655 | 13.8063 | 6.9755 | 38.076 | 85.644 | 7.5124 | 197.9194 | 85.1798 | 235.0599 | 11.3025 | 58.2495 | 2.5828 | 102 | 32.1793 | 0 | 320.8757 | 0
9510 | 795.5127 | 4.1017 | 38.0205 | 92.1179 | 83.941 | 5.7 | 72.89 | 13.7203 | 6.96 | 39.1701 | 82.7438 | 8.8088 | 207.7972 | 88.9167 | 227.9853 | 11.4159 | 60.4143 | 2.5764 | 107 | 32.9799 | 0 | 369.693 | 0
9511 | 840.8186 | 5.9547 | 47.6014 | 94.1783 | 78.9408 | 10.4487 | 85.4356 | 13.6686 | 9.6072 | 62.281 | 92.7691 | 18.062 | 245.1073 | 155.1157 | 243.3901 | 13.8282 | 59.1138 | 2.5693 | 196 | 43.1691 | 0 | 427.258 | 0
9512 | 890.0147 | 10.2828 | 78.2661 | 100.1165 | 75.9394 | 13.2992 | 111.4377 | 14.4727 | 16.4057 | 87.4562 | 136.7191 | 35.0489 | 305.8993 | 238.5875 | 352.3563 | 29.6324 | 65.7081 | 7.8595 | 286 | 53.5317 | 0 | 462.3365 | 0
9513 | 986.5894 | 14.6345 | 94.5686 | 114.9131 | 70.939 | 18.0487 | 128.9483 | 15.2011 | 22.9591 | 90.0128 | 166.1086 | 37.5803 | 368.6111 | 299.5053 | 487.1572 | 38.4707 | 74.4412 | 15.8685 | 273 | 61.1448 | 0 | 523.1942 | 0
9514 | 1077.4747 | 16.0986 | 101.4988 | 129.4243 | 72.9338 | 16.1505 | 144.2439 | 15.6079 | 23.0348 | 92.4356 | 190.382 | 38.9418 | 415.6595 | 346.1954 | 578.4225 | 39.9898 | 95.1514 | 18.9498 | 380 | 68.0169 | 0 | 562.9985 | 0.072319
9515 | 1140.7615 | 17.0239 | 102.187 | 138.1638 | 69.9341 | 18.9992 | 156.3145 | 16.1142 | 20.063 | 98.3724 | 198.6834 | 41.9053 | 427.2673 | 371.7835 | 632.0177 | 41.8566 | 123.8873 | 19.6528 | 367 | 73.8341 | 0 | 588.6618 | 0.096283
9516 | 1158.8115 | 20.6865 | 104.4051 | 142.8631 | 70.9351 | 18.0503 | 149.4279 | 12.2881 | 19.877 | 98.1125 | 197.8662 | 43.0922 | 432.1866 | 384.2268 | 663.6242 | 42.3693 | 130.0706 | 19.7972 | 362 | 80.9893 | 0 | 592.5794 | 0.10018
9517 | 1140.5325 | 19.9296 | 102.5201 | 140.7597 | 73.9387 | 15.2008 | 151.4165 | 14.1382 | 22.2487 | 91.1865 | 198.4882 | 43.324 | 420.8678 | 378.4979 | 655.025 | 42.0476 | 122.6062 | 19.5946 | 356 | 74.7916 | 0 | 576.9762 | 0.047635
9518 | 1133.4864 | 14.2684 | 102.2454 | 143.9521 | 73.9381 | 15.2 | 158.7341 | 15.7522 | 23.8394 | 94.6157 | 199.2159 | 42.7939 | 427.0936 | 376.1236 | 629.1025 | 44.7 | 122.3186 | 19.6798 | 290 | 71.0435 | 0 | 585.04 | 0.028688
9519 | 1130.5481 | 11.8984 | 102.9282 | 142.5202 | 70.9346 | 18.0492 | 157.3748 | 15.7349 | 20.3763 | 99.1949 | 202.018 | 41.4086 | 440.9389 | 381.6238 | 621.3276 | 46.7834 | 121.1689 | 19.9277 | 256 | 75.0373 | 0 | 605.4079 | 0.016152
9520 | 1110.4473 | 13.2069 | 98.5861 | 137.7595 | 69.938 | 18.9997 | 157.4069 | 16.4188 | 18.473 | 93.6251 | 207.0659 | 39.8058 | 423.1888 | 361.2731 | 595.0712 | 43.2146 | 119.8515 | 19.9495 | 266 | 70.5857 | 0 | 607.3786 | 0.0038072
9521 | 1072.5775 | 10.5846 | 93.9814 | 129.8103 | 71.9369 | 17.1005 | 148.8561 | 12.0184 | 18.3328 | 90.0586 | 205.354 | 35.8829 | 405.5718 | 337.7053 | 543.8428 | 34.4488 | 118.4952 | 18.8935 | 228 | 59.3404 | 0 | 566.2779 | 0
9522 | 1044.8882 | 7.4358 | 88.4868 | 119.2263 | 76.9322 | 12.3547 | 126.9773 | 13.549 | 21.009 | 77.1135 | 189.3102 | 36.8817 | 356.1336 | 283.5675 | 466.8549 | 20.0389 | 112.2957 | 17.6719 | 218 | 55.5065 | 0 | 419.5566 | 0
9523 | 1007.1374 | 5.9659 | 82.9239 | 109.9892 | 79.9405 | 9.4974 | 118.6999 | 14.9431 | 19.3252 | 62.9831 | 161.9693 | 29.7983 | 308.6369 | 192.6021 | 388.4759 | 13.9705 | 105.964 | 16.6524 | 201 | 51.0137 | 0 | 370.9303 | 0
9524 | 954.1012 | 6.3899 | 71.8735 | 104.964 | 80.9431 | 8.5503 | 92.6544 | 14.2878 | 11.016 | 54.2808 | 149.9093 | 14.7621 | 268.2149 | 156.8128 | 328.8503 | 11.7722 | 93.8134 | 10.8523 | 176 | 47.013 | 0 | 320.761 | 0
9525 | 904.1995 | 5.4214 | 42.2652 | 97.0656 | 79.9476 | 9.4997 | 87.2701 | 10.687 | 7.429 | 46.7774 | 141.1481 | 9.7082 | 238.2637 | 159.5978 | 280.855 | 10.6302 | 85.7459 | 6.7429 | 167 | 42.5628 | 0 | 303.4238 | 0
9526 | 872.8303 | 5.1244 | 27.159 | 93.1905 | 79.9468 | 9.5 | 89.3363 | 10.4579 | 6.7745 | 38.8486 | 122.4899 | 9.6941 | 214.1562 | 152.3292 | 242.6186 | 10.2559 | 82.445 | 5.5654 | 156 | 37.3967 | 0 | 292.4338 | 0
9527 | 843.8543 | 4.5594 | 25.1679 | 91.6386 | 79.9481 | 9.5 | 76.8492 | 13.2693 | 6.6515 | 32.933 | 98.9464 | 9.5526 | 204.1241 | 127.6172 | 233.5091 | 10.2091 | 82.3358 | 5.0996 | 137 | 35.0229 | 0 | 297.404 | 0
9528 | 818.3985 | 3.1594 | 25.0446 | 91.0711 | 79.9517 | 9.5 | 70.2409 | 14.0352 | 6.7016 | 32.3946 | 88.4838 | 9.5176 | 193.4475 | 115.0497 | 240.6972 | 10.1276 | 81.1699 | 3.8749 | 119 | 34.8091 | 0 | 293.614 | 0
9529 | 810.9483 | 2.7348 | 24.9673 | 91.8163 | 72.308 | 9.5 | 75.7584 | 13.8193 | 6.5304 | 30.3312 | 85.0767 | 8.8039 | 186.0428 | 109.441 | 250.3121 | 9.8948 | 80.1999 | 3.1594 | 109 | 35.1455 | 0 | 297.0112 | 0
9530 | 796.8835 | 2.9237 | 24.8101 | 93.4308 | 72.3069 | 9.5 | 74.7237 | 13.7506 | 6.1279 | 28.9697 | 84.0529 | 8.2658 | 182.8447 | 105.9192 | 250.8749 | 10.0525 | 79.9301 | 2.6684 | 109 | 34.9821 | 0 | 296.9421 | 0
9531 | 783.6428 | 2.8127 | 24.8869 | 92.5438 | 72.3084 | 9.5 | 69.1883 | 13.9865 | 6.0903 | 28.6811 | 84.2611 | 8.5333 | 180.6417 | 106.4708 | 254.6337 | 10.0513 | 79.9543 | 2.4939 | 102 | 34.2417 | 0 | 291.2712 | 0
9532 | 781.4325 | 2.8831 | 24.7636 | 91.9389 | 75.3088 | 6.6508 | 71.8014 | 13.8612 | 5.9293 | 28.672 | 83.632 | 7.8066 | 179.4254 | 107.5446 | 245.9276 | 10.0913 | 79.8066 | 2.5402 | 101 | 33.1606 | 0 | 293.2245 | 0
9533 | 782.0496 | 3.3265 | 24.8484 | 93.0932 | 72.3102 | 9.4992 | 76.5559 | 13.7649 | 6.0005 | 28.8599 | 83.4928 | 7.4246 | 183.2112 | 106.4508 | 235.2282 | 10.1049 | 81.3916 | 2.5533 | 99 | 32.683 | 0 | 317.9228 | 0
9534 | 789.6947 | 4.0444 | 32.359 | 94.3283 | 71.3037 | 10.4497 | 75.8017 | 13.6568 | 6.0313 | 29.2904 | 84.3041 | 9.5098 | 191.8664 | 107.7102 | 228.9313 | 9.7534 | 82.5443 | 2.5077 | 105 | 32.0862 | 0 | 361.7 | 0
9535 | 823.4333 | 5.719 | 46.1885 | 101.3862 | 69.3014 | 12.3495 | 88.0307 | 13.4969 | 9.2235 | 55.6852 | 99.7354 | 18.1315 | 230.1464 | 173.9252 | 246.2217 | 12.8722 | 80.254 | 2.55 | 172 | 38.0333 | 0 | 416.7374 | 0
9536 | 898.264 | 10.7663 | 74.328 | 102.7068 | 65.301 | 16.1489 | 115.0646 | 14.6914 | 13.99 | 89.4085 | 151.2177 | 33.8438 | 298.383 | 241.8173 | 323.1525 | 28.6669 | 85.5303 | 8.017 | 256 | 52.6658 | 0 | 447.8158 | 0
9537 | 968.9422 | 12.4772 | 93.5248 | 115.5055 | 62.2991 | 18.9992 | 135.311 | 16.1424 | 19.3192 | 87.1904 | 178.1862 | 39.5348 | 355.2142 | 294.7734 | 452.6566 | 37.6636 | 93.7392 | 15.0093 | 290 | 58.5484 | 0 | 518.5615 | 0
9538 | 1048.2535 | 9.6713 | 99.8009 | 128.3459 | 66.2976 | 15.2011 | 153.7533 | 16.7516 | 22.5079 | 103.7742 | 186.1068 | 39.5699 | 390.8405 | 343.1725 | 533.7602 | 40.4218 | 88.0392 | 18.0308 | 362 | 67.5918 | 0 | 575.4293 | 0.016367
9539 | 1110.371 | 9.5873 | 103.6001 | 138.2539 | 63.305 | 18.0492 | 164.2833 | 16.9549 | 23.5688 | 114.2893 | 191.5213 | 42.2608 | 404.8571 | 364.2479 | 586.8609 | 41.5501 | 89.4938 | 19.4258 | 362 | 75.2209 | 0 | 596.3863 | 0.024068
9540 | 1178.3226 | 12.1003 | 106.8791 | 140.4555 | 63.3032 | 18.05 | 156.8357 | 16.5177 | 22.2605 | 118.084 | 192.2811 | 43.9554 | 415.7347 | 385.4427 | 631.4255 | 42.6222 | 92.572 | 19.6247 | 356 | 84.6064 | 0 | 612.6802 | 0.027376
9541 | 1171.3518 | 12.6248 | 104.7397 | 133.4554 | 61.3021 | 19.9495 | 156.2638 | 16.573 | 18.5182 | 105.4203 | 195.8403 | 43.7458 | 413.4105 | 385.6011 | 633.0603 | 44.3087 | 90.8655 | 19.4895 | 354 | 81.8383 | 0 | 600.2446 | 0.026641
9542 | 1161.9543 | 12.0014 | 103.8022 | 135.2708 | 65.2992 | 16.1555 | 161.3414 | 13.3377 | 17.4245 | 95.5325 | 197.5851 | 45.2031 | 421.253 | 381.7468 | 634.4644 | 44.3187 | 93.7339 | 19.9054 | 268 | 79.1621 | 0 | 616.5904 | 0.02535
9543 | 1179.8911 | 10.9844 | 106.4563 | 137.2826 | 64.308 | 17.1 | 159.3671 | 13.0455 | 17.4087 | 97.4412 | 198.44 | 43.1938 | 423.6251 | 380.8776 | 630.1322 | 43.2967 | 92.1523 | 20.0818 | 257 | 77.4346 | 0 | 598.8467 | 0.013278
9544 | 1161.8684 | 7.6035 | 100.5649 | 134.2245 | 64.3109 | 17.0953 | 161.0791 | 15.0784 | 17.1758 | 99.4735 | 196.987 | 41.156 | 419.8009 | 372.0537 | 601.9858 | 41.2957 | 88.286 | 19.9153 | 287 | 70.4571 | 0 | 610.5798 | 0.0043589
9545 | 1099.9174 | 6.6522 | 90.4598 | 130.5189 | 69.3033 | 12.3513 | 145.5146 | 16.0466 | 18.9672 | 96.8801 | 196.3461 | 40.1833 | 400.9545 | 349.0997 | 546.874 | 36.8863 | 84.1571 | 19.5767 | 248 | 62.8364 | 0 | 568.2941 | 0
9546 | 1035.2937 | 7.0634 | 78.7806 | 115.2875 | 74.3003 | 7.6034 | 131.088 | 15.0404 | 21.5959 | 80.7082 | 178.9035 | 36.5875 | 350.6692 | 283.5871 | 468.2286 | 25.1375 | 77.6625 | 17.9338 | 240 | 61.2232 | 0 | 422.4185 | 0
9547 | 992.9621 | 8.9931 | 76.7782 | 101.6203 | 76.3092 | 5.6984 | 119.433 | 14.7222 | 20.6622 | 56.1408 | 153.3411 | 28.0421 | 306.5045 | 194.9715 | 394.3518 | 19.835 | 69.5682 | 16.3693 | 209 | 54.3127 | 0 | 369.2912 | 0
9548 | 938.5368 | 9.0426 | 65.4309 | 97.606 | 76.3104 | 5.7 | 106.6047 | 9.6218 | 12.6264 | 47.6139 | 142.2577 | 14.4961 | 271.3498 | 158.6712 | 336.8297 | 17.1011 | 60.1835 | 10.7756 | 197 | 47.2591 | 0 | 325.833 | 0
9549 | 897.1002 | 6.4521 | 36.0805 | 97.0413 | 76.3079 | 5.7 | 104.434 | 12.0377 | 8.569 | 48.0873 | 130.2077 | 10.2028 | 250.9976 | 141.0273 | 304.8079 | 11.9193 | 53.8086 | 6.7319 | 179 | 41.8107 | 0 | 315.3846 | 0
9550 | 863.9163 | 4.9159 | 26.2196 | 97.0801 | 76.3061 | 5.7 | 85.5491 | 13.8137 | 7.2142 | 41.8857 | 110.204 | 10.2009 | 234.0284 | 118.5902 | 278.5617 | 10.3692 | 52.4017 | 5.0661 | 164 | 35.2548 | 0 | 310.4001 | 0
9551 | 837.6411 | 8.7759 | 25.7389 | 97.7941 | 77.3061 | 4.7503 | 73.8422 | 13.8306 | 6.4085 | 33.6037 | 94.1582 | 9.5497 | 218.8209 | 108.6122 | 262.7312 | 10.322 | 51.3365 | 4.4727 | 136 | 34.2014 | 0 | 299.1669 | 0
9552 | 817.7979 | 10.5134 | 25.6164 | 94.5626 | 76.3054 | 5.6997 | 75.1032 | 13.796 | 6.101 | 30.1813 | 89.4211 | 9.1453 | 206.0695 | 104.1304 | 247.7149 | 10.1836 | 51.7971 | 4.0265 | 120 | 33.0026 | 0 | 296.3261 | 0
9553 | 821.0019 | 10.3041 | 25.6084 | 90.9785 | 73.4872 | 4.7503 | 79.4928 | 13.7325 | 6.0776 | 30.017 | 88.6524 | 9.0305 | 197.4893 | 97.76 | 235.5557 | 10.1921 | 51.2075 | 3.7043 | 110 | 32.4994 | 0 | 306.4127 | 0
9554 | 805.0414 | 9.2053 | 25.657 | 93.0617 | 72.4864 | 5.6997 | 71.1566 | 13.9467 | 6.0622 | 29.826 | 86.7465 | 8.9918 | 188.5831 | 92.7264 | 232.9602 | 10.0229 | 50.9684 | 3.1592 | 108 | 31.5287 | 0 | 311.4551 | 0
9555 | 794.3495 | 4.5266 | 25.6159 | 93.3891 | 70.4871 | 7.5995 | 66.8797 | 13.8349 | 6.2079 | 29.9412 | 86.0039 | 8.9902 | 177.6149 | 91.8386 | 240.0528 | 10.0858 | 50.9153 | 2.6811 | 107 | 31.178 | 0 | 321.5291 | 0
9556 | 792.4105 | 2.4605 | 25.6339 | 92.9835 | 72.489 | 5.7005 | 73.8635 | 13.7247 | 6.2127 | 30.3639 | 86.3117 | 8.894 | 173.5899 | 90.4064 | 228.6067 | 10.1362 | 50.8453 | 2.5166 | 104 | 30.7197 | 0 | 333.152 | 0
9557 | 791.2185 | 2.9427 | 25.5236 | 92.3658 | 73.4848 | 4.7503 | 71.2093 | 13.6776 | 6.2258 | 30.339 | 86.0618 | 8.8055 | 175.5258 | 89.2427 | 215.9612 | 10.1386 | 52.242 | 2.4575 | 104 | 30.3355 | 0 | 341.9553 | 0
9558 | 811.214 | 4.2269 | 32.8039 | 92.7614 | 72.4841 | 5.6997 | 73.5984 | 13.5987 | 6.5195 | 32.3642 | 85.0602 | 9.9173 | 183.15 | 92.9257 | 217.2572 | 10.1308 | 54.0377 | 2.459 | 110 | 31.4546 | 0 | 388.4197 | 0
9559 | 865.209 | 5.5786 | 50.1029 | 101.1868 | 68.4843 | 9.4989 | 93.465 | 13.7019 | 10.2529 | 49.1382 | 98.2565 | 18.365 | 226.3353 | 165.7701 | 236.6331 | 12.6552 | 51.3916 | 4.1076 | 172 | 40.0629 | 0 | 434.7924 | 0
9560 | 906.5834 | 10.547 | 76.8366 | 108.1755 | 64.4796 | 13.2989 | 112.4479 | 14.245 | 14.6178 | 85.1684 | 142.8162 | 34.6223 | 291.7753 | 251.8914 | 337.7853 | 27.307 | 56.7167 | 6.148 | 265 | 50.9793 | 0 | 472.5553 | 0
9561 | 993.4458 | 9.3518 | 90.7761 | 121.2388 | 61.4823 | 16.1492 | 129.5294 | 15.3642 | 17.534 | 94.8764 | 168.6506 | 40.3416 | 346.2259 | 312.6168 | 461.5172 | 34.8164 | 66.4805 | 10.2314 | 305 | 57.8371 | 0 | 543.5792 | 0
9562 | 1078.9794 | 6.0188 | 95.1804 | 133.7467 | 62.4802 | 15.2003 | 150.4953 | 15.432 | 20.7466 | 92.6944 | 186.3651 | 39.8964 | 415.3282 | 344.5233 | 552.8232 | 40.8019 | 78.8226 | 16.1232 | 368 | 67.4637 | 0 | 612.1413 | 0.018129
9563 | 1127.4071 | 5.1258 | 96.2247 | 137.0322 | 60.4739 | 17.1042 | 153.8586 | 15.6712 | 26.3669 | 92.2446 | 194.9234 | 41.3985 | 445.9775 | 348.7732 | 593.1468 | 43.7312 | 105.2554 | 17.1933 | 369 | 69.1201 | 0 | 585.0593 | 0.026309
9564 | 1163.5511 | 5.0607 | 100.6883 | 136.0174 | 59.4845 | 18.045 | 148.7008 | 13.1378 | 25.6747 | 93.1256 | 191.9958 | 41.061 | 477.2936 | 365.2195 | 607.1081 | 43.4424 | 108.259 | 17.3801 | 339 | 79.2981 | 0 | 595.8909 | 0.029891
9565 | 1166.8438 | 5.002 | 103.7314 | 135.6658 | 61.4765 | 16.1505 | 155.1001 | 12.9498 | 20.9292 | 100.3819 | 196.8771 | 40.8082 | 468.9623 | 371.2319 | 597.029 | 43.8986 | 107.849 | 18.149 | 346 | 80.8017 | 0 | 583.8356 | 0.032854
9566 | 1174.749 | 4.7518 | 102.5214 | 142.3762 | 60.4794 | 17.0997 | 159.5992 | 15.2981 | 21.7014 | 110.4524 | 200.8513 | 42.7026 | 462.2206 | 376.787 | 585.292 | 44.2295 | 112.5141 | 19.0624 | 282 | 75.7981 | 0 | 610.2626 | 0.027898
9567 | 1160.8133 | 4.715 | 101.3557 | 145.2892 | 59.4752 | 18.0497 | 160.4793 | 14.1553 | 22.0873 | 103.5576 | 204.2006 | 39.2067 | 482.2422 | 375.4758 | 581.2072 | 43.058 | 120.0995 | 19.7965 | 259 | 73.8135 | 0 | 627.5749 | 0.032982
9568 | 1143.6366 | 4.9409 | 99.2866 | 143.0696 | 58.4754 | 18.9997 | 158.8649 | 11.7487 | 14.0453 | 87.7372 | 201.4269 | 37.5084 | 490.1984 | 376.3179 | 591.9099 | 41.433 | 120.5259 | 19.9541 | 272 | 70.9457 | 0 | 604.3547 | 0.011012
9569 | 1114.7154 | 6.0095 | 89.2607 | 133.5055 | 69.4764 | 8.5529 | 140.1966 | 14.3639 | 10.4483 | 79.6433 | 197.98 | 33.4217 | 439.2808 | 352.8249 | 550.0361 | 32.6731 | 111.7067 | 19.1767 | 264 | 58.2664 | 0 | 545.638 | 0
9570 | 1072.3088 | 6.5556 | 78.5442 | 117.4748 | 71.4824 | 6.6505 | 128.3997 | 14.3129 | 12.916 | 66.2374 | 179.8458 | 29.4605 | 365.4791 | 288.9226 | 453.4395 | 18.3778 | 92.0102 | 17.9336 | 219 | 50.9356 | 0 | 403.9796 | 0
9571 | 1027.1157 | 5.8988 | 73.0651 | 102.8941 | 72.4838 | 5.7003 | 115.2404 | 9.5122 | 12.895 | 50.4102 | 150.5213 | 24.2206 | 308.2559 | 203.9328 | 388.0259 | 13.4591 | 78.5082 | 17.1434 | 200 | 48.6491 | 0 | 335.876 | 0
9572 | 988.7976 | 7.568 | 62.9958 | 96.7176 | 72.486 | 5.7 | 83.6594 | 10.9969 | 9.0587 | 46.31 | 139.2527 | 13.4033 | 279.1598 | 159.8618 | 345.7501 | 12.4305 | 65.5898 | 10.408 | 184 | 44.2039 | 0 | 286.6235 | 0
9573 | 958.8615 | 11.1514 | 34.7499 | 95.1529 | 72.4895 | 5.7 | 75.6239 | 13.5946 | 7.323 | 43.5157 | 129.7619 | 11.1632 | 257.6096 | 132.8299 | 305.6432 | 11.7312 | 56.246 | 5.5387 | 173 | 39.6808 | 0 | 271.4032 | 0
9574 | 926.6063 | 12.0585 | 25.4118 | 93.5133 | 72.4896 | 5.7 | 75.1881 | 13.9345 | 6.8332 | 37.0594 | 111.2203 | 10.1426 | 232.5678 | 117.9203 | 278.1018 | 10.8327 | 52.3251 | 4.0616 | 165 | 33.5943 | 0 | 261.0154 | 0
9575 | 901.9409 | 7.787 | 25.1837 | 93.3672 | 72.4893 | 5.7 | 68.4167 | 11.1784 | 6.5208 | 32.3477 | 94.7643 | 9.4741 | 215.1434 | 107.8111 | 272.4544 | 10.5589 | 51.3479 | 3.8403 | 150 | 30.5962 | 0 | 261.1712 | 0
9576 | 877.9369 | 3.6504 | 24.9914 | 92.6137 | 73.4864 | 4.7503 | 69.8685 | 10.0112 | 6.493 | 31.1165 | 87.8781 | 9.2863 | 203.9612 | 100.6308 | 253.3355 | 10.4866 | 51.4691 | 3.8444 | 135 | 30.7466 | 0 | 257.499 | 0
9577 | 876.6488 | 2.6708 | 24.8893 | 91.3071 | 72.4873 | 5.6997 | 75.7872 | 12.7945 | 6.2162 | 31.1156 | 85.0506 | 9.44 | 193.793 | 93.8347 | 235.7241 | 10.4667 | 51.3374 | 2.9161 | 119 | 31.082 | 0 | 272.2602 | 0
9578 | 876.2008 | 2.6927 | 25.0267 | 91.6066 | 73.4842 | 4.7503 | 69.5863 | 13.8634 | 6.1573 | 31.087 | 84.4334 | 9.0745 | 189.2936 | 89.0312 | 227.9692 | 10.3777 | 51.5406 | 2.624 | 117 | 30.5892 | 0 | 276.8789 | 0
9579 | 863.6241 | 2.9439 | 24.9893 | 93.1201 | 72.4887 | 5.6997 | 67.8235 | 13.7769 | 6.3233 | 31.0534 | 84.6229 | 8.8581 | 187.3421 | 89.5973 | 228.5587 | 10.2019 | 51.6624 | 2.5784 | 109 | 31.1658 | 0 | 276.2674 | 0
9580 | 859.6264 | 2.6277 | 24.9363 | 93.6718 | 72.4889 | 5.7 | 74.8297 | 13.7798 | 6.3943 | 31.1261 | 84.5463 | 8.8696 | 186.8197 | 91.4461 | 227.1026 | 10.364 | 51.5316 | 2.4905 | 111 | 31.164 | 0 | 279.9668 | 0
9581 | 862.1292 | 2.9902 | 24.9196 | 93.7541 | 71.4888 | 6.6497 | 70.338 | 13.7619 | 6.3355 | 31.2986 | 82.8871 | 8.821 | 190.7906 | 88.3528 | 219.4317 | 10.3333 | 52.6811 | 2.4291 | 106 | 30.7796 | 0 | 310.0899 | 0
9582 | 882.265 | 4.1066 | 34.755 | 95.0554 | 72.4839 | 5.7003 | 72.0834 | 13.8235 | 6.6729 | 32.9174 | 83.408 | 11.1508 | 201.5341 | 92.4968 | 221.0551 | 10.3561 | 54.7855 | 2.4033 | 110 | 32.432 | 0 | 353.9478 | 0
9583 | 915.0362 | 5.7099 | 50.9386 | 97.4046 | 70.4835 | 7.5995 | 92.1288 | 13.5703 | 11.8686 | 51.793 | 99.4195 | 17.6467 | 233.0234 | 160.0759 | 249.0507 | 12.8094 | 52.4258 | 3.1728 | 186 | 40.0074 | 0 | 388.9625 | 0
9584 | 969.1735 | 11.2364 | 76.935 | 102.5775 | 64.4815 | 13.2984 | 110.9396 | 13.9207 | 13.1353 | 87.3996 | 148.8683 | 30.302 | 295.2205 | 241.0693 | 351.0436 | 28.7316 | 60.1458 | 8.9156 | 256 | 50.3559 | 0 | 447.6094 | 0
9585 | 1054.1868 | 17.7801 | 91.3883 | 114.2404 | 62.4801 | 15.1995 | 130.1316 | 15.4765 | 14.4498 | 99.3054 | 177.3332 | 34.147 | 350.5016 | 299.2527 | 465.7086 | 36.9063 | 69.6761 | 18.1037 | 271 | 56.3484 | 0 | 510.3235 | 0
9586 | 1121.7873 | 21.1419 | 97.3158 | 125.5119 | 62.4786 | 15.2 | 150.7607 | 16.8056 | 18.2848 | 98.7022 | 188.2931 | 34.7067 | 387.5926 | 338.1187 | 546.3441 | 41.1387 | 80.9395 | 19.2121 | 332 | 64.1956 | 0 | 550.9913 | 0.020813
9587 | 1176.0485 | 18.2906 | 95.2718 | 131.0831 | 61.4769 | 16.1497 | 146.9387 | 11.8613 | 24.0478 | 98.6069 | 193.405 | 36.2043 | 406.5449 | 355.5399 | 576.9723 | 43.5685 | 88.702 | 18.1772 | 325 | 67.6194 | 0 | 569.2252 | 0.025447
9588 | 1199.8202 | 13.2698 | 96.9081 | 134.1552 | 63.4772 | 14.2505 | 143.3804 | 14.3124 | 24.8123 | 99.2666 | 195.0688 | 35.2309 | 417.2325 | 367.9191 | 580.0011 | 42.0944 | 95.7917 | 18.4543 | 308 | 72.1734 | 0 | 576.7437 | 0.027984
9589 | 1181.5033 | 10.1087 | 96.8289 | 133.9194 | 59.4837 | 18.0489 | 153.6676 | 16.6464 | 21.787 | 92.0114 | 200.9898 | 36.3022 | 407.65 | 368.4871 | 588.9265 | 43.8961 | 92.3833 | 18.8957 | 330 | 68.8423 | 0 | 600.5057 | 0.026587
9590 | 1166.864 | 10.7644 | 98.2238 | 137.8219 | 62.4766 | 15.205 | 154.1255 | 10.7717 | 20.6067 | 85.2917 | 206.7297 | 37.3643 | 421.7847 | 368.6644 | 621.0282 | 44.9334 | 92.8063 | 19.7834 | 293 | 67.1509 | 0 | 610.4488 | 0.023261
9591 | 1142.8365 | 7.2397 | 99.6958 | 138.9162 | 62.4802 | 15.1958 | 150.7395 | 13.2013 | 19.2743 | 90.2177 | 201.6187 | 36.3931 | 424.4061 | 360.8414 | 620.3288 | 43.6325 | 94.3564 | 19.903 | 287 | 68.2304 | 0 | 586.6185 | 0.01676
9592 | 1110.5919 | 9.7333 | 96.4545 | 136.2461 | 62.4756 | 15.2 | 151.1876 | 15.4035 | 13.6387 | 97.8509 | 194.4583 | 33.073 | 405.6248 | 336.8345 | 580.4376 | 41.3665 | 93.0297 | 19.1127 | 318 | 61.0296 | 0 | 553.6619 | 0.0073897
9593 | 1084.0858 | 12.6112 | 91.8094 | 126.7212 | 63.4793 | 14.2503 | 134.9608 | 10.2121 | 8.8654 | 95.0564 | 191.1304 | 31.9284 | 376.786 | 311.7115 | 499.7236 | 34.2333 | 90.2757 | 18.2571 | 309 | 53.1709 | 0 | 499.7868 | 0
9594 | 1017.5067 | 8.4487 | 81.2773 | 115.2493 | 71.4832 | 6.6521 | 122.0408 | 13.0663 | 11.1755 | 88.8333 | 183.7309 | 32.5079 | 327.2124 | 250.3542 | 418.5386 | 18.8377 | 85.9215 | 17.2891 | 272 | 49.2832 | 0 | 370.9811 | 0
9595 | 958.8968 | 5.5898 | 49.0951 | 100.322 | 72.4857 | 5.7003 | 109.2287 | 14.6207 | 13.354 | 69.4543 | 155.6689 | 30.1353 | 288.3162 | 172.7018 | 354.2631 | 15.6379 | 77.1552 | 16.1565 | 254 | 46.6348 | 0 | 319.6199 | 0
9596 | 925.0202 | 5.483 | 37.3214 | 94.7546 | 72.4829 | 5.7 | 77.2084 | 10.9365 | 10.3993 | 59.0065 | 133.3539 | 22.5213 | 251.4501 | 140.1572 | 306.4424 | 16.8142 | 60.2962 | 9.8331 | 215 | 43.9654 | 0 | 275.9129 | 0
9597 | 878.253 | 4.9042 | 27.8409 | 93.8539 | 72.4864 | 5.7 | 69.6098 | 9.2908 | 8.3876 | 51.1013 | 107.8941 | 12.8106 | 227.3311 | 136.4268 | 277.5116 | 13.3949 | 52.8588 | 5.5601 | 242 | 41.5114 | 0 | 270.1336 | 0
9598 | 863.0236 | 4.9614 | 24.456 | 92.2296 | 72.4866 | 5.7 | 70.3782 | 10.7188 | 7.8921 | 42.8157 | 93.3053 | 9.5418 | 210.263 | 125.5023 | 279.2585 | 11.2191 | 52.8035 | 4.1666 | 233 | 38.3698 | 0 | 282.19 | 0
9599 | 851.1458 | 4.4326 | 24.0425 | 90.0445 | 72.4813 | 5.7 | 66.6269 | 12.8478 | 7.39 | 38.247 | 87.8238 | 9.3717 | 201.6765 | 105.3307 | 287.0312 | 10.6308 | 50.1999 | 3.9249 | 214 | 35.6553 | 0 | 281.951 | 0
9600 | 837.4847 | 3.2612 | 24.1299 | 89.5363 | 73.4809 | 4.7503 | 68.5567 | 13.6741 | 7.091 | 35.8714 | 85.0705 | 9.3606 | 194.6541 | 95.4794 | 272.8913 | 10.7354 | 48.7582 | 3.8851 | 207 | 36.1817 | 0 | 276.2423 | 0
9601 | 824.3569 | 3.7118 | 24.0157 | 89.4359 | 72.4851 | 5.6997 | 73.8816 | 13.6443 | 6.61 | 35.0641 | 83.6661 | 9.425 | 190.9268 | 89.8039 | 265.1493 | 10.8601 | 49.3242 | 4.2461 | 154 | 34.7368 | 0 | 276.7437 | 0
9602 | 814.015 | 8.6568 | 24.2528 | 90.8826 | 72.4873 | 5.7 | 67.1921 | 13.6468 | 6.2895 | 35.1421 | 84.1734 | 9.3299 | 187.9072 | 89.5811 | 264.5306 | 10.9151 | 48.7444 | 4.2953 | 146 | 34.8658 | 0 | 280.9164 | 0
9603 | 797.4329 | 10.3727 | 23.9589 | 91.4981 | 73.4866 | 4.7503 | 64.5884 | 13.6495 | 6.3303 | 33.434 | 85.6217 | 9.2033 | 182.9509 | 91.7808 | 257.6528 | 10.88 | 48.6125 | 4.1976 | 141 | 34.2472 | 0 | 270.0338 | 0
9604 | 790.5363 | 10.2497 | 24.0465 | 90.9397 | 69.4882 | 8.5489 | 71.0845 | 13.9309 | 6.1908 | 32.4943 | 86.4353 | 9.1821 | 180.2918 | 90.9012 | 244.9549 | 10.6392 | 48.6904 | 4.2316 | 127 | 37.3368 | 0 | 265.3375 | 0
9605 | 801.79 | 9.7488 | 24.0588 | 91.5895 | 73.4864 | 4.7511 | 66.5605 | 13.745 | 6.182 | 32.7719 | 85.9313 | 9.1535 | 179.9063 | 87.7957 | 226.7867 | 10.6985 | 50.1753 | 4.0589 | 117 | 36.5606 | 0 | 264.2836 | 0
9606 | 793.4173 | 6.108 | 24.3707 | 90.7881 | 72.4893 | 5.6997 | 64.066 | 13.6119 | 6.3467 | 32.7668 | 85.5402 | 9.1629 | 177.4649 | 87.1183 | 221.8778 | 10.8065 | 52.3145 | 3.2484 | 113 | 33.8418 | 0 | 271.3274 | 0
9607 | 804.1397 | 4.4684 | 38.8143 | 89.9361 | 73.4837 | 4.7503 | 70.6952 | 13.6052 | 6.4521 | 33.4165 | 86.3984 | 8.0879 | 177.2079 | 87.373 | 219.1345 | 10.8157 | 49.7929 | 2.7839 | 119 | 35.0558 | 0 | 275.3225 | 0
9608 | 817.2581 | 4.5705 | 46.0747 | 89.85 | 72.4822 | 5.6997 | 70.6297 | 13.5061 | 6.556 | 33.8261 | 94.8408 | 10.0758 | 183.512 | 86.9871 | 219.1657 | 10.8212 | 48.6612 | 2.9559 | 117 | 44.2696 | 0 | 272.8251 | 0
9609 | 819.8932 | 4.655 | 55.5532 | 87.6756 | 71.4839 | 6.6497 | 79.5466 | 13.5441 | 5.7658 | 41.0947 | 111.1629 | 14.4965 | 188.1233 | 86.5924 | 214.8687 | 10.2387 | 48.0828 | 3.4067 | 127 | 49.0981 | 0 | 271.9703 | 0.011663
9610 | 844.524 | 4.8523 | 70.5933 | 85.9859 | 72.4796 | 5.7003 | 96.6312 | 13.3597 | 7.2864 | 58.1274 | 128.8234 | 15.6018 | 195.8608 | 92.8493 | 216.9257 | 10.1779 | 48.4289 | 5.3221 | 169 | 50.675 | 0 | 273.5837 | 0.016967
9611 | 866.8411 | 3.8753 | 77.678 | 86.7145 | 71.4797 | 6.6497 | 92.9402 | 14.8552 | 8.5999 | 65.88 | 145.4898 | 15.483 | 210.1693 | 109.0643 | 227.3747 | 10.2654 | 48.8708 | 10.465 | 175 | 49.9696 | 0 | 273.2189 | 0.021906
9612 | 886.0255 | 3.6339 | 79.0863 | 91.334 | 71.4853 | 6.65 | 80.0762 | 15.3133 | 8.605 | 64.3231 | 137.0118 | 16.0597 | 225.7059 | 119.4931 | 248.1388 | 10.3925 | 48.8242 | 12.579 | 216 | 52.4365 | 0 | 271.0789 | 0.02651
9613 | 880.4003 | 3.3822 | 80.0857 | 97.625 | 71.4893 | 6.65 | 82.1627 | 8.8076 | 8.7503 | 62.8961 | 130.1752 | 15.6683 | 234.0617 | 130.1552 | 282.341 | 10.4466 | 49.3721 | 13.1288 | 206 | 51.5477 | 0 | 270.4538 | 0.024895
9614 | 868.1341 | 3.7393 | 76.5987 | 100.2522 | 71.4876 | 6.65 | 86.3816 | 11.1341 | 10.565 | 63.3402 | 130.6376 | 15.5996 | 237.4923 | 129.0109 | 312.3732 | 10.2198 | 50.2143 | 13.7253 | 225 | 52.9555 | 0 | 274.6599 | 0.021386
9615 | 883.3152 | 4.1792 | 48.7837 | 102.3997 | 71.4875 | 6.65 | 88.2276 | 13.287 | 10.165 | 62.5103 | 130.6981 | 16.4019 | 237.8263 | 127.3722 | 325.3465 | 10.2867 | 49.738 | 12.1918 | 217 | 52.5496 | 0 | 277.718 | 0.012558
9616 | 891.8942 | 5.0921 | 37.2625 | 102.1726 | 70.4888 | 7.5997 | 85.4584 | 13.1345 | 10.0912 | 53.3887 | 132.7645 | 16.1533 | 240.9759 | 125.6526 | 320.0299 | 10.4245 | 48.7809 | 7.0043 | 224 | 46.1291 | 0 | 276.6556 | 0.0049658
9617 | 889.2601 | 5.7677 | 27.5816 | 99.157 | 70.4861 | 7.6 | 77.6508 | 13.3863 | 12.7455 | 37.4164 | 136.591 | 10.1457 | 240.8207 | 131.9873 | 310.0902 | 10.5906 | 48.2976 | 5.1021 | 215 | 44.5749 | 0 | 268.8544 | 0
9618 | 888.6905 | 5.3896 | 23.9912 | 99.0799 | 71.4827 | 6.6503 | 66.6476 | 10.7295 | 14.3277 | 32.602 | 131.0477 | 7.9294 | 238.8761 | 125.4251 | 307.2954 | 10.8422 | 49.5032 | 5.0832 | 206 | 43.1921 | 0 | 275.0267 | 0
9619 | 869.2711 | 5.3619 | 23.8308 | 98.7823 | 73.4824 | 4.7505 | 71.9713 | 10.3362 | 11.9429 | 32.1109 | 108.8609 | 8.011 | 231.4204 | 114.6462 | 285.7572 | 10.6094 | 50.5215 | 4.4536 | 219 | 39.8148 | 0 | 274.157 | 0
9620 | 857.9476 | 5.2636 | 23.8897 | 97.87 | 72.4885 | 5.6997 | 88.9049 | 12.8693 | 8.462 | 31.1267 | 108.1649 | 8.063 | 226.0218 | 121.0168 | 263.5449 | 10.7398 | 50.4429 | 4.3324 | 200 | 36.2749 | 0 | 277.9052 | 0
9621 | 850.1236 | 5.1934 | 23.985 | 97.3658 | 72.4938 | 5.7 | 79.2523 | 13.8621 | 6.8735 | 29.3814 | 107.652 | 8.1017 | 217.6618 | 120.4667 | 252.9916 | 10.9639 | 51.1604 | 4.1597 | 184 | 34.7825 | 0 | 273.3928 | 0
9622 | 834.6263 | 5.3205 | 24.0026 | 96.5187 | 73.4895 | 4.7503 | 65.4889 | 13.7289 | 7.9428 | 28.2557 | 96.9224 | 8.2228 | 202.7369 | 112.3919 | 255.6163 | 10.8611 | 50.8672 | 3.7658 | 184 | 34.209 | 0 | 267.9857 | 0
9623 | 833.9291 | 4.6306 | 23.7774 | 96.0109 | 72.4859 | 5.6997 | 70.8046 | 13.8497 | 8.106 | 28.4692 | 92.1616 | 8.5982 | 201.0752 | 106.9888 | 261.5151 | 10.816 | 49.67 | 3.1777 | 170 | 34.6458 | 0 | 288.0867 | 0
9624 | 837.8897 | 3.4189 | 23.8455 | 95.7884 | 73.4847 | 4.7503 | 70.8044 | 9.0589 | 7.8482 | 29.5565 | 91.4588 | 8.2509 | 199.9613 | 103.5283 | 270.8714 | 10.5297 | 49.3128 | 2.8114 | 142 | 34.9849 | 0 | 292.0778 | 0
9625 | 841.1283 | 3.1643 | 23.7134 | 94.6133 | 72.4853 | 5.6997 | 63.8692 | 11.1503 | 7.0475 | 29.5889 | 88.1382 | 8.0598 | 198.0329 | 103.1846 | 269.8719 | 10.6422 | 49.3108 | 3.0165 | 141 | 33.8385 | 0 | 282.2464 | 0
9626 | 820.7295 | 3.0772 | 23.8556 | 91.8497 | 73.4898 | 4.7503 | 67.0044 | 13.5208 | 6.449 | 29.4918 | 86.7668 | 7.9564 | 190.4765 | 102.1788 | 261.678 | 10.8038 | 49.5479 | 3.1048 | 144 | 33.6119 | 0 | 286.6345 | 0
9627 | 796.1565 | 2.8417 | 23.957 | 91.0593 | 66.4923 | 11.3982 | 72.4012 | 13.7597 | 6.1007 | 29.1938 | 86.8751 | 7.8503 | 184.3339 | 99.6425 | 254.7108 | 10.867 | 49.4252 | 2.7061 | 130 | 34.1845 | 0 | 281.4457 | 0
9628 | 792.1632 | 2.7246 | 24.0672 | 90.9012 | 67.492 | 10.4503 | 65.7256 | 13.2043 | 6.2035 | 28.3493 | 86.6784 | 8.2421 | 176.8943 | 90.6242 | 249.15 | 10.7754 | 49.4393 | 2.7219 | 124 | 33.3565 | 0 | 274.2812 | 0
9629 | 797.5672 | 3.1374 | 24.0027 | 91.2149 | 68.4919 | 9.5003 | 64.1883 | 9.2029 | 6.2442 | 28.2488 | 87.0679 | 8.0133 | 172.9613 | 86.8984 | 251.2502 | 10.5897 | 51.0806 | 2.6155 | 120 | 37.7079 | 0 | 265.7655 | 0
9630 | 797.4806 | 4.1632 | 24.065 | 93.6082 | 72.4879 | 5.7011 | 71.8637 | 11.9224 | 6.1153 | 29.0474 | 88.2541 | 7.8248 | 173.0036 | 85.6484 | 254.7851 | 10.8261 | 53.4334 | 2.839 | 117 | 42.0939 | 0 | 267.1412 | 0
9631 | 809.6002 | 4.365 | 24.0189 | 94.0698 | 70.4894 | 7.5995 | 68.5065 | 13.7282 | 6.1847 | 30.0504 | 89.5962 | 7.795 | 173.9844 | 86.2915 | 246.3919 | 10.911 | 50.977 | 2.6192 | 118 | 34.9135 | 0 | 264.6291 | 0
9632 | 811.2404 | 4.3404 | 24.0857 | 93.1366 | 73.4862 | 4.7508 | 68.175 | 13.6106 | 6.1798 | 28.8985 | 91.049 | 7.7537 | 179.2127 | 87.5687 | 233.4905 | 10.8246 | 48.929 | 2.7474 | 126 | 35.943 | 0 | 271.3196 | 0
9633 | 812.5315 | 3.2208 | 23.8866 | 89.3164 | 71.4837 | 6.6495 | 83.6847 | 13.3237 | 5.3645 | 34.3721 | 90.3974 | 5.8543 | 182.5235 | 85.7039 | 225.0008 | 10.4123 | 47.6888 | 3.2667 | 124 | 37.9116 | 0 | 253.5293 | 0.007608
9634 | 832.5585 | 2.8055 | 29.6972 | 88.4934 | 71.4823 | 6.65 | 86.7067 | 13.1259 | 6.5048 | 54.1085 | 91.29 | 4.9547 | 187.1444 | 87.3586 | 222.766 | 10.1375 | 46.9658 | 3.7056 | 150 | 38.1814 | 0 | 256.6392 | 0.02277
9635 | 865.7659 | 2.8329 | 36.3111 | 86.6915 | 72.4814 | 5.7003 | 89.1627 | 11.9902 | 7.3523 | 64.4434 | 102.0022 | 5.239 | 203.9384 | 96.7025 | 234.4797 | 10.2672 | 48.3635 | 4.0672 | 168 | 37.8074 | 0 | 264.2522 | 0.031269
9636 | 876.9461 | 2.6757 | 38.0317 | 87.4835 | 72.4823 | 5.7 | 97.8217 | 8.7821 | 7.7753 | 65.3809 | 113.2316 | 5.6364 | 216.0149 | 106.0356 | 257.8919 | 10.3261 | 51.572 | 4.1921 | 162 | 40.6104 | 0 | 266.1466 | 0.033017
9637 | 879.0877 | 2.737 | 38.1403 | 91.5148 | 72.4809 | 5.7 | 101.7816 | 11.2981 | 9.7203 | 62.2899 | 129.7648 | 6.4059 | 231.0492 | 128.8419 | 275.6891 | 10.2847 | 52.757 | 4.8139 | 164 | 40.4488 | 0 | 266.9314 | 0.029009
9638 | 887.0783 | 2.767 | 38.2721 | 92.9455 | 72.4813 | 5.7 | 92.9114 | 12.9598 | 10.6064 | 60.2123 | 137.4187 | 8.4288 | 235.1857 | 152.2578 | 289.689 | 10.2944 | 51.0919 | 5.4094 | 162 | 41.2808 | 0 | 263.8986 | 0.027615
9639 | 874.272 | 2.9742 | 38.3829 | 91.4964 | 73.4803 | 4.7503 | 83.5164 | 12.9248 | 10.6976 | 61.3064 | 137.3846 | 10.6622 | 235.7759 | 144.0815 | 295.0249 | 10.0731 | 50.6829 | 5.4492 | 172 | 42.1967 | 0 | 275 | 0.018586
9640 | 877.6968 | 2.7568 | 36.9561 | 90.0167 | 72.481 | 5.6997 | 78.8349 | 10.6718 | 9.2906 | 51.4433 | 136.017 | 11.1444 | 236.6917 | 137.4201 | 285.9727 | 10.2823 | 50.5006 | 6.1378 | 170 | 41.7398 | 0 | 272.8934 | 0.0070785
9641 | 898.0054 | 4.0645 | 27.378 | 90.0213 | 71.4869 | 6.6497 | 68.911 | 9.6841 | 7.5912 | 33.0978 | 135.4179 | 12.5576 | 244.5008 | 144.9362 | 279.0655 | 10.424 | 50.9811 | 6.4316 | 183 | 40.1936 | 0 | 277.4571 | 0
9642 | 916.2261 | 4.7478 | 24.1911 | 90.8892 | 71.4893 | 6.65 | 65.9498 | 12.4615 | 9.4816 | 29.3944 | 138.6243 | 20.0116 | 237.5152 | 140.049 | 281.8271 | 10.6315 | 51.8572 | 6.4031 | 190 | 39.5785 | 0 | 284.18 | 0
9643 | 915.7132 | 4.7677 | 24.3171 | 91.714 | 72.4887 | 5.7003 | 73.9402 | 13.6958 | 10.1947 | 30.9417 | 138.8833 | 21.4573 | 221.5398 | 122.0355 | 285.8248 | 10.7988 | 53.7501 | 5.6977 | 160 | 39.2899 | 0 | 285.9845 | 0
9644 | 905.9387 | 5.2417 | 24.2119 | 95.4052 | 71.4882 | 6.6497 | 70.1387 | 13.7411 | 8.876 | 31.4537 | 130.5426 | 13.0737 | 210.0327 | 113.3019 | 285.8162 | 10.5807 | 52.4055 | 5.295 | 154 | 39.9652 | 0 | 275.6707 | 0
9645 | 885.7395 | 5.9201 | 24.3951 | 96.0983 | 72.4908 | 5.7003 | 64.3526 | 9.8981 | 8.0345 | 31.3917 | 104.5272 | 9.5645 | 210.9539 | 104.9021 | 262.291 | 10.7564 | 50.7324 | 5.033 | 141 | 39.7978 | 0 | 277.2437 | 0
9646 | 869.5477 | 5.332 | 24.4023 | 95.1057 | 70.4921 | 7.5995 | 69.2821 | 10.9505 | 7.5245 | 30.9989 | 91.8517 | 9.4034 | 205.681 | 99.8657 | 239.722 | 10.7945 | 50.3349 | 4.4349 | 139 | 37.6789 | 0 | 274.7905 | 0
9647 | 852.915 | 4.2519 | 24.4049 | 95.0168 | 72.4861 | 5.7005 | 70.289 | 13.4442 | 7.0288 | 32.9176 | 89.9967 | 9.5335 | 193.6808 | 97.3158 | 228.6345 | 10.7779 | 49.5061 | 4.0359 | 117 | 36.5638 | 0 | 269.704 | 0
9648 | 834.0693 | 3.1263 | 24.1589 | 93.9373 | 72.4821 | 5.7016 | 63.7454 | 13.8329 | 6.8542 | 34.1196 | 89.2193 | 9.3909 | 184.0391 | 94.4568 | 230.9339 | 10.74 | 48.7674 | 3.8298 | 109 | 35.5053 | 0 | 271.6699 | 0
9649 | 815.5076 | 2.8009 | 23.9807 | 94.2623 | 72.4892 | 5.6984 | 64.0559 | 13.7396 | 6.8042 | 33.4794 | 87.7573 | 9.5095 | 177.5793 | 91.2626 | 229.7208 | 10.5166 | 49.4971 | 3.6539 | 104 | 33.2577 | 0 | 271.5386 | 0
9650 | 786.681 | 3.6871 | 23.7086 | 94.7147 | 72.4868 | 5.7 | 69.5042 | 13.7193 | 7.1197 | 32.7497 | 86.4829 | 9.6428 | 174.1538 | 90.4047 | 228.5642 | 10.6936 | 48.8181 | 2.9731 | 104 | 33.3573 | 0 | 273.0728 | 0
9651 | 762.162 | 3.4057 | 23.8819 | 93.9011 | 72.4898 | 5.7 | 63.6671 | 13.7371 | 6.9275 | 32.1692 | 86.3989 | 9.4523 | 172.9423 | 92.9317 | 232.977 | 10.6727 | 48.4134 | 2.7113 | 107 | 32.6003 | 0 | 273.0731 | 0
9652 | 762.2124 | 2.8483 | 24.9285 | 92.1128 | 73.4901 | 4.7503 | 61.5013 | 13.7551 | 6.6997 | 31.6637 | 86.0953 | 9.3384 | 172.7898 | 96.11 | 231.4991 | 10.7408 | 48.566 | 2.7377 | 107 | 33.4113 | 0 | 276.0823 | 0
9653 | 774.7458 | 3.1484 | 27.9902 | 94.1388 | 72.488 | 5.6997 | 70.5097 | 13.9146 | 6.6875 | 32.0255 | 85.9002 | 9.23 | 175.4634 | 91.5168 | 224.6571 | 10.801 | 50.1858 | 2.7523 | 104 | 31.9079 | 0 | 319.3784 | 0
9654 | 775.1862 | 4.2399 | 33.1259 | 92.1131 | 72.4837 | 5.7 | 72.8181 | 13.7637 | 7.377 | 32.1995 | 86.0677 | 10.0094 | 184.6188 | 93.4373 | 225.5096 | 10.4894 | 52.0951 | 2.7251 | 104 | 33.9082 | 0 | 334.965 | 0
9655 | 821.6065 | 5.5673 | 52.9405 | 96.4732 | 69.4805 | 8.5492 | 80.052 | 13.4889 | 10.579 | 50.0745 | 106.8608 | 21.6097 | 217.9627 | 156.7478 | 253.7124 | 13.2528 | 49.5828 | 5.5823 | 154 | 42.7466 | 0 | 390.2168 | 0
9656 | 879.7167 | 10.5687 | 78.2774 | 104.7368 | 64.6398 | 13.2987 | 104.1889 | 15.2491 | 14.052 | 95.239 | 156.0427 | 35.7372 | 276.7011 | 241.5615 | 368.1387 | 27.0474 | 55.8233 | 11.2122 | 274 | 53.205 | 0 | 438.9274 | 0
9657 | 964.5061 | 12.2048 | 89.9522 | 113.2817 | 61.5649 | 16.1492 | 135.307 | 16.6441 | 20.3952 | 110.4061 | 186.3351 | 41.9929 | 342.871 | 295.259 | 470.4509 | 34.5753 | 65.8691 | 15.1511 | 288 | 59.8211 | 0 | 504.9027 | 0.023642
9658 | 1036.8338 | 13.3386 | 100.2234 | 125.0847 | 60.4793 | 17.0997 | 149.1407 | 16.742 | 23.0345 | 105.0512 | 197.5301 | 41.8957 | 382.4172 | 335.1108 | 530.1457 | 38.5948 | 76.0761 | 18.727 | 379 | 65.8814 | 0 | 588.3957 | 0.071256
9659 | 1085.635 | 14.7877 | 100.1334 | 131.5492 | 61.4794 | 16.1503 | 158.0266 | 16.72 | 22.8358 | 95.1947 | 202.3593 | 41.5857 | 411.8004 | 357.6775 | 580.5838 | 41.3337 | 81.9511 | 17.7226 | 336 | 63.1237 | 0 | 595.8378 | 0.08326
9660 | 1132.1316 | 12.2289 | 103.4331 | 135.7868 | 61.4788 | 16.15 | 158.2854 | 16.782 | 20.8525 | 91.8374 | 203.2635 | 42.5809 | 430.5292 | 368.7724 | 602.1384 | 41.7663 | 84.1373 | 16.8604 | 309 | 69.208 | 0 | 606.5546 | 0.090536
9661 | 1127.5762 | 7.5444 | 101.9372 | 129.0063 | 62.4761 | 15.2003 | 150.8167 | 12.1009 | 19.0765 | 88.9018 | 205.7783 | 44.4623 | 422.2213 | 367.0783 | 596.9589 | 44.5287 | 82.2099 | 18.1032 | 347 | 65.7501 | 0 | 626.7862 | 0.099806
9662 | 1141.4278 | 5.1308 | 98.8653 | 131.7572 | 59.4751 | 18.0492 | 160.5752 | 15.3642 | 24.637 | 91.0682 | 207.3952 | 44.7323 | 427.4074 | 374.9206 | 568.7707 | 44.4753 | 85.7239 | 18.5246 | 337 | 65.7488 | 0 | 640.2105 | 0.068106
9663 | 1167.5858 | 4.4669 | 102.844 | 136.6613 | 63.4784 | 14.2511 | 161.184 | 17.1155 | 24.6995 | 96.9653 | 204.9835 | 44.6433 | 438.0179 | 390.8082 | 561.868 | 43.1688 | 90.3904 | 18.0781 | 318 | 69.1773 | 0 | 636.215 | 0.050194
9664 | 1135.5003 | 6.8843 | 100.3194 | 140.5359 | 60.4794 | 17.0992 | 152.684 | 16.4615 | 16.9602 | 94.5715 | 207.7916 | 41.6999 | 434.0378 | 384.6006 | 548.1614 | 41.009 | 91.5176 | 18.6049 | 250 | 65.1052 | 0 | 617.2342 | 0.034233
9665 | 1123.0802 | 6.6812 | 95.343 | 137.7268 | 64.4757 | 13.3011 | 147.8098 | 16.2181 | 13.5792 | 87.6547 | 201.7986 | 38.915 | 412.5405 | 364.0015 | 495.8591 | 33.1607 | 88.1963 | 18.314 | 240 | 60.2006 | 0 | 567.0082 | 0
9666 | 1057.8384 | 6.5046 | 89.1464 | 124.7103 | 71.4743 | 6.6518 | 126.5137 | 15.5316 | 12.7941 | 76.29 | 184.1104 | 39.1761 | 366.6022 | 291.7976 | 433.1227 | 18.8804 | 81.5095 | 17.4521 | 224 | 56.4872 | 0 | 448.5209 | 0
9667 | 990.5013 | 6.2313 | 80.8194 | 111.3921 | 72.4796 | 5.7003 | 108.831 | 14.4135 | 9.8421 | 61.4283 | 156.4809 | 33.513 | 308.7037 | 198.4285 | 406.1366 | 13.6482 | 75.7304 | 16.7911 | 208 | 53.572 | 0 | 403.3569 | 0
9668 | 960.2164 | 5.5261 | 62.0692 | 106.646 | 71.481 | 6.6497 | 96.4394 | 14.0863 | 8.5394 | 51.8317 | 140.1862 | 19.2401 | 323.7808 | 150.2174 | 358.3513 | 12.3856 | 67.457 | 10.5967 | 187 | 50.3141 | 0 | 335.4663 | 0
9669 | 920.7624 | 5.4206 | 33.7341 | 105.4103 | 72.4844 | 5.7003 | 83.3745 | 13.9573 | 8.0098 | 47.8402 | 129.5017 | 15.8768 | 372.068 | 139.7723 | 320.251 | 11.1392 | 58.8181 | 6.377 | 173 | 48.7676 | 0 | 305.4831 | 0
9670 | 901.6547 | 5.2416 | 25.1639 | 104.1634 | 73.4843 | 4.7503 | 73.7174 | 13.9604 | 7.2825 | 41.8654 | 113.6753 | 21.782 | 341.9468 | 134.9679 | 281.9473 | 10.9107 | 54.9873 | 4.8989 | 171 | 42.1371 | 0 | 306.7796 | 0
9671 | 867.9147 | 5.0507 | 25.0124 | 98.6601 | 72.4819 | 5.6997 | 68.0535 | 13.7758 | 6.7762 | 38.2217 | 98.416 | 15.4819 | 236.0415 | 113.6357 | 261.9352 | 10.8443 | 52.1801 | 4.4095 | 148 | 35.7067 | 0 | 319.7784 | 0
9672 | 845.3994 | 3.5983 | 24.9892 | 94.7629 | 72.4804 | 5.7 | 64.9558 | 13.7306 | 6.7747 | 24.0217 | 61.1894 | 11.6418 | 59.2027 | 66.0834 | 170.2783 | 10.9265 | 32.2842 | 3.8641 | 126 | 33.9469 | 0 | 158.5659 | 0
9673 | 839.7178 | 2.6815 | 24.7678 | 93.6458 | 72.48 | 5.7 | 69.0994 | 13.7937 | 6.7842 | 35.486 | 88.0214 | 11.4585 | 189.9192 | 92.6476 | 240.2599 | 10.887 | 50.4582 | 3.0225 | 117 | 31.0405 | 0 | 304.6833 | 0
9674 | 838.1703 | 2.866 | 25.0534 | 93.985 | 73.4852 | 4.7503 | 67.4021 | 13.8938 | 6.9795 | 35.5787 | 89.4233 | 11.4178 | 193.8798 | 93.674 | 246.5504 | 10.6423 | 50.2937 | 2.6258 | 116 | 30.9574 | 0 | 310.5574 | 0
9675 | 831.2153 | 2.9602 | 24.8815 | 94.3641 | 72.4847 | 5.6997 | 61.7362 | 13.7872 | 6.9487 | 35.3725 | 91.5519 | 11.3683 | 188.7882 | 92.3277 | 249.1069 | 10.8234 | 50.168 | 2.5594 | 117 | 30.189 | 0 | 312.1419 | 0
9676 | 831.2504 | 2.8898 | 25.0907 | 94.0969 | 70.4827 | 7.5995 | 67.2007 | 13.7503 | 6.949 | 35.3734 | 91.2559 | 11.3076 | 181.3702 | 88.2222 | 235.0146 | 10.8081 | 50.4023 | 2.5919 | 116 | 30.8264 | 0 | 305.2973 | 0
9677 | 826.9601 | 3.0246 | 25.1849 | 93.2582 | 72.4802 | 5.7005 | 66.2499 | 13.6942 | 6.963 | 35.3314 | 88.9429 | 11.2255 | 184.1988 | 87.7549 | 221.8897 | 10.7565 | 51.7547 | 2.5892 | 112 | 31.033 | 0 | 331.7582 | 0
9678 | 824.8398 | 4.1216 | 34.3608 | 94.0909 | 72.4778 | 5.7 | 68.3313 | 13.8463 | 7.0782 | 37.5982 | 86.6257 | 13.7189 | 196.5752 | 94.0347 | 223.3891 | 10.7908 | 53.5783 | 2.5598 | 129 | 31.8789 | 0 | 376.7446 | 0
9679 | 864.2289 | 5.9301 | 49.6173 | 101.0935 | 70.4782 | 7.5995 | 88.5047 | 13.6485 | 12.3828 | 57.5001 | 99.484 | 20.8991 | 236.2577 | 162.6169 | 251.1573 | 12.889 | 51.1244 | 2.6047 | 191 | 40.2278 | 0 | 441.5499 | 0
9680 | 915.1275 | 14.8667 | 78.4857 | 105.2857 | 64.4804 | 13.2984 | 109.1487 | 14.9377 | 19.8565 | 97.0013 | 149.7244 | 33.5811 | 303.1951 | 249.1531 | 354.3865 | 27.9891 | 56.6076 | 7.9066 | 260 | 54.2763 | 0 | 470.7084 | 0
9681 | 1014.9345 | 18.533 | 95.1426 | 119.3643 | 62.473 | 15.1995 | 123.9549 | 15.5793 | 25.228 | 105.4982 | 185.3772 | 37.5062 | 372.1315 | 313.679 | 484.7755 | 36.1023 | 67.5335 | 15.0063 | 309 | 63.7105 | 0 | 534.2555 | 0.012128
9682 | 1080.7761 | 18.7397 | 98.4357 | 132.0513 | 63.4733 | 14.2503 | 149.1837 | 17.5399 | 25.3718 | 104.0947 | 200.765 | 39.0446 | 414.7632 | 357.2981 | 554.4303 | 39.2667 | 77.4708 | 17.6989 | 352 | 74.9461 | 0 | 599.5187 | 0.026642
9683 | 1139.6006 | 16.3292 | 98.0839 | 137.2683 | 60.4774 | 17.0992 | 153.183 | 18.7664 | 22.3474 | 103.8644 | 206.3981 | 42.6518 | 427.467 | 376.7265 | 594.5688 | 41.1768 | 82.0463 | 18.3116 | 371 | 81.9461 | 0 | 608.6592 | 0.042434
9684 | 1204.7088 | 13.8494 | 101.4639 | 138.7565 | 58.4744 | 18.9995 | 152.725 | 17.9981 | 19.6155 | 105.5955 | 205.1682 | 43.8264 | 435.4842 | 385.2422 | 629.0498 | 40.5222 | 85.2545 | 18.1756 | 368 | 86.2376 | 0 | 624.8738 | 0.047811
9685 | 1179.4979 | 10.522 | 100.7051 | 138.2567 | 60.4771 | 17.1005 | 154.8309 | 17.3512 | 17.6134 | 94.797 | 203.1253 | 41.5238 | 415.2979 | 371.7736 | 621.1785 | 41.3313 | 85.8394 | 17.8821 | 344 | 75.2823 | 0 | 634.9812 | 0.063086
9686 | 1173.0741 | 11.5506 | 101.4112 | 141.1079 | 58.4737 | 19.0048 | 150.0209 | 17.3182 | 15.4589 | 88.6527 | 206.5894 | 39.0076 | 423.7127 | 362.6764 | 585.6269 | 43.0656 | 102.7473 | 18.1481 | 340 | 73.7492 | 0 | 640.7296 | 0.15154
9687 | 1181.9265 | 11.5743 | 103.7986 | 139.0546 | 61.4769 | 16.15 | 152.2518 | 16.5982 | 14.4109 | 88.0222 | 210.3066 | 37.1343 | 435.0935 | 363.4581 | 570.5765 | 43.3141 | 111.1179 | 18.409 | 308 | 75.693 | 0 | 634.264 | 0.10089
9688 | 1163.308 | 8.2811 | 99.7322 | 134.4496 | 62.4798 | 15.1958 | 145.3087 | 15.9128 | 14.5639 | 84.8188 | 209.2195 | 34.6689 | 423.765 | 363.6043 | 575.3742 | 40.6738 | 107.7638 | 17.7981 | 349 | 72.095 | 0 | 627.3733 | 0.070815
9689 | 1111.6346 | 10.9684 | 89.52 | 134.6663 | 68.4761 | 9.5016 | 135.9322 | 15.6144 | 14.7487 | 78.8799 | 206.9934 | 30.2469 | 398.5854 | 342.2136 | 530.6222 | 34.978 | 89.69 | 18.0202 | 266 | 64.1813 | 0 | 570.5061 | 0
9690 | 1046.7565 | 14.0425 | 77.4744 | 123.5593 | 68.4781 | 9.5 | 122.1089 | 14.3117 | 14.502 | 78.6955 | 194.5102 | 30.2191 | 348.905 | 281.396 | 443.1118 | 20.5897 | 81.0487 | 18.0417 | 235 | 59.4778 | 0 | 423.5842 | 0
9691 | 1009.5302 | 10.8819 | 78.1432 | 109.8057 | 71.4806 | 6.6508 | 109.0122 | 13.9924 | 13.2824 | 60.1997 | 170.7282 | 27.2577 | 305.7167 | 216.6142 | 390.487 | 14.3285 | 74.2169 | 17.239 | 224 | 53.4287 | 0 | 386.1243 | 0
9692 | 965.2326 | 7.5072 | 71.6391 | 104.3826 | 72.4825 | 5.7003 | 86.0269 | 13.9835 | 8.8163 | 50.4688 | 155.5593 | 13.9933 | 274.1614 | 181.3604 | 364.221 | 12.4742 | 64.5549 | 10.5585 | 250 | 50.7696 | 0 | 351.9409 | 0
9693 | 920.9187 | 11.3514 | 38.6739 | 100.6028 | 72.4819 | 5.7 | 70.0759 | 13.9837 | 6.8458 | 51.4463 | 147.7723 | 9.1618 | 255.4648 | 155.0855 | 327.08 | 11.5057 | 58.4478 | 5.9248 | 218 | 49.1807 | 0 | 335.4789 | 0
9694 | 910.1487 | 13.631 | 26.257 | 98.3639 | 72.4873 | 5.7 | 66.9956 | 14.2268 | 6.3962 | 44.4215 | 125.9331 | 8.9921 | 230.3801 | 134.5919 | 280.6024 | 10.6868 | 55.1422 | 4.166 | 197 | 44.9696 | 0 | 321.1839 | 0
9695 | 906.5128 | 9.6967 | 25.7544 | 97.5452 | 72.4867 | 5.7 | 67.7683 | 14.1148 | 5.9933 | 36.0224 | 101.0173 | 8.7099 | 210.5379 | 126.7813 | 273.4448 | 10.7276 | 54.0366 | 2.9874 | 178 | 43.1044 | 0 | 319.1453 | 0
9696 | 885.2892 | 5.5983 | 25.7171 | 97.9646 | 71.4873 | 6.6497 | 63.889 | 13.9742 | 5.6077 | 21.2174 | 60.9277 | 8.7859 | 59.9369 | 77.8634 | 186.3405 | 10.7594 | 33.3727 | 2.5004 | 154 | 41.17 | 0 | 167.1599 | 0
9697 | 881.183 | 3.3891 | 25.647 | 97.5839 | 72.4838 | 5.7003 | 63.754 | 13.9142 | 5.6328 | 31.0285 | 90.5142 | 8.5839 | 198.4764 | 113.8745 | 257.3799 | 10.7062 | 52.0275 | 2.5581 | 143 | 39.2559 | 0 | 330.1742 | 0
9698 | 849.1188 | 2.9468 | 25.6028 | 95.5327 | 72.4814 | 5.7 | 65.2307 | 13.934 | 5.6778 | 32.9903 | 90.312 | 8.5551 | 197.1776 | 110.1391 | 241.9215 | 10.6977 | 52.0423 | 2.5415 | 137 | 39.1044 | 0 | 336.9544 | 0
9699 | 829.1547 | 2.7529 | 25.5799 | 95.9391 | 73.4808 | 4.7503 | 62.3892 | 13.8035 | 5.7788 | 32.4085 | 89.9602 | 8.5879 | 191.0694 | 109.0562 | 246.8127 | 10.3673 | 52.1012 | 2.4355 | 129 | 39.9198 | 0 | 337.5846 | 0
9700 | 820.5772 | 2.5109 | 25.522 | 96.6804 | 72.4825 | 5.6997 | 64.0245 | 13.7993 | 5.8415 | 32.4346 | 89.6685 | 8.5877 | 188.3673 | 108.3818 | 254.3021 | 10.5674 | 52.0887 | 2.4105 | 123 | 38.0038 | 0 | 336.3157 | 0
9701 | 820.646 | 3.0499 | 25.3875 | 96.6617 | 71.4847 | 6.6497 | 65.5247 | 13.7037 | 5.6278 | 32.1196 | 88.9267 | 8.4755 | 192.5632 | 107.8823 | 244.0716 | 10.6527 | 53.2819 | 2.4391 | 117 | 37.0374 | 0 | 353.3916 | 0
9702 | 830.1768 | 4.1444 | 35.923 | 98.313 | 71.4798 | 6.65 | 69.2007 | 13.6966 | 5.8195 | 34.4763 | 90.1793 | 13.8127 | 200.1526 | 110.6449 | 240.3037 | 10.5825 | 55.5857 | 2.4536 | 134 | 38.3226 | 0 | 409.6564 | 0
9703 | 873.9408 | 6.8171 | 52.1447 | 103.9677 | 71.4748 | 6.65 | 84.3283 | 13.7374 | 8.0083 | 59.3659 | 101.3058 | 24.5247 | 233.441 | 164.6356 | 260.7063 | 13.5259 | 54.0024 | 2.7247 | 195 | 47.9432 | 0 | 448.127 | 0
9704 | 926.8397 | 12.8767 | 78.1359 | 106.4347 | 64.475 | 13.2982 | 111.8781 | 14.065 | 13.6818 | 92.5417 | 142.1069 | 34.543 | 283.7443 | 237.0325 | 349.8403 | 29.2675 | 58.7767 | 3.5712 | 237 | 59.596 | 0 | 485.1915 | 0
9705 | 994.3306 | 20.7311 | 93.3577 | 117.2032 | 62.4756 | 15.1995 | 130.8271 | 17.0566 | 24.6122 | 101.9405 | 173.4626 | 36.8993 | 340.9618 | 297.2773 | 462.9609 | 38.0352 | 72.5841 | 6.8185 | 301 | 66.9989 | 0 | 559.8486 | 0.016823
9706 | 1088.9805 | 20.7818 | 101.8701 | 126.9226 | 62.4775 | 15.2 | 147.3456 | 17.9274 | 24.9012 | 106.1051 | 189.537 | 34.6865 | 405.0058 | 339.774 | 549.5182 | 40.2485 | 97.9025 | 10.0557 | 365 | 73.497 | 0 | 613.2241 | 0.042004
9707 | 1120.8172 | 14.9232 | 105.793 | 133.3485 | 60.4774 | 17.0995 | 152.6574 | 18.1966 | 13.4106 | 109.5019 | 196.9466 | 37.3845 | 426.3854 | 355.5646 | 603.7202 | 40.7315 | 105.3303 | 15.0798 | 390 | 77.5508 | 0 | 618.2562 | 0.059836
9708 | 1146.7626 | 11.4644 | 106.4907 | 143.6737 | 58.4769 | 18.9995 | 149.565 | 18.2489 | 8.1014 | 99.2457 | 191.3062 | 37.3768 | 426.2464 | 367.9735 | 615.3882 | 40.7343 | 104.7231 | 18.7496 | 376 | 77.9583 | 0 | 625.7818 | 0.082138
9709 | 1142.0543 | 11.205 | 102.3041 | 133.553 | 60.4804 | 17.1005 | 151.2698 | 17.7612 | 7.3517 | 91.802 | 184.8948 | 35.9979 | 420.8437 | 358.8806 | 598.2795 | 40.9539 | 102.1496 | 19.4796 | 363 | 74.5208 | 0 | 667.7037 | 0.071115
9710 | 1162.6303 | 9.9869 | 102.681 | 136.015 | 62.4776 | 15.2048 | 152.6423 | 17.4207 | 9.618 | 100.6721 | 188.2431 | 35.247 | 431.8638 | 359.0954 | 598.608 | 43.3175 | 103.948 | 19.8141 | 327 | 74.7908 | 0 | 649.7917 | 0.077276
9711 | 1164.608 | 8.1567 | 107.3211 | 139.936 | 59.4856 | 18.045 | 150.3549 | 17.5176 | 10.4338 | 107.5872 | 190.0685 | 35.2478 | 454.5317 | 371.5979 | 584.735 | 43.2087 | 106.8872 | 20.3427 | 307 | 76.2809 | 0 | 627.3744 | 0.07082
9712 | 1128.5539 | 8.7851 | 101.0747 | 138.0114 | 60.4815 | 17.1003 | 150.5215 | 17.2677 | 10.0933 | 105.7164 | 190.7126 | 36.3771 | 439.7225 | 362.7214 | 557.5575 | 41.9614 | 105.721 | 20.3708 | 280 | 67.5127 | 0 | 626.091 | 0.017653
9713 | 1101.9108 | 6.5619 | 90.3285 | 134.5297 | 64.4795 | 13.3011 | 137.1295 | 17.1047 | 12.947 | 90.8981 | 188.9891 | 36.1747 | 417.755 | 335.8972 | 521.9725 | 36.8333 | 101.4666 | 19.0544 | 241 | 64.083 | 0 | 577.5807 | 0
9714 | 1050.9722 | 6.2454 | 76.7386 | 124.7629 | 66.4771 | 11.4005 | 128.3382 | 16.1566 | 17.13 | 80.0725 | 174.6912 | 37.4899 | 375.8156 | 267.188 | 440.5281 | 21.6884 | 95.01 | 17.1197 | 208 | 60.5957 | 0 | 448.6107 | 0
9715 | 981.8839 | 5.8929 | 72.4636 | 110.2403 | 69.477 | 8.5508 | 112.7095 | 15.4998 | 16.5928 | 60.0139 | 151.4349 | 32.2991 | 317.3357 | 196.8578 | 379.3788 | 16.53 | 88.4606 | 15.9069 | 220 | 57.8032 | 0 | 390.9754 | 0
9716 | 930.2946 | 5.9113 | 63.7916 | 102.819 | 72.4801 | 5.7008 | 90.921 | 14.6558 | 10.965 | 50.8707 | 142.7956 | 16.3528 | 272.6918 | 168.9955 | 341.6657 | 13.2486 | 80.7113 | 9.967 | 182 | 49.6841 | 0 | 363.8863 | 0
9717 | 901.2702 | 6.0012 | 34.545 | 101.3315 | 72.487 | 5.7 | 86.6555 | 14.3645 | 7.6985 | 47.4176 | 136.9662 | 10.4755 | 246.8087 | 147.9292 | 332.8088 | 11.6643 | 77.1237 | 5.8468 | 167 | 46.3834 | 0 | 333.9531 | 0
9718 | 879.6886 | 5.2919 | 24.8718 | 99.824 | 71.4866 | 6.6497 | 84.4197 | 14.1553 | 7.1083 | 42.0498 | 120.6897 | 10.6529 | 222.9888 | 119.5632 | 299.6444 | 11.4816 | 76.5398 | 4.5489 | 155 | 42.0021 | 0 | 325.423 | 0
9719 | 862.9254 | 4.6168 | 24.8439 | 98.3739 | 71.4838 | 6.65 | 72.8457 | 14.2304 | 6.7862 | 38.312 | 99.0278 | 12.7102 | 211.8021 | 104.2817 | 260.4715 | 11.2487 | 75.7158 | 3.9649 | 139 | 41.0497 | 0 | 332.7188 | 0
9720 | 838.9444 | 3.3893 | 24.8177 | 96.9919 | 70.4841 | 7.5997 | 71.0605 | 14.0178 | 6.5983 | 23.6106 | 59.9407 | 11.9078 | 61.4064 | 63.2344 | 171.8827 | 11.2892 | 47.1691 | 3.4893 | 130 | 40.0183 | 0 | 166.6769 | 0
9721 | 835.178 | 2.6212 | 24.738 | 95.6284 | 72.4812 | 5.7005 | 67.5694 | 13.8672 | 6.6126 | 37.31 | 90.7768 | 10.2691 | 199.0385 | 90.1639 | 263.917 | 11.2609 | 74.033 | 2.8449 | 118 | 37.8682 | 0 | 322.2568 | 0
9722 | 817.8799 | 2.6474 | 24.8324 | 92.4834 | 72.4833 | 5.7 | 65.5224 | 14.0867 | 6.5661 | 37.7068 | 90.5312 | 9.8718 | 193.3979 | 87.3679 | 258.2213 | 11.2035 | 73.8205 | 2.6911 | 114 | 36.9916 | 0 | 319.9752 | 0
9723 | 800.1744 | 2.829 | 24.7966 | 91.5124 | 73.4801 | 4.7503 | 68.0614 | 13.95 | 6.4537 | 36.5016 | 89.3248 | 9.8433 | 189.9904 | 85.6015 | 240.5951 | 11.1417 | 74.1942 | 2.5385 | 110 | 36.4779 | 0 | 321.9103 | 0
9724 | 797.455 | 2.9411 | 24.6704 | 92.0936 | 69.4818 | 8.5489 | 65.9098 | 13.8617 | 6.377 | 36.7851 | 88.8497 | 9.75 | 189.5175 | 86.8543 | 243.1967 | 10.975 | 73.6799 | 2.4725 | 107 | 36.0469 | 0 | 319.0468 | 0
9725 | 794.1215 | 3.3125 | 24.6168 | 91.0409 | 72.48 | 5.7008 | 65.0323 | 13.8083 | 6.2525 | 35.619 | 88.9766 | 9.6378 | 194.2056 | 85.2982 | 243.3914 | 11.0203 | 74.9141 | 2.4712 | 104 | 36.4521 | 0 | 335.6823 | 0
9726 | 804.9757 | 4.1188 | 32.2324 | 91.8899 | 72.4756 | 5.7 | 75.3307 | 13.94 | 6.5459 | 52.3468 | 90.0065 | 11.4447 | 205.2783 | 91.4764 | 234.7701 | 10.9946 | 76.6725 | 2.4944 | 109 | 39.9562 | 0 | 394.076 | 0
9727 | 831.3615 | 6.8521 | 51.5045 | 97.3511 | 71.4782 | 6.6497 | 90.7732 | 13.728 | 12.0765 | 87.9168 | 102.1788 | 20.0504 | 235.0901 | 160.8177 | 251.4076 | 13.5747 | 75.2695 | 3.926 | 196 | 47.2032 | 0 | 436.0667 | 0
9728 | 883.8532 | 11.9877 | 76.9891 | 99.2897 | 65.4812 | 12.3484 | 107.7612 | 14.2249 | 13.5945 | 107.5073 | 143.9836 | 32.4366 | 282.405 | 242.9439 | 343.7705 | 28.8881 | 77.2867 | 7.7893 | 309 | 57.3339 | 0 | 479.1024 | 0
9729 | 963.0984 | 12.8461 | 90.8255 | 109.4628 | 62.4794 | 15.1992 | 131.6578 | 16.0819 | 16.548 | 108.7606 | 172.9873 | 38.2016 | 336.536 | 300.1813 | 467.5602 | 37.0463 | 85.95 | 16.5326 | 327 | 65.0597 | 0 | 541.4041 | 0.016041
9730 | 1072.3795 | 12.6012 | 96.3447 | 121.6738 | 61.4758 | 16.1497 | 141.7877 | 17.0634 | 18.1912 | 112.1055 | 191.7941 | 39.3466 | 384.8087 | 329.5092 | 560.3199 | 40.66 | 92.6887 | 17.7879 | 369 | 70.8205 | 0 | 612.8783 | 0.030817
9731 | 1144.1365 | 7.4344 | 100.8038 | 130.4286 | 61.4734 | 16.15 | 144.8574 | 17.3788 | 18.6151 | 107.9475 | 199.6704 | 41.6633 | 406.0599 | 343.8333 | 586.1147 | 41.7753 | 98.0542 | 17.1575 | 389 | 73.2674 | 0 | 671.8623 | 0.036303
9732 | 1179.8577 | 5.2594 | 101.9192 | 138.8979 | 58.4744 | 18.9992 | 147.2753 | 16.8226 | 19.1634 | 116.4039 | 195.5606 | 40.6676 | 412.1282 | 354.4845 | 593.5204 | 41.7749 | 100.6461 | 17.9488 | 361 | 82.5594 | 0 | 692.7549 | 0.049901
9733 | 1159.7844 | 8.9939 | 100.6537 | 139.9739 | 60.4767 | 17.1005 | 144.2396 | 16.406 | 19.6009 | 118.0116 | 197.0053 | 39.7651 | 414.7824 | 361.1647 | 599.6532 | 42.416 | 101.6225 | 19.0596 | 370 | 79.8537 | 0 | 680.5624 | 0.061764
9734 | 1196.5604 | 16.2343 | 103.8495 | 143.356 | 61.4745 | 16.1503 | 155.414 | 17.3793 | 23.4076 | 111.431 | 202.5413 | 41.0023 | 485.2406 | 362.4234 | 612.5258 | 43.3751 | 102.5077 | 20.1033 | 306 | 83.5936 | 0 | 709.3822 | 0.070173
9735 | 1212.2617 | 19.0653 | 103.3206 | 153.1268 | 63.4751 | 14.2505 | 158.1674 | 17.2704 | 24.01 | 112.2722 | 203.0395 | 36.7354 | 558.395 | 368.8847 | 617.5879 | 44.2332 | 100.2515 | 20.7489 | 284 | 78.4272 | 0 | 684.8361 | 0.031648
9736 | 1192.9429 | 18.8043 | 98.4099 | 143.2326 | 62.4765 | 15.1997 | 150.0996 | 16.8988 | 18.6748 | 110.1302 | 207.182 | 37.7412 | 565.4609 | 357.8947 | 614.7644 | 42.9918 | 87.4061 | 20.9376 | 263 | 73.4855 | 0 | 683.6575 | 0.010512
9737 | 1160.0217 | 11.9989 | 88.7517 | 136.0453 | 67.4743 | 10.4513 | 136.1716 | 15.8841 | 16.2923 | 103.8199 | 203.0984 | 38.6803 | 542.2804 | 338.0836 | 563.0775 | 35.4628 | 80.8882 | 20.0469 | 259 | 65.2911 | 0 | 614.582 | 0
9738 | 1096.9607 | 10.1992 | 78.3541 | 123.065 | 71.4722 | 6.6511 | 119.0724 | 14.3525 | 18.6638 | 82.2287 | 181.6611 | 38.4298 | 496.5011 | 279.0827 | 483.2719 | 19.4027 | 75.0584 | 18.8714 | 224 | 57.2403 | 0 | 456.2097 | 0
9739 | 1019.779 | 7.7083 | 73.662 | 113.411 | 72.4766 | 5.7003 | 105.6953 | 14.0377 | 17.9796 | 62.3816 | 155.9729 | 29.3976 | 458.1643 | 195.2902 | 392.995 | 13.1668 | 68.7523 | 14.7505 | 212 | 51.2165 | 0 | 388.7213 | 0
9740 | 964.0622 | 6.4884 | 63.8739 | 112.8919 | 72.4814 | 5.7 | 77.9851 | 14.0443 | 17.8605 | 59.7385 | 142.8074 | 13.7445 | 426.19 | 164.5884 | 347.6796 | 11.9651 | 60.4119 | 7.8618 | 183 | 43.9391 | 0 | 346.4944 | 0
9741 | 935.8389 | 5.9156 | 34.3022 | 108.9306 | 72.4806 | 5.7 | 68.9612 | 14.1641 | 17.9108 | 53.849 | 129.5323 | 8.7269 | 398.5568 | 146.9946 | 331.0422 | 11.5497 | 53.645 | 4.638 | 180 | 40.0042 | 0 | 338.9927 | 0
9742 | 903.5458 | 5.3999 | 24.5832 | 103.4117 | 72.4794 | 5.7 | 70.9938 | 14.0595 | 15.6255 | 43.9421 | 109.0862 | 8.8667 | 373.7021 | 127.2769 | 303.4839 | 11.4113 | 50.7637 | 3.5268 | 162 | 35.7424 | 0 | 338.3487 | 0
9743 | 858.5159 | 4.2339 | 24.3598 | 103.4817 | 72.4785 | 5.7 | 66.2898 | 13.9546 | 9.1242 | 37.5814 | 92.9415 | 8.7184 | 289.5817 | 116.0067 | 270.759 | 11.3877 | 49.9265 | 3.1594 | 145 | 34.7405 | 0 | 340.7457 | 0
9744 | 822.9872 | 3.0853 | 24.2643 | 103.9163 | 72.48 | 5.7 | 66.0027 | 14.0356 | 6.8642 | 24.439 | 58.2056 | 8.6156 | 76.1901 | 66.4308 | 169.1622 | 11.1374 | 31.4774 | 3.0543 | 127 | 35.5508 | 0 | 173.1644 | 0
9745 | 813.3474 | 2.7046 | 24.4402 | 103.6374 | 73.4852 | 4.7503 | 69.1287 | 14.087 | 6.893 | 39.1375 | 87.3988 | 8.6446 | 191.1852 | 88.389 | 240.519 | 11.2941 | 50.0595 | 3.053 | 119 | 34.922 | 0 | 335.2344 | 0
9746 | 809.141 | 2.6563 | 24.5011 | 101.2284 | 72.4858 | 5.6997 | 65.7384 | 14.0713 | 6.7738 | 38.7369 | 87.8347 | 8.9294 | 190.8526 | 84.8 | 245.2993 | 11.3623 | 50.1987 | 3.0508 | 117 | 33.9317 | 0 | 328.2957 | 0
9747 | 801.2038 | 2.7639 | 24.3868 | 98.9469 | 72.4839 | 5.7 | 65.4502 | 14.0235 | 6.806 | 39.0901 | 87.5952 | 8.885 | 192.6835 | 83.4212 | 249.5935 | 11.2579 | 50.947 | 3.0103 | 113 | 33.0373 | 0 | 327.3888 | 0
9748 | 804.9319 | 3.1861 | 24.5669 | 99.2158 | 70.4859 | 7.5995 | 68.6068 | 14.2311 | 6.7878 | 38.3042 | 87.3547 | 8.7015 | 191.0022 | 83.3509 | 235.4968 | 11.2842 | 50.4278 | 2.9918 | 110 | 32.8987 | 0 | 330.4979 | 0
9749 | 794.7531 | 3.2675 | 24.4442 | 99.7043 | 72.4833 | 5.7005 | 65.3395 | 14.0729 | 6.6573 | 38.4984 | 87.0224 | 8.6137 | 194.961 | 83.9459 | 221.7423 | 11.0189 | 51.4445 | 3.0137 | 107 | 32.7111 | 0 | 358.4643 | 0
9750 | 807.8122 | 4.026 | 31.2975 | 100.0758 | 72.4799 | 5.7 | 70.3998 | 13.8521 | 7.1547 | 49.4719 | 89.0087 | 9.611 | 203.9114 | 89.4312 | 231.7748 | 11.1674 | 53.6011 | 3.0272 | 108 | 34.4539 | 0 | 410.1355 | 0
9751 | 853.5105 | 7.1545 | 49.6214 | 105.1184 | 70.4805 | 7.5995 | 92.2636 | 13.7183 | 9.5917 | 78.3215 | 101.1538 | 19.26 | 237.1629 | 156.511 | 267.5978 | 13.6208 | 51.034 | 3.0341 | 158 | 45.7665 | 0 | 455.0994 | 0
9752 | 906.291 | 14.5215 | 77.9281 | 106.8652 | 64.477 | 13.2984 | 107.1933 | 14.6464 | 9.6673 | 99.7093 | 142.0867 | 32.8174 | 283.1189 | 233.5407 | 373.5571 | 28.101 | 54.1975 | 8.5602 | 253 | 60.1918 | 0 | 487.9078 | 0
9753 | 984.1918 | 19.4046 | 93.4973 | 118.2249 | 63.4865 | 14.2379 | 123.7364 | 16.5579 | 7.7805 | 99.7287 | 178.5907 | 33.5791 | 339.0452 | 284.8935 | 478.8997 | 37.7693 | 63.568 | 16.754 | 290 | 70.6906 | 0 | 554.1094 | 0.015387
9754 | 1055.5398 | 16.4568 | 96.9527 | 131.9067 | 60.4602 | 17.1111 | 143.5665 | 17.9378 | 12.406 | 100.8487 | 192.619 | 34.0207 | 385.0906 | 316.7698 | 531.2337 | 42.0138 | 77.9602 | 18.3773 | 348 | 74.0069 | 0 | 611.3545 | 0.023049
9755 | 1107.6452 | 15.1748 | 99.3867 | 137.8056 | 60.4863 | 17.0858 | 146.8623 | 17.981 | 22.2988 | 96.2417 | 204.0157 | 41.0038 | 407.6478 | 345.2447 | 579.5828 | 42.4532 | 101.6593 | 17.3783 | 355 | 79.8085 | 0 | 652.0142 | 0.027444
9756 | 1131.1232 | 13.331 | 101.8396 | 136.4807 | 58.463 | 19.0137 | 146.0201 | 17.6285 | 23.8778 | 98.7557 | 213.5676 | 39.5218 | 419.2664 | 362.8199 | 588.2666 | 42.269 | 113.7454 | 17.555 | 322 | 84.161 | 0 | 668.0251 | 0.032246
9757 | 1145.5757 | 10.077 | 100.4198 | 138.6756 | 62.4779 | 15.2011 | 146.5877 | 17.3098 | 19.0803 | 90.2042 | 209.7737 | 41.8144 | 418.0108 | 356.2123 | 574.092 | 43.8487 | 114.8313 | 19.1496 | 358 | 79.1113 | 0 | 702.4611 | 0.044577
9758 | 1167.547 | 13.5798 | 101.1004 | 138.0597 | 61.4784 | 16.1497 | 141.8773 | 17.1609 | 20.086 | 92.9998 | 212.3773 | 41.1536 | 423.565 | 359.9223 | 587.5813 | 45.1925 | 113.8795 | 20.595 | 304 | 78.3255 | 0 | 704.5673 | 0.03276
9759 | 1178.0622 | 11.7595 | 100.0311 | 138.434 | 55.4809 | 21.8484 | 145.3091 | 17.6413 | 19.0258 | 95.6717 | 208.1502 | 37.585 | 412.8125 | 357.0588 | 598.8712 | 43.3009 | 115.6243 | 20.5626 | 286 | 77.0359 | 0 | 733.7939 | 0.029835
9760 | 1162.2796 | 9.4393 | 96.7747 | 134.9381 | 57.4825 | 19.9505 | 137.8335 | 16.7905 | 9.8767 | 92.403 | 199.5875 | 34.9004 | 390.4017 | 331.8278 | 586.429 | 41.1324 | 114.5118 | 20.0504 | 293 | 65.6813 | 0 | 686.4647 | 0.02218
9761 | 1103.5107 | 6.9286 | 93.6252 | 130.1821 | 64.4813 | 13.3018 | 126.5818 | 15.6712 | 6.547 | 84.9405 | 193.5585 | 33.9213 | 371.1067 | 301.97 | 512.5484 | 33.3704 | 107.7554 | 19.7298 | 270 | 58.1492 | 0 | 525.8513 | 0.00087569
9762 | 1041.164 | 6.1635 | 82.1999 | 121.5993 | 72.4816 | 5.7021 | 118.3587 | 14.5058 | 9.9843 | 76.1215 | 186.8279 | 36.2332 | 329.753 | 248.7684 | 423.254 | 21.0045 | 99.2316 | 18.1937 | 226 | 51.0372 | 0 | 392.2212 | 0
9763 | 986.0606 | 6.0531 | 50.2073 | 107.3934 | 72.4828 | 5.7 | 96.8749 | 13.8831 | 12.2106 | 63.7722 | 154.1899 | 33.1362 | 288.3393 | 186.5201 | 343.0268 | 15.0564 | 91.5103 | 14.795 | 215 | 45.8287 | 0 | 330.8833 | 0
9764 | 947.5675 | 5.8441 | 38.0373 | 102.8501 | 72.4842 | 5.7 | 74.4881 | 14.1488 | 11.1117 | 57.3727 | 128.4106 | 20.051 | 257.9617 | 163.8231 | 310.3295 | 13.3907 | 81.3916 | 8.608 | 196 | 45.9455 | 0 | 299.0466 | 0
9765 | 918.534 | 5.4691 | 28.3909 | 101.2962 | 70.4889 | 7.5995 | 72.9753 | 14.1093 | 9.9396 | 52.6873 | 100.6682 | 13.9788 | 233.7342 | 143.0616 | 287.7395 | 12.0353 | 73.0504 | 5.936 | 177 | 39.3766 | 0 | 296.0605 | 0
9766 | 891.0672 | 5.4418 | 24.608 | 100.7924 | 72.4822 | 5.7005 | 66.1607 | 13.8658 | 9.3903 | 41.048 | 88.0655 | 13.3974 | 210.1544 | 123.2391 | 261.9205 | 10.8418 | 69.608 | 5.289 | 177 | 37.0795 | 0 | 299.7223 | 0
9767 | 870.8286 | 4.9334 | 24.3071 | 99.8175 | 72.4805 | 5.7016 | 64.885 | 13.894 | 9.2815 | 34.4255 | 86.3425 | 13.2529 | 199.9843 | 118.2947 | 249.5688 | 10.3533 | 68.7777 | 4.9694 | 168 | 38.0888 | 0 | 296.9112 | 0
9768 | 843.7355 | 3.5209 | 23.994 | 99.7587 | 72.4827 | 5.6984 | 70.6344 | 13.7692 | 8.4802 | 23.0058 | 56.6012 | 13.3653 | 58.3001 | 75.3381 | 169.3373 | 10.2822 | 43.1889 | 4.4763 | 155 | 38.0769 | 0 | 156.6479 | 0
9769 | 843.0402 | 3.1474 | 24.4286 | 100.7142 | 72.4823 | 5.7 | 66.1168 | 13.8148 | 7.214 | 35.2129 | 85.2105 | 13.3173 | 182.4895 | 116.1757 | 251.9738 | 10.1814 | 69.7084 | 4.1223 | 162 | 37.3262 | 0 | 304.1501 | 0
9770 | 838.1944 | 3.9655 | 24.5711 | 101.5232 | 72.4847 | 5.7016 | 63.4551 | 14.0764 | 6.668 | 36.2213 | 85.2145 | 13.2011 | 180.4843 | 113.768 | 264.2921 | 10.2958 | 69.7162 | 3.999 | 155 | 36.8786 | 0 | 312.8944 | 0
9771 | 833.6142 | 3.3957 | 24.455 | 101.1997 | 71.4862 | 6.6482 | 69.4656 | 13.9015 | 6.6214 | 35.4869 | 84.9139 | 13.147 | 178.7533 | 110.1113 | 266.1108 | 10.2844 | 69.2258 | 4.1746 | 143 | 35.8676 | 0 | 301.7553 | 0
9772 | 817.8219 | 3.1657 | 24.2009 | 100.7672 | 72.4789 | 5.7003 | 66.954 | 13.7613 | 6.8021 | 34.4439 | 84.0111 | 13.257 | 175.6863 | 94.0345 | 250.3266 | 10.2112 | 69.017 | 3.4184 | 135 | 36.2764 | 0 | 302.085 | 0
9773 | 810.9992 | 3.3498 | 24.4697 | 101.1478 | 72.4843 | 5.7 | 63.1953 | 13.7307 | 6.3683 | 33.1107 | 83.1386 | 13.0359 | 172.6099 | 87.1683 | 241.5914 | 10.2191 | 70.9034 | 2.8331 | 130 | 35.2852 | 0 | 301.1854 | 0
9774 | 806.3647 | 4.1273 | 25.5051 | 101.5558 | 72.4824 | 5.7 | 67.7962 | 13.9709 | 6.4495 | 33.71 | 84.0424 | 12.8822 | 171.1605 | 85.6265 | 247.8147 | 9.9856 | 72.9638 | 2.7652 | 116 | 34.9535 | 0 | 304.0884 | 0
9775 | 814.4469 | 5.0993 | 46.0481 | 103.6322 | 72.4797 | 5.7 | 66.8162 | 13.7715 | 6.5815 | 34.6843 | 85.2738 | 12.8256 | 171.0317 | 85.9435 | 236.7221 | 10.0974 | 70.4092 | 2.7618 | 111 | 37.1744 | 0 | 299.1054 | 0
9776 | 818.1167 | 4.2815 | 52.9841 | 102.3875 | 72.482 | 5.7 | 64.6833 | 13.4211 | 6.1815 | 32.3416 | 89.3061 | 13.6243 | 177.1925 | 87.3201 | 222.8294 | 9.9514 | 68.2786 | 2.8491 | 115 | 42.2547 | 0 | 299.4772 | 0
9777 | 819.1986 | 3.2133 | 58.9641 | 101.3375 | 72.4777 | 5.7 | 77.0766 | 13.215 | 5.5757 | 38.573 | 112.7277 | 17.8451 | 184.1998 | 86.4034 | 225.6891 | 9.7035 | 67.8082 | 3.2752 | 111 | 46.6883 | 0 | 297.7268 | 0.17455
9778 | 851.0687 | 3.5099 | 71.5091 | 100.5854 | 72.4833 | 5.7 | 78.6199 | 13.378 | 6.69 | 58.9589 | 128.3924 | 19.193 | 195.1168 | 89.5951 | 226.8234 | 9.6938 | 68.3404 | 5.3711 | 125 | 47.122 | 0 | 305.3526 | 0.22604
9779 | 872.9342 | 3.4559 | 78.3849 | 99.6578 | 68.487 | 9.4989 | 75.0318 | 13.5271 | 6.0462 | 65.5029 | 141.9028 | 19.4572 | 214.1467 | 109.363 | 230.0596 | 9.414 | 68.5005 | 10.7254 | 145 | 47.3734 | 0 | 314.0537 | 0.23494
9780 | 873.6796 | 3.2852 | 78.8613 | 100.2812 | 70.4794 | 7.6005 | 79.0633 | 13.266 | 5.5384 | 64.2503 | 130.0634 | 19.1715 | 231.48 | 119.1268 | 242.718 | 9.0359 | 68.0635 | 12.7264 | 161 | 48.5459 | 0 | 333.5386 | 0.15856
9781 | 877.7028 | 3.1623 | 78.5672 | 101.3915 | 71.4761 | 6.6503 | 79.4868 | 13.1239 | 5.7714 | 62.7563 | 126.4685 | 19.5062 | 238.4733 | 122.7493 | 248.5551 | 8.9852 | 67.9361 | 12.6884 | 209 | 48.0662 | 0 | 336.4551 | 0.18134
9782 | 882.5624 | 4.3381 | 75.6131 | 103.579 | 71.4785 | 6.65 | 78.5969 | 13.1946 | 5.8003 | 61.4677 | 133.7428 | 19.3623 | 242.1086 | 128.5095 | 262.272 | 9.2768 | 68.3733 | 12.7323 | 186 | 49.4219 | 0 | 320.5277 | 0.094205
9783 | 871.8039 | 8.585 | 48.6976 | 102.5257 | 72.4788 | 5.7003 | 93.719 | 13.1403 | 7.0732 | 62.3053 | 139.5564 | 19.9097 | 240.729 | 131.2615 | 287.3297 | 9.6396 | 68.8678 | 10.7224 | 190 | 53.1313 | 0 | 312.6656 | 0.042991
9784 | 873.8882 | 5.9102 | 37.5926 | 107.6151 | 71.4795 | 6.6497 | 95.0046 | 13.094 | 7.8623 | 55.0064 | 139.1462 | 19.4369 | 232.7956 | 143.7054 | 315.0105 | 9.4562 | 68.1376 | 5.9161 | 187 | 49.8143 | 0 | 317.5867 | 0.029434
9785 | 871.1655 | 3.9074 | 28.0387 | 112.0473 | 73.4796 | 4.7505 | 79.9897 | 13.8676 | 9.6669 | 36.3283 | 136.086 | 11.7687 | 228.9695 | 150.7682 | 329.9461 | 9.5747 | 68.8757 | 4.1062 | 178 | 47.8844 | 0 | 309.6821 | 0.0021414
9786 | 852.9209 | 5.7112 | 25.4641 | 107.9617 | 71.4823 | 6.6495 | 70.0125 | 15.1086 | 10.2983 | 34.4288 | 128.1482 | 10.6359 | 230.1103 | 156.2669 | 313.8976 | 9.9955 | 71.1664 | 4.4727 | 192 | 46.0427 | 0 | 310.6717 | 0
9787 | 845.0335 | 10.297 | 25.1129 | 105.139 | 72.4834 | 5.7003 | 69.8924 | 14.4149 | 8.2737 | 38.8299 | 103.7886 | 11.5366 | 226.7665 | 162.2139 | 294.6591 | 10.1612 | 71.3021 | 4.7732 | 215 | 44.6625 | 0 | 303.4206 | 0
9788 | 837.2145 | 12.1758 | 24.8221 | 105.1066 | 71.4879 | 6.6497 | 65.8333 | 14.208 | 7.5015 | 38.5249 | 94.2849 | 12.0222 | 214.514 | 166.9067 | 282.087 | 10.2011 | 72.0482 | 4.8985 | 202 | 42.496 | 0 | 301.6097 | 0
9789 | 817.0811 | 11.6746 | 24.5461 | 104.5804 | 72.485 | 5.7003 | 67.5786 | 14.0753 | 7.2305 | 38.2957 | 93.6102 | 11.7504 | 204.78 | 152.6791 | 274.5007 | 9.943 | 70.9436 | 4.7414 | 195 | 41.3971 | 0 | 311.674 | 0
9790 | 803.8428 | 7.4177 | 24.5355 | 101.6414 | 72.4908 | 5.7 | 75.6555 | 13.994 | 7.0627 | 37.8232 | 92.0027 | 11.5421 | 197.044 | 138.0771 | 269.0282 | 10.058 | 70.5452 | 3.6223 | 186 | 40.9294 | 0 | 314.1519 | 0
9791 | 793.3905 | 5.2523 | 24.5505 | 98.1777 | 72.4873 | 5.7 | 78.0712 | 13.9502 | 6.6172 | 35.2887 | 89.7176 | 11.5406 | 191.6858 | 124.655 | 267.1346 | 10.1533 | 70.4338 | 2.9607 | 170 | 41.8869 | 0 | 313.9152 | 0
9792 | 773.3855 | 3.7619 | 24.4691 | 97.6003 | 72.481 | 5.7 | 71.5366 | 14.0525 | 6.5073 | 22.3023 | 58.2873 | 11.0732 | 56.4159 | 72.3393 | 177.2204 | 10.0848 | 44.271 | 3.194 | 143 | 40.011 | 0 | 158.3344 | 0
9793 | 784.3432 | 3.4236 | 24.3303 | 97.8344 | 72.4827 | 5.7 | 70.9954 | 13.9409 | 6.4727 | 34.9363 | 87.606 | 9.2643 | 187.1589 | 103.1926 | 250.3295 | 10.0818 | 70.2431 | 4.0927 | 133 | 39.8582 | 0 | 304.426 | 0
9794 | 771.7648 | 3.2981 | 24.2747 | 97.1738 | 72.4833 | 5.7 | 65.7784 | 13.8178 | 6.4858 | 34.0327 | 87.2211 | 8.4454 | 183.3235 | 94.5949 | 244.0872 | 9.8827 | 69.7368 | 4.3563 | 127 | 41.4023 | 0 | 298.8693 | 0
9795 | 759.5414 | 3.1147 | 24.2651 | 97.2842 | 66.4861 | 11.3984 | 65.2192 | 13.7791 | 6.2635 | 34.404 | 85.9835 | 8.9523 | 175.9516 | 90.966 | 242.0691 | 10.083 | 69.5793 | 3.9923 | 127 | 42.0885 | 0 | 294.8409 | 0
9796 | 757.4121 | 2.8778 | 24.2464 | 97.2773 | 66.4817 | 11.4 | 68.9897 | 13.7559 | 6.256 | 34.4041 | 85.4892 | 8.2484 | 171.6241 | 90.5621 | 241.744 | 10.1312 | 69.4941 | 3.1665 | 122 | 41.3893 | 0 | 291.5935 | 0
9797 | 753.9632 | 3.117 | 24.4188 | 99.296 | 68.4787 | 9.5032 | 65.4786 | 14.0221 | 6.3043 | 34.096 | 85.8651 | 7.3541 | 168.894 | 87.8557 | 239.5427 | 10.1013 | 71.0598 | 2.7168 | 125 | 43.9703 | 0 | 289.8684 | 0
9798 | 753.8335 | 4.3135 | 24.407 | 99.6066 | 72.4851 | 5.6984 | 64.495 | 14.0076 | 6.7902 | 35.1155 | 87.1712 | 7.2511 | 167.6339 | 86.1509 | 233.1923 | 10.1291 | 73.2906 | 2.6876 | 125 | 46.6677 | 0 | 294.513 | 0
9799 | 767.8376 | 5.2073 | 24.6099 | 100.2043 | 70.4833 | 7.5995 | 69.5333 | 13.8659 | 6.8223 | 34.1639 | 88.6834 | 7.2511 | 168.2146 | 86.8258 | 236.1069 | 9.902 | 70.8214 | 2.6766 | 116 | 38.5345 | 0 | 292.2 | 0
9800 | 774.701 | 4.2749 | 24.3311 | 98.1099 | 71.4862 | 6.6503 | 65.5377 | 13.5677 | 6.2655 | 31.2611 | 92.456 | 6.1276 | 172.5104 | 89.2098 | 237.4161 | 9.7832 | 68.6619 | 2.8673 | 116 | 39.2081 | 0 | 285.7919 | 0
9801 | 778.3567 | 3.0561 | 24.537 | 96.6287 | 72.4816 | 5.7003 | 61.5588 | 13.3693 | 5.6113 | 38.7859 | 102.4428 | 4.818 | 175.8983 | 90.2165 | 226.1918 | 9.6067 | 67.8393 | 3.4786 | 128 | 39.455 | 0 | 285.2147 | 0.019588
9802 | 782.9878 | 2.89 | 29.9031 | 96.1631 | 70.4781 | 7.5995 | 71.0221 | 13.2786 | 6.1538 | 60.3548 | 97.9949 | 4.4259 | 181.8681 | 101.4228 | 233.1336 | 9.5493 | 67.8281 | 3.844 | 151 | 41.2592 | 0 | 288.4069 | 0.059831
9803 | 817.0552 | 3.3809 | 36.5944 | 96.0131 | 70.4756 | 7.6 | 77.9775 | 13.3674 | 5.9168 | 71.8102 | 116.5709 | 4.3977 | 195.0974 | 119.0768 | 250.3931 | 9.5456 | 68.4618 | 3.8052 | 155 | 41.1811 | 0 | 291.8784 | 0.058815
9804 | 828.2833 | 4.3919 | 38.1717 | 96.6845 | 72.4759 | 5.7005 | 77.6841 | 13.1839 | 7.7955 | 72.7881 | 123.3691 | 4.5934 | 205.3652 | 128.6507 | 260.8022 | 9.3954 | 68.8074 | 3.742 | 177 | 43.0251 | 0 | 304.4693 | 0.067929
9805 | 831.9251 | 4.527 | 38.3561 | 98.1545 | 72.4766 | 5.7 | 94.9375 | 13.1039 | 10.2898 | 71.9993 | 135.9096 | 8.0594 | 215.1453 | 134.925 | 255.5584 | 9.5345 | 68.543 | 3.6422 | 176 | 42.7668 | 0 | 295.7597 | 0.066386
9806 | 830.5309 | 8.0976 | 38.1964 | 101.0106 | 72.4818 | 5.7 | 96.444 | 13.1333 | 10.2047 | 70.4389 | 159.1602 | 9.0754 | 221.5558 | 141.8562 | 253.7178 | 9.6098 | 67.9701 | 3.82 | 183 | 44.5789 | 0 | 304.6171 | 0.061474
9807 | 838.4208 | 10.1056 | 38.278 | 103.8208 | 73.4774 | 4.7503 | 71.527 | 13.0621 | 9.1718 | 65.6504 | 159.0244 | 8.8799 | 229.8364 | 147.0359 | 276.3937 | 9.6046 | 67.7443 | 3.9686 | 171 | 43.3478 | 0 | 295.9986 | 0.056642
9808 | 838.7667 | 5.5436 | 36.7182 | 103.5883 | 72.4763 | 5.6997 | 76.8505 | 13.3281 | 6.5938 | 57.4972 | 142.572 | 9.7064 | 227.6122 | 146.961 | 286.8473 | 9.7023 | 67.3233 | 4.452 | 177 | 44.6443 | 0 | 306.046 | 0.033921
9809 | 839.5873 | 3.462 | 27.187 | 101.8491 | 72.4775 | 5.7 | 96.3857 | 13.1532 | 5.5033 | 36.102 | 133.5596 | 10.3746 | 220.9575 | 134.154 | 290.4252 | 9.3736 | 67.8296 | 4.9128 | 161 | 44.8741 | 0 | 309.8806 | 0.0040384
9810 | 847.6799 | 5.013 | 24.3665 | 104.3463 | 72.4769 | 5.7 | 82.1784 | 13.541 | 6.2773 | 32.8864 | 135.7645 | 12.5406 | 221.9062 | 131.5611 | 294.7395 | 9.8213 | 69.0156 | 5.0862 | 162 | 45.5172 | 0 | 306.5153 | 0
9811 | 841.5478 | 5.4628 | 24.7169 | 105.3979 | 71.4844 | 6.6497 | 81.7092 | 14.0626 | 6.8624 | 36.3705 | 133.247 | 13.8104 | 219.2758 | 127.0341 | 304.2923 | 10.1558 | 70.641 | 5.0565 | 144 | 45.4355 | 0 | 311.5393 | 0
9812 | 824.8705 | 5.2171 | 25.0544 | 103.6774 | 70.4887 | 7.5997 | 88.6782 | 14.0774 | 7.0145 | 36.6976 | 129.1457 | 12.471 | 210.0572 | 119.7041 | 291.6926 | 10.1745 | 70.2322 | 5.0286 | 147 | 47.6867 | 0 | 309.9211 | 0
9813 | 804.7623 | 6.9693 | 25.2645 | 103.613 | 72.4852 | 5.7005 | 73.7129 | 14.0748 | 7.083 | 35.9985 | 116.606 | 11.1977 | 210.932 | 106.2245 | 262.0004 | 10.1707 | 69.915 | 4.7342 | 139 | 41.9398 | 0 | 298.2235 | 0
9814 | 791.5282 | 7.4106 | 25.1356 | 103.9908 | 72.485 | 5.7016 | 67.312 | 14.4727 | 6.9925 | 33.7344 | 98.0535 | 8.3731 | 205.6761 | 99.242 | 249.6407 | 9.9273 | 70.2085 | 4.1581 | 137 | 39.1941 | 0 | 311.0617 | 0
9815 | 773.2234 | 5.0831 | 25.08 | 102.5861 | 71.4877 | 6.6482 | 70.0578 | 14.2114 | 6.6216 | 33.0111 | 88.9189 | 7.3343 | 194.7831 | 95.4967 | 246.3447 | 10.0677 | 70.003 | 3.8827 | 125 | 39.6862 | 0 | 316.471 | 0
9816 | 757.0122 | 3.3574 | 24.8335 | 102.1024 | 72.4795 | 5.7018 | 67.267 | 13.9408 | 6.5885 | 21.6565 | 57.5582 | 7.226 | 57.0467 | 60.6662 | 172.3131 | 10.1551 | 43.9009 | 3.5244 | 122 | 39.4616 | 0 | 151.0592 | 0
9817 | 763.5911 | 3.2834 | 25.0172 | 102.0327 | 72.4888 | 5.6984 | 65.1159 | 13.9554 | 6.6944 | 32.4523 | 86.0604 | 7.1595 | 176.8708 | 89.5811 | 245.15 | 10.1507 | 69.4906 | 3.3947 | 112 | 37.7008 | 0 | 298.2204 | 0
9818 | 756.1182 | 3.0581 | 25.0451 | 101.877 | 72.4841 | 5.7 | 68.223 | 13.9499 | 6.5916 | 33.0251 | 85.9409 | 7.4414 | 172.6333 | 87.6338 | 232.7256 | 10.1238 | 69.6464 | 3.1691 | 107 | 37.0261 | 0 | 297.3688 | 0
9819 | 746.1749 | 2.9582 | 25.0826 | 101.447 | 72.4843 | 5.7 | 66.6518 | 14.1838 | 6.3608 | 33.0741 | 85.9467 | 8.1707 | 169.9787 | 92.7279 | 244.4234 | 9.9048 | 69.7227 | 2.8819 | 116 | 37.3776 | 0 | 299.8862 | 0
9820 | 741.9368 | 2.9951 | 26.167 | 98.8804 | 72.4828 | 5.7016 | 64.9875 | 14.1813 | 6.1809 | 34.0871 | 85.8763 | 7.4943 | 168.7682 | 96.8476 | 248.5503 | 10.0744 | 69.5892 | 2.6923 | 111 | 36.3668 | 0 | 305.4693 | 0
9821 | 746.908 | 3.3582 | 29.6849 | 101.5629 | 72.4821 | 5.7 | 68.3094 | 13.9889 | 6.44 | 34.7621 | 85.7328 | 7.5709 | 173.2765 | 91.1835 | 232.2916 | 10.1818 | 70.9304 | 2.6441 | 107 | 36.2441 | 0 | 357.2351 | 0
9822 | 754.4028 | 4.5156 | 38.788 | 101.3954 | 71.484 | 6.6482 | 73.2455 | 13.8941 | 7.4442 | 45.3145 | 86.9511 | 8.439 | 182.9663 | 91.0441 | 229.0023 | 10.1026 | 73.0989 | 2.761 | 113 | 38.2463 | 0 | 385.6802 | 0
9823 | 802.4768 | 5.9094 | 53.148 | 105.9129 | 69.4818 | 8.5495 | 85.6414 | 13.8153 | 8.3992 | 76.9979 | 112.0155 | 17.8005 | 227.8172 | 163.4018 | 266.489 | 12.4654 | 71.294 | 4.2074 | 179 | 45.8452 | 0 | 423.7644 | 0
9824 | 869.623 | 6.2329 | 76.5707 | 107.3922 | 65.6453 | 12.3489 | 111.8906 | 15.0184 | 11.5555 | 92.3548 | 151.2301 | 33.6419 | 283.643 | 229.8788 | 347.0699 | 23.48 | 74.9269 | 11.6983 | 282 | 59.0705 | 0 | 488.9347 | 0
9825 | 933.2707 | 5.3571 | 88.249 | 116.749 | 61.5761 | 16.1489 | 131.1835 | 16.8481 | 19.4094 | 92.945 | 169.0227 | 40.8141 | 333.7204 | 280.2724 | 441.7333 | 29.6114 | 82.7531 | 15.3034 | 271 | 70.4416 | 0 | 555.4061 | 0.026421
9826 | 1011.3848 | 6.2783 | 96.3066 | 128.7222 | 64.4777 | 17.0997 | 143.2195 | 17.1367 | 24.3237 | 102.7615 | 187.6188 | 41.3398 | 385.5311 | 313.8597 | 525.0729 | 31.8246 | 92.4221 | 17.3889 | 352 | 71.5842 | 0 | 601.6759 | 0.052843
9827 | 1117.8138 | 10.4345 | 100.5171 | 132.3356 | 99.7433 | 18.9995 | 153.1421 | 17.2561 | 27.9271 | 97.4993 | 216.113 | 42.7788 | 417.3262 | 334.0558 | 574.5787 | 31.6633 | 98.1736 | 16.0195 | 371 | 72.0419 | 0 | 605.8927 | 0.071128
9828 | 1166.4292 | 11.8238 | 106.2958 | 142.7452 | 114.2668 | 16.1508 | 150.7076 | 17.2986 | 25.7675 | 96.6309 | 214.5983 | 42.2823 | 414.4304 | 356.6014 | 592.3786 | 31.6289 | 101.5394 | 16.4764 | 340 | 77.2877 | 0 | 637.7554 | 0.10737
9829 | 1155.8121 | 7.6403 | 102.6396 | 140.2427 | 83.8292 | 13.3008 | 147.784 | 17.0617 | 19.6957 | 98.8536 | 208.6258 | 44.5192 | 401.9963 | 352.3918 | 568.5995 | 31.9667 | 97.7093 | 18.4306 | 357 | 69.5043 | 0 | 620.3571 | 0.083308
9830 | 1185.6299 | 5.1332 | 102.385 | 145.6962 | 63.5601 | 15.1995 | 149.607 | 17.8155 | 22.7435 | 98.2636 | 217.1846 | 46.2108 | 401.7149 | 352.726 | 547.3528 | 31.7702 | 97.594 | 19.3283 | 286 | 65.0596 | 0 | 699.7566 | 0.068505
9831 | 1212.6628 | 5.1243 | 105.4006 | 145.827 | 63.4811 | 14.2503 | 145.3868 | 17.712 | 21.1927 | 100.8413 | 213.7972 | 44.4694 | 407.9909 | 360.1243 | 534.6934 | 31.8925 | 96.229 | 19.0955 | 278 | 66.2471 | 0 | 705.1651 | 0.15703
9832 | 1182.8488 | 7.2616 | 105.1452 | 136.3509 | 59.4747 | 18.054 | 145.9259 | 17.2668 | 18.4412 | 95.354 | 207.0783 | 40.3974 | 406.6823 | 355.3389 | 526.8509 | 32.0069 | 94.3931 | 18.7466 | 255 | 63.8272 | 0 | 639.8605 | 0.13222
9833 | 1159.3224 | 5.841 | 100.2064 | 132.3418 | 70.487 | 7.5979 | 137.6374 | 17.3682 | 18.0362 | 84.0222 | 200.0246 | 38.8604 | 376.899 | 340.2579 | 480.5948 | 26.9453 | 100.0403 | 18.7735 | 228 | 62.0256 | 0 | 598.6374 | 0.026713
9834 | 1091.1838 | 6.2264 | 92.6981 | 122.5982 | 72.4811 | 5.7005 | 121.6012 | 16.2281 | 14.306 | 68.5991 | 179.5096 | 39.3907 | 327.0689 | 285.722 | 395.7882 | 13.6206 | 95.2209 | 18.0365 | 200 | 59.0505 | 0 | 440.4602 | 0
9835 | 1029.4798 | 6.6162 | 82.4848 | 113.6086 | 70.4807 | 7.5995 | 104.4237 | 14.9589 | 10.1225 | 58.4033 | 150.1436 | 33.0861 | 281.9446 | 219.0198 | 345.8434 | 9.5241 | 88.0351 | 14.5104 | 192 | 55.4284 | 0 | 388.4053 | 0
9836 | 986.4029 | 5.5109 | 72.9601 | 109.7829 | 72.483 | 5.7005 | 75.8032 | 14.4552 | 8.6873 | 58.5836 | 137.9481 | 23.5364 | 253.4022 | 180.6433 | 327.9823 | 9.3699 | 79.0813 | 7.9726 | 179 | 52.3042 | 0 | 331.3497 | 0
9837 | 947.7651 | 5.5762 | 39.2687 | 108.9335 | 72.4846 | 5.7 | 70.0816 | 14.131 | 8.2533 | 55.3972 | 132.024 | 15.6507 | 229.8789 | 152.413 | 327.8477 | 9.3377 | 75.0467 | 5.2531 | 169 | 49.1954 | 0 | 314.5532 | 0
9838 | 902.876 | 4.9519 | 24.9858 | 105.9965 | 72.4859 | 5.7 | 68.305 | 13.9519 | 7.4448 | 47.3489 | 113.1274 | 9.8405 | 204.243 | 126.2705 | 289.2314 | 9.2339 | 72.8193 | 4.3946 | 155 | 40.5228 | 0 | 305.7812 | 0
9839 | 872.5111 | 4.1058 | 24.0529 | 100.9315 | 72.4812 | 5.7016 | 64.5377 | 13.844 | 6.9192 | 40.591 | 93.3618 | 8.1556 | 195.244 | 109.7413 | 265.2861 | 9.2536 | 72.1466 | 3.2466 | 138 | 38.1257 | 0 | 294.8929 | 0
9840 | 847.7216 | 3.7614 | 24.1607 | 100.1111 | 72.4842 | 5.6984 | 64.6702 | 13.8853 | 6.8988 | 24.9035 | 56.635 | 8.0111 | 57.2467 | 66.3908 | 170.0188 | 9.2933 | 45.4025 | 2.7128 | 127 | 37.1292 | 0 | 154.5441 | 0
9841 | 839.2159 | 3.5321 | 24.1519 | 99.5355 | 71.4802 | 6.6497 | 65.2503 | 13.9827 | 6.6935 | 36.9886 | 82.7086 | 7.8176 | 180.2306 | 96.6536 | 227.7788 | 9.2112 | 71.8409 | 2.741 | 118 | 35.3545 | 0 | 303.6353 | 0
9842 | 831.5792 | 2.8256 | 24.1534 | 99.1572 | 71.4831 | 6.65 | 61.6426 | 13.8288 | 6.8222 | 35.8643 | 85.3411 | 8.0316 | 183.0819 | 94.2153 | 238.495 | 9.1918 | 71.8327 | 3.0437 | 115 | 36.7888 | 0 | 299.6603 | 0
9843 | 814.0501 | 2.4625 | 24.2643 | 97.8544 | 73.4833 | 4.7505 | 63.9747 | 13.7835 | 7.0605 | 37.3095 | 88.3952 | 8.4305 | 179.3627 | 92.9833 | 239.9923 | 9.1915 | 71.7026 | 2.8113 | 107 | 35.465 | 0 | 305.5215 | 0
9844 | 810.4175 | 2.4336 | 24.2501 | 98.3369 | 72.4821 | 5.6997 | 65.6388 | 14.0498 | 6.9767 | 36.9285 | 88.8782 | 8.0197 | 173.2704 | 89.951 | 231.7041 | 9.1924 | 71.743 | 2.6608 | 105 | 35.3358 | 0 | 311.8994 | 0
9845 | 803.5699 | 3.1229 | 24.4732 | 99.28 | 72.4849 | 5.7 | 62.3291 | 14.0219 | 6.9128 | 37.6772 | 87.3957 | 7.8172 | 176.765 | 88.9168 | 225.5998 | 9.2093 | 73.2928 | 2.6741 | 103 | 36.0266 | 0 | 342.6943 | 0
9846 | 804.5914 | 4.2024 | 35.3637 | 99.2722 | 72.4816 | 5.7 | 69.0059 | 13.8379 | 6.8598 | 47.0304 | 84.7479 | 9.4157 | 186.1939 | 94.805 | 233.5201 | 9.181 | 75.113 | 2.6963 | 106 | 35.3472 | 0 | 399.4391 | 0
9847 | 850.1855 | 8.7767 | 49.2855 | 104.5687 | 71.4802 | 6.6497 | 84.7323 | 13.6568 | 11.5413 | 82.2076 | 96.8507 | 17.4821 | 215.192 | 163.6432 | 256.3405 | 11.5862 | 73.1745 | 2.7787 | 176 | 48.3954 | 0 | 439.279 | 0
9848 | 911.4448 | 14.5842 | 77.0407 | 105.5662 | 65.4778 | 12.3484 | 103.4294 | 14.4938 | 17.3202 | 91.0338 | 139.7947 | 31.8874 | 267.8476 | 234.5545 | 331.3839 | 23.7032 | 75.7827 | 7.0758 | 284 | 59.0639 | 0 | 476.5505 | 0
9849 | 1002.0436 | 20.2024 | 94.7148 | 113.3503 | 60.478 | 17.0987 | 126.7139 | 16.0987 | 20.3177 | 85.3249 | 181.7735 | 39.204 | 339.2348 | 292.6593 | 458.033 | 31.0851 | 82.0339 | 15.2067 | 295 | 68.7208 | 0 | 560.7917 | 0.041695
9850 | 1082.1659 | 24.2506 | 102.9223 | 127.3078 | 62.4782 | 15.2005 | 142.7874 | 16.6081 | 20.7825 | 100.4018 | 192.923 | 40.5645 | 397.5005 | 330.3954 | 552.7738 | 33.0126 | 89.2913 | 18.4938 | 340 | 75.0273 | 0 | 610.5848 | 0.062985
9851 | 1138.6454 | 24.6848 | 101.982 | 135.8277 | 57.4785 | 19.9487 | 149.9334 | 17.0535 | 21.6502 | 107.493 | 185.8905 | 41.4743 | 422.5814 | 348.9914 | 588.5704 | 33.6445 | 94.2165 | 19.0284 | 342 | 78.8477 | 0 | 601.565 | 0.048595
9852 | 1158.8985 | 19.9343 | 102.0713 | 140.0034 | 60.4818 | 17.1008 | 156.1125 | 18.8701 | 20.6268 | 110.9874 | 184.7368 | 40.1835 | 422.3642 | 366.2982 | 613.7317 | 34.771 | 95.2444 | 19.2282 | 316 | 79.0281 | 0 | 615.7662 | 0.053248
9853 | 1143.5488 | 11.4542 | 99.6999 | 137.1633 | 62.4778 | 15.2005 | 152.1018 | 19.5447 | 18.2862 | 104.7703 | 198.3463 | 39.0554 | 408.9542 | 365.644 | 610.8814 | 34.3855 | 92.6143 | 19.2796 | 314 | 68.3688 | 0 | 630.3477 | 0.13397
9854 | 1161.5245 | 7.1147 | 100.5713 | 139.9704 | 63.4717 | 14.2542 | 146.1661 | 12.6805 | 20.927 | 98.1993 | 213.6496 | 40.9112 | 411.5058 | 364.9999 | 614.3439 | 33.8936 | 95.5731 | 19.6087 | 273 | 62.1079 | 0 | 637.7363 | 0.19262
9855 | 1157.2456 | 6.163 | 99.8249 | 141.0118 | 61.4816 | 16.1455 | 156.3228 | 14.7201 | 20.5684 | 100.464 | 210.308 | 39.3546 | 423.0958 | 360.6598 | 604.3685 | 33.2312 | 97.2244 | 19.6483 | 271 | 63.6094 | 0 | 652.7977 | 0.18423
9856 | 1135.7577 | 5.9948 | 98.2687 | 139.5419 | 62.4791 | 15.2003 | 149.6586 | 16.9967 | 17.7533 | 95.1444 | 207.7716 | 38.7473 | 413.9229 | 352.2174 | 569.9055 | 32.5259 | 97.5977 | 19.5648 | 291 | 61.168 | 0 | 624.8559 | 0.15563
9857 | 1095.3829 | 5.024 | 91.6607 | 129.7779 | 69.48 | 8.5518 | 136.0741 | 10.8157 | 16.9342 | 91.4059 | 197.3373 | 38.4124 | 388.8095 | 328.9649 | 483.4108 | 27.339 | 96.2318 | 19.2516 | 224 | 58.574 | 0 | 588.4606 | 0.03269
9858 | 1043.6897 | 5.9043 | 84.6933 | 117.0793 | 70.4799 | 7.6003 | 131.6438 | 13.0097 | 17.441 | 82.3514 | 181.2672 | 40.0715 | 350.043 | 268.5239 | 392.5759 | 14.386 | 93.22 | 18.027 | 203 | 57.9015 | 0 | 436.2199 | 0
9859 | 988.9779 | 6.2394 | 82.1549 | 108.9192 | 70.4806 | 7.6 | 108.5951 | 14.2792 | 16.0932 | 67.6831 | 158.7131 | 35.2774 | 309.9567 | 190.2086 | 339.7363 | 10.2093 | 86.7191 | 13.9983 | 214 | 53.943 | 0 | 374.4475 | 0
9860 | 935.8207 | 5.6853 | 69.4834 | 105.8455 | 72.4831 | 5.7005 | 83.309 | 14.0828 | 10.7021 | 55.6163 | 147.9121 | 19.5105 | 287.4904 | 154.3056 | 310.3274 | 10.2695 | 74.2711 | 7.7405 | 162 | 49.8198 | 0 | 331.4488 | 0
9861 | 903.7438 | 5.2549 | 35.9788 | 101.4375 | 72.4831 | 5.7 | 75.8546 | 14.0761 | 8.7446 | 50.6991 | 137.2079 | 12.4879 | 267.778 | 145.2788 | 277.1895 | 10.0682 | 69.7748 | 5.2387 | 162 | 47.3033 | 0 | 304.1728 | 0
9862 | 877.6005 | 4.9804 | 24.7846 | 99.1022 | 72.4893 | 5.7 | 70.3244 | 14.0142 | 8.432 | 44.401 | 119.6684 | 11.9037 | 239.1458 | 133.9113 | 251.5665 | 10.1848 | 68.7302 | 4.5929 | 153 | 40.1332 | 0 | 299.6111 | 0
9863 | 864.1993 | 4.1869 | 24.7983 | 98.8617 | 72.4885 | 5.7 | 71.0299 | 14.2458 | 7.8327 | 40.7135 | 100.8843 | 12.0123 | 223.2423 | 125.215 | 241.4697 | 10.283 | 69.2686 | 4.3677 | 144 | 36.9796 | 0 | 292.4759 | 0
9864 | 846.9746 | 3.3559 | 24.7215 | 101.7687 | 72.4849 | 5.7 | 71.5379 | 14.0966 | 6.78 | 25.2062 | 61.1067 | 11.8144 | 64.2516 | 78.6338 | 161.1949 | 10.2805 | 43.365 | 3.6594 | 116 | 37.207 | 0 | 153.1839 | 0
9865 | 836.0786 | 2.8794 | 24.7731 | 101.1372 | 72.4807 | 5.7 | 67.9159 | 13.9086 | 6.311 | 36.7183 | 89.9448 | 11.536 | 208.5965 | 125.5692 | 226.3862 | 10.2779 | 68.4751 | 3.2274 | 112 | 36.9468 | 0 | 304.6813 | 0
9866 | 824.6746 | 2.8499 | 24.9286 | 98.4233 | 71.4811 | 6.6497 | 68.1251 | 14.1528 | 6.1883 | 38.5416 | 91.8924 | 11.8949 | 209.7578 | 117.9936 | 228.0265 | 10.0374 | 68.319 | 2.9642 | 106 | 34.4901 | 0 | 310.2347 | 0
9867 | 815.7269 | 2.7014 | 24.8423 | 97.2651 | 71.4882 | 6.65 | 71.4083 | 14.0231 | 6.3248 | 38.0834 | 93.0191 | 12.1854 | 208.8417 | 111.6832 | 234.5924 | 10.1582 | 68.2217 | 2.727 | 106 | 34.8746 | 0 | 314.0008 | 0
9868 | 808.8558 | 2.7702 | 24.8716 | 100.1412 | 72.4849 | 5.7003 | 67.9305 | 13.903 | 6.1822 | 35.9797 | 92.5672 | 11.6293 | 207.1362 | 106.2445 | 242.4018 | 10.2508 | 68.1899 | 2.6565 | 108 | 34.005 | 0 | 318.1844 | 0
9869 | 802.046 | 3.5681 | 24.8878 | 98.3867 | 73.4795 | 4.7503 | 67.866 | 13.8207 | 6.3007 | 35.9397 | 92.3261 | 11.3707 | 211.1211 | 104.7331 | 226.555 | 10.2428 | 69.4583 | 2.6646 | 105 | 34.1258 | 0 | 347.006 | 0
9870 | 815.1331 | 4.6754 | 43.2911 | 99.2991 | 72.4771 | 5.6997 | 79.0129 | 13.7034 | 6.595 | 46.4879 | 92.8994 | 12.7662 | 220.2149 | 107.809 | 225.3771 | 10.1546 | 71.3743 | 2.6988 | 110 | 33.1019 | 0 | 407.4879 | 0
9871 | 851.2392 | 6.041 | 63.1284 | 103.8648 | 71.4756 | 6.6497 | 89.9267 | 13.893 | 9.0522 | 71.9099 | 104.348 | 20.6199 | 257.0059 | 173.6107 | 248.8238 | 12.4233 | 68.7814 | 2.7767 | 173 | 43.813 | 0 | 444.1377 | 0
9872 | 903.2305 | 6.1052 | 79.8537 | 106.4553 | 65.4788 | 12.3484 | 106.2658 | 14.2359 | 9.4238 | 75.5168 | 143.4167 | 30.3046 | 309.0334 | 237.1281 | 329.1313 | 24.114 | 71.026 | 5.2964 | 276 | 56.7097 | 0 | 477.4339 | 0
9873 | 975.6459 | 5.3345 | 94.0062 | 116.5728 | 62.4797 | 15.1992 | 130.3177 | 15.6138 | 7.8383 | 79.2983 | 170.0821 | 33.1298 | 362.3224 | 289.0407 | 435.9333 | 32.01 | 80.833 | 12.8248 | 291 | 61.8679 | 0 | 555.0709 | 0.18718
9874 | 1051.0388 | 4.8717 | 100.1092 | 125.9485 | 60.4775 | 17.0995 | 140.7352 | 17.3805 | 11.3133 | 93.4844 | 186.5003 | 36.8919 | 408.5683 | 327.9604 | 500.9883 | 32.8351 | 87.5293 | 16.1719 | 349 | 63.667 | 0 | 612.072 | 0.23982
9875 | 1090.934 | 4.7789 | 99.9332 | 131.4296 | 60.4755 | 17.1 | 149.5351 | 16.9284 | 16.7628 | 108.3984 | 190.4095 | 40.6364 | 434.0637 | 349.6084 | 550.4719 | 33.3832 | 90.4627 | 17.4383 | 327 | 66.4343 | 0 | 595.4622 | 0.2468
9876 | 1133.1051 | 4.9846 | 102.3339 | 140.0168 | 62.4777 | 15.2005 | 159.4999 | 14.3674 | 18.1597 | 114.497 | 188.7112 | 40.7504 | 449.0466 | 359.5046 | 555.2145 | 33.4613 | 95.1756 | 18.7391 | 307 | 77.4026 | 0 | 622.527 | 0.25555
9877 | 1120.0236 | 4.9065 | 101.1192 | 143.0153 | 64.4826 | 13.3005 | 149.306 | 11.788 | 12.245 | 100.8577 | 192.329 | 41.5073 | 443.0473 | 358.5216 | 562.3675 | 33.6371 | 96.7845 | 18.7927 | 315 | 71.9421 | 0 | 618.8043 | 0.29852
9878 | 1152.8755 | 8.0105 | 101.5962 | 145.7507 | 60.4893 | 17.0989 | 151.3709 | 13.9608 | 14.7688 | 95.9667 | 199.0328 | 43.303 | 444.0212 | 345.9812 | 569.9334 | 33.2085 | 97.7297 | 18.1282 | 261 | 70.46 | 0 | 631.0863 | 0.2934
9879 | 1169.5094 | 12.3995 | 105.3616 | 143.7931 | 62.4833 | 15.2005 | 159.7928 | 10.5126 | 15.5057 | 107.0654 | 202.3407 | 42.1667 | 444.4763 | 343.2509 | 575.8399 | 33.5558 | 94.6523 | 18.2283 | 270 | 70.5551 | 0 | 603.1131 | 0.26103
9880 | 1124.0376 | 14.9826 | 99.9874 | 142.363 | 62.4762 | 15.2042 | 159.0381 | 13.733 | 11.3 | 107.6756 | 202.8803 | 39.4613 | 436.1168 | 340.1239 | 575.5432 | 33.8908 | 84.3343 | 18.8917 | 272 | 70.0076 | 0 | 610.9734 | 0.16002
9881 | 1076.1283 | 12.2002 | 90.8033 | 133.0281 | 67.4818 | 10.4471 | 142.0855 | 15.9637 | 10.256 | 98.5634 | 199.0344 | 36.6613 | 417.6916 | 323.1893 | 524.2008 | 29.0749 | 79.3819 | 18.6757 | 249 | 70.5924 | 0 | 563.5632 | 0.043259
9882 | 1030.8747 | 8.1508 | 82.6454 | 120.2131 | 69.4764 | 8.5505 | 129.852 | 15.2861 | 14.3375 | 86.9767 | 185.6038 | 37.4732 | 381.6014 | 261.9904 | 453.7888 | 17.1178 | 77.7983 | 16.9641 | 220 | 66.7313 | 0 | 418.0159 | 0
9883 | 989.7028 | 6.5813 | 74.7867 | 110.3266 | 71.4815 | 6.6505 | 116.1408 | 14.672 | 14.355 | 63.0565 | 158.0621 | 31.0661 | 332.8944 | 182.9423 | 403.4789 | 13.0867 | 72.0613 | 14.6109 | 219 | 57.9068 | 0 | 372.2043 | 0
9884 | 936.0811 | 5.56 | 61.4806 | 103.1546 | 71.4825 | 6.65 | 89.6204 | 14.4028 | 9.281 | 54.4287 | 142.188 | 14.1977 | 304.8578 | 141.7411 | 350.1285 | 12.9892 | 64.9641 | 8.9709 | 194 | 51.8724 | 0 | 326.3975 | 0
9885 | 892.6078 | 5.1585 | 34.1069 | 102.1928 | 71.4839 | 6.65 | 78.6353 | 14.1203 | 7.2512 | 53.7349 | 132.3912 | 8.7391 | 274.0871 | 124.9376 | 297.7146 | 12.6131 | 58.5657 | 5.8879 | 183 | 48.1126 | 0 | 305.1463 | 0
9886 | 865.5425 | 6.0714 | 25.2719 | 101.7303 | 72.4865 | 5.7003 | 72.2282 | 14.0098 | 6.7133 | 47.8432 | 112.3235 | 8.7219 | 244.3936 | 113.6381 | 263.6091 | 11.0521 | 56.1562 | 5.0667 | 180 | 42.7727 | 0 | 305.7344 | 0
9887 | 856.6657 | 5.7347 | 25.233 | 103.5174 | 70.4879 | 7.5995 | 67.7972 | 14.1801 | 6.3014 | 37.6297 | 92.1281 | 8.473 | 225.1119 | 113.815 | 251.8385 | 10.1653 | 55.6782 | 4.4598 | 177 | 40.7022 | 0 | 301.9876 | 0
9888 | 833.9426 | 3.9977 | 25.0653 | 104.629 | 70.4886 | 7.6 | 69.948 | 14.0783 | 6.373 | 22.7801 | 56.5995 | 8.3714 | 64.3651 | 69.7587 | 168.5738 | 10.0145 | 34.7064 | 4.2458 | 164 | 40.4276 | 0 | 155.5783 | 0
9889 | 812.058 | 3.0136 | 25.0742 | 100.6522 | 72.4883 | 5.7005 | 69.2705 | 13.8421 | 6.3325 | 35.1799 | 84.6199 | 8.1295 | 199.2885 | 97.8229 | 246.7243 | 9.9967 | 54.5952 | 4.2391 | 154 | 40.6312 | 0 | 306.7405 | 0
9890 | 796.7056 | 2.853 | 25.1233 | 100.5268 | 71.4831 | 6.6497 | 65.3407 | 14.031 | 6.3617 | 34.0543 | 85.3731 | 8.418 | 196.639 | 94.7086 | 247.4655 | 9.943 | 54.266 | 4.1858 | 138 | 41.3199 | 0 | 313.6393 | 0
9891 | 784.1938 | 2.7251 | 25.1441 | 103.2032 | 72.4849 | 5.7003 | 69.7006 | 13.9331 | 6.3112 | 32.3047 | 86.4017 | 9.378 | 196.1914 | 89.3829 | 247.8757 | 9.7867 | 54.4016 | 3.3513 | 133 | 39.9155 | 0 | 320.5135 | 0
9892 | 781.4091 | 2.8621 | 25.2318 | 103.3813 | 71.4845 | 6.6497 | 68.7862 | 13.8516 | 6.2133 | 33.211 | 86.967 | 8.5157 | 193.6983 | 85.062 | 238.4086 | 9.8738 | 54.4453 | 2.9825 | 128 | 37.2517 | 0 | 321.855 | 0
9893 | 785.1092 | 3.1224 | 24.9007 | 102.8085 | 72.4807 | 5.7003 | 66.146 | 13.8269 | 6.4191 | 33.4468 | 86.6082 | 7.9664 | 197.8395 | 84.0477 | 223.5954 | 9.9211 | 56.5103 | 2.9949 | 128 | 37.1971 | 0 | 343.0757 | 0
9894 | 793.8588 | 4.0096 | 40.6747 | 102.8844 | 72.4851 | 5.7 | 73.7726 | 13.6955 | 6.6192 | 47.4031 | 87.9348 | 12.0112 | 208.2333 | 91.4485 | 225.5182 | 9.9022 | 57.7746 | 3.0059 | 124 | 35.2666 | 0 | 397.7001 | 0
9895 | 827.5129 | 5.1458 | 57.8854 | 105.7188 | 69.481 | 8.5492 | 90.256 | 13.7686 | 12.3696 | 71.5737 | 99.7442 | 20.0711 | 239.5096 | 158.0434 | 244.4238 | 12.2487 | 55.9912 | 3.4183 | 186 | 49.468 | 0 | 427.9849 | 0
9896 | 884.9207 | 7.2853 | 78.6108 | 108.4102 | 64.4755 | 13.2987 | 106.1487 | 13.9762 | 14.339 | 85.8823 | 138.015 | 32.2457 | 289.8122 | 235.5048 | 331.3597 | 23.3743 | 60.3548 | 7.4626 | 273 | 61.9369 | 0 | 467.2904 | 0
9897 | 973.6182 | 8.9277 | 92.5701 | 121.4184 | 62.4753 | 15.1995 | 125.3284 | 14.7634 | 16.2283 | 81.1825 | 166.3773 | 38.701 | 351.2618 | 284.4007 | 449.6689 | 29.7709 | 69.7485 | 14.7055 | 288 | 68.8959 | 0 | 541.6437 | 0.067986
9898 | 1073.9998 | 11.945 | 100.6231 | 136.8333 | 61.4772 | 16.1497 | 148.024 | 12.0153 | 18.3512 | 85.9018 | 187.6128 | 40.3584 | 394.9245 | 327.7391 | 528.0202 | 31.6989 | 76.3861 | 16.8951 | 375 | 72.9507 | 0 | 617.4732 | 0.03085
9899 | 1116.6612 | 12.3274 | 101.363 | 147.8052 | 62.479 | 15.2003 | 146.9284 | 15.1238 | 23.1288 | 87.364 | 199.263 | 42.3269 | 421.6408 | 358.7629 | 575.9804 | 32.952 | 81.8143 | 16.81 | 400 | 72.6869 | 0 | 619.708 | 0.039678
9900 | 1137.7965 | 8.9384 | 103.5139 | 149.5061 | 62.4784 | 15.2 | 147.0405 | 13.6147 | 22.1702 | 101.3844 | 201.6008 | 41.5486 | 513.3151 | 379.8759 | 597.6294 | 33.7655 | 86.3524 | 17.3491 | 357 | 76.6935 | 0 | 650.1236 | 0.037055
9901 | 1144.2593 | 5.8683 | 107.3068 | 146.6421 | 63.4766 | 14.2503 | 151.8449 | 13.7701 | 14.9271 | 94.1858 | 204.5269 | 36.9598 | 458.342 | 369.5276 | 581.7257 | 33.0332 | 82.6369 | 18.5629 | 355 | 76.6777 | 0 | 607.253 | 0.034369
9902 | 1139.9201 | 4.7085 | 106.8792 | 146.1794 | 60.4813 | 17.0992 | 149.2055 | 16.517 | 9.6756 | 88.1901 | 206.4119 | 36.4637 | 421.2589 | 364.192 | 573.4489 | 32.4855 | 83.082 | 19.4109 | 300 | 76.8086 | 0 | 653.092 | 0.0764
9903 | 1150.4287 | 6.7358 | 106.1365 | 144.4417 | 60.4817 | 17.1 | 151.1287 | 11.6461 | 9.1345 | 92.3104 | 208.679 | 37.4331 | 448.5039 | 370.316 | 572.5073 | 33.8815 | 83.9401 | 20.1375 | 291 | 75.9943 | 0 | 614.1273 | 0.064452
9904 | 1133.0328 | 5.6516 | 101.5586 | 139.5332 | 62.4785 | 15.2005 | 149.795 | 13.8625 | 9.8818 | 97.7075 | 210.1128 | 37.4104 | 528.0612 | 364.2572 | 556.1534 | 32.8885 | 82.3596 | 20.2994 | 280 | 69.215 | 0 | 595.2695 | 0.030025
9905 | 1098.5647 | 8.4297 | 92.3054 | 132.7119 | 71.4737 | 6.6524 | 135.8571 | 14.3914 | 7.204 | 90.6688 | 204.7861 | 33.2177 | 540.4044 | 344.1374 | 514.5599 | 27.3252 | 79.4077 | 20.0494 | 255 | 59.9677 | 0 | 560.4442 | 0.0029565
9906 | 1064.7439 | 7.599 | 87.1928 | 120.0853 | 71.4757 | 6.65 | 130.734 | 11.9101 | 7.8828 | 75.0937 | 186.9677 | 32.2764 | 506.3677 | 263.4077 | 455.9713 | 14.9738 | 73.1315 | 18.1553 | 206 | 55.2996 | 0 | 405.874 | 0
9907 | 1022.9946 | 6.2872 | 82.2626 | 106.244 | 71.479 | 6.6518 | 114.6999 | 14.0613 | 8.0872 | 61.8475 | 155.4786 | 26.5543 | 424.7471 | 176.1664 | 396.7046 | 11.1092 | 64.9903 | 14.4428 | 195 | 51.1989 | 0 | 358.8292 | 0
9908 | 973.894 | 8.9654 | 66.6216 | 101.054 | 72.4864 | 5.6984 | 84.9637 | 10.118 | 9.455 | 51.5795 | 140.6788 | 13.3332 | 310.0404 | 149.4728 | 359.5537 | 11.2159 | 55.8665 | 8.5933 | 188 | 47.2137 | 0 | 307.4097 | 0
9909 | 934.8292 | 6.417 | 34.9285 | 100.1662 | 73.4794 | 4.7503 | 81.6398 | 12.4593 | 7.7532 | 45.5495 | 131.3524 | 8.2524 | 258.5313 | 133.6852 | 304.3692 | 11.0003 | 51.1922 | 5.6223 | 168 | 46.3231 | 0 | 283.5578 | 0
9910 | 885.2218 | 4.4601 | 24.8125 | 102.4337 | 70.484 | 7.5992 | 89.6554 | 14.0216 | 6.6882 | 38.4745 | 111.9714 | 8.0328 | 240.7795 | 119.3946 | 274.6225 | 10.853 | 50.5011 | 4.4214 | 170 | 43.117 | 0 | 283.172 | 0
9911 | 866.7455 | 4.0023 | 24.712 | 101.4386 | 71.4798 | 6.6503 | 78.8615 | 9.1335 | 6.2172 | 33.0323 | 93.5472 | 7.9995 | 225.5554 | 106.698 | 265.1775 | 10.6658 | 49.7315 | 3.2568 | 143 | 41.8419 | 0 | 279.5527 | 0
9912 | 843.2755 | 3.4825 | 24.5395 | 96.9439 | 73.4781 | 4.7505 | 70.5851 | 11.6131 | 6.0917 | 20.5612 | 57.5679 | 7.9958 | 64.2932 | 65.711 | 171.2065 | 10.8104 | 31.0484 | 2.737 | 126 | 41.8772 | 0 | 142.896 | 0
9913 | 832.1889 | 2.7229 | 24.4981 | 95.4422 | 72.4784 | 5.6997 | 74.9918 | 9.9463 | 6.1891 | 31.6022 | 85.6023 | 7.9294 | 199.9608 | 94.6948 | 231.7212 | 10.8821 | 48.9995 | 2.6789 | 122 | 40.4707 | 0 | 271.3595 | 0
9914 | 822.7685 | 2.4224 | 24.5662 | 96.8172 | 72.481 | 5.7 | 67.4337 | 10.2543 | 6.2282 | 31.5669 | 84.2007 | 7.9094 | 192.8821 | 92.7773 | 226.0889 | 10.878 | 49.01 | 2.6407 | 118 | 38.1725 | 0 | 269.3302 | 0
9915 | 810.4668 | 2.7748 | 24.4878 | 97.4568 | 72.4851 | 5.7 | 62.5674 | 12.7734 | 6.1512 | 31.426 | 83.5609 | 8.7148 | 190.6592 | 94.0333 | 224.8732 | 10.8669 | 48.6288 | 2.6376 | 116 | 35.9654 | 0 | 276.7913 | 0
9916 | 802.5604 | 2.5809 | 24.7172 | 97.0855 | 73.4801 | 4.7503 | 72.4804 | 8.0764 | 6.2203 | 31.4362 | 85.238 | 8.1463 | 189.7439 | 87.8047 | 221.8737 | 10.6827 | 48.8619 | 2.6323 | 112 | 35.1657 | 0 | 274.742 | 0
9917 | 810.1623 | 2.8662 | 24.5251 | 96.7622 | 72.4823 | 5.6997 | 72.8571 | 11.3675 | 6.2528 | 31.4006 | 86.1046 | 7.7233 | 191.4404 | 85.5718 | 217.0266 | 10.8002 | 50.623 | 2.6905 | 111 | 34.8365 | 0 | 310.0015 | 0
9918 | 831.3152 | 4.1297 | 38.0374 | 97.9652 | 70.4836 | 7.5995 | 69.4731 | 12.1616 | 6.4797 | 42.0738 | 87.8008 | 10.2359 | 202.9088 | 92.883 | 221.2541 | 10.8799 | 52.6989 | 2.6963 | 110 | 34.8723 | 0 | 360.1551 | 0
9919 | 854.5522 | 7.9895 | 51.0239 | 103.7607 | 69.4786 | 8.5497 | 85.5003 | 8.9714 | 7.9152 | 61.4784 | 100.1044 | 17.4751 | 245.7369 | 160.035 | 246.4122 | 13.3047 | 50.2047 | 2.6869 | 155 | 45.4329 | 0 | 405.1907 | 0
9920 | 908.8504 | 15.0576 | 76.5179 | 107.1911 | 65.4785 | 12.3489 | 110.89 | 12.2308 | 7.1216 | 79.7897 | 141.1796 | 33.0998 | 295.2463 | 236.3841 | 342.9314 | 24.0142 | 54.9926 | 7.5617 | 303 | 55.8564 | 0 | 428.6868 | 0
9921 | 1002.4379 | 22.6705 | 93.1992 | 120.0229 | 62.4774 | 15.1992 | 123.7454 | 14.6135 | 6.5012 | 87.1278 | 179.2526 | 36.2728 | 348.7204 | 297.5635 | 468.9442 | 28.9614 | 65.825 | 15.5506 | 304 | 65.814 | 0 | 497.7081 | 0.030362
9922 | 1096.4957 | 23.341 | 101.1764 | 127.8308 | 63.471 | 14.2503 | 134.7353 | 11.0413 | 12.2965 | 94.6595 | 195.6185 | 37.8361 | 389.4414 | 336.0654 | 562.1327 | 30.2502 | 75.3331 | 17.3456 | 333 | 75.7853 | 0 | 563.3436 | 0.056177
9923 | 1150.5277 | 17.3243 | 102.6234 | 131.4311 | 64.4711 | 13.3003 | 152.5244 | 14.858 | 22.6553 | 105.9012 | 202.8777 | 40.2921 | 414.133 | 352.3115 | 583.719 | 31.2057 | 84.8302 | 17.405 | 310 | 80.4245 | 0 | 537.0096 | 0.089692
9924 | 1196.8412 | 15.6337 | 102.6796 | 136.8892 | 62.4807 | 15.1995 | 151.0453 | 11.4649 | 24.0842 | 100.9576 | 204.2189 | 37.5023 | 422.1975 | 360.2598 | 576.1068 | 31.5572 | 85.801 | 18.1084 | 316 | 83.6685 | 0 | 580.8555 | 0.099435
9925 | 1182.6195 | 12.5764 | 103.3806 | 138.5499 | 60.4816 | 17.0995 | 145.8249 | 14.3361 | 18.6958 | 91.0562 | 210.5036 | 40.7841 | 410.7885 | 353.6849 | 559.2097 | 31.5934 | 82.6235 | 19.091 | 351 | 73.8194 | 0 | 574.6006 | 0.030015
9926 | 1202.1278 | 10.3775 | 103.0883 | 141.2043 | 61.4818 | 16.1503 | 157.3356 | 11.7216 | 18.0082 | 93.1897 | 219.5563 | 45.1362 | 411.937 | 356.1923 | 554.0391 | 31.2915 | 85.0962 | 20.2336 | 299 | 74.7727 | 0 | 615.4949 | 0.034457
9927 | 1204.6779 | 6.5909 | 100.2143 | 139.9679 | 63.4818 | 14.2505 | 150.2174 | 14.3702 | 17.4523 | 90.8646 | 219.0896 | 44.3426 | 412.9133 | 349.2622 | 553.3562 | 31.3838 | 88.5877 | 20.4261 | 278 | 74.621 | 0 | 599.617 | 0.046326
9928 | 1151.9018 | 4.6614 | 97.4272 | 137.6472 | 61.4812 | 16.1495 | 143.0172 | 12.5211 | 11.3654 | 82.1158 | 211.1355 | 41.4415 | 397.5743 | 334.0743 | 534.0558 | 30.8936 | 85.5288 | 19.7986 | 277 | 69.1691 | 0 | 582.6887 | 0.032208
9929 | 1087.4907 | 5.3947 | 92.5404 | 131.2385 | 69.4814 | 8.5521 | 133.0113 | 11.6399 | 8.6225 | 81.5518 | 207.642 | 34.9045 | 367.8363 | 307.698 | 506.1836 | 26.1798 | 78.5727 | 18.5788 | 269 | 62.7171 | 0 | 482.0657 | 0.0043899
9930 | 1019.3585 | 7.3934 | 82.1464 | 118.2264 | 70.4822 | 7.6003 | 112.5366 | 13.1227 | 7.9872 | 75.459 | 196.9796 | 33.0484 | 313.0306 | 242.6269 | 413.4937 | 15.2424 | 69.806 | 16.6685 | 229 | 56.926 | 0 | 369.5481 | 0
9931 | 971.4484 | 6.3938 | 50.0485 | 105.2007 | 71.4818 | 6.6521 | 101.9961 | 11.1517 | 11.0378 | 56.6648 | 165.5441 | 30.1065 | 263.012 | 162.5887 | 342.9837 | 11.4654 | 61.5227 | 14.1769 | 211 | 53.1664 | 0 | 318.0048 | 0
9932 | 911.7142 | 5.2352 | 38.8143 | 98.0353 | 72.4867 | 5.6984 | 84.764 | 10.0577 | 9.4444 | 44.8618 | 137.0383 | 20.9588 | 238.4959 | 122.9215 | 314.0576 | 10.9364 | 55.8014 | 8.9497 | 195 | 52.2831 | 0 | 302.4061 | 0
9933 | 885.982 | 4.73 | 27.902 | 96.7314 | 72.4807 | 5.7 | 73.4969 | 12.7221 | 7.9748 | 41.1545 | 108.0222 | 14.6517 | 223.3768 | 116.1378 | 292.5913 | 10.7703 | 52.2153 | 6.3231 | 176 | 49.3239 | 0 | 297.6312 | 0
9934 | 863.5064 | 4.474 | 23.594 | 97.8432 | 72.4828 | 5.7 | 75.0671 | 13.7104 | 7.1742 | 41.0138 | 110.6846 | 12.1047 | 206.2398 | 112.4623 | 270.9269 | 10.7931 | 49.4332 | 5.3395 | 173 | 43.7332 | 0 | 287.1925 | 0
9935 | 843.1908 | 4.1114 | 23.5877 | 100.819 | 71.4842 | 6.6497 | 74.0014 | 13.6195 | 6.4774 | 36.8669 | 110.3882 | 12.5775 | 196.1613 | 109.2436 | 266.3482 | 10.7712 | 48.5764 | 4.7616 | 172 | 42.4183 | 0 | 281.4549 | 0
9936 | 825.3049 | 3.4239 | 23.4461 | 101.6777 | 72.4821 | 5.7003 | 68.1439 | 13.7277 | 6.8558 | 22.6972 | 64.7551 | 11.1101 | 57.9866 | 72.1396 | 178.315 | 10.5598 | 30.3607 | 4.4042 | 161 | 41.0816 | 0 | 146.8447 | 0
9937 | 815.8587 | 2.9869 | 23.5134 | 100.2691 | 71.483 | 6.6497 | 69.1047 | 13.9231 | 6.4474 | 35.7463 | 86.8059 | 8.9539 | 181.1232 | 105.9944 | 253.5139 | 10.6707 | 47.5129 | 4.2162 | 143 | 40.9357 | 0 | 295.8907 | 0
9938 | 816.6541 | 2.8955 | 23.5314 | 100.0173 | 71.4826 | 6.65 | 69.9447 | 13.7999 | 6.1828 | 35.6692 | 86.1967 | 8.1033 | 178.2497 | 92.5925 | 255.0532 | 10.7387 | 47.5454 | 4.1811 | 144 | 42.4527 | 0 | 289.5669 | 0
9939 | 812.5094 | 2.8188 | 23.3519 | 101.7415 | 72.4855 | 5.7003 | 66.256 | 13.7181 | 6.3189 | 34.9155 | 86.2891 | 8.5162 | 176.2575 | 86.8534 | 242.6778 | 10.7476 | 47.556 | 4.0111 | 154 | 41.7308 | 0 | 278.9556 | 0
9940 | 799.3581 | 2.9654 | 23.431 | 102.0273 | 72.4843 | 5.7 | 68.0716 | 13.6932 | 6.3115 | 34.629 | 87.1612 | 8.5376 | 174.9458 | 85.1468 | 240.783 | 10.7386 | 47.7842 | 4.0584 | 147 | 38.9777 | 0 | 272.3708 | 0
9941 | 800.2652 | 3.2074 | 23.5839 | 99.8823 | 71.483 | 6.6497 | 69.8371 | 13.8964 | 6.2527 | 35.22 | 88.4385 | 8.1053 | 174.3188 | 83.7022 | 240.6706 | 10.5444 | 49.2013 | 4.1317 | 141 | 37.0354 | 0 | 276.2631 | 0
9942 | 809.2395 | 3.8565 | 26.649 | 104.4861 | 72.484 | 5.7003 | 65.9231 | 13.8456 | 6.1898 | 36.3032 | 88.8532 | 7.9165 | 172.1682 | 82.1277 | 238.5587 | 10.6449 | 51.0733 | 3.6286 | 131 | 37.4961 | 0 | 280.8059 | 0
9943 | 820.2922 | 4.1462 | 36.28 | 104.5682 | 72.4806 | 5.7 | 67.7778 | 13.6681 | 6.2455 | 36.8186 | 88.7362 | 7.8631 | 172.8335 | 83.3507 | 229.5325 | 10.7624 | 48.3241 | 3.0829 | 134 | 39.2484 | 0 | 282.0556 | 0
9944 | 828.1318 | 3.8539 | 38.0863 | 102.3745 | 72.4814 | 5.7 | 71.1868 | 13.4506 | 6.8386 | 32.9102 | 92.7299 | 8.5597 | 179.0677 | 82.3502 | 220.0352 | 10.4367 | 46.7252 | 3.139 | 135 | 46.2969 | 0 | 277.3113 | 0
9945 | 840.1628 | 2.9057 | 52.5476 | 100.6846 | 71.4855 | 6.6497 | 73.6406 | 13.2906 | 6.0108 | 40.3059 | 109.5457 | 13.5827 | 184.1388 | 85.3645 | 221.948 | 10.2444 | 47.2324 | 3.699 | 186 | 52.0597 | 0 | 277.836 | 0.012627
9946 | 874.4617 | 3.1754 | 66.5608 | 100.1665 | 70.4821 | 7.5997 | 80.0226 | 13.1692 | 6.8264 | 55.4959 | 130.6287 | 15.7737 | 194.4892 | 89.7887 | 241.047 | 10.0246 | 48.3467 | 6.22 | 185 | 52.6068 | 0 | 283.6218 | 0.035253
9947 | 898.8268 | 3.0932 | 77.4528 | 101.8602 | 72.4786 | 5.7005 | 83.2091 | 13.4993 | 6.3134 | 63.7002 | 148.6572 | 16.6388 | 204.3936 | 95.6496 | 249.5607 | 10.1329 | 49.1647 | 12.2031 | 213 | 56.366 | 0 | 289.3285 | 0.043831
9948 | 900.199 | 3.1605 | 79.4855 | 105.3034 | 72.4791 | 5.7 | 80.4211 | 14.2778 | 10.3561 | 60.748 | 137.2095 | 17.6019 | 213.3313 | 107.0963 | 246.4564 | 10.2312 | 49.4875 | 14.3944 | 197 | 55.6603 | 0 | 291.7 | 0.04984
9949 | 898.855 | 3.1978 | 79.7692 | 105.7457 | 72.479 | 5.7 | 84.2511 | 9.708 | 8.0284 | 69.243 | 129.8173 | 16.6581 | 224.2269 | 125.0113 | 238.182 | 10.2715 | 48.4671 | 14.3411 | 188 | 55.9191 | 0 | 308.9163 | 0.036203
9950 | 905.6918 | 3.1548 | 77.1214 | 101.5443 | 72.476 | 5.7 | 87.8865 | 11.0886 | 8.9257 | 54.9311 | 132.8676 | 16.5118 | 228.9551 | 128.7614 | 255.6317 | 10.2415 | 47.0313 | 14.5226 | 211 | 52.6131 | 0 | 310.2797 | 0.042277
9951 | 907.7654 | 2.7445 | 49.4325 | 99.9256 | 72.4832 | 5.7 | 80.0907 | 13.0054 | 9.4 | 54.5661 | 135.519 | 17.0535 | 231.9749 | 126.7588 | 284.8979 | 10.0027 | 47.7221 | 12.4264 | 194 | 55.1384 | 0 | 305.4075 | 0.047938
9952 | 913.7152 | 6.2078 | 38.3117 | 99.6872 | 72.4806 | 5.7 | 74.578 | 13.0627 | 8.6833 | 49.3329 | 133.4088 | 21.6041 | 234.2483 | 126.8364 | 288.5213 | 10.0913 | 46.6252 | 7.2485 | 199 | 51.6546 | 0 | 302.5007 | 0.01231
9953 | 909.6216 | 9.5898 | 27.1731 | 97.6175 | 72.4821 | 5.7 | 78.482 | 8.125 | 8.8723 | 32.2308 | 130.9159 | 22.0277 | 231.2946 | 136.373 | 274.0621 | 10.2127 | 46.6356 | 5.6831 | 207 | 50.5763 | 0 | 285.5055 | 0.0034148
9954 | 908.7215 | 11.5105 | 23.5198 | 97.6993 | 70.4837 | 7.5995 | 73.1486 | 11.2615 | 13.2747 | 29.1549 | 125.1887 | 27.1908 | 231.6825 | 143.6304 | 280.2753 | 10.5698 | 48.3288 | 5.7464 | 207 | 51.0148 | 0 | 282.705 | 0
9955 | 887.9733 | 12.2229 | 23.6235 | 96.2551 | 72.4832 | 5.7005 | 70.6303 | 13.7222 | 13.874 | 31.5603 | 102.2547 | 26.8477 | 226.2556 | 137.3615 | 274.8384 | 10.771 | 48.6357 | 5.4148 | 213 | 46.0757 | 0 | 283.7471 | 0
9956 | 873.0268 | 11.2245 | 23.7016 | 95.4479 | 72.4867 | 5.7 | 79.4343 | 10.4653 | 11.7072 | 34.8337 | 106.923 | 24.0382 | 215.4497 | 127.1794 | 273.7903 | 10.6846 | 48.3137 | 4.9035 | 205 | 41.0588 | 0 | 276.2332 | 0
9957 | 849.1132 | 6.5487 | 23.6126 | 96.2336 | 72.4919 | 5.7 | 75.278 | 10.6673 | 13.8045 | 32.6272 | 112.6373 | 21.3596 | 207.1072 | 120.1967 | 267.5207 | 10.8528 | 48.2664 | 4.4724 | 208 | 38.7212 | 0 | 278.3774 | 0
9958 | 829.8109 | 4.4417 | 23.7291 | 95.7186 | 72.4834 | 5.7 | 65.779 | 12.8013 | 11.4457 | 29.7838 | 97.4641 | 22.5559 | 198.1135 | 116.1526 | 258.744 | 10.8214 | 48.0674 | 3.375 | 201 | 39.8496 | 0 | 276.3245 | 0
9959 | 826.4865 | 3.8076 | 23.536 | 95.4121 | 72.4764 | 5.7 | 70.4095 | 13.4464 | 8.4389 | 29.5191 | 90.6212 | 23.2766 | 197.083 | 113.0304 | 251.6764 | 10.8306 | 47.8554 | 3.0174 | 197 | 41.5042 | 0 | 277.8977 | 0
9960 | 811.9932 | 4.1365 | 23.7551 | 95.8048 | 72.481 | 5.7 | 76.2843 | 8.6033 | 7.3814 | 19.462 | 58.7165 | 23.6208 | 58.1847 | 70.7119 | 167.4332 | 10.8607 | 30.2052 | 3.1019 | 164 | 43.8886 | 0 | 138.7964 | 0
9961 | 842.4561 | 3.2432 | 23.5518 | 96.3671 | 73.4811 | 4.7503 | 67.0518 | 11.3379 | 6.896 | 30.1746 | 86.9077 | 18.658 | 184.2719 | 106.3141 | 247.0345 | 10.6372 | 48.03 | 3.5905 | 171 | 43.1995 | 0 | 272.1173 | 0
9962 | 834.3565 | 2.6633 | 23.6009 | 97.6503 | 70.4846 | 7.5992 | 64.721 | 13.6224 | 6.7581 | 29.5415 | 86.8132 | 13.5006 | 177.9076 | 101.6496 | 240.8618 | 10.7839 | 47.9053 | 3.5678 | 165 | 39.2404 | 0 | 276.6275 | 0
9963 | 812.3551 | 2.7741 | 23.5793 | 98.3851 | 65.4868 | 12.3487 | 74.3323 | 10.0715 | 6.4835 | 28.3073 | 86.775 | 12.3337 | 176.177 | 91.0835 | 236.5585 | 10.9226 | 47.978 | 2.9606 | 156 | 38.5963 | 0 | 274.8504 | 0
9964 | 799.6148 | 2.9779 | 23.616 | 98.3259 | 67.4846 | 10.4505 | 71.8006 | 10.3862 | 6.5122 | 28.2308 | 87.2599 | 13.1677 | 174.75 | 85.3959 | 234.8253 | 10.9645 | 48.0544 | 2.7242 | 148 | 40.0671 | 0 | 273.2741 | 0
9965 | 791.0792 | 3.1182 | 23.7665 | 97.9238 | 68.4837 | 9.5003 | 64.8484 | 13.0579 | 6.3192 | 28.1035 | 87.436 | 13.1263 | 171.7417 | 81.9786 | 232.5473 | 10.9188 | 49.4755 | 2.7276 | 144 | 45.4395 | 0 | 268.1665 | 0
9966 | 792.6438 | 3.819 | 23.6731 | 97.9605 | 72.4822 | 5.7011 | 70.7978 | 9.2942 | 6.2702 | 28.044 | 88.5224 | 12.406 | 168.3715 | 80.4452 | 225.7151 | 10.6354 | 51.5873 | 2.7635 | 129 | 45.4538 | 0 | 274.8728 | 0
9967 | 808.8875 | 4.1381 | 23.7229 | 98.4486 | 72.4827 | 5.7 | 77.5311 | 10.7427 | 6.462 | 28.0935 | 90.8581 | 12.219 | 166.9175 | 84.3265 | 218.661 | 10.7568 | 48.8041 | 2.7662 | 125 | 41.6162 | 0 | 272.9409 | 0
9968 | 812.1958 | 3.9874 | 23.6346 | 96.931 | 71.4865 | 6.6497 | 67.9246 | 13.1257 | 6.1 | 25.9491 | 89.3922 | 11.5167 | 172.0334 | 82.8613 | 210.4201 | 10.5614 | 47.7803 | 2.9561 | 128 | 38.9224 | 0 | 270.1428 | 0
9969 | 805.5851 | 2.852 | 23.4838 | 94.7529 | 70.4849 | 7.5997 | 63.6597 | 8.2396 | 5.5717 | 33.5107 | 88.8013 | 10.4913 | 176.5949 | 80.2387 | 204.011 | 10.3229 | 46.7507 | 3.4948 | 130 | 38.6087 | 0 | 259.7458 | 0.033913
9970 | 820.1021 | 2.2705 | 29.5075 | 95.2241 | 72.481 | 5.7005 | 76.3341 | 10.5697 | 6.7702 | 51.6764 | 94.005 | 9.6876 | 181.7517 | 86.0514 | 203.4332 | 10.1938 | 46.1228 | 3.6857 | 184 | 38.5564 | 0 | 250.7222 | 0.06273
9971 | 850.9653 | 2.2109 | 36.8308 | 95.3856 | 72.4793 | 5.7 | 86.6625 | 10.8536 | 6.8342 | 61.4275 | 107.4619 | 9.4668 | 196.5886 | 92.4105 | 207.9643 | 9.9743 | 47.4459 | 4.094 | 181 | 37.6027 | 0 | 269.465 | 0.078614
9972 | 859.3476 | 2.5071 | 39.2896 | 95.9397 | 70.4812 | 7.5995 | 79.6646 | 8.7345 | 5.7683 | 60.7824 | 123.0759 | 9.4527 | 207.24 | 99.1998 | 212.4988 | 10.0332 | 47.3323 | 4.5724 | 189 | 40.0865 | 0 | 265.3916 | 0.075805
9973 | 860.3903 | 2.6743 | 38.7756 | 96.2902 | 72.4778 | 5.7005 | 81.4198 | 10.0637 | 5.4984 | 61.2834 | 132.977 | 9.4477 | 213.9911 | 105.0379 | 230.9615 | 10.0979 | 47.7457 | 4.9174 | 195 | 44.0817 | 0 | 266.5038 | 0.035261
9974 | 864.6546 | 3.0984 | 38.6635 | 97.3368 | 73.48 | 4.7503 | 100.537 | 7.9787 | 5.5951 | 60.4658 | 136.3249 | 9.446 | 225.4577 | 112.2217 | 248.5118 | 10.0776 | 47.1944 | 5.6888 | 200 | 46.8378 | 0 | 256.992 | 0.08259
9975 | 866.4363 | 3.0801 | 39.3213 | 97.4769 | 72.4819 | 5.6997 | 109.1677 | 10.1332 | 5.4265 | 60.3732 | 136.1016 | 10.2857 | 230.9302 | 112.9958 | 275.3413 | 9.5692 | 46.797 | 5.8977 | 202 | 47.6891 | 0 | 264.2585 | 0.071579
9976 | 863.6926 | 2.8581 | 38.6786 | 97.353 | 72.4788 | 5.7 | 87.5107 | 7.6936 | 5.35 | 50.8906 | 136.6363 | 12.078 | 226.9895 | 111.3326 | 278.3753 | 9.1575 | 47.0989 | 6.0053 | 192 | 46.8839 | 0 | 259.8968 | 0.040807
9977 | 871.0764 | 2.8441 | 27.1062 | 96.7835 | 72.4782 | 5.7 | 74.3506 | 10.7856 | 5.3435 | 32.3228 | 136.9949 | 10.766 | 220.3505 | 114.0675 | 269.3881 | 9.4666 | 47.1083 | 5.5259 | 196 | 46.4113 | 0 | 262.6877 | 0.0039721
9978 | 873.0458 | 4.1423 | 23.1867 | 98.0991 | 73.4777 | 4.7503 | 79.4104 | 8.09 | 5.9874 | 27.4686 | 136.846 | 11.323 | 217.1308 | 119.4895 | 287.3323 | 10.2513 | 48.7799 | 5.52 | 175 | 43.5843 | 0 | 263.7634 | 0
9979 | 859.4568 | 5.1358 | 23.3163 | 99.3718 | 69.4838 | 8.5489 | 79.1372 | 10.8587 | 6.519 | 28.7642 | 138.9595 | 12.1013 | 212.2983 | 117.7885 | 284.1955 | 10.5964 | 48.7091 | 5.4262 | 148 | 42.8232 | 0 | 272.5109 | 0
9980 | 842.3169 | 9.6621 | 23.2844 | 99.2177 | 71.4806 | 6.6505 | 68.8038 | 10.3313 | 6.8859 | 29.2939 | 131.2146 | 12.4138 | 201.4835 | 111.9798 | 270.4258 | 10.6698 | 49.4101 | 5.2941 | 141 | 40.6889 | 0 | 265.3134 | 0
9981 | 832.7848 | 12.1497 | 23.3579 | 98.7884 | 73.4798 | 4.7505 | 74.3039 | 9.5306 | 6.8054 | 29.2767 | 106.1874 | 12.3286 | 197.3866 | 105.2399 | 251.1962 | 10.4571 | 49.1382 | 5.2175 | 138 | 38.4777 | 0 | 261.0916 | 0
9982 | 820.4653 | 14.8656 | 23.4939 | 98.3003 | 72.4787 | 5.6997 | 87.2873 | 11.901 | 6.5288 | 29.9065 | 93.7883 | 12.2544 | 191.2342 | 98.5781 | 230.716 | 10.5813 | 48.247 | 5.4521 | 138 | 38.1699 | 0 | 247.8871 | 0
9983 | 817.1401 | 17.6243 | 23.4318 | 98.6865 | 72.4798 | 5.7 | 85.9647 | 8.1311 | 6.1998 | 29.3406 | 91.8921 | 12.2445 | 181.108 | 93.1648 | 216.8973 | 10.6801 | 47.6629 | 5.1325 | 134 | 36.0633 | 0 | 249.8607 | 0
9984 | 805.495 | 14.5 | 23.4259 | 97.7011 | 72.4852 | 5.7 | 69.1978 | 11.5562 | 6.2194 | 14.0814 | 45.2409 | 12.2571 | 0 | 53.2575 | 146.5306 | 10.6873 | 30.0427 | 4.1937 | 122 | 36.2711 | 0 | 112.3322 | 0
9985 | 809.8857 | 10.6799 | 23.4102 | 97.8348 | 71.4833 | 6.6497 | 72.1506 | 8.4402 | 6.1553 | 27.7428 | 89.3528 | 12.4138 | 167.3915 | 84.762 | 214.1511 | 10.6999 | 47.9515 | 3.2301 | 117 | 35.5825 | 0 | 252.4216 | 0
9986 | 812.8127 | 7.2139 | 23.4786 | 96.7139 | 72.483 | 5.7003 | 75.8032 | 10.9594 | 6.2605 | 27.7454 | 89.2645 | 12.7914 | 166.3094 | 86.2923 | 212.6389 | 10.5311 | 47.5976 | 2.9588 | 110 | 35.8356 | 0 | 260.785 | 0
9987 | 798.0969 | 3.5782 | 23.5688 | 96.3252 | 72.4858 | 5.7 | 65.8763 | 10.2521 | 6.3415 | 28.2487 | 89.3724 | 12.9233 | 166.5859 | 87.6335 | 215.3853 | 10.6661 | 47.622 | 2.9518 | 111 | 36.0003 | 0 | 255.1193 | 0
9988 | 793.7482 | 2.8237 | 24.5632 | 96.7552 | 72.4855 | 5.7 | 64.5192 | 9.923 | 6.2855 | 28.1869 | 89.4249 | 12.488 | 166.0878 | 94.4731 | 213.6412 | 10.9388 | 47.5461 | 2.9422 | 107 | 35.7749 | 0 | 269.1543 | 0
9989 | 796.8461 | 3.0406 | 27.7129 | 98.2422 | 72.4892 | 5.7 | 73.272 | 12.6096 | 6.1812 | 28.6718 | 89.2874 | 12.2851 | 170.9857 | 87.3801 | 209.5909 | 10.9141 | 49.1771 | 2.9272 | 107 | 35.7625 | 0 | 324.3072 | 0
9990 | 798.5366 | 4.1875 | 33.0488 | 97.0285 | 71.4854 | 6.6497 | 76.9829 | 8.3313 | 6.7305 | 40.0683 | 90.4713 | 13.615 | 180.0886 | 87.6955 | 214.4675 | 10.9597 | 51.6268 | 2.9951 | 115 | 38.6306 | 0 | 344.9354 | 0
9991 | 846.4392 | 5.9161 | 50.1218 | 99.5594 | 70.4775 | 7.5997 | 82.1976 | 11.1557 | 9.5543 | 62.8916 | 110.9099 | 16.8783 | 216.7628 | 163.4471 | 244.4559 | 13.3757 | 49.532 | 3.989 | 174 | 47.5887 | 0 | 387.2317 | 0
9992 | 910.9934 | 6.5975 | 75.9927 | 106.3333 | 64.7139 | 13.2984 | 108.7569 | 13.2745 | 11.2593 | 77.1425 | 145.9837 | 28.0907 | 277.3144 | 240.352 | 328.1002 | 27.5673 | 53.7469 | 11.445 | 258 | 57.2422 | 0 | 444.9424 | 0
9993 | 1000.5471 | 5.9335 | 93.2795 | 119.9096 | 64.6059 | 13.3 | 139.4968 | 10.4791 | 16.6324 | 78.0163 | 170.2033 | 33.6766 | 334.111 | 299.3847 | 455.5877 | 34.7497 | 65.3318 | 15.9104 | 296 | 64.6569 | 0 | 499.3175 | 0.015424
9994 | 1092.2184 | 6.405 | 99.6507 | 131.9308 | 63.4746 | 14.2497 | 157.9148 | 15.1038 | 20.3816 | 86.9628 | 187.7339 | 36.3498 | 374.2052 | 338.3497 | 542.9949 | 39.547 | 77.7586 | 18.3731 | 364 | 71.3089 | 0 | 563.3106 | 0.048436
9995 | 1139.2893 | 10.3761 | 98.0924 | 136.0074 | 60.4805 | 17.0992 | 161.1228 | 11.5893 | 20.6704 | 96.858 | 197.3957 | 40.9869 | 391.9547 | 355.5891 | 593.9486 | 40.4186 | 86.1159 | 17.6404 | 347 | 80.5713 | 0 | 576.4086 | 0.05612
9996 | 1166.9126 | 12.2235 | 101.1362 | 137.5651 | 59.4797 | 18.0497 | 163.782 | 14.6154 | 19.151 | 99.9624 | 202.3642 | 41.8439 | 409.9515 | 377.1781 | 618.7242 | 39.6476 | 90.3221 | 17.3762 | 301 | 87.5509 | 0 | 589.9776 | 0.075933
9997 | 1189.7782 | 8.0594 | 101.712 | 137.3412 | 61.4758 | 16.1505 | 163.4799 | 12.125 | 17.924 | 97.3029 | 202.2926 | 44.0336 | 451.8752 | 371.0772 | 616.6456 | 41.1606 | 87.9722 | 18.2892 | 353 | 78.0196 | 0 | 593.299 | 0.026979
9998 | 1200.7322 | 6.8788 | 105.6773 | 143.5782 | 63.4754 | 14.2505 | 162.5942 | 14.4863 | 22.9717 | 92.2545 | 209.1762 | 45.5072 | 513.8829 | 365.3896 | 604.0366 | 42.4848 | 90.3179 | 18.4157 | 286 | 77.2321 | 0 | 608.7225 | 0.015162
9999 | 1207.8299 | 7.2392 | 106.1653 | 143.1111 | 62.4754 | 15.1997 | 164.2025 | 13.0592 | 22.9598 | 89.7443 | 218.4595 | 44.5458 | 541.1577 | 364.1831 | 595.4311 | 41.2663 | 91.7818 | 21.1735 | 283 | 75.8403 | 0 | 595.6186 | 0.0057477
10000 | 1176.5986 | 5.8807 | 102.9561 | 143.1002 | 61.4767 | 16.1497 | 162.3258 | 13.9753 | 19.2263 | 92.8708 | 213.4212 | 40.2251 | 535.3335 | 358.8883 | 573.4063 | 40.8194 | 91.9644 | 20.1529 | 275 | 69.5253 | 0 | 576.9466 | 0.0034745
10001 | 1152.2605 | 5.2581 | 98.0716 | 138.2224 | 69.4739 | 8.5521 | 153.7712 | 11.5938 | 16.175 | 91.9508 | 204.9622 | 36.637 | 511.9681 | 342.0046 | 512.1346 | 34.0459 | 87.745 | 18.9889 | 255 | 63.521 | 0 | 551.4862 | 0.0012371
10002 | 1085.5069 | 6.2045 | 93.0147 | 119.8726 | 70.4786 | 7.6003 | 139.3935 | 11.4852 | 11.8876 | 76.8402 | 186.8936 | 33.0109 | 465.5646 | 275.1251 | 427.2492 | 21.2653 | 78.4796 | 18.2843 | 235 | 61.8024 | 0 | 421.8154 | 0
10003 | 1038.5496 | 5.8779 | 85.6844 | 105.412 | 70.4814 | 7.6 | 122.4967 | 9.5761 | 9.3204 | 57.2624 | 156.089 | 26.5417 | 411.6368 | 190.7279 | 373.6418 | 21.5894 | 68.3342 | 14.4612 | 209 | 57.8135 | 0 | 376.589 | 0
10004 | 996.8767 | 4.8904 | 69.7099 | 100.2915 | 71.4825 | 6.6521 | 102.0458 | 8.5191 | 7.3786 | 49.5187 | 142.2801 | 13.206 | 376.0829 | 148.5412 | 339.7571 | 15.4664 | 58.0911 | 8.1899 | 196 | 52.2304 | 0 | 309.5919 | 0
10005 | 935.6647 | 5.4219 | 48.2205 | 98.7079 | 72.4819 | 5.6984 | 88.3257 | 9.6141 | 6.7097 | 46.294 | 133.5409 | 8.4962 | 352.5047 | 126.9302 | 313.0872 | 11.3122 | 53.3027 | 5.7034 | 187 | 47.0967 | 0 | 277.4082 | 0
10006 | 906.7008 | 5.0027 | 42.2325 | 97.0091 | 70.4785 | 7.5995 | 80.417 | 8.5665 | 6.4478 | 42.5893 | 117.6776 | 8.1899 | 320.4949 | 110.5147 | 282.1636 | 10.6492 | 50.1162 | 4.9945 | 177 | 44.3724 | 0 | 273.6453 | 0
10007 | 882.3087 | 4.317 | 40.799 | 96.3202 | 71.4782 | 6.6503 | 72.2884 | 9.7538 | 6.3242 | 37.2071 | 97.8371 | 7.8813 | 300.3372 | 102.4381 | 270.7787 | 10.6742 | 48.7683 | 4.733 | 152 | 39.3198 | 0 | 275.233 | 0
10008 | 854.6742 | 3.3557 | 40.1604 | 96.4292 | 72.4796 | 5.7003 | 73.6673 | 9.177 | 6.3028 | 22.667 | 59.6068 | 7.8005 | 88.2756 | 58.5843 | 176.7084 | 10.5871 | 30.5998 | 3.9968 | 138 | 36.6632 | 0 | 140.1488 | 0
10009 | 847.0352 | 2.6288 | 40.236 | 96.0575 | 73.4783 | 4.7503 | 78.1964 | 9.6909 | 6.2471 | 32.3662 | 86.6569 | 7.7375 | 293.9062 | 96.3529 | 242.076 | 10.3448 | 48.2517 | 3.7568 | 133 | 35.6926 | 0 | 272.5597 | 0
10010 | 851.1471 | 2.4703 | 40.1094 | 95.0859 | 72.4798 | 5.6997 | 78.1924 | 9.95 | 6.3313 | 29.5593 | 89.4167 | 8.1812 | 293.9599 | 91.7347 | 240.2573 | 10.4632 | 48.0245 | 3.2089 | 126 | 35.5583 | 0 | 270.0456 | 0
10011 | 838.006 | 2.5157 | 40.0034 | 94.8646 | 72.4801 | 5.7 | 74.128 | 9.118 | 6.1998 | 28.6933 | 91.8841 | 8.3197 | 285.4767 | 88.2289 | 244.4496 | 10.5031 | 47.8811 | 2.8002 | 122 | 35.5042 | 0 | 274.1962 | 0
10012 | 830.1067 | 2.6119 | 39.9037 | 94.9726 | 72.4783 | 5.7 | 65.4902 | 11.5905 | 6.0512 | 28.7362 | 91.9937 | 7.7589 | 276.417 | 86.7143 | 235.3819 | 10.4951 | 47.7644 | 2.7327 | 119 | 35.4511 | 0 | 275.5487 | 0
10013 | 825.4295 | 3.1229 | 40.2193 | 95.3404 | 71.4797 | 6.6497 | 71.1585 | 8.3889 | 6.2422 | 28.9431 | 90.1421 | 7.5524 | 279.2371 | 85.3059 | 223.402 | 10.3841 | 49.5859 | 2.71 | 112 | 36.6682 | 0 | 302.928 | 0
10014 | 828.7319 | 4.0904 | 41.1211 | 95.1142 | 71.4779 | 6.65 | 81.3037 | 11.355 | 6.5869 | 40.4369 | 89.3073 | 10.0721 | 290.6301 | 93.5703 | 226.4487 | 10.2511 | 52.0199 | 2.711 | 118 | 35.9871 | 0 | 367.2645 | 0
10015 | 872.4233 | 6.0038 | 48.1152 | 99.344 | 71.4759 | 6.65 | 87.259 | 9.8037 | 8.2852 | 64.3778 | 103.0629 | 21.9132 | 326.9008 | 171.7071 | 249.5248 | 13.1732 | 49.1939 | 2.7297 | 196 | 50.9134 | 0 | 405.3484 | 0
10016 | 937.2012 | 8.9124 | 70.1079 | 100.955 | 63.4785 | 14.2479 | 102.6466 | 10.7506 | 12.2164 | 77.6796 | 148.5207 | 33.6599 | 378.4593 | 238.5981 | 342.0606 | 26.6516 | 52.1455 | 5.5904 | 293 | 60.0175 | 0 | 446.5744 | 0
10017 | 1029.7941 | 14.6624 | 91.7099 | 116.4354 | 61.4727 | 16.1495 | 129.9911 | 14.533 | 15.0614 | 79.5092 | 180.9861 | 35.5151 | 462.2915 | 283.5531 | 474.4349 | 34.8581 | 75.3348 | 12.8859 | 291 | 68.8658 | 0 | 504.9152 | 0.089116
10018 | 1137.8474 | 15.1015 | 97.6055 | 129.174 | 60.4685 | 17.0997 | 150.6796 | 9.7342 | 19.1473 | 82.1946 | 198.7666 | 33.6522 | 523.9131 | 316.4408 | 553.7231 | 39.8244 | 98.6776 | 17.3942 | 358 | 73.0673 | 0 | 569.9667 | 0.10684
10019 | 1190.7027 | 13.1985 | 98.9555 | 141.3486 | 61.4717 | 16.1503 | 146.8118 | 13.816 | 24.4366 | 108.1551 | 205.9949 | 35.8549 | 540.1931 | 339.4864 | 592.4836 | 41.3435 | 107.2109 | 17.4148 | 335 | 73.3077 | 0 | 595.2212 | 0.12933
10020 | 1216.9113 | 7.6353 | 103.3619 | 140.9954 | 61.477 | 16.15 | 152.667 | 11.7242 | 23.4818 | 112.8468 | 202.9639 | 35.6878 | 548.313 | 358.8562 | 601.8529 | 41.2872 | 103.3186 | 17.0483 | 322 | 78.5441 | 0 | 598.9241 | 0.23716
10021 | 1193.9113 | 5.2726 | 102.7679 | 139.8205 | 59.4778 | 18.0495 | 157.0893 | 12.0897 | 18.7905 | 94.9065 | 204.2177 | 37.2715 | 545.0288 | 356.6628 | 584.9707 | 42.0989 | 97.4434 | 17.284 | 354 | 69.3059 | 0 | 611.785 | 0.28
10022 | 1186.7973 | 5.0641 | 102.6432 | 140.8588 | 60.4789 | 17.1003 | 158.0718 | 10.8986 | 17.8575 | 99.5588 | 205.0451 | 41.2275 | 547.4384 | 355.0643 | 592.7235 | 42.6725 | 99.3704 | 17.6889 | 319 | 66.4532 | 0 | 598.9252 | 0.27951
10023 | 1196.6924 | 7.2452 | 102.7234 | 142.7272 | 61.4766 | 16.1503 | 159.1066 | 10.3191 | 16.7657 | 105.1303 | 213.6622 | 41.8974 | 549.0471 | 362.8806 | 574.6806 | 40.8094 | 97.5996 | 17.8469 | 281 | 68.0397 | 0 | 600.5691 | 0.24692
10024 | 1183.2552 | 11.1738 | 99.1674 | 140.9488 | 60.4794 | 17.0997 | 156.0298 | 11.6889 | 14.8453 | 101.3407 | 208.3074 | 38.7865 | 472.9909 | 363.6218 | 554.4756 | 38.2483 | 84.6685 | 17.6733 | 277 | 68.3654 | 0 | 616.9719 | 0.1575
10025 | 1160.1666 | 8.3477 | 89.8707 | 131.5432 | 68.475 | 9.5021 | 146.273 | 9.3817 | 15.4403 | 83.6448 | 206.1332 | 35.4609 | 409.3196 | 345.1266 | 510.1903 | 30.9968 | 79.9829 | 17.2779 | 245 | 65.691 | 0 | 552.8753 | 0.011309
10026 | 1100.4784 | 6.5222 | 86.1481 | 119.1147 | 71.4769 | 6.6508 | 132.1768 | 12.1041 | 17.3258 | 65.5123 | 197.1557 | 33.6439 | 364.5555 | 281.1185 | 442.2417 | 17.9511 | 73.3716 | 16.6102 | 234 | 64.5857 | 0 | 403.8368 | 0
10027 | 1042.728 | 6.3102 | 82.3709 | 107.5442 | 71.4813 | 6.6518 | 113.7804 | 11.5887 | 15.8685 | 50.6404 | 165.3714 | 24.8362 | 321.7322 | 204.4876 | 382.2193 | 13.415 | 65.5204 | 14.1903 | 227 | 59.1313 | 0 | 370.228 | 0
10028 | 990.5165 | 5.7588 | 70.3025 | 103.986 | 71.4864 | 6.6482 | 101.6632 | 9.7934 | 11.567 | 45.1008 | 150.7136 | 13.9072 | 287.6361 | 171.2073 | 329.4206 | 12.0675 | 55.2615 | 8.3757 | 201 | 54.3944 | 0 | 323.647 | 0
10029 | 944.549 | 6.3068 | 38.1391 | 100.2929 | 71.4775 | 6.65 | 89.1301 | 12.2608 | 10.1828 | 40.5956 | 135.7966 | 11.7361 | 261.0981 | 151.286 | 279.1022 | 10.9133 | 50.2632 | 5.6038 | 178 | 51.0831 | 0 | 293.5286 | 0
10030 | 908.9586 | 5.2929 | 24.6984 | 96.7882 | 72.4797 | 5.7003 | 78.4616 | 8.3096 | 9.8933 | 33.2475 | 111.698 | 11.0891 | 234.6273 | 129.004 | 251.6615 | 10.7716 | 48.5937 | 4.7118 | 162 | 43.7457 | 0 | 287.1451 | 0
10031 | 880.3603 | 4.1652 | 23.4562 | 95.8116 | 70.4822 | 7.5995 | 88.062 | 11.2012 | 11.6433 | 28.7528 | 91.1253 | 8.156 | 214.4373 | 118.7361 | 249.6259 | 10.8566 | 48.2904 | 4.1243 | 150 | 40.0955 | 0 | 280.3662 | 0
10032 | 850.4884 | 3.2526 | 23.6625 | 94.9262 | 72.4818 | 5.7005 | 85.2218 | 9.315 | 9.9863 | 18.2639 | 56.5482 | 7.0729 | 61.3377 | 74.1176 | 162.9371 | 10.8867 | 30.3811 | 3.9712 | 133 | 38.5416 | 0 | 144.5112 | 0
10033 | 850.4863 | 2.6746 | 23.4405 | 94.7861 | 72.4809 | 5.7 | 70.8107 | 10.4021 | 7.6353 | 28.2205 | 85.7112 | 7.082 | 198.183 | 110.7563 | 224.1142 | 10.9633 | 48.1309 | 4.0085 | 129 | 37.1475 | 0 | 274.2822 | 0
10034 | 847.9822 | 2.5514 | 23.4231 | 94.4532 | 72.4815 | 5.7 | 68.2611 | 11.9835 | 7.0585 | 29.0983 | 86.4018 | 7.7429 | 193.0423 | 106.6744 | 224.1742 | 10.7816 | 47.6147 | 3.3046 | 117 | 37.7581 | 0 | 277.9135 | 0
10035 | 837.9196 | 2.4947 | 23.6554 | 94.4091 | 72.4835 | 5.7 | 77.0483 | 8.6966 | 7.0643 | 29.6642 | 86.4392 | 7.9856 | 189.7742 | 103.635 | 232.2213 | 10.9317 | 47.5818 | 2.9149 | 113 | 37.4983 | 0 | 281.7383 | 0
10036 | 831.4738 | 2.4424 | 23.6016 | 95.9316 | 73.4784 | 4.7503 | 72.9061 | 11.5296 | 7.0987 | 29.2538 | 85.7477 | 7.3383 | 189.1466 | 102.2876 | 230.7794 | 11.0724 | 47.5278 | 2.785 | 108 | 37.4055 | 0 | 278.9161 | 0
10037 | 828.6572 | 2.7982 | 22.8235 | 97.1292 | 70.4812 | 7.5992 | 66.2282 | 12.7487 | 7.0813 | 29.6995 | 85.3815 | 7.0366 | 193.8187 | 102.2606 | 224.0836 | 11.0265 | 48.9887 | 2.6552 | 107 | 37.2981 | 0 | 313.109 | 0
10038 | 843.011 | 4.0212 | 27.7798 | 100.2289 | 71.4879 | 6.6429 | 77.5979 | 8.6577 | 7.1918 | 39.5899 | 86.575 | 9.6441 | 203.4673 | 108.603 | 227.8443 | 10.998 | 51.1683 | 2.6236 | 107 | 37.2013 | 0 | 370.5247 | 0
10039 | 887.6578 | 5.7492 | 40.9409 | 102.3309 | 68.4717 | 9.5066 | 97.6169 | 11.3181 | 9.992 | 62.2283 | 98.2227 | 22.7311 | 237.7389 | 169.574 | 244.4441 | 13.2917 | 50.1225 | 2.6091 | 160 | 49.0165 | 0 | 404.467 | 0
10040 | 942.9938 | 5.6925 | 70.0728 | 102.3771 | 65.4747 | 12.3492 | 111.7439 | 8.4835 | 11.8182 | 74.6547 | 137.394 | 30.7298 | 282.6711 | 240.6949 | 348.3916 | 26.2433 | 52.5403 | 5.0764 | 293 | 59.2773 | 0 | 435.2425 | 0
10041 | 1028.4816 | 11.0198 | 91.1378 | 116.5308 | 63.4732 | 14.2495 | 129.1255 | 12.8406 | 14.9552 | 72.2542 | 170.7268 | 33.3233 | 347.4326 | 298.3589 | 457.5448 | 35.6629 | 64.6796 | 12.2387 | 295 | 68.9381 | 0 | 501.6248 | 0.097342
10042 | 1117.6286 | 18.4151 | 99.0735 | 129.7683 | 62.4708 | 15.1997 | 155.202 | 10.8986 | 17.1192 | 90.6166 | 191.8644 | 34.6813 | 391.847 | 328.592 | 541.5447 | 39.2782 | 71.5227 | 17.0716 | 338 | 73.6666 | 0 | 593.3378 | 0.16312
10043 | 1161.1544 | 20.414 | 100.8226 | 135.4331 | 58.4697 | 18.9989 | 165.5608 | 13.3344 | 20.282 | 92.8076 | 208.1881 | 37.2724 | 403.3992 | 348.4589 | 582.8328 | 40.2807 | 82.0885 | 17.7663 | 337 | 75.0995 | 0 | 592.1553 | 0.17202
10044 | 1199.5967 | 14.4384 | 102.4006 | 136.2527 | 63.4696 | 14.2513 | 157.8095 | 10.1447 | 21.5205 | 100.1336 | 210.7701 | 37.5242 | 412.9365 | 365.0036 | 582.1468 | 39.5038 | 84.3792 | 17.5645 | 319 | 80.0362 | 0 | 580.3142 | 0.16296
10045 | 1194.95 | 10.1399 | 101.9939 | 139.6493 | 64.4747 | 13.3003 | 161.469 | 12.082 | 21.9957 | 103.2195 | 208.6278 | 36.6039 | 417.2975 | 362.7308 | 567.7087 | 41.3265 | 82.646 | 18.1668 | 363 | 73.6907 | 0 | 585.0467 | 0.12471
10046 | 1210.1825 | 8.6778 | 104.393 | 141.4252 | 61.4759 | 16.1492 | 166.1405 | 10.1926 | 21.8948 | 95.4066 | 212.5617 | 42.131 | 433.6848 | 360.5784 | 580.5897 | 42.0582 | 85.3733 | 18.3273 | 320 | 79.5188 | 0 | 605.8216 | 0.066786
10047 | 1228.5328 | 6.6615 | 106.4282 | 140.8434 | 64.4706 | 13.3008 | 167.9649 | 11.6895 | 20.8942 | 99.9442 | 219.9389 | 43.1374 | 473.067 | 366.6741 | 585.8815 | 41.6671 | 88.1466 | 18.7297 | 310 | 83.7208 | 0 | 614.3621 | 0.056584
10048 | 1196.3072 | 11.9392 | 102.4969 | 140.5323 | 61.4769 | 16.1492 | 161.8076 | 11.7932 | 17.6948 | 101.4715 | 214.3663 | 40.2945 | 469.8413 | 362.9542 | 574.5583 | 39.5258 | 89.2819 | 19.3916 | 253 | 75.5683 | 0 | 590.2284 | 0.028568
10049 | 1146.9213 | 8.8434 | 94.6429 | 134.5565 | 70.4725 | 7.6024 | 152.0402 | 10.1152 | 16.8547 | 99.2378 | 211.0665 | 37.3125 | 512.905 | 343.9482 | 535.7568 | 35.877 | 85.5445 | 18.8231 | 258 | 70.42 | 0 | 520.7072 | 0.0065063
10050 | 1080.5225 | 6.244 | 81.7122 | 121.6521 | 73.4765 | 4.7508 | 138.0563 | 11.7819 | 22.3814 | 87.6126 | 213.0157 | 35.6155 | 406.2632 | 280.8177 | 470.1797 | 21.5831 | 78.4548 | 17.8354 | 233 | 61.4686 | 0 | 374.1374 | 0
10051 | 1038.1185 | 5.7401 | 76.7012 | 106.2456 | 72.4778 | 5.7013 | 116.646 | 9.3406 | 24.0913 | 63.7794 | 183.6475 | 32.3449 | 329.7173 | 199.2722 | 405.4197 | 13.9121 | 71.6892 | 14.6876 | 253 | 57.9083 | 0 | 356.1265 | 0
10052 | 976.3089 | 5.3597 | 63.4734 | 100.75 | 72.4844 | 5.6984 | 103.1336 | 12.2879 | 20.5748 | 51.0125 | 159.8294 | 19.5062 | 311.2102 | 182.5665 | 354.2093 | 11.4289 | 61.3563 | 8.7933 | 196 | 53.0628 | 0 | 300.9831 | 0
10053 | 938.559 | 8.3217 | 30.5123 | 98.4414 | 72.4799 | 5.7 | 100.4926 | 9.0232 | 15.969 | 45.8772 | 145.6561 | 15.5945 | 328.7973 | 163.0371 | 303.1382 | 10.9366 | 53.0231 | 5.9406 | 176 | 47.9044 | 0 | 271.0019 | 0
10054 | 902.0572 | 9.9042 | 18.1045 | 97.8622 | 72.4785 | 5.7 | 89.8458 | 11.2286 | 9.5573 | 38.5667 | 123.1469 | 14.2365 | 258.1078 | 125.6105 | 271.2988 | 10.6737 | 49.9592 | 5.0155 | 180 | 40.2867 | 0 | 262.6895 | 0
10055 | 884.4877 | 10.475 | 17.2463 | 95.9594 | 72.4801 | 5.7 | 74.4782 | 7.3471 | 6.8448 | 32.9948 | 99.4424 | 13.6021 | 214.0705 | 108.1338 | 250.9126 | 10.7919 | 49.4587 | 4.426 | 161 | 37.4257 | 0 | 258.16 | 0
10056 | 867.9948 | 13.3437 | 17.1103 | 95.3587 | 72.482 | 5.7 | 78.9782 | 11.0038 | 6.5485 | 20.4825 | 60.8143 | 13.3312 | 61.0764 | 65.5405 | 161.2703 | 10.8433 | 30.9931 | 3.7934 | 148 | 37.5774 | 0 | 127.1844 | 0
10057 | 875.5138 | 16.3498 | 17.0955 | 95.2329 | 70.4846 | 7.5995 | 82.6324 | 7.4689 | 6.5902 | 28.1583 | 90.1279 | 11.5628 | 190.4682 | 92.7572 | 236.1381 | 10.7464 | 48.8029 | 2.9151 | 133 | 36.4648 | 0 | 251.9735 | 0
10058 | 880.2941 | 17.1014 | 16.9864 | 94.6724 | 72.484 | 5.7005 | 81.4886 | 10.7953 | 6.266 | 25.8909 | 88.134 | 9.2306 | 187.9051 | 87.6631 | 243.2182 | 10.673 | 48.5496 | 2.6077 | 128 | 35.2192 | 0 | 252.733 | 0
10059 | 870.4501 | 11.859 | 17.0089 | 96.1189 | 73.4781 | 4.7503 | 71.6755 | 8.2707 | 6.2232 | 25.5239 | 87.6736 | 11.1837 | 183.252 | 85.4423 | 245.4867 | 10.4416 | 48.138 | 2.592 | 127 | 34.6201 | 0 | 260.429 | 0
10060 | 853.5168 | 5.1771 | 17.0218 | 94.4321 | 72.4805 | 5.6997 | 71.8487 | 11.0707 | 6.1238 | 25.9964 | 87.818 | 9.6295 | 181.4053 | 86.5676 | 227.6948 | 10.5372 | 48.0528 | 2.6194 | 129 | 33.8613 | 0 | 264.288 | 0
10061 | 845.6704 | 3.5727 | 17.0528 | 94.9473 | 72.4801 | 5.7 | 78.8556 | 13.3838 | 6.2277 | 25.8244 | 87.7392 | 8.5605 | 186.2576 | 87.1766 | 214.5194 | 10.5754 | 49.5165 | 2.635 | 118 | 34.5563 | 0 | 303.4578 | 0
10062 | 860.6446 | 5.0207 | 23.1149 | 96.7146 | 72.4823 | 5.7 | 77.7407 | 13.4254 | 6.419 | 36.0343 | 89.5919 | 10.5773 | 196.6075 | 95.5327 | 221.3772 | 10.4958 | 52.4007 | 2.6386 | 117 | 36.0908 | 0 | 352.8216 | 0
10063 | 887.3651 | 6.7311 | 40.2385 | 103.9313 | 71.4809 | 6.6497 | 87.0099 | 8.4876 | 9.179 | 63.4642 | 102.4465 | 19.9632 | 243.4521 | 169.6561 | 247.1566 | 13.1152 | 53.1653 | 3.1846 | 199 | 50.9852 | 0 | 400.6374 | 0
10064 | 947.7211 | 7.9807 | 68.5257 | 105.314 | 65.4765 | 12.3484 | 114.0824 | 11.818 | 11.153 | 80.713 | 142.2225 | 33.2388 | 287.0573 | 239.776 | 332.6408 | 26.4597 | 56.4449 | 6.4339 | 319 | 56.5901 | 0 | 427.8097 | 0
10065 | 1071.418 | 14.9765 | 87.4649 | 117.8906 | 61.4738 | 16.1489 | 133.8341 | 12.7719 | 14.9142 | 87.4713 | 176.3423 | 39.3349 | 336.3119 | 289.7179 | 446.8944 | 33.9533 | 68.6041 | 15.6522 | 333 | 64.8348 | 0 | 507.3623 | 0.039154
10066 | 1155.0291 | 14.6614 | 98.6928 | 129.0859 | 61.4728 | 16.15 | 144.6498 | 11.4958 | 19.8792 | 96.0091 | 196.0628 | 40.8158 | 383.685 | 317.9284 | 540.1034 | 40.049 | 79.6717 | 17.8602 | 441 | 66.1639 | 0 | 563.4329 | 0.062149
10067 | 1205.2229 | 13.0881 | 98.7283 | 133.7552 | 61.476 | 16.15 | 160.543 | 12.3363 | 24.9507 | 105.4504 | 204.3624 | 42.3746 | 413.2394 | 338.6591 | 573.487 | 41.3329 | 87.2937 | 17.5826 | 365 | 68.1342 | 0 | 566.3446 | 0.068133
10068 | 1227.1081 | 8.6355 | 100.6246 | 136.3864 | 63.4751 | 14.2505 | 165.5386 | 11.4248 | 23.8172 | 107.742 | 210.2612 | 41.8181 | 429.6829 | 359.1301 | 587.9881 | 40.603 | 91.2566 | 17.9886 | 333 | 69.7177 | 0 | 579.2047 | 0.12462
10069 | 1229.7943 | 6.7575 | 102.2792 | 140.7164 | 64.4752 | 13.3003 | 153.0167 | 12.4934 | 20.8922 | 97.8712 | 209.5429 | 40.227 | 415.6391 | 354.5308 | 583.7697 | 41.3625 | 105.2434 | 18.1848 | 351 | 67.2755 | 0 | 621.1421 | 0.09672
10070 | 1234.3882 | 10.0325 | 102.9761 | 144.1127 | 63.4729 | 14.2497 | 158.5379 | 11.5176 | 22.8878 | 93.0957 | 220.6606 | 39.9504 | 525.4907 | 355.3641 | 607.6469 | 42.2576 | 109.6394 | 19.2055 | 287 | 70.1473 | 0 | 627.9774 | 0.12959
10071 | 1242.6506 | 7.3456 | 100.3018 | 141.8944 | 62.47 | 15.1997 | 161.1704 | 12.8163 | 22.187 | 94.1108 | 238.2768 | 39.8496 | 583.293 | 361.8278 | 589.2366 | 42.8514 | 106.5614 | 19.3912 | 286 | 70.2455 | 0 | 605.3957 | 0.081611
10072 | 1222.1116 | 5.2141 | 100.6435 | 140.3438 | 61.4675 | 16.1497 | 151.5512 | 13.2261 | 16.382 | 93.9184 | 233.6511 | 39.5773 | 575.3552 | 355.4153 | 561.287 | 44.9089 | 104.3613 | 19.6751 | 265 | 68.8624 | 0 | 608.9028 | 0.038402
10073 | 1179.6785 | 9.8787 | 87.6055 | 134.9396 | 64.4685 | 13.3008 | 148.1159 | 14.4588 | 9.6563 | 87.1129 | 210.6705 | 38.4871 | 506.7876 | 335.7667 | 525.1429 | 36.5519 | 89.1046 | 19.3249 | 232 | 61.8719 | 0 | 561.736 | 0.0082728
10074 | 1100.1382 | 13.036 | 76.169 | 120.3217 | 71.4713 | 6.6518 | 130.3043 | 10.4405 | 13.1181 | 86.5433 | 190.0439 | 38.57 | 398.9615 | 280.2904 | 450.5397 | 19.9234 | 80.7692 | 17.6114 | 233 | 55.7449 | 0 | 384.243 | 0
10075 | 1045.4869 | 8.6104 | 70.4802 | 105.7338 | 72.4757 | 5.7003 | 110.9481 | 12.8552 | 14.2538 | 80.0015 | 158.441 | 34.1819 | 336.4054 | 220.3633 | 404.7055 | 13.3883 | 75.6274 | 14.5472 | 218 | 49.7367 | 0 | 367.7667 | 0
10076 | 997.4361 | 5.3789 | 58.4252 | 100.0333 | 72.4784 | 5.7 | 96.2535 | 13.069 | 9.811 | 70.8111 | 142.0353 | 19.9595 | 292.8947 | 185.4083 | 360.4902 | 12.5418 | 63.7132 | 8.714 | 189 | 46.8776 | 0 | 324.9047 | 0
10077 | 951.3008 | 6.6257 | 27.4113 | 97.2478 | 72.4815 | 5.7 | 79.1794 | 10.4953 | 7.4703 | 56.1345 | 130.6877 | 14.8041 | 290.7242 | 157.7999 | 324.0196 | 11.7569 | 56.5454 | 6.2946 | 187 | 43.4212 | 0 | 302.1685 | 0
10078 | 917.271 | 10.1331 | 17.1515 | 96.6338 | 71.4809 | 6.6497 | 73.7856 | 11.1106 | 6.8905 | 43.9887 | 115.0954 | 14.6574 | 348.979 | 136.4848 | 300.5143 | 11.5412 | 54.522 | 5.6036 | 180 | 40.5602 | 0 | 297.8925 | 0
10079 | 892.0624 | 11.8401 | 16.9216 | 97.3441 | 72.4766 | 5.7003 | 80.5379 | 13.1408 | 6.3715 | 35.8614 | 98.6386 | 13.8436 | 363.0795 | 115.6354 | 283.2128 | 11.2016 | 52.8381 | 4.5262 | 156 | 40.5805 | 0 | 290.3624 | 0
10080 | 855.5772 | 10.6805 | 16.5589 | 98.0624 | 73.477 | 4.7503 | 77.4359 | 13.6443 | 6.1957 | 20.9919 | 61.0577 | 17.3892 | 106.2093 | 68.238 | 178.4682 | 11.215 | 32.7809 | 3.8438 | 141 | 38.4775 | 0 | 152.2151 | 0
10081 | 866.2291 | 10.0734 | 16.372 | 98.1659 | 72.4828 | 5.6997 | 71.2664 | 13.6753 | 6.2617 | 28.1119 | 91.0122 | 12.3999 | 215.7732 | 97.8862 | 229.5724 | 11.2208 | 51.6627 | 3.7934 | 129 | 33.8608 | 0 | 296.1701 | 0
10082 | 855.3372 | 8.1995 | 16.3192 | 97.4887 | 72.483 | 5.7 | 75.5934 | 13.6572 | 6.4333 | 26.0689 | 91.2047 | 7.4224 | 194.4039 | 95.4298 | 221.1356 | 11.315 | 51.4551 | 3.2393 | 121 | 34.0109 | 0 | 306.9056 | 0
10083 | 828.6025 | 5.5709 | 16.2286 | 96.6663 | 72.4781 | 5.7 | 75.3705 | 13.9254 | 6.3682 | 25.9913 | 91.4639 | 7.3225 | 195.3265 | 94.2752 | 227.2056 | 11.2378 | 51.7219 | 3.1446 | 118 | 33.9348 | 0 | 303.1852 | 0
10084 | 819.7014 | 3.5071 | 16.4823 | 94.4542 | 73.477 | 4.7503 | 71.3209 | 13.754 | 6.363 | 27.688 | 89.715 | 6.8299 | 188.7143 | 90.2574 | 235.6648 | 11.0209 | 51.946 | 2.8617 | 115 | 33.0989 | 0 | 312.8203 | 0
10085 | 815.4958 | 3.827 | 16.3956 | 94.3413 | 72.4801 | 5.6997 | 73.1904 | 13.5871 | 6.3513 | 29.6001 | 88.838 | 6.5144 | 189.8173 | 87.3362 | 243.3595 | 11.1943 | 53.0113 | 2.7142 | 115 | 33.2013 | 0 | 350.3247 | 0
10086 | 823.8976 | 4.4514 | 21.8985 | 96.8318 | 71.4825 | 6.6497 | 80.1184 | 13.5765 | 6.4618 | 40.3614 | 90.1115 | 10.0516 | 199.7219 | 97.5293 | 235.0564 | 11.2112 | 55.4406 | 2.7386 | 113 | 33.1333 | 0 | 404.9148 | 0
10087 | 867.5426 | 6.0048 | 38.7557 | 101.0919 | 68.4792 | 9.4992 | 87.3355 | 13.4615 | 9.9572 | 62.3232 | 101.1387 | 21.2237 | 238.4251 | 163.5323 | 246.6994 | 13.3544 | 52.5512 | 2.6911 | 189 | 48.2401 | 0 | 444.3695 | 0
10088 | 925.1338 | 6.7374 | 68.2118 | 101.1382 | 65.4776 | 12.3492 | 105.6627 | 14.4639 | 9.3062 | 76.2507 | 142.661 | 30.1386 | 284.8722 | 223.6606 | 344.1557 | 24.2733 | 57.4316 | 5.4991 | 264 | 56.6655 | 0 | 477.3131 | 0
10089 | 1012.8463 | 7.7534 | 91.956 | 113.1219 | 64.4759 | 13.2997 | 124.4009 | 15.5626 | 7.091 | 92.8572 | 173.2277 | 33.8025 | 342.2639 | 278.0479 | 472.3077 | 29.1533 | 68.1984 | 13.4862 | 324 | 58.0182 | 0 | 548.7057 | 0.21252
10090 | 1100.3867 | 7.7468 | 100.1825 | 124.7943 | 63.471 | 14.2497 | 135.5093 | 18.0447 | 11.5682 | 101.1148 | 190.3719 | 35.2749 | 394.6692 | 304.6007 | 534.4633 | 31.2802 | 76.6883 | 17.1029 | 372 | 58.9932 | 0 | 595.298 | 0.2595
10091 | 1150.1749 | 5.7844 | 97.6626 | 133.9133 | 62.4768 | 15.1997 | 144.4461 | 19.4727 | 19.451 | 99.0957 | 201.8526 | 35.8243 | 410.6313 | 331.4231 | 574.8955 | 32.727 | 97.4632 | 17.6204 | 353 | 65.6674 | 0 | 618.9751 | 0.25843
10092 | 1197.9846 | 5.5178 | 101.2234 | 134.8 | 60.4786 | 17.0995 | 144.3772 | 16.0894 | 20.1205 | 96.5618 | 198.8833 | 33.7635 | 420.0577 | 340.5253 | 580.6775 | 31.9261 | 100.8041 | 17.9933 | 331 | 66.6147 | 0 | 634.4957 | 0.26603
10093 | 1163.665 | 10.1826 | 101.983 | 136.654 | 63.48 | 14.2508 | 140.591 | 12.9136 | 11.6462 | 86.0056 | 197.7938 | 35.8002 | 416.9269 | 334.7907 | 546.4134 | 30.8331 | 96.0307 | 18.9173 | 358 | 56.0219 | 0 | 605.1815 | 0.31732
10094 | 1136.6823 | 7.6573 | 101.9056 | 138.3554 | 63.4815 | 14.25 | 147.2846 | 15.8035 | 7.8048 | 87.2974 | 202.8213 | 37.0436 | 420.3992 | 338.4186 | 565.8173 | 30.1568 | 98.2515 | 19.1603 | 295 | 54.5604 | 0 | 629.1183 | 0.31182
10095 | 1160.3694 | 5.503 | 102.7391 | 136.0941 | 65.4776 | 12.3505 | 142.4687 | 11.9281 | 7.6752 | 88.4671 | 208.6047 | 37.9418 | 418.428 | 346.2894 | 579.289 | 30.3329 | 99.0429 | 18.6282 | 276 | 58.0894 | 0 | 629.8628 | 0.28365
10096 | 1121.3925 | 5.0361 | 100.0161 | 132.8927 | 61.4775 | 16.1489 | 139.9808 | 14.1016 | 7.8588 | 89.7016 | 204.4483 | 34.2755 | 463.6719 | 338.0599 | 544.9103 | 30.1035 | 88.4993 | 18.4346 | 275 | 59.2998 | 0 | 577.915 | 0.20783
10097 | 1086.5662 | 4.8712 | 93.6538 | 130.0922 | 69.4721 | 8.5521 | 129.9683 | 14.7331 | 8.0763 | 76.1822 | 195.0532 | 30.4807 | 513.9595 | 311.2158 | 493.6202 | 26.8014 | 78.0812 | 17.5602 | 260 | 58.641 | 0 | 510.5962 | 0.092664
10098 | 1046.7222 | 6.9066 | 81.2472 | 118.7112 | 71.4726 | 6.6505 | 111.2493 | 13.5692 | 7.3832 | 64.5752 | 175.6387 | 29.7801 | 491.0152 | 246.3 | 424.101 | 17.7624 | 73.3591 | 16.5252 | 236 | 58.782 | 0 | 395.4443 | 0
10099 | 972.7732 | 12.7421 | 49.4372 | 107.371 | 70.4694 | 7.5997 | 107.3712 | 13.2635 | 8.026 | 53.2747 | 151.0497 | 27.6274 | 449.6303 | 184.8393 | 364.1903 | 12.2889 | 69.3728 | 13.1446 | 229 | 53.6623 | 0 | 342.6472 | 0
10100 | 938.7208 | 18.03 | 39.3029 | 102.1397 | 70.4727 | 7.6021 | 91.0565 | 13.6289 | 8.1449 | 43.2833 | 133.415 | 19.4146 | 418.6695 | 164.7361 | 319.076 | 10.6722 | 57.08 | 7.3906 | 214 | 48.0736 | 0 | 302.5784 | 0
10101 | 905.0855 | 15.4233 | 31.4189 | 100.266 | 70.4835 | 7.5979 | 83.2924 | 13.6525 | 8.0671 | 40.0917 | 104.622 | 11.3903 | 336.1052 | 135.7721 | 284.2212 | 10.2801 | 50.2739 | 5.1985 | 196 | 46.1388 | 0 | 285.9736 | 0
10102 | 897.2208 | 11.4484 | 24.1792 | 97.8475 | 71.479 | 6.6503 | 78.3323 | 13.6154 | 7.6129 | 36.1765 | 92.6666 | 8.9014 | 249.8374 | 112.9279 | 269.3368 | 10.0361 | 49.7472 | 4.3756 | 187 | 40.4301 | 0 | 290.6785 | 0
10103 | 864.305 | 6.6419 | 20.1418 | 97.0877 | 73.4782 | 4.7505 | 70.5724 | 13.6062 | 7.7939 | 31.2817 | 87.4191 | 8.6401 | 219.9783 | 103.2811 | 259.0092 | 9.9941 | 49.2347 | 3.4032 | 175 | 41.78 | 0 | 291.6272 | 0
10104 | 836.9567 | 3.8982 | 19.1939 | 97.0673 | 72.4809 | 5.6997 | 66.8872 | 13.7232 | 7.4284 | 19.5238 | 55.2692 | 8.3257 | 64.6601 | 65.2514 | 169.187 | 9.8239 | 30.7041 | 3.7227 | 165 | 42.2397 | 0 | 153.2943 | 0
10105 | 829.9178 | 3.0603 | 19.1368 | 98.9493 | 70.4784 | 7.6016 | 71.3605 | 13.6416 | 6.9234 | 30.436 | 79.9563 | 8.1964 | 207.7929 | 98.1506 | 233.2821 | 9.8472 | 48.7186 | 3.66 | 160 | 42.8952 | 0 | 315.8213 | 0
10106 | 828.8861 | 2.9704 | 19.3531 | 101.715 | 72.4785 | 5.6984 | 68.8966 | 13.5771 | 6.8458 | 31.5126 | 79.3691 | 8.1871 | 202.0684 | 96.8441 | 242.8994 | 9.8696 | 49.6251 | 3.4755 | 157 | 45.3362 | 0 | 318.8694 | 0
10107 | 815.6176 | 3.2823 | 19.1899 | 103.9869 | 73.4768 | 4.7503 | 65.1886 | 13.6063 | 6.9532 | 32.3146 | 79.2507 | 8.2402 | 194.8833 | 94.0382 | 250.6627 | 9.9885 | 48.8524 | 3.2266 | 145 | 44.0454 | 0 | 308.7766 | 0
10108 | 812.835 | 3.0037 | 19.1905 | 101.1413 | 72.4818 | 5.6997 | 69.1027 | 13.8705 | 6.947 | 32.457 | 79.2564 | 8.3969 | 193.5282 | 98.5803 | 256.8277 | 9.8907 | 48.3784 | 2.9601 | 136 | 41.4102 | 0 | 304.0805 | 0
10109 | 810.891 | 3.4417 | 19.3747 | 100.15 | 72.4818 | 5.7 | 68.2377 | 13.736 | 6.8655 | 32.3338 | 79.6064 | 8.2814 | 192.2312 | 95.3866 | 230.2213 | 9.7394 | 50.0095 | 2.8729 | 123 | 40.7948 | 0 | 313.4518 | 0
10110 | 809.3405 | 4.407 | 28.229 | 99.839 | 72.4824 | 5.7 | 67.3136 | 13.6831 | 6.9762 | 31.8266 | 80.6458 | 8.198 | 189.4163 | 88.1165 | 214.3216 | 9.8155 | 52.3478 | 2.9003 | 124 | 39.8835 | 0 | 310.3839 | 0
10111 | 813.7951 | 4.5959 | 38.1117 | 98.9749 | 73.4797 | 4.7503 | 69.8565 | 13.6239 | 7.0085 | 29.6925 | 81.0277 | 8.0348 | 189.0425 | 85.8664 | 212.9563 | 9.9008 | 49.6076 | 2.9296 | 120 | 40.5744 | 0 | 317.4171 | 0
10112 | 822.1812 | 3.7616 | 44.4233 | 96.7817 | 71.4823 | 6.6495 | 69.7291 | 13.3095 | 6.7922 | 26.3844 | 87.2132 | 8.1545 | 197.4759 | 82.9386 | 211.5868 | 10.8953 | 47.5444 | 2.9578 | 116 | 47.6053 | 0 | 313.305 | 0
10113 | 829.6107 | 3.1856 | 47.6614 | 96.0583 | 72.4815 | 5.7003 | 74.4757 | 13.4747 | 6.0363 | 34.837 | 103.1298 | 12.6602 | 204.0784 | 84.5113 | 221.0498 | 13.0417 | 47.3701 | 3.4082 | 127 | 48.7126 | 0 | 307.0013 | 0.20431
10114 | 852.0506 | 3.3344 | 51.8229 | 96.275 | 70.4807 | 7.5995 | 81.1499 | 13.2524 | 5.684 | 57.2222 | 118.6034 | 14.6345 | 212.0671 | 91.4152 | 215.7667 | 12.0651 | 48.0914 | 5.4973 | 179 | 44.0924 | 0 | 312.8873 | 0.15141
10115 | 862.8006 | 3.6405 | 64.4997 | 98.3679 | 70.4781 | 7.6 | 86.5079 | 9.3309 | 6.037 | 64.739 | 136.2608 | 14.8164 | 227.8903 | 109.8251 | 233.3466 | 11.5124 | 48.8778 | 11.2327 | 199 | 40.2107 | 0 | 318.2406 | 0.14195
10116 | 873.6109 | 3.9914 | 69.5059 | 97.406 | 71.478 | 6.6503 | 81.5143 | 10.9003 | 6.1613 | 62.9866 | 127.8807 | 14.6929 | 236.9161 | 122.1704 | 264.5215 | 11.0955 | 51.0672 | 13.2746 | 211 | 41.2237 | 0 | 325.174 | 0.081421
10117 | 890.1269 | 4.6175 | 69.2711 | 96.285 | 72.4764 | 5.7003 | 83.9281 | 13.4665 | 6.2503 | 58.6682 | 121.3395 | 14.4961 | 239.5532 | 128.8771 | 267.5681 | 10.7727 | 48.6205 | 13.7186 | 222 | 40.9107 | 0 | 339.9635 | 0.16001
10118 | 878.1143 | 4.0312 | 62.8114 | 96.2798 | 71.4751 | 6.6497 | 93.092 | 7.6205 | 6.1968 | 59.5912 | 122.5573 | 14.7379 | 238.9778 | 130.3753 | 259.814 | 11.3511 | 47.6638 | 14.6972 | 203 | 44.3371 | 0 | 318.7096 | 0.05184
10119 | 868.0993 | 3.8367 | 39.69 | 96.6795 | 72.4771 | 5.7003 | 86.6084 | 10.7183 | 6.0668 | 57.1047 | 126.2379 | 15.4694 | 240.6533 | 134.7946 | 268.9423 | 11.3302 | 47.1215 | 13.1054 | 215 | 50.0801 | 0 | 310.2373 | 0.044693
10120 | 876.6412 | 4.7955 | 32.0196 | 97.5741 | 73.4758 | 4.7503 | 75.0013 | 13.0655 | 5.9153 | 48.8257 | 128.3106 | 15.346 | 257.2684 | 139.7234 | 289.5646 | 11.459 | 49.6832 | 7.97 | 213 | 47.8049 | 0 | 319.0544 | 0.0076062
10121 | 875.6883 | 5.1171 | 23.1674 | 97.2696 | 68.4774 | 9.4987 | 84.934 | 12.9968 | 6.0689 | 35.8084 | 126.8781 | 10.7534 | 302.0904 | 154.649 | 308.2313 | 11.3605 | 52.3576 | 5.8105 | 223 | 47.036 | 0 | 320.8187 | 0.0012807
10122 | 857.6213 | 10.0482 | 18.3745 | 99.3112 | 65.4737 | 12.3492 | 79.6462 | 13.3025 | 9.1338 | 40.2447 | 119.3232 | 10.4715 | 270.2761 | 152.8538 | 303.7576 | 10.2618 | 53.572 | 5.0629 | 227 | 44.2805 | 0 | 307.4535 | 0
10123 | 852.3367 | 17.1763 | 17.7295 | 105.9496 | 70.4718 | 7.6013 | 69.8253 | 13.3796 | 14.9905 | 37.6185 | 96.4795 | 8.256 | 243.3013 | 141.1466 | 293.7176 | 9.9951 | 52.3897 | 4.8374 | 224 | 43.0488 | 0 | 304.5895 | 0
10124 | 843.8747 | 18.1906 | 17.7734 | 111.3832 | 72.4765 | 5.7005 | 71.4785 | 13.385 | 17.1798 | 35.3084 | 87.5872 | 7.0592 | 237.7511 | 121.7093 | 292.3991 | 9.9029 | 50.6725 | 4.9525 | 214 | 43.0631 | 0 | 300.7485 | 0
10125 | 828.4327 | 13.7762 | 17.6891 | 112.3872 | 72.4748 | 5.7 | 74.5683 | 13.6237 | 12.7433 | 34.0573 | 87.5433 | 7.3338 | 226.577 | 109.4317 | 286.0346 | 9.9556 | 50.0307 | 4.9068 | 213 | 44.3425 | 0 | 304.2902 | 0
10126 | 815.0268 | 12.9895 | 17.6126 | 113.051 | 73.4772 | 4.7503 | 69.1043 | 9.6749 | 9.898 | 30.8174 | 88.5557 | 7.2186 | 214.7176 | 107.3477 | 264.6479 | 10.0467 | 49.536 | 4.181 | 212 | 43.7941 | 0 | 301.3058 | 0
10127 | 810.3825 | 12.0927 | 17.4753 | 109.6159 | 72.4798 | 5.6997 | 68.9378 | 10.3889 | 7.6768 | 29.6752 | 87.9961 | 7.0885 | 206.9045 | 109.6406 | 252.308 | 10.1078 | 48.6935 | 3.8491 | 191 | 44.0233 | 0 | 302.2014 | 0
10128 | 799.3106 | 6.1845 | 17.3067 | 102.2599 | 73.4783 | 4.7503 | 77.4146 | 12.8772 | 6.8812 | 19.4629 | 57.4942 | 7.0824 | 60.6827 | 70.851 | 163.8644 | 10.0425 | 30.6261 | 3.1762 | 157 | 42.069 | 0 | 167.3742 | 0
10129 | 816.1924 | 3.1066 | 17.1711 | 99.3014 | 73.4821 | 4.75 | 76.1044 | 8.181 | 6.9073 | 28.1073 | 86.3818 | 7.1125 | 201.0465 | 100.845 | 236.5846 | 9.8952 | 48.6482 | 2.6955 | 150 | 42.4723 | 0 | 331.8982 | 0
10130 | 810.1176 | 3.0286 | 17.2374 | 97.17 | 72.4866 | 5.6997 | 69.5069 | 11.309 | 6.8768 | 27.5233 | 85.8065 | 8.5628 | 196.605 | 95.1501 | 238.0756 | 10.055 | 48.4796 | 2.7495 | 149 | 42.1399 | 0 | 320.7269 | 0
10131 | 801.4759 | 2.7664 | 17.2779 | 97.4935 | 66.4876 | 11.3984 | 74.2614 | 10.907 | 6.9686 | 27.3841 | 85.7014 | 7.6101 | 194.2316 | 86.6107 | 241.7621 | 9.9742 | 48.6076 | 2.6533 | 153 | 43.3373 | 0 | 316.3149 | 0
10132 | 797.4289 | 2.7885 | 17.1524 | 98.6616 | 68.4852 | 9.5005 | 80.2377 | 9.4688 | 7.0335 | 27.4569 | 85.4211 | 9.4035 | 194.3616 | 82.9992 | 232.4176 | 10.0058 | 48.7056 | 2.5546 | 149 | 42.891 | 0 | 309.8707 | 0
10133 | 785.265 | 3.4317 | 17.0844 | 99.7365 | 65.4817 | 12.3492 | 74.722 | 11.6433 | 7.0472 | 27.7181 | 85.4445 | 9.5128 | 191.4534 | 83.0381 | 217.9373 | 10.0047 | 50.3343 | 2.6431 | 147 | 43.7896 | 0 | 295.8082 | 0
10134 | 789.136 | 4.5055 | 17.1595 | 99.4179 | 72.4785 | 5.7034 | 68.4839 | 8.3494 | 6.9712 | 28.4104 | 87.1062 | 7.5682 | 190.6062 | 83.2977 | 211.2971 | 9.6676 | 52.3439 | 2.9228 | 144 | 50.8124 | 0 | 294.9222 | 0
10135 | 800.2016 | 4.5743 | 17.0037 | 99.6717 | 73.4868 | 4.7487 | 76.5582 | 11.6475 | 6.9687 | 28.206 | 88.0636 | 6.898 | 189.9567 | 84.8882 | 209.8453 | 9.8725 | 49.7572 | 3.0501 | 141 | 42.8487 | 0 | 290.3131 | 0
10136 | 798.563 | 4.5402 | 16.6291 | 96.9857 | 72.4822 | 5.6997 | 79.4522 | 7.9996 | 6.0591 | 24.1851 | 86.1678 | 5.9356 | 198.7462 | 82.0631 | 203.451 | 10.0564 | 47.8856 | 3.2689 | 127 | 42.0775 | 0 | 284.4272 | 0
10137 | 805.512 | 3.3248 | 16.7149 | 95.5964 | 72.4806 | 5.7 | 68.5866 | 10.5102 | 5.9085 | 32.698 | 87.9946 | 7.6479 | 205.9948 | 82.5186 | 201.9064 | 11.0853 | 49.1524 | 3.7905 | 144 | 41.0085 | 0 | 281.0631 | 0.0314
10138 | 824.9915 | 2.9071 | 20.3055 | 95.7318 | 72.4804 | 5.7 | 67.8241 | 10.8212 | 5.8638 | 49.9671 | 90.4492 | 7.5392 | 207.3545 | 86.4755 | 205.4067 | 11.0818 | 50.4861 | 4.1591 | 161 | 42.2504 | 0 | 285.8862 | 0.042693
10139 | 845.4681 | 3.0504 | 29.3124 | 96.4006 | 67.4786 | 10.4487 | 85.9156 | 8.4503 | 5.7885 | 58.8923 | 100.5885 | 5.197 | 216.7829 | 97.4786 | 208.5761 | 10.5526 | 51.9479 | 4.6621 | 158 | 43.0803 | 0 | 293.7952 | 0.057918
10140 | 857.8541 | 2.9081 | 32.79 | 97.1323 | 70.4766 | 7.6008 | 95.4629 | 11.2976 | 6.038 | 57.9811 | 110.1977 | 4.3021 | 229.4572 | 107.3335 | 216.5126 | 10.4756 | 53.9444 | 4.8758 | 164 | 43.9044 | 0 | 299.0671 | 0.064763
10141 | 859.3216 | 2.9408 | 32.8348 | 97.4499 | 72.4742 | 5.7005 | 95.0232 | 7.2083 | 6.2188 | 58.3978 | 125.6754 | 4.2493 | 236.1929 | 115.5188 | 224.69 | 10.7751 | 52.731 | 5.546 | 182 | 44.1483 | 0 | 290.052 | 0.038357
10142 | 857.7728 | 3.5766 | 32.4338 | 98.2891 | 72.477 | 5.7 | 97.3569 | 10.4425 | 7.7263 | 56.4608 | 132.2632 | 4.2578 | 238.1428 | 124.5468 | 240.2863 | 10.6171 | 50.6526 | 5.9336 | 170 | 46.706 | 0 | 290.8152 | 0.047138
10143 | 854.317 | 3.5413 | 32.5192 | 100.3147 | 71.4787 | 6.6497 | 98.2237 | 7.5219 | 6.8838 | 53.9999 | 139.8261 | 5.0946 | 237.0406 | 133.0504 | 266.4643 | 10.7636 | 50.643 | 6.0657 | 173 | 53.5845 | 0 | 302.1485 | 0.052676
10144 | 870.1283 | 5.4691 | 32.3634 | 102.9371 | 71.4753 | 6.65 | 86.2001 | 10.237 | 6.1682 | 45.7585 | 157.5263 | 6.7356 | 236.2284 | 116.0786 | 291.3719 | 10.2945 | 51.6318 | 6.4713 | 182 | 51.3099 | 0 | 291.1217 | 0.046088
10145 | 903.4497 | 10.0372 | 23.4664 | 101.028 | 73.4736 | 4.7505 | 83.1525 | 8.4279 | 6.1606 | 30.1909 | 154.5632 | 5.4872 | 263.5714 | 106.3943 | 285.9534 | 10.1787 | 51.4941 | 6.1594 | 169 | 49.506 | 0 | 297.135 | 0.012473
10146 | 907.8665 | 16.8556 | 17.9958 | 99.3889 | 72.4756 | 5.6997 | 87.1424 | 9.8704 | 6.3672 | 26.2551 | 148.4122 | 5.4117 | 349.2744 | 112.6815 | 270.2846 | 10.0495 | 51.2752 | 6.1951 | 164 | 48.9436 | 0 | 281.4422 | 0
10147 | 884.6555 | 23.6258 | 17.3679 | 100.0787 | 73.478 | 4.7503 | 84.344 | 9.8739 | 7.0205 | 30.5356 | 156.2423 | 6.9142 | 377.1045 | 116.3819 | 266.9715 | 9.7687 | 52.2298 | 5.8585 | 145 | 46.9464 | 0 | 279.6182 | 0
10148 | 864.378 | 18.4241 | 17.7194 | 102.4785 | 72.4835 | 5.7013 | 73.8421 | 9.8304 | 7.68 | 32.383 | 139.6726 | 7.7631 | 373.0629 | 109.1065 | 265.847 | 9.6653 | 52.2134 | 5.3426 | 147 | 42.8976 | 0 | 286.7289 | 0
10149 | 838.6373 | 12.6095 | 17.3241 | 101.6954 | 72.4833 | 5.6984 | 66.9744 | 10.4818 | 9.7635 | 35.8969 | 101.595 | 13.3115 | 369.2045 | 102.7095 | 259.2203 | 9.4187 | 51.3941 | 4.7274 | 140 | 42.532 | 0 | 279.8566 | 0
10150 | 822.6755 | 11.2843 | 17.4511 | 100.1768 | 73.4783 | 4.7503 | 75.6096 | 8.908 | 11.1507 | 34.1197 | 87.8842 | 17.2555 | 335.2916 | 99.5452 | 240.6369 | 9.5925 | 51.1137 | 4.4734 | 130 | 40.36 | 0 | 271.3841 | 0
10151 | 805.1593 | 10.758 | 17.4643 | 99.9617 | 72.4807 | 5.6997 | 81.1977 | 11.4142 | 8.0603 | 32.4753 | 86.5469 | 10.7902 | 244.0809 | 94.3437 | 238.4824 | 9.6633 | 51.9709 | 4.4738 | 124 | 39.6394 | 0 | 259.9472 | 0
10152 | 781.1252 | 10.0751 | 17.1322 | 100.0258 | 72.4825 | 5.7 | 72.4441 | 8.1534 | 6.5322 | 20.4365 | 56.3812 | 7.3965 | 62.0693 | 59.2524 | 162.6273 | 9.8093 | 32.6239 | 4.5559 | 123 | 38.5112 | 0 | 134.151 | 0
10153 | 780.2775 | 6.3045 | 17.0767 | 100.2749 | 73.4832 | 4.7503 | 72.4991 | 11.3056 | 6.7008 | 29.8936 | 84.8247 | 6.9982 | 201.8814 | 88.4621 | 228.1798 | 9.742 | 51.3098 | 4.2273 | 125 | 34.3962 | 0 | 262.0557 | 0
10154 | 778.5502 | 3.2809 | 17.1306 | 99.7264 | 71.4863 | 6.6495 | 77.8612 | 8.1392 | 6.8788 | 28.8458 | 84.3112 | 7.7073 | 199.3215 | 85.2226 | 219.7791 | 9.6334 | 51.01 | 3.8492 | 120 | 33.4505 | 0 | 263.0139 | 0
10155 | 762.7042 | 2.6932 | 17.1784 | 99.8816 | 71.482 | 6.65 | 79.8956 | 11.1558 | 6.7654 | 28.3428 | 83.6442 | 7.9094 | 197.1985 | 86.5919 | 220.0477 | 9.7167 | 50.6231 | 3.7453 | 117 | 33.7431 | 0 | 268.786 | 0
10156 | 767.3152 | 2.9439 | 17.7885 | 99.6975 | 73.4807 | 4.7505 | 79.4263 | 8.1362 | 6.6609 | 28.5567 | 83.4267 | 7.0427 | 195.9745 | 90.9592 | 219.1268 | 9.9074 | 50.8817 | 3.6868 | 113 | 34.4777 | 0 | 271.8161 | 0
10157 | 759.4132 | 3.2502 | 19.2274 | 100.8501 | 72.4829 | 5.6997 | 70.9939 | 10.867 | 6.5757 | 28.9946 | 83.8227 | 6.6916 | 196.6459 | 86.3117 | 213.9921 | 9.8697 | 52.7125 | 2.9637 | 113 | 33.9144 | 0 | 330.3779 | 0
10158 | 776.8812 | 4.0752 | 24.1255 | 100.8179 | 72.484 | 5.7 | 80.8982 | 8.3589 | 7.4602 | 41.4587 | 86.6705 | 9.6053 | 203.0225 | 91.5198 | 219.3885 | 9.9309 | 54.1859 | 2.7805 | 118 | 36.7343 | 0 | 348.2455 | 0
10159 | 829.2533 | 5.6638 | 45.355 | 104.3255 | 69.479 | 8.5492 | 99.7688 | 10.4527 | 6.9672 | 61.0952 | 106.635 | 21.3159 | 241.8811 | 174.0721 | 239.4052 | 12.3492 | 51.7701 | 3.7355 | 177 | 45.254 | 0 | 381.015 | 0
10160 | 884.9962 | 12.5347 | 69.0666 | 110.9349 | 66.7254 | 11.3992 | 122.9257 | 10.761 | 10.2707 | 70.6765 | 142.4503 | 32.1571 | 297.2401 | 242.7259 | 321.8329 | 25.9992 | 55.3543 | 9.2758 | 293 | 54.4257 | 0 | 442.4484 | 0
10161 | 967.5106 | 19.6501 | 91.5497 | 123.31 | 64.6135 | 13.2995 | 146.0102 | 12.1573 | 17.945 | 71.3777 | 171.7878 | 39.671 | 348.28 | 300.7274 | 424.8501 | 35.0496 | 65.8114 | 14.1869 | 304 | 67.3818 | 0 | 516.1467 | 0.018126
10162 | 1074.5333 | 20.992 | 99.1954 | 136.0077 | 61.4811 | 16.1492 | 160.5575 | 12.394 | 21.4922 | 77.7961 | 183.5401 | 42.1864 | 385.2254 | 339.7804 | 525.3172 | 41.6906 | 76.6053 | 17.7501 | 360 | 73.29 | 0 | 542.5669 | 0.064378
10163 | 1130.6498 | 19.5958 | 100.5985 | 145.2637 | 63.4836 | 14.2505 | 169.2279 | 13.9299 | 21.4757 | 78.6047 | 185.4822 | 42.6644 | 404.1143 | 354.4799 | 592.859 | 42.7103 | 88.6098 | 17.4 | 343 | 78.675 | 0 | 579.1466 | 0.046967
10164 | 1163.1553 | 17.5106 | 104.0679 | 153.4689 | 62.4839 | 15.1997 | 172.8696 | 12.3007 | 19.3292 | 83.3203 | 187.4582 | 42.2499 | 414.3049 | 366.2628 | 613.3465 | 40.9345 | 87.5079 | 17.4603 | 320 | 88.3968 | 0 | 657.4857 | 0.041081
10165 | 1180.2758 | 17.3671 | 102.0244 | 150.894 | 62.4784 | 15.2 | 168.0412 | 16.5797 | 16.9303 | 87.7189 | 193.231 | 42.313 | 410.8177 | 369.2333 | 602.8326 | 42.1644 | 83.1904 | 18.8364 | 340 | 82.297 | 0 | 648.6842 | 0.031368
10166 | 1186.2746 | 11.4225 | 100.5657 | 153.0631 | 61.4783 | 16.1497 | 169.3612 | 12.075 | 21.622 | 94.6528 | 201.0978 | 45.2702 | 420.8416 | 372.7413 | 607.655 | 42.7885 | 81.9126 | 19.4077 | 293 | 80.8108 | 0 | 662.6452 | 0.013949
10167 | 1212.1305 | 7.2656 | 100.7778 | 151.9271 | 60.4793 | 17.0997 | 172.8356 | 14.5197 | 21.5227 | 95.6251 | 208.944 | 43.8652 | 437.5832 | 371.8727 | 610.8046 | 42.8316 | 85.0768 | 20.0334 | 275 | 80.1343 | 0 | 623.7769 | 0.0098639
10168 | 1200.3584 | 8.6062 | 99.3821 | 151.2623 | 60.4786 | 17.1 | 173.3132 | 13.1729 | 19.0948 | 96.0802 | 207.2818 | 40.8326 | 446.6305 | 365.333 | 580.0269 | 42.8907 | 84.7016 | 20.3368 | 275 | 75.9004 | 0 | 629.0227 | 0.0053652
10169 | 1159.264 | 7.6832 | 95.4719 | 145.4363 | 66.4761 | 11.4016 | 159.1893 | 13.055 | 13.9206 | 87.515 | 202.4432 | 38.8657 | 421.4749 | 343.4223 | 518.0653 | 33.4834 | 84.024 | 19.4688 | 263 | 72.5742 | 0 | 588.7384 | 0.0013792
10170 | 1082.8624 | 6.5786 | 92.4767 | 129.4003 | 71.4814 | 6.6513 | 139.8701 | 13.297 | 8.4619 | 71.9835 | 190.5911 | 36.5328 | 399.6658 | 279.9301 | 435.3277 | 17.8967 | 76.0412 | 17.3559 | 247 | 59.7359 | 0 | 430.8322 | 0
10171 | 1042.5488 | 6.0751 | 85.4432 | 117.2891 | 70.4872 | 7.5997 | 120.6187 | 8.6578 | 7.3286 | 58.7924 | 163.8384 | 27.0793 | 327.1941 | 198.1283 | 384.1475 | 12.5143 | 67.7914 | 14.2895 | 244 | 55.8489 | 0 | 389.8294 | 0
10172 | 989.5608 | 6.1397 | 72.6415 | 115.3447 | 71.484 | 6.6503 | 107.9525 | 10.7472 | 7.0055 | 54.9902 | 148.1647 | 16.644 | 311.7889 | 166.3409 | 341.6499 | 10.9439 | 59.9238 | 8.2258 | 211 | 49.2017 | 0 | 332.4469 | 0
10173 | 961.5023 | 5.6484 | 38.767 | 110.1982 | 72.4858 | 5.7003 | 108.3179 | 6.7123 | 6.3012 | 49.0391 | 137.3421 | 13.2003 | 274.5522 | 140.8752 | 306.4522 | 10.4271 | 54.0294 | 5.2453 | 191 | 43.7609 | 0 | 314.2761 | 0
10174 | 930.2193 | 4.9746 | 24.5942 | 106.2517 | 70.4854 | 7.5995 | 98.4635 | 9.3911 | 6.0777 | 40.9756 | 118.648 | 12.7401 | 240.2773 | 115.1679 | 266.3586 | 9.9657 | 51.5936 | 4.2855 | 185 | 37.805 | 0 | 304.1967 | 0
10175 | 918.1651 | 4.1913 | 21.9635 | 104.3441 | 72.4837 | 5.7005 | 85.5763 | 7.6033 | 5.9779 | 41.5619 | 97.0563 | 12.6391 | 221.0955 | 106.5447 | 246.3699 | 10.1162 | 51.5876 | 3.9552 | 165 | 35.9818 | 0 | 306.4983 | 0
10176 | 894.7453 | 3.0684 | 18.3576 | 102.8655 | 72.49 | 5.7 | 81.578 | 8.4072 | 5.9193 | 24.3106 | 59.0907 | 12.7461 | 63.4407 | 63.276 | 159.3161 | 10.2662 | 32.3946 | 3.4111 | 147 | 34.9068 | 0 | 149.6665 | 0
10177 | 884.6748 | 2.9821 | 17.0832 | 102.4485 | 72.4877 | 5.7 | 80.5 | 8.6924 | 5.7528 | 30.5547 | 88.4975 | 12.7725 | 205.8739 | 87.1892 | 218.062 | 10.1642 | 50.7328 | 2.9006 | 137 | 32.4274 | 0 | 288.4915 | 0
10178 | 879.9154 | 2.6563 | 17.155 | 101.542 | 72.4846 | 5.7 | 79.9915 | 7.2851 | 5.8032 | 28.7076 | 91.7695 | 12.7669 | 210.5559 | 84.7367 | 218.2731 | 10.2079 | 50.5046 | 2.7329 | 115 | 32.4128 | 0 | 293.377 | 0
10179 | 854.1809 | 2.4525 | 16.9711 | 101.6307 | 72.4905 | 5.7 | 78.815 | 9.6055 | 5.8858 | 28.6118 | 94.4973 | 12.7474 | 205.2509 | 85.1054 | 226.5482 | 9.8888 | 50.5862 | 2.7149 | 117 | 32.6205 | 0 | 294.906 | 0
10180 | 839.721 | 2.8784 | 16.9934 | 101.8108 | 72.4912 | 5.7 | 78.7554 | 6.7687 | 5.7567 | 28.4651 | 94.8967 | 12.6803 | 197.8271 | 86.6179 | 228.8401 | 10.1194 | 50.4803 | 2.7174 | 114 | 34.2414 | 0 | 297.1942 | 0
10181 | 828.0754 | 3.4801 | 16.9788 | 103.7889 | 72.4885 | 5.7 | 79.0029 | 10.6425 | 5.6713 | 28.7248 | 92.8982 | 12.6413 | 200.7613 | 86.7045 | 222.8542 | 10.0802 | 51.9127 | 2.7366 | 110 | 35.1953 | 0 | 320.95 | 0
10182 | 831.3982 | 4.0578 | 23.4214 | 105.1665 | 71.4858 | 6.6497 | 85.4766 | 7.1488 | 5.9682 | 40.9408 | 90.4328 | 16.6088 | 208.5926 | 92.5479 | 223.8974 | 10.6887 | 53.9996 | 2.7452 | 111 | 34.3752 | 0 | 369.5675 | 0
10183 | 872.2097 | 7.9766 | 35.7497 | 109.3109 | 68.484 | 9.4992 | 98.8323 | 10.5757 | 11.8233 | 59.106 | 102.2108 | 22.0147 | 241.0693 | 153.9663 | 241.5848 | 13.7258 | 51.0311 | 2.7948 | 199 | 47.9445 | 0 | 424.1586 | 0
10184 | 938.2853 | 15.9622 | 64.3479 | 110.3925 | 64.4757 | 13.3026 | 109.9695 | 8.0402 | 16.5983 | 72.0281 | 144.5589 | 29.594 | 295.1945 | 229.7922 | 335.9695 | 28.2207 | 53.3185 | 5.6652 | 270 | 59.4019 | 0 | 462.8658 | 0.02119
10185 | 1047.1978 | 22.1065 | 87.94 | 123.2337 | 63.48 | 14.246 | 128.4506 | 13.3413 | 18.1203 | 69.682 | 174.7875 | 33.4267 | 357.8947 | 287.5523 | 487.8025 | 36.564 | 65.3114 | 13.3988 | 302 | 66.5573 | 0 | 538.8154 | 0.0539
10186 | 1160.8656 | 16.9218 | 99.3549 | 133.3276 | 63.4761 | 14.25 | 151.3225 | 11.1829 | 20.2153 | 75.943 | 187.9201 | 34.4734 | 402.9763 | 324.4416 | 600.4114 | 41.4864 | 79.8675 | 17.1109 | 319 | 75.0537 | 0 | 610.5962 | 0.078159
10187 | 1214.3206 | 7.9712 | 99.7633 | 136.2163 | 61.4746 | 16.1495 | 157.6286 | 13.3074 | 23.2702 | 81.2091 | 198.5978 | 37.7695 | 424.2394 | 342.3256 | 610.5162 | 42.0774 | 86.2629 | 18.4142 | 325 | 70.5876 | 0 | 619.8468 | 0.10296
10188 | 1208.9449 | 6.1531 | 102.0684 | 139.1507 | 59.4779 | 18.0495 | 147.968 | 10.6884 | 22.608 | 84.3502 | 202.7785 | 40.3515 | 444.4745 | 362.5315 | 595.0838 | 42.3388 | 87.0619 | 18.432 | 330 | 81.7718 | 0 | 644.2361 | 0.092631
10189 | 1181.0274 | 5.3511 | 103.1988 | 143.4688 | 62.476 | 15.2008 | 153.8013 | 12.5837 | 19.7253 | 84.1047 | 203.6419 | 41.1622 | 430.4767 | 359.4467 | 595.4632 | 42.5357 | 82.3701 | 18.4454 | 333 | 73.0263 | 0 | 655.0001 | 0.077271
10190 | 1175.4792 | 4.257 | 103.6623 | 146.9118 | 63.4809 | 14.2503 | 163.3135 | 10.529 | 16.9562 | 93.38 | 205.7739 | 41.9852 | 425.5881 | 374.1197 | 600.5569 | 43.1075 | 80.9548 | 19.2538 | 279 | 77.3264 | 0 | 654.1155 | 0.089426
10191 | 1175.6488 | 8.6175 | 102.678 | 145.0542 | 60.4856 | 17.0992 | 169.0026 | 11.6513 | 16.875 | 98.383 | 213.7449 | 42.3406 | 432.6311 | 374.1089 | 600.7611 | 41.1608 | 82.945 | 19.3941 | 288 | 81.463 | 0 | 639.0404 | 0.066103
10192 | 1142.9897 | 11.6207 | 100.2977 | 139.5837 | 59.484 | 18.0497 | 162.0908 | 11.7398 | 15.4315 | 89.986 | 221.4158 | 42.259 | 424.3414 | 367.592 | 567.9345 | 39.6979 | 83.1229 | 18.9972 | 268 | 72.31 | 0 | 603.3164 | 0.031345
10193 | 1107.5459 | 11.5266 | 92.8668 | 131.5516 | 68.4772 | 9.5024 | 149.3907 | 11.2871 | 14.1989 | 82.1716 | 221.005 | 40.3158 | 404.8381 | 338.5698 | 500.7118 | 32.8855 | 81.1177 | 18.1725 | 247 | 62.6181 | 0 | 579.0246 | 0.019863
10194 | 1053.8293 | 8.3181 | 85.6318 | 116.8532 | 70.4813 | 7.6005 | 134.8472 | 10.6423 | 14.2874 | 74.1402 | 192.6462 | 37.7601 | 363.9944 | 282.7679 | 413.19 | 18.1494 | 74.9012 | 16.2743 | 209 | 58.2272 | 0 | 433.2972 | 0
10195 | 987.6859 | 5.9938 | 82.1427 | 105.5368 | 72.4864 | 5.7005 | 116.8128 | 12.3997 | 12.9008 | 69.4638 | 156.9879 | 30.9955 | 322.842 | 202.6485 | 360.3003 | 12.4812 | 69.0481 | 13.7012 | 203 | 55.9517 | 0 | 406.1483 | 0
10196 | 933.3564 | 5.8305 | 68.0749 | 100.9084 | 72.4887 | 5.7016 | 94.3178 | 8.212 | 8.6522 | 60.9261 | 143.2002 | 15.6262 | 295.091 | 160.5277 | 336.2714 | 11.5364 | 58.1137 | 9.0307 | 182 | 50.4718 | 0 | 362.8114 | 0
10197 | 911.3271 | 6.2812 | 34.1622 | 98.2289 | 72.4948 | 5.6984 | 84.6344 | 11.5403 | 6.6223 | 53.6206 | 132.7885 | 10.4756 | 264.9841 | 142.4907 | 313.6982 | 10.7135 | 53.0493 | 6.6412 | 176 | 48.297 | 0 | 314.1368 | 0
10198 | 890.7393 | 5.2759 | 23.5144 | 97.3036 | 73.4851 | 4.7503 | 72.545 | 8.4772 | 6.2252 | 44.7612 | 115.1809 | 10.2819 | 229.9519 | 127.8014 | 273.946 | 10.4121 | 51.6315 | 5.5735 | 160 | 44.185 | 0 | 279.6126 | 0
10199 | 861.1584 | 4.2755 | 23.0586 | 96.7358 | 73.481 | 4.75 | 67 | 10.7643 | 6.0023 | 38.7809 | 93.5878 | 9.4359 | 205.3531 | 117.6142 | 256.5343 | 10.0505 | 50.6759 | 4.9384 | 142 | 39.5785 | 0 | 272.347 | 0
10200 | 838.3476 | 3.479 | 22.9105 | 95.8758 | 72.4875 | 5.6997 | 77.6378 | 12.2159 | 6.0188 | 24.159 | 57.7375 | 9.0131 | 59.1774 | 68.1066 | 177.337 | 10.2512 | 31.6892 | 4.3494 | 125 | 38.5333 | 0 | 141.2509 | 0
10201 | 836.8396 | 2.954 | 22.1016 | 94.9549 | 57.8871 | 7.5995 | 80.4221 | 8.6134 | 6.2363 | 34.1346 | 91.187 | 9.0731 | 197.0582 | 112.6824 | 258.8543 | 10.5318 | 50.2806 | 4.0559 | 121 | 41.4878 | 0 | 272.6177 | 0
10202 | 833.3884 | 3.2177 | 18.3614 | 95.3005 | 60.8852 | 4.7508 | 71.1034 | 11.602 | 6.4462 | 32.6944 | 91.3398 | 9.1659 | 195.5327 | 106.2268 | 257.6539 | 10.4397 | 50.2665 | 4.1778 | 116 | 41.2369 | 0 | 277.0886 | 0
10203 | 822.7502 | 2.8268 | 16.8943 | 94.4316 | 59.8831 | 5.6997 | 70.6528 | 8.6292 | 6.4068 | 32.43 | 90.4772 | 9.0558 | 191.0821 | 104.4248 | 260.3691 | 10.4725 | 50.164 | 3.8377 | 111 | 41.2311 | 0 | 276.4783 | 0
10204 | 812.6836 | 2.5827 | 16.9716 | 94.46 | 60.8776 | 4.7503 | 78.4117 | 10.7361 | 6.3198 | 32.1442 | 90.0862 | 8.9249 | 189.2659 | 104.7475 | 254.8768 | 10.1537 | 50.302 | 3.0314 | 111 | 39.1075 | 0 | 282.4699 | 0
10205 | 811.4351 | 3.2559 | 16.776 | 94.069 | 59.884 | 5.6997 | 74.168 | 13.3249 | 6.171 | 32.3156 | 89.8143 | 8.908 | 192.9863 | 106.4964 | 242.825 | 10.2398 | 51.5601 | 2.7508 | 104 | 40.0798 | 0 | 304.8871 | 0
10206 | 818.4288 | 4.0984 | 22.7916 | 94.8586 | 60.8836 | 4.7503 | 72.9963 | 7.8971 | 6.4568 | 41.1285 | 89.5211 | 10.0502 | 200.4796 | 114.4762 | 237.525 | 10.3546 | 53.6636 | 3.5611 | 109 | 39.4927 | 0 | 366.1874 | 0
10207 | 863.6643 | 5.4873 | 37.4126 | 100.4316 | 53.8828 | 11.3982 | 94.2241 | 10.8967 | 7.4357 | 60.7098 | 99.1133 | 18.2362 | 234.3947 | 168.0479 | 254.7906 | 13.0514 | 50.8721 | 7.0172 | 176 | 50.1044 | 0 | 430.1365 | 0
10208 | 929.8369 | 10.6439 | 67.5113 | 102.7375 | 46.8851 | 18.0482 | 119.5258 | 9.9722 | 9.8197 | 72.0416 | 139.5721 | 29.9096 | 288.7456 | 238.1123 | 348.7562 | 27.053 | 53.3533 | 9.0997 | 283 | 66.9208 | 0 | 489.1903 | 0.010336
10209 | 1016.4223 | 10.5037 | 85.9797 | 117.2322 | 43.8813 | 20.8992 | 132.8591 | 11.0857 | 13.984 | 74.629 | 174.9678 | 37.4197 | 343.4324 | 305.1891 | 488.1495 | 36.9557 | 62.2531 | 13.755 | 316 | 81.5821 | 0 | 567.7189 | 0.03776
10210 | 1099.3245 | 11.9142 | 97.2366 | 131.3342 | 41.8743 | 22.7995 | 150.4883 | 11.9837 | 15.7973 | 87.9705 | 195.1802 | 39.0829 | 393.4928 | 354.1973 | 579.6697 | 42.0509 | 74.5086 | 16.2702 | 331 | 83.1703 | 0 | 605.0558 | 0.04866
10211 | 1148.563 | 16.2637 | 100.5813 | 136.6918 | 44.8751 | 19.9508 | 165.3366 | 12.5349 | 16.9018 | 103.1038 | 200.4346 | 42.3725 | 409.7471 | 376.8595 | 624.6975 | 44.2516 | 81.7066 | 17.8725 | 338 | 84.0666 | 0 | 598.9042 | 0.057841
10212 | 1171.4946 | 18.54 | 104.766 | 140.1774 | 42.8848 | 21.8495 | 167.9261 | 11.5473 | 16.9173 | 105.209 | 199.5267 | 40.9387 | 432.0772 | 391.9884 | 628.3479 | 43.7601 | 83.8412 | 18.6808 | 305 | 90.2117 | 0 | 594.8359 | 0.057077
10213 | 1145.7116 | 16.6021 | 101.9413 | 138.8717 | 42.8846 | 21.85 | 158.8041 | 13.5815 | 11.4952 | 97.5364 | 198.5922 | 41.7188 | 440.9766 | 391.6298 | 599.3701 | 43.3343 | 82.7225 | 18.7453 | 350 | 83.9947 | 0 | 611.4186 | 0.077293
10214 | 1145.5946 | 17.9108 | 102.8143 | 144.7644 | 37.8846 | 26.5987 | 162.2035 | 12.3904 | 15.8313 | 105.1954 | 202.9206 | 44.8091 | 447.1794 | 387.8235 | 595.4015 | 43.9465 | 83.5853 | 18.9766 | 294 | 83.3969 | 0 | 632.1781 | 0.061145
10215 | 1185.7731 | 18.3963 | 105.8554 | 145.7287 | 40.8747 | 23.7508 | 166.1123 | 16.002 | 17.844 | 109.3078 | 210.0361 | 43.3248 | 461.1582 | 378.9152 | 604.8062 | 42.9882 | 86.5311 | 19.768 | 288 | 86.979 | 0 | 640.5487 | 0.042025
10216 | 1186.5813 | 14.4371 | 104.8619 | 146.4274 | 49.8762 | 15.2024 | 155.5398 | 13.0517 | 10.9359 | 107.3992 | 212.9405 | 40.5712 | 451.4154 | 371.1787 | 614.0879 | 38.4596 | 88.5498 | 19.9708 | 297 | 80.0986 | 0 | 610.4887 | 0.018619
10217 | 1137.6232 | 12.8752 | 90.8839 | 134.667 | 56.8806 | 8.5518 | 149.8622 | 14.7556 | 6.9938 | 99.7979 | 204.8277 | 38.7685 | 424.8741 | 346.1543 | 563.6138 | 33.4219 | 86.7186 | 18.8002 | 257 | 73.4986 | 0 | 562.389 | 0.011285
10218 | 1070.0793 | 13.5623 | 76.729 | 118.8811 | 57.8776 | 7.6024 | 137.9071 | 9.7528 | 11.3091 | 86.3495 | 187.9013 | 38.5625 | 379.0084 | 275.6564 | 466.6274 | 19.641 | 77.1252 | 17.5485 | 239 | 66.9669 | 0 | 405.8687 | 0
10219 | 989.7704 | 13.3578 | 70.8682 | 106.5388 | 55.8833 | 9.4974 | 123.5487 | 11.5405 | 16.854 | 72.2287 | 161.4802 | 33.842 | 330.1766 | 185.1592 | 388.2013 | 12.5367 | 66.1413 | 14.6171 | 204 | 62.9307 | 0 | 371.8924 | 0
10220 | 935.2467 | 10.5941 | 66.4935 | 101.9415 | 57.8794 | 7.6005 | 104.0373 | 9.1156 | 14.5416 | 63.1594 | 146.0846 | 24.6749 | 297.7625 | 141.9003 | 335.2051 | 10.929 | 55.5228 | 8.7354 | 189 | 56.5888 | 0 | 329.5324 | 0
10221 | 896.6156 | 6.3382 | 35.2729 | 99.2512 | 58.8837 | 6.6503 | 98.9265 | 11.9072 | 8.612 | 59.882 | 134.6343 | 15.7218 | 272.4065 | 127.8551 | 296.9294 | 10.4245 | 51.6915 | 5.9502 | 177 | 50.9982 | 0 | 312.6117 | 0
10222 | 878.0385 | 4.6815 | 24.0153 | 98.0649 | 58.8852 | 6.65 | 86.5753 | 11.0361 | 6.851 | 53.0985 | 119.9658 | 13.2825 | 253.0858 | 119.4286 | 282.6724 | 10.1999 | 50.9894 | 5.0234 | 178 | 45.5457 | 0 | 286.856 | 0
10223 | 856.4478 | 4.0956 | 23.6764 | 97.2154 | 58.8858 | 6.65 | 81.5764 | 11.0864 | 7.4804 | 40.6354 | 99.2226 | 13.1653 | 242.9363 | 110.2761 | 273.5361 | 10.0456 | 50.612 | 3.786 | 154 | 42.5496 | 0 | 284.9116 | 0
10224 | 827.1877 | 3.0634 | 23.5956 | 96.5427 | 58.882 | 6.65 | 83.6413 | 13.7383 | 7.009 | 23.4278 | 60.0716 | 13.2205 | 70.4314 | 61.7814 | 175.3074 | 9.6216 | 31.7158 | 3.0702 | 134 | 41.6583 | 0 | 143.6818 | 0
10225 | 828.9975 | 2.6889 | 23.5878 | 97.0725 | 53.5775 | 5.7003 | 73.7211 | 9.2618 | 6.763 | 32.9594 | 90.6971 | 13.3346 | 223.7122 | 99.4482 | 235.562 | 9.7476 | 50.291 | 2.811 | 122 | 40.7171 | 0 | 291.0771 | 0
10226 | 826.6551 | 2.5473 | 23.5718 | 97.2358 | 53.581 | 5.7 | 69.9039 | 11.2282 | 6.2998 | 31.3943 | 90.0095 | 13.0908 | 218.1475 | 96.213 | 230.8686 | 9.8618 | 50.2699 | 2.756 | 122 | 43.0862 | 0 | 293.1534 | 0
10227 | 819.1799 | 2.4715 | 23.6446 | 97.1168 | 53.5801 | 5.7 | 79.0983 | 13.4941 | 6.2462 | 31.3791 | 89.3291 | 13.2896 | 213.3824 | 91.7439 | 234.9605 | 9.9012 | 50.3036 | 2.8132 | 118 | 41.4464 | 0 | 299.365 | 0
10228 | 811.5834 | 2.4654 | 23.7388 | 95.7237 | 50.5806 | 8.5492 | 76.5148 | 8.3898 | 6.0707 | 31.661 | 88.9781 | 13.047 | 211.335 | 90.6197 | 231.2647 | 9.7653 | 50.3554 | 3.0001 | 116 | 40.0156 | 0 | 298.3502 | 0
10229 | 808.6793 | 3.0543 | 23.5426 | 93.9523 | 53.5792 | 5.7008 | 69.5319 | 11.252 | 5.8653 | 31.1748 | 89.1111 | 12.8473 | 215.5373 | 90.0607 | 225.8524 | 9.561 | 51.69 | 2.8661 | 115 | 38.7865 | 0 | 322.5488 | 0
10230 | 826.1311 | 3.9072 | 33.0454 | 94.6481 | 52.5823 | 6.6497 | 80.4599 | 11.4365 | 5.8917 | 39.6182 | 90.9796 | 14.244 | 227.4834 | 99.1755 | 230.5187 | 9.703 | 53.7425 | 2.8514 | 115 | 38.564 | 0 | 382.8692 | 0
10231 | 858.9379 | 5.7289 | 54.4252 | 101.2903 | 46.5751 | 12.3484 | 100.871 | 9.3151 | 10.8906 | 60.7703 | 103.6376 | 19.2417 | 254.3208 | 167.3673 | 249.2132 | 12.3579 | 51.2756 | 4.2545 | 172 | 53.4107 | 0 | 420.0637 | 0
10232 | 909.4745 | 7.1188 | 77.7305 | 103.0953 | 41.5723 | 17.0987 | 110.9809 | 12.7574 | 10.2066 | 82.7405 | 147.2777 | 30.1027 | 300.7729 | 239.2717 | 328.3453 | 27.865 | 53.9918 | 7.2804 | 263 | 63.6734 | 0 | 449.9213 | 0.028145
10233 | 1001.921 | 10.7802 | 93.0009 | 118.733 | 37.5703 | 20.8989 | 126.7221 | 13.8073 | 8.4182 | 87.7305 | 173.7897 | 35.9158 | 364.8005 | 295.7801 | 477.7232 | 36.6909 | 64.4368 | 15.2168 | 296 | 73.1327 | 0 | 526.68 | 0.028233
10234 | 1090.5301 | 13.9685 | 98.8522 | 133.7028 | 38.5737 | 19.9503 | 154.0973 | 12.5724 | 12.2522 | 87.1425 | 191.8114 | 38.4471 | 416.5846 | 340.103 | 583.4896 | 41.9472 | 76.0507 | 17.3761 | 384 | 80.255 | 0 | 556.5477 | 0.035991
10235 | 1163.6593 | 14.5464 | 98.2018 | 141.4791 | 34.5763 | 23.7489 | 158.5955 | 12.9476 | 21.2158 | 83.6718 | 200.77 | 39.2819 | 438.0773 | 356.1683 | 618.9564 | 43.802 | 102.9589 | 17.3736 | 344 | 79.563 | 0 | 592.4514 | 0.044522
10236 | 1225.1487 | 10.1557 | 103.4734 | 138.5933 | 37.5746 | 20.9008 | 152.4099 | 12.7559 | 22.2352 | 100.1463 | 204.2013 | 36.0492 | 450.2938 | 369.2165 | 620.0028 | 44.0593 | 112.9235 | 17.8397 | 320 | 84.1642 | 0 | 601.7796 | 0.075367
10237 | 1222.0468 | 6.3771 | 104.0439 | 138.5165 | 37.5788 | 20.9 | 158.7298 | 12.0596 | 17.2903 | 98.8486 | 208.5187 | 38.5959 | 437.6515 | 362.8462 | 617.2344 | 45.2872 | 106.4426 | 18.3951 | 367 | 77.203 | 0 | 615.22 | 0.081998
10238 | 1225.9419 | 5.1653 | 105.1448 | 142.3895 | 37.5762 | 20.9 | 159.2365 | 13.5345 | 17.7728 | 94.2966 | 211.5828 | 40.6402 | 443.7047 | 360.9977 | 593.9377 | 45.5975 | 104.6991 | 18.6782 | 377 | 72.3118 | 0 | 620.5533 | 0.098945
10239 | 1215.9507 | 5.4075 | 104.8393 | 145.1906 | 37.5755 | 20.9 | 158.4594 | 11.1191 | 18.534 | 91.892 | 218.42 | 40.0116 | 440.661 | 361.7644 | 588.1466 | 45.1668 | 111.0122 | 18.6282 | 327 | 80.9631 | 0 | 576.2926 | 0.12328
10240 | 1190.7952 | 8.3519 | 101.7167 | 146.391 | 40.5786 | 18.0508 | 159.0612 | 14.4228 | 14.372 | 82.7372 | 230.0379 | 39.6252 | 425.4904 | 357.8476 | 572.8492 | 42.7222 | 112.7309 | 18.8161 | 283 | 80.0692 | 0 | 576.7399 | 0.068447
10241 | 1137.7545 | 7.3711 | 91.12 | 135.5504 | 44.5782 | 14.2511 | 143.0406 | 10.8864 | 11.8513 | 83.9392 | 220.1521 | 38.0633 | 401.6223 | 330.0521 | 516.028 | 34.3758 | 113.8423 | 18.3031 | 279 | 73.5146 | 0 | 519.7765 | 0.023965
10242 | 1046.7459 | 9.1283 | 77.2692 | 117.6515 | 53.576 | 5.7024 | 126.809 | 13.1684 | 11.8368 | 77.0833 | 202.5616 | 36.9514 | 373.4647 | 258.4143 | 446.9517 | 18.9522 | 110.9945 | 16.6686 | 239 | 67.7837 | 0 | 376.6715 | 0
10243 | 1009.6684 | 7.6226 | 72.6844 | 106.8387 | 53.5803 | 5.7 | 120.9513 | 11.7796 | 12.4072 | 64.6721 | 166.8219 | 32.2441 | 342.0177 | 183.0118 | 375.9252 | 12.8241 | 107.5431 | 13.8996 | 215 | 63.5055 | 0 | 333.6399 | 0
10244 | 969.4632 | 6.2632 | 63.6834 | 101.2235 | 53.5832 | 5.7 | 99.6306 | 11.1178 | 9.1328 | 60.586 | 143.2524 | 17.5949 | 303.6703 | 144.2011 | 320.0597 | 11.0023 | 95.585 | 8.1526 | 189 | 59.719 | 0 | 291.6665 | 0
10245 | 926.2429 | 5.4714 | 34.1657 | 97.2983 | 53.5815 | 5.7 | 84.8251 | 10.9099 | 11.0022 | 55.5022 | 130.8343 | 12.3337 | 280.3726 | 126.2284 | 285.8381 | 10.4377 | 84.566 | 5.5918 | 172 | 52.7306 | 0 | 270.7836 | 0
10246 | 891.5836 | 4.825 | 23.8446 | 95.7414 | 53.5724 | 5.7 | 81.1526 | 9.2898 | 13.3622 | 45.5754 | 113.4267 | 11.8938 | 255.0349 | 111.901 | 263.2214 | 10.2647 | 80.7096 | 5.0561 | 175 | 47.2306 | 0 | 258.3189 | 0
10247 | 859.7201 | 4.261 | 23.6102 | 95.3492 | 52.5743 | 6.6497 | 71.4431 | 11.7498 | 10.2444 | 39.07 | 95.3612 | 10.6709 | 234.4169 | 99.3352 | 254.1754 | 10.1078 | 79.8969 | 4.3877 | 152 | 43.9662 | 0 | 258.3769 | 0
10248 | 831.18 | 3.1374 | 23.4576 | 96.6177 | 52.58 | 6.65 | 68.6394 | 7.8779 | 7.0094 | 24.7709 | 59.9305 | 11.8629 | 68.4176 | 64.6337 | 163.3786 | 10.0912 | 50.2519 | 3.3008 | 140 | 42.4723 | 0 | 132.0439 | 0
10249 | 838.8287 | 2.7716 | 23.5671 | 98.045 | 54.5829 | 4.7505 | 79.1907 | 11.2395 | 6.0916 | 37.9812 | 91.3372 | 12.4908 | 196.7529 | 94.3331 | 226.3555 | 9.8677 | 79.6915 | 2.8476 | 129 | 41.6681 | 0 | 262.2323 | 0
10250 | 838.6645 | 2.6017 | 23.6455 | 98.0467 | 53.5843 | 5.6997 | 82.3467 | 8.0848 | 6.1755 | 33.7257 | 91.3284 | 10.8017 | 193.1263 | 88.0583 | 223.0494 | 9.9901 | 79.7799 | 2.8209 | 133 | 40.1066 | 0 | 263.3987 | 0
10251 | 836.3882 | 2.9406 | 23.5066 | 98.5793 | 53.582 | 5.7 | 71.1072 | 11.2455 | 6.2311 | 31.4986 | 90.4449 | 10.2902 | 192.4909 | 85.6528 | 225.7804 | 10.0596 | 79.8982 | 2.7943 | 136 | 38.8926 | 0 | 256.0491 | 0
10252 | 820.2068 | 3.3518 | 23.4933 | 98.2103 | 54.581 | 4.7503 | 71.683 | 8.7268 | 5.9735 | 31.272 | 90.799 | 10.1489 | 192.4474 | 84.1677 | 224.358 | 10.0218 | 80.0415 | 2.7838 | 129 | 38.381 | 0 | 262.0885 | 0
10253 | 821.1066 | 3.2753 | 23.5616 | 98.2782 | 53.5845 | 5.6997 | 79.3492 | 10.7201 | 6.1506 | 31.2985 | 91.5404 | 10.039 | 197.2983 | 86.0482 | 221.7177 | 10.0678 | 81.6522 | 2.8074 | 123 | 38.557 | 0 | 292.9711 | 0
10254 | 839.2663 | 4.2731 | 32.3449 | 98.6313 | 54.5817 | 4.7503 | 80.2207 | 10.5904 | 6.6291 | 46.0329 | 92.3306 | 11.0916 | 208.2841 | 92.9666 | 229.2279 | 9.8285 | 84.5349 | 3.4791 | 124 | 39.1773 | 0 | 346.6702 | 0
10255 | 879.3344 | 5.9834 | 47.1989 | 102.58 | 49.5801 | 9.4987 | 87.814 | 9.6244 | 7.9992 | 64.6853 | 103.5238 | 16.7297 | 240.1376 | 173.2436 | 249.1653 | 12.541 | 81.2677 | 4.3657 | 172 | 45.7969 | 0 | 383.0532 | 0
10256 | 942.3155 | 6.7091 | 73.931 | 105.2442 | 39.5816 | 18.9974 | 115.8217 | 12.7908 | 6.6095 | 75.0638 | 147.9287 | 29.4021 | 298.4692 | 235.7622 | 331.9119 | 27.2118 | 84.1712 | 6.9461 | 257 | 62.402 | 0 | 419.774 | 0.01066
10257 | 1013.7286 | 11.2176 | 95.5225 | 119.5158 | 32.5766 | 25.6482 | 142.4131 | 9.34 | 6.5437 | 72.258 | 183.1777 | 33.0514 | 356.1622 | 287.2165 | 470.878 | 36.4 | 97.7972 | 13.4614 | 301 | 72.3163 | 0 | 500.3228 | 0.067328
10258 | 1100.2608 | 21.2163 | 101.863 | 133.8451 | 39.5677 | 19.0018 | 152.0217 | 13.9176 | 13.0307 | 80.6896 | 194.5737 | 29.8084 | 402.5813 | 316.7558 | 559.8181 | 40.9988 | 106.8151 | 16.2999 | 361 | 74.2971 | 0 | 552.9911 | 0.11237
10259 | 1138.9722 | 22.3519 | 100.7495 | 141.9478 | 39.57 | 19 | 156.616 | 10.2366 | 21.166 | 90.3442 | 195.4861 | 28.6848 | 419.5445 | 340.2887 | 585.2906 | 39.9648 | 116.3355 | 17.4367 | 364 | 71.5592 | 0 | 557.0689 | 0.14632
10260 | 1148.4492 | 23.6247 | 103.8574 | 142.2443 | 38.574 | 19.9497 | 161.1271 | 12.1496 | 22.0268 | 80.6854 | 195.8938 | 30.7282 | 425.6385 | 356.37 | 581.8543 | 40.6723 | 121.3943 | 18.3016 | 341 | 79.843 | 0 | 577.8058 | 0.10933
10261 | 1141.9683 | 21.08 | 103.0108 | 139.044 | 38.573 | 19.95 | 159.9775 | 10.3623 | 12.837 | 76.6813 | 193.7021 | 34.1608 | 419.2072 | 348.9397 | 579.0047 | 43.8385 | 117.606 | 18.376 | 417 | 71.4428 | 0 | 555.3899 | 0.10784
10262 | 1150.2869 | 15.7 | 102.5704 | 141.0242 | 43.5707 | 15.2013 | 162.5724 | 10.1396 | 9.8239 | 72.0002 | 199.2643 | 32.4893 | 429.1863 | 354.0991 | 593.9567 | 45.0834 | 116.8506 | 18.9354 | 289 | 73.4263 | 0 | 581.0317 | 0.12591
10263 | 1150.7022 | 8.6323 | 101.2241 | 142.2457 | 43.5671 | 15.2 | 162.0652 | 10.2427 | 10.1351 | 81.6621 | 200.3943 | 30.3614 | 421.33 | 358.9591 | 588.8726 | 42.737 | 117.6903 | 19.6303 | 289 | 70.6634 | 0 | 562.6241 | 0.099824
10264 | 1134.9034 | 5.5527 | 99.9228 | 139.8415 | 45.571 | 13.3005 | 158.4861 | 10.3063 | 8.4488 | 80.8401 | 198.5283 | 31.6548 | 409.1727 | 347.073 | 582.5203 | 40.3209 | 117.4849 | 18.8432 | 292 | 66.4997 | 0 | 530.8757 | 0.053184
10265 | 1083.9486 | 5.1398 | 96.4912 | 131.9202 | 45.5766 | 13.3 | 147.1035 | 9.8587 | 8.6957 | 79.6022 | 193.5012 | 30.3623 | 385.0174 | 310.2274 | 521.8967 | 34.344 | 107.261 | 16.9557 | 260 | 59.9621 | 0 | 477.3301 | 0.026121
10266 | 1010.1336 | 6.2296 | 89.1854 | 121.4064 | 48.5716 | 10.4537 | 124.0864 | 10.0545 | 9.2692 | 64.6911 | 175.4317 | 29.6792 | 338.4921 | 240.7483 | 409.9009 | 18.8711 | 85.5474 | 15.4497 | 237 | 58.8076 | 0 | 355.3021 | 0
10267 | 966.6849 | 6.1018 | 84.2732 | 108.4943 | 49.5796 | 9.4974 | 113.2888 | 8.6168 | 9.1107 | 56.6951 | 148.5184 | 26.4811 | 292.5645 | 177.4522 | 332.8648 | 15.301 | 74.263 | 12.4582 | 227 | 54.7874 | 0 | 303.4274 | 0
10268 | 921.1498 | 8.7532 | 76.306 | 101.9132 | 52.5749 | 6.6508 | 98.7147 | 10.1197 | 8.0668 | 54.3605 | 128.6571 | 13.7018 | 259.1029 | 147.0999 | 287.326 | 14.3976 | 60.6683 | 7.067 | 205 | 52.2354 | 0 | 259.3806 | 0
10269 | 880.6571 | 8.2797 | 39.6585 | 99.7507 | 51.5768 | 7.5997 | 79.9555 | 8.449 | 7.6183 | 51.6693 | 105.1028 | 8.9416 | 235.9142 | 125.6132 | 260.4305 | 11.5862 | 52.5533 | 4.3858 | 188 | 47.1419 | 0 | 238.5727 | 0
10270 | 868.7411 | 5.5096 | 24.141 | 98.4177 | 50.583 | 8.5497 | 76.9466 | 10.0173 | 7.1313 | 43.3159 | 93.16 | 9.0027 | 220.3329 | 105.3091 | 255.7207 | 10.4697 | 50.9928 | 4.3447 | 192 | 43.1761 | 0 | 238.1275 | 0
10271 | 842.7344 | 4.4319 | 22.9089 | 97.5848 | 51.5824 | 7.6003 | 79.8066 | 8.7626 | 7.423 | 41.1364 | 90.6997 | 8.8206 | 210.8041 | 97.5922 | 250.5895 | 10.2271 | 49.9571 | 3.9208 | 172 | 42.6944 | 0 | 236.7483 | 0
10272 | 814.907 | 3.5991 | 22.8007 | 97.722 | 52.583 | 6.6503 | 69.8937 | 10.0282 | 8.0113 | 26.0342 | 58.5449 | 8.7976 | 61.4926 | 60.8396 | 166.9536 | 10.1917 | 32.0102 | 3.6496 | 173 | 43.0626 | 0 | 122.0446 | 0
10273 | 803.6535 | 3.1262 | 23.151 | 96.4261 | 50.5838 | 8.5495 | 69.9309 | 8.6839 | 7.066 | 40.4865 | 86.0518 | 8.8536 | 201.9526 | 91.233 | 247.0066 | 10.1873 | 50.0945 | 4.0588 | 157 | 43.5526 | 0 | 241.77 | 0
10274 | 802.5527 | 2.7059 | 23.1564 | 95.9811 | 49.5834 | 9.4997 | 78.3506 | 9.8882 | 6.2799 | 38.3854 | 85.7074 | 8.7477 | 200.0177 | 85.2966 | 243.3467 | 9.8832 | 49.6045 | 3.9924 | 151 | 41.8817 | 0 | 247.198 | 0
10275 | 796.2846 | 2.5267 | 22.8125 | 96.0883 | 52.5847 | 6.6508 | 74.2844 | 8.873 | 6.1956 | 34.945 | 85.5177 | 8.6867 | 191.5569 | 80.8468 | 243.8469 | 10.047 | 49.4434 | 3.7919 | 153 | 39.0076 | 0 | 244.9786 | 0
10276 | 785.5931 | 2.4743 | 22.6623 | 95.873 | 51.583 | 7.5997 | 67.7203 | 10.3003 | 6.0706 | 34.4716 | 86.2292 | 10.9412 | 186.1777 | 79.6838 | 231.7566 | 10.1751 | 49.5226 | 3.7263 | 148 | 38.3507 | 0 | 246.3994 | 0
10277 | 784.8728 | 2.9723 | 22.9065 | 95.9024 | 50.5832 | 8.5497 | 75.3617 | 8.5374 | 5.9598 | 33.7931 | 87.6795 | 9.9659 | 183.9471 | 79.429 | 220.448 | 10.0709 | 50.9242 | 3.6751 | 136 | 37.5473 | 0 | 240.2574 | 0
10278 | 784.4757 | 3.8648 | 25.6228 | 95.0426 | 50.5813 | 8.55 | 79.6036 | 10.7386 | 5.9615 | 32.4367 | 89.081 | 8.6577 | 181.6511 | 79.7026 | 217.3329 | 10.026 | 53.2051 | 3.6437 | 129 | 36.5535 | 0 | 242.5041 | 0
10279 | 795.8195 | 4.2882 | 38.3129 | 93.624 | 53.5773 | 5.7008 | 69.3807 | 8.1416 | 5.9055 | 30.5423 | 87.9243 | 7.9203 | 181.7419 | 81.4831 | 210.64 | 9.6594 | 50.1886 | 3.611 | 122 | 38.5663 | 0 | 246.2158 | 0
10280 | 806.7846 | 4.1644 | 51.7647 | 92.0761 | 50.5808 | 8.5492 | 70.3297 | 10.9413 | 5.3783 | 27.16 | 90.7737 | 8.0945 | 188.6369 | 82.051 | 203.9693 | 10.1807 | 48.7931 | 3.7096 | 125 | 42.5253 | 0 | 248.6586 | 0.01349
10281 | 811.5803 | 3.2224 | 61.4041 | 91.5275 | 50.5827 | 8.55 | 86.2783 | 7.5334 | 5.137 | 32.0423 | 110.0018 | 13.5834 | 194.8185 | 86.6142 | 199.2765 | 10.8837 | 48.7896 | 4.1883 | 142 | 47.5235 | 0 | 241.625 | 0.027219
10282 | 828.5781 | 2.5725 | 68.904 | 91.9753 | 52.5795 | 6.6505 | 87.3323 | 10.5621 | 6.7755 | 40.701 | 133.805 | 15.8425 | 208.0247 | 92.195 | 201.6856 | 10.3835 | 48.6136 | 6.2958 | 181 | 52.7382 | 0 | 238.951 | 0.03907
10283 | 861.3987 | 2.7068 | 78.0285 | 92.3088 | 50.5787 | 8.5495 | 88.3926 | 6.7095 | 6.398 | 49.3296 | 148.4836 | 16.0223 | 225.3368 | 106.8442 | 218.603 | 9.5122 | 48.8669 | 11.7981 | 184 | 54.1182 | 0 | 253.5144 | 0.066352
10284 | 876.3199 | 3.0401 | 80.3249 | 92.3924 | 50.5791 | 8.55 | 98.7838 | 9.6196 | 5.3378 | 48.1111 | 136.2513 | 19.0367 | 237.0897 | 109.8634 | 236.6537 | 9.4286 | 48.9458 | 13.7332 | 207 | 54.99 | 0 | 263.27 | 0.07303
10285 | 871.9599 | 2.7682 | 80.4414 | 91.5203 | 51.5786 | 7.6003 | 105.666 | 7.205 | 5.123 | 51.2897 | 146.3883 | 19.6112 | 241.0178 | 109.5274 | 267.8014 | 9.4867 | 48.8139 | 14.0463 | 195 | 53.7838 | 0 | 257.1139 | 0.069404
10286 | 876.803 | 2.4808 | 80.4516 | 91.769 | 52.5815 | 6.6503 | 111.7906 | 8.0697 | 5.2188 | 50.0195 | 147.2768 | 16.1582 | 237.6693 | 119.0739 | 284.1705 | 9.417 | 48.5669 | 14.0893 | 173 | 56.1938 | 0 | 248.9915 | 0.077986
10287 | 885.8722 | 4.0667 | 75.8756 | 95.8108 | 50.5813 | 8.5495 | 109.4678 | 7.9475 | 5.4292 | 48.3566 | 143.3599 | 15.5347 | 237.1839 | 118.065 | 308.4946 | 9.4341 | 48.8248 | 12.0275 | 182 | 57.8041 | 0 | 239.542 | 0.054108
10288 | 884.5236 | 9.5442 | 74.498 | 96.0517 | 50.5753 | 8.55 | 100.5434 | 6.9286 | 5.3137 | 49.7243 | 151.2501 | 15.9679 | 237.5289 | 120.5438 | 334.912 | 9.3122 | 49.3107 | 6.8219 | 171 | 54.16 | 0 | 235.9875 | 0.051681
10289 | 880.8275 | 14.1435 | 40.4991 | 96.0081 | 52.5753 | 6.6505 | 108.1102 | 8.8531 | 5.0895 | 35.3005 | 142.4325 | 9.2698 | 235.8229 | 124.3352 | 319.6146 | 9.1817 | 49.1445 | 4.9002 | 174 | 49.8633 | 0 | 261.7405 | 0.017337
10290 | 867.9877 | 13.1269 | 24.5374 | 98.2315 | 52.5756 | 6.65 | 106.0648 | 8.1729 | 5.5603 | 29.6826 | 121.2563 | 7.5719 | 247.1845 | 129.7925 | 293.4931 | 8.636 | 49.6642 | 5.0571 | 177 | 47.7479 | 0 | 252.223 | 0
10291 | 828.9155 | 10.7956 | 23.1604 | 96.3428 | 49.5773 | 9.4992 | 100.8506 | 9.5374 | 6.1886 | 32.3294 | 98.2151 | 8.785 | 240.7103 | 127.2321 | 285.3783 | 8.7935 | 50.7288 | 5.21 | 186 | 47.2752 | 0 | 253.7676 | 0
10292 | 834.6342 | 6.7515 | 23.3401 | 95.8643 | 50.5788 | 8.5526 | 89.8629 | 8.546 | 6.3411 | 33.2013 | 90.2716 | 9.4502 | 229.2851 | 111.4093 | 268.3978 | 9.5558 | 51.3371 | 5.367 | 195 | 45.2275 | 0 | 260.3893 | 0
10293 | 825.7845 | 5.401 | 23.3001 | 95.9667 | 51.5833 | 7.5979 | 88.7358 | 9.859 | 6.2958 | 35.1629 | 87.3092 | 12.4438 | 217.1175 | 104.395 | 258.9565 | 9.7775 | 51.4572 | 4.8952 | 187 | 43.3297 | 0 | 250.8634 | 0
10294 | 810.296 | 4.6883 | 23.321 | 95.6173 | 49.5732 | 9.4995 | 78.3215 | 12.7852 | 6.2943 | 37.4445 | 83.8465 | 17.7443 | 217.1338 | 96.5429 | 248.1608 | 9.5299 | 50.0296 | 3.9359 | 184 | 42.6387 | 0 | 254.0108 | 0
10295 | 807.2342 | 4.5251 | 23.2795 | 95.2666 | 50.574 | 8.5503 | 74.3854 | 8.0452 | 6.0075 | 37.3903 | 82.2023 | 15.5033 | 219.2262 | 90.2783 | 247.5264 | 9.5169 | 49.6339 | 3.8165 | 166 | 42.2351 | 0 | 251.8616 | 0
10296 | 800.0335 | 5.2489 | 22.9996 | 95.3948 | 52.5785 | 6.6505 | 77.2639 | 11.0137 | 5.9818 | 22.7157 | 54.706 | 10.4776 | 65.5332 | 55.9846 | 167.4898 | 9.6375 | 31.3035 | 3.4879 | 133 | 41.2767 | 0 | 129.7366 | 0
10297 | 809.7944 | 8.6405 | 23.1678 | 95.4882 | 50.5817 | 8.5495 | 67.401 | 11.5774 | 5.9282 | 32.751 | 83.8343 | 10.6516 | 213.805 | 83.0676 | 238.6949 | 9.641 | 49.8418 | 3.1865 | 125 | 39.0706 | 0 | 254.3361 | 0
10298 | 806.4233 | 9.8284 | 23.2085 | 95.4696 | 49.5827 | 9.4997 | 64.4092 | 9.2249 | 5.9885 | 32.328 | 83.3086 | 9.7602 | 208.3133 | 86.5249 | 239.0648 | 9.7145 | 50.032 | 3.0541 | 127 | 39.7062 | 0 | 250.0421 | 0
10299 | 785.1894 | 9.7976 | 23.0576 | 95.4883 | 46.5821 | 12.3492 | 73.046 | 12.1656 | 5.932 | 31.1298 | 83.2872 | 9.0578 | 203.8181 | 86.7364 | 242.1007 | 9.5213 | 50.0632 | 2.7929 | 123 | 40.0497 | 0 | 262.3307 | 0
10300 | 779.2161 | 9.2284 | 23.0676 | 97.6865 | 46.5758 | 12.35 | 69.4189 | 13.7505 | 5.9029 | 30.7838 | 82.705 | 8.8623 | 199.9447 | 82.7499 | 245.3219 | 9.5788 | 49.9736 | 2.5611 | 123 | 39.3912 | 0 | 266.8258 | 0
10301 | 767.2135 | 4.9733 | 23.2808 | 100.616 | 45.5791 | 13.2997 | 63.8115 | 13.5199 | 6.0171 | 31.0556 | 82.1651 | 8.7507 | 197.2939 | 81.3844 | 242.0149 | 9.6654 | 52.0814 | 2.4679 | 114 | 42.0278 | 0 | 270.5794 | 0
10302 | 775.4861 | 4.0312 | 24.6867 | 103.3202 | 50.5768 | 8.5513 | 70.3198 | 8.4442 | 5.9382 | 31.5125 | 84.3047 | 8.7266 | 195.2805 | 83.8607 | 240.4614 | 9.6447 | 53.5432 | 2.4279 | 106 | 47.9441 | 0 | 267.3845 | 0
10303 | 783.9897 | 4.3873 | 46.8189 | 103.5846 | 52.5779 | 6.6505 | 70.6891 | 11.2642 | 5.9473 | 30.441 | 85.0127 | 8.3511 | 195.8428 | 81.7646 | 229.0672 | 9.5549 | 50.6523 | 2.3979 | 110 | 40.0724 | 0 | 268.0549 | 0
10304 | 786.6637 | 4.4835 | 57.622 | 102.0051 | 50.5814 | 8.5495 | 64.2084 | 13.2322 | 5.3289 | 27.0551 | 82.8964 | 6.6131 | 201.1299 | 80.9475 | 217.7119 | 10.3785 | 48.5911 | 2.7837 | 111 | 41.1714 | 0 | 255.6127 | 0.011565
10305 | 793.2347 | 3.6388 | 59.9306 | 104.3694 | 48.579 | 10.4495 | 65.9058 | 13.2981 | 5.4165 | 35.37 | 90.0086 | 5.9096 | 206.9522 | 87.0428 | 214.7807 | 12.4087 | 48.417 | 3.5251 | 126 | 43.1689 | 0 | 257.9044 | 0.027187
10306 | 807.1236 | 2.7927 | 67.6542 | 105.4848 | 50.5776 | 8.5505 | 77.205 | 10.2186 | 5.2096 | 49.7766 | 91.8494 | 5.9414 | 216.0793 | 97.6369 | 223.3948 | 11.5146 | 48.3949 | 3.7057 | 167 | 44.2497 | 0 | 253.401 | 0.030735
10307 | 844.5597 | 2.8176 | 77.7792 | 105.5059 | 51.5754 | 7.6003 | 90.8117 | 9.697 | 5.1058 | 56.0104 | 98.4202 | 5.1373 | 234.5306 | 105.7201 | 242.7632 | 10.7425 | 48.4902 | 4.8304 | 156 | 45.7995 | 0 | 261.5519 | 0.051684
10308 | 847.137 | 3.3086 | 79.4998 | 103.5859 | 49.578 | 9.4995 | 95.7666 | 12.1729 | 4.8978 | 59.9647 | 108.607 | 4.4091 | 248.4821 | 116.0082 | 255.3964 | 10.5497 | 48.5883 | 5.5254 | 191 | 49.0804 | 0 | 267.2815 | 0.058136
10309 | 856.9999 | 3.1352 | 78.5705 | 100.0727 | 51.5715 | 7.6005 | 94.4273 | 10.5619 | 4.9462 | 60.579 | 120.0979 | 5.0166 | 255.3712 | 130.8103 | 256.9397 | 10.5964 | 48.706 | 5.8705 | 197 | 51.2296 | 0 | 261.8571 | 0.055202
10310 | 857.1862 | 2.7389 | 77.936 | 98.4722 | 52.5714 | 6.6503 | 87.446 | 8.9915 | 5.0932 | 58.4985 | 124.8687 | 5.381 | 262.7007 | 146.6256 | 254.6089 | 10.4332 | 49.3169 | 5.9844 | 184 | 50.6355 | 0 | 266.4574 | 0.0492
10311 | 854.4182 | 3.1452 | 80.2458 | 100.5498 | 50.5754 | 8.5495 | 88.0619 | 11.6743 | 5.5209 | 56.6404 | 129.7353 | 6.6174 | 263.8013 | 153.4153 | 291.9665 | 10.5986 | 48.8405 | 6.3801 | 182 | 55.8449 | 0 | 269.1188 | 0.026011
10312 | 865.1771 | 6.5149 | 76.3704 | 108.7168 | 49.577 | 9.4997 | 98.2079 | 13.2251 | 6.586 | 56.0157 | 131.849 | 9.0966 | 255.6471 | 147.1646 | 306.6806 | 10.5142 | 49.7931 | 6.9694 | 180 | 55.4909 | 0 | 274.4037 | 0.013997
10313 | 858.0239 | 16.4164 | 40.866 | 109.5323 | 52.5806 | 6.6508 | 91.3535 | 13.21 | 6.4951 | 38.976 | 131.3522 | 10.487 | 253.2634 | 136.3671 | 298.3307 | 10.4009 | 49.9029 | 7.208 | 184 | 57.1042 | 0 | 265.3724 | 0.0092137
10314 | 855.0311 | 20.2887 | 24.8176 | 107.1052 | 52.5784 | 6.65 | 85.5196 | 13.2897 | 5.8708 | 32.1395 | 143.2389 | 11.8313 | 257.4388 | 126.1865 | 282.9728 | 9.33 | 49.8193 | 7.0669 | 159 | 50.8222 | 0 | 255.5453 | 0
10315 | 863.4617 | 15.693 | 24.2169 | 108.709 | 49.5797 | 9.4992 | 81.3309 | 13.522 | 6.3048 | 35.5729 | 159.8842 | 16.4626 | 253.452 | 128.564 | 269.6531 | 9.321 | 50.7999 | 7.0585 | 146 | 50.1051 | 0 | 265.1815 | 0
10316 | 858.3388 | 13.907 | 24.661 | 109.2849 | 49.5842 | 9.5 | 77.3593 | 13.6904 | 6.4801 | 38.3835 | 137.8774 | 19.6396 | 243.1358 | 119.976 | 271.2621 | 9.512 | 51.5354 | 6.6134 | 144 | 46.4707 | 0 | 267.8382 | 0
10317 | 841.1454 | 16.8236 | 24.8748 | 109.1012 | 51.5845 | 7.6005 | 71.021 | 13.7573 | 6.6768 | 39.4424 | 112.7761 | 12.7885 | 236.3407 | 105.9635 | 276.393 | 9.4819 | 51.0589 | 5.8379 | 144 | 43.2591 | 0 | 272.5384 | 0
10318 | 834.9207 | 12.323 | 24.6294 | 108.3468 | 49.5824 | 9.4995 | 70.3478 | 14.041 | 6.6203 | 39.5431 | 102.1311 | 8.9529 | 229.3041 | 100.0985 | 261.079 | 9.4524 | 50.2118 | 4.7936 | 141 | 44.0043 | 0 | 274.2906 | 0
10319 | 809.54 | 6.8153 | 24.4492 | 106.8763 | 49.5813 | 9.5 | 71.8066 | 13.8491 | 6.2151 | 38.2418 | 87.8391 | 8.6299 | 226.184 | 95.8693 | 254.3106 | 9.1938 | 49.5925 | 4.5026 | 127 | 43.993 | 0 | 274.282 | 0
10320 | 798.6492 | 7.7168 | 24.6576 | 105.0195 | 52.5805 | 6.6508 | 66.2824 | 13.7603 | 6.1802 | 24.5641 | 54.3162 | 8.6176 | 67.7016 | 59.6683 | 174.9457 | 9.3815 | 31.4553 | 4.3643 | 130 | 39.2373 | 0 | 140.5915 | 0
10321 | 797.8097 | 5.8297 | 24.7143 | 105.0765 | 51.5829 | 7.5997 | 64.8708 | 13.7875 | 6.2712 | 37.5913 | 81.6273 | 8.6643 | 204.2726 | 85.9145 | 256.4483 | 9.494 | 49.7852 | 3.5562 | 125 | 35.8444 | 0 | 279.5843 | 0
10322 | 798.8992 | 3.5909 | 24.6231 | 104.5925 | 47.5848 | 11.3989 | 69.367 | 13.8189 | 6.1037 | 38.3316 | 81.4936 | 8.7044 | 197.894 | 85.5296 | 248.546 | 9.4705 | 49.8555 | 3.488 | 114 | 36.2473 | 0 | 281.4674 | 0
10323 | 774.5307 | 3.1573 | 24.5616 | 103.7562 | 50.583 | 8.5508 | 65.3277 | 13.7848 | 6.0658 | 39.8575 | 81.3511 | 8.7796 | 197.5782 | 89.3607 | 242.0932 | 9.4237 | 49.6272 | 3.425 | 109 | 36.4699 | 0 | 285.7903 | 0
10324 | 779.3591 | 2.9654 | 25.1805 | 103.2493 | 51.5798 | 7.6003 | 63.122 | 13.8584 | 6.1732 | 38.6859 | 80.7564 | 8.9324 | 195.7154 | 90.9013 | 232.2073 | 9.2431 | 49.4505 | 2.8945 | 108 | 35.5595 | 0 | 278.3535 | 0
10325 | 779.6202 | 3.2616 | 26.3814 | 104.8426 | 48.5755 | 10.4492 | 67.4958 | 13.8267 | 6.2315 | 38.6733 | 80.7458 | 8.9728 | 197.0187 | 84.7023 | 236.1889 | 9.3695 | 50.9475 | 2.6684 | 107 | 35.0656 | 0 | 337.7357 | 0
10326 | 794.7267 | 4.3152 | 30.9504 | 105.3617 | 48.5742 | 10.45 | 71.1755 | 13.6229 | 6.5625 | 48.665 | 81.6748 | 10.4689 | 206.258 | 88.7702 | 241.6793 | 9.3757 | 53.2022 | 2.7083 | 108 | 35.5759 | 0 | 357.3803 | 0
10327 | 837.7093 | 5.6358 | 48.3137 | 110.3181 | 46.5769 | 12.3495 | 80.6147 | 13.6284 | 8.2045 | 72.8603 | 101.7333 | 18.5606 | 247.7446 | 158.5745 | 252.7947 | 11.8149 | 50.4718 | 3.532 | 178 | 44.4795 | 0 | 402.1624 | 0
10328 | 897.1052 | 7.8991 | 76.4653 | 114.2688 | 39.8213 | 18.9982 | 107.3113 | 14.1821 | 9.4606 | 85.774 | 139.5986 | 31.5955 | 290.087 | 221.0092 | 333.6097 | 24.988 | 52.0111 | 9.0876 | 288 | 63.5706 | 0 | 460.5328 | 0.016402
10329 | 980.9379 | 8.213 | 90.6352 | 121.8313 | 35.7105 | 22.7989 | 131.1075 | 16.2517 | 9.5257 | 87.94 | 168.7811 | 39.862 | 333.1928 | 282.3059 | 453.4978 | 35.5957 | 61.7859 | 16.4417 | 295 | 75.7342 | 0 | 533.4376 | 0.031226
10330 | 1073.7373 | 6.6064 | 99.8128 | 133.2199 | 40.5738 | 18.0513 | 147.8504 | 16.6623 | 11.6402 | 89.5596 | 190.9795 | 41.7303 | 379.8451 | 321.4289 | 522.4616 | 41.725 | 72.5186 | 16.6969 | 380 | 81.4747 | 0 | 583.9808 | 0.045875
10331 | 1134.0805 | 9.8246 | 97.4588 | 138.4938 | 38.5749 | 19.9495 | 156.0727 | 17.104 | 16.1148 | 86.458 | 201.8181 | 45.6463 | 402.9155 | 343.3375 | 555.4853 | 42.1939 | 78.585 | 15.8058 | 324 | 81.393 | 0 | 604.0684 | 0.09099
10332 | 1159.1737 | 13.392 | 97.8474 | 141.9435 | 40.5719 | 18.0505 | 154.5824 | 17.0758 | 16.0933 | 84.8705 | 207.2308 | 43.7066 | 415.7777 | 367.9362 | 601.4923 | 41.3247 | 82.4389 | 15.5634 | 368 | 90.026 | 0 | 602.2911 | 0.092899
10333 | 1164.4257 | 10.8231 | 98.5473 | 143.6447 | 38.5743 | 19.9495 | 157.8592 | 11.702 | 16.2242 | 87.763 | 209.1869 | 42.5935 | 416.7368 | 378.4213 | 596.1497 | 42.5205 | 77.0479 | 16.8561 | 383 | 86.9381 | 0 | 605.7672 | 0.083513
10334 | 1169.8444 | 7.9698 | 96.916 | 147.7899 | 33.5783 | 24.6987 | 155.8838 | 14.749 | 17.4532 | 99.5134 | 208.4131 | 40.3919 | 414.8024 | 376.2425 | 605.6863 | 43.7856 | 76.8563 | 18.3893 | 383 | 90.052 | 0 | 611.8083 | 0.094761
10335 | 1160.0337 | 5.4557 | 97.0057 | 150.6862 | 36.5716 | 21.8508 | 155.8834 | 17.0943 | 16.5443 | 104.3356 | 212.1704 | 37.3457 | 420.7356 | 378.2986 | 612.1933 | 44.6025 | 78.5934 | 19.0855 | 354 | 93.1668 | 0 | 585.8633 | 0.066934
10336 | 1147.8861 | 7.1508 | 97.4732 | 151.8279 | 44.5731 | 14.2521 | 158.5762 | 16.1671 | 10.3568 | 93.4122 | 209.9925 | 38.8021 | 418.8595 | 367.14 | 585.3316 | 43.3704 | 79.1076 | 19.1564 | 271 | 86.1222 | 0 | 584.8486 | 0.031273
10337 | 1099.2538 | 11.0421 | 95.5792 | 145.3487 | 46.5757 | 12.3505 | 143.7655 | 15.8733 | 8.8042 | 84.2212 | 201.0177 | 38.2652 | 402.6703 | 337.0813 | 501.0083 | 35.7551 | 77.1553 | 18.7157 | 243 | 71.5971 | 0 | 554.9757 | 0.027885
10338 | 1031.0704 | 12.9494 | 91.2584 | 137.2161 | 50.5753 | 8.5511 | 130.3895 | 15.3915 | 8.9951 | 71.9865 | 183.2671 | 36.8542 | 362.4929 | 276.7034 | 424.3268 | 19.2318 | 72.4963 | 18.2224 | 220 | 65.2538 | 0 | 408.7776 | 0
10339 | 996.2224 | 9.0718 | 80.3366 | 128.8189 | 52.5735 | 6.6505 | 118.8305 | 14.4656 | 9.8696 | 61.7463 | 156.9063 | 35.4585 | 319.8872 | 193.5221 | 386.0086 | 13.2015 | 65.8907 | 15.5231 | 232 | 61.485 | 0 | 376.0788 | 0
10340 | 953.7583 | 6.265 | 63.2727 | 120.1175 | 52.5796 | 6.65 | 98.7387 | 14.0216 | 9.5966 | 62.1044 | 146.5071 | 25.9456 | 279.6544 | 154.9292 | 349.5049 | 12.2327 | 58.2607 | 9.2459 | 194 | 55.6057 | 0 | 340.9997 | 0
10341 | 909.564 | 5.1676 | 34.1409 | 113.5098 | 53.5814 | 5.7003 | 84.3385 | 13.9655 | 8.2609 | 57.9184 | 137.3904 | 15.6743 | 252.4208 | 133.0271 | 294.7375 | 10.7569 | 55.4452 | 6.4502 | 178 | 51.5185 | 0 | 342.3007 | 0
10342 | 875.0962 | 4.8145 | 24.8969 | 110.7271 | 53.5815 | 5.7 | 73.5793 | 14.0847 | 7.5103 | 48.7278 | 120.8095 | 10.3407 | 237.0746 | 117.5368 | 284.352 | 9.9512 | 53.4187 | 5.6753 | 167 | 47.4102 | 0 | 338.7239 | 0
10343 | 844.5145 | 9.1098 | 24.7835 | 109.9793 | 53.5759 | 5.7 | 67.1039 | 13.8727 | 7.3497 | 42.7248 | 103.049 | 13.8675 | 219.8948 | 106.2783 | 284.9816 | 9.6336 | 51.3425 | 5.1067 | 148 | 42.8377 | 0 | 345.6311 | 0
10344 | 843.0436 | 10.4442 | 24.7554 | 109.7061 | 52.5784 | 6.6497 | 70.051 | 13.8339 | 7.341 | 27.0701 | 63.6777 | 11.4044 | 64.0388 | 64.4236 | 186.1677 | 9.6488 | 31.8801 | 4.783 | 132 | 39.5025 | 0 | 178.8985 | 0
10345 | 838.4056 | 9.7788 | 24.6352 | 109.8923 | 50.5796 | 8.5495 | 68.0483 | 13.8958 | 7.198 | 38.8921 | 94.7725 | 9.4673 | 207.9915 | 94.9223 | 236.2805 | 9.6772 | 49.5308 | 4.3904 | 121 | 35.6415 | 0 | 348.1548 | 0
10346 | 834.2086 | 9.7289 | 24.6351 | 109.6914 | 52.5808 | 6.6505 | 64.118 | 14.1604 | 7.3887 | 36.5368 | 96.3433 | 9.3402 | 211.1307 | 91.6257 | 229.7081 | 9.7178 | 49.3352 | 3.8359 | 117 | 34.5145 | 0 | 354.2272 | 0
10347 | 823.1977 | 9.9218 | 24.7047 | 108.7136 | 52.5789 | 6.6518 | 66.5422 | 14.0374 | 7.2262 | 37.1098 | 98.9344 | 9.4927 | 205.1883 | 88.6539 | 247.1865 | 9.702 | 49.441 | 3.6801 | 122 | 33.5662 | 0 | 349.0077 | 0
10348 | 810.1354 | 9.0218 | 24.6251 | 107.8546 | 52.5835 | 6.6482 | 66.8922 | 13.9137 | 7.2055 | 36.9488 | 100.2921 | 9.3008 | 196.9714 | 84.1767 | 258.2077 | 9.5057 | 49.2064 | 3.6793 | 117 | 34.9821 | 0 | 354.9784 | 0
10349 | 810.0274 | 6.3995 | 24.7786 | 107.9672 | 52.577 | 6.65 | 63.617 | 13.8875 | 7.2888 | 37.5552 | 98.0379 | 9.1562 | 200.8504 | 81.9373 | 251.6668 | 9.567 | 50.3908 | 3.6536 | 109 | 35.3152 | 0 | 392.2489 | 0
10350 | 823.4689 | 5.0128 | 37.2959 | 107.6339 | 52.5762 | 6.6518 | 71.5451 | 13.8223 | 7.7099 | 47.3554 | 95.5276 | 10.12 | 211.15 | 90.1815 | 247.238 | 9.6358 | 52.702 | 3.6349 | 110 | 33.7616 | 0 | 450.2871 | 0
10351 | 860.2238 | 10.0127 | 52.466 | 109.6407 | 50.5782 | 8.5476 | 85.0861 | 14.2024 | 8.2961 | 76.3792 | 105.8168 | 15.2246 | 246.5914 | 160.9673 | 257.5775 | 12.0778 | 49.7442 | 5.0245 | 196 | 41.3585 | 0 | 481.9121 | 0
10352 | 906.9073 | 12.3806 | 78.4994 | 112.1956 | 44.5766 | 14.2484 | 101.5171 | 14.5068 | 12.6668 | 81.1471 | 151.8929 | 29.7628 | 295.6585 | 225.9535 | 368.4788 | 25.3667 | 52.3527 | 9.2412 | 290 | 63.2829 | 0 | 525.2831 | 0.057219
10353 | 1017.0353 | 17.5378 | 92.1554 | 124.2648 | 43.5726 | 15.1997 | 121.8676 | 15.6284 | 14.4507 | 86.4969 | 187.1246 | 33.7051 | 351.7101 | 271.8733 | 488.213 | 33.3564 | 62.0441 | 15.3306 | 303 | 71.9176 | 0 | 593.0178 | 0.11054
10354 | 1104.0246 | 19.2026 | 102.528 | 139.4202 | 44.5755 | 14.2503 | 137.1749 | 17.152 | 16.4385 | 88.8031 | 199.4939 | 34.4814 | 394.2035 | 315.0182 | 558.1864 | 37.095 | 73.8346 | 17.4746 | 341 | 74.5571 | 0 | 637.4515 | 0.13251
10355 | 1159.9662 | 13.9389 | 104.0924 | 145.3053 | 43.5765 | 15.1997 | 140.939 | 17.2133 | 18.863 | 90.1298 | 201.7199 | 39.2718 | 404.6094 | 341.4336 | 597.8799 | 39.6499 | 78.1657 | 17.4653 | 328 | 76.4294 | 0 | 657.0818 | 0.23392
10356 | 1164.4401 | 10.2317 | 105.5572 | 145.6527 | 42.5735 | 16.1497 | 153.7687 | 17.038 | 18.3111 | 91.0047 | 201.5508 | 39.2264 | 423.5249 | 361.7323 | 328.3887 | 40.3188 | 81.9211 | 17.4258 | 327 | 86.4415 | 0 | 675.714 | 0.1662
10357 | 1135.7818 | 9.1203 | 103.8576 | 144.0317 | 38.5664 | 19.9545 | 149.3509 | 16.8455 | 18.0465 | 97.249 | 210.3476 | 39.7705 | 457.4768 | 351.6687 | 574.4621 | 42.6912 | 79.3736 | 18.1822 | 339 | 83.7056 | 0 | 670.0872 | 0.15785
10358 | 1177.2522 | 7.7534 | 103.8335 | 144.6692 | 42.5765 | 16.1455 | 146.0461 | 15.7072 | 18.757 | 107.4891 | 214.9639 | 41.0824 | 448.4567 | 352.7007 | 579.2236 | 43.5593 | 81.7245 | 19.9311 | 315 | 85.7014 | 0 | 692.0092 | 0.074887
10359 | 1199.7269 | 5.6077 | 106.208 | 148.3909 | 36.5742 | 21.8484 | 143.816 | 13.2615 | 17.1343 | 108.8212 | 216.9299 | 40.6968 | 463.1841 | 357.8331 | 577.9606 | 43.6184 | 84.0245 | 20.267 | 267 | 83.1045 | 0 | 674.2266 | 0.067009
10360 | 1165.8562 | 5.2475 | 99.7798 | 147.2666 | 35.5745 | 22.7997 | 141.5827 | 12.1154 | 15.419 | 105.632 | 213.7722 | 38.6769 | 436.5801 | 344.9789 | 575.2729 | 41.3736 | 82.7384 | 20.2932 | 261 | 77.8121 | 0 | 686.9831 | 0.043105
10361 | 1128.4457 | 5.2293 | 91.0587 | 140.9861 | 39.5738 | 19.0011 | 137.8071 | 10.1303 | 15.1974 | 93.7196 | 205.3602 | 35.8939 | 403.6544 | 322.6293 | 534.1217 | 33.9052 | 80.3851 | 20.2645 | 250 | 67.5303 | 0 | 616.0709 | 0.040773
10362 | 1071.1913 | 5.9386 | 86.292 | 128.105 | 47.5719 | 11.4021 | 122.4862 | 8.2035 | 14.1928 | 79.3313 | 186.9137 | 32.2298 | 367.2618 | 274.9429 | 456.35 | 20.0969 | 77.1261 | 19.5243 | 214 | 65.3174 | 0 | 457.418 | 0
10363 | 1016.1513 | 7.203 | 82.4454 | 114.0243 | 47.5764 | 11.4 | 112.6503 | 7.6714 | 12.5185 | 61.7992 | 161.4502 | 28.0763 | 329.929 | 203.0154 | 392.2401 | 13.5601 | 68.4101 | 16.175 | 216 | 62.9178 | 0 | 402.1235 | 0
10364 | 969.3699 | 13.3679 | 72.0754 | 109.5407 | 48.5768 | 10.4503 | 91.4134 | 7.3432 | 8.1557 | 55.3584 | 148.6983 | 15.335 | 296.7337 | 170.8333 | 331.9394 | 12.1226 | 60.0349 | 8.9735 | 191 | 56.7064 | 0 | 355.0253 | 0
10365 | 938.1574 | 16.8681 | 41.9035 | 107.5859 | 48.5809 | 10.45 | 74.2207 | 7.6738 | 7.2824 | 52.0552 | 138.4644 | 9.722 | 272.4224 | 152.2852 | 289.1967 | 11.4426 | 55.5891 | 5.6719 | 175 | 53.9653 | 0 | 339.2843 | 0
10366 | 910.4415 | 9.2909 | 27.1535 | 106.0074 | 46.5835 | 12.3495 | 73.4197 | 7.9839 | 7.5809 | 44.1091 | 125.1387 | 9.6577 | 242.1464 | 139.0297 | 265.7212 | 11.2199 | 54.2418 | 4.835 | 159 | 47.5222 | 0 | 339.8724 | 0
10367 | 894.4952 | 6.1506 | 24.8911 | 105.4696 | 48.5829 | 10.4505 | 69.4718 | 6.9253 | 6.7677 | 41.6325 | 121.8817 | 9.7798 | 222.2747 | 131.1546 | 251.0078 | 11.1681 | 54.0477 | 4.5744 | 143 | 45.1408 | 0 | 340.8432 | 0
10368 | 881.4976 | 5.1713 | 24.99 | 105.7724 | 48.5831 | 10.45 | 66.1852 | 6.5811 | 6.3755 | 27.4491 | 77.4681 | 9.7342 | 63.6981 | 78.2652 | 168.398 | 10.9412 | 33.7928 | 4.5169 | 127 | 44.6457 | 0 | 165.4041 | 0
10369 | 869.1327 | 3.2528 | 24.8321 | 103.9785 | 48.5833 | 10.45 | 68.9171 | 8.3993 | 5.8913 | 41.1808 | 100.4527 | 12.4689 | 209.4219 | 108.3151 | 252.3991 | 11.041 | 53.2313 | 3.7404 | 120 | 44.1901 | 0 | 323.2888 | 0
10370 | 857.0652 | 2.5994 | 24.9973 | 102.5886 | 48.5791 | 10.45 | 66.3121 | 8.2335 | 5.65 | 39.8366 | 94.4357 | 10.4322 | 207.9884 | 102.6119 | 241.2901 | 10.9891 | 52.7825 | 2.9019 | 116 | 39.5442 | 0 | 328.3188 | 0
10371 | 848.1912 | 2.8817 | 25.0314 | 102.3162 | 48.5789 | 10.45 | 63.4663 | 7.4348 | 5.9235 | 37.8386 | 94.1946 | 9.0653 | 203.9395 | 103.6178 | 233.034 | 11.014 | 52.7 | 2.6796 | 117 | 37.4066 | 0 | 328.0286 | 0
10372 | 844.7213 | 2.684 | 24.8254 | 102.2374 | 48.5767 | 10.45 | 66.5117 | 8.9718 | 5.9929 | 37.9301 | 93.9632 | 9.1027 | 198.2534 | 104.0549 | 225.6426 | 11.0292 | 52.8033 | 2.6765 | 116 | 36.3488 | 0 | 332.433 | 0
10373 | 838.6064 | 3.3588 | 24.5204 | 102.0275 | 46.5804 | 12.3495 | 65.5691 | 7.7076 | 5.8267 | 37.5635 | 93.5889 | 9.0667 | 199.6322 | 102.639 | 233.4536 | 10.8362 | 54.1184 | 2.7167 | 109 | 35.6535 | 0 | 365.3422 | 0
10374 | 844.0057 | 4.1874 | 36.447 | 102.1571 | 48.5748 | 10.4505 | 69.207 | 9.2053 | 5.8784 | 50.2204 | 94.697 | 10.1832 | 210.0838 | 109.3379 | 233.8972 | 10.9152 | 56.2809 | 2.7132 | 112 | 36.5369 | 0 | 409.3945 | 0
10375 | 888.217 | 5.2601 | 53.2475 | 106.7844 | 44.5832 | 14.2489 | 86.2221 | 7.8381 | 9.9272 | 75.6245 | 105.7347 | 18.1157 | 246.8445 | 172.208 | 246.7185 | 13.2331 | 53.3303 | 3.9322 | 167 | 46.7331 | 0 | 446.0715 | 0
10376 | 954.5989 | 6.9984 | 78.159 | 107.9234 | 41.5799 | 17.0992 | 106.5248 | 7.3344 | 9.7133 | 83.2602 | 147.4022 | 30.9813 | 301.8049 | 240.5139 | 358.1725 | 27.0626 | 56.3187 | 9.0035 | 276 | 63.7944 | 0 | 498.2262 | 0.01409
10377 | 1056.2449 | 12.6934 | 91.2138 | 122.3342 | 39.5761 | 18.9995 | 122.5379 | 10.1254 | 12.347 | 87.9798 | 185.791 | 38.239 | 359.7089 | 299.7338 | 470.9942 | 36.8787 | 66.3797 | 15.8484 | 318 | 74.7465 | 0 | 555.8984 | 0.047565
10378 | 1149.1312 | 16.3328 | 97.5435 | 133.6312 | 36.5719 | 21.8492 | 142.135 | 10.2053 | 14.6575 | 107.6067 | 203.678 | 40.1227 | 405.7245 | 340.4849 | 545.9941 | 40.9313 | 78.1358 | 18.9984 | 382 | 80.2746 | 0 | 592.4664 | 0.068161
10379 | 1157.9224 | 17.2215 | 99.5846 | 138.9885 | 36.5751 | 21.85 | 147.9569 | 10.4891 | 18.2077 | 109.7705 | 205.8121 | 41.8799 | 422.5751 | 356.7168 | 599.9205 | 42.5809 | 86.8355 | 20.0503 | 320 | 79.9847 | 0 | 594.4115 | 0.15229
10380 | 1198.7951 | 18.6728 | 107.5071 | 143.5387 | 39.5728 | 19.0008 | 151.0176 | 10.5649 | 17.7687 | 107.5623 | 202.1203 | 41.9002 | 430.8807 | 376.1802 | 626.3488 | 42.4929 | 87.5636 | 20.0115 | 309 | 86.7013 | 0 | 602.4156 | 0.20477
10381 | 1200.3413 | 16.8005 | 103.4795 | 140.9613 | 40.574 | 18.0503 | 156.0167 | 9.6427 | 16.4622 | 106.7652 | 200.9946 | 42.8598 | 427.2482 | 371.8813 | 629.2279 | 41.9918 | 81.633 | 19.792 | 340 | 83.3114 | 0 | 602.213 | 0.17869
10382 | 1214.3979 | 11.6542 | 102.2567 | 149.6833 | 36.5742 | 21.8489 | 150.4408 | 7.9962 | 17.9515 | 110.353 | 212.6057 | 44.627 | 432.8293 | 363.8991 | 627.4175 | 43.6226 | 83.9889 | 20.6789 | 279 | 87.9192 | 0 | 618.6939 | 0.084271
10383 | 1214.9046 | 6.9783 | 102.7385 | 152.1218 | 38.5743 | 19.9505 | 155.5051 | 8.0641 | 19.199 | 110.1055 | 213.3932 | 44.6629 | 439.3725 | 358.3761 | 626.7353 | 42.4096 | 84.6847 | 21.2226 | 257 | 86.0194 | 0 | 640.152 | 0.06355
10384 | 1161.5878 | 5.2455 | 99.1977 | 151.8324 | 37.5761 | 20.8997 | 155.6676 | 7.8689 | 19.4702 | 101.6098 | 208.8426 | 42.0896 | 431.2395 | 348.8936 | 600.9962 | 40.4379 | 84.167 | 20.7666 | 258 | 79.8076 | 0 | 659.2507 | 0.026036
10385 | 1138.6978 | 5.9204 | 89.869 | 147.7002 | 37.5763 | 20.9 | 141.6127 | 8.0187 | 18.5225 | 96.6426 | 200.8183 | 39.8916 | 406.8346 | 322.3077 | 554.8026 | 35.0934 | 80.8613 | 19.7659 | 230 | 69.9037 | 0 | 608.501 | 0.0088947
10386 | 1071.1057 | 7.6363 | 77.3796 | 136.594 | 46.5638 | 12.3558 | 136.6648 | 7.3933 | 17.5523 | 83.884 | 190.3052 | 35.7677 | 367.7545 | 271.1845 | 477.2514 | 19.5275 | 74.154 | 18.504 | 208 | 66.1156 | 0 | 447.2874 | 0.00068895
10387 | 1009.0245 | 6.795 | 76.2913 | 120.5059 | 48.5789 | 10.4471 | 123.6145 | 7.3604 | 12.5255 | 72.7336 | 164.1957 | 33.3294 | 328.0191 | 206.3859 | 405.7145 | 13.1501 | 68.2034 | 15.5874 | 198 | 62.7358 | 0 | 384.9584 | 0
10388 | 981.5496 | 9.148 | 71.6966 | 114.549 | 48.5798 | 10.45 | 103.6676 | 6.9103 | 7.8278 | 64.2278 | 147.925 | 22.12 | 291.4328 | 162.2614 | 371.2457 | 11.8128 | 60.8494 | 9.5265 | 190 | 59.9853 | 0 | 330.7486 | 0
10389 | 937.0344 | 12.6113 | 39.7306 | 113.0252 | 48.5824 | 10.45 | 89.045 | 5.912 | 6.4692 | 55.0578 | 138.456 | 17.3045 | 261.9085 | 130.0582 | 329.1979 | 11.3118 | 55.8852 | 6.5841 | 169 | 56.3388 | 0 | 310.0788 | 0
10390 | 895.2764 | 11.9799 | 25.0434 | 112.5927 | 48.5784 | 10.45 | 74.7472 | 5.5514 | 6.2123 | 47.0419 | 121.1288 | 16.7437 | 234.9833 | 109.054 | 277.7858 | 11.2414 | 53.4959 | 5.0824 | 162 | 48.0863 | 0 | 302.6546 | 0
10391 | 885.908 | 7.3828 | 23.5656 | 112.5874 | 48.583 | 10.45 | 76.4149 | 5.7743 | 6.1787 | 37.386 | 102.8711 | 22.4612 | 215.2962 | 98.6334 | 259.4936 | 11.3034 | 52.635 | 4.1328 | 140 | 41.612 | 0 | 307.2588 | 0
10392 | 866.0633 | 3.6795 | 23.7742 | 112.2002 | 47.5816 | 11.3997 | 83.3176 | 5.7743 | 6.104 | 21.8953 | 62.9936 | 26.3177 | 61.1859 | 61.3839 | 172.0116 | 11.3148 | 33.05 | 3.2952 | 126 | 40.2846 | 0 | 160.8972 | 0
10393 | 852.874 | 2.8414 | 23.4543 | 111.2831 | 47.5808 | 11.4 | 76.5881 | 5.9621 | 5.8648 | 33.0326 | 92.7398 | 17.1169 | 201.1939 | 93.2122 | 244.4665 | 11.1276 | 52.1857 | 3.0349 | 122 | 35.7445 | 0 | 309.9595 | 0
10394 | 850.7508 | 2.5486 | 23.48 | 102.8556 | 47.5807 | 11.4 | 70.8386 | 5.9623 | 6.2127 | 32.7296 | 92.1035 | 12.5111 | 198.6575 | 87.0611 | 231.2282 | 11.2048 | 52.3043 | 3.0794 | 117 | 33.0252 | 0 | 307.6733 | 0
10395 | 837.8395 | 2.3398 | 23.2921 | 98.3836 | 49.581 | 9.5005 | 77.3235 | 6.0933 | 6.2342 | 32.5993 | 91.9675 | 12.4045 | 193.6899 | 83.9936 | 229.7149 | 11.3923 | 52.4191 | 3.078 | 117 | 32.328 | 0 | 310.5048 | 0
10396 | 839.4317 | 2.4896 | 23.2673 | 97.8341 | 48.5811 | 10.4497 | 79.2654 | 6.0563 | 6.127 | 32.4778 | 91.8701 | 12.3611 | 189.5326 | 83.6189 | 226.7063 | 11.3938 | 52.4225 | 3.0474 | 113 | 32.5294 | 0 | 308.6098 | 0
10397 | 836.7958 | 3.0162 | 23.3562 | 96.572 | 48.582 | 10.45 | 70.422 | 5.4978 | 6.0312 | 32.5911 | 91.6905 | 12.3169 | 193.2243 | 83.6737 | 221.3079 | 11.2596 | 53.8885 | 3.0332 | 112 | 34.7011 | 0 | 337.2915 | 0
10398 | 839.4247 | 3.8453 | 33.9155 | 96.1295 | 48.5755 | 10.45 | 76.0603 | 5.0522 | 6.178 | 42.2423 | 95.0887 | 13.2541 | 203.5807 | 92.2643 | 221.9553 | 11.0405 | 56.4471 | 3.1829 | 112 | 34.3569 | 0 | 384.7133 | 0
10399 | 883.577 | 5.7577 | 48.8182 | 102.4883 | 46.5759 | 12.3495 | 97.0428 | 4.9189 | 6.3444 | 64.2965 | 104.8809 | 19.96 | 244.7989 | 174.9234 | 256.4474 | 13.5657 | 53.0504 | 4.5168 | 178 | 38.7674 | 0 | 426.9158 | 0
10400 | 947.3503 | 6.2814 | 72.3624 | 104.0553 | 42.5752 | 16.1489 | 115.5774 | 5.4756 | 7.1038 | 84.6079 | 145.4906 | 32.2145 | 296.8401 | 241.27 | 334.4127 | 29.2958 | 57.9342 | 7.7584 | 300 | 61.218 | 0 | 452.6209 | 0.0153
10401 | 1033.4087 | 11.0127 | 90.3479 | 116.1742 | 40.5722 | 18.0495 | 132.9012 | 6.5882 | 12.3565 | 94.5461 | 185.3985 | 38.4915 | 352.6136 | 295.8864 | 453.8133 | 37.2078 | 64.0308 | 16.4738 | 299 | 74.8548 | 0 | 562.3671 | 0.033979
10402 | 1133.9463 | 17.4289 | 98.8265 | 130.8902 | 36.5727 | 21.8489 | 157.9145 | 7.3966 | 17.1508 | 91.4305 | 199.6052 | 40.573 | 391.9318 | 344.1822 | 542.4238 | 42.3573 | 70.3912 | 18.2943 | 386 | 75.9361 | 0 | 667.3828 | 0.084298
10403 | 1177.5652 | 21.1607 | 99.9423 | 134.5667 | 39.5758 | 19.0008 | 166.3417 | 7.5536 | 23.1577 | 105.4356 | 203.4352 | 41.8504 | 415.3886 | 366.8216 | 595.6389 | 44.5821 | 78.1675 | 19.1417 | 329 | 77.2975 | 0 | 676.7635 | 0.10014
10404 | 1194.6788 | 17.2378 | 104.6887 | 133.987 | 40.5754 | 18.0503 | 157.3823 | 7.3866 | 22.209 | 105.8998 | 202.85 | 41.9883 | 422.846 | 375.3995 | 600.1948 | 43.5706 | 81.9835 | 19.7217 | 329 | 77.7923 | 0 | 686.7913 | 0.09443
10405 | 1212.8258 | 15.4774 | 101.8686 | 134.6923 | 40.5771 | 18.05 | 161.3994 | 7.6621 | 13.2583 | 95.8481 | 208.6582 | 41.4511 | 417.2782 | 367.4358 | 582.4975 | 43.7794 | 82.214 | 19.1759 | 387 | 76.0827 | 0 | 703.0808 | 0.12301
10406 | 1217.0466 | 9.3982 | 104.0049 | 138.6395 | 38.5771 | 19.9495 | 164.7707 | 6.6226 | 14.04 | 98.0743 | 211.105 | 41.2686 | 419.4622 | 368.6904 | 570.8611 | 45.3736 | 85.497 | 19.5211 | 356 | 78.9445 | 0 | 694.8437 | 0.065988
10407 | 1243.5764 | 4.9677 | 105.6539 | 147.9348 | 38.5756 | 19.95 | 162.6887 | 7.4588 | 15.871 | 106.3371 | 214.0587 | 40.8745 | 436.299 | 375.7235 | 585.4841 | 44.901 | 85.152 | 20.0098 | 305 | 81.9551 | 0 | 674.7737 | 0.055425
10408 | 1230.0063 | 4.8998 | 99.7938 | 153.3875 | 38.578 | 19.95 | 165.7908 | 6.649 | 15.2733 | 104.7418 | 213.5732 | 40.3327 | 437.3888 | 368.5328 | 583.5383 | 42.9612 | 84.5016 | 19.5144 | 267 | 77.6269 | 0 | 676.6911 | 0.039131
10409 | 1161.8773 | 8.7876 | 88.6901 | 144.385 | 44.5717 | 14.2516 | 154.9253 | 6.5154 | 14.6236 | 90.2081 | 206.9533 | 38.2365 | 408.1817 | 335.4369 | 512.5737 | 36.1464 | 81.9607 | 18.5312 | 243 | 67.5016 | 0 | 567.2233 | 0.024659
10410 | 1068.9916 | 7.6651 | 76.4001 | 126.1292 | 49.5651 | 9.5013 | 131.1338 | 6.2757 | 9.9246 | 69.3892 | 183.9776 | 36.3117 | 362.2735 | 266.3247 | 430.3689 | 28.2464 | 76.5208 | 17.3283 | 217 | 63.3217 | 0 | 403.3468 | 0.0019591
10411 | 1007.2434 | 5.6359 | 74.1088 | 114.3646 | 49.5702 | 9.5 | 122.2715 | 6.3846 | 7.3545 | 63.0749 | 159.4927 | 32.0277 | 327.7443 | 196.9221 | 380.1653 | 17.3282 | 71.0449 | 14.2122 | 203 | 57.6729 | 0 | 376.9486 | 0
10412 | 974.1733 | 4.7485 | 71.8511 | 109.9677 | 49.5722 | 9.5 | 97.2484 | 6.0468 | 7.0312 | 62.4867 | 146.5812 | 16.4113 | 302.9422 | 183.7359 | 332.9263 | 12.1683 | 61.0265 | 8.35 | 187 | 54.4449 | 0 | 321.2675 | 0
10413 | 926.8047 | 6.3411 | 41.7889 | 106.8108 | 48.5772 | 10.4497 | 87.9303 | 5.5356 | 7.2007 | 54.4318 | 136.0632 | 10.7265 | 275.5863 | 161.3603 | 295.3862 | 10.3845 | 55.4301 | 5.9725 | 180 | 47.5703 | 0 | 301.7493 | 0
10414 | 899.5805 | 6.8391 | 24.5757 | 103.7267 | 48.5757 | 10.45 | 88.9757 | 5.4766 | 7.1725 | 43.1044 | 119.7849 | 10.4638 | 244.3272 | 131.1392 | 280.6443 | 10.0824 | 53.6693 | 4.8606 | 166 | 41.6315 | 0 | 290.7867 | 0
10415 | 879.3648 | 4.6778 | 22.4382 | 102.3343 | 47.5747 | 11.3997 | 83.9056 | 5.0082 | 6.7358 | 37.6314 | 100.9821 | 10.3589 | 222.8783 | 111.0834 | 270.2902 | 10.11 | 53.2646 | 3.7175 | 150 | 38.5715 | 0 | 296.4823 | 0
10416 | 857.3003 | 3.0212 | 22.2428 | 101.6022 | 49.5742 | 9.5005 | 71.6368 | 4.7695 | 6.5012 | 22.048 | 61.2612 | 10.1875 | 63.1989 | 67.2732 | 169.9683 | 10.0707 | 33.3494 | 2.9063 | 132 | 34.9971 | 0 | 156.4514 | 0
10417 | 849.6573 | 2.4365 | 22.2632 | 101.7635 | 48.5782 | 10.4497 | 68.324 | 4.7419 | 6.5632 | 31.4971 | 91.4102 | 10.0584 | 201.7176 | 97.4766 | 224.7711 | 10.0604 | 52.8196 | 2.6948 | 114 | 33.4567 | 0 | 308.1439 | 0
10418 | 845.768 | 2.3045 | 22.1636 | 101.7806 | 49.5775 | 9.5003 | 77.4845 | 4.9985 | 6.5715 | 31.6298 | 91.3171 | 9.9322 | 200.4861 | 92.0312 | 219.0772 | 9.8568 | 52.4081 | 2.7069 | 114 | 32.0387 | 0 | 296.8909 | 0
10419 | 843.662 | 2.8912 | 22.2859 | 101.8514 | 48.5774 | 10.4497 | 76.8232 | 5.2868 | 6.6745 | 31.6067 | 91.5983 | 9.9366 | 199.398 | 87.6773 | 228.3887 | 9.9659 | 52.6963 | 2.7271 | 112 | 34.2219 | 0 | 305.3709 | 0
10420 | 833.6437 | 2.6703 | 22.0837 | 102.6045 | 49.5754 | 9.5029 | 67.4251 | 5.8231 | 6.7415 | 31.4414 | 91.5662 | 9.9085 | 198.6977 | 83.7276 | 232.4094 | 10.0374 | 52.9701 | 2.7509 | 106 | 32.3257 | 0 | 297.0494 | 0
10421 | 838.5251 | 3.44 | 22.1774 | 102.3033 | 48.5808 | 10.4471 | 70.6728 | 6.1115 | 6.578 | 31.4287 | 91.3142 | 9.8694 | 202.4873 | 84.3739 | 226.855 | 10.0574 | 54.514 | 2.7251 | 103 | 31.2365 | 0 | 327.2419 | 0
10422 | 844.8407 | 4.3741 | 30.6189 | 101.5553 | 48.5757 | 10.45 | 81.0251 | 6.2992 | 6.854 | 40.5034 | 93.4543 | 10.8491 | 215.6831 | 94.4912 | 230.7821 | 10.0007 | 56.9118 | 2.6967 | 113 | 31.294 | 0 | 378.9565 | 0
10423 | 898.1449 | 5.6989 | 43.6873 | 103.2792 | 47.5771 | 11.3997 | 86.8603 | 6.0835 | 6.8467 | 59.7536 | 106.0592 | 17.4359 | 248.1867 | 166.8885 | 258.0151 | 12.0511 | 53.8091 | 3.4001 | 184 | 43.6081 | 0 | 407.6172 | 0
10424 | 950.7265 | 5.6716 | 72.451 | 105.9899 | 41.5737 | 17.0984 | 103.15 | 5.7695 | 7.048 | 80.9054 | 147.2386 | 26.3181 | 288.4868 | 232.5491 | 355.0299 | 28.0216 | 55.8131 | 8.8314 | 257 | 62.7455 | 0 | 458.205 | 0.13343
10425 | 1020.5303 | 7.2824 | 90.6369 | 117.7981 | 38.5725 | 19.9492 | 132.7957 | 6.8873 | 8.1093 | 81.2522 | 183.6071 | 30.3722 | 351.1388 | 288.8993 | 471.7502 | 35.5872 | 64.5905 | 15.573 | 347 | 65.897 | 0 | 591.1905 | 0.19479
10426 | 1087.1373 | 8.0289 | 98.8997 | 133.9849 | 38.5669 | 19.95 | 145.7332 | 8.2103 | 9.2316 | 85.4567 | 192.898 | 31.0476 | 403.537 | 317.4053 | 532.1917 | 39.735 | 74.0162 | 17.473 | 364 | 67.3098 | 0 | 653.5794 | 0.1998
10427 | 1139.459 | 8.2591 | 96.9423 | 141.1891 | 41.5689 | 17.1008 | 140.7042 | 8.1276 | 10.572 | 95.6509 | 193.255 | 35.1876 | 424.5402 | 341.6498 | 567.9511 | 40.3107 | 81.1474 | 17.6449 | 326 | 68.8835 | 0 | 662.628 | 0.21867
10428 | 1147.7212 | 8.3131 | 97.5503 | 143.2474 | 38.5683 | 19.9492 | 148.3416 | 8.252 | 15.14 | 96.5833 | 194.5939 | 37.9749 | 433.0931 | 363.3972 | 580.0329 | 40.5747 | 82.4058 | 17.7622 | 323 | 68.5362 | 0 | 603.8709 | 0.24432
10429 | 1131.8054 | 10.128 | 95.1743 | 139.2289 | 36.5705 | 21.8495 | 156.4536 | 8.0236 | 15.167 | 91.4061 | 196.7066 | 36.8304 | 419.7867 | 355.6115 | 580.5777 | 41.239 | 78.5232 | 17.818 | 381 | 64.6637 | 0 | 584.1727 | 0.28825
10430 | 1139.4438 | 13.0052 | 93.8492 | 144.7509 | 37.5694 | 20.9003 | 162.595 | 8.1815 | 16.9474 | 89.918 | 207.3658 | 34.8535 | 423.9064 | 350.2644 | 593.3808 | 42.3912 | 80.2122 | 18.0961 | 305 | 64.9555 | 0 | 587.0491 | 0.30534
10431 | 1131.3202 | 9.2354 | 95.1053 | 145.1643 | 40.5698 | 18.0508 | 164.1894 | 8.5265 | 18.4888 | 88.4372 | 209.4922 | 31.9437 | 427.6382 | 352.945 | 594.9167 | 42.1536 | 82.3808 | 18.5732 | 285 | 65.2856 | 0 | 602.9732 | 0.29947
10432 | 1121.5057 | 5.4217 | 93.8879 | 143.94 | 38.5733 | 19.955 | 161.385 | 7.1079 | 18.8993 | 96.0104 | 203.5731 | 31.9452 | 411.0187 | 350.8289 | 572.4707 | 38.7543 | 80.2579 | 18.4539 | 273 | 66.026 | 0 | 585.5668 | 0.23735
10433 | 1065.0294 | 4.4401 | 89.0635 | 136.867 | 41.5761 | 17.0953 | 150.6721 | 5.4427 | 16.8777 | 93.6546 | 196.6812 | 31.7306 | 387.8589 | 321.1835 | 497.2692 | 29.078 | 76.1166 | 17.7239 | 249 | 61.3943 | 0 | 513.9285 | 0.11625
10434 | 1009.8712 | 5.3046 | 85.3917 | 125.9285 | 48.5707 | 10.4518 | 132.7786 | 5.3003 | 15.0608 | 77.3525 | 182.3224 | 29.7661 | 349.4451 | 246.4303 | 404.7311 | 17.2422 | 69.4378 | 17.2852 | 217 | 62.2002 | 0 | 414.0741 | 0.015771
10435 | 979.4079 | 5.3278 | 82.6402 | 112.9951 | 47.5725 | 11.3997 | 109.0934 | 5.6096 | 14.5645 | 65.6431 | 160.5959 | 26.6907 | 305.2507 | 162.2058 | 367.5439 | 13.7045 | 63.56 | 14.7557 | 216 | 62.0157 | 0 | 371.0182 | 0
10436 | 939.8762 | 5.3893 | 71.8496 | 106.4645 | 46.5734 | 12.3497 | 90.8929 | 6.019 | 11.6353 | 59.7342 | 144.6088 | 15.418 | 269.1011 | 130.8559 | 326.5018 | 13.3723 | 58.0019 | 9.2788 | 186 | 58.1984 | 0 | 326.8487 | 0
10437 | 911.7202 | 5.2846 | 37.6569 | 104.358 | 49.5732 | 9.5008 | 75.983 | 6.1431 | 8.7055 | 55.4501 | 118.518 | 9.9684 | 250.8643 | 126.5117 | 284.1112 | 11.3912 | 56.2447 | 6.5264 | 177 | 51.9009 | 0 | 298.5548 | 0
10438 | 889.0358 | 5.2577 | 24.547 | 103.7123 | 48.5762 | 10.4497 | 66.8644 | 5.5745 | 7.9642 | 42.6712 | 102.6842 | 9.2479 | 228.3167 | 124.765 | 264.7706 | 9.8145 | 54.0503 | 5.358 | 161 | 41.6514 | 0 | 296.7936 | 0
10439 | 853.1066 | 4.2522 | 23.7329 | 102.9974 | 49.572 | 9.5003 | 71.3209 | 5.414 | 7.2047 | 36.3096 | 98.2147 | 9.2001 | 213.1636 | 120.3075 | 261.7619 | 9.2576 | 52.8857 | 4.7255 | 151 | 36.2914 | 0 | 296.6691 | 0
10440 | 841.146 | 3.1068 | 23.6812 | 102.4578 | 49.5749 | 9.5 | 70.3012 | 5.4699 | 6.7953 | 22.638 | 64.1344 | 9.0644 | 61.2366 | 70.3852 | 174.4023 | 9.2775 | 33.4992 | 3.9441 | 142 | 34.2364 | 0 | 154.2708 | 0
10441 | 835.561 | 2.705 | 23.9629 | 101.767 | 48.578 | 10.4497 | 64.8852 | 5.4823 | 6.9507 | 33.534 | 96.9895 | 9.0072 | 200.9435 | 90.8339 | 252.6989 | 9.3562 | 52.7986 | 3.6286 | 129 | 32.7515 | 0 | 299.9699 | 0
10442 | 831.6489 | 3.0007 | 23.8572 | 102.209 | 49.5798 | 9.5003 | 66.907 | 6.2123 | 7.4457 | 32.973 | 96.5477 | 8.9391 | 198.3573 | 84.824 | 249.7399 | 9.3576 | 52.1592 | 3.5073 | 121 | 32.4898 | 0 | 307.054 | 0
10443 | 821.5535 | 2.5891 | 23.8459 | 102.4547 | 48.5793 | 10.4497 | 70.2117 | 6.5692 | 7.5097 | 32.5094 | 96.571 | 8.8636 | 195.1463 | 81.8784 | 252.8394 | 9.1312 | 51.4931 | 2.8864 | 122 | 31.2976 | 0 | 311.8025 | 0
10444 | 817.2459 | 2.391 | 23.7647 | 102.3635 | 48.5815 | 10.45 | 64.424 | 6.8495 | 6.997 | 32.2309 | 96.5036 | 8.8625 | 193.5348 | 81.9669 | 246.6593 | 9.1776 | 51.1422 | 2.6293 | 120 | 31.4067 | 0 | 307.8948 | 0
10445 | 813.9622 | 2.9998 | 23.8104 | 102.6043 | 47.5789 | 11.3997 | 64.8248 | 6.1648 | 6.73 | 32.4466 | 96.8011 | 8.8268 | 192.9276 | 81.2721 | 231.4808 | 9.3262 | 52.9574 | 2.6416 | 125 | 34.5852 | 0 | 306.0439 | 0
10446 | 817.0637 | 3.9634 | 24.2984 | 102.6983 | 48.581 | 10.4503 | 72.1622 | 5.5848 | 6.8605 | 32.8903 | 97.9103 | 8.8132 | 191.9534 | 81.373 | 224.8265 | 9.2897 | 55.3852 | 2.6675 | 124 | 32.0073 | 0 | 310.106 | 0
10447 | 835.7115 | 4.2818 | 42.9957 | 100.117 | 48.5818 | 10.45 | 67.1066 | 5.4869 | 6.1936 | 29.1371 | 96.3252 | 7.2874 | 196.3889 | 81.4189 | 221.4545 | 9.072 | 51.5059 | 2.5439 | 122 | 32.4569 | 0 | 314.6755 | 0
10448 | 843.2985 | 3.112 | 49.3179 | 102.7887 | 49.5815 | 9.5003 | 65.0987 | 5.8216 | 5.9869 | 27.4499 | 100.7221 | 7.8396 | 216.9468 | 84.1344 | 217.2314 | 8.6849 | 49.823 | 3.1493 | 117 | 47.7162 | 0 | 309.734 | 0.071623
10449 | 849.7295 | 2.8633 | 54.3048 | 102.9806 | 48.576 | 10.4497 | 80.7901 | 6.2133 | 7.2053 | 36.7233 | 125.9952 | 13.3864 | 233.6303 | 91.4424 | 228.2251 | 8.5853 | 50.0813 | 5.1613 | 128 | 55.7457 | 0 | 307.3611 | 0.099703
10450 | 888.6052 | 3.0497 | 68.6838 | 101.2184 | 48.5728 | 10.45 | 83.7906 | 5.4215 | 12.9017 | 50.8569 | 142.4832 | 16.3741 | 248.5837 | 107.1792 | 238.6015 | 8.489 | 50.681 | 8.1877 | 140 | 53.7621 | 0 | 300.6227 | 0.061428
10451 | 906.0153 | 2.9138 | 84.7895 | 100.907 | 47.5695 | 11.4029 | 78.8432 | 4.6258 | 16.7903 | 59.1512 | 153.5406 | 20.1088 | 263.9824 | 116.5966 | 241.8146 | 8.1206 | 50.0604 | 14.2046 | 167 | 50.0159 | 0 | 312.8573 | 0.12461
10452 | 909.8259 | 3.1117 | 87.2697 | 101.5992 | 49.5805 | 9.4974 | 88.1238 | 3.6502 | 17.6175 | 58.5086 | 142.3894 | 21.6496 | 272.8856 | 129.5665 | 244.0154 | 7.8845 | 50.5342 | 17.0392 | 202 | 49.8047 | 0 | 310.517 | 0.19976
10453 | 899.8753 | 3.2636 | 85.396 | 102.7732 | 48.5733 | 10.4497 | 107.9567 | 3.761 | 16.5784 | 56.4871 | 135.6227 | 22.0223 | 275.1488 | 132.1004 | 256.2559 | 7.7123 | 50.0688 | 17.1249 | 194 | 49.3958 | 0 | 293.4549 | 0.23728
10454 | 885.2094 | 3.267 | 83.6729 | 105.209 | 49.5722 | 9.5003 | 114.46 | 3.5005 | 15.0792 | 56.5363 | 135.403 | 22.223 | 270.9533 | 134.4553 | 278.6589 | 7.8739 | 49.7512 | 17.5733 | 207 | 52.6634 | 0 | 294.3031 | 0.30051
10455 | 881.1327 | 2.85 | 83.0823 | 105.6018 | 49.5707 | 9.5 | 112.1224 | 4.0278 | 14.018 | 57.1306 | 134.5537 | 19.5576 | 263.9839 | 137.614 | 284.6719 | 7.9698 | 50.1809 | 16.238 | 244 | 49.8752 | 0 | 293.3192 | 0.20761
10456 | 885.8624 | 5.3139 | 77.8252 | 103.75 | 49.5707 | 9.5 | 97.4376 | 4.1609 | 14.0727 | 51.3089 | 136.4538 | 19.518 | 259.6114 | 134.929 | 300.949 | 7.8512 | 50.9105 | 11.5679 | 229 | 46.0614 | 0 | 294.5068 | 0.10574
10457 | 873.9691 | 9.083 | 38.8539 | 102.6118 | 49.5729 | 9.5 | 102.0651 | 4.0669 | 14.9021 | 40.4294 | 139.4806 | 18.36 | 271.5161 | 143.5505 | 301.683 | 8.1047 | 50.6413 | 9.1515 | 238 | 45.6286 | 0 | 300.6005 | 0.039574
10458 | 880.4705 | 11.0807 | 23.2491 | 102.9403 | 49.5735 | 9.5 | 101.4725 | 5.2971 | 15.6013 | 34.5864 | 133.9041 | 18.737 | 276.9459 | 153.3213 | 312.2879 | 8.4381 | 50.9939 | 8.2361 | 221 | 52.6987 | 0 | 293.9552 | 0.0028151
10459 | 869.299 | 7.8064 | 23.0379 | 102.2908 | 46.5804 | 12.3492 | 97.2042 | 5.6473 | 14.7704 | 35.5061 | 126.1399 | 15.7834 | 251.3307 | 137.4844 | 297.9186 | 8.8426 | 52.3064 | 7.3304 | 258 | 47.7434 | 0 | 312.4828 | 0
10460 | 848.6954 | 5.2008 | 23.3094 | 104.9323 | 48.58 | 10.4505 | 95.823 | 5.4841 | 13.5602 | 37.5208 | 124.0989 | 15.1069 | 229.7262 | 127.3377 | 286.4905 | 9.1762 | 52.9723 | 6.8537 | 273 | 42.9508 | 0 | 309.7449 | 0
10461 | 835.5749 | 4.745 | 22.8817 | 103.6715 | 49.5792 | 9.5003 | 87.363 | 5.6712 | 13.3946 | 37.7163 | 111.6185 | 22.8733 | 219.4364 | 112.7896 | 272.0851 | 9.2058 | 52.5571 | 6.318 | 232 | 41.5181 | 0 | 312.088 | 0
10462 | 839.1366 | 4.7478 | 22.9817 | 102.567 | 48.5774 | 10.4526 | 89.2144 | 5.6585 | 11.4188 | 36.5447 | 102.1684 | 22.6899 | 209.9854 | 105.0307 | 261.7027 | 9.1322 | 51.9064 | 5.6354 | 233 | 39.5734 | 0 | 317.4672 | 0
10463 | 815.3855 | 4.3986 | 23.0035 | 103.6021 | 48.5808 | 10.4471 | 85.1805 | 6.4057 | 8.5708 | 35.2063 | 97.9253 | 13.9326 | 201.9029 | 100.1562 | 245.2259 | 8.9794 | 51.5419 | 5.2886 | 219 | 38.3257 | 0 | 318.5583 | 0
10464 | 806.5219 | 3.1851 | 23.1693 | 103.4272 | 49.5742 | 9.5003 | 75.2927 | 6.8275 | 6.7867 | 22.6731 | 63.2274 | 10.3492 | 58.525 | 61.11 | 159.823 | 9.0914 | 32.4438 | 5.2423 | 196 | 36.5223 | 0 | 163.0064 | 0
10465 | 812.0687 | 2.7616 | 23.2815 | 102.5896 | 48.5793 | 10.4497 | 72.9947 | 6.6647 | 9.1487 | 34.4191 | 95.1717 | 10.204 | 192.0891 | 85.9198 | 244.7355 | 9.1134 | 51.7487 | 4.7505 | 163 | 35.6934 | 0 | 317.4209 | 0
10466 | 798.1554 | 2.87 | 23.2472 | 101.9302 | 49.5828 | 9.5003 | 84.9139 | 6.013 | 7.2648 | 32.888 | 95.5712 | 10.2202 | 186.6428 | 84.3112 | 253.8777 | 9.2721 | 51.6514 | 4.2914 | 131 | 35.0099 | 0 | 324.2654 | 0
10467 | 789.3726 | 2.6601 | 23.376 | 102.2109 | 42.5775 | 16.1526 | 80.3231 | 5.6433 | 5.9756 | 32.2446 | 96.8765 | 10.1929 | 184.2016 | 82.0025 | 263.6327 | 9.2325 | 51.6452 | 3.2369 | 117 | 34.5969 | 0 | 319.8514 | 0
10468 | 785.4129 | 2.602 | 23.1902 | 102.6439 | 43.5871 | 15.1958 | 68.5433 | 5.6272 | 6.1777 | 32.3706 | 95.9035 | 11.7736 | 183.2064 | 82.2321 | 246.5509 | 9.0379 | 51.5374 | 2.8175 | 114 | 32.6537 | 0 | 317.503 | 0
10469 | 777.3512 | 2.9885 | 23.2906 | 102.3182 | 42.5785 | 16.1497 | 72.2977 | 6.3737 | 6.1023 | 32.4756 | 95.4641 | 10.8529 | 182.4925 | 83.3977 | 230.7798 | 9.0401 | 52.9935 | 2.7776 | 109 | 33.476 | 0 | 313.1633 | 0
10470 | 780.2945 | 3.8227 | 24.724 | 102.8751 | 49.5782 | 9.5018 | 68.9503 | 6.779 | 6.126 | 32.4714 | 96.6439 | 10.1866 | 181.3449 | 81.7286 | 226.2636 | 9.1531 | 55.7018 | 2.7585 | 107 | 41.6475 | 0 | 318.0158 | 0
10471 | 799.0485 | 4.1845 | 40.2295 | 100.4842 | 48.5808 | 10.4497 | 63.8009 | 6.4443 | 6.8265 | 29.328 | 95.4799 | 8.9604 | 181.8091 | 79.5118 | 223.7009 | 8.9637 | 52.0252 | 2.7662 | 104 | 33.3795 | 0 | 315.6455 | 0
10472 | 813.4981 | 3.7391 | 53.8277 | 100.6865 | 49.5801 | 9.5003 | 69.836 | 5.5092 | 5.886 | 28.945 | 96.6924 | 7.6787 | 193.0786 | 84.2145 | 220.5045 | 8.7181 | 50.1088 | 3.2688 | 109 | 39.5003 | 0 | 311.2896 | 0.035181
10473 | 822.7545 | 3.1418 | 62.4364 | 101.8257 | 47.5777 | 11.3995 | 69.9337 | 4.7141 | 6.4062 | 38.2563 | 108.3295 | 10.4483 | 205.2337 | 99.302 | 244.3987 | 8.5245 | 50.1219 | 4.7642 | 119 | 42.6188 | 0 | 305.9902 | 0.052241
10474 | 848.1708 | 2.979 | 69.3216 | 101.755 | 49.5711 | 9.5005 | 74.5495 | 4.291 | 12.4043 | 52.0647 | 114.5856 | 18.138 | 209.69 | 110.9452 | 270.8263 | 8.6115 | 50.3068 | 7.233 | 170 | 42.7653 | 0 | 309.1762 | 0.064368
10475 | 857.9047 | 3.25 | 80.0863 | 100.7879 | 48.5761 | 10.4497 | 94.393 | 4.7583 | 15.2363 | 58.6963 | 115.5706 | 22.0456 | 218.7405 | 121.0936 | 293.3012 | 8.6293 | 51.0871 | 9.2706 | 148 | 45.8117 | 0 | 310.2177 | 0.084414
10476 | 881.9075 | 4.1065 | 82.3504 | 103.0983 | 49.572 | 9.5003 | 109.4077 | 4.3809 | 15.5947 | 63.177 | 118.6846 | 15.9932 | 228.95 | 132.7045 | 292.6475 | 8.0437 | 51.9045 | 9.8498 | 154 | 42.1784 | 0 | 321.2668 | 0.078865
10477 | 899.4815 | 3.2371 | 82.0755 | 105.4592 | 49.5731 | 9.5 | 107.2488 | 3.9756 | 15.6325 | 62.2196 | 132.6057 | 11.873 | 239.5075 | 137.8974 | 297.2634 | 7.8453 | 51.4493 | 9.7079 | 170 | 42.7338 | 0 | 310.4367 | 0.12121
10478 | 909.7245 | 2.9891 | 82.0509 | 103.9619 | 48.5705 | 10.4526 | 107.402 | 4.2917 | 15.7868 | 61.4659 | 161.1933 | 11.6577 | 246.4777 | 142.2432 | 308.2279 | 7.5898 | 51.8779 | 10.2884 | 166 | 46.0259 | 0 | 305.4662 | 0.097637
10479 | 910.4151 | 4.5595 | 82.0912 | 102.8549 | 48.5788 | 10.4471 | 110.2403 | 3.4099 | 15.4785 | 57.6799 | 163.2709 | 12.5073 | 246.8159 | 145.0508 | 299.754 | 7.7123 | 52.1702 | 10.6739 | 169 | 47.2558 | 0 | 308.3942 | 0.071594
10480 | 920.0733 | 3.4506 | 75.6858 | 104.31 | 48.5757 | 10.45 | 112.9153 | 2.8957 | 15.373 | 54.4011 | 147.1354 | 10.9842 | 245.7591 | 143.0189 | 286.2418 | 7.8835 | 52.6521 | 10.4768 | 165 | 49.8534 | 0 | 316.2795 | 0.068755
10481 | 906.1488 | 5.6832 | 38.6855 | 102.7208 | 48.5754 | 10.45 | 100.118 | 3.4614 | 15.3431 | 39.2187 | 140.733 | 10.8176 | 244.2518 | 148.5987 | 303.6003 | 7.8543 | 51.9401 | 10.3466 | 175 | 48.9281 | 0 | 306.5237 | 0.026504
10482 | 902.6731 | 10.1625 | 23.5984 | 102.2594 | 48.5728 | 10.45 | 99.8832 | 4.5124 | 15.9089 | 32.2483 | 138.3875 | 15.0749 | 243.6922 | 152.5287 | 318.7639 | 8.3372 | 51.3276 | 9.8577 | 155 | 52.665 | 0 | 294.4785 | 0.0026495
10483 | 906.5491 | 11.6421 | 22.9105 | 103.5335 | 47.5726 | 11.3997 | 93.3894 | 5.4035 | 15.221 | 35.3664 | 139.8289 | 23.26 | 244.1001 | 149.5908 | 324.4491 | 8.6608 | 51.1811 | 8.8325 | 144 | 50.4078 | 0 | 310.459 | 0
10484 | 911.7933 | 11.1534 | 23.1471 | 104.5947 | 47.5708 | 11.4032 | 102.6705 | 6.2952 | 11.0445 | 37.0065 | 133.9119 | 18.7934 | 234.1671 | 134.1524 | 298.5543 | 8.9921 | 51.6024 | 8.0999 | 135 | 47.4819 | 0 | 313.2821 | 0
10485 | 881.0477 | 6.6254 | 22.9713 | 103.8704 | 47.579 | 11.3968 | 104.5123 | 6.4128 | 8.9909 | 35.2472 | 103.8123 | 11.6458 | 224.6384 | 123.3883 | 283.0969 | 9.1353 | 51.5295 | 7.1262 | 130 | 42.5209 | 0 | 309.5524 | 0
10486 | 859.9395 | 4.4725 | 22.9482 | 103.4755 | 47.5767 | 11.4 | 91.4191 | 5.6463 | 7.5811 | 33.9338 | 101.8878 | 9.3986 | 211.3477 | 117.4047 | 271.9335 | 9.1341 | 52.4536 | 5.8819 | 130 | 38.5432 | 0 | 307.6356 | 0
10487 | 847.2424 | 3.8871 | 23.1257 | 102.6961 | 48.5808 | 10.4503 | 83.084 | 5.3497 | 6.8905 | 32.4146 | 100.1962 | 10.3293 | 201.4872 | 109.4112 | 246.2566 | 9.175 | 51.9264 | 5.1724 | 126 | 35.9187 | 0 | 314.7042 | 0
10488 | 839.0723 | 2.8052 | 23.0232 | 102.1499 | 46.5784 | 12.3495 | 92.6573 | 5.4739 | 6.5315 | 20.8116 | 65.8755 | 10.0305 | 57.9829 | 63.8805 | 157.0702 | 8.8929 | 32.5274 | 4.8458 | 124 | 35.0532 | 0 | 157.3958 | 0
10489 | 826.2121 | 2.431 | 23.0667 | 102.5368 | 48.5793 | 10.4505 | 81.1879 | 5.8929 | 6.5418 | 32.3424 | 98.4234 | 9.1864 | 187.6443 | 86.871 | 225.5621 | 9.0851 | 51.4364 | 4.54 | 119 | 33.2571 | 0 | 311.3601 | 0
10490 | 832.153 | 2.4338 | 23.1869 | 102.0456 | 48.5794 | 10.45 | 78.8237 | 6.97 | 6.4968 | 32.5918 | 97.2198 | 9.1048 | 184.6305 | 86.6125 | 228.0408 | 9.2106 | 50.9731 | 3.69 | 106 | 31.95 | 0 | 313.6052 | 0
10491 | 812.973 | 2.4858 | 23.2112 | 101.7374 | 48.5804 | 10.45 | 81.1378 | 7.044 | 6.5815 | 32.1559 | 96.4713 | 9.0627 | 180.2831 | 93.3456 | 236.1043 | 9.1167 | 50.966 | 3.4346 | 103 | 31.6838 | 0 | 314.5934 | 0
10492 | 803.0881 | 2.6269 | 23.6663 | 101.2894 | 48.5777 | 10.45 | 72.4043 | 6.0011 | 6.6872 | 32.085 | 95.4872 | 8.8998 | 176.5597 | 94.3642 | 235.5242 | 9.2291 | 50.7534 | 3.3228 | 103 | 32.1816 | 0 | 313.7708 | 0
10493 | 801.4749 | 3.0889 | 25.0356 | 104.4444 | 49.5803 | 9.5003 | 63.6729 | 5.6298 | 6.6747 | 32.5225 | 95.287 | 8.8612 | 179.2909 | 86.0325 | 227.9973 | 8.9988 | 52.531 | 3.2977 | 103 | 32.283 | 0 | 363.0671 | 0
10494 | 812.6919 | 3.9828 | 34.4504 | 104.8539 | 48.5777 | 10.4497 | 72.3421 | 5.7049 | 6.7603 | 38.9462 | 96.8334 | 9.7216 | 191.6884 | 92.6724 | 232.2142 | 9.0089 | 55.0141 | 3.4175 | 105 | 32.2985 | 0 | 390.4683 | 0
10495 | 855.8718 | 8.1963 | 43.4924 | 108.855 | 46.5776 | 12.3495 | 91.4373 | 6.5512 | 8.993 | 54.6859 | 114.2221 | 14.3508 | 232.9882 | 159.5622 | 254.567 | 11.6847 | 51.4919 | 4.2734 | 183 | 38.4962 | 0 | 416.6186 | 0
10496 | 917.4451 | 15.4306 | 67.7984 | 112.6595 | 40.8202 | 18.0484 | 106.0515 | 7.4177 | 14.375 | 83.9426 | 148.6469 | 31.3923 | 291.6017 | 217.6138 | 324.9232 | 26.1171 | 53.5239 | 10.2044 | 289 | 63.175 | 0 | 472.0121 | 0.029843
10497 | 1005.4526 | 14.269 | 92.4631 | 122.2164 | 36.7138 | 21.8489 | 128.3549 | 7.8473 | 18.6182 | 100.8247 | 185.2698 | 40.472 | 340.1151 | 275.562 | 426.5229 | 34.9721 | 65.5423 | 15.2304 | 276 | 76.3618 | 0 | 533.6443 | 0.041823
10498 | 1099.2714 | 10.6379 | 100.6618 | 128.7869 | 35.5796 | 22.7997 | 151.637 | 7.6973 | 19.8767 | 105.5599 | 200.888 | 41.7218 | 379.2791 | 324.2822 | 508.1059 | 40.4374 | 77.1456 | 19.3086 | 336 | 80.2828 | 0 | 576.7559 | 0.063437
10499 | 1147.7998 | 9.545 | 100.7363 | 133.1875 | 38.5753 | 19.9508 | 151.8378 | 8.4173 | 20.9647 | 98.876 | 202.8722 | 42.2572 | 391.9836 | 339.4958 | 588.5896 | 41.4306 | 85.1145 | 19.2103 | 355 | 77.3784 | 0 | 614.7795 | 0.081075
10500 | 1181.0506 | 6.7235 | 103.9436 | 131.6506 | 40.5707 | 18.0555 | 153.7707 | 9.14 | 21.049 | 102.6615 | 203.709 | 43.3558 | 396.8052 | 351.1375 | 589.8997 | 40.9182 | 86.0994 | 18.4849 | 333 | 76.852 | 0 | 620.5442 | 0.15648
10501 | 1145.0839 | 4.9314 | 107.1947 | 129.6144 | 36.5817 | 21.8439 | 162.4267 | 10.2243 | 20.3495 | 102.9254 | 204.8235 | 40.5222 | 391.2883 | 347.2052 | 581.1959 | 41.9997 | 81.5231 | 17.984 | 322 | 74.3828 | 0 | 626.4682 | 0.11004
10502 | 1160.7951 | 4.4286 | 105.2059 | 140.2628 | 36.579 | 21.85 | 159.9415 | 10.9277 | 19.0095 | 100.8435 | 220.3621 | 38.149 | 399.0241 | 353.5956 | 567.9205 | 42.7981 | 80.2543 | 18.5506 | 283 | 75.2156 | 0 | 650.6084 | 0.12194
10503 | 1166.1087 | 4.6056 | 107.5232 | 147.4956 | 38.5776 | 19.9505 | 162.8766 | 9.863 | 18.4345 | 99.6663 | 227.2432 | 34.5454 | 403.0854 | 351.1993 | 560.4231 | 41.6343 | 80.4481 | 19.1354 | 295 | 75.5237 | 0 | 636.1591 | 0.094225
10504 | 1135.5649 | 4.7732 | 103.3101 | 150.2932 | 35.5722 | 22.7992 | 164.1019 | 8.8973 | 18.1639 | 101.5466 | 208.3999 | 29.9588 | 396.4735 | 345.6047 | 548.0339 | 42.1074 | 82.27 | 19.8719 | 267 | 81.5968 | 0 | 597.5418 | 0.061699
10505 | 1083.01 | 4.583 | 97.2358 | 147.6497 | 39.5691 | 19.0011 | 150.768 | 7.8607 | 17.5927 | 94.5164 | 193.2689 | 27.3542 | 374.4349 | 319.8154 | 490.497 | 33.5058 | 78.4243 | 19.336 | 240 | 71.1138 | 0 | 557.7131 | 0.025409
10506 | 1027.2654 | 5.7468 | 92.8679 | 128.8706 | 45.5727 | 13.3016 | 131.1349 | 6.6966 | 16.5814 | 83.6669 | 180.3915 | 26.1763 | 334.9272 | 249.8425 | 437.5836 | 18.1009 | 72.2897 | 18.9848 | 202 | 67.9817 | 0 | 438.4797 | 0.0057914
10507 | 995.0935 | 6.2483 | 84.7157 | 113.6888 | 48.5771 | 10.4508 | 129.9374 | 5.8253 | 14.3095 | 65.3575 | 156.75 | 28.0116 | 284.5467 | 170.7831 | 391.6217 | 12.1053 | 69.1723 | 17.1135 | 203 | 58.6779 | 0 | 399.7224 | 0
10508 | 959.6324 | 5.3471 | 74.2265 | 109.6739 | 48.5786 | 10.45 | 113.9955 | 5.1502 | 10.0312 | 54.8136 | 144.7944 | 28.5647 | 253.3092 | 139.0812 | 338.004 | 10.258 | 62.1858 | 11.1644 | 189 | 52.2923 | 0 | 346.1757 | 0
10509 | 908.3214 | 4.7841 | 41.3425 | 104.5868 | 47.5768 | 11.3997 | 105.7672 | 5.2684 | 8.4107 | 49.7162 | 135.5623 | 27.6649 | 235.9768 | 126.7497 | 297.1463 | 9.6505 | 55.091 | 8.3468 | 176 | 43.3181 | 0 | 332.2168 | 0
10510 | 877.6803 | 4.7066 | 30.3254 | 99.7642 | 47.5798 | 11.4 | 108.7381 | 5.2653 | 7.2952 | 41.2536 | 119.4008 | 24.7776 | 218.6874 | 114.8115 | 277.3526 | 9.6283 | 52.0537 | 7.3892 | 172 | 39.4881 | 0 | 325.2738 | 0
10511 | 855.8377 | 4.1917 | 30.1518 | 96.8336 | 49.586 | 9.5005 | 92.21 | 5.2143 | 6.4672 | 36.3511 | 100.2793 | 22.5122 | 209.7426 | 102.274 | 261.9217 | 9.6303 | 51.5404 | 6.2312 | 153 | 37.3841 | 0 | 317.9256 | 0
10512 | 845.6866 | 8.0723 | 29.9548 | 96.6523 | 48.5873 | 10.4497 | 82.7565 | 5.2123 | 6.2189 | 22.4886 | 61.4129 | 19.5342 | 60.59 | 62.1181 | 166.5143 | 9.6584 | 32.4225 | 5.2973 | 127 | 35.2923 | 0 | 158.961 | 0
10513 | 832.2306 | 7.6169 | 29.7882 | 96.4096 | 49.5874 | 9.5003 | 89.4492 | 5.3897 | 6.3052 | 32.3466 | 93.4911 | 12.772 | 196.5795 | 90.5187 | 221.14 | 9.4365 | 51.5822 | 4.8385 | 122 | 33.3154 | 0 | 311.6359 | 0
10514 | 834.8502 | 3.6607 | 29.8188 | 96.0721 | 48.586 | 10.4497 | 86.2315 | 4.9156 | 6.2943 | 31.5596 | 96.0258 | 10.4829 | 198.5526 | 87.3227 | 215.39 | 9.4885 | 51.2792 | 4.49 | 121 | 32.5471 | 0 | 313.3126 | 0
10515 | 822.1475 | 2.5235 | 29.7858 | 96.7061 | 48.5875 | 10.45 | 77.6049 | 4.5078 | 6.3417 | 31.4197 | 98.2067 | 10.3662 | 193.9216 | 84.256 | 225.0682 | 9.4944 | 51.7862 | 4.3347 | 123 | 32.121 | 0 | 303.1243 | 0
10516 | 807.6176 | 2.4531 | 29.9095 | 96.1692 | 48.587 | 10.45 | 70.2207 | 4.4656 | 6.2625 | 31.4112 | 99.0416 | 10.2581 | 187.3204 | 84.3306 | 229.0282 | 9.5027 | 51.9366 | 4.3174 | 114 | 32.0718 | 0 | 295.8029 | 0
10517 | 815.3538 | 3.0278 | 29.7514 | 96.6813 | 49.5863 | 9.5003 | 78.1766 | 4.7467 | 6.3275 | 31.5972 | 96.8884 | 10.2291 | 190.2217 | 86.1655 | 222.8707 | 9.5042 | 53.0465 | 4.3168 | 109 | 32.8015 | 0 | 321.2558 | 0
10518 | 819.8826 | 4.144 | 51.3819 | 97.0814 | 49.5862 | 9.5 | 87.8279 | 4.8394 | 6.4488 | 40.0413 | 94.5508 | 14.2121 | 200.6537 | 96.4134 | 220.5155 | 9.2867 | 55.1371 | 4.3082 | 127 | 32.3033 | 0 | 369.3856 | 0
10519 | 871.7736 | 8.6435 | 64.6821 | 98.1052 | 44.5816 | 14.2487 | 91.6167 | 4.9442 | 10.4647 | 57.494 | 110.3109 | 17.6009 | 236.3407 | 162.2519 | 243.5793 | 11.6747 | 51.3735 | 5.7051 | 165 | 41.3399 | 0 | 400.8056 | 0
10520 | 941.0162 | 15.4755 | 81.0735 | 102.7715 | 40.5764 | 18.0489 | 112.6307 | 5.8893 | 13.9678 | 71.5419 | 157.0431 | 32.5291 | 295.6706 | 225.1806 | 332.6169 | 26.3237 | 53.7236 | 9.9927 | 252 | 71.0243 | 0 | 431.991 | 0.02055
10521 | 1031.1374 | 16.4502 | 94.1267 | 119.183 | 38.5772 | 19.9495 | 144.5661 | 7.2281 | 16.4787 | 86.2057 | 178.4926 | 41.783 | 346.3648 | 277.9526 | 452.8375 | 35.5144 | 62.9166 | 17.7574 | 295 | 83.6892 | 0 | 492.9629 | 0.057057
10522 | 1106.0686 | 10.6153 | 98.973 | 132.0587 | 40.5772 | 18.0505 | 163.8317 | 8.1157 | 17.3492 | 80.7305 | 183.9605 | 43.1585 | 387.0709 | 316.9615 | 541.6178 | 40.6086 | 73.9672 | 19.1337 | 382 | 77.6297 | 0 | 556.4384 | 0.066612
10523 | 1128.2264 | 8.027 | 101.0786 | 136.6519 | 40.5755 | 18.05 | 163.6037 | 8.639 | 19.1902 | 83.4519 | 183.3201 | 43.7566 | 406.9786 | 336.3552 | 577.5066 | 42.1636 | 86.1842 | 18.7535 | 342 | 79.2314 | 0 | 574.8905 | 0.057416
10524 | 1148.8738 | 8.1393 | 102.2985 | 140.0223 | 38.5746 | 19.9495 | 168.7708 | 9.139 | 19.8327 | 89.3918 | 177.4841 | 44.5001 | 418.8834 | 354.9907 | 576.3229 | 41.9442 | 88.6341 | 18.9862 | 301 | 85.3007 | 0 | 577.1084 | 0.064301
10525 | 1168.737 | 7.966 | 103.692 | 139.9736 | 37.5795 | 20.8997 | 171.929 | 9.1964 | 20.2257 | 100.1501 | 179.9593 | 44.9536 | 424.5119 | 357.3767 | 582.6531 | 44.2616 | 81.9335 | 19.0912 | 366 | 81.7777 | 0 | 584.8738 | 0.048765
10526 | 1158.135 | 6.2324 | 104.736 | 148.3639 | 39.5817 | 19.0005 | 170.4266 | 8.4943 | 21.7803 | 108.4225 | 185.5138 | 42.3559 | 430.6031 | 354.9381 | 582.4267 | 45.9912 | 81.587 | 19.5037 | 310 | 77.0651 | 0 | 589.4241 | 0.057409
10527 | 1158.8687 | 4.9742 | 103.0786 | 148.7169 | 38.5799 | 19.9497 | 171.8265 | 8.6536 | 22.8603 | 111.9709 | 186.2635 | 35.7215 | 431.7497 | 349.7987 | 571.0157 | 44.4717 | 81.1448 | 20.2116 | 307 | 75.7296 | 0 | 579.1512 | 0.03654
10528 | 1149.6713 | 4.7791 | 101.3813 | 141.1939 | 38.5748 | 19.95 | 166.2758 | 8.7557 | 22.8407 | 106.1712 | 185.5374 | 29.5614 | 416.5753 | 336.5788 | 557.9485 | 43.2591 | 79.4821 | 20.2855 | 291 | 75.5082 | 0 | 566.4294 | 0.02328
10529 | 1111.2668 | 5.6796 | 89.946 | 134.7761 | 38.5748 | 19.95 | 151.8138 | 7.1266 | 22.4757 | 103.0756 | 184.8788 | 31.9905 | 390.615 | 310.5341 | 495.3184 | 36.8197 | 78.9194 | 19.8011 | 270 | 62.1437 | 0 | 519.4995 | 0.0092596
10530 | 1027.8382 | 6.1276 | 85.6935 | 121.4212 | 46.5767 | 12.3521 | 138.3884 | 5.2229 | 21.9654 | 88.0435 | 186.7137 | 35.338 | 351.9458 | 250.1236 | 418.5439 | 27.658 | 72.1772 | 19.0024 | 225 | 56.2232 | 0 | 368.1981 | 0.004125
10531 | 974.7006 | 6.0392 | 86.4606 | 107.1754 | 49.5743 | 9.5034 | 127.0048 | 4.7587 | 16.1006 | 66.5054 | 170.7619 | 33.2784 | 304.0494 | 181.6355 | 364.5171 | 15.3312 | 66.3795 | 16.0509 | 219 | 49.3527 | 0 | 331.207 | 0
10532 | 940.0147 | 5.5951 | 71.6772 | 101.2381 | 48.5828 | 10.4471 | 110.9177 | 4.6509 | 9.378 | 58.204 | 154.9168 | 17.4734 | 265.3419 | 150.1891 | 315.6638 | 11.0437 | 58.7792 | 9.5701 | 192 | 44.1442 | 0 | 291.1933 | 0
10533 | 909.1995 | 4.7539 | 40.5175 | 97.2629 | 48.5774 | 10.45 | 95.7543 | 4.8927 | 7.0295 | 55.1967 | 140.7793 | 11.2165 | 239.6007 | 138.789 | 271.961 | 10.0717 | 53.0017 | 6.5223 | 174 | 42.3513 | 0 | 266.8816 | 0
10534 | 883.2521 | 4.4077 | 31.1402 | 97.7132 | 49.5789 | 9.5003 | 86.971 | 5.018 | 6.3843 | 45.9713 | 120.9412 | 12.964 | 221.1996 | 129.6515 | 248.9073 | 9.8097 | 51.8453 | 6.2489 | 175 | 38.448 | 0 | 268.0271 | 0
10535 | 869.8188 | 3.8972 | 30.9755 | 97.0947 | 48.5861 | 10.4497 | 83.3529 | 5.253 | 6.2057 | 38.8884 | 104.1085 | 11.1843 | 211.078 | 122.4539 | 249.357 | 9.8213 | 52.0037 | 5.8958 | 141 | 35.4995 | 0 | 270.7206 | 0
10536 | 845.5865 | 3.1572 | 30.8517 | 96.5298 | 48.5857 | 10.45 | 96.707 | 5.1755 | 6.2358 | 24.0133 | 65.5785 | 9.9158 | 62.0521 | 74.6098 | 170.5109 | 9.8097 | 32.6983 | 5.3396 | 127 | 33.4428 | 0 | 134.2306 | 0
10537 | 832.2444 | 2.7896 | 30.8808 | 96.6233 | 48.5831 | 10.45 | 100.8118 | 5.0579 | 6.2753 | 35.1877 | 98.0608 | 9.7818 | 203.5985 | 106.2631 | 244.0054 | 9.7804 | 51.7471 | 4.7296 | 121 | 28.6153 | 0 | 257.2016 | 0
10538 | 830.8527 | 2.7612 | 30.8753 | 96.0752 | 48.583 | 10.45 | 90.7025 | 4.8224 | 6.3656 | 34.9997 | 97.9691 | 9.1114 | 199.1142 | 104.9231 | 223.5506 | 9.5319 | 51.7641 | 4.3967 | 130 | 27.517 | 0 | 254.7444 | 0
10539 | 824.1873 | 2.6767 | 30.645 | 95.827 | 48.5848 | 10.45 | 79.5283 | 4.6616 | 6.5115 | 35.231 | 97.5275 | 8.8128 | 195.8753 | 103.3887 | 222.3847 | 9.4675 | 51.8606 | 3.8552 | 128 | 27.2079 | 0 | 255.0301 | 0
10540 | 818.8531 | 2.5142 | 30.5195 | 96.5375 | 47.5865 | 11.3997 | 82.3174 | 4.4447 | 6.4263 | 34.9957 | 96.7167 | 8.7763 | 191.7725 | 102.3947 | 218.4576 | 9.4301 | 51.7412 | 3.1874 | 120 | 25.6022 | 0 | 256.8363 | 0
10541 | 815.2766 | 3.0905 | 30.7286 | 96.2551 | 48.5827 | 10.4503 | 84.3532 | 4.4036 | 6.404 | 35.1608 | 96.3793 | 8.8111 | 192.9846 | 102.1006 | 211.671 | 9.3675 | 53.1637 | 2.9684 | 108 | 28.5153 | 0 | 279.8899 | 0
10542 | 824.7189 | 4.2085 | 51.5744 | 97.1953 | 49.5823 | 9.5003 | 80.804 | 5.066 | 7.2146 | 48.3399 | 98.5414 | 9.9547 | 204.0427 | 109.1833 | 212.5862 | 9.3737 | 55.2858 | 3.006 | 110 | 26.5042 | 0 | 329.1275 | 0
10543 | 872.9139 | 7.1333 | 65.7327 | 99.0703 | 47.5791 | 11.3995 | 96.3363 | 5.6916 | 8.6963 | 60.9798 | 108.0781 | 14.3145 | 242.1971 | 163.2418 | 226.3954 | 11.2977 | 51.553 | 5.5934 | 211 | 29.9355 | 0 | 369.5859 | 0
10544 | 913.9581 | 10.1148 | 81.1537 | 102.5308 | 41.5816 | 17.0984 | 122.0254 | 6.5832 | 10.8625 | 81.1371 | 148.1307 | 28.4161 | 298.7687 | 219.4419 | 303.1781 | 25.1284 | 54.2372 | 7.9867 | 268 | 57.601 | 0 | 394.9979 | 0.16625
10545 | 1005.5175 | 11.9959 | 94.2024 | 118.9677 | 40.5767 | 18.0497 | 139.0874 | 7.9929 | 17.0591 | 91.7525 | 173.5432 | 33.5494 | 347.8309 | 268.3069 | 412.8806 | 35.6407 | 67.0344 | 13.018 | 295 | 67.1779 | 0 | 462.8055 | 0.17761
10546 | 1079.7309 | 12.4978 | 101.5586 | 131.9815 | 40.5735 | 18.05 | 141.9575 | 8.2922 | 19.5138 | 92.43 | 175.743 | 33.3747 | 381.1553 | 306.0379 | 496.6152 | 39.5816 | 95.3162 | 15.8778 | 370 | 65.0573 | 0 | 523.9567 | 0.2637
10547 | 1130.811 | 11.9117 | 103.1151 | 140.665 | 37.573 | 20.8992 | 153.3989 | 7.4572 | 19.8522 | 93.4947 | 180.1499 | 37.7406 | 413.1556 | 331.1551 | 545.5327 | 40.5405 | 107.698 | 16.6433 | 330 | 64.5647 | 0 | 539.6997 | 0.25556
10548 | 1164.1453 | 11.754 | 105.4886 | 143.5281 | 36.5679 | 21.8558 | 163.0158 | 6.9124 | 19.725 | 95.9704 | 180.4661 | 37.7969 | 412.5271 | 349.7328 | 545.3548 | 38.6634 | 108.7297 | 17.3251 | 338 | 63.8387 | 0 | 567.0501 | 0.28418
10549 | 1149.3905 | 15.9282 | 105.8565 | 142.6985 | 39.5808 | 18.9947 | 161.4284 | 7.2469 | 17.6692 | 92.4688 | 181.5633 | 38.6588 | 404.3345 | 348.2385 | 530.7271 | 38.8637 | 104.905 | 18.1328 | 341 | 57.0967 | 0 | 573.8974 | 0.31403
10550 | 1157.3479 | 14.2269 | 106.6536 | 139.1505 | 39.574 | 19 | 161.3464 | 7.2168 | 16.4672 | 91.2134 | 199.8083 | 38.2443 | 418.0267 | 346.1197 | 527.124 | 40.4486 | 105.2058 | 18.6779 | 292 | 59.7624 | 0 | 556.3077 | 0.30525
10551 | 1160.4975 | 8.4944 | 107.5647 | 140.3318 | 39.5734 | 19 | 162.6271 | 7.0436 | 16.7013 | 76.4908 | 209.8684 | 38.3802 | 435.9651 | 350.7449 | 519.9392 | 40.1507 | 106.226 | 18.9468 | 278 | 61.767 | 0 | 548.6416 | 0.29766
10552 | 1161.5308 | 10.2898 | 102.4614 | 136.3647 | 38.5698 | 19.9497 | 158.7793 | 6.0556 | 16.4645 | 76.0052 | 204.2199 | 37.5712 | 421.0133 | 343.4828 | 512.8065 | 38.5735 | 104.8089 | 19.171 | 262 | 64.9107 | 0 | 550.6209 | 0.15054
10553 | 1122.4302 | 12.0028 | 91.4563 | 129.3802 | 45.5714 | 13.3018 | 147.7218 | 5.4234 | 15.7697 | 78.977 | 208.0282 | 36.929 | 387.4206 | 321.6865 | 466.9005 | 32.4694 | 105.4841 | 19.0723 | 261 | 55.5495 | 0 | 502.8094 | 0.12914
10554 | 1081.8032 | 12.9293 | 81.6224 | 117.3647 | 46.5765 | 12.3503 | 132.1517 | 5.7882 | 15.124 | 78.1372 | 194.5288 | 34.9 | 347.3687 | 256.8289 | 395.7064 | 19.0293 | 98.2327 | 18.4409 | 219 | 55.7741 | 0 | 373.146 | 0.022624
10555 | 1019.5318 | 10.6445 | 85.019 | 108.9673 | 48.5779 | 10.4534 | 125.4067 | 6.3367 | 15.3183 | 63.4337 | 170.6899 | 30.8321 | 299.5434 | 187.9511 | 358.608 | 13.4602 | 92.3296 | 15.8933 | 215 | 48.4547 | 0 | 361.9676 | 0
10556 | 993.9184 | 6.7628 | 78.1866 | 106.142 | 47.5831 | 11.3968 | 103.128 | 6.3356 | 13.0233 | 56.0937 | 148.9363 | 21.924 | 267.3298 | 149.0419 | 338.7821 | 11.715 | 86.2159 | 10.0134 | 193 | 45.22 | 0 | 309.3844 | 0
10557 | 958.514 | 9.6503 | 67.078 | 100.2128 | 49.5805 | 9.5005 | 90.8627 | 5.3984 | 10.9737 | 47.8889 | 128.6774 | 16.9854 | 244.7027 | 132.5502 | 310.0387 | 10.471 | 82.2393 | 7.2817 | 174 | 41.9679 | 0 | 291.2773 | 0
10558 | 928.9064 | 11.7445 | 64.778 | 97.2746 | 48.5812 | 10.4497 | 92.6762 | 5.0224 | 9.3351 | 35.7701 | 106.9363 | 13.5575 | 225.608 | 121.2597 | 264.6465 | 9.9678 | 80.3298 | 5.6132 | 173 | 37.0208 | 0 | 277.928 | 0
10559 | 919.3729 | 11.2523 | 64.1841 | 97.2599 | 48.5831 | 10.45 | 93.6251 | 4.3376 | 6.7265 | 30.9188 | 88.3157 | 11.5008 | 212.5232 | 107.118 | 245.9548 | 9.9998 | 79.9474 | 5.227 | 143 | 30.312 | 0 | 285.3525 | 0
10560 | 896.2911 | 8.9738 | 63.9214 | 97.076 | 49.5826 | 9.5029 | 84.8243 | 4.2122 | 5.8498 | 19.8452 | 55.2589 | 11.3777 | 60.9692 | 65.0434 | 163.0458 | 10.1036 | 50.3927 | 5.2717 | 130 | 27.5462 | 0 | 143.007 | 0
10561 | 876.8805 | 4.4625 | 63.9262 | 95.3926 | 48.5849 | 10.4471 | 81.2778 | 4.2068 | 5.8157 | 30.5099 | 84.4681 | 11.2215 | 196.6401 | 91.7809 | 234.4262 | 10.0843 | 80.2018 | 4.6957 | 118 | 25.9816 | 0 | 283.9735 | 0
10562 | 861.5575 | 2.6362 | 63.8974 | 95.7183 | 48.5852 | 10.45 | 81.8882 | 4.462 | 5.9175 | 30.2108 | 84.3572 | 11.1195 | 192.751 | 86.5033 | 228.0033 | 10.1339 | 80.1298 | 4.4408 | 117 | 25.9013 | 0 | 280.5274 | 0
10563 | 832.3546 | 2.5948 | 65.0053 | 96.4813 | 47.5842 | 11.4029 | 77.6098 | 4.8457 | 5.5802 | 30.2454 | 85.5705 | 11.7213 | 189.2245 | 85.8222 | 232.7694 | 9.9004 | 80.2591 | 4.4272 | 117 | 25.0518 | 0 | 282.1605 | 0
10564 | 830.4278 | 2.6854 | 65.7662 | 96.0086 | 48.5886 | 10.4471 | 69.2601 | 5.1896 | 5.43 | 30.4266 | 85.0817 | 11.3678 | 188.7667 | 84.9415 | 225.5171 | 9.8186 | 80.4061 | 4.4094 | 109 | 24.9532 | 0 | 289.1754 | 0
10565 | 830.5316 | 3.0904 | 66.2058 | 97.5577 | 49.5986 | 9.4871 | 75.2761 | 5.1371 | 5.774 | 30.4552 | 84.4687 | 11.1215 | 193.3522 | 84.6567 | 215.2849 | 10.008 | 81.9569 | 4.4354 | 111 | 25.2023 | 0 | 302.2534 | 0
10566 | 850.6516 | 4.0165 | 65.9303 | 96.0916 | 48.567 | 10.4629 | 86.4298 | 5.0672 | 6.4468 | 44.2168 | 85.6664 | 14.0031 | 203.5341 | 95.9176 | 215.0636 | 10.0547 | 84.1858 | 4.4124 | 112 | 25.6173 | 0 | 345.8022 | 0
10567 | 878.8635 | 6.5777 | 68.0563 | 99.6723 | 46.5803 | 12.3495 | 91.8798 | 4.8006 | 7.9845 | 57.0894 | 94.4373 | 16.9895 | 239.3738 | 164.3656 | 224.9789 | 11.9381 | 80.2777 | 4.9466 | 184 | 33.3848 | 0 | 390.9967 | 0
10568 | 931.6276 | 12.5128 | 82.6769 | 102.8587 | 38.5825 | 19.9479 | 109.4114 | 5.2434 | 12.6859 | 81.0671 | 138.6982 | 31.0793 | 299.8177 | 221.3714 | 305.9648 | 27.2024 | 83.7765 | 7.5827 | 295 | 61.1721 | 0 | 422.5595 | 0.01709
10569 | 1032.9092 | 13.7644 | 96.9965 | 115.2825 | 38.5789 | 19.95 | 130.6195 | 5.9519 | 15.1155 | 91.2441 | 165.4767 | 38.2923 | 369.819 | 270.5242 | 425.8208 | 34.1519 | 92.9444 | 13.3914 | 310 | 66.701 | 0 | 496.2787 | 0.045737
10570 | 1106.1146 | 13.5329 | 102.5632 | 124.8147 | 36.5751 | 21.8495 | 146.1593 | 6.3463 | 15.6593 | 93.4064 | 180.9428 | 37.0909 | 400.0565 | 303.1627 | 492.7806 | 37.1304 | 95.7736 | 18.1593 | 353 | 64.667 | 0 | 560.2272 | 0.06664
10571 | 1134.5582 | 12.0032 | 102.3549 | 124.8395 | 36.5712 | 21.85 | 149.4947 | 6.1733 | 15.965 | 94.9505 | 193.3567 | 36.8924 | 417.7136 | 326.6369 | 551.3617 | 38.629 | 107.7713 | 18.0889 | 398 | 65.2414 | 0 | 587.7391 | 0.049869
10572 | 1178.3429 | 6.684 | 106.1188 | 122.329 | 36.5716 | 21.85 | 155.614 | 5.569 | 16.1288 | 94.2831 | 191.6011 | 37.6888 | 415.4014 | 337.2416 | 576.215 | 40.0879 | 113.9887 | 17.6264 | 344 | 69.9627 | 0 | 607.1714 | 0.047382
10573 | 1163.7903 | 5.1294 | 106.5469 | 123.6332 | 40.5752 | 18.0511 | 159.9631 | 6.0854 | 14.698 | 85.964 | 190.0745 | 39.2954 | 401.8274 | 338.5084 | 563.7089 | 40.4826 | 113.8849 | 17.984 | 352 | 68.3619 | 0 | 591.4018 | 0.055134
10574 | 1146.3801 | 9.5064 | 107.4923 | 133.1645 | 39.5756 | 18.9997 | 165.5688 | 7.1377 | 14.335 | 82.8564 | 194.3798 | 39.5126 | 411.3027 | 338.3786 | 557.4148 | 40.8131 | 117.0266 | 18.5952 | 315 | 72.6247 | 0 | 607.1145 | 0.030417
10575 | 1149.249 | 9.4559 | 108.6343 | 135.8604 | 40.5679 | 18.0503 | 166.8413 | 7.6408 | 13.775 | 96.8378 | 198.9565 | 34.7192 | 416.1794 | 339.3066 | 558.9269 | 39.3432 | 111.1503 | 18.6062 | 291 | 73.5802 | 0 | 590.8437 | 0.03719
10576 | 1149.402 | 6.5876 | 102.3304 | 129.7035 | 38.5704 | 19.9495 | 161.261 | 7.2632 | 12.9323 | 103.3701 | 196.7739 | 30.2006 | 404.0303 | 332.3935 | 535.8578 | 38.4481 | 102.7962 | 18.6022 | 274 | 72.6786 | 0 | 566.4871 | 0.044115
10577 | 1121.3634 | 5.4543 | 91.2345 | 125.2545 | 45.5711 | 13.3018 | 152.3877 | 5.6699 | 12.4635 | 100.6532 | 202.3017 | 26.5247 | 389.3278 | 303.2468 | 476.4946 | 30.4477 | 99.4075 | 18.2545 | 250 | 58.6445 | 0 | 518.687 | 0.016157
10578 | 1061.7403 | 7.1902 | 84.9803 | 113.8633 | 49.5731 | 9.5011 | 138.9454 | 4.8985 | 12.6547 | 85.3603 | 195.2412 | 25.6339 | 351.7476 | 224.4628 | 388.4405 | 14.9693 | 99.4098 | 17.6777 | 226 | 55.4092 | 0 | 384.4465 | 0.0026034
10579 | 995.0638 | 13.4991 | 80.5812 | 104.1061 | 45.5791 | 13.2989 | 127.2417 | 5.1079 | 11.4329 | 62.0344 | 168.2806 | 26.7085 | 296.7765 | 147.1472 | 332.8326 | 10.0781 | 96.8446 | 15.1353 | 209 | 46.3813 | 0 | 351.8324 | 0
10580 | 950.821 | 9.9757 | 75.2647 | 97.7795 | 49.5712 | 9.5037 | 104.3102 | 4.9801 | 8.8035 | 52.4026 | 139.3927 | 15.5497 | 257.0671 | 120.5093 | 302.0177 | 9.3573 | 70.7438 | 9.2099 | 181 | 41.1351 | 0 | 310.3442 | 0
10581 | 917.1276 | 5.4965 | 44.5851 | 92.7657 | 48.5778 | 10.45 | 91.8803 | 4.7028 | 7.163 | 48.6152 | 123.4793 | 9.749 | 237.5827 | 108.3299 | 291.3874 | 8.8853 | 56.7033 | 6.6486 | 171 | 37.2025 | 0 | 275.2703 | 0
10582 | 896.1353 | 4.9629 | 31.5537 | 91.8985 | 48.5872 | 10.4471 | 95.3521 | 4.4 | 6.742 | 40.8954 | 105.858 | 9.4702 | 217.6934 | 100.0818 | 267.7451 | 8.8093 | 53.5096 | 5.8184 | 171 | 34.3247 | 0 | 274.3959 | 0
10583 | 867.0769 | 4.1217 | 30.3131 | 92.3273 | 48.5851 | 10.45 | 100.1104 | 3.7836 | 6.55 | 35.0595 | 84.704 | 9.3441 | 205.6397 | 95.8337 | 253.1921 | 8.5971 | 52.549 | 5.3218 | 154 | 33.7116 | 0 | 274.0354 | 0
10584 | 847.8343 | 2.8888 | 30.3164 | 90.6436 | 47.5806 | 11.3997 | 94.8977 | 3.4431 | 6.3252 | 21.3065 | 51.2131 | 9.3286 | 59.4276 | 62.4249 | 166.5126 | 8.6489 | 32.8577 | 4.8124 | 136 | 32.7703 | 0 | 138.2262 | 0
10585 | 846.011 | 2.6619 | 30.2147 | 89.7805 | 49.5841 | 9.5005 | 97.5725 | 3.829 | 6.3102 | 30.8347 | 78.4975 | 9.2815 | 191.2627 | 88.5563 | 235.2588 | 8.782 | 52.4121 | 4.2329 | 120 | 33.379 | 0 | 272.2688 | 0
10586 | 834.7483 | 2.6584 | 30.3418 | 91.1244 | 48.5866 | 10.4497 | 99.4207 | 4.3264 | 6.3157 | 30.3107 | 80.288 | 9.2194 | 185.857 | 81.6663 | 231.6166 | 9.0174 | 52.6306 | 3.6344 | 116 | 32.6068 | 0 | 269.9267 | 0
10587 | 826.656 | 2.4242 | 30.2048 | 90.4179 | 49.5862 | 9.5003 | 89.7065 | 4.9403 | 6.482 | 30.4675 | 80.6098 | 9.3976 | 183.8182 | 79.7253 | 234.3993 | 9.5439 | 52.761 | 3.191 | 114 | 28.3775 | 0 | 271.5978 | 0
10588 | 827.7433 | 2.5073 | 30.1881 | 89.2857 | 48.589 | 10.4497 | 81.2604 | 5.0013 | 6.3278 | 31.0649 | 80.5519 | 9.2051 | 186.1631 | 79.1786 | 230.4121 | 9.4921 | 52.8061 | 3.0547 | 108 | 26.4972 | 0 | 275.432 | 0
10589 | 834.5858 | 2.9517 | 30.0908 | 89.3657 | 48.5822 | 10.45 | 84.082 | 4.9952 | 6.3475 | 31.1424 | 80.2357 | 9.0733 | 184.4577 | 79.0873 | 223.4122 | 9.5077 | 54.241 | 3.0431 | 108 | 29.2256 | 0 | 302.8933 | 0
10590 | 839.404 | 4.8615 | 45.5862 | 90.9212 | 48.5822 | 10.45 | 90.1336 | 5.2684 | 6.8702 | 47.6177 | 82.4167 | 11.6578 | 194.1478 | 89.2866 | 227.9071 | 9.4998 | 56.636 | 3.0453 | 117 | 28.2071 | 0 | 349.6184 | 0
10591 | 888.1605 | 7.7719 | 64.3027 | 89.0945 | 46.5811 | 12.3495 | 97.1434 | 4.5379 | 8.2712 | 67.0827 | 90.6814 | 15.1061 | 230.1111 | 159.7982 | 246.0925 | 11.6647 | 52.516 | 4.5071 | 201 | 33.3092 | 0 | 382.973 | 0
10592 | 951.7925 | 12.2592 | 83.788 | 90.9948 | 41.575 | 17.1034 | 106.4031 | 4.8412 | 11.1795 | 93.7725 | 131.0322 | 31.5349 | 286.4386 | 217.7451 | 343.7522 | 27.6096 | 55.1985 | 9.1455 | 237 | 58.3234 | 0 | 427.2856 | 0.069825
10593 | 1021.8869 | 11.385 | 95.5609 | 106.648 | 38.5779 | 19.9472 | 123.2252 | 5.7022 | 18.6402 | 103.1444 | 168.9819 | 39.6918 | 337.8961 | 259.0942 | 449.0858 | 36.0965 | 75.3694 | 14.4232 | 300 | 61.4143 | 0 | 522.0169 | 0.15038
10594 | 1082.8455 | 8.6084 | 100.4788 | 118.8137 | 38.5661 | 19.9528 | 134.8614 | 6.909 | 19.9988 | 105.5558 | 182.2023 | 42.3562 | 381.7794 | 283.0433 | 498.3002 | 41.0705 | 99.2583 | 16.7576 | 329 | 57.8276 | 0 | 579.4422 | 0.15746
10595 | 1115.6741 | 7.1131 | 100.9816 | 122.3948 | 38.5733 | 19.95 | 131.3468 | 7.2969 | 19.7708 | 106.4675 | 185.4968 | 44.1992 | 406.6083 | 295.5103 | 533.3099 | 42.9732 | 111.3426 | 17.3425 | 313 | 55.956 | 0 | 605.6732 | 0.18462
10596 | 1133.9912 | 5.6765 | 102.7254 | 124.8799 | 39.5764 | 19.0003 | 131.1263 | 7.4466 | 20.2427 | 102.8737 | 188.0359 | 44.3792 | 418.4008 | 303.4588 | 531.2681 | 43.1871 | 115.4223 | 17.7744 | 307 | 60.239 | 0 | 604.8122 | 0.20441
10597 | 1115.7468 | 4.7744 | 101.614 | 126.1262 | 39.5767 | 19 | 142.7925 | 7.6055 | 18.5697 | 113.0541 | 195.1462 | 42.1527 | 409.651 | 309.4121 | 527.0607 | 43.6637 | 108.4719 | 18.0737 | 327 | 63.7061 | 0 | 597.8838 | 0.19135
10598 | 1114.6787 | 8.7217 | 106.0212 | 132.1457 | 37.5766 | 20.8995 | 149.3043 | 6.7978 | 19.4052 | 111.0443 | 196.0051 | 41.7228 | 413.2999 | 313.9896 | 539.8194 | 44.9115 | 105.7021 | 18.2001 | 269 | 64.0292 | 0 | 615.5261 | 0.21038
10599 | 1111.5322 | 11.2517 | 106.5889 | 137.8247 | 41.5802 | 17.1011 | 145.1998 | 6.2392 | 20.751 | 106.161 | 193.3907 | 38.7527 | 410.5267 | 311.1927 | 525.5724 | 43.4214 | 105.3424 | 18.2081 | 262 | 63.8341 | 0 | 579.6804 | 0.16157
10600 | 1072.0992 | 8.4262 | 102.3454 | 134.1598 | 39.5834 | 18.9995 | 138.3234 | 6.3967 | 20.5954 | 108.7784 | 188.3897 | 33.3715 | 398.9498 | 301.3242 | 509.5009 | 40.1043 | 101.223 | 17.2055 | 264 | 66.0789 | 0 | 547.805 | 0.15571
10601 | 1036.9337 | 5.1814 | 95.9116 | 112.658 | 43.5781 | 15.2011 | 127.3693 | 6.0499 | 20.4549 | 102.9656 | 176.3779 | 28.9289 | 370.6695 | 272.6157 | 454.5846 | 30.2437 | 99.1707 | 16.5049 | 262 | 57.5344 | 0 | 481.8655 | 0.097739
10602 | 993.0063 | 4.8758 | 85.1326 | 102.6259 | 36.5807 | 21.8482 | 118.2274 | 5.3331 | 19.462 | 83.1896 | 156.1041 | 29.4409 | 321.0703 | 204.2813 | 373.0451 | 18.6183 | 93.2758 | 16.6321 | 226 | 57.881 | 0 | 379.54 | 0.030463
10603 | 970.4999 | 5.3105 | 52.6226 | 96.618 | 47.5792 | 11.4029 | 103.3948 | 5.0745 | 12.87 | 56.7002 | 132.2012 | 26.7898 | 283.2727 | 131.9029 | 328.1004 | 16.8888 | 92.9557 | 14.3037 | 214 | 49.8933 | 0 | 327.6425 | 0
10604 | 923.932 | 4.8694 | 40.1477 | 93.0785 | 48.581 | 10.4503 | 93.4992 | 4.898 | 9.53 | 51.386 | 112.5646 | 14.8339 | 251.3018 | 118.1991 | 305.3586 | 14.3879 | 68.5547 | 8.8137 | 193 | 44.0987 | 0 | 283.5262 | 0
10605 | 870.4853 | 4.5128 | 31.0243 | 91.5412 | 49.5795 | 9.5003 | 87.8439 | 4.746 | 9.8592 | 49.2079 | 87.0935 | 9.8799 | 222.1802 | 117.4734 | 285.0793 | 11.7938 | 55.4466 | 6.5905 | 167 | 34.8103 | 0 | 270.1923 | 0
10606 | 849.0563 | 4.5712 | 25.6523 | 91.5376 | 48.5791 | 10.4497 | 71.5647 | 4.2347 | 8.3022 | 40.3205 | 76.849 | 9.8987 | 197.8881 | 104.8347 | 268.9932 | 11.1491 | 53.8001 | 6.1302 | 172 | 29.6823 | 0 | 261.0036 | 0
10607 | 834.7232 | 3.9257 | 24.6718 | 92.1202 | 48.5787 | 10.45 | 64.5517 | 4.0976 | 8.0172 | 35.3943 | 76.1408 | 9.9539 | 189.5282 | 102.2342 | 274.6511 | 11.0324 | 53.4192 | 6.0468 | 155 | 29.4045 | 0 | 266.1691 | 0
10608 | 816.4354 | 2.9362 | 24.5341 | 91.3937 | 49.579 | 9.5003 | 73.6929 | 4.2204 | 7.846 | 21.5706 | 50.1336 | 9.9502 | 56.0256 | 60.812 | 187.8162 | 10.8232 | 33.6001 | 5.6366 | 148 | 31.4448 | 0 | 134.1614 | 0
10609 | 814.052 | 3.0122 | 24.678 | 89.3383 | 48.5804 | 10.4497 | 72.4761 | 4.9468 | 6.6493 | 30.3543 | 76.2354 | 9.8532 | 195.8225 | 88.0492 | 274.5567 | 10.8604 | 53.399 | 4.735 | 134 | 29.3979 | 0 | 269.0352 | 0
10610 | 807.8136 | 2.8725 | 24.7003 | 90.554 | 49.5833 | 9.5003 | 63.3026 | 5.0788 | 6.359 | 29.8085 | 76.2781 | 9.6734 | 198.3085 | 87.5413 | 257.0042 | 10.9682 | 54.2731 | 3.4178 | 130 | 31.113 | 0 | 267.2616 | 0
10611 | 799.3203 | 2.6986 | 24.7157 | 89.8338 | 46.5797 | 12.3492 | 67.4251 | 5.0377 | 6.5605 | 29.3943 | 74.8247 | 9.2777 | 192.6568 | 93.125 | 245.0418 | 11.0243 | 53.6383 | 2.9804 | 126 | 30.7993 | 0 | 280.6409 | 0
10612 | 803.1702 | 2.6048 | 24.5912 | 89.0482 | 49.5792 | 9.5008 | 74.3402 | 5.0357 | 6.8207 | 29.1374 | 74.3044 | 9.2545 | 190.6334 | 89.1762 | 232.784 | 10.8301 | 53.3552 | 3.2574 | 123 | 27.8063 | 0 | 284.6101 | 0
10613 | 794.3459 | 3.0274 | 24.5423 | 89.574 | 48.5817 | 10.4497 | 65.9431 | 5.329 | 6.4628 | 30.0435 | 75.2459 | 9.2259 | 190.8595 | 83.4483 | 226.2762 | 10.5791 | 54.6556 | 3.5774 | 125 | 28.6256 | 0 | 283.222 | 0
10614 | 797.7416 | 3.8322 | 25.2361 | 88.8165 | 48.5808 | 10.45 | 61.9053 | 4.8334 | 6.2613 | 29.8337 | 87.0934 | 9.1532 | 187.2292 | 80.6289 | 228.4429 | 10.7343 | 56.9083 | 3.1927 | 115 | 28.558 | 0 | 286.6696 | 0
10615 | 815.7244 | 4.3318 | 38.6364 | 86.5002 | 49.5835 | 9.5003 | 70.6375 | 4.1982 | 5.6623 | 25.7929 | 84.7413 | 7.4769 | 186.5615 | 76.4469 | 224.1781 | 10.5916 | 53.194 | 2.8535 | 114 | 30.7515 | 0 | 273.7107 | 0
10616 | 828.6875 | 3.6194 | 48.0093 | 85.6979 | 48.5807 | 10.4497 | 71.4058 | 3.9733 | 9.3573 | 38.1769 | 80.9382 | 8.3844 | 210.9147 | 74.0468 | 224.0303 | 11.9495 | 51.5771 | 2.9973 | 113 | 48.6107 | 0 | 264.7883 | 0.043835
10617 | 843.1757 | 2.7437 | 57.1 | 85.7591 | 48.5817 | 10.45 | 72.5698 | 3.8416 | 13.9962 | 61.0472 | 93.9076 | 14.601 | 229.6958 | 76.6673 | 219.6005 | 12.7367 | 50.8621 | 3.5623 | 112 | 56.063 | 0 | 265.925 | 0.085262
10618 | 866.2331 | 2.8303 | 71.8419 | 87.9062 | 48.5774 | 10.45 | 80.0988 | 4.1777 | 16.7663 | 75.8283 | 107.9027 | 15.9924 | 231.5181 | 81.0053 | 218.1991 | 11.684 | 50.6821 | 5.8454 | 137 | 53.721 | 0 | 262.3599 | 0.11997
10619 | 865.9803 | 3.0099 | 80.329 | 90.2841 | 49.5733 | 9.5029 | 88.4625 | 5.0651 | 16.8568 | 81.159 | 147.4621 | 15.4806 | 237.6571 | 86.2849 | 213.8819 | 11.0059 | 50.9045 | 11.7002 | 137 | 48.084 | 0 | 280.2815 | 0.19993
10620 | 879.9717 | 3.1226 | 84.1981 | 88.501 | 49.5772 | 9.4974 | 89.1559 | 5.1846 | 16.4867 | 73.9234 | 153.6176 | 16.1641 | 249.2105 | 94.9454 | 221.3775 | 10.763 | 50.5278 | 13.9694 | 166 | 43.6112 | 0 | 273.7984 | 0.26659
10621 | 891.3186 | 4.5625 | 84.4208 | 87.4833 | 46.5751 | 12.3492 | 85.1868 | 4.3556 | 17.3402 | 73.9008 | 146.7112 | 18.8397 | 256.9623 | 97.1179 | 235.8343 | 10.9142 | 51.3998 | 14.2479 | 180 | 44.0416 | 0 | 264.6315 | 0.20847
10622 | 879.4149 | 10.0852 | 80.4368 | 88.008 | 48.5751 | 10.4505 | 88.7505 | 3.5928 | 16.0588 | 71.8459 | 123.3403 | 18.3692 | 265.6684 | 98.3164 | 248.3003 | 10.8899 | 51.1778 | 14.2727 | 187 | 44.0409 | 0 | 253.8672 | 0.14044
10623 | 876.2885 | 6.7599 | 53.6933 | 90.46 | 49.5777 | 9.5003 | 99.3048 | 3.6953 | 11.712 | 58.9521 | 111.7209 | 16.2875 | 261.3796 | 99.2791 | 242.5938 | 10.7693 | 50.7588 | 12.2497 | 197 | 45.4784 | 0 | 259.2136 | 0.20948
10624 | 880.3671 | 4.505 | 41.629 | 90.3326 | 48.5771 | 10.4497 | 96.0907 | 4.5131 | 8.8114 | 54.3956 | 112.2715 | 16.0425 | 255.0218 | 99.9906 | 227.3075 | 10.7238 | 51.285 | 7.3799 | 199 | 43.9434 | 0 | 257.0473 | 0.2336
10625 | 876.6247 | 8.257 | 31.8024 | 88.0454 | 49.5741 | 9.5003 | 86.4442 | 4.1887 | 7.6196 | 39.8786 | 111.3335 | 10.312 | 254.8184 | 115.9184 | 227.5501 | 10.4688 | 50.7989 | 5.7087 | 202 | 40.9437 | 0 | 263.4475 | 0.15801
10626 | 857.4662 | 10.6128 | 26.1845 | 90.2434 | 49.5787 | 9.5 | 89.1812 | 4.1513 | 7.5227 | 31.7637 | 100.8768 | 5.546 | 255.8934 | 120.647 | 243.1828 | 9.1472 | 50.8644 | 6.005 | 204 | 42.8762 | 0 | 272.8535 | 0.057925
10627 | 850.1794 | 11.4453 | 25.0109 | 91.4815 | 48.579 | 10.4497 | 76.2181 | 5.1312 | 7.375 | 30.7555 | 80.7103 | 5.5971 | 237.9973 | 120.7909 | 254.6615 | 9.2449 | 51.2423 | 6.7587 | 214 | 40.7693 | 0 | 282.5146 | 0
10628 | 836.3025 | 7.9978 | 24.8996 | 90.5451 | 48.575 | 10.45 | 85.183 | 5.7062 | 7.7057 | 34.2264 | 73.7456 | 6.9362 | 227.0236 | 121.7138 | 250.8136 | 9.3848 | 51.4527 | 6.8947 | 214 | 38.1229 | 0 | 287.4977 | 0
10629 | 833.98 | 8.0771 | 25.1875 | 90.1853 | 49.5741 | 9.5003 | 90.8313 | 5.4391 | 8.9378 | 37.7776 | 82.6279 | 7.4228 | 221.8499 | 103.7971 | 247.0459 | 9.5311 | 51.7821 | 6.3737 | 209 | 36.1334 | 0 | 271.5126 | 0
10630 | 828.0543 | 10.9406 | 25.669 | 89.9555 | 47.5753 | 11.3995 | 69.3842 | 5.0014 | 10.134 | 37.1848 | 86.9657 | 7.4288 | 216.4929 | 95.5844 | 250.7325 | 9.6488 | 51.521 | 5.3118 | 199 | 37.1807 | 0 | 266.8324 | 0
10631 | 814.6543 | 11.4628 | 25.5992 | 89.8674 | 47.5792 | 11.4 | 65.5085 | 5.1285 | 9.3865 | 36.9077 | 78.0952 | 7.4597 | 221.3433 | 91.8328 | 256.9668 | 9.7325 | 51.5846 | 5.019 | 180 | 33.3748 | 0 | 255.459 | 0
10632 | 809.7936 | 10.1549 | 25.3511 | 89.5408 | 48.5816 | 10.4503 | 71.1838 | 5.5592 | 7.2926 | 24.1617 | 48.5849 | 7.5176 | 66.107 | 60.4303 | 176.19 | 9.6716 | 32.5775 | 4.6295 | 146 | 34.5248 | 0 | 137.5752 | 0
10633 | 830.5589 | 5.964 | 25.3756 | 89.1953 | 49.5835 | 9.5003 | 63.4827 | 6.227 | 6.3639 | 33.1932 | 73.5174 | 8.7425 | 205.7433 | 87.8128 | 252.8552 | 9.5027 | 51.5926 | 3.7913 |  | 35.6193 | 0 | 267.5939 | 0
10634 | 817.3866 | 3.1509 | 25.4276 | 89.0057 | 48.5781 | 10.4497 | 60.1571 | 7.071 | 6.374 | 29.8105 | 73.9733 | 8.3013 | 200.6931 | 83.0108 | 240.8609 | 9.5972 | 51.2219 | 3.0015 |  | 36.7249 | 0 | 275.2748 | 0
10635 | 809.144 | 2.8045 | 25.7037 | 89.3261 | 42.5807 | 16.1484 | 66.924 | 6.885 | 6.3818 | 30.5149 | 74.089 | 8.0296 | 197.7656 | 81.7708 | 243.1191 | 9.6396 | 51.4216 | 2.922 |  | 35.0095 | 0 | 271.9474 | 0
10636 | 793.2192 | 2.6804 | 25.7335 | 89.4135 | 43.5811 | 15.2003 | 64.1988 | 6.0948 | 6.4936 | 30.2266 | 74.2252 | 7.8971 | 196.5001 | 81.2143 | 243.1832 | 9.7003 | 51.7924 | 3.0748 |  | 33.2305 | 0 | 269.4309 | 0
10637 | 785.5208 | 3.2323 | 26.2328 | 89.5148 | 44.5828 | 14.2503 | 61.1329 | 6.1666 | 6.4136 | 29.9771 | 74.4631 | 7.8153 | 195.6415 | 81.1787 | 238.3686 | 9.7375 | 53.4394 | 3.3717 |  | 34.5529 | 0 | 278.5481 | 0
10638 | 785.7822 | 4.1764 | 26.4202 | 90.4582 | 48.583 | 10.4511 | 67.5638 | 7.1774 | 6.2238 | 29.1228 | 73.7804 | 7.4179 | 191.4671 | 79.5628 | 222.8704 | 9.4614 | 55.5185 | 3.0317 |  | 43.0579 | 0 | 281.8403 | 0
10639 | 793.1195 | 3.5245 | 26.1009 | 89.2891 | 47.5802 | 11.3997 | 64.2401 | 7.4105 | 5.6038 | 27.9115 | 71.0055 | 5.6977 | 189.1853 | 76.798 | 209.9612 | 9.2167 | 51.9092 | 2.7366 |  | 32.9699 | 0 | 267.7308 | 0
10640 | 804.765 | 2.5754 | 25.4095 | 87.9908 | 46.5822 | 12.3497 | 59.6303 | 5.4885 | 5.2152 | 26.4563 | 70.4945 | 5.0029 | 194.3947 | 77.2241 | 206.8769 | 11.4797 | 50.0574 | 2.8987 |  | 28.423 | 0 | 260.2513 | 0.1063
10641 | 809.447 | 2.3673 | 24.8755 | 87.8414 | 48.5799 | 10.4505 | 67.1288 | 4.6773 | 5.3148 | 37.2648 | 72.4042 | 4.9778 | 202.8469 | 78.6649 | 206.3613 | 11.9809 | 49.8176 | 3.4317 |  | 28.6263 | 0 | 264.924 | 0.065361
10642 | 827.599 | 2.5584 | 28.9158 | 90.2469 | 48.5818 | 10.45 | 71.4943 | 4.4854 | 5.3227 | 55.1918 | 83.4555 | 4.9648 | 206.8668 | 84.0531 | 206.483 | 11.849 | 49.6312 | 3.6545 |  | 31.3438 | 0 | 274.5043 | 0.098853
10643 | 858.6364 | 2.5688 | 37.6931 | 90.6689 | 45.5776 | 13.2992 | 74.7565 | 4.6536 | 5.5437 | 64.5753 | 94.5111 | 5.2203 | 212.92 | 106.8046 | 201.877 | 11.1518 | 49.3447 | 3.6477 |  | 27.6205 | 0 | 281.9582 | 0.13869
10644 | 858.8524 | 2.383 | 41.0019 | 88.2738 | 47.5728 | 11.4005 | 80.8233 | 4.3525 | 5.2387 | 67.1518 | 108.1608 | 5.6023 | 217.2759 | 115.5408 | 201.2079 | 10.6865 | 50.17 | 3.6252 |  | 29.2557 | 0 | 283.2618 | 0.14018
10645 | 856.2865 | 2.7577 | 41.2227 | 86.4745 | 49.5765 | 9.5005 | 86.3643 | 4.0976 | 5.2807 | 67.6634 | 113.0797 | 8.6544 | 220.2102 | 120.2639 | 216.7512 | 11.1066 | 50.9651 | 3.6219 |  | 25.8674 | 0 | 275.2703 | 0.12397
10646 | 865.8557 | 2.9403 | 41.1617 | 86.5077 | 49.5806 | 9.5 | 84.8796 | 4.1609 | 5.4603 | 63.8711 | 113.9312 | 12.9057 | 221.0515 | 127.669 | 234.4414 | 11.0657 | 51.1259 | 3.6388 |  | 29.9135 | 0 | 262.6783 | 0.10608
10647 | 861.0035 | 2.8563 | 40.9917 | 86.7734 | 48.5778 | 10.4497 | 88.363 | 3.8424 | 5.1887 | 64.9531 | 136.227 | 18.9719 | 224.8638 | 122.4868 | 251.2424 | 11.3634 | 52.2388 | 3.6844 |  | 34.752 | 0 | 269.0622 | 0.10062
10648 | 866.7948 | 3.7341 | 40.7994 | 90.2601 | 48.5756 | 10.45 | 100.0514 | 3.6748 | 5.257 | 61.1526 | 144.7529 | 18.3735 | 223.5368 | 109.6765 | 256.9203 | 11.2308 | 54.9526 | 3.6942 |  | 35.548 | 0 | 269.6383 | 0.088211
10649 | 863.3869 | 8.0495 | 31.5544 | 92.022 | 47.5749 | 11.3997 | 89.314 | 4.3084 | 6.0594 | 36.467 | 124.6614 | 16.6714 | 221.4196 | 105.8866 | 254.3851 | 11.3905 | 56.3065 | 3.7278 |  | 34.073 | 0 | 268.4423 | 0.02872
10650 | 876.9285 | 16.3034 | 26.3719 | 89.371 | 49.5789 | 9.5005 | 74.7107 | 4.5863 | 6.2172 | 26.233 | 116.4715 | 16.7298 | 222.7183 | 108.1328 | 259.9606 | 10.6528 | 55.6407 | 3.9886 |  | 33.4886 | 0 | 257.8699 | 0.0078888
10651 | 865.8667 | 19.15 | 25.6511 | 92.3905 | 48.5836 | 10.4497 | 67.5006 | 5.4706 | 6.2898 | 29.3529 | 120.937 | 13.7398 | 223.9828 | 107.5716 | 264.3436 | 9.6951 | 52.7634 | 4.7798 |  | 35.6504 | 0 | 259.3755 | 0
10652 | 855.7372 | 18.9851 | 25.6879 | 93.4958 | 48.5807 | 10.45 | 73.6266 | 5.8806 | 6.5192 | 32.0908 | 124.6236 | 9.5959 | 220.3143 | 102.7625 | 271.7925 | 9.6486 | 52.4409 | 5.0377 |  | 33.7121 | 0 | 264.3287 | 0
10653 | 839.2504 | 14.4912 | 25.7549 | 90.4242 | 48.5826 | 10.45 | 72.7208 | 5.9154 | 6.4968 | 32.2711 | 109.4634 | 8.5169 | 223.113 | 96.1916 | 243.9818 | 9.4801 | 52.1861 | 4.811 |  | 28.8045 | 0 | 266.6472 | 0
10654 | 825.7006 | 7.6011 | 25.9023 | 89.0036 | 48.5836 | 10.45 | 64.5685 | 5.9065 | 6.3668 | 31.8548 | 83.8438 | 8.1733 | 216.7783 | 87.9578 | 230.5444 | 9.5788 | 51.7797 | 3.9848 |  | 27.5771 | 0 | 268.0033 | 0
10655 | 808.8941 | 4.3453 | 25.6159 | 89.326 | 48.5794 | 10.45 | 66.0126 | 5.6072 | 6.1365 | 30.7026 | 72.8917 | 7.97 | 208.992 | 87.0157 | 234.0446 | 9.6536 | 51.2922 | 3.7845 |  | 26.3894 | 0 | 263.6789 | 0
10656 | 799.5513 | 2.9167 | 25.5151 | 88.7756 | 48.58 | 10.45 | 72.4242 | 5.2453 | 5.8549 | 19.6748 | 47.6871 | 7.946 | 61.2571 | 56.0953 | 159.4809 | 9.6611 | 32.1027 | 3.9961 |  | 27.081 | 0 | 132.5933 | 0
10657 | 791.3036 | 2.4514 | 25.5044 | 88.5354 | 49.5775 | 9.5003 | 65.3016 | 5.0999 | 5.9464 | 30.1009 | 71.7572 | 7.8991 | 189.373 | 81.8342 | 222.3168 | 9.6578 | 50.8015 | 4.2593 | 104 | 25.3662 | 0 | 265.9237 | 0
10658 | 793.7313 | 2.4965 | 25.9279 | 90.0738 | 46.582 | 12.3492 | 62.0397 | 5.1616 | 6.0918 | 30.5434 | 71.4973 | 7.7953 | 191.41 | 81.8042 | 219.3266 | 9.4938 | 51.5676 | 3.8763 | 102 | 25.2847 | 0 | 262.75 | 0
10659 | 786.8196 | 2.7525 | 25.8223 | 90.9879 | 48.5849 | 10.4505 | 69.896 | 5.5976 | 6.1272 | 31.1802 | 71.5097 | 7.7759 | 188.3849 | 87.1389 | 225.7089 | 9.6616 | 51.6691 | 2.9531 | 105 | 26.0411 | 0 | 266.9522 | 0
10660 | 785.3904 | 2.8776 | 26.2688 | 90.9548 | 48.5853 | 10.45 | 68.0634 | 6.0039 | 5.9663 | 31.4646 | 71.6306 | 7.7645 | 183.8669 | 90.1369 | 225.0334 | 9.8047 | 51.5451 | 2.649 | 101 | 25.0038 | 0 | 269.6698 | 0
10661 | 777.7568 | 3.0227 | 27.5034 | 90.5708 | 48.5807 | 10.45 | 62.2004 | 6.1568 | 5.9145 | 31.488 | 71.4797 | 7.7803 | 180.8589 | 83.6009 | 220.8557 | 9.7784 | 53.0064 | 2.6329 | 104 | 24.9737 | 0 | 318.2916 | 0
10662 | 781.8239 | 4.2655 | 34.7753 | 89.4303 | 49.5802 | 9.5003 | 72.7417 | 6.4608 | 6.1682 | 41.9004 | 72.1898 | 9.8722 | 194.0955 | 90.5664 | 222.4516 | 9.706 | 55.212 | 3.0337 | 106 | 26.4387 | 0 | 337.7816 | 0
10663 | 827.2163 | 5.3836 | 48.586 | 90.8502 | 47.5794 | 11.3995 | 89.3341 | 5.2844 | 8.364 | 64.8947 | 92.5914 | 15.8562 | 233.1137 | 170.3687 | 250.5363 | 11.8889 | 51.8584 | 4.1469 | 178 | 34.6061 | 0 | 347.3563 | 0
10664 | 897.9801 | 5.1382 | 76.7313 | 96.8661 | 41.8241 | 17.0984 | 105.2227 | 5.1038 | 13.3467 | 85.3128 | 139.1796 | 30.3038 | 279.4478 | 228.6756 | 352.185 | 26.4664 | 54.4756 | 9.2032 | 273 | 52.917 | 0 | 419.253 | 0.025017
10665 | 995.3285 | 5.7673 | 95.1734 | 108.2404 | 38.7121 | 19.9492 | 126.6528 | 6.2317 | 22.257 | 85.3535 | 169.6048 | 38.9999 | 328.1275 | 276.4232 | 454.8279 | 33.9445 | 65.7027 | 12.867 | 309 | 59.5517 | 0 | 494.8806 | 0.038534
10666 | 1082.329 | 8.9933 | 101.8447 | 121.9603 | 38.5716 | 19.95 | 147.2287 | 6.9627 | 26.205 | 92.0342 | 180.22 | 39.8427 | 369.7846 | 310.8603 | 522.2125 | 38.9828 | 75.1194 | 14.5573 | 348 | 62.8902 | 0 | 559.5424 | 0.0672
10667 | 1133.4714 | 10.6858 | 99.3814 | 125.4177 | 38.5685 | 19.95 | 144.3079 | 7.2859 | 27.4327 | 101.0284 | 198.3662 | 40.4286 | 390.9905 | 333.1604 | 555.6249 | 41.4648 | 82.8359 | 16.3989 | 343 | 64.0697 | 0 | 569.8822 | 0.073359
10668 | 1163.1359 | 9.6651 | 100.0736 | 124.5668 | 37.575 | 20.8997 | 144.6795 | 7.4507 | 23.9158 | 109.9829 | 192.0548 | 40.104 | 409.7178 | 350.5172 | 573.3484 | 39.6592 | 105.7604 | 17.209 | 324 | 68.3585 | 0 | 581.9549 | 0.091094
10669 | 1154.3162 | 8.4115 | 103.7927 | 121.8904 | 38.5756 | 19.9503 | 160.0201 | 7.0465 | 15.4683 | 106.4448 | 187.8204 | 40.7688 | 408.5932 | 345.0032 | 561.5032 | 39.2396 | 106.8066 | 17.9953 | 350 | 60.4762 | 0 | 602.9653 | 0.083913
10670 | 1161.5001 | 10.1585 | 106.5057 | 125.4593 | 37.5765 | 20.8997 | 164.7975 | 7.2195 | 19.757 | 100.8688 | 192.7461 | 39.8924 | 411.9537 | 336.598 | 546.6493 | 39.1841 | 106.3765 | 18.343 | 291 | 59.654 | 0 | 606.8423 | 0.080024
10671 | 1187.6793 | 12.0337 | 104.5785 | 130.527 | 38.5746 | 19.9503 | 156.8114 | 8.2246 | 22.4115 | 102.7739 | 196.0269 | 39.3699 | 420.0404 | 334.3606 | 537.854 | 39.5697 | 106.0243 | 17.9472 | 261 | 59.3591 | 0 | 562.2987 | 0.060099
10672 | 1141.8463 | 11.0182 | 103.3551 | 126.6657 | 40.5727 | 18.0505 | 154.3563 | 8.3319 | 14.9385 | 94.4235 | 187.4782 | 36.1777 | 418.59 | 328.8866 | 515.6025 | 39.1517 | 104.5383 | 17.6732 | 267 | 64.9388 | 0 | 587.3858 | 0.094784
10673 | 1104.8621 | 7.8152 | 100.4198 | 128.2403 | 40.5746 | 18.05 | 147.6856 | 7.2661 | 8.471 | 90.8426 | 184.9765 | 30.8895 | 390.6177 | 305.4725 | 456.1136 | 31.406 | 103.0217 | 17.4842 | 229 | 54.3654 | 0 | 558.7325 | 0.038511
10674 | 1058.2662 | 6.0438 | 94.2141 | 114.8123 | 46.577 | 12.3516 | 132.6929 | 6.3617 | 6.1805 | 73.2875 | 164.9909 | 28.2942 | 339.2752 | 233.3626 | 373.4157 | 16.2128 | 97.3959 | 16.28 | 225 | 53.5888 | 0 | 436.6811 | 0.002595
10675 | 1014.7774 | 5.9495 | 87.1089 | 103.169 | 47.5773 | 11.4003 | 120.8846 | 5.8029 | 6.4553 | 56.4131 | 136.5504 | 26.2006 | 285.6405 | 160.8339 | 331.5035 | 10.8539 | 87.5622 | 13.1583 | 208 | 50.2298 | 0 | 397.3542 | 0
10676 | 958.5026 | 5.1556 | 69.4907 | 101.3716 | 45.5783 | 13.2995 | 99.6395 | 5.1376 | 6.698 | 52.2438 | 123.7924 | 13.4545 | 251.8429 | 137.2836 | 307.3395 | 10.0522 | 78.26 | 7.4249 | 189 | 42.7134 | 0 | 340.9191 | 0
10677 | 920.8971 | 5.2523 | 36.9543 | 95.4673 | 48.578 | 10.4508 | 83.4301 | 4.8405 | 6.7476 | 50.1389 | 114.4641 | 10.2449 | 233.4062 | 116.3207 | 296.2522 | 9.8448 | 74.1853 | 5.0534 | 174 | 36.7588 | 0 | 317.4382 | 0
10678 | 893.5437 | 4.9123 | 26.5129 | 90.7137 | 48.583 | 10.45 | 82.3455 | 4.3897 | 6.6131 | 41.458 | 98.4408 | 11.6525 | 217.4981 | 99.2395 | 272.8725 | 9.6076 | 74.5152 | 4.08 | 172 | 31.2436 | 0 | 309.464 | 0
10679 | 871.7798 | 4.4187 | 26.536 | 90.2831 | 49.5822 | 9.5003 | 82.2414 | 4.5832 | 6.3814 | 34.3853 | 79.4808 | 11.5747 | 215.6499 | 91.9907 | 256.8698 | 9.7497 | 74.2543 | 3.282 | 151 | 27.6469 | 0 | 307.2242 | 0
10680 | 836.4143 | 3.9328 | 26.2881 | 89.3218 | 48.5812 | 10.4497 | 71.2263 | 4.9634 | 6.009 | 21.1014 | 48.1453 | 11.6675 | 64.9589 | 57.1915 | 166.9283 | 9.7816 | 45.913 | 2.9162 | 130 | 28.3476 | 0 | 157.1775 | 0
10681 | 831.6897 | 2.9163 | 26.2467 | 88.3525 | 49.5825 | 9.5003 | 74.8702 | 4.8498 | 5.7074 | 30.4754 | 70.8738 | 11.4463 | 194.9885 | 81.5786 | 223.6905 | 9.7095 | 71.7179 | 2.7136 | 121 | 27.5292 | 0 | 300.3936 | 0
10682 | 830.4713 | 2.5287 | 26.0695 | 88.6943 | 48.5806 | 10.4497 | 78.516 | 4.7638 | 5.8263 | 29.6215 | 74.7019 | 11.015 | 192.8318 | 79.7311 | 217.4084 | 9.6466 | 71.5639 | 3.1185 | 122 | 26.2568 | 0 | 296.956 | 0
10683 | 816.1644 | 2.3816 | 26.1929 | 88.6636 | 49.5786 | 9.5003 | 78.7325 | 4.814 | 5.5703 | 29.5963 | 76.9143 | 10.8904 | 188.9421 | 79.5043 | 225.2268 | 9.4107 | 71.6247 | 3.0285 | 120 | 26.3382 | 0 | 302.9307 | 0
10684 | 812.0796 | 2.3176 | 26.1333 | 88.4733 | 49.5788 | 9.5 | 68.9606 | 4.6672 | 5.6478 | 29.67 | 76.5944 | 10.9107 | 178.8305 | 80.3619 | 229.3515 | 9.4416 | 71.5362 | 2.7624 | 114 | 26.1318 | 0 | 302.6331 | 0
10685 | 812.7078 | 2.8935 | 26.3147 | 88.3409 | 48.5804 | 10.4497 | 69.5648 | 4.2485 | 5.8805 | 31.2473 | 75.041 | 10.8734 | 178.5227 | 82.2684 | 221.9237 | 9.4877 | 73.1013 | 2.6716 | 107 | 26.9412 | 0 | 329.2643 | 0
10686 | 824.9098 | 4.0908 | 35.9092 | 88.8063 | 48.5781 | 10.45 | 82.3996 | 4.1242 | 6.456 | 49.4842 | 72.7844 | 14.2213 | 194.0928 | 92.2354 | 224.2113 | 9.3896 | 75.3199 | 2.6549 | 111 | 27.4774 | 0 | 368.5322 | 0
10687 | 866.5475 | 6.5182 | 51.9521 | 95.3252 | 46.5751 | 12.3495 | 94.5251 | 4.079 | 8.81 | 66.7757 | 85.2998 | 20.0403 | 238.2274 | 166.3406 | 262.0316 | 11.8338 | 71.8534 | 4.4833 | 195 | 34.9423 | 0 | 414.9202 | 0.019592
10688 | 923.5269 | 16.3353 | 77.0255 | 97.1833 | 42.5712 | 16.1489 | 106.8718 | 5.5449 | 16.325 | 84.7695 | 137.7575 | 32.0599 | 294.0092 | 232.0911 | 352.5242 | 26.183 | 74.4753 | 7.9227 | 249 | 57.2763 | 0 | 452.9798 | 0.028451
10689 | 1020.6957 | 22.7492 | 95.5246 | 109.727 | 41.5684 | 17.0997 | 134.7998 | 6.6602 | 23.346 | 82.4264 | 173.528 | 38.9865 | 341.0883 | 283.7401 | 461.907 | 33.9218 | 86.0775 | 15.4722 | 294 | 65.8735 | 0 | 537.3058 | 0.067778
10690 | 1102.8727 | 15.2307 | 101.6542 | 123.1217 | 42.5725 | 16.1503 | 153.8297 | 7.2968 | 25.3165 | 92.0398 | 184.7649 | 39.5116 | 383.6891 | 319.9483 | 523.3992 | 37.9617 | 94.3229 | 17.5566 | 370 | 66.9677 | 0 | 615.1549 | 0.14304
10691 | 1161.5297 | 6.9019 | 102.1926 | 128.1753 | 40.5802 | 18.0495 | 157.6975 | 7.3798 | 24.1057 | 97.7162 | 185.2814 | 41.335 | 401.8265 | 337.358 | 540.9875 | 40.1435 | 97.9117 | 17.8682 | 316 | 64.0866 | 0 | 632.9344 | 0.14376
10692 | 1215.2307 | 4.9344 | 104.8564 | 130.6408 | 40.5755 | 18.05 | 160.432 | 8.0328 | 20.6087 | 98.7992 | 182.0505 | 39.8095 | 409.6222 | 352.0637 | 554.272 | 39.2643 | 101.7423 | 18.0691 | 323 | 74.5855 | 0 | 646.546 | 0.13081
10693 | 1217.8749 | 4.9233 | 105.558 | 130.3607 | 38.5763 | 19.9495 | 164.5653 | 7.5729 | 17.0722 | 85.7036 | 181.567 | 40.0908 | 413.5468 | 356.3657 | 545.8787 | 39.7167 | 100.5905 | 18.0911 | 342 | 64.0153 | 0 | 649.3429 | 0.16077
10694 | 1212.7731 | 7.4391 | 104.4727 | 137.8605 | 39.5756 | 19.0003 | 164.7075 | 6.8217 | 21.3007 | 73.4168 | 190.2049 | 41.4029 | 413.7739 | 356.1716 | 541.5056 | 40.1241 | 100.2922 | 17.7753 | 298 | 66.9296 | 0 | 643.4065 | 0.13567
10695 | 1193.8943 | 10.9967 | 102.1728 | 137.2278 | 39.5747 | 19 | 163.6729 | 7.9154 | 22.3643 | 68.301 | 194.9431 | 41.1172 | 413.5047 | 344.9789 | 546.0661 | 40.7604 | 102.994 | 17.725 | 265 | 71.4373 | 0 | 615.2633 | 0.081928
10696 | 1137.669 | 12.2311 | 99.861 | 132.8445 | 40.5717 | 18.0503 | 159.5081 | 8.0404 | 17.4338 | 68.1029 | 192.138 | 39.9465 | 421.7685 | 353.4591 | 549.2866 | 40.3068 | 100.3239 | 18.2875 | 268 | 76.8465 | 0 | 599.1107 | 0.025072
10697 | 1117.7451 | 14.5209 | 89.6122 | 126.1124 | 45.5682 | 13.3013 | 139.522 | 6.8825 | 15.0009 | 68.8073 | 183.4594 | 37.7622 | 405.4732 | 335.4416 | 497.0922 | 33.1183 | 88.7043 | 17.4514 | 256 | 63.4746 | 0 | 545.9406 | 0.0079389
10698 | 1069.8061 | 14.4233 | 85.5101 | 115.4149 | 47.5769 | 11.4005 | 121.2972 | 5.9931 | 13.7333 | 64.1024 | 163.175 | 35.9544 | 361.3877 | 272.6554 | 409.5366 | 17.9439 | 75.1152 | 16.8875 | 229 | 55.8121 | 0 | 415.7333 | 0.0034232
10699 | 1012.7978 | 8.9463 | 84.6809 | 104.0563 | 49.5786 | 9.5005 | 115.4315 | 5.5319 | 12.103 | 46.758 | 139.7677 | 30.8767 | 312.965 | 198.4842 | 356.0816 | 12.2338 | 67.5914 | 14.4528 | 210 | 48.1926 | 0 | 375.665 | 0
10700 | 983.9236 | 7.8291 | 70.4039 | 99.5597 | 47.5782 | 11.3995 | 94.2137 | 5.3472 | 8.181 | 41.8004 | 134.1127 | 19.0183 | 284.4722 | 166.3312 | 317.8209 | 11.0708 | 62.4826 | 8.9082 | 194 | 44.1492 | 0 | 333.187 | 0
10701 | 943.5583 | 10.201 | 37.6066 | 96.4605 | 48.5827 | 10.4503 | 78.6647 | 5.1605 | 6.7428 | 39.985 | 126.6429 | 15.7823 | 259.3831 | 150.3181 | 281.6416 | 10.6062 | 58.0481 | 5.803 | 184 | 35.5975 | 0 | 310.9747 | 0
10702 | 909.7345 | 7.0506 | 26.0063 | 91.3371 | 48.5783 | 10.45 | 76.5021 | 5.0667 | 6.4067 | 31.9695 | 101.5424 | 14.1736 | 218.5569 | 133.9451 | 268.6436 | 10.4234 | 55.8022 | 4.6733 | 172 | 31.0634 | 0 | 313.8808 | 0
10703 | 887.4464 | 4.3042 | 25.5836 | 89.1078 | 47.5768 | 11.3997 | 70.5607 | 5.0736 | 6.2198 | 26.496 | 79.9603 | 12.7527 | 194.3306 | 121.1 | 248.7622 | 10.1874 | 53.6991 | 4.3834 | 158 | 30.2267 | 0 | 312.1583 | 0
10704 | 863.022 | 3.102 | 25.4214 | 88.6803 | 48.5757 | 10.4503 | 67.8355 | 4.508 | 6.1355 | 16.2669 | 49.1104 | 12.4996 | 56.2445 | 74.4089 | 161.6444 | 10.2715 | 33.3855 | 4.3818 | 143 | 26.2107 | 0 | 157.9138 | 0
10705 | 855.3361 | 2.629 | 25.5083 | 89.3901 | 49.5768 | 9.5003 | 75.4247 | 4.2636 | 6.2032 | 24.1488 | 73.9619 | 12.6211 | 176.3205 | 110.2755 | 240.6529 | 10.4911 | 52.8558 | 3.8259 |  | 25.7315 | 0 | 308.4671 | 0
10706 | 852.2725 | 2.5332 | 25.5135 | 88.6243 | 48.581 | 10.4497 | 75.1908 | 4.6334 | 6.2687 | 24.35 | 75.971 | 12.3631 | 173.4983 | 106.3839 | 247.2509 | 10.4421 | 52.9464 | 3.0973 |  | 26.2625 | 0 | 315.7775 | 0
10707 | 836.0983 | 2.5248 | 25.4977 | 88.4091 | 49.5774 | 9.5003 | 64.4496 | 4.7953 | 6.2943 | 24.5515 | 75.7681 | 12.1852 | 171.9891 | 105.0208 | 254.1268 | 10.3467 | 53.137 | 2.8825 |  | 25.5633 | 0 | 316.4572 | 0
10708 | 829.6786 | 2.529 | 25.3927 | 88.3141 | 48.58 | 10.4497 | 65.6372 | 5.1078 | 6.386 | 24.3326 | 74.2889 | 11.9313 | 170.116 | 104.8607 | 244.4883 | 10.215 | 52.8924 | 2.9245 |  | 25.3243 | 0 | 316.3307 | 0
10709 | 829.3187 | 3.0126 | 25.4043 | 88.3751 | 48.5799 | 10.45 | 73.8528 | 5.3132 | 6.3093 | 24.7052 | 73.7523 | 11.8145 | 171.4587 | 104.1442 | 231.3604 | 10.2194 | 54.2297 | 2.914 |  | 25.5025 | 0 | 340.0157 | 0
10710 | 838.0164 | 5.0632 | 37.5041 | 88.1442 | 49.5759 | 9.5003 | 73.8719 | 5.379 | 6.7346 | 39.467 | 74.0693 | 13.5464 | 186.3118 | 111.6286 | 217.1248 | 10.1799 | 56.5685 | 2.8816 |  | 25.5673 | 0 | 383.6084 | 0
10711 | 894.1548 | 8.495 | 52.5508 | 90.3215 | 48.5726 | 10.4497 | 84.1894 | 5.3152 | 10.4074 | 59.999 | 85.5544 | 17.1593 | 226.8893 | 162.4088 | 237.3097 | 12.7063 | 53.0126 | 2.7573 |  | 32.9906 | 0 | 424.5967 | 0.025028
10712 | 942.7073 | 12.516 | 78.1507 | 93.8145 | 43.5773 | 15.1987 | 116.7023 | 5.6991 | 15.7933 | 74.6541 | 135.5603 | 31.6648 | 285.4285 | 222.3158 | 333.0736 | 28.7045 | 56.2258 | 5.1468 |  | 57.5339 | 0 | 464.4377 | 0.056229
10713 | 1028.8025 | 14.1273 | 94.6635 | 109.7868 | 41.5714 | 17.0995 | 139.8531 | 5.5931 | 23.0775 | 81.2111 | 173.2273 | 40.4058 | 341.4104 | 279.1935 | 445.114 | 38.1068 | 66.1166 | 11.8216 |  | 66.2652 | 0 | 538.9527 | 0.10207
10714 | 1115.032 | 9.9975 | 101.3256 | 122.367 | 40.5683 | 18.0497 | 140.8002 | 6.3432 | 25.0648 | 94.5662 | 182.5194 | 42.3413 | 390.3107 | 320.0754 | 528.3852 | 40.9042 | 73.4192 | 15.3824 |  | 67.1283 | 0 | 613.6858 | 0.097497
10715 | 1154.8694 | 11.4996 | 101.9825 | 132.1842 | 40.5756 | 18.05 | 149.6215 | 7.1858 | 21.7708 | 106.397 | 190.4067 | 43.7616 | 414.4122 | 348.8667 | 577.9272 | 41.7356 | 83.5246 | 16.4182 |  | 68.9614 | 0 | 637.8056 | 0.11499
10716 | 1173.07 | 16.285 | 104.0748 | 135.8411 | 42.5732 | 16.1505 | 157.6909 | 7.6343 | 19.8005 | 112.872 | 187.6405 | 40.7454 | 427.197 | 365.7337 | 596.3396 | 40.5407 | 88.0689 | 17.5342 |  | 74.753 | 0 | 643.3958 | 0.16075
10717 | 1159.7508 | 17.2894 | 103.5348 | 134.4206 | 42.5747 | 16.15 | 163.0257 | 7.8385 | 16.6605 | 93.2982 | 183.9929 | 40.9671 | 421.2865 | 355.1137 | 573.3834 | 41.0163 | 88.7925 | 18.6788 |  | 67.333 | 0 | 646.4575 | 0.18703
10718 | 1159.2811 | 11.3972 | 102.9499 | 142.1619 | 38.5744 | 19.9489 | 162.6211 | 7.0857 | 18.4253 | 98.5975 | 185.0997 | 39.4848 | 419.8065 | 343.9886 | 560.4803 | 43.429 | 86.9715 | 18.5998 |  | 69.8991 | 0 | 660.65 | 0.13382
10719 | 1177.3449 | 8.1675 | 104.8741 | 144.9259 | 38.577 | 19.95 | 162.7126 | 6.2523 | 19.1042 | 107.642 | 187.1308 | 39.6639 | 429.1554 | 340.6318 | 563.6307 | 43.4447 | 84.0979 | 18.247 |  | 68.6221 | 0 | 669.4854 | 0.13616
10720 | 1146.1716 | 5.7519 | 100.5492 | 137.478 | 40.5788 | 18.0505 | 158.5015 | 6.9462 | 15.3653 | 103.371 | 187.9672 | 38.9607 | 421.1655 | 338.2364 | 552.6083 | 40.0007 | 82.9883 | 18.1375 |  | 64.171 | 0 | 660.5107 | 0.088421
10721 | 1138.8687 | 4.7006 | 91.501 | 133.8601 | 46.5712 | 12.3516 | 147.0418 | 6.7495 | 11.6319 | 96.4434 | 184.8279 | 36.8037 | 405.9158 | 315.5112 | 495.7907 | 32.0288 | 82.2178 | 17.8554 |  | 53.8518 | 0 | 571.7399 | 0.083207
10722 | 1085.6386 | 5.0526 | 79.7099 | 118.8028 | 48.5744 | 10.4505 | 131.6313 | 5.5949 | 16.7317 | 78.0565 | 163.0039 | 35.5855 | 370.3681 | 245.5079 | 396.9307 | 17.259 | 72.1177 | 16.8575 |  | 47.233 | 0 | 427.7545 | 0.027488
10723 | 1022.249 | 5.6823 | 74.7278 | 109.9452 | 47.5732 | 11.4029 | 118.697 | 5.5263 | 17.182 | 49.4701 | 134.0632 | 29.7831 | 330.804 | 160.3253 | 337.7679 | 10.8632 | 64.2364 | 14.2445 |  | 45.5862 | 0 | 391.1537 | 0
10724 | 964.612 | 5.183 | 64.9089 | 103.0255 | 48.5804 | 10.4471 | 103.4827 | 5.2953 | 10.5708 | 40.7261 | 124.1777 | 14.8538 | 303.0846 | 127.5583 | 302.6432 | 10.6514 | 58.7469 | 8.813 |  | 43.422 | 0 | 351.1394 | 0
10725 | 929.807 | 5.3081 | 37.1225 | 94.451 | 47.5835 | 11.3997 | 94.2776 | 4.726 | 7.1634 | 38.0931 | 117.0247 | 9.054 | 276.6198 | 112.3174 | 278.9514 | 9.9072 | 55.5535 | 5.9196 |  | 37.3221 | 0 | 327.2843 | 0
10726 | 894.0051 | 4.9751 | 28.1093 | 94.0451 | 48.5803 | 10.4503 | 89.9303 | 4.5907 | 6.7754 | 30.5766 | 99.2151 | 9.002 | 241.0687 | 102.5266 | 258.3551 | 9.4069 | 54.2707 | 4.2657 |  | 34.7613 | 0 | 332.8788 | 0
10727 | 870.2769 | 4.475 | 25.8282 | 93.7758 | 48.5772 | 10.45 | 88.7132 | 4.5919 | 6.482 | 27.4531 | 79.6036 | 9.0816 | 220.0322 | 96.9201 | 237.3082 | 9.3505 | 54.1717 | 3.2913 |  | 32.3797 | 0 | 327.2602 | 0
10728 | 855.28 | 3.5262 | 24.8375 | 91.0523 | 49.5774 | 9.5003 | 81.4785 | 4.9907 | 6.3631 | 16.7889 | 48.0874 | 9.0607 | 63.3302 | 57.9511 | 151.7347 | 9.1665 | 34.0555 | 4.5316 |  | 29.2716 | 0 | 163.2375 | 0
10729 | 851.1415 | 2.7226 | 24.8811 | 89.8047 | 48.579 | 10.4497 | 69.0821 | 5.4126 | 6.4488 | 24.3953 | 72.1724 | 8.9606 | 179.0816 | 93.5134 | 216.1229 | 9.2019 | 53.8538 | 4.6042 | 131 | 28.7192 | 0 | 324.3328 | 0
10730 | 852.8193 | 2.5866 | 24.8066 | 89.8554 | 48.5787 | 10.45 | 70.2858 | 5.6114 | 6.3008 | 24.4044 | 72.0787 | 8.7964 | 171.8353 | 89.4786 | 219.7309 | 9.2822 | 53.5735 | 4.045 | 128 | 27.7188 | 0 | 320.862 | 0
10731 | 841.5894 | 2.602 | 24.8146 | 89.2608 | 49.5804 | 9.5003 | 77.7653 | 5.893 | 6.1368 | 24.4447 | 72.1077 | 8.7707 | 168.5006 | 85.5255 | 225.1959 | 9.2911 | 53.5407 | 3.8979 | 126 | 27.7176 | 0 | 324.642 | 0
10732 | 836.3887 | 2.4592 | 24.9726 | 89.1405 | 48.5815 | 10.4497 | 69.3749 | 6.2749 | 6.1573 | 24.8853 | 72.0723 | 8.7718 | 168.4901 | 83.9385 | 221.8445 | 9.3276 | 53.6924 | 3.9288 | 116 | 30.8913 | 0 | 323.6416 | 0
10733 | 835.033 | 3.0089 | 24.8282 | 89.1615 | 49.579 | 9.5003 | 65.2587 | 6.2199 | 6.0367 | 25.0844 | 71.8498 | 8.7409 | 171.8042 | 79.5926 | 215.6312 | 8.9976 | 55.1514 | 3.946 | 112 | 28.8641 | 0 | 350.2828 | 0
10734 | 847.7255 | 3.9787 | 32.9047 | 88.1897 | 47.5792 | 11.3995 | 78.3092 | 5.5552 | 6.1663 | 35.671 | 71.5015 | 12.5988 | 186.3578 | 87.6607 | 213.2807 | 9.0267 | 57.1483 | 3.9715 | 111 | 26.9987 | 0 | 398.9813 | 0
10735 | 881.4594 | 6.7121 | 56.0927 | 91.9106 | 45.5777 | 13.2995 | 90.2837 | 5.0621 | 9.3933 | 58.0471 | 83.2205 | 18.335 | 228.1332 | 155.5304 | 234.2009 | 11.5043 | 53.7857 | 4.4486 | 186 | 31.5885 | 0 | 440.1684 | 0.033036
10736 | 942.352 | 10.245 | 78.2334 | 94.751 | 40.5742 | 18.0487 | 103.0681 | 6.0869 | 12.0088 | 85.6289 | 136.6791 | 31.4234 | 275.776 | 211.2788 | 319.5575 | 27.0005 | 57.1232 | 6.6887 | 306 | 51.2344 | 0 | 490.3376 | 0.15687
10737 | 1028.8104 | 10.9544 | 93.5949 | 112.2053 | 40.5701 | 18.05 | 127.0959 | 8.0941 | 19.4658 | 100.4362 | 177.1741 | 40.1852 | 332.1599 | 260.9027 | 424.2765 | 36.0064 | 67.6391 | 13.2961 | 315 | 60.2786 | 0 | 567.1262 | 0.22888
10738 | 1118.8847 | 11.0658 | 99.219 | 119.926 | 38.5705 | 19.9495 | 141.9662 | 8.037 | 21.7489 | 94.9944 | 185.7022 | 40.5833 | 378.1453 | 302.9871 | 498.3468 | 39.0056 | 78.8787 | 16.2506 | 366 | 58.4885 | 0 | 618.13 | 0.25784
10739 | 1124.4164 | 11.2297 | 102.2996 | 128.3891 | 37.5714 | 20.8997 | 135.6875 | 7.1279 | 18.58 | 89.807 | 184.6761 | 40.4134 | 407.3131 | 322.2498 | 537.6269 | 39.6205 | 85.0178 | 16.8246 | 374 | 62.9762 | 0 | 605.2963 | 0.26845
10740 | 1169.8911 | 11.477 | 105.3993 | 128.3939 | 40.5685 | 18.0508 | 143.7863 | 5.9968 | 18.3029 | 98.4765 | 181.3242 | 39.6823 | 423.4885 | 332.4069 | 545.6591 | 40.6508 | 83.2218 | 17.4304 | 350 | 68.004 | 0 | 582.7248 | 0.30306
10741 | 1162.4705 | 9.7338 | 104.8043 | 129.498 | 40.5685 | 18.05 | 147.9234 | 5.5298 | 20.1835 | 101.0837 | 183.6834 | 39.3105 | 412.2044 | 317.4628 | 528.4157 | 41.3341 | 82.019 | 17.4286 | 347 | 56.4799 | 0 | 593.2481 | 0.33209
10742 | 1161.6367 | 6.8689 | 104.1267 | 136.9901 | 41.57 | 17.1003 | 153.8239 | 5.9524 | 20.684 | 100.4488 | 189.2043 | 40.4311 | 411.2892 | 315.8734 | 538.9232 | 41.8459 | 85.9791 | 17.649 | 307 | 57.1015 | 0 | 629.7598 | 0.33463
10743 | 1161.6591 | 5.0644 | 102.5389 | 138.5919 | 40.5674 | 18.0497 | 155.6252 | 6.1095 | 19.6897 | 100.5994 | 190.0459 | 40.9698 | 417.848 | 319.4135 | 545.6898 | 41.6733 | 100.0155 | 17.9556 | 295 | 61.2883 | 0 | 602.0794 | 0.30658
10744 | 1128.6913 | 4.7625 | 99.4381 | 133.7394 | 37.5656 | 20.8992 | 149.9401 | 6.8064 | 13.677 | 100.6269 | 187.0083 | 38.4987 | 406.0252 | 307.8736 | 538.8003 | 41.332 | 102.6653 | 18.0195 | 301 | 66.2786 | 0 | 582.532 | 0.23861
10745 | 1107.3896 | 4.8079 | 89.205 | 126.7314 | 42.5678 | 16.1513 | 141.543 | 4.9659 | 8.3478 | 93.8193 | 184.5128 | 32.4573 | 374.3842 | 288.079 | 489.0735 | 34.7515 | 101.6427 | 18.0992 | 279 | 57.4792 | 0 | 545.6134 | 0.17565
10746 | 1069.4874 | 5.2405 | 76.6687 | 111.9422 | 47.5685 | 11.4013 | 132.1679 | 5.2443 | 8.3367 | 82.8165 | 166.463 | 29.2008 | 346.0479 | 236.9287 | 438.2406 | 19.159 | 96.4507 | 17.4496 | 254 | 55.4436 | 0 | 407.291 | 0.093108
10747 | 1000.2541 | 6.0974 | 79.4101 | 97.2532 | 48.5741 | 10.4503 | 117.9507 | 5.7698 | 13.0232 | 63.7541 | 137.5537 | 25.1174 | 315.65 | 174.8415 | 402.8032 | 13.0542 | 72.3939 | 14.3759 | 243 | 45.7797 | 0 | 368.473 | 0
10748 | 955.0441 | 6.4342 | 72.1453 | 93.9701 | 49.5741 | 9.5003 | 97.9087 | 5.9116 | 12.8783 | 60.09 | 125.9168 | 20.9664 | 286.51 | 145.6366 | 362.6791 | 11.7892 | 60.1733 | 8.3696 | 213 | 43.5461 | 0 | 328.8469 | 0
10749 | 924.8361 | 11.3812 | 36.2211 | 91.9791 | 48.5729 | 10.4497 | 107.4193 | 6.057 | 9.7978 | 56.418 | 116.1629 | 19.1553 | 276.8083 | 125.4448 | 320.6561 | 10.9073 | 56.1443 | 5.4736 | 195 | 40.7305 | 0 | 307.871 | 0
10750 | 909.3651 | 13.5806 | 24.3741 | 89.8797 | 49.5708 | 9.5003 | 105.5316 | 5.5573 | 8.0932 | 45.5961 | 98.152 | 12.2893 | 252.9096 | 104.6124 | 301.6547 | 10.6026 | 54.2811 | 4.5842 | 193 | 39.9094 | 0 | 289.332 | 0
10751 | 899.5854 | 11.7962 | 24.2819 | 90.0515 | 48.5786 | 10.4497 | 100.9041 | 5.3647 | 7.5535 | 38.5135 | 81.265 | 9.3762 | 229.6484 | 92.4949 | 293.9717 | 10.5774 | 53.7 | 4.3499 | 187 | 39.7868 | 0 | 288.5071 | 0
10752 | 876.7487 | 10.2235 | 24.3584 | 89.8432 | 49.5798 | 9.5003 | 94.3791 | 5.7374 | 7.4457 | 23.8046 | 50.1111 | 9.5856 | 65.4983 | 52.3159 | 195.5186 | 10.4593 | 33.6919 | 4.3548 | 181 | 39.9631 | 0 | 147.0583 | 0
10753 | 865.0378 | 7.6968 | 24.2098 | 89.0102 | 48.5752 | 10.4497 | 90.0738 | 6.2335 | 6.9957 | 32.8105 | 75.7984 | 9.5849 | 212.3687 | 85.0066 | 274.2197 | 10.3131 | 53.6551 | 4.3707 | 163 | 37.4687 | 0 | 299.4002 | 0
10754 | 863.5336 | 4.0715 | 24.2485 | 89.6994 | 49.5769 | 9.5003 | 81.1178 | 7.1988 | 6.8415 | 30.4903 | 75.5914 | 9.0887 | 203.3261 | 85.0244 | 263.7564 | 10.3411 | 53.2138 | 4.6179 | 137 | 41.2 | 0 | 306.6822 | 0
10755 | 855.88 | 2.8633 | 24.2226 | 89.4433 | 48.5759 | 10.4497 | 77.385 | 7.1884 | 6.7568 | 29.2428 | 74.8912 | 8.8392 | 194.8525 | 82.4987 | 259.0876 | 10.4678 | 53.134 | 4.4633 | 135 | 42.7024 | 0 | 310.4656 | 0
10756 | 847.2872 | 3.1868 | 24.0485 | 89.8482 | 47.5775 | 11.3997 | 73.112 | 6.1295 | 6.5623 | 28.7939 | 73.801 | 9.2011 | 198.2601 | 79.3459 | 252.4144 | 10.4086 | 53.2315 | 3.5231 | 128 | 42.8584 | 0 | 312.6001 | 0
10757 | 845.1571 | 3.4243 | 19.5268 | 90.0407 | 48.5762 | 10.4503 | 69.0116 | 6.1037 | 6.3638 | 28.1893 | 72.615 | 8.9617 | 200.0709 | 78.4997 | 254.3808 | 10.5138 | 54.3927 | 2.9769 | 119 | 39.0228 | 0 | 348.1424 | 0
10758 | 858.4706 | 4.0345 | 26.0594 | 88.6909 | 48.5767 | 10.45 | 79.4468 | 6.1714 | 6.3387 | 38.1259 | 71.9678 | 10.4109 | 207.2318 | 90.2704 | 249.0708 | 10.0981 | 56.5553 | 2.8375 | 121 | 35.4087 | 0 | 391.8477 | 0
10759 | 900.7253 | 4.4473 | 40.5443 | 89.6994 | 45.5781 | 13.2992 | 94.6409 | 6.5084 | 9.8115 | 61.9976 | 82.3803 | 15.4696 | 239.9938 | 143.4869 | 253.5007 | 12.4747 | 53.3109 | 2.6773 | 174 | 37.7515 | 0 | 419.282 | 0.021748
10760 | 948.9816 | 9.0388 | 66.2107 | 93.6389 | 40.5747 | 18.0487 | 110.3063 | 6.8284 | 11.6028 | 79.3542 | 125.5752 | 23.863 | 280.2727 | 192.0157 | 339.512 | 29.0317 | 56.3622 | 4.7088 | 281 | 52.911 | 0 | 466.6838 | 0.083386
10761 | 1004.7982 | 17.8775 | 91.8803 | 109.8383 | 39.5737 | 18.9997 | 136.758 | 7.7647 | 10.3438 | 87.3006 | 161.4129 | 26.5121 | 322.3043 | 243.8737 | 444.9195 | 37.4936 | 64.818 | 11.2991 | 337 | 54.9351 | 0 | 530.4337 | 0.19096
10762 | 1073.0599 | 23.5261 | 98.9909 | 117.4845 | 39.5745 | 19 | 154.9086 | 6.7737 | 12.9907 | 87.8572 | 180.0775 | 31.6794 | 361.3956 | 283.6419 | 493.3158 | 41.1257 | 76.4517 | 14.1398 | 343 | 55.8857 | 0 | 575.1922 | 0.26621
10763 | 1104.9382 | 20.743 | 100.433 | 126.0882 | 39.5749 | 19 | 158.3443 | 5.9244 | 14.5395 | 81.4854 | 186.8788 | 36.5338 | 387.6794 | 303.3125 | 518.7772 | 42.1544 | 99.698 | 14.7815 | 360 | 55.8344 | 0 | 592.4084 | 0.21471
10764 | 1111.1975 | 14.3111 | 104.1038 | 130.6162 | 41.5778 | 17.1005 | 154.8751 | 6.3946 | 14.7647 | 76.6343 | 188.1145 | 35.0635 | 400.0293 | 311.6888 | 530.2249 | 42.6326 | 106.2321 | 15.2008 | 377 | 57.2515 | 0 | 590.2106 | 0.27846
10765 | 1116.9279 | 12.0884 | 104.8224 | 125.2761 | 39.5721 | 19.0048 | 150.952 | 6.8784 | 10.8468 | 71.6797 | 191.2134 | 32.5408 | 392.1695 | 305.8562 | 528.4301 | 42.7467 | 105.9255 | 15.4865 | 367 | 46.3717 | 0 | 579.7837 | 0.31259
10766 | 1124.0078 | 11.3002 | 106.087 | 129.1926 | 38.5767 | 19.9445 | 157.097 | 6.6372 | 7.6173 | 73.9314 | 192.5869 | 29.3959 | 390.9013 | 304.9247 | 541.075 | 43.8489 | 104.5696 | 15.603 | 293 | 46.886 | 0 | 592.6499 | 0.19848
10767 | 1123.763 | 11.227 | 101.8991 | 132.1538 | 40.5682 | 18.0505 | 163.2389 | 6.0197 | 7.0102 | 76.5183 | 196.8781 | 26.5884 | 397.3419 | 308.2758 | 551.8459 | 42.47 | 105.6841 | 15.7314 | 259 | 53.3767 | 0 | 532.5795 | 0.15234
10768 | 1090.3552 | 7.9079 | 96.055 | 127.598 | 40.5661 | 18.055 | 155.9696 | 5.8415 | 7.3955 | 86.6657 | 197.9424 | 29.1547 | 399.0689 | 299.2245 | 548.6258 | 39.0486 | 103.5604 | 16.3303 | 264 | 58.2197 | 0 | 519.678 | 0.07494
10769 | 1055.4845 | 4.7745 | 88.7403 | 116.6582 | 47.5719 | 11.3968 | 142.5133 | 5.1074 | 7.0496 | 81.1728 | 189.5202 | 26.3186 | 379.55 | 282.236 | 493.7189 | 32.7325 | 82.813 | 15.4088 | 240 | 51.5754 | 0 | 454.1486 | 0.03763
10770 | 1012.8473 | 4.3943 | 78.2956 | 103.5584 | 47.5707 | 11.4 | 127.6886 | 4.8342 | 9.1469 | 68.0977 | 170.7935 | 22.9313 | 338.2287 | 226.5526 | 400.3604 | 20.0344 | 69.4549 | 14.6587 | 215 | 51.5936 | 0 | 337.2189 | 0.012225
10771 | 952.2224 | 5.0801 | 51.8938 | 93.3735 | 46.5785 | 12.3497 | 111.1723 | 4.706 | 12.9032 | 44.6542 | 137.6118 | 20.5867 | 293.8098 | 147.6726 | 338.0169 | 15.8877 | 63.8858 | 11.9798 | 220 | 48.6856 | 0 | 306.943 | 0
10772 | 902.6225 | 4.9925 | 43.1522 | 89.5065 | 48.5727 | 10.4505 | 78.7515 | 4.694 | 10.0225 | 38.5758 | 118.5983 | 11.4227 | 254.6799 | 137.322 | 308.9681 | 13.4312 | 56.5174 | 6.6685 | 211 | 43.6567 | 0 | 270.4926 | 0
10773 | 877.2468 | 4.6793 | 34.5951 | 89.9796 | 48.5738 | 10.45 | 73.3328 | 4.7041 | 8.8155 | 36.5991 | 92.1738 | 7.3886 | 231.1187 | 137.0225 | 283.0955 | 11.4314 | 54.0805 | 4.9762 | 175 | 36.8517 | 0 | 258.7436 | 0
10774 | 862.2979 | 4.2583 | 29.3311 | 88.8959 | 48.5777 | 10.45 | 78.3924 | 4.1296 | 9.3341 | 27.9128 | 78.4455 | 7.2328 | 212.7762 | 117.792 | 250.5671 | 11.1154 | 52.6454 | 5.2286 | 171 | 31.3902 | 0 | 251.977 | 0
10775 | 835.9294 | 3.6683 | 28.4734 | 88.3917 | 49.5757 | 9.5003 | 74.9988 | 4.035 | 8.0981 | 24.1259 | 75.4396 | 7.246 | 188.634 | 106.6898 | 238.8419 | 11.0043 | 51.5781 | 4.734 | 146 | 30.8635 | 0 | 254.0895 | 0
10776 | 821.3732 | 2.8203 | 28.3397 | 88.7942 | 48.5788 | 10.4497 | 67.6672 | 4.403 | 6.7059 | 15.5734 | 48.4581 | 7.4665 | 53.1078 | 66.3624 | 161.233 | 11.0473 | 32.3226 | 4.3226 | 146 | 33.3769 | 0 | 130.7206 | 0
10777 | 821.761 | 2.6479 | 28.546 | 88.6254 | 49.5791 | 9.5003 | 75.6261 | 4.7864 | 6.3757 | 24.4714 | 72.0929 | 7.3523 | 183.9238 | 100.2898 | 237.9776 | 11.1024 | 51.1788 | 4.0739 | 133 | 38.2039 | 0 | 259.5475 | 0
10778 | 821.2495 | 2.5827 | 28.7975 | 88.0988 | 48.5807 | 10.4497 | 78.8821 | 4.9132 | 6.1192 | 24.7552 | 72.107 | 7.1182 | 183.4683 | 92.3776 | 236.3926 | 10.8683 | 51.3778 | 3.8151 | 129 | 33.1303 | 0 | 261.5944 | 0
10779 | 809.7239 | 2.4854 | 28.6321 | 88.091 | 49.58 | 9.5003 | 67.798 | 4.9595 | 6.321 | 24.5753 | 70.7885 | 7.2088 | 182.3942 | 86.813 | 242.9266 | 10.9361 | 51.3249 | 3.2005 | 112 | 30.7825 | 0 | 258.5486 | 0
10780 | 808.0189 | 2.7109 | 28.5417 | 88.2106 | 48.5791 | 10.4497 | 69.4706 | 5.0159 | 6.44 | 24.3078 | 70.798 | 7.587 | 181.3566 | 83.4344 | 242.0526 | 11.043 | 51.3507 | 2.8607 | 107 | 30.1529 | 0 | 260.567 | 0
10781 | 807.8661 | 3.0806 | 28.4827 | 88.2599 | 49.582 | 9.5003 | 75.9184 | 5.269 | 6.2322 | 24.2339 | 71.9709 | 7.2411 | 179.6464 | 82.7052 | 230.2103 | 10.9098 | 52.8398 | 2.639 | 114 | 26.8651 | 0 | 257.9304 | 0
10782 | 803.9659 | 3.766 | 29.6958 | 87.2383 | 48.5827 | 10.4497 | 74.4646 | 4.8853 | 5.9923 | 22.6329 | 70.424 | 6.3128 | 177.7017 | 81.0274 | 220.227 | 10.7738 | 54.8402 | 2.5615 | 108 | 26.9093 | 0 | 262.6185 | 0
10783 | 827.1488 | 2.991 | 45.9356 | 85.8102 | 49.5788 | 9.5003 | 63.62 | 4.0215 | 5.3528 | 19.7519 | 67.9206 | 4.7383 | 176.7922 | 79.4135 | 209.5135 | 10.3177 | 50.8281 | 2.4599 | 102 | 29.1687 | 0 | 250.7751 | 0.028769
10784 | 827.5982 | 2.5995 | 49.5528 | 85.0779 | 48.5817 | 10.4497 | 72.6273 | 3.1778 | 5.4099 | 20.2992 | 73.692 | 6.0881 | 183.577 | 81.145 | 207.995 | 10.6973 | 50.2421 | 2.5802 | 102 | 34.2812 | 0 | 251.9893 | 0.062135
10785 | 826.8633 | 2.3395 | 54.7391 | 87.1351 | 47.5767 | 11.3997 | 86.5039 | 3.4378 | 5.4733 | 37.9572 | 98.5597 | 12.5947 | 191.1343 | 82.6726 | 217.1509 | 11.073 | 50.54 | 3.1096 | 136 | 36.6307 | 0 | 257.4775 | 0.09068
10786 | 858.0823 | 2.4719 | 67.7752 | 88.0036 | 47.5732 | 11.4 | 89.4605 | 3.7202 | 7.1915 | 57.625 | 120.0686 | 14.8784 | 195.8837 | 88.8594 | 220.2237 | 11.0403 | 50.9723 | 5.1714 | 168 | 31.9715 | 0 | 255.6253 | 0.085718
10787 | 876.9553 | 2.582 | 78.5991 | 89.7824 | 49.5755 | 9.5005 | 88.9534 | 3.7884 | 8.224 | 68.6793 | 134.2928 | 16.6915 | 208.2635 | 99.9386 | 211.8934 | 10.6327 | 50.3485 | 10.3697 | 186 | 29.0282 | 0 | 266.2994 | 0.11093
10788 | 877.2292 | 2.6779 | 80.6353 | 89.2353 | 48.5763 | 10.4497 | 88.5573 | 3.1019 | 10.7572 | 68.0806 | 121.521 | 19.0697 | 220.2072 | 116.7321 | 230.3902 | 10.3511 | 50.1581 | 12.4085 | 172 | 28.4218 | 0 | 261.1401 | 0.1376
10789 | 868.1478 | 2.9009 | 80.7528 | 86.1794 | 48.577 | 10.45 | 69.962 | 2.6327 | 12.6661 | 64.1109 | 115.5439 | 17.7399 | 226.3535 | 124.9668 | 246.5934 | 10.454 | 51.1694 | 12.5883 | 181 | 27.2606 | 0 | 250.0792 | 0.1301
10790 | 869.2493 | 2.4789 | 75.8925 | 87.6761 | 49.5748 | 9.5003 | 58.3477 | 3.5232 | 13.0723 | 67.4085 | 115.5575 | 18.4969 | 225.8866 | 128.7278 | 269.3414 | 10.1538 | 51.4701 | 12.6815 | 177 | 26.2936 | 0 | 260.3147 | 0.11386
10791 | 878.6098 | 2.3934 | 49.1302 | 87.9902 | 49.5787 | 9.5 | 63.4171 | 3.064 | 10.4774 | 66.0906 | 117.2862 | 19.4452 | 221.0954 | 131.9827 | 301.7408 | 10.5022 | 51.5357 | 10.8211 | 207 | 32.5225 | 0 | 256.9563 | 0.12689
10792 | 866.6838 | 2.3436 | 39.0831 | 87.3603 | 49.5785 | 9.5 | 70.9504 | 3.4571 | 7.3347 | 55.1742 | 122.0872 | 16.6066 | 223.0733 | 127.368 | 307.5366 | 10.5274 | 51.0298 | 5.8779 | 201 | 31.4027 | 0 | 262.3607 | 0.073851
10793 | 861.2601 | 6.2164 | 29.7597 | 87.512 | 48.5771 | 10.4497 | 75.4728 | 3.949 | 6.0565 | 32.7887 | 120.5504 | 8.018 | 244.6867 | 125.0974 | 298.5096 | 10.5312 | 51.4693 | 3.8506 | 195 | 27.4061 | 0 | 263.3399 | 0.049225
10794 | 850.1372 | 9.4826 | 24.4631 | 86.9798 | 49.5807 | 9.5003 | 77.5132 | 4.4084 | 5.7237 | 22.0693 | 108.7648 | 7.3746 | 250.0202 | 121.7268 | 281.6722 | 9.4546 | 51.8009 | 3.5755 | 220 | 29.3087 | 0 | 254.8022 | 0.013682
10795 | 837.332 | 12.959 | 23.9021 | 87.9393 | 49.5779 | 9.5 | 78.597 | 4.3871 | 6.0585 | 22.0211 | 86.4284 | 9.4293 | 242.4706 | 116.1133 | 277.5198 | 9.2369 | 50.7822 | 3.5584 | 210 | 31.4778 | 0 | 251.3919 | 0
10796 | 833.4398 | 17.4476 | 24.1215 | 89.6995 | 48.5753 | 10.4497 | 78.7958 | 4.9195 | 6.8507 | 25.3245 | 77.0293 | 8.388 | 235.0734 | 117.1418 | 259.6446 | 9.9387 | 50.9439 | 3.6207 | 202 | 31.6214 | 0 | 259.5801 | 0
10797 | 824.089 | 18.8066 | 24.423 | 91.5456 | 44.5796 | 14.2489 | 79.1331 | 4.5673 | 6.7058 | 28.9137 | 75.0945 | 7.2759 | 226.9496 | 116.5911 | 244.7919 | 10.3825 | 51.6839 | 3.4185 | 203 | 31.4751 | 0 | 243.2493 | 0
10798 | 820.9197 | 11.1444 | 24.4945 | 90.3889 | 46.5778 | 12.3505 | 76.084 | 4.399 | 6.5715 | 27.2478 | 74.3422 | 6.9349 | 219.8574 | 107.5676 | 239.8382 | 10.1739 | 51.4868 | 3.0701 | 196 | 29.7926 | 0 | 253.1908 | 0
10799 | 808.9125 | 4.9743 | 24.5689 | 90.1035 | 48.5784 | 10.4505 | 65.4875 | 4.5197 | 6.5513 | 25.0018 | 74.1719 | 6.7607 | 199.4291 | 102.8465 | 244.8195 | 10.312 | 50.7459 | 3.396 | 176 | 28.7312 | 0 | 261.5806 | 0
10800 | 816.2252 | 3.2604 | 24.6986 | 90.6967 | 48.5818 | 10.45 | 67.5265 | 4.6575 | 6.4253 | 15.9711 | 49.1523 | 6.7655 | 56.9852 | 66.0452 | 168.5391 | 10.3759 | 32.1251 | 3.6336 | 143 | 29.1364 | 0 | 135.5077 | 0
10801 | 845.0063 | 2.6811 | 24.5198 | 89.7727 | 48.5848 | 10.45 | 74.5648 | 5.403 | 6.3442 | 24.4573 | 73.2318 | 6.7722 | 192.8841 | 98.603 | 244.2144 | 10.4343 | 50.9282 | 3.3803 | 147 | 29.0098 | 0 | 269.9965 | 0
10802 | 852.5375 | 2.6063 | 24.4958 | 89.2324 | 48.58 | 10.45 | 65.6417 | 5.5178 | 7.2919 | 24.4294 | 72.0016 | 6.5607 | 187.8897 | 95.7312 | 245.3707 | 10.4554 | 50.479 | 3.1783 | 154 | 27.1589 | 0 | 268.753 | 0
10803 | 812.1293 | 3.0133 | 24.5614 | 90.7349 | 42.5798 | 16.1484 | 63.3985 | 5.5849 | 0 | 12.2727 | 35.6441 | 6.451 |  | 50.7099 | 130.9427 | 10.0839 | 25.5409 | 3.0247 | 157 | 27.8026 | 0 | 130.0293 | 0
10804 | 806.7034 | 3.3214 | 24.6233 | 89.9999 | 44.5804 | 14.2505 | 71.5773 | 5.6781 | 7.2086 | 24.7418 | 70.9576 | 6.4249 | 184.2132 | 98.3536 | 236.2371 | 10.2507 | 51.408 | 2.7332 | 150 | 30.5192 | 0 | 280.7713 | 0
10805 | 815.468 | 3.8841 | 24.5688 | 90.0819 | 43.5775 | 15.1997 | 68.5391 | 5.6485 | 6.602 | 24.9972 | 70.9449 | 6.5258 | 182.9809 | 99.6606 | 220.6399 | 10.3032 | 52.802 | 2.9266 | 129 | 38.1629 | 0 | 281.0551 | 0
10806 | 822.1598 | 4.3533 | 24.3214 | 88.4871 | 48.5726 | 10.4513 | 60.4354 | 4.9099 | 6.2787 | 24.3058 | 71.0422 | 6.2204 | 181.5531 | 98.103 | 214.4447 | 10.293 | 52.2755 | 2.6742 | 121 | 30.3616 | 0 | 275.0016 | 0
10807 | 822.6586 | 3.6703 | 24.0399 | 86.4656 | 49.5788 | 9.5003 | 66.9781 | 4.5042 | 6.263 | 21.7419 | 70.9201 | 4.2721 | 180.7059 | 94.2367 | 209.7246 | 10.6049 | 49.9438 | 2.6437 | 117 | 31.8787 | 0 | 265.9858 | 0.028956
10808 | 823.7901 | 2.5842 | 24.1605 | 85.881 | 47.575 | 11.3995 | 68.8844 | 3.5589 | 5.6637 | 23.5157 | 71.3631 | 3.5042 | 184.8426 | 92.3863 | 203.986 | 11.103 | 48.875 | 3.1739 | 128 | 28.4996 | 0 | 263.9333 | 0.038258
10809 | 830.9429 | 2.4021 | 28.2443 | 86.1551 | 48.5745 | 10.4503 | 65.7062 | 3.7849 | 5.42 | 36.6957 | 73.9824 | 3.8214 | 189.5104 | 94.309 | 203.6005 | 11.4456 | 48.8572 | 3.3727 | 141 | 22.7066 | 0 | 264.7052 | 0.18632
10810 | 854.9498 | 3.2919 | 37.3998 | 86.0368 | 48.5819 | 10.45 | 80.091 | 4.0683 | 5.4415 | 51.7121 | 80.8617 | 3.9543 | 191.9992 | 99.1022 | 211.845 | 10.7421 | 49.7553 | 3.4124 | 153 | 18.2794 | 0 | 261.4614 | 0.22605
10811 | 859.0678 | 2.8974 | 40.1488 | 85.9181 | 44.5839 | 14.2489 | 90.9242 | 3.8772 | 5.7797 | 57.7272 | 88.428 | 3.9308 | 208.6756 | 105.5725 | 221.082 | 10.469 | 50.6611 | 3.688 | 171 | 18.7381 | 0 | 260.102 | 0.23108
10812 | 857.9949 | 2.4092 | 40.0752 | 86.0871 | 45.5792 | 13.3003 | 91.7369 | 3.6981 | 5.9315 | 57.6839 | 97.1959 | 4.273 | 219.6419 | 109.2763 | 224.7334 | 10.1834 | 51.0732 | 3.8261 | 156 | 17.6658 | 0 | 261.1328 | 0.24503
10813 | 879.4742 | 2.8433 | 40.1975 | 86.1759 | 48.5785 | 10.4508 | 88.4114 | 2.6369 | 5.694 | 57.23 | 107.8649 | 4.2376 | 220.2739 | 111.0378 | 229.2006 | 10.0043 | 51.373 | 3.8218 | 151 | 18.2228 | 0 | 263.4605 | 0.25389
10814 | 868.8182 | 3.1275 | 39.8919 | 89.7676 | 49.5814 | 9.5003 | 80.8154 | 2.8391 | 5.5943 | 57.5136 | 116.2811 | 4.6733 | 221.7201 | 112.4627 | 239.5316 | 10.2131 | 51.4763 | 3.583 | 164 | 27.9962 | 0 | 263.4705 | 0.26118
10815 | 859.0745 | 2.4335 | 39.0662 | 90.9037 | 48.578 | 10.4497 | 78.1442 | 3.4034 | 5.6944 | 53.4465 | 122.0414 | 7.7172 | 220.664 | 108.8366 | 250.2076 | 10.4916 | 51.0239 | 3.5521 | 165 | 29.1904 | 0 | 255.9052 | 0.22096
10816 | 861.2461 | 2.6961 | 29.8494 | 88.1925 | 47.5709 | 11.3997 | 76.0554 | 3.4783 | 5.7637 | 37.9592 | 123.6243 | 8.0096 | 235.6945 | 102.7881 | 255.9335 | 10.4883 | 50.752 | 3.7344 | 166 | 32.5315 | 0 | 249.1094 | 0.16336
10817 | 845.2836 | 7.6941 | 24.5113 | 87.6073 | 47.5771 | 11.4 | 74.9109 | 2.1017 | 6.1269 | 22.4864 | 121.6191 | 5.8207 | 309.115 | 101.0134 | 254.796 | 9.5999 | 50.8893 | 3.9938 | 155 | 32.5958 | 0 | 245.4114 | 0.11448
10818 | 842.1223 | 10.0699 | 23.5551 | 87.445 | 48.5784 | 10.4503 | 88.3714 | 3.4582 | 6.6047 | 18.6341 | 118.9242 | 4.9064 | 335.6787 | 100.1717 | 249.4967 | 8.7494 | 50.8197 | 3.8829 | 145 | 33.6414 | 0 | 242.673 | 0.047841
10819 | 833.2825 | 11.4724 | 23.9881 | 88.7589 | 47.5734 | 11.3997 | 90.2206 | 4.5335 | 6.5026 | 19.9307 | 115.0764 | 4.9236 | 333.8328 | 97.6782 | 243.7742 | 8.9103 | 56.4285 | 3.6424 | 130 | 36.3926 | 0 | 242.1595 | 0
10820 | 821.9277 | 10.7106 | 24.2197 | 90.2952 | 49.5731 | 9.5005 | 93.1403 | 5.0494 | 6.571 | 22.7742 | 103.3072 | 6.3232 | 333.2649 | 94.9823 | 238.6494 | 9.7652 | 65.2693 | 3.6241 | 135 | 34.5776 | 0 | 245.7825 | 0
10821 | 805.1531 | 9.0771 | 24.3925 | 90.5706 | 48.5765 | 10.4497 | 82.1939 | 5.1754 | 6.812 | 25.1256 | 88.7934 | 6.9871 | 332.2938 | 92.6193 | 231.4941 | 10.1675 | 68.9346 | 3.7051 | 121 | 30.2774 | 0 | 251.6108 | 0
10822 | 795.1874 | 10.1491 | 24.5066 | 90.1722 | 48.5787 | 10.45 | 68.6059 | 5.3097 | 6.5243 | 25.3321 | 82.3083 | 7.0743 | 328.6299 | 91.9066 | 222.4598 | 10.3421 | 64.6442 | 3.6553 | 118 | 28.2182 | 0 | 254.4091 | 0
10823 | 774.7524 | 9.2553 | 24.5887 | 89.879 | 47.5793 | 11.3997 | 73.0616 | 4.6385 | 6.3571 | 24.7401 | 79.2753 | 7.0629 | 324.3886 | 90.474 | 215.648 | 10.1028 | 55.933 | 3.3683 | 112 | 26.9789 | 0 | 254.9384 | 0
10824 | 778.2174 | 4.4155 | 24.5601 | 89.2104 | 48.577 | 10.4503 | 78.2344 | 4.4122 | 6.1051 | 16.0068 | 50.4552 | 6.973 | 95.9687 | 56.1014 | 152.5904 | 10.2447 | 32.4901 | 2.8518 | 107 | 26.8685 | 0 | 128.2322 | 0
10825 | 783.9443 | 2.4422 | 24.4733 | 88.904 | 48.5745 | 10.45 | 64.9804 | 4.6147 | 6.1605 | 24.5136 | 74.8088 | 6.7258 | 291.7447 | 84.8078 | 230.0505 | 10.2447 | 50.2974 | 2.6593 | 102 | 26.2895 | 0 | 258.7927 | 0
10826 | 783.3449 | 2.3667 | 24.496 | 89.0319 | 48.5748 | 10.45 | 61.1368 | 4.9743 | 6.349 | 24.6241 | 74.9336 | 6.6318 | 284.9167 | 87.9536 | 236.3973 | 10.3112 | 50.3304 | 2.6315 | 104 | 27.5302 | 0 | 265.6054 | 0
10827 | 775.8101 | 2.3336 | 25.0129 | 89.2568 | 48.5808 | 10.45 | 70.5674 | 5.1488 | 6.071 | 24.7345 | 74.2418 | 6.639 | 283.3586 | 91.7473 | 239.769 | 10.2402 | 50.0835 | 2.6304 | 107 | 28.6951 | 0 | 267.5592 | 0
10828 | 777.9059 | 2.7655 | 26.1152 | 90.4335 | 48.5785 | 10.45 | 73.0156 | 5.171 | 5.8773 | 24.7763 | 73.2246 | 6.6398 | 283.93 | 88.3093 | 234.288 | 10.1369 | 50.6001 | 2.6429 | 100 | 26.4153 | 0 | 291.1771 | 0
10829 | 792.4567 | 3.7137 | 33.4933 | 90.0187 | 49.5736 | 9.5003 | 69.1452 | 5.2022 | 6.1472 | 29.8134 | 73.8435 | 7.9216 | 281.0472 | 86.2905 | 227.6673 | 10.122 | 52.6525 | 2.6642 | 111 | 27.6317 | 0 | 322.2328 | 0
10830 | 849.1322 | 4.9974 | 47.9455 | 91.1773 | 45.5749 | 13.2989 | 86.1259 | 5.1196 | 6.8661 | 46.607 | 84.7756 | 15.9192 | 293.1072 | 126.9934 | 233.2096 | 13.0517 | 52.2977 | 3.7188 | 169 | 33.6413 | 0 | 357.2823 | 0
10831 | 910.873 | 9.0854 | 75.9708 | 97.5261 | 54.5813 | 16.1492 | 109.0967 | 5.6826 | 8.2108 | 63.8888 | 113.717 | 29.3874 | 341.9108 | 195.5377 | 282.9801 | 27.6174 | 52.1557 | 10.1445 | 279 | 54.4625 | 0 | 404.3402 | 0.032671
10832 | 993.3036 | 9.5299 | 89.9902 | 110.4471 | 93.2936 | 18.9992 | 133.7973 | 6.5813 | 13.7025 | 73.4678 | 149.2319 | 34.9739 | 386.7988 | 253.0524 | 381.7111 | 35.3514 | 58.0494 | 14.7665 | 304 | 60.3955 | 0 | 463.3801 | 0.055592
10833 | 1081.1219 | 9.8503 | 94.6124 | 124.2564 | 110.3123 | 19 | 150.1097 | 6.8019 | 21.8633 | 85.0215 | 173.1561 | 35.8094 | 460.1169 | 301.7374 | 490.9778 | 40.6487 | 68.0902 | 16.6756 | 386 | 63.8711 | 0 | 534.6818 | 0.040593
10834 | 1141.3941 | 9.422 | 96.1823 | 125.2108 | 109.2889 | 18.0503 | 160.486 | 8.7011 | 25.1743 | 96.9653 | 182.9002 | 40.5275 | 501.6392 | 331.9462 | 578.1956 | 41.3347 | 86.6216 | 18.889 | 344 | 63.9089 | 0 | 570.3716 | 0.052056
10835 | 1145.5246 | 5.9045 | 102.8839 | 125.7189 | 111.2104 | 18.05 | 161.3278 | 9.3845 | 25.34 | 101.5631 | 185.9967 | 39.9368 | 538.6189 | 344.4518 | 625.4998 | 39.9246 | 104.4594 | 19.7862 | 306 | 74.1519 | 0 | 575.8465 | 0.061374
10836 | 1168.9676 | 10.5933 | 105.8605 | 128.8639 | 111.2759 | 19.9495 | 157.2736 | 9.1337 | 23.441 | 101.835 | 186.106 | 38.8553 | 558.2233 | 352.5186 | 615.8721 | 39.4489 | 105.2908 | 19.9318 | 335 | 68.131 | 0 | 588.3157 | 0.055576
10837 | 1174.8352 | 13.1886 | 104.0068 | 136.0606 | 111.3478 | 20.8997 | 165.4344 | 9.591 | 17.4375 | 99.6341 | 187.3875 | 42.9898 | 553.2636 | 355.3585 | 583.6339 | 41.6723 | 94.5155 | 20.1735 | 284 | 73.0092 | 0 | 596.2271 | 0.053305
10838 | 1190.6028 | 12.4184 | 102.7319 | 135.7609 | 115.6762 | 18.0508 | 168.5314 | 11.0131 | 21.8531 | 96.3729 | 190.2765 | 43.4955 | 570.1862 | 358.6756 | 564.3978 | 42.0392 | 86.5481 | 20.4037 | 313 | 75.5834 | 0 | 584.9926 | 0.051465
10839 | 1169.7624 | 13.0103 | 99.7154 | 129.9369 | 114.5614 | 19.9495 | 160.9749 | 11.7874 | 24.2459 | 92.8666 | 191.4614 | 39.8632 | 596.5934 | 354.5578 | 555.8473 | 40.1735 | 84.9762 | 20.5163 | 253 | 72.9732 | 0 | 562.9805 | 0.035212
10840 | 1134.4981 | 11.8177 | 95.5117 | 124.1546 | 122.7667 | 12.3521 | 153.887 | 8.7251 | 18.2539 | 84.0532 | 188.5513 | 37.3679 | 584.8447 | 333.1311 | 520.0044 | 32.5858 | 83.7284 | 19.7398 | 234 | 61.3187 | 0 | 536.2415 | 0.061086
10841 | 1088.3527 | 10.766 | 91.8378 | 111.9244 | 124.9997 | 11.4003 | 141.298 | 5.8065 | 10.6026 | 72.5347 | 176.1079 | 35.6653 | 556.1728 | 287.8019 | 454.0983 | 18.4937 | 78.8003 | 18.7531 | 205 | 54.3556 | 0 | 456.5321 | 0.056903
10842 | 1037.4221 | 8.1068 | 79.1976 | 103.3459 | 124.3416 | 11.4 | 128.7153 | 3.8084 | 12.3326 | 58.0167 | 152.0711 | 28.2532 | 511.3964 | 222.2095 | 391.4798 | 12.0924 | 71.5985 | 15.5423 | 197 | 53.158 | 0 | 367.007 | 0.019647
10843 | 983.5689 | 6.3389 | 70.3392 | 100.2758 | 122.6123 | 10.4503 | 101.7985 | 4.2481 | 13.6618 | 44.2985 | 130.8381 | 12.623 | 434.9791 | 173.2353 | 334.1819 | 9.7486 | 65.085 | 9.5173 | 197 | 48.3322 | 0 | 317.6783 | 0
10844 | 938.243 | 5.0403 | 41.9001 | 93.7782 | 121.6219 | 10.45 | 88.012 | 4.6282 | 10.0815 | 39.5485 | 120.9721 | 7.9209 | 398.3976 | 148.0811 | 284.213 | 9.3631 | 60.7086 | 6.7995 | 182 | 41.1587 | 0 | 284.8641 | 0
10845 | 896.5311 | 4.1415 | 25.6936 | 89.8849 | 120.4048 | 10.45 | 83.9504 | 4.4135 | 8.9493 | 36.6461 | 110.3447 | 7.9885 | 381.7955 | 127.128 | 250.7514 | 9.52 | 58.5876 | 5.6805 | 173 | 32.568 | 0 | 274.181 | 0
10846 | 882.9837 | 3.7243 | 23.3003 | 88.8858 | 117.5351 | 10.45 | 84.7566 | 4.5669 | 7.8976 | 30.4329 | 93.5251 | 8.1106 | 352.2639 | 107.9833 | 236.061 | 9.5916 | 56.9725 | 4.6908 | 144 | 29.6329 | 0 | 267.7876 | 0
10847 | 863.2085 | 2.7248 | 23.327 | 88.7423 | 115.7549 | 9.5003 | 86.255 | 4.6163 | 7.0887 | 25.4803 | 81.2429 | 7.8211 | 347.2095 | 94.2478 | 235.7773 | 9.9944 | 56.0101 | 4.2472 | 124 | 30.1727 | 0 | 267.6775 | 0
10848 | 866.8572 | 2.2807 | 23.2098 | 89.4583 | 111.8005 | 10.4497 | 80.766 | 4.5674 | 6.8784 | 15.7547 | 51.5751 | 7.4118 | 91.881 | 60.1959 | 159.1138 | 9.8758 | 34.8282 | 3.6664 | 114 | 28.7247 | 0 | 134.1273 | 0
10849 | 866.411 | 2.3039 | 23.1831 | 88.6403 | 109.9222 | 9.5003 | 74.323 | 3.9408 | 6.7747 | 24.0959 | 79.4342 | 7.1947 | 312.0105 | 90.3639 | 229.7491 | 9.8606 | 55.0232 | 3.3997 | 108 | 27.0728 | 0 | 263.5001 | 0
10850 | 847.5167 | 2.2973 | 23.1578 | 88.6608 | 106.1711 | 10.4497 | 80.4206 | 3.7103 | 6.9481 | 24.1841 | 82.0639 | 7.1451 | 294.1073 | 86.1504 | 226.2868 | 10.0239 | 54.9632 | 2.8627 | 112 | 26.2122 | 0 | 267.7219 | 0
10851 | 839.1988 | 2.3154 | 23.2606 | 88.873 | 106.059 | 9.5003 | 83.7956 | 4.1411 | 6.8457 | 24.428 | 83.5896 | 7.1595 | 286.9825 | 81.942 | 227.3688 | 9.9991 | 55.0101 | 2.6201 | 102 | 27.2981 | 0 | 270.9548 | 0
10852 | 839.9903 | 3.3292 | 23.2095 | 88.6121 | 102.5946 | 10.4497 | 72.3146 | 4.5594 | 6.7772 | 24.7803 | 83.0746 | 7.2805 | 276.5075 | 80.0862 | 223.7886 | 10.0492 | 55.862 | 2.6098 | 102 | 26.9314 | 0 | 281.1353 | 0
10853 | 855.6412 | 3.9365 | 29.8764 | 88.8048 | 91.1032 | 10.45 | 80.6623 | 4.8833 | 6.8087 | 30.718 | 81.4852 | 9.6047 | 277.2252 | 84.5549 | 221.4089 | 9.7239 | 57.9262 | 2.6365 | 106 | 26.689 | 0 | 308.8145 | 0
10854 | 888.8568 | 5.4482 | 43.6203 | 90.3152 | 82.2507 | 12.3495 | 100.7757 | 5.1947 | 6.8456 | 49.8024 | 87.0074 | 15.7316 | 290.5415 | 123.9536 | 232.1891 | 12.4951 | 57.6235 | 3.1275 | 172 | 35.6998 | 0 | 355.5273 | 0
10855 | 950.2911 | 9.4926 | 72.1814 | 92.8361 | 84.6211 | 18.0484 | 115.3701 | 5.7495 | 10.5337 | 70.9088 | 119.9424 | 27.4476 | 337.2857 | 191.8719 | 282.6027 | 26.9562 | 57.5816 | 5.8409 | 278 | 56.6255 | 0 | 407.2706 | 0.0081724
10856 | 1039.2091 | 13.2633 | 90.111 | 107.2738 | 89.0222 | 20.8992 | 133.7873 | 6.4827 | 14.406 | 81.4911 | 165.0565 | 32.5879 | 392.0811 | 259.2718 | 388.8166 | 35.2648 | 63.9082 | 12.1422 | 301 | 66.2543 | 0 | 471.1648 | 0.025741
10857 | 1145.4811 | 12.5394 | 99.0187 | 123.2137 | 91.646 | 20.9 | 155.9336 | 6.6025 | 22.4065 | 84.8563 | 189.2857 | 36.5147 | 452.1848 | 310.8089 | 504.6301 | 40.139 | 74.2612 | 15.9715 | 383 | 71.7248 | 0 | 536.2016 | 0.05743
10858 | 1198.4981 | 8.9218 | 99.6904 | 129.1213 | 88.6367 | 25.6487 | 163.0797 | 6.809 | 25.5042 | 86.8897 | 195.0915 | 40.6312 | 512.4778 | 339.0947 | 570.3476 | 41.073 | 82.3012 | 17.5029 | 357 | 74.8651 | 0 | 576.2343 | 0.041083
10859 | 1220.5075 | 7.5439 | 103.7575 | 133.2684 | 95.5508 | 20.9013 | 165.8707 | 7.2911 | 26.0488 | 95.2323 | 194.5976 | 40.2924 | 535.7398 | 358.488 | 594.5842 | 41.9344 | 90.3993 | 17.9208 | 348 | 84.5007 | 0 | 614.5934 | 0.049758
10860 | 1207.6235 | 11.258 | 100.5576 | 130.4536 | 98.1366 | 19.9503 | 166.5383 | 7.568 | 23.756 | 100.9824 | 193.5699 | 39.647 | 554.3923 | 363.3369 | 599.3042 | 43.4014 | 101.8829 | 18.357 | 402 | 77.8078 | 0 | 630.1201 | 0.053748
10861 | 1224.8427 | 7.8393 | 98.3412 | 134.6543 | 98.1622 | 20.8997 | 172.0211 | 7.0925 | 18.7352 | 98.9161 | 194.166 | 39.6592 | 544.6856 | 355.8672 | 593.039 | 46.0654 | 110.4174 | 18.4357 | 316 | 79.0076 | 0 | 616.2128 | 0.05076
10862 | 1226.1328 | 4.5903 | 95.7838 | 138.352 | 98.7578 | 19.9503 | 173.6417 | 7.11 | 22.2857 | 97.5619 | 196.3781 | 39.4768 | 547.0182 | 353.7283 | 584.4635 | 46.0019 | 114.0068 | 18.4533 | 273 | 77.1 | 0 | 628.0494 | 0.1541
10863 | 1193.2247 | 5.3492 | 99.1011 | 136.1327 | 101.7301 | 19.95 | 167.1764 | 7.0751 | 20.8298 | 97.2186 | 197.5754 | 38.4058 | 549.1178 | 353.4593 | 580.0047 | 43.8105 | 114.889 | 19.1262 | 235 | 75.0206 | 0 | 624.4233 | 0.046017
10864 | 1141.401 | 4.9315 | 87.8728 | 130.578 | 112.2006 | 16.1511 | 151.5855 | 6.5129 | 15.0855 | 99.4013 | 194.5358 | 36.7414 | 547.3923 | 337.3007 | 543.3022 | 36.1254 | 114.3328 | 18.7957 | 243 | 65.2477 | 0 | 572.1595 | 0.025351
10865 | 1088.0882 | 4.6013 | 75.0424 | 114.36 | 118.9365 | 13.3008 | 137.076 | 5.7494 | 11.617 | 91.9694 | 181.9824 | 32.2579 | 525.0391 | 288.1163 | 465.9901 | 18.9514 | 110.935 | 17.0607 | 233 | 59.0437 | 0 | 463.886 | 0.013889
10866 | 1036.0619 | 11.9946 | 70.5866 | 99.9934 | 123.1375 | 10.4508 | 125.2524 | 4.9935 | 10.1174 | 71.3505 | 157.5285 | 24.022 | 467.7759 | 222.273 | 384.704 | 11.6337 | 104.5996 | 14.2861 | 203 | 50.6709 | 0 | 365.2374 | 0.0050795
10867 | 989.6773 | 9.2834 | 61.2524 | 97.1032 | 124.2806 | 10.45 | 100.4137 | 4.3776 | 8.321 | 54.2702 | 134.7141 | 11.5863 | 428.8963 | 174.8332 | 331.6361 | 10.1126 | 92.2834 | 8.6862 | 185 | 43.073 | 0 | 317.4581 | 0
10868 | 952.8089 | 8.9368 | 32.8182 | 94.1316 | 125.9819 | 9.5003 | 96.1934 | 3.9084 | 6.7592 | 44.8136 | 124.5356 | 7.9145 | 408.1541 | 151.2916 | 293.9783 | 9.4851 | 71.655 | 5.8822 | 172 | 36.7564 | 0 | 285.7116 | 0
10869 | 919.7473 | 7.4875 | 23.4539 | 90.5577 | 121.877 | 10.4497 | 98.4709 | 3.85 | 6.6025 | 36.9434 | 114.4019 | 7.9823 | 392.9067 | 134.07 | 259.0063 | 9.6626 | 56.5871 | 5.1927 | 162 | 31.8557 | 0 | 272.7187 | 0
10870 | 892.1882 | 6.4247 | 23.8429 | 89.4175 | 118.234 | 9.5003 | 80.4219 | 4.5743 | 6.5065 | 29.6256 | 97.1958 | 7.8883 | 356.4778 | 120.375 | 234.0559 | 9.6585 | 53.0131 | 4.7728 | 145 | 29.9205 | 0 | 264.9387 | 0
10871 | 870.1888 | 3.8181 | 23.7873 | 89.0825 | 113.3308 | 10.4497 | 69.6143 | 4.8203 | 6.3368 | 25.5149 | 84.6704 | 7.8925 | 338.6927 | 112.3848 | 222.5137 | 9.7614 | 52.7302 | 4.5937 | 131 | 29.0461 | 0 | 262.5929 | 0
10872 | 872.76 | 2.9036 | 23.7435 | 89.6296 | 109.8561 | 10.45 | 78.6882 | 4.7917 | 6.042 | 16.009 | 54.0161 | 7.8421 | 88.9193 | 69.3636 | 154.5657 | 9.6954 | 33.2069 | 4.4724 | 119 | 28.8959 | 0 | 136.1032 | 0
10873 | 861.0082 | 2.7928 | 23.6507 | 90.5414 | 107.5931 | 9.5003 | 79.2865 | 5.0016 | 5.9055 | 24.3061 | 81.4831 | 7.8938 | 312.5785 | 102.2552 | 232.0799 | 9.6003 | 52.6514 | 4.3421 | 106 | 28.4576 | 0 | 267.5809 | 0
10874 | 852.4683 | 2.4292 | 23.7673 | 89.8374 | 103.9391 | 10.4497 | 69.8312 | 4.9858 | 6.0601 | 24.3316 | 81.3639 | 7.7298 | 306.4636 | 99.8592 | 236.6652 | 9.6074 | 52.2972 | 3.8558 | 103 | 29.0555 | 0 | 271.0295 | 0
10875 | 852.245 | 2.3244 | 23.628 | 90.5875 | 93.5299 | 10.45 | 70.6577 | 4.628 | 6.016 | 24.1918 | 81.2065 | 7.6713 | 300.4148 | 99.7713 | 232.3377 | 9.74 | 51.8909 | 3.12 | 102 | 27.959 | 0 | 271.4935 | 0
10876 | 850.7534 | 2.7628 | 23.7546 | 90.1431 | 97.8458 | 9.5003 | 77.7044 | 4.1326 | 5.9557 | 24.1024 | 81.064 | 7.6916 | 294.3973 | 99.7028 | 221.1319 | 9.6387 | 52.6319 | 2.9133 | 102 | 28.6829 | 0 | 279.8622 | 0
10877 | 864.4453 | 3.916 | 30.6861 | 89.0443 | 97.5543 | 10.4497 | 78.7219 | 3.9977 | 5.821 | 32.6342 | 81.196 | 8.9717 | 299.4008 | 102.8831 | 215.4019 | 9.7061 | 54.6099 | 3.0049 | 103 | 27.7123 | 0 | 310.6805 | 0
10878 | 915.9237 | 5.3908 | 44.761 | 94.8927 | 90.2749 | 11.3997 | 84.8088 | 4.409 | 7.404 | 51.2593 | 86.8106 | 15.7651 | 309.1769 | 136.6875 | 226.9564 | 11.9591 | 54.2822 | 5.0264 | 179 | 31.506 | 0 | 357.4995 | 0
10879 | 970.3479 | 9.4748 | 76.5787 | 95.612 | 77.9757 | 18.9979 | 112.5611 | 5.5818 | 9.1393 | 68.2331 | 113.8004 | 30.3046 | 352.952 | 199.2468 | 280.168 | 27.5629 | 54.5643 | 9.2742 | 262 | 54.3987 | 0 | 406.7033 | 0.018524
10880 | 1059.5268 | 16.5757 | 93.1241 | 109.3006 | 82.9987 | 18.0503 | 136.583 | 6.7369 | 13.5475 | 76.8892 | 154.509 | 35.5389 | 396.0767 | 257.579 | 386.8213 | 38.4258 | 60.5667 | 15.9784 | 274 | 63.0244 | 0 | 469.2577 | 0.045565
10881 | 1151.4179 | 16.7853 | 101.8 | 124.4689 | 85.7709 | 19.9495 | 144.8489 | 7.3008 | 21.7166 | 79.8339 | 181.5983 | 37.6688 | 446.5871 | 300.9128 | 497.5077 | 42.3356 | 69.3397 | 18.4424 | 330 | 66.9276 | 0 | 545.5477 | 0.058261
10882 | 1185.8135 | 16.7156 | 101.498 | 128.5267 | 77.4072 | 20.8997 | 156.6774 | 7.3266 | 21.7166 | 85.6732 | 193.25 | 42.4652 | 506.4861 | 336.909 | 568.5903 | 43.1735 | 77.223 | 18.5022 | 348 | 72.515 | 0 | 585.1036 | 0.081157
10883 | 1208.3293 | 10.9881 | 104.0876 | 132.7005 | 84.6433 | 19.9503 | 163.3764 | 7.5229 |  | 95.2773 | 195.6194 | 40.6973 | 539.7889 | 365.4281 | 609.364 | 41.9763 | 83.0619 | 18.9906 | 340 | 83.7222 | 0 | 597.2254 | 0.12696
10884 | 1209.8924 | 9.3225 | 102.0491 | 129.9788 | 92.9173 | 19.0003 | 152.3231 | 7.1899 |  | 93.8535 | 192.9558 | 38.737 | 549.1171 | 370.1476 | 608.6477 | 43.772 | 85.5292 | 18.9044 | 353 | 75.5307 | 0 | 606.4919 | 0.10094
10885 | 1211.4363 | 10.9514 | 99.6665 | 132.467 | 92.8628 | 20.8995 | 157.19 | 7.2502 |  | 85.034 | 193.386 | 40.9611 | 558.8314 | 360.4172 | 589.2332 | 45.0109 | 87.3259 | 17.9853 | 277 | 75.2159 | 0 | 617.2371 | 0.090843
10886 | 1226.2161 | 9.9244 | 100.6856 | 140.3542 | 97.4422 | 19.0005 | 166.5517 | 7.3465 |  | 88.8762 | 195.6672 | 40.9947 | 618.3317 | 357.7631 | 588.2517 | 43.7882 | 89.6232 | 17.7401 | 264 | 77.6487 | 0 | 623.1235 | 0.11731
10887 | 1204.0094 | 8.7458 | 101.4183 | 137.453 | 98.7799 | 19 | 162.7083 | 7.2686 |  | 95.3557 | 194.7498 | 39.2727 | 639.7192 | 353.5807 | 599.9578 | 40.4768 | 89.934 | 18.2613 | 271 | 72.1918 | 0 | 592.9146 | 0.0898
10888 | 1160.8668 | 5.805 | 90.4007 | 130.439 | 106.1949 | 12.3518 | 146.2866 | 6.8221 |  | 92.7971 | 190.1827 | 36.9333 | 553.7843 | 335.9652 | 576.7296 | 33.6205 | 88.2441 | 18.1033 | 245 | 60.667 | 0 | 544.4928 | 0.065268
10889 | 1087.6222 | 4.3826 | 76.2068 | 113.8245 | 110.3171 | 11.4003 | 134.725 | 5.7779 |  | 79.8511 | 180.1039 | 32.9124 | 520.1804 | 286.8973 | 494.6267 | 18.9335 | 81.4545 | 16.6324 | 220 | 55.0287 | 0 | 455.021 | 0.045792
10890 | 1031.3745 | 4.2635 | 70.2661 | 98.1917 | 116.0296 | 10.4503 | 124.7505 | 5.4191 |  | 58.4388 | 159.1253 | 26.8758 | 495.19 | 211.512 | 406.0324 | 11.3132 | 71.7435 | 13.3693 | 202 | 49.6182 | 0 | 371.3834 | 0.022862
10891 | 1003.6322 | 5.2042 | 59.1473 | 93.0244 | 116.8595 | 10.45 | 99.8587 | 5.3777 |  | 43.0117 | 138.5824 | 11.5768 | 491.819 | 158.6154 | 347.6088 | 9.6503 | 62.7779 | 8.4369 | 193 | 47.1427 | 0 | 328.1909 | 0
10892 | 977.1915 | 5.6428 | 32.5576 | 91.8408 | 116.2948 | 10.45 | 85.5684 | 5.6643 |  | 40.4759 | 130.0717 | 7.4962 | 376.5382 | 133.5443 | 317.9173 | 9.675 | 56.3354 | 6.2443 | 180 | 39.864 | 0 | 295.4951 | 0
10893 | 939.8001 | 5.0727 | 24.084 | 89.8529 | 116.0742 | 10.45 | 70.87 | 5.8053 |  | 40.6155 | 120.1214 | 8.2212 | 298.3436 | 112.9175 | 302.9749 | 9.4252 | 53.803 | 5.206 | 166 | 37.5995 | 0 | 284.9689 | 0
10894 | 918.2013 | 4.233 | 23.8409 | 88.733 | 116.0239 | 9.5003 | 62.1453 | 5.2897 |  | 36.7496 | 102.3042 | 8.224 | 268.7342 | 95.7225 | 290.5537 | 9.4306 | 52.8085 | 4.6649 | 143 | 32.3382 | 0 | 278.8378 | 0
10895 | 901.5563 | 3.6617 | 24.0124 | 89.2765 | 113.3119 | 10.4497 | 72.4012 | 5.4555 |  | 32.4299 | 89.3779 | 8.0506 | 236.5173 | 86.4926 | 271.7519 | 9.5418 | 52.5453 | 4.1495 | 129 | 29.4408 | 0 | 277.6357 | 0
10896 | 902.2975 | 3.1263 | 24.0141 | 89.7658 | 112.2859 | 9.5003 | 70.2859 | 5.5663 |  | 19.2281 | 57.5709 | 7.9835 | 56.9286 | 55.1461 | 172.6196 | 9.5849 | 33.1793 | 3.7087 | 115 | 27.047 | 0 | 138.1605 | 0
10897 | 889.8691 | 2.706 | 24.0079 | 90.8903 | 110.1083 | 9.5 | 63.1841 | 5.4716 |  | 27.8168 | 87.079 | 7.8854 | 209.8892 | 83.7941 | 241.9079 | 9.5169 | 52.5756 | 3.6482 | 111 | 27.7772 | 0 | 273.0482 | 0
10898 | 880.9118 | 2.4137 | 23.9971 | 91.1822 | 106.0553 | 10.4497 | 68.3608 | 5.7707 |  | 27.5058 | 87.0344 | 8.1256 | 203.169 | 83.0181 | 237.5381 | 9.3221 | 52.471 | 3.3306 | 107 | 27.8316 | 0 | 277.4078 | 0
10899 | 879.0346 | 2.4689 | 23.9654 | 91.2914 | 102.9293 | 10.45 | 73.5228 | 5.2653 |  | 27.5318 | 86.3145 | 8.1602 | 199.9994 | 82.9051 | 232.7106 | 9.5308 | 52.262 | 3.0388 | 106 | 27.5737 | 0 | 277.4507 | 0
10900 | 871.3765 | 2.8366 | 23.9006 | 91.2887 | 94.9598 | 10.45 | 63.775 | 4.7478 |  | 27.5576 | 85.8431 | 7.6697 | 195.4595 | 81.5158 | 225.9555 | 9.4844 | 52.9048 | 2.9644 | 104 | 27.5336 | 0 | 286.627 | 0
10901 | 882.8094 | 3.7286 | 30.6236 | 91.3052 | 86.3057 | 10.45 | 68.3077 | 4.6561 |  | 33.2936 | 86.1694 | 10.8263 | 183.7236 | 84.6724 | 222.4051 | 9.5353 | 54.8512 | 3.1945 | 107 | 27.454 | 0 | 319.6293 | 0
10902 | 922.2403 | 5.1967 | 45.7696 | 95.8705 | 82.7806 | 12.3495 | 93.05 | 4.5506 |  | 51.9805 | 93.0168 | 15.45 | 186.999 | 126.5972 | 228.9918 | 12.2107 | 54.3638 | 4.1068 | 183 | 35.8759 | 0 | 372.2461 | 0
10903 | 979.9503 | 7.8446 | 75.6035 | 98.2915 | 78.4349 | 16.1489 | 106.0256 | 5.7551 |  | 72.5037 | 121.0405 | 28.2716 | 224.9179 | 190.4537 | 270.0794 | 27.8866 | 53.9215 | 6.3726 | 282 | 54.2703 | 0 | 414.6085 | 0.028937
10904 | 1063.9687 | 9.6506 | 91.3814 | 114.8936 | 80.1229 | 18.0495 | 115.9727 | 7.4075 |  | 79.6754 | 161.2416 | 35.1362 | 283.9894 | 245.4559 | 354.8693 | 35.5721 | 59.8913 | 12.1264 | 290 | 65.7702 | 0 | 485.1735 | 0.079002
10905 | 1158.9359 | 7.8639 | 97.9968 | 127.7687 | 76.5069 | 18.05 | 144.8947 | 7.9477 |  | 86.2038 | 186.5377 | 34.173 | 343.9526 | 292.9636 | 453.6266 | 38.9647 | 68.5879 | 18.0259 | 342 | 69.7296 | 0 | 600.287 | 0.11676
10906 | 1187.654 | 5.4913 | 102.0167 | 132.4518 | 78.1928 | 19.9495 | 154.0661 | 7.6492 |  | 95.3974 | 195.536 | 30.0132 | 392.5854 | 328.7845 | 523.2117 | 40.5678 | 76.835 | 18.159 | 348 | 70.8909 | 0 | 663.9341 | 0.15339
10907 | 1228.6412 | 8.9889 | 102.4303 | 134.5007 | 87.0009 | 21.8495 | 145.8687 | 7.6344 |  | 97.6241 | 198.4461 | 32.5539 | 414.8492 | 348.8989 | 557.5524 | 42.4947 | 82.8121 | 18.5231 | 350 | 82.3877 | 0 | 668.9871 | 0.11695
10908 | 1216.2745 | 11.2146 | 99.6436 | 133.2911 | 94.8159 | 19.0008 | 147.0031 | 8.1304 |  | 97.9106 | 197.4994 | 37.765 | 424.874 | 350.8387 | 578.4742 | 43.3847 | 82.9232 | 19.2148 | 379 | 70.9994 | 0 | 668.9851 | 0.088036
10909 | 1217.7165 | 11.073 | 99.6668 | 137.062 | 96.4169 | 19.9497 | 149.3898 | 8.8918 |  | 97.3991 | 196.3613 | 41.4853 | 418.2223 | 351.0344 | 582.4333 | 43.007 | 82.1473 | 18.9282 | 325 | 74.7968 | 0 | 679.5825 | 0.092
10910 | 1237.4593 | 10.8649 | 99.7736 | 134.3768 | 100.5639 | 18.0505 | 149.4992 | 8.8364 |  | 95.1307 | 197.1663 | 41.3713 | 421.7466 | 357.8208 | 577.0727 | 43.6681 | 83.7055 | 18.4785 | 279 | 76.0345 | 0 | 679.2585 | 0.078668
10911 | 1214.2431 | 7.943 | 98.7673 | 132.9892 | 103.8726 | 18.05 | 151.144 | 7.9068 |  | 92.3844 | 196.3473 | 39.6059 | 432.2251 | 359.4975 | 573.4134 | 42.2404 | 83.7989 | 18.5774 | 288 | 74.3176 | 0 | 643.5569 | 0.07944
10912 | 1149.4429 | 7.4706 | 89.3817 | 127.8081 | 110.4626 | 12.3516 | 145.3611 | 7.1476 |  | 88.467 | 190.9963 | 36.8248 | 426.9909 | 345.6937 | 553.2507 | 33.6133 | 82.3536 | 18.5846 | 254 | 65.125 | 0 | 600.6661 | 0.048786
10913 | 1096.2639 | 6.6609 | 78.4963 | 115.5714 | 109.1972 | 11.4003 | 132.6271 | 6.9777 |  | 81.8099 | 179.8966 | 35.2383 | 405.1328 | 304.3102 | 485.3595 | 18.4137 | 78.1416 | 17.7659 | 217 | 50.8124 | 0 | 513.6113 | 0.030338
10914 | 1031.5968 | 5.4192 | 76.1684 | 102.8259 | 105.941 | 10.4503 | 115.8406 | 4.1902 |  | 64.301 | 160.6373 | 28.7325 | 358.3491 | 226.0702 | 394.5409 | 10.9578 | 70.2769 | 14.0136 | 205 | 57.2858 | 0 | 419.0918 | 0.0098128
10915 | 982.1356 | 5.072 | 68.5498 | 95.4783 | 92.3581 | 9.5003 | 93.9191 | 3.3072 |  | 44.6688 | 141.8692 | 16.4672 | 297.8476 | 156.2157 | 329.622 | 9.4112 | 61.9994 | 7.7601 | 182 | 50.5968 | 0 | 365.7919 | 0
10916 | 959.3951 | 7.8244 | 38.5015 | 92.9119 | 85.0228 | 9.5 | 94.645 | 4.1981 |  | 38.201 | 130.3856 | 8.6999 | 253.9597 | 126.2328 | 281.0273 | 9.2752 | 56.4615 | 5.1623 | 173 | 43.8649 | 0 | 332.2705 | 0
10917 | 930.5724 | 10.8434 | 25.0036 | 90.6387 | 83.7321 | 10.4497 | 94.0483 | 4.3897 |  | 35.8782 | 116.747 | 6.9059 | 233.8175 | 111.7433 | 252.805 | 9.1316 | 54.4892 | 4.5769 | 163 | 40.3912 | 0 | 319.6722 | 0
10918 | 901.4699 | 10.9545 | 24.1637 | 90.0344 | 84.0073 | 9.5003 | 85.1356 | 4.2781 |  | 32.946 | 99.9 | 6.8824 | 209.3693 | 100.0853 | 246.4874 | 8.8744 | 54.1563 | 3.6012 | 143 | 35.8795 | 0 | 305.9559 | 0
10919 | 883.4177 | 7.0587 | 24.0872 | 90.0016 | 83.8998 | 9.5 | 81.2282 | 4.1842 |  | 30.6765 | 88.6053 | 6.8702 | 192.0257 | 92.7146 | 241.7854 | 9.0181 | 54.0814 | 3.1886 | 121 | 34.394 | 0 | 304.0203 | 0
10920 | 885.7128 | 3.3167 | 23.7165 | 90.5016 | 84.0062 | 9.5 | 80.1861 | 3.6519 |  | 18.0705 | 55.7789 | 7.1641 | 50.0457 | 57.8213 | 155.8515 | 9.1318 | 34.0263 | 3 | 108 | 30.6375 | 0 | 159.2248 | 0
10921 | 880.5806 | 2.2755 | 23.8329 | 90.3127 | 83.8752 | 9.5 | 79.4036 | 3.4233 |  | 26.0216 | 84.0722 | 6.7941 | 183.1631 | 85.7332 | 221.4914 | 9.0503 | 53.8919 | 3.0821 | 108 | 30.1653 | 0 | 308.9584 | 0
10922 | 864.788 | 2.2981 | 24.0816 | 90.0747 | 84.0735 | 9.5 | 79.0768 | 4.0624 |  | 25.275 | 85.18 | 6.6731 | 184.0174 | 82.6816 | 219.4019 | 9.1038 | 53.924 | 3.0255 | 106 | 29.8794 | 0 | 309.2108 | 0
10923 | 855.9717 | 2.2871 | 24.261 | 90.5755 | 84.1514 | 9.5 | 79.0213 | 4.3301 |  | 24.3242 | 86.1246 | 6.7859 | 180.2495 | 81.795 | 217.7516 | 8.8004 | 53.7928 | 2.9065 | 103 | 29.4438 | 0 | 313.3356 | 0
10924 | 850.0935 | 2.731 | 24.0026 | 90.4987 | 84.53 | 9.5 | 78.7521 | 4.335 |  | 23.533 | 91.8348 | 6.6448 | 169.268 | 82.2288 | 211.3595 | 8.8551 | 54.5952 | 2.8558 | 101 | 29.0671 | 0 | 324.5676 | 0
10925 | 869.9744 | 4.2866 | 34.1413 | 90.4559 | 84.8637 | 9.5 | 84.6462 | 4.5327 |  | 30.3865 | 96.4257 | 8.1477 | 163.1849 | 86.4023 | 207.529 | 8.9715 | 56.6595 | 2.8833 | 107 | 29.2332 | 0 | 356.2952 | 0
10926 | 914.1943 | 5.1942 | 53.1084 | 94.7406 | 80.9107 | 12.3492 | 98.5654 | 3.7295 |  | 51.2543 | 96.914 | 16.0849 | 167.0418 | 127.5484 | 221.8897 | 11.6236 | 55.9121 | 2.9017 | 159 | 34.1901 | 0 | 401.6366 | 0
10927 | 962.2846 | 9.7647 | 81.0602 | 96.8771 | 75.2425 | 17.0987 | 116.584 | 3.7877 |  | 72.7443 | 117.8161 | 28.356 | 217.3941 | 197.0735 | 281.1806 | 27.1286 | 55.8525 | 5.7164 | 232 | 56.4435 | 0 | 448.1182 | 0.020081
10928 | 1040.3476 | 18.1473 | 94.4512 | 110.3986 | 72.7064 | 19.9492 | 134.4037 | 5.4631 |  | 82.9083 | 154.5107 | 33.9873 | 276.4627 | 260.8982 | 394.9078 | 36.9759 | 62.7657 | 15.9565 | 293 | 64.2085 | 0 | 513.5586 | 0.044487
10929 | 1113.3986 | 16.3826 | 99.976 | 127.3122 | 75.6795 | 19.0003 | 147.8035 | 6.4458 |  | 85.6435 | 180.3208 | 35.2535 | 337.45 | 307.693 | 513.7585 | 41.4632 | 72.3035 | 18.5826 | 359 | 76.1322 | 0 | 589.4385 | 0.064083
10930 | 1175.4415 | 10.5734 | 100.6359 | 134.1055 | 82.5699 | 22.7989 | 151.9717 | 6.5432 |  | 87.3931 | 193.1192 | 37.626 | 386.093 | 334.7822 | 578.5961 | 43.3179 | 88.0549 | 18.2014 | 373 | 82.154 | 0 | 623.8749 | 0.081883
10931 | 1203.7455 | 13.668 | 103.9854 | 137.3552 | 94.512 | 18.0513 | 151.9962 | 6.9746 |  | 88.7877 | 197.1588 | 41.0732 | 425.7732 | 353.8977 | 597.973 | 42.491 | 102.9499 | 18.3659 | 357 | 84.4344 | 0 | 632.01 | 0.0923
10932 | 1196.7887 | 19.941 | 105.1067 | 132.9237 | 95.7289 | 18.05 | 133.8062 | 8.1346 |  | 84.8522 | 196.8721 | 43.697 | 448.8042 | 358.5629 | 588.9447 | 42.4309 | 103.8645 | 18.8197 | 378 | 66.3279 | 0 | 637.058 | 0.10657
10933 | 1183.6089 | 18.2749 | 104.8391 | 138.2513 | 95.8419 | 18.05 | 132.4644 | 7.7298 |  | 73.9839 | 196.9512 | 43.0945 | 449.5054 | 355.9746 | 575.8958 | 42.0315 | 101.1171 | 19.151 | 288 | 65.2748 | 0 | 637.7733 | 0.10732
10934 | 1185.0338 | 15.4583 | 102.7074 | 138.544 | 94.7233 | 18.9997 | 135.0397 | 6.504 |  | 68.7973 | 192.418 | 41.7267 | 496.6862 | 358.9865 | 571.0458 | 39.6297 | 100.9344 | 19.4839 | 263 | 61.6762 | 0 | 642.1073 | 0.084591
10935 | 1173.3389 | 12.7917 | 98.4308 | 134.4701 | 93.9871 | 25.6482 | 132.642 | 4.6326 |  | 73.3185 | 182.7002 | 37.5388 | 523.5207 | 352.2042 | 557.8278 | 36.9683 | 97.3107 | 19.2457 | 261 | 54.7996 | 0 | 623.3282 | 0.08341
10936 | 1117.0754 | 6.7248 | 94.2127 | 125.4335 | 116.5548 | 8.5548 | 128.7632 | 3.2208 |  | 73.1799 | 175.1624 | 30.7464 | 561.9398 | 321.5322 | 512.2184 | 29.4039 | 88.0953 | 18.4873 | 249 | 43.7601 | 0 | 562.428 | 0.074661
10937 | 1042.8708 | 3.756 | 80.9409 | 115.5369 | 111.7379 | 9.4997 | 113.698 | 2.9783 |  | 64.5175 | 163.9254 | 25.683 | 529.277 | 261.367 | 420.8258 | 17.2106 | 76.4451 | 17.1015 | 251 | 41.7201 | 0 | 465.35 | 0.048046
10938 | 985.3457 | 3.456 | 48.848 | 104.0875 | 113.2552 | 4.7513 | 92.668 | 2.7484 |  | 49.8678 | 142.412 | 20.331 | 388.7092 | 180.9653 | 349.0634 | 13.1603 | 67.2931 | 13.4681 | 213 | 45.0373 | 0 | 381.8574 | 0.023823
10939 | 964.646 | 4.3317 | 38.0714 | 98.0741 | 111.3489 | 5.7013 | 71.5759 | 2.4924 |  | 39.0755 | 121.673 | 10.7688 | 319.3332 | 124.1335 | 315.6519 | 11.5479 | 61.9015 | 7.6141 | 181 | 45.7806 | 0 | 339.3616 | 0
10940 | 948.8965 | 4.6411 | 29.5896 | 100.1964 | 111.6484 | 4.7487 | 66.8521 | 3.2913 |  | 38.2117 | 101.6412 | 8.0328 | 287.3694 | 111.7814 | 284.7331 | 11.1368 | 59.7613 | 5.4551 | 163 | 44.0156 | 0 | 320.9597 | 0
10941 | 915.7016 | 4.7856 | 23.7757 | 99.3884 | 111.5998 | 4.75 | 64.9327 | 3.6644 |  | 35.4183 | 84.382 | 7.7766 | 263.157 | 108.1734 | 261.3583 | 10.1096 | 58.5365 | 4.8472 | 147 | 37.8771 | 0 | 307.0011 | 0
10942 | 900.0595 | 4.1258 | 22.6419 | 97.1849 | 99.4799 | 4.75 | 55.6464 | 2.6808 |  | 29.5923 | 78.8172 | 7.629 | 243.8201 | 97.3842 | 255.9902 | 9.5086 | 56.477 | 4.2986 | 146 | 35.3416 | 0 | 299.714 | 0
10943 | 869.0113 | 3.1074 | 22.5537 | 97.5806 | 90.9219 | 4.75 | 55.123 | 3.331 |  | 27.8016 | 77.0286 | 10.8785 | 221.9031 | 90.8104 | 258.7631 | 9.0596 | 55.3995 | 3.3772 | 134 | 33.7591 | 0 | 298.877 | 0
10944 | 904.2482 | 2.6087 | 23.0097 | 97.4069 |  | 5.6997 | 57.5071 | 3.7752 |  | 17.1801 | 49.2974 | 8.9457 | 56.4267 | 57.227 | 167.4017 | 9.2249 | 34.1249 | 2.9031 | 135 | 33.4249 | 0 |  | 0
10945 | 898.4981 | 2.5994 | 22.8308 | 96.735 |  | 4.7503 | 57.6169 | 2.911 |  | 26.0725 | 73.3888 | 7.4024 | 209.7799 | 90.2528 | 240.0154 | 9.2398 | 54.163 | 2.8579 | 123 | 34.9154 | 0 |  | 0
10946 | 872.3673 | 2.3485 | 22.6181 | 96.8802 |  | 4.75 | 61.8847 | 2.9676 |  | 25.6493 | 71.6663 | 7.4156 | 200.4058 | 92.6224 | 240.8239 | 9.2782 | 54.2686 | 2.8745 | 126 | 30.8569 | 0 |  | 0
10947 | 864.8322 | 2.2424 | 22.6219 | 97.249 |  | 4.75 | 58.0769 | 3.8303 |  | 24.9578 | 70.725 | 7.989 | 195.0657 | 92.6857 | 239.4457 | 9.1845 | 54.265 | 2.8646 | 133 | 29.1974 | 0 |  | 0
10948 | 864.6049 | 2.6778 | 22.9826 | 97.4671 |  | 4.75 | 68.9322 | 3.9296 |  | 24.1204 | 70.6721 | 7.5943 | 189.3596 | 92.3247 | 226.7226 | 8.9981 | 54.9478 | 2.8399 | 126 | 30.9403 | 0 |  | 0
10949 | 866.5915 | 3.5798 | 23.5698 | 96.6557 |  | 4.75 | 75.2813 | 2.8055 |  | 23.7434 | 71.6993 | 7.2758 | 184.3394 | 90.9647 | 217.4065 | 8.9643 | 57.5067 | 2.8126 | 121 | 31.0008 | 0 |  | 0
10950 | 878.0672 | 3.9494 | 36.1619 | 96.5581 |  | 5.6997 | 74.273 | 3.1232 |  | 22.7977 | 72.1461 | 6.8787 | 180.6795 | 89.961 | 214.2239 | 8.9335 | 56.9552 | 2.7869 | 122 | 30.6872 | 0 |  | 0
10951 | 883.8659 | 5.013 | 45.2504 | 95.4711 |  | 4.7503 | 75.5099 | 3.454 |  | 25.2428 | 73.7893 | 9.3342 | 180.1758 | 89.9038 | 209.8147 | 8.6081 | 53.4576 | 2.9422 | 125 | 47.5403 | 0 |  | 0.021566
10952 | 886.9311 | 4.2363 | 55.5399 | 93.9361 |  | 6.6495 | 83.935 | 3.5534 |  | 38.8386 | 85.1474 | 14.7309 | 189.872 | 88.4486 | 207.1484 | 8.5819 | 52.2107 | 3.4208 | 146 | 56.0882 | 0 |  | 0.074907
10953 | 916.2946 | 2.5605 | 70.7108 | 93.3764 |  | 5.7003 | 86.8673 | 3.0294 |  | 56.7381 | 104.4156 | 19.4992 | 199.9484 | 98.8782 | 210.8426 | 8.3099 | 52.0687 | 5.5046 | 134 | 55.3963 | 0 |  | 0.079704
10954 | 934.3959 | 5.2108 | 82.4996 | 95.3928 |  | 5.7 | 83.8325 | 2.4142 |  | 69.4178 | 121.5843 | 21.0882 | 207.1928 | 118.7804 | 220.2693 | 8.4299 | 52.8983 | 10.7469 | 142 | 53.8825 | 0 |  | 0.094405
10955 | 943.3619 | 8.3428 | 84.6644 | 97.9959 |  | 5.7 | 87.6903 | 3.5004 |  | 73.78 | 122.17 | 18.3022 | 227.8817 | 130.3965 | 231.2752 | 8.4986 | 53.8446 | 12.7944 | 141 | 55.7102 | 0 |  | 0.12703
10956 | 944.0584 | 9.4761 | 84.038 | 97.5555 |  | 5.7 | 78.4466 | 4.0423 |  | 70.2684 | 110.7032 | 17.7017 | 244.4667 | 138.21 | 237.0636 | 8.5409 | 53.7584 | 13.0474 | 142 | 57.5228 | 0 |  | 0.10551
10957 | 941.4064 | 5.8876 | 75.4937 | 98.4094 |  | 4.7503 | 84.7725 | 3.121 |  | 65.3967 | 106.2367 | 20.5542 | 250.3936 | 139.0074 | 242.1776 | 8.6071 | 54.2287 | 13.4928 | 142 | 56.4583 | 0 |  | 0.094443
10958 | 939.085 | 2.9351 | 38.7234 | 101.3294 |  | 5.6997 | 91.7592 | 2.011 |  | 63.6438 | 108.8412 | 23.6581 | 249.6967 | 134.5681 | 249.1248 | 8.3019 | 54.7943 | 11.5075 | 150 | 49.6001 | 0 |  | 0.084316
10959 | 959.514 | 2.809 | 23.8766 | 101.7626 |  | 4.7503 | 92.0102 | 2.5358 |  | 61.4113 | 112.7593 | 20.8515 | 248.234 | 126.1589 | 262.4416 | 8.4883 | 54.3299 | 6.2243 | 162 | 53.1286 | 0 |  | 0.073927
10960 | 959.2087 | 2.8396 | 22.5926 | 97.5237 |  | 4.75 | 81.4106 | 2.0058 |  | 51.187 | 113.8612 | 11.0038 | 246.5157 | 111.2058 | 271.074 | 8.4467 | 53.3364 | 4.3337 | 157 | 43.7079 | 0 |  | 0.05022
10961 | 952.8143 | 2.6648 | 22.7896 | 97.3537 |  | 4.75 | 83.5206 | 2.565 |  | 34.1147 | 107.6665 | 7.5779 | 242.476 | 103.2398 | 267.117 | 8.5555 | 52.9307 | 4.4831 | 166 | 36.2611 | 0 |  | 0.030122
10962 | 934.8387 | 2.3633 | 22.4345 | 97.5219 |  | 4.75 | 71.9258 | 3.1865 |  | 21.809 | 90.3534 | 8.5868 | 238.5244 | 104.1542 | 261.9607 | 8.5206 | 53.1126 | 4.6851 | 173 | 32.2954 | 0 |  | 0.012455
10963 | 915.0825 | 3.7617 | 22.7024 | 99.7961 |  | 4.75 | 79.278 | 3.5342 |  | 19.4252 | 74.6157 | 9.4142 | 227.8884 | 102.7575 | 257.8483 | 8.3424 | 53.3551 | 4.6087 | 200 | 31.4591 | 0 |  | 0
10964 | 904.7907 | 4.3459 | 23.2042 | 104.6878 |  | 4.75 | 89.9334 | 3.8002 |  | 21.9198 | 73.1 | 9.7198 | 215.8568 | 96.5187 | 250.3319 | 8.8559 | 53.6659 | 4.4433 | 217 | 34.1481 | 0 |  | 0
10965 | 881.3599 | 4.3797 | 23.6917 | 102.7147 |  | 5.6997 | 81.3178 | 3.3977 |  | 24.8489 | 75.971 | 8.5101 | 209.9979 | 92.1434 | 245.6763 | 8.9135 | 53.6891 | 4.0168 | 212 | 32.7641 | 0 |  | 0
10966 | 871.3704 | 3.8258 | 23.8415 | 100.1256 |  | 4.7503 | 76.2311 | 3.386 |  | 25.3258 | 75.1149 | 7.9601 | 205.9853 | 88.4341 | 245.4194 | 9.0358 | 53.5081 | 3.8476 | 197 | 33.4269 | 0 |  | 0
10967 | 857.9812 | 2.8411 | 23.7979 | 97.5823 |  | 4.75 | 75.2863 | 4.0547 |  | 26.8164 | 73.4974 | 8.0382 | 193.2426 | 90.4326 | 248.4088 | 8.9552 | 53.4509 | 3.6379 | 184 | 33.4168 | 0 |  | 0
10968 | 886.4107 | 2.4218 | 23.7907 | 96.9238 |  | 5.6997 | 75.6061 | 4.3096 |  | 18.1862 | 48.0706 | 8.3985 | 49.6343 | 60.8709 | 164.9277 | 8.8128 | 33.7429 | 3.5254 | 178 | 32.8009 | 0 |  | 0
10969 | 883.4209 | 2.4365 | 24.301 | 97.0414 |  | 5.7 | 75.4457 | 4.6893 |  | 28.6919 | 72.8423 | 7.9097 | 182.9727 | 94.3628 | 240.5177 | 8.8388 | 53.9847 | 3.1675 | 178 | 32.4799 | 0 |  | 0
10970 | 870.3933 | 2.4409 | 24.402 | 96.4099 |  | 11.3984 | 74.9406 | 4.5735 |  | 27.2538 | 72.7248 | 7.5048 | 187.1451 | 92.007 | 240.9103 | 8.9838 | 54.088 | 3.2105 | 173 | 34.4988 | 0 |  | 0
10971 | 858.8067 | 2.3348 | 24.1622 | 96.9383 |  | 9.5005 | 74.3861 | 4.2866 |  | 26.0008 | 72.6018 | 7.9082 | 189.1082 | 92.1681 | 238.6141 | 9.0697 | 53.721 | 3.5202 | 153 | 33.6278 | 0 |  | 0
10972 | 855.4404 | 2.7982 | 24.0867 | 97.2258 |  | 10.4497 | 71.8237 | 3.7797 |  | 26.0482 | 72.9737 | 8.1181 | 182.2754 | 92.6945 | 227.5911 | 8.9352 | 54.4304 | 3.1117 | 136 | 38.8528 | 0 |  | 0
10973 | 856.7347 | 3.8122 | 24.1824 | 96.8107 |  | 4.7516 | 66.9802 | 3.555 |  | 25.3866 | 77.6826 | 7.6174 | 178.8273 | 91.3015 | 216.8194 | 8.7777 | 56.4204 | 2.8128 | 121 | 42.7068 | 0 |  | 0
10974 | 868.8348 | 4.1211 | 23.9689 | 96.1111 |  | 5.6997 | 71.2667 | 3.9386 |  | 22.9393 | 79.5891 | 6.3642 | 177.9209 | 89.5087 | 209.6899 | 8.6075 | 55.801 | 2.7462 | 122 | 32.9157 | 0 |  | 0
10975 | 875.6835 | 3.3384 | 23.4586 | 94.4784 |  | 4.7503 | 72.7609 | 4.2536 |  | 20.1911 | 73.8837 | 4.9972 | 175.7998 | 88.11 | 202.7232 | 8.5349 | 52.999 | 2.743 | 120 | 34.9487 | 0 |  | 0.023866
10976 | 880.9465 | 2.25 | 23.1888 | 94.6194 |  | 6.6495 | 74.3399 | 4.0434 |  | 23.2331 | 71.7218 | 5.4324 | 179.1188 | 88.1782 | 199.9473 | 8.4607 | 51.8145 | 3.2147 | 122 | 32.8291 | 0 |  | 0.060845
10977 | 885.5648 | 2.0736 | 23.2675 | 93.923 |  | 6.65 | 82.1765 | 3.9282 |  | 35.5016 | 75.2999 | 8.0283 | 181.4082 | 91.1417 | 206.1179 | 8.5343 | 51.9932 | 3.4202 | 183 | 33.4116 | 0 |  | 0.066584
10978 | 898.048 | 2.0822 | 23.3522 | 95.0913 |  | 5.7003 | 97.2596 | 2.2245 |  | 49.2721 | 82.8201 | 8.107 | 187.6354 | 97.2467 | 221.1635 | 8.3278 | 52.2377 | 3.4042 | 192 | 31.1837 | 0 |  | 0.077158
10979 | 912.9965 | 1.9155 | 22.8842 | 98.9957 |  | 4.7503 | 89.8331 | 2.7452 |  | 55.3274 | 91.7657 | 5.4464 | 201.702 | 102.5437 | 233.5701 | 8.389 | 51.9716 | 3.3942 | 162 | 24.495 | 0 |  | 0.18724
10980 | 921.8731 | 2.6056 | 22.5913 | 100.2048 |  | 5.6997 | 80.3076 | 2.6498 |  | 56.1591 | 102.7408 | 6.2175 | 215.4857 | 107.9158 | 246.3667 | 8.5325 | 52.0075 | 3.675 | 197 | 17.6315 | 0 |  | 0.23469
10981 | 927.5329 | 3.0396 | 22.7615 | 99.844 |  | 4.7503 | 87.7525 | 2.5562 |  | 55.1749 | 113.6416 | 6.0263 | 223.1748 | 121.7353 | 256.3894 | 8.5325 | 52.0504 | 4.5787 | 178 | 17.8721 | 0 |  | 0.24639
10982 | 942.0934 | 3.0982 | 22.9531 | 100.4438 |  | 5.6997 | 91.256 | 1.8323 |  | 54.2512 | 118.822 | 7.7819 | 231.4558 | 137.8729 | 259.8082 | 8.6028 | 52.0489 | 4.8902 | 187 | 19.9037 | 0 |  | 0.25066
10983 | 944.7479 | 2.713 | 22.7656 | 97.5022 |  | 4.7503 | 97.4046 | 2.418 |  | 47.6558 | 120.6514 | 8.5047 | 235.1763 | 141.4647 | 261.8751 | 8.3505 | 52.5645 | 4.4902 | 181 | 23.8637 | 0 |  | 0.093565
10984 | 945.7993 | 2.2826 | 22.4643 | 96.1549 |  | 4.75 | 79.4134 | 1.8936 |  | 32.2163 | 120.9714 | 7.8691 | 230.5122 | 137.6086 | 260.6102 | 8.5161 | 52.4028 | 4.0587 | 173 | 27.898 | 0 |  | 0.11366
10985 | 930.4145 | 2.1754 | 22.4569 | 97.8136 |  | 4.75 | 80.5008 | 2.4859 |  | 22.0888 | 118.6434 | 4.9397 | 225.1019 | 134.9058 | 262.6737 | 8.4895 | 51.747 | 3.9356 | 156 | 30.2088 | 0 |  | 0.036165
10986 | 916.6827 | 2.1792 | 22.5353 | 101.1477 |  | 4.75 | 80.9149 | 3.2052 |  | 20.8518 | 114.4531 | 4.4401 | 221.0098 | 130.3161 | 264.033 | 8.5187 | 51.5975 | 4.1966 | 149 | 32.5323 | 0 |  | 0.030028
10987 | 904.5896 | 3.4815 | 22.9449 | 102.0188 |  | 4.75 | 77.7065 | 3.8871 |  | 21.4296 | 110.1107 | 4.7387 | 212.4168 | 120.0055 | 255.7948 | 8.4763 | 51.6994 | 4.6812 | 155 | 32.5294 | 0 |  | 0
10988 | 891.6942 | 4.0004 | 23.4193 | 100.4672 |  | 4.75 | 78.1704 | 4.2863 |  | 23.0774 | 98.5115 | 6.2153 | 209.3404 | 110.7339 | 247.1427 | 8.6294 | 52.2594 | 4.8542 | 136 | 31.4896 | 0 |  | 0
10989 | 867.2396 | 4.3188 | 23.8675 | 98.2466 |  | 5.6997 | 78.6005 | 3.5868 |  | 25.1649 | 84.5015 | 7.0364 | 214.0909 | 105.5039 | 243.012 | 8.8479 | 52.8386 | 4.2863 | 138 | 30.8356 | 0 |  | 0
10990 | 845.3871 | 3.8012 | 23.909 | 97.8894 |  | 6.6497 | 77.9972 | 3.2058 |  | 25.1762 | 77.5658 | 7.2136 | 205.8047 | 100.9278 | 242.0415 | 9.0031 | 52.8653 | 4.043 | 124 | 30.0679 | 0 |  | 0
10991 | 821.1802 | 2.7998 | 24.0249 | 97.5897 |  | 5.7003 | 77.9032 | 3.936 |  | 25.1839 | 73.3629 | 7.3137 | 195.4946 | 98.9095 | 231.9229 | 8.9959 | 52.6983 | 3.9624 | 116 | 28.8143 | 0 |  | 0
10992 | 824.7476 | 2.3916 | 23.9661 | 97.2863 |  | 4.7503 | 78.6999 | 4.3099 |  | 15.9876 | 46.6361 | 7.467 | 50.4764 | 61.5241 | 147.0677 | 8.9168 | 32.995 | 3.1081 | 117 | 27.6911 | 0 |  | 0
10993 | 825.1853 | 2.6635 | 23.917 | 97.8548 |  | 5.6997 | 78.2758 | 4.2983 |  | 24.003 | 69.7127 | 7.1822 | 167.7005 | 94.9532 | 207.8628 | 8.7854 | 52.4679 | 2.6946 | 117 | 28.4285 | 0 |  | 0
10994 | 811.215 | 2.5798 | 23.874 | 97.1521 |  | 4.7503 | 77.3274 | 4.6897 |  | 23.2472 | 69.5979 | 7.3248 | 160.5443 | 96.161 | 213.1727 | 8.8041 | 52.6584 | 2.6433 | 113 | 27.7741 | 0 |  | 0
10995 | 804.2055 | 2.3126 | 24.7253 | 97.1756 |  | 5.6997 | 77.1088 | 3.9718 |  | 23.083 | 69.5391 | 7.1675 | 155.1952 | 96.7365 | 219.4529 | 9.0074 | 52.7133 | 2.6424 | 119 | 27.2053 | 0 |  | 0
10996 | 809.7254 | 2.7195 | 25.5447 | 98.1489 |  | 4.7503 | 76.9513 | 3.4288 |  | 23.0772 | 70.2077 | 6.9988 | 152.7367 | 94.381 | 217.374 | 8.9297 | 53.4134 | 2.6454 | 108 | 27.2155 | 0 |  | 0
10997 | 844.3525 | 3.7815 | 35.6959 | 97.6891 |  | 5.6997 | 81.6366 | 3.8925 |  | 27.3804 | 72.8462 | 8.4853 | 151.7614 | 94.4063 | 214.4459 | 8.9811 | 55.419 | 2.9314 | 120 | 29.1065 | 0 |  | 0
10998 | 882.3657 | 4.9522 | 52.9393 | 99.6614 |  | 8.5492 | 95.8845 | 4.1462 |  | 40.5507 | 85.36 | 13.6877 | 156.6944 | 125.3571 | 229.96 | 11.0284 | 55.0097 | 3.7905 | 173 | 37.5205 | 0 |  | 0
10999 | 933.3192 | 10.9888 | 80.3843 | 107.5196 |  | 16.1479 | 114.4953 | 5.8641 |  | 58.1898 | 113.9776 | 28.7076 | 204.1539 | 179.6464 | 285.7666 | 24.1505 | 55.6095 | 9.1505 | 283 | 54.3849 | 0 |  | 0.043739
11000 | 1036.3656 | 18.7138 | 91.2615 | 119.7274 |  | 18.9992 | 129.7946 | 8.4363 |  | 68.8293 | 145.6117 | 35.9969 | 302.0484 | 239.1099 | 381.4757 | 33.3391 | 63.4998 | 13.8752 | 317 | 61.3447 | 0 |  | 0.10929
11001 | 1136.454 | 22.3676 | 97.3571 | 130.8034 |  | 19.9497 | 150.2965 | 7.8921 |  | 77.6922 | 168.3066 | 39.5997 | 436.7251 | 299.5221 | 492.7063 | 40.5285 | 73.0571 | 17.2427 | 318 | 62.416 | 0 |  | 0.17487
11002 | 1178.5922 | 20.6769 | 98.395 | 137.0626 |  | 19.95 | 158.2243 | 7.8852 |  | 91.4623 | 180.0863 | 44.514 | 439.2537 | 337.8018 | 573.2532 | 42.5201 | 79.093 | 17.18 | 343 | 55.9576 | 0 |  | 0.25085
11003 | 1197.5655 | 16.3575 | 102.9361 | 137.9002 |  | 18.0505 | 160.0412 | 7.5167 |  | 101.0921 | 184.2477 | 42.8037 | 423.7694 | 353.7816 | 603.8274 | 41.8789 | 83.2652 | 17.0845 | 383 | 59.8709 | 0 |  | 0.27257
11004 | 1180.4551 | 12.2268 | 103.5251 | 135.7316 |  | 18.9997 | 152.1879 | 6.4079 |  | 95.0335 | 184.6981 | 36.4059 | 442.4118 | 356.7685 | 598.9323 | 42.8451 | 82.5633 | 17.3147 | 387 | 48.5001 | 0 |  | 0.29498
11005 | 1193.3405 | 7.9925 | 101.721 | 139.375 |  | 20.8995 | 155.3778 | 6.6151 |  | 80.4166 | 184.5999 | 32.384 | 463.3729 | 353.3011 | 580.0037 | 43.0316 | 80.6328 | 17.5486 | 305 | 52.8047 | 0 |  | 0.26777
11006 | 1203.2633 | 5.4158 | 101.4888 | 146.779 |  | 24.6989 | 153.564 | 6.2003 |  | 66.3144 | 187.1495 | 33.0594 | 490.3841 | 347.1619 | 564.8507 | 40.619 | 81.4316 | 17.6975 | 290 | 57.9716 | 0 |  | 0.31643
11007 | 1159.6185 | 5.0629 | 102.8832 | 136.3852 |  | 31.3482 | 143.4595 | 5.9234 |  | 58.2432 | 185.0566 | 33.2529 | 549.9466 | 336.5669 | 556.1069 | 39.1044 | 79.2868 | 17.8433 | 269 | 59.123 | 0 |  | 0.27376
11008 | 1118.7371 | 4.5943 | 98.0074 | 125.5017 |  | 27.5511 | 139.9717 | 5.6525 |  | 60.0958 | 176.3191 | 30.4934 | 507.691 | 319.937 | 530.2156 | 32.1907 | 75.4765 | 17.2472 | 225 | 52.8693 | 0 |  | 0.20824
11009 | 1088.7472 | 4.5015 | 94.2509 | 115.464 |  | 17.1029 | 123.4824 | 3.916 |  | 56.107 | 164.7922 | 28.204 | 460.8832 | 276.7146 | 474.1566 | 16.511 | 70.8194 | 16.3144 | 205 | 50.7065 | 0 |  | 0.14473
11010 | 1049.4794 | 3.5706 | 81.7275 | 104.1634 |  | 12.3513 | 116.3546 | 4.3205 |  | 46.9841 | 146.4585 | 22.8992 | 378.2281 | 206.704 | 408.8479 | 10.4535 | 64.5768 | 13.2246 | 194 | 51.4655 | 0 |  | 0.057746
11011 | 993.2653 | 4.2145 | 62.8033 | 99.5341 |  | 11.4003 | 96.6337 | 4.8556 |  | 41.9546 | 128.144 | 10.1262 | 313.8328 | 154.4988 | 349.2233 | 9.5679 | 57.9218 | 7.2872 | 179 | 49.1856 | 0 |  | 0
11012 | 942.5538 | 5.1007 | 32.9153 | 97.6055 |  | 11.4 | 93.0712 | 4.4653 |  | 41.5109 | 119.5302 | 7.8565 | 332.6402 | 136.8186 | 299.9973 | 9.3085 | 53.6328 | 5.3343 | 176 | 43.5856 | 0 |  | 0
11013 | 911.4679 | 4.7239 | 23.7352 | 97.2209 |  | 10.4503 | 95.7664 | 4.1336 |  | 40.0027 | 109.2678 | 8.3715 | 375.3238 | 129.47 | 264.7598 | 9.3947 | 52.3916 | 5.2969 | 161 | 37.8979 | 0 |  | 0
11014 | 899.2449 | 4.0459 | 24.0022 | 97.3877 |  | 10.45 | 86.1668 | 4.0082 |  | 34.5257 | 91.3116 | 7.9845 | 367.7747 | 119.3481 | 240.459 | 9.5344 | 52.0351 | 4.3386 | 142 | 33.2661 | 0 |  | 0
11015 | 881.175 | 2.9972 | 23.8911 | 98.4453 |  | 10.45 | 77.434 | 3.9872 |  | 30.1199 | 79.165 | 7.736 | 268.2375 | 112.0654 | 226.8873 | 9.7811 | 52.1588 | 4.0661 | 123 | 32.8575 | 0 |  | 0
11016 | 880.5888 | 2.4113 | 23.646 | 97.3357 |  | 4.7516 | 67.0486 | 4.0269 |  | 18.4994 | 51.1478 | 7.6097 | 59.6125 | 70.629 | 149.8768 | 9.7897 | 32.6008 | 4.2501 | 111 | 34.7148 | 0 |  | 0
11017 | 873.2799 | 2.2562 | 23.8641 | 96.6903 |  | 5.6997 | 73.6917 | 4.4573 |  | 27.8975 | 78.9993 | 7.5978 | 204.9422 | 104.9231 | 218.2334 | 9.5861 | 51.505 | 3.6568 | 103 | 30.1489 | 0 |  | 0
11018 | 863.3878 | 2.2802 | 23.7081 | 95.9051 |  | 4.7503 | 78.5613 | 4.8812 |  | 28.1399 | 80.7745 | 7.5346 | 198.2981 | 99.7727 | 223.7389 | 9.486 | 51.1828 | 3.8851 | 108 | 28.9499 | 0 |  | 0
11019 | 854.5878 | 2.4898 | 23.7561 | 95.0751 |  | 5.6997 | 68.9965 | 4.7265 |  | 28.134 | 81.7039 | 7.4957 | 191.091 | 97.9551 | 230.09 | 9.4755 | 51.0614 | 3.6854 | 102 | 28.7026 | 0 |  | 0
11020 | 853.6581 | 2.8555 | 23.8754 | 95.9135 |  | 4.7503 | 68.5165 | 4.6374 |  | 27.89 | 81.2364 | 7.6852 | 175.9107 | 98.8114 | 228.5998 | 9.6282 | 51.9013 | 3.3245 | 102 | 29.6677 | 0 |  | 0
11021 | 879.9531 | 3.818 | 35.917 | 96.2976 |  | 4.75 | 81.1788 | 4.1952 |  | 32.7787 | 79.4763 | 8.8142 | 169.0101 | 103.1931 | 224.531 | 9.5575 | 54.0381 | 3.2869 | 101 | 28.9897 | 0 |  | 0
11022 | 926.1567 | 4.8393 | 52.1332 | 100.2885 |  | 8.5489 | 94.5745 | 3.8949 |  | 42.0263 | 83.1369 | 13.1984 | 174.4058 | 136.944 | 233.2571 | 11.8987 | 53.522 | 3.2281 | 182 | 34.5537 | 0 |  | 0
11023 | 973.3743 | 8.6582 | 80.0997 | 101.9609 |  | 19.9468 | 105.4927 | 4.7233 |  | 56.5556 | 107.7705 | 28.4706 | 233.3644 | 196.7456 | 296.2598 | 26.907 | 53.5113 | 7.8325 | 263 | 55.1777 | 0 |  | 0.024443
11024 | 1057.3653 | 11.0286 | 94.3209 | 117.2501 |  | 25.6484 | 133.5017 | 7.4456 |  | 71.5404 | 146.8784 | 33.2823 | 350.0775 | 255.8788 | 415.5434 | 35.9573 | 59.7349 | 14.9007 | 290 | 64.1377 | 0 |  | 0.045562
11025 | 1141.5917 | 14.1318 | 98.5038 | 132.8154 |  | 19.9516 | 159.55 | 7.8735 |  | 79.2285 | 174.5131 | 35.9357 | 428.1291 | 306.9364 | 526.5591 | 41.4755 | 79.7073 | 17.3841 | 360 | 70.8894 | 0 |  | 0.075071
11026 | 1205.0542 | 15.1504 | 98.0642 | 139.7411 |  | 19.95 | 150.5194 | 8.3842 |  | 88.4179 | 184.0376 | 41.7721 | 532.055 | 339.5373 | 592.9027 | 42.2426 | 101.1212 | 17.9403 | 342 | 70.2945 | 0 |  | 0.081665
11027 | 1223.4439 | 10.392 | 102.2983 | 140.5017 |  | 19.0003 | 150.6513 | 7.1296 |  | 97.9153 | 183.6974 | 43.5922 | 499.4365 | 356.9915 | 624.781 | 41.7871 | 106.502 | 17.7758 | 347 | 69.2286 | 0 |  | 0.1401
11028 | 1215.33 | 7.0416 | 102.5146 | 132.4253 |  | 21.8492 | 155.4803 | 6.9177 |  | 95.1772 | 180.711 | 42.9079 | 483.4938 | 364.6671 | 629.1196 | 42.5074 | 103.9516 | 18.0368 | 345 | 53.634 | 0 |  | 0.22311
11029 | 1242.5413 | 8.3501 | 101.4532 | 137.7472 |  | 22.7997 | 160.0553 | 6.1876 |  | 89.2962 | 182.0935 | 40.3771 | 449.5627 | 361.174 | 607.6938 | 43.0772 | 102.0175 | 18.9448 | 335 | 53.6792 | 0 |  | 0.26169
11030 | 1251.0972 | 6.8043 | 103.3106 | 143.8271 |  | 19.9508 | 166.7827 | 6.0201 |  | 89.7339 | 187.12 | 41.5346 | 441.2274 | 353.029 | 588.6351 | 42.1287 | 101.4661 | 19.3643 | 305 | 55.1657 | 0 |  | 0.23416
11031 | 1219.5444 | 7.0038 | 99.3351 | 138.0916 |  | 17.1008 | 160.6832 | 5.236 |  | 86.515 | 187.4046 | 38.126 | 444.1508 | 341.4431 | 580.1605 | 39.5267 | 99.891 | 19.5132 | 252 | 57.7017 | 0 |  | 0.25685
11032 | 1168.8627 | 6.3542 | 87.6424 | 130.3523 |  | 11.4016 | 141.0965 | 5.6463 |  | 80.6926 | 183.2348 | 35.4778 | 435.7052 | 323.7319 | 549.3678 | 32.7035 | 98.1581 | 18.4681 | 256 | 60.5368 | 0 |  | 0.18303
11033 | 1123.2622 | 4.7126 | 75.4687 | 115.9419 |  | 9.5005 | 134.0268 | 4.5014 |  | 69.5043 | 174.0125 | 35.9453 | 461.4362 | 286.7216 | 478.8971 | 17.7768 | 94.5018 | 16.7765 | 244 | 55.3042 | 0 |  | 0.1399
11034 | 1064.1631 | 3.7313 | 70.5661 | 100.2052 |  | 7.6005 | 126.7644 | 4.1392 |  | 54.7927 | 156.1624 | 30.0422 | 427.1172 | 224.7088 | 406.4208 | 11.0144 | 88.4501 | 12.7627 | 222 | 58.9345 | 0 |  | 0.052449
11035 | 1010.871 | 4.2742 | 58.9873 | 94.3246 |  | 4.7508 | 109.9821 | 4.7426 |  | 47.7905 | 139.5662 | 12.6314 | 419.4621 | 174.3251 | 362.7481 | 9.6436 | 81.2331 | 6.4556 | 205 | 59.5776 | 0 |  | 0
11036 | 972.9391 | 4.4433 | 31.9472 | 91.4452 |  | 5.6997 | 92.0025 | 4.364 |  | 46.4726 | 128.9933 | 7.6504 | 333.3957 | 153.2834 | 328.8943 | 8.9206 | 74.8895 | 4.4522 | 187 | 53.4689 | 0 |  | 0
11037 | 952.2952 | 4.6134 | 23.6198 | 90.618 |  | 4.7503 | 86.1096 | 2.6231 |  | 42.7035 | 114.2267 | 7.9954 | 248.4798 | 141.1738 | 298.5852 | 8.7788 | 72.059 | 4.0889 | 160 | 45.3023 | 0 |  | 0
11038 | 938.0424 | 4.2736 | 23.5077 | 90.2738 |  | 4.75 | 84.5695 | 3.2851 |  | 35.8901 | 94.587 | 8.0867 | 220.9398 | 130.487 | 265.9319 | 8.449 | 71.8691 | 3.9301 | 141 | 41.0261 | 0 |  | 0
11039 | 905.0299 | 2.9434 | 23.6236 | 90.9112 |  | 5.6997 | 82.4352 | 4.0568 |  | 30.3048 | 80.7037 | 8.377 | 202.6096 | 123.7849 | 241.1721 | 8.6344 | 72.3729 | 3.8051 | 123 | 38.2227 | 0 |  | 0
11040 | 901.3328 | 2.4036 | 23.8277 | 90.0044 |  | 4.7503 | 81.3902 | 4.2441 |  | 17.3819 | 50.7795 | 8.0753 | 57.1723 | 76.5898 | 162.4277 | 8.6204 | 45.2876 | 3.7506 | 105 | 31.0576 | 0 |  | 0
11041 | 893.8188 | 2.3523 | 23.8734 | 90.6939 |  | 4.75 | 79.8497 | 4.3747 |  | 25.3348 | 76.6842 | 7.7835 | 186.2385 | 114.3376 | 242.5258 | 9.0978 | 71.8107 | 3.4691 | 101 | 29.7422 | 0 |  | 0
11042 | 873.4934 | 2.2851 | 24.0975 | 91.1535 |  | 5.6997 | 80.1925 | 4.0265 |  | 25.4806 | 76.8939 | 7.7265 | 186.1224 | 112.9657 | 245.3873 | 9.399 | 71.5542 | 2.9297 | 102 | 29.2376 | 0 |  | 0
11043 | 862.9281 | 2.3071 | 23.9573 | 90.9553 |  | 4.7503 | 80.3791 | 3.7122 |  | 25.4448 | 76.9695 | 7.7085 | 184.9055 | 112.9859 | 237.0724 | 9.3387 | 71.569 | 2.7194 | 99 | 29.6644 | 0 |  | 0
11044 | 863.7274 | 2.7758 | 24.0725 | 90.1554 |  | 4.75 | 79.7984 | 3.7288 |  | 25.2853 | 78.9449 | 8.0421 | 178.0423 | 112.4315 | 223.8453 | 9.3393 | 72.3438 | 2.6835 | 102 | 30.1724 | 0 |  | 0
11045 | 880.0219 | 3.9123 | 34.1216 | 89.6216 |  | 5.6997 | 85.2121 | 4.2586 |  | 26.2657 | 82.0936 | 11.1731 | 173.3684 | 114.8334 | 221.745 | 9.3703 | 74.0673 | 2.6605 | 110 | 29.1224 | 0 |  | 0
11046 | 933.9441 | 4.885 | 47.8714 | 92.7142 |  | 8.5492 | 98.6324 | 4.2811 |  | 32.2945 | 86.3864 | 17.6202 | 174.3321 | 145.859 | 250.3591 | 11.5503 | 73.4317 | 3.0008 | 180 | 36.3871 | 0 |  | 0
11047 | 984.0393 | 14.2188 | 74.9442 | 95.1652 |  | 19.9468 | 121.3779 | 5.8003 |  | 53.7992 | 109.5485 | 31.895 | 225.947 | 199.9814 | 306.1339 | 27.3544 | 73.4816 | 6.3225 | 266 | 54.7752 | 0 |  | 0.10364
11048 | 1083.9491 | 22.7482 | 91.7193 | 111.0482 |  | 37.0452 | 140.8067 | 7.3137 |  | 81.4794 | 147.4143 | 38.8584 | 281.6807 | 246.8925 | 395.8887 | 35.062 | 79.4254 | 13.6683 | 298 | 61.0406 | 0 |  | 0.20028
11049 | 1181.1763 | 20.0649 | 99.7485 | 124.4532 |  | 34.2008 | 158.2593 | 5.759 |  | 97.6354 | 171.5788 | 39.8142 | 376.393 | 285.8877 | 494.4792 | 37.6525 | 88.9609 | 16.2774 | 360 | 62.014 | 0 |  | 0.27079
11050 | 1237.5303 | 17.9043 | 100.7146 | 130.824 |  | 29.4513 | 160.9351 | 6.2888 |  | 103.2282 | 182.2081 | 41.7503 | 467.2625 | 318.3472 | 553.146 | 39.6399 | 98.7268 | 15.9639 | 330 | 62.0657 | 0 |  | 0.28974
11051 | 1248.1835 | 17.0601 | 105.3639 | 133.2088 |  | 29.45 | 155.0792 | 7.1013 |  | 106.2811 | 186.5113 | 42.0515 | 529.7996 | 343.2987 | 570.3677 | 37.9382 | 104.3634 | 16.1615 | 339 | 63.354 | 0 |  | 0.28929
11052 | 1253.0816 | 15.5151 | 103.5024 | 130.9945 |  | 27.5505 | 158.2388 | 5.6263 |  | 103.3398 | 187.0733 | 40.2256 | 552.8567 | 350.4487 | 570.3405 | 39.0762 | 103.6995 | 17.352 | 347 | 55.2533 | 0 |  | 0.2969
11053 | 1270.2886 | 13.9941 | 103.5781 | 131.6058 |  | 27.55 | 164.3832 | 6.077 |  | 95.1485 | 188.3479 | 40.3958 | 517.0087 | 344.9536 | 570.3819 | 39.9827 | 102.1411 | 17.9478 | 287 | 56.6419 | 0 |  | 0.26739
11054 | 1295.9158 | 8.2729 | 102.8679 | 135.0628 |  | 22.8013 | 168.4071 | 6.6222 |  | 97.9987 | 189.2633 | 39.2298 | 557.3335 | 347.0412 | 583.7337 | 40.1004 | 103.3744 | 18.148 | 273 | 64.4284 | 0 |  | 0.12149
11055 | 1268.9729 | 4.9503 | 95.9367 | 135.9014 |  | 20.9005 | 160.43 | 6.1486 |  | 101.4751 | 188.7234 | 38.8453 | 564.5555 | 351.6196 | 594.8472 | 38.313 | 105.7465 | 18.0928 | 275 | 61.7478 | 0 |  | 0.13532
11056 | 1209.8337 | 4.2667 | 86.5775 | 128.3627 |  | 23.7492 | 147.9311 | 5.6281 |  | 97.4613 | 186.5044 | 38.1761 | 508.0822 | 339.9925 | 570.2009 | 31.5128 | 105.6503 | 17.6454 | 252 | 50.2101 | 0 |  | 0.10808
11057 | 1138.1761 | 5.3102 | 82.7524 | 112.7508 |  | 16.1566 | 135.3591 | 5.6356 |  | 86.3385 | 178.362 | 36.4988 | 482.0855 | 285.2825 | 501.9426 | 17.7351 | 93.1154 | 16.8877 | 227 | 51.4059 | 0 |  | 0.14391
11058 | 1076.3071 | 6.7689 | 80.9498 | 100.1284 |  | 10.4471 | 116.9461 | 5.2816 |  | 64.8579 | 155.6165 | 30.0928 | 466.9011 | 197.0859 | 417.5475 | 10.5792 | 75.5536 | 14.3273 | 209 | 48.8817 | 0 |  | 0.058795
11059 | 1030.9805 | 9.4777 | 66.009 | 94.1365 |  | 10.45 | 93.8177 | 4.2602 |  | 50.8154 | 133.6569 | 20.3314 | 350.0716 | 134.7837 | 351.1366 | 9.1346 | 64.9335 | 8.6637 | 186 | 49.2553 | 0 |  | 0
11060 | 998.7522 | 10.6088 | 33.6847 | 90.9889 |  | 8.5505 | 90.1108 | 3.4621 |  | 50.4237 | 127.0162 | 19.0961 | 329.8642 | 115.5084 | 319.539 | 9.2444 | 59.4747 | 6.0704 | 170 | 43.5339 | 0 |  | 0
11061 | 972.9326 | 6.7713 | 23.8932 | 89.618 |  | 6.6505 | 104.8125 | 3.9829 |  | 46.2779 | 117.0636 | 12.6607 | 275.7284 | 110.1988 | 299.4754 | 9.1494 | 57.8948 | 5.6383 | 163 | 36.3851 | 0 |  | 0
11062 | 958.1794 | 4.3344 | 23.6975 | 89.2703 |  | 7.5997 | 100.9122 | 4.5984 |  | 36.3365 | 97.5172 | 8.6945 | 224.7216 | 111.552 | 274.5236 | 9.6223 | 57.4213 | 5.0338 | 136 | 31.9205 | 0 |  | 0
11063 | 927.0035 | 2.9382 | 23.7273 | 89.105 |  | 4.7508 | 85.1975 | 4.6675 |  | 31.0006 | 83.8116 | 8.2671 | 203.8337 | 111.5934 | 256.6191 | 9.5838 | 56.7426 | 4.369 | 134 | 31.2161 | 0 |  | 0
11064 | 911.7052 | 2.5768 | 23.4928 | 88.8971 |  | 5.6997 | 80.2799 | 4.603 |  | 19.0224 | 52.8622 | 7.9549 | 58.6586 | 60.6639 | 162.8892 | 9.6615 | 35.4744 | 3.7229 | 125 | 31.8094 | 0 |  | 0
11065 | 902.5048 | 2.6208 | 23.6087 | 88.766 |  | 4.7503 | 79.7064 | 4.6601 |  | 28.4527 | 78.8587 | 7.7045 | 193.9727 | 83.5348 | 225.935 | 9.7784 | 56.1185 | 2.9355 | 122 | 30.7557 | 0 |  | 0
11066 | 892.7169 | 2.6985 | 23.5998 | 88.7053 |  | 4.75 | 77.1407 | 4.9553 |  | 28.1086 | 77.9697 | 7.6831 | 187.6643 | 79.5582 | 217.0844 | 9.7176 | 56.0727 | 2.6838 | 113 | 30.0152 | 0 |  | 0
11067 | 892.3044 | 2.6032 | 23.6432 | 88.8066 |  | 5.6997 | 66.3568 | 4.5896 |  | 28.1377 | 78.5536 | 7.676 | 176.622 | 78.3969 | 217.7535 | 9.8296 | 56.0078 | 2.7136 | 102 | 30.4623 | 0 |  | 0
11068 | 885.8137 | 2.97 | 23.5718 | 88.8026 |  | 4.7503 | 71.3428 | 4.3996 |  | 28.1919 | 78.8688 | 7.6694 | 175.1797 | 78.2739 | 216.6987 | 9.5174 | 56.7685 | 2.7211 | 102 | 29.8368 | 0 |  | 0
11069 | 914.6712 | 4.2551 | 33.4957 | 89.0575 |  | 5.6997 | 82.4392 | 4.6594 |  | 32.8347 | 79.1133 | 10.8495 | 175.2501 | 84.9478 | 215.9734 | 9.6061 | 58.856 | 2.6786 | 115 | 29.7954 | 0 |  | 0
11070 | 963.2563 | 9.6601 | 47.8546 | 93.2088 |  | 8.5492 | 85.4089 | 4.3623 |  | 48.2224 | 86.0181 | 16.9054 | 177.5924 | 131.1778 | 229.287 | 12.4242 | 58.5217 | 2.5642 | 177 | 41.2208 | 0 |  | 0
11071 | 1017.9271 | 16.9111 | 78.515 | 95.6841 |  | 16.1479 | 99.7952 | 5.4186 |  | 68.9245 | 116.8208 | 32.9831 | 231.7357 | 199.8907 | 306.1146 | 27.6445 | 57.8937 | 5.0971 | 290 | 58.9066 | 0 |  | 0.036356
11072 | 1104.341 | 19.4612 | 96.1146 | 111.0295 |  | 18.9992 | 127.3765 | 6.7681 |  | 82.4591 | 160.3557 | 39.8816 | 297.4946 | 250.724 | 422.1029 | 37.0084 | 63.3491 | 12.3031 | 322 | 61.9956 | 0 |  | 0.082311
11073 | 1184.7031 | 14.3895 | 96.8477 | 125.3932 |  | 19 | 150.9133 | 5.8318 |  | 96.9416 | 186.4469 | 38.1701 | 346.9229 | 288.1007 | 493.158 | 39.9023 | 72.7384 | 15.3784 | 344 | 68.3666 | 0 |  | 0.12016
11074 | 1228.4084 | 10.4127 | 102.1367 | 129.3197 |  | 19.9497 | 158.3541 | 3.8498 |  | 108.485 | 194.0025 | 39.3898 | 385.1311 | 314.871 | 540.8308 | 40.6499 | 85.3796 | 16.1469 | 326 | 69.9827 | 0 |  | 0.093972
11075 | 1251.2766 | 8.8676 | 107.587 | 134.7873 |  | 22.7992 | 150.3022 | 3.9838 |  | 105.7361 | 191.3727 | 40.5813 | 401.7849 | 332.326 | 588.0762 | 40.14 | 99.2883 | 16.5253 | 324 | 74.3886 | 0 |  | 0.2326
11076 | 1253.6042 | 8.3012 | 104.6562 | 131.9471 |  | 19.9508 | 151.1563 | 4.7496 |  | 103.198 | 187.6931 | 40.1594 | 416.0044 | 336.2773 | 602.7021 | 39.562 | 103.8434 | 17.0993 | 329 | 63.0335 | 0 |  | 0.2828
11077 | 1249.7898 | 6.5073 | 106.6761 | 137.6047 |  | 19.95 | 154.5147 | 3.9693 |  | 99.2052 | 187.4651 | 38.9197 | 426.8253 | 337.6858 | 594.8417 | 38.1453 | 103.3031 | 17.7563 | 293 | 64.2192 | 0 |  | 0.096168
11078 | 1259.0195 | 5.0133 | 105.9132 | 140.5196 |  | 20.8997 | 156.122 | 4.0306 |  | 93.3326 | 190.1975 | 39.0976 | 436.8383 | 345.6543 | 588.0673 | 39.2051 | 104.6149 | 18.2277 | 277 | 66.9513 | 0 |  | 0.088139
11079 | 1225.6956 | 4.7518 | 99.8901 | 134.7383 |  | 16.1513 | 150.0535 | 4.6879 |  | 92.532 | 191.4046 | 38.9594 | 452.6447 | 344.1323 | 576.9413 | 37.7614 | 106.0197 | 18.4115 | 260 | 62.2744 | 0 |  | 0.15702
11080 | 1177.7361 | 4.2399 | 87.6941 | 126.6713 |  | 15.2003 | 139.2832 | 4.9941 |  | 84.6502 | 188.3102 | 35.5721 | 448.4333 | 323.9749 | 535.5158 | 30.3313 | 105.0077 | 17.4083 | 256 | 49.5831 | 0 |  | 0.057883
11081 | 1134.1579 | 3.8604 | 74.2315 | 110.7711 |  | 7.6042 | 126.3218 | 4.3836 |  | 70.5761 | 177.7785 | 32.1201 | 490.1444 | 279.5051 | 461.2746 | 16.256 | 99.8881 | 15.6676 | 236 | 50.0278 | 0 |  | 0.092354
11082 | 1058.4798 | 4.6993 | 66.9595 | 95.7056 |  | 6.6482 | 115.0689 | 3.4407 |  | 56.7336 | 156.205 | 27.1608 | 512.7166 | 203.9112 | 392.5807 | 10.9551 | 93.7549 | 12.1994 | 210 | 47.6393 | 0 |  | 0.048719
11083 | 1012.6385 | 5.6475 | 57.2096 | 91.1987 |  | 7.5997 | 94.6958 | 3.1013 |  | 46.8798 | 137.9052 | 15.7935 | 464.1812 | 144.4706 | 343.2329 | 10.2658 | 86.3349 | 5.9112 | 190 | 47.5187 | 0 |  | 0.00071768
11084 | 988.2626 | 5.3795 | 30.1276 | 90.9235 |  | 6.6503 | 91.8739 | 4.0007 |  | 45.0454 | 127.6802 | 12.9577 | 343.9671 | 126.5241 | 298.7341 | 9.2728 | 80.1154 | 4.1918 | 174 | 42.1144 | 0 |  | 0
11085 | 955.3371 | 4.7048 | 20.9751 | 89.7649 |  | 6.65 | 95.6455 | 4.6856 |  | 41.0522 | 111.4947 | 13.1136 | 248.1826 | 118.5066 | 261.3693 | 8.9199 | 77.6397 | 3.93 | 172 | 37.6185 | 0 |  | 0
11086 | 926.1154 | 8.4321 | 20.9443 | 89.2508 |  | 6.65 | 86.6783 | 4.6018 |  | 33.0192 | 90.2557 | 13.0013 | 212.2263 | 109.0658 | 243.9179 | 8.9464 | 76.9345 | 3.7638 | 150 | 34.6332 | 0 |  | 0
11087 | 909.2335 | 7.1008 | 20.9729 | 89.5592 |  | 6.65 | 80.4421 | 4.3958 |  | 27.7101 | 77.4477 | 13.6233 | 198.5326 | 101.1059 | 239.2323 | 8.9197 | 76.2634 | 3.6407 | 118 | 35.2071 | 0 |  | 0
11088 | 915.3296 | 3.4407 | 20.9364 | 88.7024 |  | 6.65 | 79.0081 | 3.5937 |  | 17.0424 | 49.018 | 10.6627 | 57.7082 | 62.6371 | 158.3715 | 8.6793 | 47.148 | 3.688 | 109 | 38.6168 | 0 |  | 0
11089 | 910.178 | 2.791 | 20.8779 | 88.1052 |  | 6.65 | 79.1556 | 3.6077 |  | 25.7364 | 74.0123 | 8.4988 | 181.4036 | 94.2575 | 225.5745 | 8.7353 | 74.1035 | 3.3374 | 106 | 32.6216 | 0 |  | 0
11090 | 893.8041 | 3.1648 | 20.9103 | 88.7833 |  | 6.65 | 78.779 | 4.5027 |  | 25.6264 | 74.9065 | 7.953 | 175.1335 | 92.6183 | 224.641 | 8.8844 | 73.7884 | 3.328 | 107 | 30.4785 | 0 |  | 0
11091 | 887.312 | 2.805 | 20.7922 | 88.4149 |  | 6.65 | 78.1758 | 4.7219 |  | 25.6542 | 75.0347 | 8.4663 | 169.9267 | 91.6394 | 223.1358 | 8.8309 | 73.8142 | 3.4214 | 106 | 29.5811 | 0 |  | 0
11092 | 888.1725 | 2.9244 | 20.8678 | 88.6431 |  | 6.65 | 78.1381 | 4.766 |  | 25.1031 | 74.3867 | 8.3011 | 167.4707 | 91.2624 | 212.9662 | 8.8352 | 74.578 | 3.4823 | 105 | 31.1988 | 0 |  | 0
11093 | 900.5115 | 4.0807 | 28.5849 | 88.77 |  | 5.7003 | 84.0577 | 4.8237 |  | 29.8916 | 74.7172 | 10.0336 | 166.686 | 96.471 | 209.5453 | 8.555 | 76.5402 | 3.7596 | 114 | 30.9576 | 0 |  | 0
11094 | 954.8939 | 8.7372 | 43.2355 | 91.2497 |  | 8.5492 | 98.1651 | 4.4301 |  | 45.7687 | 82.4446 | 14.165 | 171.0057 | 134.2108 | 219.7357 | 11.1289 | 76.0622 | 3.7366 | 170 | 40.2571 | 0 |  | 0
11095 | 1001.8952 | 16.8194 | 72.7928 | 94.7484 |  | 18.0474 | 116.2088 | 3.8093 |  | 65.7077 | 113.9704 | 28.3438 | 218.4237 | 191.5079 | 260.8991 | 26.52 | 76.8889 | 6.2067 | 257 | 54.3059 | 0 |  | 0.045085
11096 | 1089.5904 | 18.1614 | 90.2097 | 111.5544 |  | 19.9495 | 132.6524 | 4.0614 |  | 79.1398 | 155.7003 | 33.4632 | 286.9224 | 238.6337 | 360.1953 | 34.1386 | 84.2202 | 12.1719 | 267 | 56.1821 | 0 |  | 0.047628
11097 | 1176.8044 | 15.7018 | 97.4647 | 125.4509 |  | 19.0003 | 139.8581 | 4.832 |  | 89.1575 | 178.0744 | 36.6962 | 354.5458 | 275.4991 | 466.4268 | 37.6482 | 93.6965 | 15.1367 | 335 | 57.4819 | 0 |  | 0.081433
11098 | 1222.7739 | 13.4201 | 96.046 | 128.001 |  | 19.9497 | 148.3022 | 3.7329 |  | 97.1263 | 184.488 | 39.1667 | 488.8393 | 301.4046 | 523.8351 | 39.3653 | 101.2677 | 15.9617 | 340 | 56.1011 | 0 |  | 0.087568
11099 | 1233.9224 | 7.86 | 94.8097 | 129.1748 |  | 17.1008 | 157.2123 | 3.7853 |  | 96.5371 | 185.0551 | 37.6057 | 539.2559 | 313.9388 | 545.6823 | 39.6592 | 103.3607 | 18.8155 | 326 | 53.6365 | 0 |  | 0.12374
11100 | 1206.5827 | 4.9477 | 93.2817 | 132.6518 |  | 16.1503 | 149.4814 | 3.4455 |  | 86.1364 | 181.928 | 34.5742 | 554.5701 | 314.158 | 541.7955 | 39.9869 | 101.7596 | 17.4847 | 325 | 50.0102 | 0 |  | 0.10033
11101 | 1207.6964 | 8.5269 | 93.0882 | 136.3304 |  | 17.0997 | 147.1331 | 4.0785 |  | 77.5694 | 179.7013 | 29.2712 | 567.6661 | 313.6946 | 538.9761 | 39.943 | 100.8674 | 16.2298 | 293 | 50.2146 | 0 |  | 0.097667
11102 | 1190.341 | 20.0949 | 95.9121 | 135.0665 |  | 15.1963 | 155.2331 | 3.5546 |  | 83.6489 | 180.0853 | 26.6814 | 583.4843 | 309.8851 | 538.8281 | 38.2137 | 94.3057 | 16.4737 | 262 | 51.0248 | 0 |  | 0.16487
11103 | 1170.7038 | 22.2415 | 93.3478 | 130.9903 |  | 15.2042 | 156.3299 | 3.2452 |  | 87.6409 | 180.0949 | 25.5902 | 577.4431 | 289.119 | 513.6023 | 35.6999 | 83.2898 | 16.6065 | 258 | 44.0821 | 0 |  | 0.11296
11104 | 1118.7986 | 10.2152 | 87.7042 | 116.9803 |  | 7.6021 | 145.2989 | 3.3566 |  | 75.5515 | 176.1566 | 23.5076 | 563.1041 | 261.5872 | 453.605 | 26.8495 | 76.1622 | 16.2146 | 238 | 35.1169 | 0 |  | 0.18329
11105 | 1086.6486 | 4.1032 | 76.4564 | 106.6006 |  | 6.6503 | 134.136 | 2.1699 |  | 65.1876 | 165.2576 | 22.8991 | 436.5668 | 226.9933 | 377.9485 | 15.4368 | 71.5981 | 15.8302 | 211 | 40.6581 | 0 |  | 0.14764
11106 | 1051.3565 | 3.2279 | 46.6668 | 92.8523 |  | 6.65 | 124.6429 | 2.6108 |  | 58.7145 | 146.5877 | 20.6654 | 344.5285 | 176.6304 | 318.1304 | 11.1454 | 66.6367 | 13.1141 | 195 | 45.3757 | 0 |  | 0.064897
11107 | 1009.4773 | 3.9658 | 34.7787 | 87.2031 |  | 5.7003 | 94.97 | 2.7736 |  | 45.421 | 126.2687 | 9.3307 | 313.9048 | 136.8892 | 288.7118 | 10.981 | 60.5692 | 7.349 | 197 | 45.5011 | 0 |  | 0.0030915
11108 | 970.1686 | 4.5533 | 26.3361 | 88.334 |  | 4.7503 | 72.542 | 3.0263 |  | 35.3788 | 104.8206 | 7.0723 | 288.9043 | 121.5696 | 276.3921 | 10.4622 | 55.65 | 4.7497 | 173 | 38.2667 | 0 |  | 0
11109 | 948.1288 | 6.5709 | 21.4681 | 89.1985 |  | 5.6997 | 72.047 | 3.7158 |  | 31.3373 | 87.0019 | 11.1355 | 248.0642 | 112.484 | 260.8143 | 9.0726 | 53.5323 | 3.8652 | 170 | 37.9845 | 0 |  | 0
11110 | 934.6114 | 10.1663 | 20.687 | 89.1292 |  | 4.7503 | 77.6503 | 4.1021 |  | 29.077 | 79.3331 | 11.7778 | 216.3393 | 97.6921 | 241.0034 | 8.6852 | 53.0228 | 3.0465 | 154 | 36.0071 | 0 |  | 0
11111 | 909.9833 | 10.2148 | 20.6994 | 89.5952 |  | 4.75 | 79.2755 | 4.3884 |  | 30.9955 | 76.3154 | 11.8566 | 207.6712 | 83.8833 | 227.957 | 8.7183 | 52.6345 | 2.629 | 149 | 35.0058 | 0 |  | 0
11112 | 903.4243 | 9.8679 | 21.1285 | 90.0864 |  | 4.75 | 79.4712 | 4.5964 |  | 19.0842 | 49.796 | 11.8174 | 61.2401 | 54.2766 | 160.3301 | 8.7546 | 33.0601 | 2.5688 | 128 | 32.4739 | 0 |  | 0
11113 | 907.2887 | 9.5339 | 21.251 | 89.563 |  | 5.6997 | 79.7272 | 3.996 |  | 27.8714 | 75.8075 | 11.1944 | 197.4729 | 79.2237 | 242.7259 | 8.4072 | 52.2903 | 2.5808 | 128 | 32.8784 | 0 |  | 0
11114 | 885.0056 | 5.0855 | 21.0877 | 88.7469 |  | 4.7503 | 79.7702 | 3.972 |  | 26.1412 | 77.2517 | 8.5202 | 194.9992 | 73.3835 | 252.068 | 9.0155 | 52.2016 | 2.5373 | 124 | 30.0426 | 0 |  | 0
11115 | 880.0002 | 2.6324 | 21.0443 | 89.3872 |  | 4.75 | 74.503 | 4.2101 |  | 25.185 | 78.4542 | 7.3568 | 191.7204 | 71.7387 | 255.1534 | 9.4423 | 52.4622 | 2.5236 | 125 | 29.7059 | 0 |  | 0
11116 | 880.1681 | 2.7818 | 21.1556 | 89.5665 |  | 5.6997 | 66.5711 | 4.7332 |  | 24.1405 | 78.9193 | 6.9709 | 185.9355 | 71.7766 | 253.1563 | 9.4221 | 53.3286 | 2.5364 | 123 | 28.8542 | 0 |  | 0
11117 | 880.5306 | 3.6211 | 21.4631 | 88.9336 |  | 4.7503 | 74.3438 | 4.922 |  | 23.8402 | 79.2787 | 6.345 | 182.0951 | 71.8307 | 249.3498 | 9.3739 | 55.0742 | 2.5 | 118 | 29.0264 | 0 |  | 0
11118 | 892.9187 | 3.5601 | 34.4323 | 86.7203 |  | 4.75 | 77.392 | 4.7747 |  | 21.924 | 81.3652 | 4.056 | 180.2836 | 71.0892 | 244.01 | 8.8564 | 54.4051 | 2.3857 | 115 | 36.4828 | 0 |  | 0
11119 | 909.4416 | 2.7453 | 42.5635 | 85.9677 |  | 4.75 | 74.7728 | 4.2449 |  | 19.0404 | 82.8027 | 5.0537 | 180.4957 | 71.6374 | 233.5384 | 8.6077 | 51.6024 | 2.3869 | 111 | 40.6575 | 0 |  | 0.037492
11120 | 904.3104 | 2.1678 | 51.8157 | 84.8557 |  | 5.6997 | 82.4779 | 2.9094 |  | 22.7953 | 79.4034 | 11.4781 | 188.3408 | 81.7276 | 223.2087 | 8.2207 | 50.5385 | 2.5059 | 126 | 40.6764 | 0 |  | 0.084831
11121 | 903.7956 | 2.5453 | 69.5704 | 88.2929 |  | 5.7 | 88.5675 | 2.7643 |  | 35.1846 | 79.6036 | 14.4401 | 202.2204 | 91.6942 | 221.2537 | 7.9813 | 50.4021 | 4.4567 | 150 | 36.2925 | 0 |  | 0.17425
11122 | 924.72 | 3.2236 | 78.7186 | 87.0238 |  | 5.7 | 91.0134 | 3.1191 |  | 48.5838 | 87.1992 | 17.5652 | 209.6592 | 93.9333 | 221.0415 | 8.0477 | 50.5559 | 10.7284 | 186 | 35.8955 | 0 |  | 0.29501
11123 | 942.2341 | 3.0333 | 79.754 | 87.8949 |  | 5.7 | 92.203 | 2.2648 |  | 53.8563 | 94.6697 | 18.8447 | 219.2039 | 102.5757 | 227.9092 | 7.8549 | 51.3269 | 13.2727 | 228 | 34.1657 | 0 |  | 0.28678
11124 | 931.8244 | 2.9905 | 80.0399 | 89.1392 |  | 5.7 | 91.1176 | 3.0867 |  | 53.4333 | 106.3638 | 18.2098 | 227.0177 | 114.0531 | 252.6042 | 7.8403 | 53.671 | 13.5165 | 199 | 37.5509 | 0 |  | 0.31502
11125 | 922.132 | 9.0212 | 71.8639 | 88.0966 |  | 4.7503 | 81.9488 | 2.9642 |  | 49.7304 | 119.7241 | 19.0428 | 233.1503 | 119.0652 | 275.9522 | 8.0412 | 55.7988 | 13.8315 | 184 | 33.2358 | 0 |  | 0.32679
11126 | 918.7168 | 12.2252 | 35.4233 | 88.1042 |  | 4.75 | 76.4108 | 1.937 |  | 41.4628 | 125.2498 | 17.1713 | 231.0757 | 117.4417 | 280.7782 | 8.0758 | 55.6358 | 12.5449 | 211 | 32.5562 | 0 |  | 0.31163
11127 | 934.2535 | 11.2412 | 20.813 | 87.6315 |  | 5.6997 | 90.222 | 2.5655 |  | 36.7203 | 125.5979 | 15.755 | 228.0639 | 110.946 | 288.3257 | 8.0917 | 54.6417 | 7.7018 | 225 | 29.0164 | 0 |  | 0.28587
11128 | 928.641 | 9.7828 | 19.6396 | 87.3093 |  | 4.7503 | 88.7337 | 1.9939 |  | 31.6158 | 124.6061 | 7.8331 | 226.3492 | 103.8527 | 315.6706 | 7.8236 | 54.4882 | 5.3841 | 229 | 27.4805 | 0 |  | 0.21378
11129 | 930.583 | 5.7442 | 19.6512 | 88.1499 |  | 4.75 | 79.3713 | 1.454 |  | 25.4175 | 119.1371 | 4.5746 | 224.4252 | 97.788 | 328.6395 | 7.8956 | 54.6757 | 4.8505 | 220 | 25.6316 | 0 |  | 0.15197
11130 | 914.0557 | 5.7102 | 19.7534 | 88.8242 |  | 4.75 | 76.1244 | 2.7754 |  | 23.3991 | 101.1602 | 3.7128 | 221.3425 | 100.6346 | 308.0758 | 8.1566 | 55.2527 | 4.7105 | 224 | 30.3285 | 0 |  | 0.073225
11131 | 893.7511 | 9.822 | 19.6497 | 87.9669 |  | 4.75 | 77.6681 | 3.4666 |  | 21.4514 | 82.0971 | 3.189 | 218.4828 | 105.8241 | 284.2203 | 8.0409 | 56.6852 | 4.0715 | 235 | 32.2826 | 0 |  | 0.0016562
11132 | 873.8386 | 11.5658 | 20.1164 | 88.1005 |  | 4.75 | 77.1447 | 4.0824 |  | 21.1569 | 78.6728 | 4.6868 | 214.6469 | 108.0268 | 268.9873 | 8.2335 | 63.315 | 3.7736 | 232 | 31.4961 | 0 |  | 0
11133 | 863.557 | 11.7823 | 20.5614 | 89.0492 |  | 5.6997 | 76.5677 | 3.7339 |  | 23.0543 | 86.8901 | 5.8924 | 212.3425 | 108.8912 | 253.7484 | 8.2218 | 72.2315 | 3.4319 | 212 | 31.0777 | 0 |  | 0
11134 | 862.5959 | 10.0371 | 20.8025 | 89.8709 |  | 4.7503 | 76.8861 | 3.1483 |  | 24.348 | 90.4107 | 7.7397 | 205.9379 | 105.1163 | 250.956 | 8.3628 | 67.4323 | 3.2443 | 200 | 31.0416 | 0 |  | 0
11135 | 846.7174 | 4.9238 | 20.918 | 89.4253 |  | 5.6997 | 77.6174 | 3.6523 |  | 25.1628 | 84.1276 | 6.8632 | 200.4273 | 98.3396 | 249.2253 | 8.4747 | 56.2571 | 2.7246 | 160 | 30.8202 | 0 |  | 0
11136 | 864.2371 | 2.5445 | 21.0071 | 89.4804 |  | 5.7 | 78.1547 | 4.2241 |  | 16.9927 | 53.2466 | 6.3828 | 58.4412 | 59.4859 | 166.1594 | 8.5738 | 33.2993 | 2.4899 | 148 | 30.229 | 0 |  | 0
11137 | 861.6516 | 2.7557 | 21.0049 | 89.4066 |  | 4.7503 | 78.1315 | 4.4465 |  | 26.0348 | 79.7653 | 6.3095 | 195.0126 | 84.0449 | 240.4617 | 8.6864 | 52.7811 | 2.4758 | 134 | 29.1811 | 0 |  | 0
11138 | 843.1372 | 2.5054 | 21.0157 | 89.4018 |  | 23.7447 | 78.0973 | 4.7786 |  | 24.7599 | 79.5076 | 6.0579 | 192.4001 | 76.854 | 242.0023 | 9.0652 | 52.846 | 2.4928 | 132 | 29.7968 | 0 |  | 0
11139 | 839.7457 | 2.2819 | 21.0443 | 89.3018 |  | 22.8003 | 77.85 | 4.6742 |  | 23.7752 | 78.4755 | 5.9554 | 190.3354 | 74.4249 | 237.1782 | 9.2456 | 52.8917 | 2.5196 | 127 | 29.7184 | 0 |  | 0
11140 | 830.1678 | 2.8441 | 21.2141 | 89.2563 |  | 18.0513 | 77.213 | 4.5067 |  | 23.6703 | 78.0204 | 5.9283 | 186.2659 | 73.985 | 227.2361 | 9.386 | 53.7317 | 2.5251 | 119 | 32.4248 | 0 |  | 0
11141 | 827.0019 | 3.7723 | 21.051 | 88.5162 |  | 6.6532 | 76.561 | 3.8918 |  | 23.2452 | 78.0544 | 5.8302 | 182.7308 | 73.4951 | 226.8317 | 8.9223 | 55.5917 | 2.4999 | 113 | 36.833 | 0 |  | 0
11142 | 838.5794 | 3.3794 | 20.5396 | 87.0318 |  | 4.7505 | 75.5073 | 3.331 |  | 20.6796 | 76.3836 | 3.8307 | 179.5053 | 72.1396 | 224.5719 | 8.1472 | 54.8294 | 2.3357 | 114 | 28.878 | 0 |  | 0
11143 | 850.8406 | 4.0463 | 20.4718 | 85.9763 |  | 4.75 | 75.2176 | 3.2183 |  | 17.9396 | 77.1571 | 3.0571 | 177.438 | 69.5143 | 215.4667 | 7.837 | 52.2426 | 2.3955 | 107 | 33.1968 | 0 |  | 0.13306
11144 | 848.6234 | 4.3636 | 20.3626 | 86.1027 |  | 5.6997 | 74.9191 | 3.6064 |  | 21.5439 | 79.3967 | 3.185 | 185.3903 | 69.4036 | 209.3991 | 7.9519 | 51.6781 | 2.9469 | 114 | 31.6729 | 0 |  | 0.22252
11145 | 868.4204 | 2.7753 | 20.2556 | 86.5811 |  | 5.7 | 78.5349 | 3.9704 |  | 34.3018 | 79.6037 | 3.1403 | 191.0427 | 81.5816 | 209.7391 | 8.0492 | 51.9687 | 3.4343 | 139 | 32.8949 | 0 |  | 0.28735
11146 | 919.008 | 2.5252 | 20.3081 | 89.3022 |  | 5.7 | 86.7411 | 3.3757 |  | 48.9034 | 86.0441 | 3.2306 | 197.2212 | 101.0708 | 216.4617 | 7.9642 | 52.1411 | 4.2824 | 151 | 32.1601 | 0 |  | 0.31588
11147 | 951.7916 | 2.9558 | 20.1714 | 91.1833 |  | 6.6497 | 92.5317 | 2.0931 |  | 56.5931 | 95.7344 | 4.3349 | 207.9545 | 115.4426 | 227.1431 | 8.0043 | 52.0065 | 4.7042 | 155 | 30.0864 | 0 |  | 0.31809
11148 | 959.554 | 3.0775 | 19.9782 | 89.8814 |  | 5.7003 | 96.9406 | 2.6866 |  | 59.6894 | 99.8535 | 6.8585 | 220.4944 | 124.5346 | 235.2776 | 7.853 | 52.097 | 5.0452 | 175 | 29.8559 | 0 |  | 0.32579
11149 | 955.0513 | 8.9198 | 19.7633 | 91.6992 |  | 5.7 | 93.8587 | 2.105 |  | 60.5139 | 107.5194 | 7.4632 | 232.6475 | 135.1539 | 244.33 | 7.8727 | 52.5802 | 5.2621 | 166 | 30.2911 | 0 |  | 0.33685
11150 | 957.2255 | 9.488 | 19.8415 | 95.3417 |  | 5.7 | 86.8682 | 2.4646 |  | 55.7104 | 118.1827 | 7.7573 | 236.2605 | 141.1046 | 261.4689 | 7.9927 | 53.3299 | 5.921 | 159 | 29.8771 | 0 |  | 0.32576
11151 | 976.5794 | 7.8883 | 19.834 | 93.2077 |  | 5.7 | 82.9848 | 3.1272 |  | 49.1293 | 112.8617 | 7.1218 | 239.9349 | 136.5073 | 275.1472 | 8.101 | 56.9818 | 7.038 | 153 | 31.756 | 0 |  | 0.29808
11152 | 973.1943 | 11.8131 | 19.661 | 91.4331 |  | 5.7 | 87.2585 | 1.9788 |  | 37.2031 | 98.8422 | 4.9659 | 241.4505 | 129.3481 | 274.2069 | 7.9761 | 66.7737 | 7.0655 | 165 | 25.2819 | 0 |  | 0.14779
11153 | 982.2358 | 7.3712 | 19.6582 | 95.2567 |  | 5.7 | 84.2513 | 1.3737 |  | 23.7662 | 93.025 | 6.6288 | 236.3532 | 124.6014 | 278.0935 | 7.6917 | 75.5587 | 6.701 | 153 | 25.9572 | 0 |  | 0.1597
11154 | 989.1932 | 3.481 | 19.9358 | 97.33 |  | 5.7 | 75.5706 | 2.7727 |  | 23.6174 | 93.5695 | 7.1267 | 227.0944 | 119.1238 | 286.7223 | 7.8937 | 77.7259 | 5.75 | 133 | 31.3345 | 0 |  | 0.035833
11155 | 948.6377 | 4.1389 | 19.7524 | 95.6642 |  | 5.7 | 81.4981 | 3.418 |  | 26.2688 | 93.4262 | 4.2303 | 220.073 | 105.2326 | 279.7756 | 7.9999 | 77.7652 | 5.1209 | 123 | 31.7901 | 0 |  | 0.0014906
11156 | 922.3218 | 7.7313 | 20.2149 | 91.7454 |  | 5.7 | 83.442 | 3.8914 |  | 24.6253 | 86.7043 | 5.9378 | 210.7663 | 96.0055 | 263.1547 | 8.166 | 77.7242 | 4.8393 | 120 | 32.8568 | 0 |  | 0
11157 | 902.5415 | 11.0507 | 20.6904 | 89.9465 |  | 5.7 | 90.2187 | 4.3075 |  | 24.9747 | 79.0077 | 6.9046 | 216.164 | 96.3767 | 255.083 | 8.4011 | 78.1695 | 4.8195 | 118 | 32.8731 | 0 |  | 0
11158 | 891.1025 | 11.2369 | 20.871 | 89.7382 |  | 4.7503 | 89.4181 | 3.7986 |  | 25.6672 | 77.1276 | 9.2262 | 215.7999 | 92.6331 | 250.0897 | 8.3557 | 72.5485 | 4.5414 | 115 | 31.7527 | 0 |  | 0
11159 | 873.4891 | 10.4295 | 20.8599 | 89.8429 |  | 5.6997 | 81.2579 | 3.2484 |  | 25.392 | 77.7714 | 9.8263 | 213.5415 | 84.4755 | 246.7386 | 8.5238 | 60.9648 | 4.0167 | 104 | 31.3908 | 0 |  | 0
11160 | 869.7177 | 9.9223 | 20.8788 | 89.1351 |  | 4.7503 | 78.3389 | 3.7935 |  | 15.9384 | 49.8893 | 9.5303 | 62.9828 | 50.5048 | 166.9673 | 8.5299 | 34.5257 | 3.689 | 101 | 29.6394 | 0 |  | 0
11161 | 867.5233 | 9.4853 | 20.8791 | 89.3241 |  | 5.6997 | 77.8091 | 4.1795 |  | 23.8763 | 73.0956 | 9.4774 | 181.9301 | 80.9943 | 237.5572 | 8.5604 | 53.1404 | 3.5834 | 102 | 31.5628 | 0 |  | 0
11162 | 848.5388 | 5.508 | 21.063 | 88.8605 |  | 4.7503 | 77.4928 | 4.2431 |  | 23.5404 | 71.317 | 9.543 | 168.0827 | 86.2899 | 223.9937 | 8.5993 | 53.2517 | 3.1458 | 111 | 29.6201 | 0 |  | 0
11163 | 845.1022 | 2.8097 | 21.4944 | 89.2582 |  | 5.6997 | 76.9277 | 4.1628 |  | 23.5247 | 71.1789 | 9.5405 | 164.4584 | 83.4741 | 215.6813 | 8.3584 | 52.7743 | 2.626 | 102 | 29.1146 | 0 |  | 0
11164 | 844.1636 | 2.8707 | 22.789 | 90.536 |  | 4.7503 | 77.1799 | 3.7564 |  | 23.5901 | 71.1161 | 9.5226 | 164.7607 | 77.6369 | 209.3596 | 8.5185 | 53.2313 | 2.4937 | 101 | 28.8839 | 0 |  | 0
11165 | 856.3948 | 4.3805 | 31.9531 | 89.7601 |  | 4.75 | 82.8043 | 3.0301 |  | 28.3363 | 71.5987 | 14.2634 | 164.2073 | 78.056 | 209.9686 | 8.5904 | 55.3995 | 2.4994 | 98 | 29.9814 | 0 |  | 0
11166 | 886.9559 | 5.5783 | 44.2485 | 90.9412 |  | 9.4987 | 95.9612 | 3.4555 |  | 42.2548 | 80.2653 | 16.3627 | 168.7562 | 113.3927 | 228.6051 | 10.8949 | 55.2669 | 2.7255 | 146 | 36.7007 | 0 |  | 0.011638
11167 | 919.39 | 10.0561 | 70.9169 | 97.7622 |  | 19.9471 | 114.1376 | 4.3586 |  | 63.3411 | 107.5737 | 26.0692 | 228.6612 | 173.8534 | 281.5535 | 23.516 | 55.992 | 8.8441 | 195 | 62.8011 | 0 |  | 0.050202
11168 | 1005.3648 | 15.5893 | 84.8654 | 111.2577 |  | 30.3971 | 133.3511 | 5.8763 |  | 78.697 | 145.5862 | 31.8645 | 287.6638 | 236.4501 | 367.3073 | 29.4503 | 62.379 | 13.6843 | 206 | 68.1313 | 0 |  | 0.082332
11169 | 1121.5751 | 16.0093 | 87.9397 | 125.832 |  | 28.5005 | 155.2399 | 6.338 |  | 81.8975 | 173.2267 | 30.352 | 341.0938 | 291.1277 | 462.3391 | 29.955 | 72.4481 | 17.1765 | 220 | 65.4824 | 0 |  | 0.11023
11170 | 1176.935 | 15.1073 | 89.1108 | 128.7657 |  | 29.4497 | 161.7872 | 6.3341 |  | 84.5386 | 183.9615 | 27.8692 | 385.9387 | 317.6588 | 529.2923 | 30.1981 | 90.536 | 16.7532 | 245 | 51.1718 | 0 |  | 0.15809
11171 | 1207.6187 | 10.7506 | 93.1723 | 133.3569 |  | 24.7013 | 161.8371 | 6.811 |  | 81.8489 | 186.1449 | 26.5269 | 400.3722 | 326.6779 | 541.1724 | 30.7026 | 105.8811 | 16.1139 | 219 | 48.366 | 0 |  | 0.24526
11172 | 1174.5569 | 8.518 | 92.5581 | 129.9912 |  | 22.8005 | 167.7385 | 6.9539 |  | 70.8285 | 185.6897 | 29.0206 | 405.246 | 331.8151 | 529.6293 | 30.9876 | 106.9819 | 16.1546 | 218 | 47.9637 | 0 |  | 0.24193
11173 | 1176.443 | 12.1109 | 96.8792 | 134.4085 |  | 19.0011 | 162.9781 | 5.351 |  | 58.0431 | 186.7799 | 28.7009 | 407.8912 | 334.0295 | 524.3879 | 31.2496 | 104.179 | 16.6074 | 204 | 50.4091 | 0 |  | 0.19703
11174 | 1190.7569 | 13.0468 | 96.3168 | 134.5717 |  | 19.9497 | 164.0125 | 5.5813 |  | 46.7508 | 190.5426 | 29.3716 | 420.8038 | 333.722 | 522.8381 | 30.6527 | 102.3847 | 16.7059 | 197 | 53.3261 | 0 |  | 0.19796
11175 | 1177.7974 | 7.9424 | 92.0709 | 129.434 |  | 15.2013 | 154.6831 | 5.7954 |  | 42.1396 | 191.2394 | 32.7845 | 416.2784 | 328.8406 | 505.9383 | 30.1839 | 99.6659 | 16.6532 | 200 | 49.9087 | 0 |  | 0.24156
11176 | 1140.3791 | 4.9246 | 86.8568 | 122.793 |  | 16.1497 | 140.805 | 4.3625 |  | 42.2649 | 184.6081 | 29.7243 | 401.2203 | 316.4431 | 455.0253 | 25.6263 | 94.5396 | 16.0282 | 173 | 43.375 | 0 |  | 0.1937
11177 | 1102.5097 | 4.5139 | 82.4362 | 107.5108 |  | 7.6024 | 132.9263 | 4.4758 |  | 42.8758 | 171.3723 | 26.8373 | 376.3126 | 272.3562 | 386.5556 | 12.9992 | 82.416 | 15.3297 | 160 | 44.4513 | 0 |  | 0.13917
11178 | 1047.4153 | 4.73 | 70.0286 | 95.6903 |  | 6.6503 | 120.5533 | 4.7269 |  | 40.7399 | 152.3034 | 20.763 | 335.7278 | 194.4916 | 324.9477 | 8.01 | 69.2961 | 12.5392 | 159 | 42.3342 | 0 |  | 0.049709
11179 | 1000.2057 | 4.2498 | 59.464 | 89.7341 |  | 5.7003 | 101.2254 | 4.6249 |  | 39.3757 | 135.2892 | 11.3055 | 280.8427 | 137.8181 | 285.6738 | 7.7639 | 61.2 | 6.8167 | 154 | 43.5749 | 0 |  | 0.0044165
11180 | 967.2622 | 4.7491 | 30.0036 | 91.6896 |  | 5.7 | 87.1431 | 3.3509 |  | 38.8069 | 125.6554 | 9.5783 | 248.1171 | 120.2332 | 285.9357 | 8.0295 | 56.3598 | 4.3029 | 145 | 38.3825 | 0 |  | 0
11181 | 933.2139 | 4.7848 | 20.3844 | 92.0622 |  | 5.7 | 85.6347 | 3.187 |  | 34.692 | 112.0672 | 7.8535 | 226.7201 | 116.4185 | 282.3453 | 8.2876 | 54.7999 | 3.9637 | 129 | 33.7292 | 0 |  | 0
11182 | 896.6513 | 4.7286 | 20.3741 | 89.2625 |  | 4.7503 | 86.0938 | 4.1929 |  | 30.4127 | 90.863 | 7.4614 | 204.8899 | 109.4095 | 260.4577 | 8.2322 | 54.0589 | 3.8051 | 120 | 33.3197 | 0 |  | 0
11183 | 880.8027 | 3.7674 | 20.493 | 88.1638 |  | 5.6997 | 85.2446 | 4.4824 |  | 28.2752 | 75.771 | 7.9143 | 199.3367 | 96.3101 | 237.9107 | 8.1159 | 53.4513 | 3.849 | 109 | 31.9921 | 0 |  | 0
11184 | 889.0517 | 2.8854 | 20.3597 | 87.789 |  | 4.7503 | 83.2488 | 4.4773 |  | 17.0638 | 47.2615 | 7.3062 | 57.6746 | 56.083 | 151.9542 | 8.8484 | 33.8216 | 3.2364 | 103 | 29.1189 | 0 |  | 0
11185 | 876.9443 | 2.9714 | 20.392 | 87.7826 |  | 5.6997 | 80.6393 | 4.8262 |  | 25.1405 | 73.0273 | 6.8539 | 197.1621 | 82.8133 | 222.3478 | 9.2085 | 53.7972 | 2.7493 | 101 | 28.9065 | 0 |  | 0
11186 | 861.9547 | 2.8003 | 20.4301 | 87.8717 |  | 4.7503 | 79.4478 | 4.7288 |  | 24.6564 | 75.9133 | 6.7747 | 186.9369 | 82.9016 | 233.4101 | 9.117 | 53.5688 | 2.6329 | 102 | 29.824 | 0 |  | 0
11187 | 866.4379 | 2.7126 | 20.4199 | 88.0101 |  | 5.6997 | 77.2638 | 4.0862 |  | 24.6281 | 77.9807 | 6.758 | 177.4042 | 83.2587 | 240.2721 | 9.1607 | 53.4657 | 2.6038 | 98 | 28.7767 | 0 |  | 0
11188 | 857.605 | 3.2038 | 20.4136 | 87.8924 |  | 5.7 | 67.5904 | 4.1716 |  | 24.8287 | 77.3448 | 6.7385 | 168.4067 | 82.9402 | 231.1726 | 8.9433 | 54.1963 | 2.5937 | 97 | 28.6335 | 0 |  | 0
11189 | 874.2481 | 4.7579 | 31.7113 | 87.5779 |  | 5.7 | 76.8049 | 4.1466 |  | 30.1383 | 74.7644 | 7.7631 | 164.7685 | 86.3797 | 218.1814 | 8.8534 | 56.2698 | 2.5684 | 94 | 28.5451 | 0 |  | 0
11190 | 921.4221 | 5.4548 | 45.2319 | 88.5983 |  | 8.5492 | 93.7542 | 5.1152 |  | 45.0062 | 81.5472 | 12.4009 | 173.2066 | 120.9198 | 221.966 | 11.2169 | 55.5098 | 3.0676 | 141 | 39.1331 | 0 |  | 0.012546
11191 | 964.7013 | 13.2285 | 72.5408 | 92.7053 |  | 17.0976 | 113.2817 | 6.1826 |  | 57.1831 | 112.5935 | 25.8529 | 228.3826 | 177.3268 | 260.0661 | 24.7846 | 55.0099 | 5.3354 | 186 | 58.8561 | 0 |  | 0.039621
11192 | 1048.9628 | 14.8545 | 82.9578 | 110.3049 |  | 17.1 | 128.2155 | 7.0102 |  | 59.008 | 151.0899 | 29.856 | 333.7732 | 228.1334 | 349.5852 | 28.5086 | 60.2153 | 11.2938 | 204 | 64.305 | 0 |  | 0.063365
11193 | 1138.8845 | 10.8099 | 91.5211 | 124.0196 |  | 18.9995 | 147.4985 | 7.0637 |  | 59.2184 | 174.0738 | 27.0922 | 456.084 | 270.4051 | 441.4144 | 28.5211 | 67.8432 | 13.9815 | 235 | 61.0479 | 0 |  | 0.13486
11194 | 1175.9752 | 11.1157 | 89.6601 | 125.9735 |  | 20.8995 | 154.4567 | 5.3647 |  | 63.1169 | 183.0644 | 27.7927 | 445.672 | 297.667 | 488.2147 | 29.3259 | 80.2725 | 14.714 | 245 | 57.6166 | 0 |  | 0.19657
11195 | 1196.9152 | 11.9391 | 90.7955 | 128.3342 |  | 19.9503 | 151.4882 | 6.2998 |  | 65.4346 | 182.8923 | 27.9352 | 401.8586 | 310.7965 | 517.0439 | 30.2569 | 94.8684 | 15.3065 | 220 | 56.1981 | 0 |  | 0.1504
11196 | 1163.6885 | 8.8582 | 90.7552 | 126.3039 |  | 19.95 | 148.685 | 6.8697 |  | 63.9778 | 180.2732 | 27.9572 | 389.6924 | 314.493 | 525.4827 | 30.1314 | 100.7028 | 15.7703 | 207 | 51.2661 | 0 |  | 0.17529
11197 | 1177.6133 | 8.1242 | 89.0411 | 130.2872 |  | 19.95 | 152.2119 | 6.5257 |  | 63.1992 | 180.8136 | 26.6606 | 376.2497 | 310.8913 | 525.0606 | 29.5911 | 99.7238 | 16.1157 | 193 | 49.9867 | 0 |  | 0.14563
11198 | 1177.9797 | 6.058 | 89.0003 | 135.2621 |  | 20.8997 | 155.0172 | 5.5996 |  | 63.1543 | 182.8698 | 25.1167 | 388.3275 | 311.0934 | 527.0097 | 27.0789 | 99.2654 | 15.7405 | 200 | 52.3362 | 0 |  | 0.1741
11199 | 1166.2968 | 4.853 | 86.054 | 131.0386 |  | 15.2016 | 149.2789 | 5.7584 |  | 61.4324 | 183.0286 | 26.1865 | 386.3182 | 310.3822 | 519.1245 | 23.9672 | 98.6552 | 14.9308 | 183 | 55.0996 | 0 |  | 0.13274
11200 | 1131.0069 | 6.7559 | 77.7801 | 122.7637 |  | 11.4011 | 138.0798 | 6.0231 |  | 64.6581 | 178.5818 | 24.475 | 379.7042 | 297.3262 | 478.5752 | 14.0467 | 92.7313 | 14.5882 | 169 | 55.5413 | 0 |  | 0.065489
11201 | 1076.9765 | 5.4298 | 67.9539 | 108.3032 |  | 7.6032 | 126.2791 | 3.8229 |  | 70.7496 | 167.0097 | 22.9564 | 359.6784 | 262.5849 | 421.596 | 9.6352 | 80.1695 | 14.6356 | 156 | 55.7843 | 0 |  | 0.10369
11202 | 1029.8979 | 7.5951 | 63.1247 | 92.9547 |  | 5.7 | 114.7306 | 4.0877 |  | 65.6728 | 147.5736 | 19.8028 | 322.4159 | 205.8999 | 378.9796 | 8.6996 | 68.7606 | 12.1687 | 154 | 48.3932 | 0 |  | 0.029021
11203 | 986.396 | 6.7466 | 56.7591 | 87.461 |  | 5.6984 | 101.8307 | 4.4844 |  | 51.8831 | 131.5345 | 10.7227 | 283.0434 | 158.9787 | 344.9161 | 8.0344 | 61.6493 | 6.1633 | 145 | 47.9557 | 0 |  | 0.0040301
11204 | 969.7582 | 12.8772 | 29.417 | 88.0794 |  | 5.7016 | 92.2215 | 4.6932 |  | 41.5605 | 133.0265 | 9.4541 | 249.744 | 142.4239 | 312.9833 | 8.1884 | 57.007 | 4.0333 | 137 | 47.04 | 0 |  | 0
11205 | 945.7799 | 13.1467 | 20.391 | 88.9078 |  | 4.7487 | 90.25 | 3.4486 |  | 35.3476 | 130.8324 | 10.2202 | 221.307 | 138.7404 | 283.2246 | 8.5737 | 55.5659 | 3.6561 | 129 | 43.1613 | 0 |  | 0
11206 | 920.3787 | 9.7415 | 20.3979 | 88.8055 |  | 5.6997 | 91.6337 | 3.4175 |  | 28.8516 | 104.0453 | 10.2424 | 197.5585 | 129.9796 | 259.6606 | 9.295 | 55.2401 | 3.2195 | 118 | 42.3275 | 0 |  | 0
11207 | 880.9246 | 4.8408 | 20.4173 | 88.8362 |  | 4.7503 | 90.1272 | 4.2461 |  | 24.7657 | 77.92 | 10.4855 | 188.604 | 122.3628 | 242.3385 | 9.5473 | 54.2776 | 3.0078 | 101 | 41.446 | 0 |  | 0
11208 | 884.4047 | 2.9431 | 20.4475 | 88.7767 |  | 5.6997 | 75.6539 | 4.7131 |  | 15.3763 | 47.1703 | 10.4547 | 54.3889 | 74.0055 | 153.3196 | 9.4323 | 33.5334 | 2.7594 | 103 | 32.1568 | 0 |  | 0
11209 | 878.6921 | 2.808 | 20.4352 | 88.8117 |  | 4.7503 | 71.2914 | 4.5869 |  | 23.4512 | 71.3327 | 10.079 | 173.1862 | 109.1274 | 219.1506 | 9.6004 | 53.7414 | 2.7568 | 98 | 32.3815 | 0 |  | 0
11210 | 863.3157 | 2.4756 | 20.4284 | 89.8223 |  | 7.5992 | 73.5228 | 4.3932 |  | 23.5948 | 71.0296 | 10.2194 | 165.1438 | 102.9317 | 223.5753 | 9.002 | 53.8897 | 2.5941 | 97 | 33.3198 | 0 |  | 0
11211 | 861.8235 | 2.4954 | 20.4842 | 89.3357 |  | 4.7508 | 74.2131 | 4.0767 |  | 23.5995 | 70.5795 | 10.332 | 162.2219 | 99.5158 | 225.407 | 8.6483 | 53.1055 | 2.496 | 99 | 34.2564 | 0 |  | 0
11212 | 858.1875 | 3.1599 | 20.565 | 89.1543 |  | 5.6997 | 73.4212 | 3.3956 |  | 23.342 | 70.3876 | 10.2748 | 161.819 | 98.5547 | 219.9639 | 8.5728 | 53.6382 | 2.5353 | 96 | 31.0403 | 0 |  | 0
11213 | 872.2636 | 4.7035 | 31.6106 | 89.2017 |  | 4.7503 | 78.59 | 3.6445 |  | 28.381 | 70.339 | 11.7949 | 162.3831 | 100.5456 | 216.3501 | 8.3458 | 55.9477 | 2.5246 | 96 | 30.0385 | 0 |  | 0
11214 | 913.0194 | 9.3837 | 46.3056 | 93.1181 |  | 13.2976 | 91.6953 | 3.8457 |  | 41.9465 | 78.7215 | 14.4644 | 167.4749 | 129.3978 | 224.3188 | 10.4581 | 55.4159 | 2.9312 | 140 | 38.9954 | 0 |  | 0.039821
11215 | 949.6938 | 17.4379 | 74.9136 | 95.606 |  | 21.8476 | 110.5406 | 4.5444 |  | 54.3335 | 110.5574 | 23.7878 | 218.6037 | 178.1748 | 266.767 | 20.0445 | 55.779 | 6.6015 | 174 | 65.055 | 0 |  | 0.12811
11216 | 1034.1841 | 18.8538 | 83.4273 | 111.0762 |  | 22.7997 | 128.9186 | 6.1204 |  | 58.3409 | 151.0207 | 31.2187 | 277.5471 | 224.4547 | 367.8773 | 24.3241 | 63.1933 | 11.966 | 203 | 69.7969 | 0 |  | 0.22171
11217 | 1119.8548 | 13.6457 | 87.1251 | 124.02 |  | 22.8 | 145.9238 | 5.8402 |  | 62.4639 | 173.7073 | 29.3205 | 322.7157 | 263.4254 | 466.3084 | 26.3199 | 72.2148 | 14.2948 | 199 | 67.9469 | 0 |  | 0.28174
11218 | 1184.5773 | 10.3327 | 86.643 | 128.5457 |  | 23.7497 | 145.905 | 5.2518 |  | 69.4365 | 180.9908 | 27.709 | 365.7911 | 289.7328 | 511.928 | 27.2879 | 78.5297 | 15.204 | 221 | 64.2806 | 0 |  | 0.31754
11219 | 1221.5753 | 8.1553 | 90.9512 | 125.7339 |  | 21.8505 | 143.0086 | 6.0658 |  | 65.7493 | 181.014 | 26.247 | 376.6677 | 302.8495 | 532.0122 | 27.7443 | 81.949 | 15.4918 | 201 | 58.9673 | 0 |  | 0.32741
11220 | 1196.6765 | 6.8065 | 91.0116 | 122.3088 |  | 26.5987 | 138.2967 | 5.1081 |  | 55.7875 | 177.7237 | 25.277 | 374.2242 | 304.354 | 536.0851 | 27.4297 | 82.4572 | 15.5544 | 197 | 52.7054 | 0 |  | 0.33751
11221 | 1174.0673 | 10.2397 | 90.578 | 127.6996 |  | 23.7508 | 148.08 | 6.3602 |  | 52.557 | 175.8033 | 25.9161 | 369.7972 | 305.8891 | 536.523 | 27.2235 | 82.0554 | 15.5003 | 192 | 54.2845 | 0 |  | 0.34162
11222 | 1184.5809 | 9.6203 | 88.5608 | 130.9659 |  | 19.9511 | 150.303 | 5.1227 |  | 54.5323 | 177.2282 | 24.6517 | 382.3159 | 307.3966 | 534.083 | 27.0852 | 83.699 | 15.3388 | 203 | 56.2467 | 0 |  | 0.31757
11223 | 1163.6189 | 6.911 | 85.6311 | 125.8428 |  | 18.0505 | 141.6542 | 5.4115 |  | 55.0992 | 180.8852 | 24.1258 | 390.9904 | 301.8254 | 526.7355 | 23.9263 | 83.7921 | 15.303 | 173 | 53.0386 | 0 |  | 0.26738
11224 | 1114.7033 | 5.2792 | 77.7168 | 118.1233 |  | 17.1003 | 141.7631 | 4.766 |  | 49.2596 | 179.6842 | 22.9271 | 374.8663 | 288.0398 | 495.3728 | 14.2712 | 80.3445 | 14.9673 | 158 | 39.7368 | 0 |  | 0.22701
11225 | 1052.3832 | 4.676 | 66.8858 | 103.1979 |  | 12.3513 | 124.3136 | 4.505 |  | 44.9123 | 168.561 | 22.1804 | 355.6021 | 246.1992 | 425.1307 | 9.9405 | 75.6022 | 14.4925 | 160 | 43.9827 | 0 |  | 0.15757
11226 | 1002.7923 | 4.3453 | 64.0441 | 92.4663 |  | 10.4505 | 116.0044 | 4.5556 |  | 43.0728 | 148.6097 | 18.7051 | 315.4683 | 184.5916 | 352.4528 | 9.4956 | 70.8802 | 12.1577 | 160 | 39.521 | 0 |  | 0.071262
11227 | 965.8104 | 4.36 | 55.6589 | 89.0723 |  | 8.5505 | 102.957 | 3.4561 |  | 39.9166 | 130.2706 | 8.802 | 267.4891 | 142.3016 | 300.7708 | 9.1395 | 66.0814 | 6.8785 | 145 | 38.3472 | 0 |  | 0.006392
11228 | 945.1362 | 4.6511 | 29.4308 | 88.0024 |  | 9.4997 | 90.7344 | 2.8171 |  | 39.3004 | 120.4074 | 11.4432 | 243.7299 | 130.573 | 277.4992 | 9.0279 | 60.2607 | 4.6145 | 138 | 36.012 | 0 |  | 0
11229 | 916.4842 | 4.5618 | 20.8335 | 89.0797 |  | 9.5 | 92.6533 | 3.7066 |  | 36.6699 | 106.9208 | 17.9069 | 225.4527 | 126.6288 | 274.0927 | 9.3882 | 56.3926 | 3.9998 | 131 | 30.9109 | 0 |  | 0
11230 | 899.4403 | 4.0925 | 20.6384 | 89.0598 |  | 8.5503 | 92.7927 | 4.2779 |  | 31.973 | 86.8869 | 15.7361 | 200.8385 | 116.4146 | 263.006 | 9.4951 | 55.4739 | 3.7919 | 126 | 30.1218 | 0 |  | 0
11231 | 883.0533 | 3.3737 | 20.7503 | 89.0073 |  | 5.7008 | 80.0838 | 4.2215 |  | 29.7227 | 73.3022 | 9.8209 | 190.8255 | 106.3955 | 252.1 | 9.5462 | 55.3387 | 3.8785 | 111 | 32.2812 | 0 |  | 0
11232 | 897.4001 | 2.7703 | 20.6275 | 88.8889 |  | 5.7 | 84.719 | 3.5225 |  | 18.5637 | 46.9258 | 8.0789 | 56.3136 | 61.8871 | 165.3896 | 9.4484 | 35.4236 | 3.995 | 112 | 29.8784 | 0 |  | 0
11233 | 894.6121 | 2.6764 | 20.889 | 89.7611 | -5.636 | 4.7503 | 88.671 | 3.219 |  | 13.9751 | 35.8045 | 7.9572 |  | 41.3323 | 128.1315 | 9.2986 | 27.9078 | 3.1203 | 118 | 28.3394 | 0 | -5.3655 | 0
11234 | 877.708 | 3.0767 | 17.6825 | 89.1799 | -4.6374 | 5.6997 | 78.7685 | 3.9392 |  | 14.6314 | 36.207 | 7.8994 |  | 39.7136 | 131.0123 | 9.4302 | 27.5386 | 2.605 | 116 | 30.7276 | 0 | -5.2732 | 0
11235 | 870.5466 | 2.6497 | 15.0032 | 88.7659 | -5.6373 | 4.7503 | 72.5364 | 4.2284 |  | 14.0758 | 35.969 | 7.8958 |  | 39.6553 | 127.1318 | 9.5647 | 27.456 | 2.5453 | 116 | 28.7501 | 0 | -5.5899 | 0
11236 | 254.959 | 0.77551 | 3.9428 | 23.3428 | -4.64 | 0.00132 | 21.2792 | 1.3051 |  | 4.221 | 11.6529 | 2.4075 |  | 10.8697 | 39.514 | 2.6049 | 7.354 | 0.79501 | 107 | 2.0835 | 0 | -5.234 | 0
11237 | 0 | 0 | 0 | 0 | 0.1352 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | -1.0305 | 0
11238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0.012426
11239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0.033094
11240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0.054885
11241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0.083342
11242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0.091469
11243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0.174
11244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0.12123
11245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0.22201
11246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0.16085
11247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0.13221
11248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0.067586
11249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0.06159
11250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0.030615
11251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 0.0039749
11252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0
11253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0
11254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0
11255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0
11256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0
11257 | [18 empty] | 106 |  |  |  | 0
11258 | [18 empty] | 101 |  |  |  | 0
11259 | [18 empty] | 100 |  |  |  | 0
11260 | [18 empty] | 97 |  |  |  | 0
11261 | [18 empty] | 99 |  |  |  | 0
11262 | [18 empty] | 116 |  |  |  | 0.013848
11263 | [18 empty] | 139 |  |  |  | 0.059322
11264 | [18 empty] | 138 |  |  |  | 0.093474
11265 | [18 empty] | 133 |  |  |  | 0.075738
11266 | [18 empty] | 140 |  |  |  | 0.13676
11267 | [18 empty] | 144 |  |  |  | 0.10818
11268 | [18 empty] | 142 |  |  |  | 0.15562
11269 | [18 empty] | 143 |  |  |  | 0.11707
11270 | [18 empty] | 147 |  |  |  | 0.11349
11271 | [18 empty] | 152 |  |  |  | 0.11538
11272 | [18 empty] | 153 |  |  |  | 0.075018
11273 | [18 empty] | 146 |  |  |  | 0.051732
11274 | [18 empty] | 139 |  |  |  | 0.026128
11275 | [18 empty] | 124 |  |  |  | 0.0046374
11276 | [18 empty] | 122 |  |  |  | 0
11277 | [18 empty] | 120 |  |  |  | 0
11278 | [18 empty] | 118 |  |  |  | 0
11279 | [18 empty] | 103 |  |  |  | 0
11280 | [18 empty] | 100 |  |  |  | 0
11281 | [18 empty] | 103 |  |  |  | 0
11282 | [18 empty] | 110 |  |  |  | 0
11283 | [18 empty] | 105 |  |  |  | 0
11284 | [18 empty] | 104 |  |  |  | 0
11285 | [18 empty] | 95 |  |  |  | 0
11286 | [18 empty] | 93 |  |  |  | 0.032577
11287 | [18 empty] | 98 |  |  |  | 0.080853
11288 | [18 empty] | 101 |  |  |  | 0.14268
11289 | [18 empty] | 100 |  |  |  | 0.15143
11290 | [18 empty] | 102 |  |  |  | 0.17079
11291 | [18 empty] | 110 |  |  |  | 0.17036
11292 | [18 empty] | 115 |  |  |  | 0.18332
11293 | [18 empty] | 109 |  |  |  | 0.14709
11294 | [18 empty] | 123 |  |  |  | 0.15586
11295 | [18 empty] | 133 |  |  |  | 0.25199
11296 | [18 empty] | 124 |  |  |  | 0.14063
11297 | [18 empty] | 132 |  |  |  | 0.10233
11298 | [18 empty] | 138 |  |  |  | 0.068332
11299 | [18 empty] | 129 |  |  |  | 0.012102
11300 | [18 empty] | 130 |  |  |  | 0
11301 | [18 empty] | 129 |  |  |  | 0
11302 | [18 empty] | 134 |  |  |  | 0
11303 | [18 empty] | 112 |  |  |  | 0
11304 | [18 empty] | 109 |  |  |  | 0
11305 | [18 empty] | 105 |  |  |  | 0
11306 | [18 empty] | 100 |  |  |  | 0
11307 | [18 empty] | 97 |  |  |  | 0
11308 | [18 empty] | 102 |  |  |  | 0
11309 | [18 empty] | 95 |  |  |  | 0
11310 | [18 empty] | 100 |  |  |  | 0.14702
11311 | [18 empty] | 100 |  |  |  | 0.22602
11312 | [18 empty] | 101 |  |  |  | 0.29875
11313 | [18 empty] | 103 |  |  |  | 0.3189
11314 | [18 empty] | 104 |  |  |  | 0.30446
11315 | [18 empty] | 104 |  |  |  | 0.28488
11316 | [18 empty] | 116 |  |  |  | 0.25351
11317 | [18 empty] | 129 |  |  |  | 0.22632
11318 | [18 empty] | 125 |  |  |  | 0.25188
11319 | [18 empty] | 119 |  |  |  | 0.23769
11320 | [18 empty] | 113 |  |  |  | 0.18115
11321 | [18 empty] | 121 |  |  |  | 0.1272
11322 | [18 empty] | 123 |  |  |  | 0.11127
11323 | [18 empty] | 116 |  |  |  | 0.032272
11324 | [18 empty] | 111 |  |  |  | 0
11325 | [18 empty] | 101 |  |  |  | 0
11326 | [18 empty] | 103 |  |  |  | 0
11327 | [18 empty] | 102 |  |  |  | 0
11328 | [18 empty] | 112 |  |  |  | 0
11329 | [18 empty] | 109 |  |  |  | 0
11330 | [18 empty] | 121 |  |  |  | 0
11331 | [18 empty] | 106 |  |  |  | 0
11332 | [18 empty] | 97 |  |  |  | 0
11333 | [18 empty] | 98 |  |  |  | 0
11334 | [18 empty] | 119 |  |  |  | 0.11854
11335 | [18 empty] | 139 |  |  |  | 0.21709
11336 | [18 empty] | 140 |  |  |  | 0.27857
11337 | [18 empty] | 138 |  |  |  | 0.31327
11338 | [18 empty] | 136 |  |  |  | 0.094393
11339 | [18 empty] | 144 |  |  |  | 0.19588
11340 | [18 empty] | 144 |  |  |  | 0.19325
11341 | [18 empty] | 143 |  |  |  | 0.28016
11342 | [18 empty] | 143 |  |  |  | 0.29867
11343 | [18 empty] | 149 |  |  |  | 0.2725
11344 | [18 empty] | 142 |  |  |  | 0.2047
11345 | [18 empty] | 152 |  |  |  | 0.203
11346 | [18 empty] | 144 |  |  |  | 0.14707
11347 | [18 empty] | 126 |  |  |  | 0.02149
11348 | [18 empty] | 117 |  |  |  | 0
11349 | [18 empty] | 117 |  |  |  | 0
11350 | [18 empty] | 118 |  |  |  | 0
11351 | [18 empty] | 108 |  |  |  | 0
11352 | [18 empty] | 104 |  |  |  | 0
11353 | [18 empty] | 99 |  |  |  | 0
11354 | [18 empty] | 105 |  |  |  | 0
11355 | [18 empty] | 104 |  |  |  | 0
11356 | [18 empty] | 101 |  |  |  | 0
11357 | [18 empty] | 114 |  |  |  | 0
11358 | [18 empty] | 187 |  |  |  | 0.020391
11359 | [18 empty] | 231 |  |  |  | 0.054358
11360 | [18 empty] | 254 |  |  |  | 0.06308
11361 | [18 empty] | 312 |  |  |  | 0.11623
11362 | [18 empty] | 294 |  |  |  | 0.1055
11363 | [18 empty] | 316 |  |  |  | 0.11461
11364 | [18 empty] | 371 |  |  |  | 0.11429
11365 | [18 empty] | 290 |  |  |  | 0.12933
11366 | [18 empty] | 262 |  |  |  | 0.10026
11367 | [18 empty] | 269 |  |  |  | 0.083832
11368 | [18 empty] | 238 |  |  |  | 0.07414
11369 | [18 empty] | 224 |  |  |  | 0.055536
11370 | [18 empty] | 206 |  |  |  | 0.027014
11371 | [18 empty] | 181 |  |  |  | 0.0054655
11372 | [18 empty] | 179 |  |  |  | 0
11373 | [18 empty] | 159 |  |  |  | 0
11374 | [18 empty] | 140 |  |  |  | 0
11375 | [18 empty] | 118 |  |  |  | 0
11376 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0
11377 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0
11378 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0
11379 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0
11380 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0
11381 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0
11382 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0.016704
11383 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 0 | 0.1022
11384 | 885.0717 | 0 | 0 | 0 | -8.5594 | 8.1314 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0.14896
11385 | 1093.7991 | 15.5467 | 65.5494 | 94.9504 | -23.6448 | 22.8027 | 139.1721 | 5.3391 |  | 38.3671 | 61.8758 | 23.7764 |  | 115.2968 | 179.7408 | 34.6142 | 34.8914 | 11.4508 | 319 | 48.1984 | 0 | -60.9492 | 0.12405
11386 | 1201.2956 | 18.844 | 90.0483 | 127.3599 | -26.6438 | 25.6492 | 155.1944 | 7.3558 |  | 56.5527 | 91.0883 | 38.0588 |  | 166.9693 | 281.1096 | 42.2071 | 42.4681 | 17.4565 | 322 | 62.2148 | 0 | -67.1422 | 0.095061
11387 | 1199.4651 | 11.6959 | 91.6239 | 130.839 | -26.6421 | 25.65 | 157.7405 | 6.8933 |  | 55.6714 | 88.5661 | 37.3246 |  | 172.6748 | 295.6818 | 41.1302 | 43.5876 | 18.0723 | 307 | 67.7308 | 0 | -55.7977 | 0.12192
11388 | 1186.0024 | 7.0927 | 94.1716 | 129.0074 | -25.6473 | 24.7003 | 158.5931 | 7.0995 |  | 50.7244 | 87.5503 | 34.8498 |  | 173.6565 | 290.007 | 42.0145 | 41.8814 | 17.8242 | 294 | 58.1454 | 0 | -52.1266 | 0.21185
11389 | 1190.4543 | 8.024 | 95.727 | 135.2564 | -27.6497 | 26.5995 | 161.3826 | 8.0313 |  | 51.0775 | 89.904 | 37.0524 |  | 176.893 | 286.2295 | 41.7067 | 40.5161 | 18.4034 | 260 | 50.1017 | 0 | -49.1471 | 0.12988
11390 | 1216.393 | 11.1188 | 94.1334 | 133.2145 | -26.6441 | 25.6503 | 166.9884 | 7.4395 |  | 49.1807 | 92.2741 | 38.2781 |  | 177.2813 | 286.5243 | 40.5444 | 45.0476 | 19.0197 | 234 | 48.6495 | 0 | -45.6367 | 0.17412
11391 | 1184.4502 | 18.0316 | 90.6276 | 128.3841 | -19.6447 | 19.0018 | 160.4079 | 6.7095 |  | 51.6369 | 91.0403 | 36.315 |  | 173.5472 | 279.5393 | 35.9902 | 47.8669 | 19.2164 | 241 | 45.5492 | 0 | -63.7749 | 0.17636
11392 | 1136.0778 | 12.7129 | 87.1183 | 124.5522 | -18.6422 | 18.0503 | 148.3248 | 5.0692 |  | 50.7676 | 87.832 | 32.7436 |  | 158.2964 | 255.0314 | 29.7258 | 47.0393 | 18.1172 | 217 | 37.7275 | 0 | -52.8872 | 0.22427
11393 | 1083.7883 | 7.2679 | 83.0472 | 110.7357 | -10.6451 | 10.4521 | 134.566 | 4.642 |  | 44.608 | 80.1967 | 33.5231 |  | 117.8121 | 215.127 | 16.1733 | 45.9446 | 16.4648 | 201 | 40.2118 | 0 | -46.7259 | 0.20177
11394 | 1032.748 | 4.8646 | 80.3273 | 97.94 | -9.6426 | 9.5003 | 123.8206 | 5.612 |  | 30.3714 | 68.3145 | 30.7778 |  | 74.2676 | 189.0573 | 9.8787 | 42.9071 | 13.0842 | 195 | 42.7713 | 0 | -23.7609 | 0.16914
11395 | 1002.0053 | 5.1245 | 72.0154 | 92.7556 | -8.6452 | 8.5526 | 106.3165 | 4.6856 |  | 22.2525 | 61.0518 | 16.5339 |  | 58.8832 | 162.7502 | 8.8502 | 38.9253 | 6.9788 | 178 | 43.8936 | 0 | -9.0397 | 0.03755
11396 | 984.0497 | 5.3533 | 36.2626 | 89.7717 | -9.6362 | 9.4974 | 97.5686 | 4.3553 |  | 19.4992 | 57.5855 | 15.4256 |  | 54.6565 | 144.3353 | 8.7977 | 37.8836 | 5.0336 | 155 | 39.5114 | 0 | -7.9475 | 0
11397 | 932.7479 | 4.7102 | 22.0411 | 94.1763 | -9.6385 | 9.5 | 91.6106 | 4.213 |  | 16.9496 | 49.2771 | 22.0388 |  | 51.8397 | 141.011 | 9.1428 | 37.8834 | 4.9454 | 143 | 34.0394 | 0 | -7.3069 | 0
11398 | 910.0642 | 3.929 | 21.1552 | 91.6035 | -6.641 | 6.6508 | 81.0599 | 4.1272 |  | 15.0539 | 39.9743 | 22.5923 |  | 49.2137 | 138.6945 | 9.0334 | 37.2419 | 4.9866 | 133 | 31.5921 | 0 | -6.5346 | 0
11399 | 257.9834 | 0 | 5.6006 | 22.8883 | 0.13101 | 0.001848 | 22.3225 | 1.2467 |  | 4.3663 | 11.8179 | 6.5049 |  | 12.9115 | 42.4334 | 2.3299 | 9.5864 | 1.5341 | 116 | 2.3257 | 0 | -1.4237 | 0
11400 | 888.4775 | 2.5934 | 21.1122 | 89.0833 | -4.638 | 4.7505 | 71.9371 | 4.4908 |  | 14.0276 | 36.5924 | 11.7877 |  | 45.7616 | 125.3921 | 9.0955 | 37.2483 | 3.6656 | 110 | 32.4109 | 0 | -5.1984 | 0
11401 | 894.8786 | 2.5498 | 21.1324 | 88.5468 | -5.6404 | 5.6997 | 73.454 | 4.6725 |  | 13.5544 | 37.2561 | 12.2736 |  | 44.5146 | 120.2865 | 9.1158 | 37.1427 | 3.5133 | 103 | 28.5843 | 0 | -5.1464 | 0
11402 | 875.9035 | 2.7099 | 21.1491 | 88.3712 | -5.6413 | 5.7 | 74.0116 | 4.9889 |  | 13.6415 | 37.4412 | 8.6674 |  | 43.5815 | 126.3545 | 9.1216 | 37.2455 | 3.5685 | 101 | 29.1067 | 0 | -5.2095 | 0
11403 | 870.2306 | 2.5541 | 21.3255 | 88.9709 | -4.6395 | 4.7503 | 74.137 | 4.8441 |  | 13.5932 | 37.2535 | 6.9979 |  | 43.2775 | 129.1144 | 8.9001 | 37.1708 | 3.4003 | 99 | 28.1693 | 0 | -5.1446 | 0
11404 | 862.0939 | 3.2258 | 21.3594 | 89.0308 | -5.6368 | 5.6997 | 73.9048 | 4.7328 |  | 13.4965 | 36.8103 | 6.7869 |  | 43.3531 | 123.5816 | 8.9982 | 38.1581 | 3.264 | 118 | 28.3653 | 0 | -5.7394 | 0
11405 | 868.4354 | 4.7641 | 35.6118 | 87.8418 | -5.6418 | 5.7 | 78.9072 | 4.6119 |  | 19.8217 | 37.1211 | 7.3734 |  | 48.3136 | 118.0438 | 8.9669 | 39.0502 | 3.0255 | 116 | 28.7508 | 0 | -7.3531 | 0
11406 | 905.4774 | 7.6123 | 54.5972 | 90.1762 | -8.6414 | 8.5492 | 90.0754 | 3.7539 |  | 30.4902 | 42.6498 | 11.2938 |  | 80.8509 | 131.3382 | 11.2759 | 37.2466 | 2.7866 | 161 | 38.084 | 0 | -31.1559 | 0.14897
11407 | 971.0381 | 15.5402 | 75.4717 | 96.0111 | -18.6438 | 18.0474 | 109.4963 | 5.2328 |  | 39.7928 | 64.805 | 25.182 |  | 117.013 | 180.9842 | 25.5371 | 38.0269 | 5.4755 | 274 | 56.4032 | 0 | -50.8893 | 0.22796
11408 | 1057.9568 | 20.8308 | 86.6441 | 110.4983 | -19.6606 | 19.005 | 129.3615 | 7.0904 |  | 41.4072 | 81.2333 | 30.3914 |  | 146.193 | 229.9968 | 33.5425 | 41.03 | 12.5993 | 279 | 68.772 | 0 | -66.4427 | 0.30998
11409 | 1145.6226 | 14.9297 | 91.0131 | 124.8331 | -19.6478 | 18.9947 | 151.505 | 8.5589 |  | 41.2208 | 89.8179 | 32.3836 |  | 161.8117 | 274.0846 | 38.4053 | 46.8302 | 18.9536 | 313 | 77.2157 | 0 | -58.1803 | 0.33844
11410 | 1178.3986 | 11.454 | 90.0454 | 129.9181 | -22.6457 | 21.8492 | 157.7288 | 8.3651 |  | 43.2629 | 91.5909 | 37.8416 |  | 175.4762 | 301.8588 | 41.1528 | 50.3999 | 18.7679 | 352 | 76.2544 | 0 | -53.3093 | 0.33008
11411 | 1205.2219 | 7.912 | 94.6385 | 130.5062 | -21.6476 | 20.9003 | 156.0976 | 7.314 |  | 49.5895 | 89.3656 | 40.4936 |  | 185.1075 | 307.5289 | 41.5186 | 51.4968 | 17.6235 | 319 | 82.9824 | 0 | -39.8325 | 0.30037
11412 | 1190.8131 | 12.3286 | 95.2154 | 129.7999 | -20.6464 | 19.9503 | 159.2319 | 7.3859 |  | 48.0174 | 88.8799 | 40.5355 |  | 184.0478 | 302.3994 | 41.1745 | 50.2947 | 17.5249 | 349 | 75.469 | 0 | 233.3458 | 0.29573
11413 | 1194.3752 | 14.9611 | 95.3992 | 130.3715 | -21.6457 | 20.8997 | 163.0654 | 6.3038 |  | 47.2856 | 91.6638 | 40.2173 |  | 187.7628 | 294.273 | 42.338 | 51.0603 | 17.9175 | 295 | 78.5017 | 0 | 217.3652 | 0.29567
11414 | 1201.122 | 9.9061 | 94.149 | 134.2597 | -19.6539 | 19.0005 | 166.9358 | 6.0283 |  | 48.1935 | 93.079 | 35.8544 |  | 184.4425 | 289.4105 | 43.4421 | 54.1988 | 18.1079 | 281 | 79.0521 | 0 | 220.966 | 0.31338
11415 | 1177.7761 | 7.5266 | 91.631 | 129.2768 | -15.6478 | 15.2011 | 161.8821 | 6.8652 |  | 51.1126 | 93.4228 | 36.3419 |  | 177.5968 | 283.7916 | 42.598 | 48.2758 | 18.276 | 255 | 74.6718 | 0 | 218.1718 | 0.25738
11416 | 1139.0564 | 10.789 | 87.8272 | 122.9628 | -15.6437 | 15.2 | 148.2845 | 7.2854 |  | 50.6525 | 90.592 | 36.338 |  | 167.9689 | 258.4134 | 34.8346 | 44.1321 | 17.7275 | 243 | 60.0815 | 0 | 190.2551 | 0.24497
11417 | 1091.4477 | 8.3952 | 83.3127 | 109.7092 | -6.6448 | 6.6524 | 132.2878 | 5.7351 |  | 38.7527 | 79.6322 | 33.7603 |  | 135.6657 | 226.2375 | 18.1074 | 39.7643 | 17.0914 | 229 | 50.6525 | 0 | 135.9709 | 0.25827
11418 | 1041.6616 | 6.3394 | 79.9883 | 97.2411 | -5.6417 | 5.7003 | 118.1735 | 4.4761 |  | 23.8097 | 67.0487 | 27.9228 |  | 89.8337 | 195.3963 | 10.3226 | 35.364 | 14.8796 | 229 | 47.6155 | 0 | 124.0184 | 0.21477
11419 | 1005.6507 | 6.1831 | 71.4013 | 92.445 | -5.6428 | 5.7 | 109.8365 | 3.7247 |  | 7.4886 | 59.7542 | 13.275 |  | 76.5798 | 170.5649 | 8.9133 | 30.9965 | 8.6579 | 184 | 44.1407 | 0 | 106.9689 | 0.066472
11420 | 963.9434 | 5.5377 | 36.8309 | 89.4742 | -5.6455 | 5.7 | 92.8637 | 3.9197 |  | 6.6472 | 56.5877 | 10.4885 |  | 73.3081 | 154.392 | 9.0273 | 28.1968 | 6.2806 | 182 | 41.1297 | 0 | 114.5653 | 0
11421 | 928.1282 | 4.6344 | 23.0376 | 88.8408 | -5.6482 | 5.7 | 81.3104 | 4.1107 |  | 7.1207 | 48.4839 | 10.7841 |  | 61.6113 | 144.5563 | 9.1719 | 27.5828 | 5.988 | 176 | 36.4208 | 0 | 110.229 | 0
11422 | 899.5455 | 3.8816 | 21.684 | 88.467 | -5.6443 | 5.7 | 80.2606 | 4.311 |  | 13.3082 | 39.1191 | 10.1354 |  | 57.0735 | 135.388 | 9.2022 | 27.3553 | 5.9258 | 152 | 36.2424 | 0 | 102.7985 | 0
11423 | 249.3252 | 1.1668 | 5.6056 | 22.0038 | 0.13004 | 0.001584 | 22.8861 | 1.308 |  | 3.8244 | 11.4359 | 2.919 |  | 14.8679 | 40.3965 | 2.3616 | 6.9665 | 1.7907 | 144 | 2.5921 | 0 | 8.3086 | 0
11424 | 882.0377 | 2.8229 | 21.3242 | 88.1019 | -5.6422 | 5.7 | 78.0644 | 3.7151 |  | 13.1383 | 35.3399 | 9.9987 |  | 52.0298 | 132.3414 | 9.105 | 27.2233 | 3.9177 | 139 | 33.2844 | 0 | 95.2332 | 0
11425 | 888.5294 | 2.6923 | 21.1241 | 88.1219 | -4.6413 | 4.7503 | 76.4704 | 3.2241 |  | 12.627 | 35.4744 | 10.0184 |  | 50.3052 | 127.585 | 9.0857 | 27.1775 | 3.0712 | 131 | 34.3913 | 0 | 96.125 | 0
11426 | 859.462 | 2.4679 | 21.1935 | 88.3143 | -5.6392 | 5.6997 | 75.3739 | 3.6449 |  | 12.2493 | 36.5753 | 10.051 |  | 49.9662 | 120.8158 | 9.1384 | 27.3421 | 2.7634 | 130 | 32.7086 | 0 | 97.0965 | 0
11427 | 865.2434 | 3.3144 | 21.2031 | 88.185 | -5.6412 | 5.7 | 75.0241 | 4.0398 |  | 12.2155 | 37.0447 | 10.0168 |  | 50.6524 | 116.1175 | 9.1763 | 27.1811 | 2.7892 | 123 | 32.7082 | 0 | 98.1608 | 0
11428 | 866.3412 | 3.4053 | 21.19 | 88.3542 | -5.6429 | 5.7 | 74.8428 | 4.1972 |  | 12.2642 | 36.9458 | 11.0634 |  | 50.0902 | 113.3465 | 8.8706 | 27.7221 | 2.7353 | 117 | 31.1987 | 0 | 104.568 | 0
11429 | 867.0856 | 4.3753 | 35.5396 | 86.4385 | -5.6427 | 5.7 | 80.1889 | 4.1207 |  | 16.0835 | 35.9897 | 11.2332 |  | 54.1177 | 113.6683 | 8.7659 | 28.7211 | 2.6459 | 118 | 31.277 | 0 | 117.8787 | 0
11430 | 915.5148 | 8.5038 | 51.6573 | 91.3416 | -11.6407 | 11.3984 | 93.7757 | 4.074 |  | 25.9977 | 41.3313 | 13.6818 |  | 85.7142 | 121.3744 | 11.2513 | 27.0568 | 2.5279 | 161 | 38.0026 | 0 | 127.0155 | 0.1495
11431 | 980.3389 | 15.7808 | 73.2167 | 95.6339 | -17.6448 | 17.0984 | 113.2677 | 5.1287 |  | 38.0168 | 65.4827 | 22.4079 |  | 116.9261 | 170.8793 | 26.9098 | 29.2878 | 4.9039 | 250 | 55.5146 | 0 | 136.7677 | 0.2546
11432 | 1061.5946 | 24.4262 | 87.2524 | 111.9098 | -17.647 | 17.1 | 131.2575 | 4.9916 |  | 38.8882 | 83.4587 | 25.3932 |  | 150.171 | 241.4167 | 36.079 | 34.6038 | 11.2972 | 308 | 68.3153 | 0 | 160.9603 | 0.31133
11433 | 1154.4774 | 20.6525 | 92.9207 | 126.5879 | -20.6471 | 19.9492 | 143.9073 | 6.5854 |  | 40.5406 | 89.9607 | 26.2206 |  | 165.545 | 282.8169 | 40.2649 | 39.4193 | 15.6746 | 358 | 71.7977 | 0 | 183.0273 | 0.33694
11434 | 1193.903 | 14.5039 | 91.3156 | 132.7684 | -22.6507 | 21.8495 | 147.6521 | 7.5233 |  | 46.8068 | 91.2501 | 28.0278 |  | 171.8675 | 296.226 | 42.2296 | 42.4162 | 17.1066 | 335 | 69.2536 | 0 | 192.22 | 0.25842
11435 | 1196.0463 | 15.3801 | 90.8561 | 130.2706 | -19.6566 | 19.0008 | 134.3908 | 6.3803 |  | 50.6611 | 88.8859 | 28.3714 |  | 177.1583 | 298.7742 | 41.6833 | 47.3639 | 17.6326 | 311 | 65.5448 | 0 | 196.745 | 0.29947
11436 | 1177.1806 | 15.3684 | 91.1895 | 131.1274 | -22.6557 | 21.8492 | 129.2847 | 6.6468 |  | 43.7115 | 88.9706 | 27.4893 |  | 172.9717 | 292.8138 | 42.5747 | 50.0589 | 18.2336 | 334 | 58.5073 | 0 | 199.9582 | 0.30454
11437 | 1190.2348 | 17.106 | 91.3444 | 137.6795 | -20.6525 | 19.9505 | 140.7724 | 6.9188 |  | 44.523 | 90.5618 | 28.144 |  | 173.1628 | 294.1467 | 43.7228 | 51.2025 | 18.5047 | 277 | 58.1732 | 0 | 196.7592 | 0.32995
11438 | 1194.5035 | 15.8747 | 90.0789 | 138.7362 | -21.6461 | 20.8997 | 147.7842 | 5.8324 |  | 49.8162 | 94.0369 | 28.3438 |  | 174.2753 | 293.8488 | 41.6067 | 51.1683 | 18.4614 | 273 | 55.2801 | 0 | 196.0413 | 0.33028
11439 | 1180.6058 | 10.4098 | 92.2778 | 134.7801 | -29.6511 | 28.5058 | 145.9374 | 5.5112 |  | 43.0608 | 94.5279 | 25.6111 |  | 168.3087 | 286.3692 | 38.1302 | 50.3729 | 18.208 | 267 | 51.1738 | 0 | 190.2754 | 0.29041
11440 | 1129.0565 | 8.7197 | 90.8267 | 117.739 | -19.638 | 18.9947 | 137.8792 | 4.9513 |  | 39.1058 | 91.9556 | 26.6713 |  | 154.1241 | 247.6729 | 29.4536 | 46.6725 | 17.7417 | 261 | 44.5152 | 0 | 168.5134 | 0.26011
11441 | 1071.0978 | 8.5231 | 78.5768 | 103.6193 | -12.6421 | 12.3518 | 125.5571 | 2.475 |  | 32.285 | 79.2001 | 27.4499 |  | 120.648 | 202.9701 | 17.9368 | 38.1528 | 17.4016 | 248 | 39.3496 | 0 | 126.4526 | 0.23032
11442 | 1020.0109 | 7.0312 | 38.9855 | 92.9159 | -10.6463 | 10.4534 | 111.5454 | 3.0282 |  | 21.3809 | 67.2398 | 25.618 |  | 73.9321 | 169.9304 | 13.3824 | 32.7823 | 14.6996 | 229 | 43.0928 | 0 | 119.6875 | 0.18667
11443 | 973.0303 | 9.9712 | 22.0039 | 87.2249 | -11.6383 | 11.3968 | 106.9842 | 3.7264 |  | 16.4484 | 65.9005 | 16.2925 |  | 56.2616 | 156.1945 | 12.6034 | 29.6562 | 8.6729 | 206 | 42.0321 | 0 | 104.1695 | 0.075306
11444 | 939.6467 | 16.9616 | 20.7154 | 86.2466 | -9.6444 | 9.5005 | 100.5336 | 3.5546 |  | 15.8381 | 53.3195 | 10.2993 |  | 53.8732 | 150.656 | 11.2481 | 27.8596 | 6.2972 | 199 | 38.5493 | 0 | 90.8476 | 0
11445 | 910.3201 | 17.1605 | 21.5449 | 87.3021 | -10.6429 | 10.4497 | 88.3476 | 3.1885 |  | 14.8209 | 40.0911 | 10.1106 |  | 53.328 | 140.6013 | 10.4869 | 27.3161 | 5.4392 | 190 | 35.9105 | 0 | 88.4124 | 0
11446 | 892.0996 | 12.949 | 21.4135 | 87.2552 | -10.6447 | 10.45 | 87.2413 | 3.8562 |  | 13.9307 | 36.2862 | 10.6988 |  | 52.2939 | 131.9087 | 10.4871 | 26.9814 | 5.3451 | 165 | 34.9638 | 0 | 93.2271 | 0
11447 | 253.2098 | 3.7272 | 5.5787 | 22.0681 | 0.1293 | 0.002903 | 25.5233 | 1.2738 |  | 4.1308 | 11.5229 | 3.2139 |  | 13.7296 | 40.2662 | 2.7463 | 6.933 | 1.6728 | 131 | 2.5215 | 0 | 6.4585 | 0
11448 | 871.8635 | 10.2594 | 21.2613 | 87.1997 | -10.641 | 10.45 | 74.16 | 4.5626 |  | 12.7382 | 35.7922 | 10.1068 |  | 47.1053 | 124.8138 | 11.1323 | 25.8766 | 4.8287 | 126 | 34.1271 | 0 | 87.4411 | 0
11449 | 862.3795 | 9.371 | 21.2954 | 87.3468 | -10.6435 | 10.45 | 74.2582 | 4.739 |  | 12.3086 | 36.7565 | 10.1704 |  | 44.6861 | 125.603 | 11.1091 | 26.0499 | 3.8162 | 128 | 37.5598 | 0 | 84.6256 | 0
11450 | 847.7712 | 4.9579 | 21.2021 | 86.5623 | -12.6441 | 12.3529 | 73.9309 | 4.7916 |  | 11.9278 | 37.8226 | 10.0039 |  | 42.9659 | 128.6631 | 11.2118 | 26.1074 | 3.4454 | 125 | 34.4596 | 0 | 88.5877 | 0
11451 | 841.5576 | 3.0108 | 21.1528 | 87.7524 | -10.6373 | 10.4471 | 73.4312 | 5.1951 |  | 11.7562 | 37.7375 | 9.8547 |  | 42.4712 | 125.4776 | 11.2423 | 26.4127 | 3.3076 | 116 | 34.148 | 0 | 88.9451 | 0
11452 | 837.0794 | 3.2932 | 21.2424 | 87.7945 | -10.6389 | 10.45 | 72.6239 | 5.1795 |  | 11.9222 | 37.2835 | 9.8085 |  | 42.2201 | 117.3338 | 11.1872 | 26.9906 | 3.2367 | 112 | 33.2114 | 0 | 88.2221 | 0
11453 | 846.9832 | 4.4174 | 22.0978 | 85.6864 | -10.6403 | 10.45 | 67.9338 | 4.3621 |  | 10.153 | 38.2711 | 8.4366 |  | 40.8396 | 110.3653 | 10.678 | 27.7303 | 3.1798 | 110 | 30.9281 | 0 | 84.7683 | 0
11454 | 852.3067 | 4.026 | 39.2819 | 84.6271 | -9.6439 | 9.5003 | 68.1798 | 3.8256 |  | 9.1512 | 41.1567 | 7.2622 |  | 39.6451 | 107.5447 | 10.527 | 25.9215 | 3.0859 | 112 | 31.3336 | 0 | 87.1245 | 0.024208
11455 | 866.3855 | 3.1013 | 49.0089 | 84.3025 | -10.6459 | 10.4497 | 74.9032 | 3.5379 |  | 9.1392 | 42.5948 | 9.6486 |  | 39.9446 | 108.9471 | 10.4456 | 25.1396 | 3.1135 | 110 | 36.5545 | 0 | 84.49 | 0.043128
11456 | 878.9429 | 3.2173 | 55.9324 | 84.1868 | -11.6451 | 11.3997 | 90.5263 | 3.1509 |  | 15.3297 | 42.0554 | 14.5511 |  | 43.248 | 113.2086 | 10.0441 | 25.6269 | 3.4662 | 113 | 38.9499 | 0 | 86.6179 | 0.068397
11457 | 901.0111 | 3.3558 | 73.3625 | 84.5487 | -10.6448 | 10.4503 | 100.1011 | 3.5925 |  | 23.431 | 42.5453 | 17.2307 |  | 49.0248 | 127.3539 | 9.7934 | 26.3491 | 6.3625 | 119 | 36.7763 | 0 | 89.6394 | 0.080922
11458 | 914.816 | 3.7426 | 85.1077 | 85.0854 | -9.6462 | 9.5003 | 100.0013 | 4.0493 |  | 27.7342 | 46.8792 | 17.1756 |  | 56.7157 | 140.3459 | 9.5897 | 26.3774 | 11.4739 | 135 | 34.7853 | 0 | 90.4161 | 0.12737
11459 | 924.3275 | 3.8887 | 86.6587 | 85.3494 | -10.6461 | 10.4497 | 90.8496 | 3.5633 |  | 28.5109 | 52.0832 | 17.3407 |  | 64.8495 | 141.9654 | 9.6445 | 26.5132 | 14.0271 | 197 | 32.9187 | 0 | 92.4094 | 0.2374
11460 | 919.5003 | 4.1285 | 86.8864 | 85.7696 | -11.6464 | 11.3997 | 89.1806 | 3.3835 |  | 27.8701 | 58.3107 | 17.7908 |  | 69.7224 | 149.1159 | 9.7879 | 26.21 | 14.1659 | 185 | 37.4231 | 0 | 91.7193 | 0.23735
11461 | 915.8882 | 8.5702 | 75.576 | 89.1524 | -10.6512 | 10.4503 | 92.2847 | 3.3078 |  | 28.1819 | 62.0516 | 18.3038 |  | 71.1891 | 161.5908 | 9.8474 | 26.4657 | 14.0597 | 171 | 30.8842 | 0 | 87.9405 | 0.19442
11462 | 911.8621 | 12.6159 | 39.2 | 90.5534 | -10.6512 | 10.45 | 95.8164 | 2.5534 |  | 28.912 | 65.7627 | 19.5047 |  | 67.5919 | 166.7545 | 9.7901 | 26.6156 | 11.7118 | 186 | 26.6344 | 0 | 84.224 | 0.1793
11463 | 911.5166 | 8.742 | 19.9632 | 87.8798 | -9.6483 | 9.5003 | 108.2265 | 2.4724 |  | 24.3514 | 74.1447 | 18.2337 |  | 61.9107 | 158.781 | 9.4916 | 26.4238 | 7.1932 | 191 | 22.0503 | 0 | 87.2462 | 0.20601
11464 | 914.5229 | 4.367 | 19.1622 | 86.0491 | -9.6463 | 9.5 | 124.5497 | 2.9189 |  | 14.4853 | 72.0157 | 12.0982 |  | 63.5772 | 154.3334 | 9.6447 | 25.9841 | 5.1146 | 204 | 21.1814 | 0 | 81.7888 | 0.13266
11465 | 911.801 | 3.9024 | 19.1482 | 85.8124 | -9.6446 | 9.5 | 120.5371 | 2.0874 |  | 9.6283 | 59.5692 | 8.3541 |  | 64.21 | 149.1866 | 9.82 | 25.6915 | 5.3389 | 196 | 25.7908 | 0 | 77.9411 | 0.10575
11466 | 891.4469 | 3.2973 | 19.1756 | 86.3357 | -10.6425 | 10.4497 | 111.275 | 2.7828 |  | 10.3569 | 50.1661 | 8.3268 |  | 60.1981 | 141.6912 | 9.7983 | 25.9083 | 4.8697 | 195 | 33.7785 | 0 | 80.5546 | 0.091297
11467 | 868.9174 | 3.1885 | 19.0729 | 85.4246 | -9.6455 | 9.5003 | 103.9238 | 3.73 |  | 11.425 | 44.3252 | 8.3128 |  | 54.6641 | 143.2232 | 9.7404 | 25.5864 | 4.5698 | 194 | 37.3744 | 0 | 85.2843 | 0.023295
11468 | 852.2279 | 4.271 | 19.4646 | 85.0771 | -10.6459 | 10.4497 | 98.0256 | 3.9201 |  | 12.1413 | 39.4808 | 8.6297 |  | 49.6389 | 143.064 | 9.5973 | 25.5704 | 4.7376 | 207 | 37.2357 | 0 | 90.426 | 0
11469 | 847.7154 | 5.0953 | 20.0848 | 86.9732 | -11.6465 | 11.3997 | 96.7326 | 4.0089 |  | 13.4572 | 38.6506 | 10.321 |  | 49.0898 | 136.9376 | 10.4387 | 25.7908 | 4.7361 | 185 | 39.3434 | 0 | 95.234 | 0
11470 | 848.3951 | 4.4907 | 20.2922 | 87.5194 | -10.6462 | 10.4503 | 85.8779 | 3.9868 |  | 14.0893 | 39.0542 | 11.0324 |  | 48.8868 | 133.282 | 11.0388 | 25.8307 | 4.5919 | 165 | 37.1533 | 0 | 95.0076 | 0
11471 | 341.8256 | 1.695 | 7.759 | 32.5577 | 0.17403 | 0.002903 | 31.9652 | 1.692 |  | 5.8594 | 16.9107 | 4.5041 |  | 18.5701 | 56.8573 | 4.2112 | 9.7555 | 1.9087 | 143 | 6.9343 | 0 | 19.2324 | 0
11472 | 844.6833 | 2.9126 | 20.3521 | 87.3307 | -10.642 | 10.45 | 77.0729 | 4.2667 |  | 12.9818 | 37.4415 | 10.4711 |  | 50.2621 | 136.2635 | 11.0233 | 25.8797 | 3.4739 | 150 | 33.2439 | 0 | 93.7107 | 0
11473 | 849.3414 | 2.7434 | 20.4148 | 87.3802 | -10.6409 | 10.45 | 75.8797 | 4.575 |  | 12.4005 | 37.8178 | 9.9677 |  | 50.5664 | 131.0978 | 10.877 | 25.8875 | 3.1144 | 146 | 32.5727 | 0 | 93.8332 | 0
11474 | 831.0157 | 2.639 | 20.4701 | 87.4573 | -18.6375 | 18.0479 | 74.1378 | 5.0817 |  | 12.1659 | 37.8116 | 9.8778 |  | 47.0653 | 125.4998 | 10.9991 | 25.8506 | 2.8824 | 135 | 33.5769 | 0 | 94.4873 | 0
11475 | 817.8652 | 2.6058 | 20.5189 | 87.3051 | -14.6411 | 14.2511 | 69.9718 | 5.4436 |  | 12.2293 | 37.6426 | 9.8664 |  | 46.5142 | 120.2004 | 11.1407 | 25.9193 | 2.8532 | 124 | 33.3005 | 0 | 93.9344 | 0
11476 | 809.2894 | 3.0542 | 20.5541 | 87.5116 | -14.6447 | 14.25 | 72.2243 | 5.6343 |  | 12.2904 | 38.2259 | 9.8306 |  | 44.5518 | 116.3038 | 11.0036 | 26.9164 | 2.9877 | 118 | 36.2769 | 0 | 94.8418 | 0
11477 | 816.955 | 3.9912 | 20.1566 | 86.2108 | -10.644 | 10.4511 | 73.8349 | 5.2411 |  | 10.4848 | 37.1747 | 8.3613 |  | 41.7353 | 112.1363 | 10.7499 | 27.3903 | 2.9689 | 119 | 37.2266 | 0 | 91.4926 | 0
11478 | 828.8185 | 3.9623 | 19.9428 | 84.6475 | -10.639 | 10.45 | 65.8092 | 4.7153 |  | 9.1609 | 35.8808 | 7.1737 |  | 40.7235 | 107.9209 | 10.4401 | 26.0828 | 2.9116 | 115 | 31.5435 | 0 | 90.8225 | 0.02007
11479 | 838.978 | 3.0741 | 19.9254 | 84.4614 | -10.6392 | 10.45 | 65.7216 | 3.8409 |  | 9.263 | 35.9971 | 7.2657 |  | 40.367 | 106.3629 | 10.4967 | 25.503 | 2.7805 | 106 | 29.7707 | 0 | 90.7597 | 0.053901
11480 | 844.7541 | 2.7988 | 19.6462 | 84.4952 | -10.6415 | 10.45 | 78.2153 | 3.0638 |  | 14.026 | 37.0398 | 7.1663 |  | 41.7782 | 107.1724 | 10.1878 | 25.2681 | 2.8031 | 123 | 23.3174 | 0 | 91.4213 | 0.082722
11481 | 853.4703 | 2.7215 | 19.8345 | 84.7716 | -10.6445 | 10.45 | 98.2181 | 3.3271 |  | 21.9013 | 41.3817 | 6.9892 |  | 43.4417 | 115.2542 | 9.7922 | 25.1311 | 2.9036 | 162 | -42.0352 | 0 | 90.5328 | 0.12145
11482 | 885.7459 | 3.0239 | 19.7702 | 85.0833 | -10.6461 | 10.45 | 112.5468 | 4.1437 |  | 27.5015 | 45.1382 | 6.9812 |  | 48.2364 | 126.8706 | 9.7332 | 25.0425 | 2.9218 | 154 | 19.2569 | 0 | 92.0514 | 0.13301
11483 | 905.8653 | 3.7697 | 19.3707 | 84.9185 | -9.6487 | 9.5003 | 109.0672 | 4.3041 |  | 28.822 | 46.7869 | 7.0744 |  | 55.2984 | 134.8783 | 9.5397 | 24.9584 | 2.9211 | 178 | 16.5629 | 0 | 91.8837 | 0.15264
11484 | 904.2291 | 3.5175 | 19.2582 | 88.2122 | -10.6489 | 10.4497 | 102.4765 | 4.0959 |  | 27.5716 | 52.1379 | 7.0479 |  | 57.6493 | 138.337 | 9.5737 | 25.0944 | 2.9122 | 162 | 14.7685 | 0 | 90.0784 | 0.19372
11485 | 901.7166 | 3.8668 | 19.3886 | 91.899 | -9.6484 | 9.5003 | 104.7039 | 3.4289 |  | 26.8904 | 56.1617 | 8.395 |  | 60.1491 | 142.2431 | 9.6893 | 25.698 | 3.9591 | 170 | 15.8378 | 0 | 92.6382 | 0.18306
11486 | 910.3044 | 3.9877 | 19.3959 | 89.5839 | -10.6464 | 10.4497 | 104.0427 | 2.8728 |  | 26.1126 | 57.7547 | 8.9515 |  | 67.4073 | 140.9847 | 9.6808 | 26.7035 | 4.8385 | 168 | 19.2556 | 0 | 92.8219 | 0.13955
11487 | 934.8342 | 6.0556 | 19.4008 | 86.8393 | -9.6466 | 9.5003 | 106.3936 | 3.467 |  | 20.9055 | 60.2128 | 10.8947 |  | 65.7716 | 140.3131 | 9.7316 | 27.3288 | 4.8819 | 166 | 20.5234 | 0 | 91.6137 | 0.18449
11488 | 937.2911 | 9.2689 | 19.4823 | 87.7763 | -11.6432 | 11.3995 | 108.2462 | 3.6383 |  | 13.4956 | 59.7627 | 16.021 |  | 61.8366 | 144.75 | 9.5246 | 27.4386 | 4.8815 | 161 | 20.5212 | 0 | 88.0096 | 0.075577
11489 | 935.5101 | 8.7131 | 19.5429 | 88.5245 | -11.6449 | 11.4 | 99.6135 | 2.2427 |  | 9.9591 | 54.9147 | 13.7291 |  | 58.7666 | 154.855 | 9.5156 | 27.3231 | 4.6469 | 152 | 26.5113 | 0 | 85.9793 | 0.1261
11490 | 917.4358 | 8.8486 | 19.4155 | 88.6799 | -9.648 | 9.5005 | 92.9366 | 2.8021 |  | 9.9145 | 52.0878 | 8.336 |  | 55.3941 | 159.2636 | 9.6662 | 26.2121 | 4.4216 | 143 | 32.3655 | 0 | 87.2859 | 0.038042
11491 | 895.8919 | 11.2686 | 19.3738 | 89.3742 | -10.6498 | 10.4497 | 90.4573 | 3.811 |  | 11.2505 | 54.3293 | 13.1038 |  | 52.9653 | 151.1615 | 9.7374 | 25.4653 | 4.3642 | 139 | 34.411 | 0 | 86.4469 | 0.014355
11492 | 881.1144 | 15.8261 | 19.4832 | 88.6941 | -9.6481 | 9.5003 | 82.0141 | 3.8893 |  | 12.2395 | 46.3125 | 15.6929 |  | 55.5925 | 140.7135 | 9.9875 | 25.4986 | 4.1541 | 140 | 35.7145 | 0 | 86.3367 | 0
11493 | 879.697 | 17.254 | 19.9047 | 88.8665 | -10.6432 | 10.4497 | 77.1959 | 3.901 |  | 12.6585 | 39.3744 | 18.9508 |  | 58.7911 | 132.7014 | 10.5367 | 26.0596 | 3.8544 | 145 | 35.6289 | 0 | 88.8744 | 0
11494 | 871.4759 | 11.2737 | 20.1672 | 88.1191 | -10.6447 | 10.45 | 77.4427 | 3.9864 |  | 12.7476 | 38.4996 | 20.9909 |  | 54.3202 | 127.3556 | 10.9424 | 26.4497 | 3.0764 | 143 | 37.0174 | 0 | 93.6411 | 0
11495 | 350.8899 | 3.2858 | 7.7395 | 32.6944 | 0.17282 | 0.002903 | 31.7683 | 1.7337 |  | 5.3455 | 16.4273 | 8.3973 |  | 19.7031 | 54.1917 | 4.2266 | 10.036 | 1.1044 | 137 | 7.2577 | 0 | 18.8132 | 0
11496 | 855.4005 | 2.4683 | 20.3218 | 87.5162 | -10.6416 | 10.45 | 76.817 | 4.3564 |  | 12.7029 | 37.3485 | 10.6551 |  | 44.0628 | 120.4666 | 11.123 | 26.0618 | 2.8258 | 135 | 34.0466 | 0 | 93.5741 | 0
11497 | 861.7485 | 2.3842 | 20.3596 | 87.4271 | -10.6415 | 10.45 | 76.5227 | 4.5949 |  | 12.7938 | 38.2041 | 10.5205 |  | 43.5256 | 117.8431 | 11.1555 | 26.0748 | 2.7983 | 121 | 32.1561 | 0 | 92.0307 | 0
11498 | 844.0346 | 2.4557 | 20.316 | 87.8496 | -10.6436 | 10.45 | 75.5862 | 4.6106 |  | 12.7692 | 37.8468 | 10.4582 |  | 45.1751 | 117.2021 | 10.9219 | 26.0577 | 2.6804 | 134 | 31.7347 | 0 | 93.5388 | 0
11499 | 832.0741 | 2.5732 | 21.0354 | 87.8168 | -10.6431 | 10.45 | 75.0068 | 4.6359 |  | 12.725 | 37.6358 | 10.4381 |  | 45.8676 | 116.5071 | 11.0125 | 26.0312 | 2.5654 | 122 | 31.4485 | 0 | 95.6557 | 0
11500 | 834.1642 | 2.9509 | 21.8317 | 88.5547 | -10.6418 | 10.45 | 74.8649 | 4.8911 |  | 12.6543 | 37.3877 | 10.4092 |  | 43.3253 | 114.4799 | 11.249 | 26.8694 | 2.5626 | 117 | 30.8486 | 0 | 110.481 | 0
11501 | 851.7193 | 4.3848 | 29.4863 | 86.5491 | -10.6419 | 10.45 | 76.9312 | 4.2229 |  | 15.7997 | 37.3535 | 10.6216 |  | 47.5119 | 114.3911 | 11.0669 | 27.5553 | 2.5363 | 113 | 32.7238 | 0 | 115.334 | 0
11502 | 889.1207 | 6.1873 | 44.124 | 87.5525 | -13.6439 | 13.2992 | 87.5787 | 3.4182 |  | 24.5004 | 42.6947 | 16.7098 |  | 79.2285 | 124.9774 | 14.4099 | 26.5628 | 2.7298 | 184 | 42.4471 | 0 | 123.3558 | 0.15451
11503 | 941.8306 | 10.6145 | 73.4391 | 96.9481 | -17.4585 | 17.0989 | 110.8079 | 4.2647 |  | 32.1437 | 63.0008 | 29.8423 |  | 116.5745 | 167.1038 | 27.7666 | 28.8228 | 6.7937 | 227 | 56.7883 | 0 | 137.7245 | 0.25481
11504 | 1026.2924 | 17.1672 | 91.4748 | 108.2542 | -18.4768 | 18.0497 | 137.4708 | 6.318 |  | 35.2749 | 78.681 | 35.4141 |  | 147.4673 | 233.9553 | 37.4281 | 33.9281 | 12.7773 | 300 | 64.5102 | 0 | 161.184 | 0.31318
11505 | 1123.9963 | 19.1111 | 98.4492 | 119.2357 | -19.6525 | 18.9997 | 149.4316 | 9.8051 |  | 42.9516 | 82.5836 | 37.9386 |  | 172.7009 | 287.5256 | 42.6034 | 38.9203 | 16.4782 | 291 | 69.2303 | 0 | 181.6339 | 0.33934
11506 | 1193.5435 | 16.2781 | 99.9025 | 127.5788 | -20.6514 | 19.9497 | 155.122 | 11.4996 |  | 51.2276 | 88.2513 | 41.4849 |  | 186.0561 | 309.9175 | 44.6114 | 43.1595 | 17.8003 | 356 | 73.5167 | 0 | 192.4803 | 0.31894
11507 | 1205.3001 | 12.8441 | 101.297 | 130.0521 | -19.6503 | 19.0003 | 162.229 | 9.4529 |  | 53.0642 | 92.2364 | 41.7869 |  | 189.0382 | 304.845 | 42.9483 | 42.3124 | 17.9388 | 352 | 72.6701 | 0 | 203.8868 | 0.29847
11508 | 1213.4275 | 8.1332 | 102.2682 | 129.3922 | -20.6524 | 19.9497 | 164.8102 | 8.7673 |  | 48.7061 | 91.3117 | 41.0973 |  | 187.3682 | 300.8729 | 41.5828 | 40.0365 | 18.1097 | 331 | 61.3281 | 0 | 212.4058 | 0.30924
11509 | 1223.2492 | 5.4697 | 105.1004 | 131.6218 | -20.6524 | 19.95 | 165.4514 | 9.0522 |  | 45.96 | 91.8398 | 40.7118 |  | 188.91 | 302.2493 | 41.7768 | 40.2911 | 18.5024 | 282 | 63.7513 | 0 | 212.6543 | 0.32867
11510 | 1230.6869 | 5.3093 | 105.912 | 136.5053 | -20.6501 | 19.95 | 165.5685 | 8.0326 |  | 45.2688 | 94.3756 | 38.9536 |  | 187.5538 | 301.2351 | 41.4619 | 41.6218 | 18.5679 | 292 | 72.5262 | 0 | 203.3763 | 0.33219
11511 | 1204.8639 | 5.3222 | 101.9732 | 134.5598 | -20.649 | 19.95 | 161.588 | 8.1652 |  | 42.5185 | 93.3174 | 36.5116 |  | 179.4483 | 289.4779 | 39.8318 | 42.041 | 18.6298 | 275 | 66.0655 | 0 | 201.057 | 0.29373
11512 | 1148.9192 | 8.2549 | 98.6474 | 124.4916 | -13.6463 | 13.3018 | 149.5775 | 7.5828 |  | 36.3814 | 89.7484 | 33.6358 |  | 165.6925 | 250.0763 | 31.1558 | 40.932 | 18.1871 | 247 | 48.1957 | 0 | 177.6708 | 0.27086
11513 | 1080.404 | 11.1745 | 96.4081 | 109.8639 | -10.6416 | 10.4508 | 134.9032 | 4.4809 |  | 28.1864 | 80.717 | 33.3189 |  | 132.3611 | 211.2063 | 17.596 | 37.3154 | 17.233 | 232 | 44.6694 | 0 | 132.3302 | 0.24658
11514 | 1019.2976 | 8.1626 | 91.9625 | 96.005 | -10.643 | 10.45 | 123.7347 | 4.2841 |  | 21.4538 | 67.5658 | 26.8584 |  | 98.3543 | 190.6426 | 10.7955 | 33.7337 | 14.1018 | 211 | 43.7581 | 0 | 120.8759 | 0.20455
11515 | 972.9673 | 5.1678 | 74.9743 | 89.8826 | -9.6418 | 9.5003 | 118.0635 | 5.1064 |  | 19.1949 | 61.2084 | 12.5214 |  | 79.2078 | 181.2005 | 9.6268 | 30.9 | 8.7264 | 209 | 42.1598 | 0 | 112.4913 | 0.10095
11516 | 952.0327 | 5.0001 | 38.8248 | 87.123 | -10.6386 | 10.4497 | 107.3356 | 4.6036 |  | 17.7272 | 57.091 | 6.8873 |  | 68.6481 | 167.9041 | 9.9585 | 28.9465 | 5.3022 | 184 | 38.9231 | 0 | 103.1991 | 0
11517 | 931.866 | 5.0385 | 21.0194 | 87.58 | -10.638 | 10.45 | 95.4856 | 4.2594 |  | 15.9786 | 48.8745 | 8.1805 |  | 64.4068 | 154.0918 | 10.6672 | 28.1213 | 3.8007 | 176 | 35.4001 | 0 | 101.0289 | 0
11518 | 900.6264 | 4.2146 | 20.24 | 87.9321 | -10.6393 | 10.45 | 79.318 | 4.1553 |  | 14.9714 | 39.6263 | 8.7854 |  | 61.2036 | 147.3746 | 10.6083 | 27.4849 | 3.1393 | 148 | 32.8182 | 0 | 103.1394 | 0
11519 | 359.2458 | 1.5746 | 7.7073 | 32.648 | 0.17513 | 0.002903 | 28.874 | 1.7713 |  | 6.1984 | 15.8684 | 3.7262 |  | 22.8306 | 63.2008 | 3.9617 | 10.256 | 1.3373 | 139 | 6.2186 | 0 | 21.2026 | 0
11520 | 876.9566 | 2.7801 | 20.1506 | 86.9849 | -9.6351 | 9.5003 | 79.1375 | 4.4849 |  | 13.0101 | 36.8622 | 8.5983 |  | 53.0028 | 134.1878 | 10.8203 | 27.2872 | 2.7867 | 132 | 30.4325 | 0 | 97.9486 | 0
11521 | 882.0091 | 2.6874 | 20.1824 | 87.076 | -10.6345 | 10.4497 | 74.8941 | 4.85 |  | 12.3934 | 38.4858 | 8.4718 |  | 51.062 | 129.9189 | 10.8763 | 27.2356 | 3.1344 | 129 | 30.4531 | 0 | 96.4679 | 0
11522 | 872.7289 | 2.5742 | 20.1868 | 86.9037 | -10.6369 | 10.45 | 67.1883 | 5.228 |  | 12.3691 | 40.1317 | 8.3762 |  | 50.3732 | 132.0251 | 10.8457 | 27.0585 | 3.1305 | 125 | 29.6404 | 0 | 98.2581 | 0
11523 | 862.1671 | 2.4969 | 20.1774 | 86.4937 | -10.638 | 10.45 | 72.456 | 5.1781 |  | 12.7818 | 40.2589 | 8.6196 |  | 50.1044 | 131.1101 | 10.5514 | 26.9258 | 3.207 | 120 | 29.9216 | 0 | 97.7155 | 0
11524 | 862.4407 | 3.0973 | 20.0973 | 86.4548 | -9.6458 | 9.5003 | 77.3499 | 5.046 |  | 12.8805 | 38.7434 | 8.4686 |  | 50.5859 | 127.2201 | 10.6339 | 28.0551 | 3.0507 | 117 | 30.1255 | 0 | 110.1326 | 0
11525 | 883.1496 | 4.6183 | 28.3599 | 85.7786 | -10.6448 | 10.4497 | 76.2077 | 4.9418 |  | 17.4617 | 37.7992 | 8.1696 |  | 56.5148 | 126.6754 | 10.585 | 28.6802 | 2.6936 | 115 | 30.1427 | 0 | 121.6043 | 0
11526 | 930.8449 | 12.2532 | 44.0051 | 91.1255 | -16.645 | 16.1484 | 90.4935 | 4.6248 |  | 25.7948 | 41.9666 | 12.9272 |  | 84.3318 | 131.1539 | 14.1727 | 27.4792 | 2.6872 | 182 | 39.5313 | 0 | 128.4643 | 0.17494
11527 | 983.5204 | 19.0656 | 70.7705 | 96.3977 | -20.6481 | 19.9489 | 114.1162 | 5.5761 |  | 32.5213 | 60.5199 | 24.5312 |  | 120.2071 | 175.1097 | 27.168 | 29.6648 | 5.6238 | 274 | 58.3943 | 0 | 144.5416 | 0.27222
11528 | 1075.0364 | 18.3633 | 91.3237 | 106.855 | -21.6457 | 20.8997 | 126.4517 | 6.5266 |  | 36.9056 | 82.4535 | 30.7072 |  | 150.4258 | 247.8064 | 35.7216 | 33.8679 | 12.0228 | 312 | 73.0328 | 0 | 176.0604 | 0.32368
11529 | 1170.6568 | 15.0866 | 101.2633 | 121.3031 | -18.6523 | 18.0508 | 141.2341 | 6.1777 |  | 39.0588 | 92.5996 | 34.3876 |  | 173.3931 | 290.5644 | 40.2128 | 45.8166 | 15.9951 | 368 | 73.6977 | 0 | 196.6781 | 0.33291
11530 | 1223.6537 | 14.4275 | 102.9906 | 129.6093 | -18.6498 | 18.05 | 156.7888 | 6.2994 |  | 39.7741 | 96.4819 | 38.0924 |  | 182.9198 | 300.5261 | 43.0172 | 53.8517 | 17.1661 | 349 | 76.1877 | 0 | 206.6804 | 0.30661
11531 | 1241.1953 | 15.1741 | 105.034 | 131.9717 | -20.6467 | 19.9495 | 155.771 | 6.8364 |  | 43.6932 | 96.902 | 37.7566 |  | 189.4119 | 309.6172 | 42.2302 | 54.5029 | 17.6853 | 327 | 84.3373 | 0 | 207.3882 | 0.29212
11532 | 1236.4242 | 17.3168 | 106.4639 | 130.965 | -19.6524 | 19.0003 | 153.3522 | 5.8478 |  | 46.7193 | 95.2264 | 36.6827 |  | 190.7604 | 310.3025 | 41.9678 | 52.6525 | 17.964 | 362 | 66.0999 | 0 | 202.8876 | 0.29949
11533 | 1225.7127 | 15.132 | 106.8491 | 137.9645 | -21.6515 | 20.8995 | 159.8448 | 5.8893 |  | 47.0864 | 95.9443 | 37.9318 |  | 192.5177 | 305.3424 | 42.9214 | 51.88 | 18.2275 | 312 | 70.2591 | 0 | 199.1149 | 0.30442
11534 | 1218.2654 | 8.5046 | 105.4422 | 139.1337 | -23.6556 | 22.7995 | 162.7414 | 7.049 |  | 44.2454 | 97.2095 | 38.737 |  | 195.1085 | 311.8908 | 43.0509 | 52.8501 | 18.1367 | 263 | 72.4092 | 0 | 198.6988 | 0.29751
11535 | 1204.7689 | 5.5878 | 104.7342 | 137.4914 | -21.6523 | 20.9005 | 154.8924 | 6.8829 |  | 38.2657 | 96.9172 | 38.0646 |  | 188.7764 | 308.1168 | 40.6631 | 50.1677 | 17.7797 | 280 | 75.7295 | 0 | 201.766 | 0.26303
11536 | 1156.0043 | 6.196 | 102.2469 | 133.9779 | -13.6465 | 13.3021 | 145.0021 | 6.2063 |  | 40.6308 | 96.5027 | 36.3539 |  | 174.1518 | 274.2547 | 34.0013 | 43.7433 | 17.6903 | 250 | 61.7272 | 0 | 182.9189 | 0.19559
11537 | 1091.3822 | 8.0651 | 95.739 | 119.96 | -12.649 | 12.3537 | 139.0161 | 5.7914 |  | 40.4879 | 87.1148 | 34.4731 |  | 140.8102 | 229.1283 | 24.0693 | 45.7948 | 17.3369 | 211 | 56.9966 | 0 | 138.1698 | 0.15216
11538 | 1028.0508 | 9.147 | 90.2365 | 106.8042 | -11.6362 | 11.3968 | 127.4591 | 4.8636 |  | 31.3514 | 72.0033 | 30.8411 |  | 102.8616 | 190.882 | 13.4095 | 45.8499 | 13.8392 | 211 | 53.6944 | 0 | 123.9752 | 0.05817
11539 | 985.5069 | 10.3168 | 78.3772 | 100.6763 | -10.6377 | 10.4503 | 107.6011 | 4.355 |  | 21.1622 | 54.3921 | 24.3353 |  | 84.2338 | 161.7293 | 9.6503 | 34.269 | 7.881 | 193 | 56.592 | 0 | 97.5099 | 0.014639
11540 | 949.7745 | 8.0488 | 41.6243 | 94.5149 | -10.6372 | 10.45 | 102.5126 | 4.5678 |  | 15.5399 | 58.2983 | 19.439 |  | 79.392 | 144.7511 | 10.3846 | 28.0414 | 5.0999 | 177 | 49.5606 | 0 | 97.8174 | 0
11541 | 920.1384 | 8.2822 | 22.1344 | 94.9124 | -10.632 | 10.45 | 98.274 | 5.0931 |  | 13.7152 | 51.3889 | 12.6956 |  | 73.0181 | 139.3971 | 10.1558 | 28.0321 | 4.98 | 158 | 43.973 | 0 | 99.9832 | 0
11542 | 903.7315 | 8.061 | 21.5798 | 95.8857 | -10.6358 | 10.45 | 91.5497 | 5.3537 |  | 12.6861 | 43.0325 | 8.8712 |  | 64.7351 | 135.967 | 9.7547 | 27.8301 | 4.6428 | 140 | 41.3548 | 0 | 101.4486 | 0
11543 | 366.3268 | 2.6979 | 8.2882 | 35.8259 | 0.17427 | 0.002903 | 37.1664 | 2.2645 |  | 5.2068 | 17.1999 | 3.7921 |  | 23.9424 | 57.8738 | 3.7269 | 10.5301 | 1.8899 | 145 | 7.9938 | 0 | 20.7538 | 0
11544 | 876.5636 | 3.7501 | 21.5065 | 94.1081 | -12.6357 | 12.3495 | 86.5373 | 5.5707 |  | 12.1119 | 38.0965 | 8.5099 |  | 57.2634 | 131.7571 | 9.53 | 27.5656 | 3.8545 | 130 | 33.3523 | 0 | 96.152 | 0
11545 | 881.9942 | 3.3441 | 21.7283 | 94.1521 | -10.6354 | 10.4505 | 76.2068 | 5.7118 |  | 12.219 | 37.991 | 8.6532 |  | 56.0037 | 128.721 | 9.6206 | 27.5101 | 3.2516 | 118 | 32.8532 | 0 | 99.4956 | 0
11546 | 872.9896 | 2.8301 | 22.1755 | 93.8753 | -10.6319 | 10.45 | 71.2176 | 5.5269 |  | 12.2908 | 37.9478 | 8.5676 |  | 55.3749 | 124.732 | 9.668 | 27.2551 | 3.0142 | 116 | 31.8966 | 0 | 100.3845 | 0
11547 | 866.9006 | 2.5743 | 22.4843 | 93.6706 | -10.635 | 10.45 | 76.9021 | 5.3061 |  | 12.2047 | 37.9822 | 8.3322 |  | 54.4276 | 123.3147 | 9.6257 | 27.2605 | 2.7936 | 113 | 32.1873 | 0 | 101.5928 | 0
11548 | 862.1905 | 3.1216 | 22.5333 | 93.4522 | -10.6354 | 10.45 | 72.4495 | 5.5596 |  | 11.8837 | 37.6919 | 8.266 |  | 53.6712 | 123.8506 | 9.2723 | 28.1574 | 2.6751 | 109 | 32.6758 | 0 | 110.8718 | 0
11549 | 878.3867 | 4.2806 | 30.8521 | 91.3526 | -10.6379 | 10.4529 | 72.2602 | 5.2306 |  | 16.0566 | 37.6877 | 7.9021 |  | 55.7094 | 121.4682 | 9.1532 | 28.7175 | 2.642 | 109 | 32.0165 | 0 | 125.0128 | 0
11550 | 931.9115 | 5.5654 | 48.5796 | 94.1897 | -20.6337 | 19.9445 | 91.5738 | 4.9429 |  | 25.943 | 42.7217 | 15.6062 |  | 83.2462 | 126.1134 | 12.8146 | 27.4163 | 2.5952 | 195 | 37.0631 | 0 | 134.6593 | 0.02819
11551 | 996.569 | 5.8077 | 75.1122 | 98.0928 | -23.6418 | 22.7992 | 108.9926 | 5.7821 |  | 37.1085 | 62.3271 | 27.0243 |  | 115.2571 | 166.8741 | 25.0286 | 29.1057 | 5.3309 | 278 | 51.0839 | 0 | 147.4537 | 0.05791
11552 | 1066.3865 | 7.1655 | 94.4764 | 108.1291 | -24.6514 | 23.7497 | 120.8143 | 6.9082 |  | 47.9573 | 82.1305 | 31.4861 |  | 139.1522 | 228.2164 | 34.4972 | 32.9065 | 11.3025 | 297 | 61.9322 | 0 | 173.2311 | 0.069347
11553 | 1163.6597 | 10.6733 | 103.1502 | 119.5278 | -22.6525 | 21.8505 | 139.6601 | 6.621 |  | 51.9685 | 92.1848 | 32.0956 |  | 159.7463 | 274.2208 | 37.5873 | 36.7861 | 15.3878 | 378 | 61.3805 | 0 | 193.567 | 0.085453
11554 | 1225.4524 | 12.751 | 103.7443 | 126.4955 | -23.6483 | 22.7997 | 150.6344 | 6.1994 |  | 53.1883 | 95.2137 | 32.6561 |  | 174.2534 | 299.3599 | 39.2583 | 39.3027 | 16.5985 | 346 | 60.5134 | 0 | 196.1566 | 0.12064
11555 | 1223.9226 | 12.5429 | 104.6357 | 129.0532 | -22.6486 | 21.8503 | 152.2329 | 5.7463 |  | 52.7736 | 93.4909 | 31.9553 |  | 186.31 | 304.0324 | 39.4402 | 39.901 | 16.341 | 341 | 66.0589 | 0 | 198.6398 | 0.1252
11556 | 1200.5004 | 12.2704 | 104.5142 | 127.3485 | -23.6418 | 22.7997 | 148.5334 | 5.6549 |  | 49.2994 | 92.8942 | 33.5838 |  | 187.929 | 299.7541 | 38.4759 | 39.1367 | 16.2548 | 355 | 54.0735 | 0 | 203.3762 | 0.11534
11557 | 1205.358 | 9.5143 | 106.5235 | 126.4118 | -23.6449 | 22.8 | 149.6705 | 6.0262 |  | 49.7396 | 94.8109 | 35.781 |  | 183.3175 | 297.8852 | 38.8204 | 39.3043 | 16.7842 | 346 | 55.5356 | 0 | 206.3637 | 0.12639
11558 | 1186.1666 | 6.108 | 109.8603 | 127.3952 | -24.6488 | 23.7497 | 158.9863 | 6.0907 |  | 50.188 | 96.8048 | 35.7435 |  | 184.8354 | 307.4752 | 38.8505 | 39.4254 | 17.1774 | 310 | 57.4145 | 0 | 200.0102 | 0.11797
11559 | 1169.5257 | 7.2288 | 111.613 | 127.2247 | -23.6476 | 22.8003 | 159.3521 | 5.4926 |  | 46.9011 | 95.7277 | 35.8847 |  | 186.6159 | 307.7346 | 38.5011 | 39.3016 | 17.3904 | 274 | 58.286 | 0 | 192.435 | 0.090554
11560 | 1135.2187 | 6.8156 | 107.7993 | 122.5126 | -17.6459 | 17.1016 | 149.5382 | 4.6937 |  | 40.7564 | 93.3373 | 34.7431 |  | 174.4237 | 271.5445 | 36.84 | 38.0722 | 17.4507 | 241 | 52.8184 | 0 | 178.1849 | 0.091425
11561 | 1099.7585 | 4.9944 | 103.2126 | 109.0399 | -15.6429 | 15.2005 | 138.6275 | 3.5639 |  | 33.3642 | 85.8183 | 33.2094 |  | 129.9273 | 223.6759 | 28.7753 | 34.7275 | 16.5522 | 223 | 47.6511 | 0 | 141.5681 | 0.058171
11562 | 1054.3611 | 4.5159 | 97.7617 | 96.5193 | -14.643 | 14.2503 | 124.0805 | 4.1467 |  | 25.4913 | 72.6674 | 25.8002 |  | 81.5533 | 189.3234 | 26.1965 | 31.9042 | 13.3939 | 218 | -22.1391 | 0 | 123.2335 | 0.027191
11563 | 1004.5793 | 4.9272 | 78.6826 | 91.2743 | -14.6388 | 14.25 | 110.3008 | 4.9273 |  | 20.3349 | 64.9281 | 12.2711 |  | 65.9303 | 171.961 | 23.6724 | 29.3718 | 8.3997 | 186 | 47.6194 | 0 | 117.6764 | 0.011351
11564 | 981.6002 | 5.6 | 41.0344 | 87.6467 | -17.6375 | 17.0992 | 103.6615 | 4.4716 |  | 17.3625 | 59.3322 | 6.2024 |  | 64.7397 | 160.5046 | 15.5012 | 27.6322 | 6.0006 | 185 | 44.324 | 0 | 114.9449 | 0
11565 | 973.6946 | 5.2129 | 20.6242 | 88.3052 | -13.6385 | 13.3011 | 101.8969 | 4.6363 |  | 17.0823 | 51.356 | 7.0868 |  | 58.6257 | 144.7659 | 10.8651 | 27.3214 | 6.0477 | 180 | 43.068 | 0 | 113.9461 | 0
11566 | 957.0998 | 4.3696 | 17.4093 | 88.9787 | -12.6381 | 12.3503 | 95.1153 | 4.9342 |  | 17.9352 | 41.2978 | 7.3226 |  | 51.5822 | 132.8906 | 10.0154 | 27.1899 | 5.7357 | 159 | 38.8383 | 0 | 110.5201 | 0
11567 | 384.1686 | 1.7865 | 6.4634 | 33.0987 | 0.173 | 0.003431 | 37.1458 | 2.0894 |  | 7.6115 | 16.0173 | 2.956 |  | 18.9948 | 56.003 | 3.7845 | 10.2508 | 2.3381 | 157 | 7.3288 | 0 | 22.379 | 0
11568 | 920.1854 | 2.5004 | 16.8993 | 89.0524 | -10.6355 | 10.45 | 87.976 | 5.3423 |  | 14.3498 | 36.4357 | 7.1689 |  | 46.2642 | 128.2873 | 9.8492 | 27.3198 | 4.3959 | 140 | 33.765 | 0 | 106.8683 | 0
11569 | 911.5666 | 2.5153 | 16.9197 | 88.5152 | -10.6352 | 10.45 | 72.6833 | 6.0808 |  | 13.9071 | 36.5155 | 6.9982 |  | 43.7697 | 131.5207 | 9.8397 | 27.2056 | 3.7844 | 129 | 31.5646 | 0 | 105.2183 | 0
11570 | 892.8429 | 2.6302 | 17.127 | 87.7028 | -10.6342 | 10.45 | 64.0043 | 6.4595 |  | 13.1246 | 36.6755 | 6.8523 |  | 42.1533 | 131.0308 | 10.015 | 27.0719 | 3.2986 | 128 | 32.3234 | 0 | 107.2888 | 0
11571 | 884.0959 | 2.5882 | 17.0751 | 86.9999 | -11.6299 | 11.3997 | 69.0103 | 6.6411 |  | 12.5879 | 36.7098 | 6.6841 |  | 42.3255 | 127.7755 | 10.0365 | 26.9685 | 3.2958 | 117 | 32.0634 | 0 | 109.8123 | 0
11572 | 872.1766 | 3.0612 | 17.0661 | 87.7749 | -10.6347 | 10.4503 | 69.1336 | 6.8268 |  | 12.3215 | 36.2556 | 6.4469 |  | 42.7116 | 123.446 | 9.9683 | 28.1784 | 3.1925 | 119 | 30.8636 | 0 | 118.8422 | 0
11573 | 886.8474 | 4.5629 | 26.2107 | 85.9353 | -10.6375 | 10.45 | 69.0564 | 5.8498 |  | 15.2864 | 35.7365 | 5.7552 |  | 47.2311 | 122.9191 | 9.3797 | 28.8061 | 2.7939 | 116 | 30.6692 | 0 | 131.2021 | 0
11574 | 914.4674 | 7.7541 | 41.2546 | 90.3508 | -11.6398 | 11.3997 | 85.5895 | 5.4845 |  | 25.0794 | 41.1222 | 11.305 |  | 78.7961 | 135.4229 | 13.1653 | 27.132 | 2.6274 | 176 | 37.6148 | 0 | 142.6435 | 0.1188
11575 | 978.9554 | 16.0554 | 70.9518 | 95.2079 | -16.6479 | 16.1487 | 109.0807 | 5.9235 |  | 37.0635 | 64.2372 | 27.8671 |  | 118.9999 | 180.5499 | 25.8371 | 28.8463 | 5.4401 | 276 | 53.6739 | 0 | 147.3575 | 0.21634
11576 | 1069.9397 | 22.8789 | 91.7205 | 107.0379 | -16.6508 | 16.15 | 127.9321 | 6.9525 |  | 44.0421 | 86.7696 | 36.1487 |  | 145.983 | 232.4552 | 35.0349 | 32.9263 | 11.4663 | 317 | 66.1339 | 0 | 163.8967 | 0.29004
11577 | 1132.8352 | 22.3227 | 98.7962 | 120.7476 | -18.646 | 18.0495 | 147.5799 | 7.0506 |  | 48.284 | 95.8244 | 35.138 |  | 164.9108 | 273.2975 | 39.0117 | 38.5455 | 14.9085 | 367 | 68.269 | 0 | 179.296 | 0.32604
11578 | 1183.2377 | 17.5049 | 100.2512 | 127.7774 | -19.6454 | 18.9997 | 156.7068 | 6.6232 |  | 51.8813 | 97.8619 | 36.8462 |  | 177.9267 | 296.2656 | 40.1178 | 46.1713 | 15.7827 | 370 | 63.2557 | 0 | 190.323 | 0.32225
11579 | 1223.9085 | 14.2856 | 103.1491 | 129.0429 | -19.6471 | 19 | 160.0153 | 5.3476 |  | 52.7829 | 97.06 | 37.9517 |  | 184.1638 | 301.4359 | 40.9045 | 49.2905 | 16.0036 | 340 | 63.7784 | 0.10036 | 203.4873 | 0.31442
11580 | 1221.245 | 12.6383 | 106.3835 | 130.4267 | -19.647 | 19 | 163.31 | 5.6184 |  | 47.7335 | 96.2901 | 37.1985 |  | 183.3718 | 297.3399 | 40.8862 | 49.2258 | 16.1253 | 339 | 54.8643 | 0.48606 | 215.2068 | 0.31393
11581 | 1229.8427 | 11.729 | 107.3942 | 134.2484 | -17.6482 | 17.1005 | 165.866 | 5.333 |  | 46.2445 | 97.1323 | 36.2649 |  | 186.8082 | 296.286 | 38.8172 | 50.0504 | 16.846 | 322 | 54.5117 | 0.71367 | 209.9661 | 0.33607
11582 | 1251.1822 | 11.3309 | 106.3723 | 138.0986 | -19.6485 | 18.9995 | 167.0523 | 5.9048 |  | 46.2007 | 99.4251 | 33.4707 |  | 185.8413 | 292.9364 | 38.4999 | 50.7477 | 17.2179 | 296 | 57.1591 | 0.74209 | 208.4305 | 0.32618
11583 | 1198.1254 | 8.5125 | 106.6084 | 133.0945 | -18.6495 | 18.0503 | 149.7542 | 5.4284 |  | 46.6046 | 102.7654 | 31.9593 |  | 177.4102 | 285.0322 | 38.3424 | 49.5265 | 17.3494 | 262 | 55.2918 | 0.74199 | 199.3182 | 0.24909
11584 | 1154.3183 | 11.7771 | 99.7375 | 127.3062 | -13.6454 | 13.3013 | 138.2739 | 6.155 |  | 47.3029 | 100.9674 | 27.412 |  | 165.7418 | 255.167 | 31.4922 | 49.4663 | 17.2643 | 245 | 53.0195 | 0.74135 | 186.3175 | 0.13646
11585 | 1112.9292 | 12.667 | 93.6842 | 109.6809 | -13.6419 | 13.3 | 137.5221 | 3.8756 |  | 41.4021 | 89.5705 | 26.0355 |  | 124.9979 | 211.0504 | 16.8276 | 47.2067 | 16.4443 | 240 | 43.4883 | 0.75216 | 130.3984 | 0.08124
11586 | 1060.2319 | 12.3328 | 87.9991 | 93.3487 | -11.6384 | 11.4005 | 132.4279 | 3.5843 |  | 32.8338 | 72.025 | 21.2688 |  | 78.3235 | 195.4087 | 11.1459 | 44.877 | 13.0749 | 216 | 46.2087 | 0.75892 | 123.4309 | 0.072331
11587 | 1020.3003 | 13.9076 | 70.9352 | 90.3873 | -10.6369 | 10.4503 | 121.0437 | 3.6587 |  | 26.3047 | 64.2902 | 8.3074 |  | 64.3315 | 173.3893 | 9.1733 | 41.9232 | 6.8726 | 191 | 46.9497 | 0.76886 | 110.4386 | 0.053835
11588 | 991.629 | 11.898 | 33.0232 | 89.4239 | -10.6358 | 10.45 | 112.5508 | 3.7302 |  | 23.7868 | 60.8132 | 4.3539 |  | 62.0857 | 146.5783 | 8.4044 | 40.2283 | 4.0625 | 167 | 41.007 | 0.77191 | 101.3287 | 0
11589 | 951.2586 | 6.4999 | 18.9736 | 89.2109 | -10.6362 | 10.45 | 100.9709 | 3.6983 |  | 22.4663 | 52.3811 | 6.15 |  | 57.8975 | 132.4224 | 8.5868 | 40.2544 | 3.4394 | 164 | 38.6112 | 0.77608 | 102.4688 | 0
11590 | 922.3081 | 4.0128 | 17.9746 | 88.0907 | -10.6375 | 10.45 | 99.9603 | 3.3578 |  | 22.5807 | 40.8059 | 6.5321 |  | 52.2584 | 131.1115 | 8.7911 | 39.2604 | 4.4939 | 156 | 39.0375 | 0.7829 | 108.6044 | 0
11591 | 253.4284 | 1.174 | 4.6134 | 21.8 | 0.12835 | 0.002903 | 28.3334 | 0.95171 |  | 6.656 | 11.4957 | 1.8582 |  | 13.1286 | 39.7291 | 2.2362 | 9.8202 | 1.4917 | 148 | 2.8521 | 0.083618 | 8.8126 | 0
11592 | 881.0789 | 2.4489 | 17.9484 | 87.8617 | -10.6327 | 10.45 | 92.1535 | 4.1666 |  | 17.7541 | 38.1179 | 6.0573 |  | 43.437 | 128.906 | 9.5776 | 38.7854 | 4.3832 | 131 | 34.0541 | 0.78618 | 103.8121 | 0
11593 | 877.2126 | 2.5565 | 18.0545 | 87.6479 | -10.6319 | 10.45 | 91.9061 | 4.337 |  | 15.5535 | 38.4257 | 6.0882 |  | 41.5106 | 127.5913 | 9.5078 | 38.7727 | 4.4955 | 131 | 33.2057 | 0.77958 | 103.29 | 0
11594 | 869.286 | 2.8757 | 18.0677 | 87.0624 | -10.6356 | 10.45 | 80.5385 | 4.6349 |  | 14.9948 | 38.0108 | 6.2328 |  | 41.6223 | 126.7548 | 9.5289 | 38.7915 | 3.6576 | 125 | 33.1416 | 0.78545 | 104.1834 | 0
11595 | 859.7587 | 2.6655 | 17.9598 | 86.5741 | -10.6417 | 10.45 | 81.7127 | 4.5768 |  | 14.9405 | 37.1032 | 6.0418 |  | 41.5572 | 126.0669 | 9.7632 | 38.9582 | 2.7995 | 127 | 33.356 | 0.78957 | 106.4583 | 0
11596 | 856.6128 | 3.0184 | 17.7561 | 86.5774 | -10.6389 | 10.45 | 80.4759 | 4.3703 |  | 14.8365 | 36.2634 | 5.9279 |  | 41.7813 | 118.4998 | 9.634 | 39.3762 | 2.5979 | 132 | 33.485 | 0.78346 | 114.7834 | 0
11597 | 863.5217 | 5.7256 | 28.2379 | 85.1953 | -10.6373 | 10.45 | 74.652 | 3.8631 |  | 16.5902 | 36.0265 | 6.0277 |  | 46.1699 | 113.2656 | 9.5992 | 40.1905 | 2.6074 | 137 | 33.1184 | 0.78956 | 128.7323 | 0
11598 | 912.0648 | 11.8055 | 38.911 | 88.4888 | -12.6449 | 12.3495 | 91.4939 | 3.3915 |  | 24.7935 | 41.6678 | 12.4514 |  | 81.9305 | 122.6827 | 11.7478 | 38.77 | 2.4608 | 182 | 40.166 | 0.79005 | 142.8194 | 0.19795
11599 | 991.1872 | 16.6864 | 69.3659 | 93.6549 | -17.6443 | 17.0987 | 115.8273 | 4.4879 |  | 33.463 | 67.1664 | 26.5196 |  | 113.4283 | 168.6744 | 26.3143 | 40.7559 | 4.7297 | 244 | 58.3489 | 0.83072 | 146.4886 | 0.29117
11600 | 1051.4531 | 17.168 | 89.1176 | 111.793 | -16.6483 | 16.1503 | 129.2884 | 6.6642 |  | 34.8215 | 86.9748 | 34.6511 |  | 146.9379 | 238.7035 | 37.2031 | 44.8001 | 11.8127 | 305 | 68.209 | 0.85107 | 172.7048 | 0.33776
11601 | 1105.2924 | 15.3085 | 96.7205 | 126.6269 | -18.6476 | 18.0495 | 151.6868 | 7.6223 |  | 38.5391 | 93.8248 | 35.7494 |  | 170.146 | 282.7548 | 43.0114 | 47.2767 | 16.0938 | 313 | 76.0794 | 0.84168 | 202.3911 | 0.35545
11602 | 1154.6484 | 12.3121 | 102.0388 | 128.767 | -22.644 | 21.8489 | 163.3479 | 7.3128 |  | 41.2798 | 97.6751 | 37.6003 |  | 179.6298 | 308.9741 | 42.9764 | 51.6994 | 18.3704 | 377 | 73.8755 | 0.84995 | 204.6095 | 0.32473
11603 | 1173.9993 | 7.276 | 100.6543 | 134.2332 | -21.6468 | 20.9003 | 168.7431 | 7.2274 |  | 44.742 | 100.1117 | 38.8873 |  | 185.3482 | 311.4451 | 41.5069 | 49.1735 | 18.2503 | 322 | 81.9424 | 0.84971 | 206.6267 | 0.30599
11604 | 1155.6466 | 6.6734 | 100.3397 | 132.129 | -18.6454 | 18.0508 | 161.2227 | 6.6994 |  | 42.359 | 99.5614 | 39.6107 |  | 182.6122 | 307.4743 | 41.6262 | 43.4998 | 17.8307 | 335 | 76.2577 | 1.0022 | 213.9262 | 0.30963
11605 | 1167.8608 | 8.1397 | 99.0949 | 131.878 | -18.6427 | 18.05 | 168.2021 | 6.06 |  | 43.4863 | 98.844 | 35.8486 |  | 184.1283 | 302.6034 | 43.5759 | 43.1341 | 18.0262 | 328 | 76.9185 | 1.3534 | 213.7362 | 0.33206
11606 | 1167.103 | 7.9161 | 97.3258 | 132.0875 | -18.6496 | 18.05 | 168.5883 | 6.8167 |  | 46.615 | 99.9971 | 36.3183 |  | 180.9177 | 298.1246 | 42.6949 | 43.1 | 18.4626 | 314 | 74.513 | 1.3908 | 212.3848 | 0.32978
11607 | 1149.2426 | 5.5848 | 94.3538 | 127.5329 | -21.6504 | 20.8992 | 160.7847 | 6.9308 |  | 39.5579 | 99.2822 | 36.6974 |  | 172.2338 | 296.7014 | 39.6337 | 40.9032 | 18.0385 | 254 | 70.0725 | 0.64673 | 205.4969 | 0.2959
11608 | 1107.3221 | 4.5345 | 90.1835 | 116.8921 | -14.6454 | 14.2518 | 150.9542 | 6.3509 |  | 37.8736 | 95.1793 | 33.6086 |  | 159.6672 | 265.189 | 31.2139 | 39.868 | 17.6136 | 240 | 61.3247 | 0.061697 | 180.4839 | 0.27847
11609 | 1050.1948 | 4.867 | 75.1428 | 103.4843 | -11.6471 | 11.4008 | 134.8871 | 4.2469 |  | 36.3734 | 85.3589 | 30.2201 |  | 132.5002 | 202.4776 | 17.0785 | 36.8479 | 17.1484 | 218 | 50.0508 | 0 | 132.7096 | 0.26699
11610 | 976.032 | 5.6554 | 39.565 | 90.3021 | -10.641 | 10.4503 | 119.455 | 3.0912 |  | 25.0801 | 68.4234 | 28.0807 |  | 105.2953 | 167.5215 | 12.4959 | 33.0741 | 13.9441 | 207 | 45.0273 | 0 | 119.2127 | 0.24101
11611 | 943.8101 | 5.8414 | 19.3712 | 85.7389 | -10.6377 | 10.45 | 107.9756 | 3.3282 |  | 19.8389 | 55.2967 | 15.2839 |  | 76.525 | 160.9056 | 11.3398 | 30.0713 | 7.6701 | 192 | 41.0966 | 0 | 111.9951 | 0.12892
11612 | 904.4047 | 5.2015 | 16.1469 | 85.6273 | -9.6401 | 9.5003 | 94.8283 | 3.9568 |  | 18.468 | 42.1723 | 11.0141 |  | 55.0987 | 156.7065 | 10.2266 | 27.4074 | 5.1452 | 168 | 37.6861 | 0 | 104.0241 | 0
11613 | 888.929 | 4.5523 | 16.3213 | 87.1924 | -10.6396 | 10.4497 | 82.7063 | 4.3455 |  | 16.7088 | 37.249 | 10.6669 |  | 50.6462 | 143.352 | 9.4754 | 26.5872 | 4.6619 | 163 | 34.1915 | 0 | 107.673 | 0
11614 | 883.7228 | 3.7286 | 16.1546 | 86.9977 | -9.6409 | 9.5003 | 95.9366 | 4.6732 |  | 16.0457 | 36.4326 | 10.458 |  | 52.313 | 140.3268 | 9.512 | 26.5883 | 4.59 | 148 | 35.9195 | 0 | 105.5272 | 0
11615 | 255.8004 | 1.1226 | 4.3195 | 22.4697 | 0.13308 | 0.00264 | 30.1363 | 1.4728 |  | 4.8872 | 11.7026 | 3.1789 |  | 14.318 | 44.5004 | 2.5683 | 7.0301 | 1.4394 | 149 | 2.4561 | 0 | 9.2864 | 0
11616 | 858.9908 | 2.7027 | 16.2101 | 86.5413 | -10.6338 | 10.45 | 85.5896 | 4.5695 |  | 16.1983 | 35.8871 | 9.5085 |  | 42.2261 | 137.5877 | 9.541 | 26.4278 | 4.3645 | 140 | 33.9172 | 0 | 107.2256 | 0
11617 | 852.5568 | 2.4846 | 16.1722 | 86.752 | -9.6371 | 9.5003 | 73.1788 | 4.2924 |  | 16.2255 | 35.9068 | 9.1774 |  | 44.1341 | 124.4051 | 9.4527 | 26.3231 | 4.1878 | 145 | 34.9284 | 0 | 107.4004 | 0
11618 | 833.231 | 2.4891 | 16.0249 | 86.6766 | -10.6395 | 10.4497 | 77.6044 | 4.2955 |  | 15.7064 | 37.1763 | 8.8155 |  | 41.1179 | 124.084 | 9.2849 | 26.6274 | 4.1067 | 142 | 34.9452 | 0 | 105.354 | 0
11619 | 833.6642 | 2.661 | 16.1354 | 86.6613 | -10.6396 | 10.45 | 82.0752 | 4.5436 |  | 15.2883 | 37.713 | 8.787 |  | 38.9671 | 126.861 | 9.2189 | 26.4032 | 4.0907 | 127 | 32.2501 | 0 | 106.1843 | 0
11620 | 846.5341 | 3.1133 | 16.1222 | 87.2798 | -9.6376 | 9.5003 | 71.8813 | 4.712 |  | 16.0309 | 37.4332 | 8.8053 |  | 39.1094 | 123.9071 | 9.3812 | 27.0696 | 4.0915 | 117 | 31.4169 | 0 | 104.9136 | 0
11621 | 839.3224 | 4.0886 | 15.8259 | 84.6021 | -10.6309 | 10.4497 | 68.7642 | 4.4461 |  | 14.2217 | 41.0522 | 6.8952 |  | 37.936 | 116.2797 | 9.0023 | 28.0613 | 3.6273 | 116 | 31.7117 | 0 | 104.6021 | 0
11622 | 850.5028 | 3.419 | 27.8933 | 83.5797 | -10.636 | 10.45 | 76.2176 | 4.5768 |  | 12.6771 | 43.3188 | 5.804 |  | 37.3901 | 111.4878 | 8.8696 | 26.2431 | 2.7499 | 112 | 29.9098 | 0 | 105.5708 | 0.18802
11623 | 873.9305 | 2.635 | 38.644 | 83.4168 | -10.6378 | 10.45 | 72.9261 | 4.9023 |  | 12.5437 | 43.7697 | 8.6545 |  | 37.9465 | 110.4855 | 8.7409 | 25.4941 | 2.4497 | 110 | 35.0569 | 0 | 104.1692 | 0.27691
11624 | 888.4415 | 2.9769 | 45.2642 | 83.4311 | -9.6419 | 9.5003 | 78.2315 | 4.8433 |  | 18.1826 | 38.649 | 14.4403 |  | 41.5299 | 112.795 | 8.4558 | 25.4398 | 2.417 | 117 | 35.7704 | 0 | 105.525 | 0.32777
11625 | 895.916 | 3.0666 | 61.6122 | 83.6997 | -10.6443 | 10.4497 | 92.8103 | 4.453 |  | 27.7083 | 39.7713 | 16.0616 |  | 48.6003 | 120.88 | 8.1697 | 25.6776 | 4.414 | 142 | 37.7217 | 0 | 107.5969 | 0.3486
11626 | 923.3846 | 2.9728 | 72.6949 | 85.9655 | -10.6478 | 10.45 | 99.1116 | 3.6654 |  | 34.1493 | 47.5437 | 15.8876 |  | 56.1289 | 124.2536 | 7.9364 | 26.2851 | 9.7447 | 158 | 32.477 | 0 | 104.3755 | 0.31823
11627 | 920.9264 | 3.28 | 74.4769 | 86.4925 | -9.6509 | 9.5003 | 99.2778 | 2.5048 |  | 32.6265 | 60.1912 | 16.2221 |  | 64.1901 | 123.9994 | 8.0049 | 25.8117 | 11.8108 | 161 | 26.6458 | 0 | 104.5076 | 0.30404
11628 | 907.7515 | 3.0295 | 73.8659 | 85.2907 | -9.6458 | 9.5 | 104.6627 | 3.1739 |  | 33.3473 | 63.3869 | 16.2568 |  | 67.1073 | 132.4772 | 7.7812 | 25.4985 | 11.7801 | 152 | 29.7315 | 0 | 102.6101 | 0.30751
11629 | 919.9899 | 7.2882 | 68.8009 | 86.1979 | -9.6423 | 9.5 | 110.7622 | 3.4756 |  | 33.2421 | 58.3741 | 16.5976 |  | 71.6176 | 140.7505 | 7.9632 | 25.6842 | 11.9784 | 164 | 34.7013 | 0 | 103.0697 | 0.32911
11630 | 933.1392 | 10.6977 | 47.1482 | 88.4266 | -9.6468 | 9.5 | 93.5905 | 2.0534 |  | 31.7438 | 56.1037 | 19.1372 |  | 69.8269 | 144.5767 | 7.9576 | 25.8337 | 10.356 | 180 | 29.9127 | 0 | 92.9622 | 0.32672
11631 | 933.4582 | 10.1276 | 37.2775 | 89.7646 | -10.6473 | 10.4497 | 89.0877 | 2.7472 |  | 26.7201 | 56.1404 | 18.6754 |  | 62.2781 | 138.3484 | 8.076 | 26.1253 | 5.0987 | 200 | 22.4144 | 0 | 91.0978 | 0.29301
11632 | 934.4426 | 7.2331 | 36.1978 | 87.0631 | -9.6452 | 9.5003 | 97.1349 | 2.1687 |  | 16.0133 | 55.7311 | 13.7536 |  | 59.2347 | 143.6741 | 8.0111 | 25.796 | 3.2597 | 193 | 21.2887 | 0 | 93.6653 | 0.27098
11633 | 930.2956 | 4.1048 | 36.1676 | 87.0276 | -8.6422 | 8.5503 | 92.2996 | 1.5014 |  | 12.2854 | 53.9896 | 13.6775 |  | 52.6516 | 149.4385 | 7.8798 | 25.7291 | 3.3193 | 204 | 25.2256 | 0 | 94.6594 | 0.25103
11634 | 907.4913 | 2.815 | 36.1705 | 91.0802 | -9.6423 | 9.4997 | 94.4715 | 2.952 |  | 12.2568 | 48.1334 | 18.1911 |  | 48.1628 | 143.8381 | 7.8632 | 25.8405 | 2.9179 | 197 | 32.1063 | 0 | 92.137 | 0.22258
11635 | 901.873 | 4.1275 | 33.8859 | 91.7298 | -10.6442 | 10.4497 | 103.6641 | 3.4051 |  | 12.186 | 45.7514 | 13.5349 |  | 47.7265 | 139.8085 | 7.9411 | 25.405 | 2.873 | 198 | 33.8202 | 0 | 95.3711 | 0.13924
11636 | 888.2726 | 7.2965 | 30.8702 | 88.9457 | -9.6433 | 9.5003 | 100.8966 | 3.7375 |  | 12.2468 | 38.1662 | 10.2543 |  | 42.5133 | 133.2869 | 8.121 | 25.3055 | 3.6318 | 203 | 34.8205 | 0 | 95.0474 | 0
11637 | 878.0689 | 6.289 | 30.457 | 88.9998 | -9.6415 | 9.5 | 97.893 | 4.4294 |  | 13.8284 | 35.5304 | 11.8368 |  | 43.8693 | 131.9664 | 8.2675 | 26.0832 | 4.6404 | 184 | 34.8359 | 0 | 103.0294 | 0
11638 | 875.5718 | 4.3138 | 30.8694 | 88.0342 | -10.6405 | 10.4497 | 101.1566 | 4.7046 |  | 15.0277 | 36.0801 | 12.997 |  | 44.004 | 129.9934 | 8.8008 | 26.2133 | 5.0256 | 168 | 32.8554 | 0 | 105.2623 | 0
11639 | 249.2485 | 1.2643 | 8.105 | 22.023 | 0.13128 | 0.002903 | 29.6228 | 1.4327 |  | 4.582 | 11.5753 | 3.9118 |  | 11.511 | 39.9243 | 2.3274 | 6.732 | 1.549 | 140 | 2.2842 | 0 | 8.9308 | 0
11640 | 887.6301 | 10.9344 | 31.0429 | 89.5555 | -10.6406 | 10.4497 | 97.4827 | 4.6756 |  | 15.2479 | 35.8491 | 12.9635 |  | 37.875 | 125.3132 | 9.2984 | 26.0735 | 4.5227 | 141 | 32.0789 | 0 | 97.6743 | 0
11641 | 889.2835 | 11.0804 | 31.2491 | 88.7469 | -10.6345 | 10.45 | 75.7942 | 4.5937 |  | 15.2361 | 36.1686 | 12.8608 |  | 36.6817 | 118.8585 | 9.285 | 26.0215 | 4.0153 | 123 | 33.9356 | 0 | 98.0985 | 0
11642 | 875.0745 | 5.4048 | 31.2239 | 87.9929 | -17.6319 | 17.0982 | 71.3787 | 4.8883 |  | 15.2563 | 35.943 | 12.9232 |  | 35.857 | 122.4315 | 9.4314 | 26.0258 | 3.0947 | 113 | 31.3933 | 0 | 101.0121 | 0
11643 | 854.3636 | 2.6316 | 31.22 | 88.0736 | -17.6358 | 17.1 | 74.7858 | 5.3064 |  | 15.2644 | 35.8683 | 12.7746 |  | 36.1058 | 123.2902 | 9.0995 | 26.166 | 2.7305 | 110 | 30.4399 | 0 | 102.9154 | 0
11644 | 857.3582 | 3.035 | 31.1112 | 86.749 | -14.6403 | 14.2547 | 67.5493 | 5.1307 |  | 15.0113 | 35.8764 | 13.0565 |  | 36.7599 | 118.5451 | 9.1964 | 27.0137 | 2.6841 | 107 | 32.2604 | 0 | 105.6377 | 0
11645 | 852.7643 | 3.846 | 30.5589 | 84.4303 | -10.6382 | 10.4471 | 65.3676 | 5.1956 |  | 13.2798 | 34.5761 | 10.869 |  | 35.8803 | 115.1739 | 8.8758 | 27.7187 | 2.5175 | 107 | 41.285 | 0 | 101.5908 | 0
11646 | 854.2193 | 2.8119 | 30.0287 | 85.445 | -10.6405 | 10.45 | 75.6011 | 5.348 |  | 12.4583 | 34.3052 | 10.0129 |  | 35.7448 | 110.258 | 8.8152 | 25.9389 | 2.4399 | 110 | 30.6543 | 0 | 102.8222 | 0.14929
11647 | 865.6421 | 2.3287 | 28.6642 | 86.0894 | -9.6404 | 9.5003 | 73.1829 | 4.5924 |  | 12.4808 | 34.6971 | 10.5205 |  | 36.1559 | 109.6374 | 8.5445 | 25.2582 | 2.4747 | 117 | 26.658 | 0 | 100.9161 | 0.2244
11648 | 874.5604 | 3.5359 | 28.3166 | 85.6023 | -10.6422 | 10.4497 | 76.3065 | 3.6975 |  | 16.6318 | 35.1718 | 10.7919 |  | 40.1306 | 114.1085 | 7.9395 | 25.2967 | 2.4888 | 118 | 26.1602 | 0 | 100.4394 | 0.28322
11649 | 903.5868 | 3.2987 | 25.3669 | 84.3414 | -9.6418 | 9.5003 | 97.4561 | 2.7237 |  | 26.8076 | 40.2137 | 10.3196 |  | 42.9746 | 133.9372 | 7.9883 | 25.4892 | 2.5573 | 121 | 20.0949 | 0 | 99.1283 | 0.26648
11650 | 919.0341 | 3.9036 | 17.5007 | 84.056 | -9.6419 | 9.5 | 106.0813 | 3.0636 |  | 31.5564 | 43.2264 | 10.1727 |  | 45.8063 | 146.8341 | 8.0181 | 25.4018 | 2.5701 | 131 | 12.475 | 0 | 97.3905 | 0.22319
11651 | 928.5184 | 3.7641 | 15.0546 | 85.1417 | -9.6454 | 9.5 | 106.0526 | 3.1916 |  | 32.2504 | 46.7597 | 10.2334 |  | 47.8315 | 142.6753 | 8.0661 | 25.7079 | 2.7676 | 147 | 9.8651 | 0 | 100.8006 | 0.1147
11652 | 915.5802 | 4.3329 | 14.9323 | 86.598 | -9.6435 | 9.5 | 89.8747 | 1.9743 |  | 31.8307 | 54.7182 | 10.143 |  | 47.9513 | 138.5204 | 8.0162 | 25.2118 | 2.7723 | 159 | 14.0391 | 0 | 96.6346 | 0.1216
11653 | 904.0981 | 6.8128 | 14.9392 | 85.7702 | -9.6433 | 9.5 | 89.6536 | 2.6336 |  | 33.5822 | 69.242 | 10.3089 |  | 51.3498 | 137.9527 | 7.8824 | 25.4662 | 2.9538 | 151 | 15.8649 | 0 | 85.1617 | 0.11589
11654 | 905.7479 | 11.2997 | 14.9104 | 84.6608 | -8.6421 | 8.5503 | 94.8263 | 3.1129 |  | 31.0769 | 69.8684 | 10.8417 |  | 54.133 | 141.4668 | 7.8953 | 25.9787 | 3.149 | 150 | 17.32 | 0 | 81.4915 | 0.30169
11655 | 913.7879 | 13.0951 | 14.8539 | 85.6303 | -9.6408 | 9.4997 | 93.2177 | 2.3137 |  | 27.2502 | 61.1056 | 12.5887 |  | 53.6342 | 141.9979 | 8.146 | 25.6899 | 3.5171 | 148 | 22.9674 | 0 | 86.0435 | 0.23447
11656 | 915.4468 | 12.8362 | 15.0165 | 87.4097 | -8.6437 | 8.5503 | 90.7665 | 3.8989 |  | 16.8672 | 61.0524 | 11.6373 |  | 49.4644 | 144.3392 | 8.048 | 25.2757 | 3.6308 | 149 | 21.0705 | 0 | 79.674 | 0.26401
11657 | 913.5753 | 9.9408 | 14.7256 | 89.6901 | -9.6387 | 9.4997 | 86.6606 | 3.1982 |  | 13.0498 | 64.8645 | 12.6896 |  | 49.3754 | 142.21 | 8.1116 | 25.732 | 3.5257 | 151 | 25.712 | 0 | 87.2095 | 0.11619
11658 | 897.2302 | 6.432 | 14.7115 | 90.1392 | -8.6391 | 8.5503 | 90.8759 | 2.6553 |  | 13.0108 | 48.2603 | 11.6007 |  | 47.2694 | 131.612 | 7.8652 | 25.6976 | 3.5363 | 156 | 28.436 | 0 | 86.48 | 0.14015
11659 | 879.8931 | 5.5759 | 15.2086 | 87.8083 | -9.642 | 9.4997 | 82.2467 | 3.611 |  | 12.8707 | 35.9517 | 10.839 |  | 44.1151 | 130.6678 | 8.0318 | 25.5615 | 3.5337 | 171 | 33.4045 | 0 | 87.6718 | 0.09902
11660 | 854.1657 | 6.2855 | 15.2454 | 88.3473 | -9.6413 | 9.5 | 80.5874 | 4.08 |  | 12.9873 | 34.0432 | 11.2386 |  | 44.2314 | 131.6102 | 8.0287 | 25.4674 | 3.7935 | 204 | 35.761 | 0 | 97.1841 | 0.0027042
11661 | 846.7467 | 6.5534 | 15.8214 | 89.7525 | -9.6428 | 9.5 | 98.9154 | 0 |  | 14.992 | 34.4269 | 12.8474 |  | 44.8846 | 138.8524 | 8.5046 | 25.6253 | 4.011 | 201 | 37.2814 | 0 | 98.0318 | 0
11662 | 852.8167 | 5.0598 | 15.9054 | 89.8539 | -10.6394 | 10.4497 | 109.1903 | 4.4335 |  | 15.7804 | 34.6084 | 13.6822 |  | 42.9146 | 139.3111 | 9.1993 | 25.9734 | 4.1505 | 186 | 38.1052 | 0 | 102.7242 | 0
11663 | 248.7138 | 0 | 4.2734 | 23.3657 | 0.13502 | 0.002903 | 32.5902 | 1.4134 |  | 4.8301 | 11.2735 | 4.1837 |  | 11.4581 | 43.7193 | 2.5112 | 6.9037 | 1.3113 | 194 | 2.7604 | 0 | 9.0481 | 0
11664 | 837.3509 | 3.2042 | 15.9391 | 87.6122 | -10.6384 | 10.4497 | 81.2683 | 4.9466 |  | 15.5774 | 35.1143 | 12.896 |  | 44.5333 | 139.7029 | 9.1762 | 24.2985 | 3.5968 | 184 | 38.8141 | 0 | 104.2361 | 0
11665 | 843.236 | 3.0903 | 15.9433 | 87.9934 | -10.6354 | 10.45 | 71.3415 | 5.4051 |  | 15.59 | 34.9728 | 12.7789 |  | 47.4586 | 138.7916 | 9.2894 | 24.0215 | 3.6038 | 181 | 40.2408 | 0 | 104.5147 | 0
11666 | 825.6776 | 2.6428 | 15.9652 | 89.0369 | -9.6348 | 9.5003 | 74.4783 | 5.2756 |  | 15.6373 | 35.245 | 13.2361 |  | 48.604 | 138.59 | 9.3982 | 23.9817 | 3.7267 | 188 | 37.8979 | 0 | 103.5538 | 0
11667 | 816.814 | 3.0073 | 16.9054 | 89.4511 | -10.6397 | 10.4497 | 70.8152 | 4.7596 |  | 15.4049 | 35.4522 | 13.5349 |  | 51.6286 | 131.6688 | 9.2969 | 24.15 | 3.551 | 182 | 39.1147 | 0 | 111.9394 | 0
11668 | 830.4461 | 3.431 | 18.3523 | 88.206 | -10.6358 | 10.45 | 64.6029 | 4.6985 |  | 15.2511 | 34.7778 | 12.8917 |  | 50.0118 | 122.8167 | 9.1524 | 24.1084 | 3.2852 | 152 | 41.0614 | 0 | 127.5309 | 0
11669 | 819.3041 | 4.1006 | 16.4866 | 85.6053 | -9.6344 | 9.5003 | 71.8828 | 4.368 |  | 17.8745 | 33.2989 | 10.691 |  | 47.4487 | 116.6781 | 8.8275 | 24.6455 | 2.682 | 144 | 42.7009 | 0 | 126.741 | 0
11670 | 830.2088 | 2.9242 | 15.5967 | 85.1991 | -10.6345 | 10.4497 | 76.1184 | 3.9498 |  | 25.1094 | 36.2568 | 10.4348 |  | 69.5757 | 121.5675 | 8.9133 | 23.832 | 2.4085 | 151 | 36.4802 | 0 | 121.5661 | 0.18151
11671 | 817.8171 | 2.8885 | 24.1341 | 85.1965 | -13.403 | 13.2992 | 76.7061 | 4.1626 |  | 25.7141 | 44.8684 | 10.3069 |  | 77.4978 | 140.2896 | 8.4978 | 23.3584 | 6.3236 | 154 | 36.4857 | 0 | 118.9033 | 0.28143
11672 | 830.2829 | 2.7153 | 28.5782 | 85.0787 | -15.508 | 15.1995 | 79.3805 | 3.9821 |  | 24.4916 | 48.9337 | 9.8316 |  | 81.2351 | 151.9634 | 8.2137 | 23.6304 | 11.397 | 145 | 35.2219 | 0 | 112.7252 | 0.31501
11673 | 841.1506 | 3.1817 | 28.0668 | 86.5087 | -13.6457 | 13.3005 | 89.8367 | 3.4698 |  | 25.439 | 50.7901 | 10.5834 |  | 88.6467 | 160.2006 | 7.837 | 24.2483 | 12.9296 | 148 | 29.965 | 0 | 106.8587 | 0.34972
11674 | 878.1036 | 3.4066 | 27.9807 | 87.3111 | -13.641 | 13.3 | 101.1054 | 2.0732 |  | 26.5438 | 53.0444 | 13.9458 |  | 96.8539 | 164.7341 | 7.9438 | 24.5085 | 13.0324 | 151 | 24.8786 | 0 | 103.8576 | 0.32485
11675 | 900.8077 | 3.6297 | 27.6581 | 86.6876 | -13.6469 | 13.3 | 117.3263 | 2.495 |  | 25.8568 | 58.3742 | 13.3168 |  | 100.7922 | 169.9088 | 8.1813 | 24.9895 | 13.2731 | 151 | 22.3836 | 0 | 104.5872 | 0.3131
11676 | 919.4067 | 3.5187 | 26.2899 | 87.3331 | -12.646 | 12.3503 | 120.2531 | 2.7842 |  | 24.143 | 61.2058 | 11.7108 |  | 100.2796 | 174.464 | 8.9345 | 25.04 | 13.7552 | 180 | 17.756 | 0 | 106.2628 | 0.31792
11677 | 928.002 | 3.6025 | 25.0075 | 89.5995 | -11.6476 | 11.4003 | 117.6331 | 2.8243 |  | 24.1204 | 63.8806 | 13.8819 |  | 100.2968 | 178.3243 | 9.288 | 24.2278 | 14.1541 | 149 | 18.6969 | 0 | 97.7792 | 0.29801
11678 | 930.5824 | 5.6272 | 24.9139 | 90.5967 | -14.6426 | 14.2492 | 127.974 | 3.7922 |  | 22.3699 | 66.4928 | 14.4793 |  | 101.5316 | 180.6208 | 9.1484 | 24.1676 | 14.6992 | 154 | 22.3547 | 0 | 95.6251 | 0.33376
11679 | 945.4981 | 6.9881 | 25.2111 | 90.1956 | -12.6478 | 12.3505 | 137.4757 | 3.138 |  | 21.0334 | 67.0325 | 12.7033 |  | 100.33 | 182.4752 | 8.9706 | 24.7513 | 14.9202 | 165 | 28.3283 | 0 | 93.8459 | 0.29824
11680 | 943.5252 | 4.6897 | 25.8676 | 89.0756 | -7.6483 | 7.6013 | 139.3899 | 2.6404 |  | 21.4735 | 66.3596 | 10.7069 |  | 94.6655 | 167.5424 | 8.6513 | 24.4422 | 14.6429 | 159 | 27.371 | 0 | 90.9113 | 0.27432
11681 | 922.9493 | 3.634 | 24.9995 | 89.9797 | -7.6459 | 7.6 | 128.0876 | 2.4811 |  | 19.0364 | 61.4601 | 9.6222 |  | 80.774 | 141.2534 | 8.6094 | 23.5291 | 14.2983 | 148 | 24.4861 | 0 | 88.567 | 0.25238
11682 | 912.499 | 5.9511 | 24.3004 | 90.8066 | -6.6426 | 6.6503 | 102.524 | 1.7317 |  | 14.0709 | 59.7739 | 9.6665 |  | 65.4302 | 138.8525 | 8.48 | 23.3008 | 11.7985 | 146 | 29.9971 | 0 | 85.0008 | 0.2289
11683 | 892.9825 | 7.9807 | 20.4983 | 89.606 | -6.6426 | 6.65 | 117.5168 | 2.2834 |  | 11.9577 | 67.2105 | 9.9583 |  | 57.2558 | 131.6679 | 8.346 | 23.036 | 7.0966 | 137 | 31.6699 | 0 | 80.4504 | 0.1462
11684 | 865.432 | 15.5931 | 15.8188 | 89.1627 | -7.6459 | 7.5997 | 119.1324 | 2.6967 |  | 11.6466 | 66.6138 | 9.7393 |  | 55.2793 | 124.0682 | 8.3134 | 23.0921 | 5.1717 | 136 | 31.9822 | 0 | 77.0676 | 0.0098922
11685 | 852.7441 | 18.9751 | 15.1936 | 91.5144 | -8.6426 | 8.5497 | 96.7665 | 2.7073 |  | 13.3987 | 49.4522 | 11.518 |  | 54.1599 | 122.9304 | 8.7918 | 23.6876 | 4.5796 | 132 | 33.5482 | 0 | 70.8107 | 0
11686 | 835.7065 | 14.5748 | 15.4832 | 94.5923 | -8.6431 | 8.55 | 93.8771 | 3.3203 |  | 14.5107 | 48.1303 | 12.8636 |  | 51.1713 | 124.09 | 8.8822 | 23.9728 | 4.3929 | 113 | 34.6699 | 0 | 77.8531 | 0
11687 | 236.4541 | 4.0349 | 4.0898 | 24.3315 | 0.13014 | 0.002376 | 27.6875 | 1.0899 |  | 4.4045 | 16.2847 | 3.892 |  | 13.3506 | 38.6066 | 2.3313 | 6.2235 | 1.3495 | 109 | 2.4119 | 0 | 4.5203 | 0
11688 | 827.4136 | 2.6109 | 15.5541 | 89.9443 | -9.6366 | 9.5 | 93.3212 | 4.0793 |  | 14.5415 | 38.1905 | 13.2468 |  | 39.1135 | 115.7533 | 8.6776 | 25.7972 | 4.2514 | 122 | 31.8327 | 0 | 88.8608 | 0
11689 | 814.0896 | 2.4358 | 15.6337 | 90.7658 | -9.6414 | 9.5 | 82.8335 | 4.2961 |  | 14.6054 | 37.1778 | 13.2408 |  | 39.4599 | 115.6746 | 8.9608 | 26.5297 | 4.1258 | 114 | 32.7352 | 0 | 92.211 | 0
11690 | 795.6453 | 2.4761 | 15.7222 | 91.4802 | -10.6348 | 10.4497 | 77.2465 | 4.568 |  | 14.6984 | 38.2261 | 13.1222 |  | 39.4304 | 119.657 | 9.4364 | 26.3365 | 3.4505 | 112 | 32.4658 | 0 | 91.0234 | 0
11691 | 793.707 | 2.5689 | 15.8893 | 91.3559 | -9.6337 | 9.5003 | 77.5722 | 4.6412 |  | 14.7527 | 37.8242 | 13.044 |  | 38.2256 | 120.4384 | 9.5756 | 26.3138 | 2.7731 | 108 | 29.9716 | 0 | 92.6196 | 0
11692 | 792.238 | 2.9878 | 16.0745 | 90.813 | -10.6355 | 10.4497 | 77.2623 | 4.2186 |  | 14.0706 | 36.4061 | 12.616 |  | 37.4118 | 115.1586 | 9.4954 | 27.0459 | 2.552 | 103 | 33.6823 | 0 | 100.1215 | 0
11693 | 805.442 | 4.1942 | 24.6615 | 88.2014 | -10.6409 | 10.45 | 81.1025 | 3.7573 |  | 15.1348 | 34.0344 | 13.5151 |  | 41.4106 | 111.6959 | 8.873 | 27.7753 | 2.4033 | 108 | 30.4355 | 0 | 108.9882 | 0
11694 | 853.6389 | 8.8926 | 44.1577 | 86.5106 | -14.6399 | 14.2489 | 93.4025 | 4.1283 |  | 21.4981 | 38.9782 | 17.1391 |  | 80.2827 | 124.5816 | 11.6869 | 26.1323 | 2.5331 | 155 | 36.4975 | 0 | 124.8173 | 0.036699
11695 | 906.3456 | 15.8906 | 74.7882 | 93.6907 | -16.6467 | 16.1495 | 110.4114 | 5.4705 |  | 33.4258 | 64.3944 | 24.562 |  | 116.552 | 184.313 | 26.2338 | 27.745 | 4.8729 | 217 | 52.49 | 0 | 140.2634 | 0.19191
11696 | 987.8829 | 13.1854 | 97.1928 | 113.211 | -20.6418 | 19.9489 | 134.1284 | 7.308 |  | 42.8141 | 85.7345 | 25.954 |  | 145.6591 | 242.4444 | 35.8375 | 32.6197 | 11.6282 | 261 | 57.1977 | 0 | 170.1245 | 0.29597
11697 | 1095.7356 | 8.8233 | 105.2727 | 131.034 | -18.6454 | 18.0505 | 149.8181 | 6.1321 |  | 51.042 | 94.3055 | 33.368 |  | 163.7516 | 281.2532 | 40.4176 | 36.34 | 15.7663 | 282 | 58.4634 | 0.044222 | 190.3415 | 0.34292
11698 | 1117.606 | 6.2082 | 107.1351 | 133.837 | -19.6449 | 18.9997 | 165.4227 | 5.8653 |  | 53.9157 | 97.2986 | 41.1435 |  | 173.8495 | 298.1861 | 40.2733 | 39.4695 | 17.6142 | 300 | 52.6827 | 0.53801 | 199.5625 | 0.33051
11699 | 1137.5858 | 5.5631 | 107.7472 | 137.122 | -18.6467 | 18.0503 | 176.6511 | 5.2244 |  | 53.2045 | 96.1905 | 40.7252 |  | 179.7356 | 299.141 | 38.8048 | 41.1401 | 18.2627 | 299 | 58.2764 | 0.53917 | 203.1168 | 0.31817
11700 | 1136.4649 | 10.256 | 108.2675 | 134.5252 | -17.6478 | 17.1003 | 181.1857 | 4.9224 |  | 50.4202 | 95.5091 | 37.2539 |  | 172.3187 | 302.065 | 38.6905 | 39.8475 | 18.7317 | 341 | 48.1841 | 0.5992 | 196.7916 | 0.27924
11701 | 1169.8843 | 12.3812 | 109.4276 | 140.696 | -17.6434 | 17.1 | 187.5064 | 4.6763 |  | 44.3711 | 98.7366 | 38.2636 |  | 175.4347 | 300.5284 | 39.4077 | 40.3952 | 19.7075 | 268 | 54.1696 | 0.54733 | 202.6069 | 0.30133
11702 | 1169.9596 | 8.1067 | 111.2831 | 145.2148 | -18.6442 | 18.0497 | 195.1769 | 4.8362 |  | 44.1818 | 101.772 | 38.511 |  | 173.7062 | 298.5839 | 38.6503 | 39.0046 | 19.8577 | 268 | 53.0541 | 0.82462 | 196.6766 | 0.33741
11703 | 1158.007 | 7.156 | 109.2453 | 140.4738 | -16.648 | 16.1505 | 189.3378 | 4.9239 |  | 39.8612 | 100.5584 | 35.421 |  | 169.4073 | 288.078 | 36.2632 | 38.5768 | 19.5304 | 254 | 50.2755 | 0.84661 | 186.403 | 0.30303
11704 | 1118.3387 | 10.9268 | 105.0971 | 134.5813 | -9.6462 | 9.5018 | 183.4507 | 4.7532 |  | 35.2156 | 96.2952 | 28.9501 |  | 158.4186 | 249.8483 | 29.663 | 37.8964 | 19.0311 | 239 | 54.4968 | 0.8749 | 157.7845 | 0.28155
11705 | 1071.241 | 12.346 | 101.0506 | 116.9057 | -10.642 | 10.4497 | 171.9952 | 3.1852 |  | 28.8781 | 83.5105 | 23.1787 |  | 128.8011 | 209.5628 | 16.2757 | 34.2292 | 18.5811 | 214 | 51.2507 | 0.89007 | 112.0868 | 0.26626
11706 | 1020.7043 | 11.6266 | 96.6757 | 99.4988 | -7.6401 | 7.6008 | 156.7927 | 2.2107 |  | 26.3433 | 65.7708 | 19.8369 |  | 90.6684 | 188.3237 | 11.3209 | 30.9225 | 14.5985 | 204 | 37.2044 | 0.89201 | 99.1766 | 0.2344
11707 | 986.6128 | 10.4232 | 81.7325 | 94.6916 | -8.6391 | 8.5497 | 140.0193 | 1.8682 |  | 25.367 | 60.9307 | 13.153 |  | 76.5923 | 172.7878 | 10.4367 | 27.9692 | 7.3876 | 162 | 36.5342 | 0.88619 | 80.8007 | 0.14175
11708 | 965.7793 | 11.2907 | 39.0041 | 91.9759 | -7.637 | 7.6003 | 127.8947 | 3.0226 |  | 23.4579 | 58.6358 | 10.7027 |  | 71.8079 | 160.2123 | 9.1363 | 26.2469 | 4.6253 | 152 | 36.1065 | 0.89551 | 74.8521 | 0.013423
11709 | 952.975 | 9.4345 | 23.3555 | 93.8161 | -8.636 | 8.5497 | 106.86 | 3.8922 |  | 21.0733 | 49.4169 | 17.5508 |  | 68.5983 | 151.472 | 9.05 | 26.3184 | 4.6987 | 139 | 36.1426 | 0.89473 | 75.8614 | 0
11710 | 915.2689 | 5.7651 | 22.6243 | 98.866 | -7.6344 | 7.6003 | 92.0803 | 2.9661 |  | 17.742 | 40.0583 | 16.5141 |  | 64.9571 | 153.5607 | 9.2372 | 26.8514 | 3.9092 | 138 | 35.3839 | 0.89806 | 86.0639 | 0
11711 | 252.8789 | 1.4744 | 5.8707 | 25.1069 | 0.13333 | 0.002112 | 25.3309 | 0.74968 |  | 4.9103 | 11.8091 | 4.3566 |  | 16.699 | 47.3416 | 2.3838 | 6.8756 | 1.0636 | 119 | 2.5594 | 0.099362 | 2.5449 | 0
11712 | 900.2309 | 2.3847 | 22.6146 | 93.1919 | -9.6378 | 9.4997 | 81.4884 | 4.501 |  | 14.6407 | 35.9524 | 9.0915 |  | 52.8315 | 130.0508 | 9.2625 | 26.1102 | 3.9992 | 112 | 33.2801 | 0.8995 | 89.9549 | 0
11713 | 898.5633 | 2.2995 | 22.6653 | 90.193 | -8.6345 | 8.5503 | 86.5432 | 4.5549 |  | 14.3265 | 36.3913 | 8.8943 |  | 50.556 | 129.8428 | 9.153 | 26.8677 | 3.0795 | 100 | -58.0861 | 0.89836 | 91.2367 | 0
11714 | 866.2882 | 2.4377 | 22.799 | 89.3626 | -9.6334 | 9.4997 | 84.4914 | 3.7072 |  | 14.4523 | 37.2529 | 8.8535 |  | 48.7749 | 127.0944 | 9.2684 | 30.2944 | 2.6564 | 98 | 32.4575 | 0.90092 | 92.5484 | 0
11715 | 849.5186 | 2.9734 | 22.78 | 89.2305 | -9.6332 | 9.5 | 92.1865 | 3.7308 |  | 14.3707 | 37.4786 | 8.852 |  | 48.1077 | 119.1426 | 9.1932 | 31.4167 | 2.6561 | 100 | 31.6436 | 0.90858 | 93.8048 | 0
11716 | 850.0594 | 3.1016 | 22.8351 | 88.7582 | -9.6344 | 9.5 | 90.9495 | 4.4242 |  | 13.868 | 36.7606 | 8.4731 |  | 48.1263 | 114.2953 | 9.1895 | 32.3982 | 2.6535 | 99 | 32.409 | 0.90039 | 98.4234 | 0
11717 | 859.0147 | 4.2428 | 33.7984 | 87.5612 | -9.6348 | 9.5 | 88.4865 | 4.4691 |  | 12.3241 | 35.792 | 8.8319 |  | 49.7447 | 113.0252 | 9.08 | 33.2902 | 2.5474 | 107 | 31.9769 | 0.90768 | 110.9114 | 0
11718 | 894.7773 | 7.0658 | 47.304 | 95.4313 | -19.6373 | 18.9974 | 89.1868 | 4.4811 |  | 16.2232 | 43.2403 | 14.2957 |  | 77.7412 | 126.3399 | 11.1381 | 30.6112 | 2.4837 | 175 | 35.5603 | 0.90299 | 126.3247 | 0.19641
11719 | 958.4889 | 10.8332 | 75.0003 | 101.0407 | 10.0067 | 22.7989 | 105.9214 | 3.284 |  | 23.0554 | 69.6036 | 26.2941 |  | 113.068 | 178.1243 | 25.3843 | 28.8086 | 5.0349 | 241 | 46.7534 | 0.99709 | 138.5042 | 0.26725
11720 | 1045.5833 | 11.4066 | 91.4227 | 114.6966 | 33.4367 | 20.9005 | 143.3081 | 4.4975 |  | 28.2208 | 90.4975 | 33.2514 |  | 138.9011 | 233.3057 | 35.5573 | 32.7171 | 12.7568 | 240 | 52.4072 | 1.6427 | 172.8905 | 0.29719
11721 | 1122.0311 | 9.039 | 97.7561 | 127.7168 | 27.3978 | 20.9 | 156.4163 | 4.8442 |  | 33.6747 | 97.6334 | 33.3645 |  | 155.366 | 274.1936 | 40.1682 | 35.5687 | 17.2502 | 335 | 54.8832 | 1.7139 | 195.0755 | 0.33183
11722 | 1151.7199 | 6.6474 | 103.6888 | 132.5534 | 22.2911 | 24.6989 | 167.7133 | 4.2102 |  | 36.5788 | 97.8144 | 35.1429 |  | 168.5155 | 299.04 | 39.8896 | 37.8604 | 18.5784 | 323 | 56.0762 | 1.7319 | 196.5987 | 0.31715
11723 | 1197.9644 | 10.1466 | 108.0392 | 137.8384 | 26.0387 | 23.7503 | 171.3876 | 4.3964 |  | 34.3266 | 96.6017 | 36.3326 |  | 175.1484 | 297.3167 | 37.5539 | 38.8467 | 18.777 | 313 | 57.5589 | 1.7317 | 194.7494 | 0.30231
11724 | 1178.9265 | 12.1774 | 106.9697 | 133.6087 | 26.4173 | 23.75 | 171.1387 | 4.6721 |  | 30.4151 | 94.4101 | 38.4367 |  | 168.5254 | 288.6545 | 38.2036 | 38.3794 | 18.8385 | 316 | 47.4386 | 1.7307 | 193.716 | 0.26507
11725 | 1189.319 | 8.5113 | 108.2488 | 136.3441 | 39.5449 | 21.8505 | 182.8511 | 5.0368 |  | 36.6015 | 94.6169 | 39.5864 |  | 170.6817 | 294.4276 | 39.3239 | 38.8265 | 19.0061 | 250 | 50.2193 | 1.7338 | 202.7305 | 0.28075
11726 | 1203.1483 | 7.6912 | 110.5118 | 140.0545 | 47.769 | 21.85 | 183.1872 | 5.1076 |  | 41.0092 | 95.6467 | 38.4367 |  | 169.8518 | 295.4739 | 38.1691 | 38.6756 | 18.9321 | 240 | 50.5585 | 1.728 | 196.8493 | 0.31339
11727 | 1184.6888 | 11.1373 | 106.6514 | 137.6694 | 7.5954 | 20.9003 | 177.413 | 4.5979 |  | 38.547 | 96.0192 | 34.787 |  | 167.4314 | 283.6466 | 34.7339 | 37.8822 | 18.4728 | 262 | 51.5891 | 1.5819 | 190.1782 | 0.28432
11728 | 1150.9517 | 10.0137 | 105.0936 | 132.2191 | -14.4527 | 16.1513 | 167.4316 | 4.1148 |  | 36.8662 | 94.269 | 31.6258 |  | 155.3031 | 256.2032 | 28.8249 | 36.6903 | 18.3306 | 258 | 41.8412 | 1.2109 | 168.3874 | 0.26903
11729 | 1080.4667 | 10.6528 | 101.4449 | 117.719 | -13.4469 | 14.2505 | 149.2197 | 3.5865 |  | 27.165 | 84.092 | 27.4206 |  | 116.9083 | 209.4577 | 15.8255 | 34.1179 | 17.5901 | 235 | 39.1624 | 1.1664 | 134.8921 | 0.25433
11730 | 1033.6618 | 9.6854 | 98.1959 | 100.5945 | -10.1346 | 11.4008 | 137.2322 | 3.4712 |  | 22.9338 | 67.9856 | 19.5409 |  | 74.9951 | 187.9902 | 11.4392 | 31.8493 | 14.6259 | 217 | 43.6396 | 1.1685 | 119.2871 | 0.22878
11731 | 974.0703 | 4.3705 | 83.1221 | 97.2375 | -10.0091 | 11.4 | 119.6494 | 3.6427 |  | 21.9764 | 62.3618 | 7.4873 |  | 61.0075 | 180.9808 | 10.9069 | 29.3017 | 8.4798 | 191 | 42.2401 | 1.1687 | 105.346 | 0.13706
11732 | 935.3772 | 3.8236 | 39.391 | 94.6823 | -11.165 | 12.3497 | 95.619 | 2.2283 |  | 21.0889 | 57.2963 | 3.42 |  | 57.1918 | 178.0561 | 9.3413 | 26.871 | 5.4065 | 174 | 40.9478 | 1.165 | 100.4233 | 0.0077533
11733 | 903.3906 | 7.8919 | 23.1443 | 94.6482 | -11.2486 | 12.35 | 84.9105 | 2.8482 |  | 18.3425 | 48.1399 | 4.9804 |  | 55.1909 | 168.3509 | 8.686 | 26.4389 | 5.1622 | 148 | 39.1213 | 1.1745 | 95.5671 | 0
11734 | 868.3843 | 10.3764 | 22.5802 | 98.8456 | -12.4701 | 13.2997 | 76.0391 | 2.4019 |  | 18.6425 | 39.6846 | 6.3667 |  | 51.2428 | 148.1724 | 8.764 | 27.0242 | 5.2861 | 133 | 37.8821 | 1.1621 | 91.7488 | 0
11735 | 247.0639 | 3.5295 | 6.0198 | 25.6643 | 0.50598 | 0.003696 | 21.2915 | 0.59943 |  | 5.84 | 11.9836 | 2.0047 |  | 13.3743 | 44.1084 | 2.3047 | 7.0917 | 1.644 | 110 | 2.7379 | 0.13218 | 6.0762 | 0
11736 | 840.616 | 9.617 | 22.471 | 94.6495 | -9.1534 | 10.45 | 73.4868 | 3.6373 |  | 17.3432 | 36.2315 | 6.633 |  | 44.997 | 127.7464 | 8.959 | 26.6658 | 4.3636 | 102 | 33.3216 | 1.1711 | 95.3675 | 0
11737 | 824.404 | 9.6037 | 22.4179 | 91.4561 | -9.3448 | 10.45 | 79.5503 | 3.7023 |  | 16.5263 | 37.4919 | 6.4409 |  | 42.5348 | 123.7801 | 9.0557 | 26.8386 | 3.3242 | 98 | 32.0823 | 1.1726 | 99.1928 | 0
11738 | 794.9849 | 9.511 | 22.3233 | 89.7285 | -10.2524 | 10.45 | 79.7038 | 2.9489 |  | 14.9269 | 37.8018 | 6.1736 |  | 40.9546 | 120.446 | 8.7604 | 26.2624 | 2.8924 | 98 | 30.8119 | 1.1721 | 95.0667 | 0
11739 | 787.0797 | 6.7893 | 22.4272 | 89.3824 | -10.6349 | 10.45 | 77.6866 | 3.3025 |  | 14.3486 | 37.461 | 6.0485 |  | 39.7408 | 116.5342 | 9.2914 | 26.0823 | 2.656 | 95 | 29.7968 | 1.1774 | 97.7585 | 0
11740 | 789.7588 | 3.9248 | 22.5499 | 88.253 | -11.6367 | 11.3997 | 75.6527 | 3.8645 |  | 13.6283 | 36.8556 | 5.6975 |  | 39.0288 | 110.9589 | 9.4869 | 26.9501 | 2.5628 | 96 | 29.378 | 1.1763 | 105.4543 | 0
11741 | 799.1917 | 4.2732 | 36.3246 | 86.5137 | -10.6403 | 10.4503 | 81.058 | 3.8752 |  | 12.2675 | 36.3841 | 6.6044 |  | 44.2422 | 110.1744 | 9.2975 | 27.9772 | 2.4493 | 95 | 29.0925 | 1.1828 | 118.721 | 0.0095377
11742 | 846.5399 | 7.5688 | 50.7188 | 88.2255 | -15.6411 | 15.1987 | 97.5405 | 3.7222 |  | 14.8932 | 41.355 | 11.9428 |  | 84.4747 | 124.021 | 11.8328 | 26.2531 | 2.4119 | 166 | 35.5817 | 1.1729 | 131.3149 | 0.178
11743 | 885.3311 | 13.3489 | 75.8059 | 96.208 | -19.6432 | 18.9989 | 119.2495 | 4.1893 |  | 24.6977 | 63.2637 | 25.4162 |  | 114.491 | 173.8403 | 26.2398 | 28.0921 | 4.7469 | 258 | 47.7139 | 1.1866 | 146.8988 | 0.050459
11744 | 953.9359 | 16.648 | 98.522 | 112.7196 | -18.6447 | 18.0503 | 138.1297 | 4.0539 |  | 36.0809 | 86.9616 | 31.4134 |  | 136.9363 | 232.7221 | 34.376 | 31.7328 | 11.8138 | 282 | 50.229 | 1.4745 | 182.3732 | 0.071864
11745 | 1031.0509 | 14.7765 | 103.3223 | 126.344 | -19.6437 | 18.9997 | 150.8471 | 4.8657 |  | 38.0043 | 95.0188 | 31.9354 |  | 155.9921 | 270.4078 | 38.1446 | 36.1623 | 16.2684 | 327 | 52.4267 | 1.7055 | 200.7204 | 0.09096
11746 | 1070.2747 | 14.2723 | 104.3973 | 133.4801 | -21.3246 | 20.8995 | 151.4959 | 4.0846 |  | 39.9244 | 96.9914 | 35.1787 |  | 169.5628 | 294.5295 | 39.1662 | 39.0269 | 18.461 | 351 | 49.5448 | 1.7304 | 200.802 | 0.10597
11747 | 1084.039 | 12.8048 | 108.7273 | 135.5002 | -19.3986 | 19.9503 | 165.8507 | 4.7487 |  | 42.8505 | 97.1239 | 38.1402 |  | 176.8377 | 296.7148 | 40.0824 | 39.9162 | 19.4147 | 314 | 54.865 | 1.7279 | 207.076 | 0.11592
11748 | 1068.1435 | 7.5455 | 107.7173 | 132.765 | -15.7847 | 17.1008 | 177.4195 | 4.1581 |  | 33.3235 | 94.4998 | 37.509 |  | 171.9311 | 293.7264 | 39.5995 | 38.0866 | 19.0888 | 340 | 44.6925 | 1.7246 | 200.8937 | 0.1197
11749 | 1081.7148 | 5.3048 | 109.846 | 136.6505 | -15.0868 | 16.1503 | 178.3608 | 3.6782 |  | 35.2401 | 95.1611 | 38.1378 |  | 175.2563 | 292.3831 | 40.5635 | 40.2608 | 18.7048 | 302 | 47.1859 | 1.7176 | 216.1317 | 0.17261
11750 | 1085.5543 | 5.3338 | 111.4674 | 138.8363 | -16.5028 | 17.0997 | 176.6709 | 4.7703 |  | 43.8751 | 99.7826 | 38.2538 |  | 174.9958 | 286.4684 | 39.8462 | 40.1419 | 18.5297 | 268 | 48.8258 | 1.9969 | 209.5096 | 0.15432
11751 | 1061.1307 | 5.1826 | 107.85 | 134.5357 | -18.1271 | 18.0497 | 172.3196 | 4.0049 |  | 42.1987 | 100.195 | 37.5366 |  | 169.0132 | 278.8902 | 39.3989 | 39.477 | 18.7306 | 250 | 48.716 | 1.9292 | 197.9193 | 0.14633
11752 | 1032.8938 | 5.145 | 104.5769 | 126.6843 | -13.4963 | 13.3013 | 163.7168 | 3.2832 |  | 36.9269 | 96.6451 | 32.926 |  | 156.8655 | 249.078 | 33.0869 | 38.0019 | 18.6093 | 231 | 41.1966 | 1.8014 | 181.4872 | 0.12107
11753 | 1007.6359 | 5.0213 | 100.9194 | 113.5039 | -9.9093 | 10.4508 | 149.8757 | 2.2879 |  | 29.6242 | 85.5709 | 29.099 |  | 122.2406 | 229.1527 | 17.6232 | 34.4601 | 17.6725 | 225 | 39.0778 | 1.7933 | 128.4767 | 0.060724
11754 | 964.5568 | 4.471 | 97.3738 | 99.4212 | -9.8912 | 10.45 | 140.1836 | 1.6761 |  | 23.1408 | 69.5095 | 23.8549 |  | 81.7076 | 206.4135 | 11.1046 | 31.4291 | 14.3156 | 198 | 42.0007 | 1.7887 | 120.7603 | 0.041276
11755 | 921.1883 | 3.4043 | 83.7469 | 95.2357 | -11.293 | 11.3997 | 116.4188 | 2.4822 |  | 22.4567 | 61.5168 | 12.5411 |  | 67.5282 | 189.3155 | 10.1802 | 27.7671 | 7.9246 | 177 | 46.3106 | 1.7885 | 107.7019 | 0.029129
11756 | 893.4816 | 4.2687 | 39.358 | 90.9493 | -14.5527 | 14.2492 | 94.9679 | 1.9098 |  | 20.0334 | 56.4129 | 9.4113 |  | 60.3108 | 167.9195 | 9.7199 | 26.1839 | 5.3488 | 175 | 52.5616 | 1.7797 | 101.5579 | 0.0010485
11757 | 867.8313 | 4.8938 | 22.7338 | 90.005 | -11.5645 | 11.4008 | 84.9181 | 2.8153 |  | 16.9016 | 47.5738 | 13.3322 |  | 58.5534 | 152.2313 | 9.9065 | 26.1309 | 4.7639 | 161 | 51.639 | 1.7922 | 100.5525 | 0
11758 | 833.6206 | 4.1613 | 21.4457 | 94.4669 | -11.118 | 11.4 | 91.8016 | 3.715 |  | 15.461 | 38.8827 | 14.1585 |  | 57.4178 | 143.6032 | 9.9067 | 26.3911 | 4.1893 | 133 | 53.6713 | 1.7922 | 100.5522 | 0
11759 | 234.0994 | 1.228 | 5.5973 | 24.3816 | 0.39766 | 0.003167 | 27.5256 | 1.1668 |  | 4.5625 | 11.5929 | 4.1166 |  | 15.0798 | 43.7166 | 2.5828 | 6.8394 | 1.2312 | 109 | 4.0223 | 0.20016 | 8.5989 | 0
11760 | 784.8617 | 2.5932 | 15.7774 | 89.3957 | -10.2242 | 10.45 | 91.0029 | 2.9469 |  | 15.4677 | 35.9681 | 10.7255 |  | 52.4576 | 116.0249 | 10.0882 | 26.2472 | 3.2216 | 117 | 37.5093 | 1.7904 | 98.2798 | 0
11761 | 782.8517 | 2.871 | 15.8108 | 89.844 | -10.5508 | 10.45 | 82.995 | 3.0165 |  | 15.5171 | 35.6351 | 10.4245 |  | 48.8658 | 111.2601 | 10.4136 | 27.1281 | 2.801 | 113 | 33.9742 | 1.7882 | 96.3768 | 0
11762 | 774.6141 | 3.0022 | 15.8908 | 89.0455 | -10.5985 | 10.45 | 78.0184 | 3.7968 |  | 15.5401 | 36.0244 | 10.3724 |  | 46.6349 | 117.9237 | 10.6613 | 30.4978 | 2.5492 | 111 | 31.8295 | 1.7916 | 99.6141 | 0
11763 | 767.781 | 2.5083 | 16.0259 | 88.4484 | -11.6373 | 11.3997 | 77.5669 | 4.4332 |  | 14.7667 | 36.2437 | 12.5633 |  | 46.2421 | 118.4665 | 10.5147 | 31.474 | 2.5051 | 102 | 31.4884 | 1.7867 | 104.153 | 0
11764 | 769.7055 | 3.018 | 15.8823 | 87.6032 | -11.6385 | 11.4 | 76.8845 | 4.3532 |  | 13.5433 | 35.5166 | 10.8699 |  | 45.8191 | 109.9088 | 10.3925 | 30.628 | 2.471 | 96 | 31.5055 | 1.7909 | 105.4813 | 0
11765 | 778.5228 | 4.0213 | 30.6812 | 86.3503 | -11.6398 | 11.4 | 82.2899 | 3.9953 |  | 12.7399 | 35.1325 | 9.4841 |  | 50.6795 | 106.3141 | 10.2787 | 30.2116 | 2.3415 | 105 | 31.3709 | 1.7941 | 112.9511 | 0.11422
11766 | 816.6653 | 4.9341 | 50.6847 | 90.6908 | -13.6367 | 13.2995 | 94.4502 | 3.6813 |  | 14.829 | 41.2101 | 14.8115 |  | 81.2936 | 122.8152 | 12.4924 | 28.0381 | 2.2996 | 163 | 35.0511 | 1.787 | 127.3987 | 0.20862
11767 | 877.431 | 5.8942 | 74.6298 | 96.1073 | -16.6406 | 16.1492 | 115.2743 | 2.5778 |  | 19.281 | 65.9652 | 29.2294 |  | 114.5983 | 180.6874 | 27.6296 | 29.139 | 5.0532 | 253 | 48.2269 | 2.1585 | 137.2927 | 0.29328
11768 | 954.5208 | 11.6066 | 100.4341 | 113.9438 | -18.6458 | 18.0495 | 137.2151 | 4.2071 |  | 22.1875 | 86.7424 | 33.4654 |  | 141.8626 | 236.9849 | 38.0394 | 33.3512 | 12.0855 | 297 | 48.7627 | 2.325 | 172.1622 | 0.26901
11769 | 1029.3219 | 17.0077 | 105.5216 | 128.3384 | -18.6448 | 18.05 | 140.456 | 4.3256 |  | 25.3613 | 96.2471 | 31.4172 |  | 155.7294 | 263.0084 | 43.154 | 37.3667 | 15.6882 | 374 | 45.054 | 2.2748 | 197.7937 | 0.17915
11770 | 1078.5411 | 19.4569 | 104.5714 | 132.4892 | -20.191 | 19.9495 | 148.0814 | 4.7072 |  | 28.3122 | 99.3952 | 33.1181 |  | 164.1367 | 283.2654 | 41.9673 | 39.6592 | 17.5037 | 352 | 44.7145 | 1.8725 | 200.5252 | 0.18935
11771 | 1109.1726 | 19.531 | 106.9475 | 134.6797 | -17.1918 | 18.0505 | 157.0964 | 3.9348 |  | 30.8804 | 99.1847 | 37.1022 |  | 167.4207 | 288.3377 | 40.2069 | 39.5835 | 17.968 | 325 | 46.4749 | 1.8265 | 201.1383 | 0.17632
11772 | 1106.7073 | 16.7046 | 105.4979 | 134.8299 | -16.2408 | 17.1003 | 162.281 | 3.9336 |  | 28.76 | 96.9128 | 39.7716 |  | 157.0361 | 280.4193 | 40.9084 | 38.9948 | 17.5949 | 299 | 41.3741 | 1.8154 | 197.4749 | 0.1316
11773 | 1127.1674 | 11.9364 | 105.0594 | 138.0184 | -16.7548 | 17.1 | 167.4424 | 4.0089 |  | 28.9115 | 94.5221 | 31.8191 |  | 159.8091 | 282.4891 | 41.3946 | 37.7842 | 18.2997 | 257 | 43.4023 | 0 | 200.6351 | 0.26922
11774 | 1101.0396 | 9.0064 | 108.9107 | 137.3559 | -22.8683 | 22.7984 | 174.9975 | 3.6484 |  | 28.4734 | 94.8976 | 25.942 |  | 161.2903 | 279.6679 | 40.6743 | 37.047 | 19.0518 | 236 | 45.2128 | 1.8122 | 197.2306 | 0.31936
11775 | 1082.4291 | 7.3941 | 109.0785 | 135.9172 | -20.8411 | 20.9005 | 175.0637 | 3.5537 |  | 28.1991 | 96.7003 | 24.2677 |  | 154.8015 | 279.0859 | 39.128 | 36.0388 | 18.7808 | 235 | 43.2162 | 1.4587 | 188.6178 | 0.29177
11776 | 1058.0273 | 5.673 | 105.8776 | 121.0898 | -10.6706 | 11.4026 | 171.6583 | 2.9153 |  | 28.8565 | 95.0999 | 21.9695 |  | 144.891 | 249.2682 | 31.2335 | 35.3706 | 17.7581 | 224 | 39.0454 | 1.2835 | 161.193 | 0.28292
11777 | 995.9627 | 5.3625 | 86.5393 | 111.6773 | -7.8015 | 8.5508 | 161.494 | 1.6421 |  | 28.5127 | 82.6281 | 21.0245 |  | 110.1637 | 208.0697 | 17.6323 | 33.2206 | 16.5767 | 226 | 34.1129 | 1.2579 | 123.3919 | 0.28098
11778 | 949.7289 | 6.1574 | 40.5511 | 100.5952 | -6.8469 | 7.6003 | 136.2865 | 1.1898 |  | 24.7564 | 64.7328 | 17.4107 |  | 68.6479 | 176.6356 | 10.7758 | 29.9416 | 12.9837 | 193 | 36.1525 | 1.2657 | 101.9735 | 0.27196
11779 | 903.9008 | 3.892 | 23.5109 | 93.6637 | -8.731 | 9.4995 | 111.2272 | 1.346 |  | 20.6301 | 53.7614 | 10.41 |  | 52.8953 | 156.9541 | 10.1647 | 26.3352 | 6.7296 | 167 | 36.8977 | 1.2645 | 96.0108 | 0.18409
11780 | 867.857 | 3.8213 | 25.4197 | 90.6725 | -8.6083 | 9.5 | 111.1855 | 2.1368 |  | 19.4869 | 41.7767 | 8.502 |  | 49.5866 | 147.7795 | 9.4118 | 24.9431 | 4.3422 | 158 | 35.415 | 1.2564 | 88.1578 | 0.03804
11781 | 850.4472 | 4.5271 | 25.9764 | 91.6263 | -7.5707 | 8.5503 | 90.8864 | 2.0187 |  | 16.3916 | 36.1991 | 7.2872 |  | 51.4521 | 141.8829 | 8.6869 | 25.5912 | 4.3367 | 158 | 31.8143 | 1.2595 | 86.3416 | 0
11782 | 846.5359 | 3.9192 | 24.457 | 98.864 | -7.8826 | 8.55 | 73.5669 | 2.808 |  | 15.7794 | 34.888 | 6.7689 |  | 49.9642 | 135.1892 | 8.7754 | 26.5817 | 4.2448 | 138 | 34.5378 | 1.2707 | 86.9621 | 0
11783 | 242.4292 | 1.1651 | 6.3502 | 25.9396 | 0.33815 | 0.002376 | 20.4171 | 0.99078 |  | 4.8695 | 11.0817 | 2.0376 |  | 13.0994 | 41.4336 | 2.3244 | 6.9949 | 1.2876 | 123 | 2.493 | 0.14492 | 7.421 | 0
11784 | 835.0026 | 2.3756 | 22.5131 | 95.8192 | -9.3451 | 9.5 | 81.9723 | 3.2329 |  | 15.5705 | 35.02 | 6.6169 |  | 47.1668 | 134.4597 | 12.2157 | 26.9644 | 4.1241 | 108 | 32.1436 | 1.259 | 89.639 | 0
11785 | 837.3223 | 2.275 | 22.7062 | 90.3142 | -9.6158 | 10.4497 | 88.9243 | 2.7427 |  | 15.7203 | 36.6537 | 6.5345 |  | 42.3997 | 128.058 | 13.1402 | 26.5859 | 3.7214 | 104 | 33.2501 | 1.263 | 90.9749 | 0
11786 | 810.7637 | 2.4114 | 22.7648 | 89.5029 | -9.1437 | 10.4529 | 81.0316 | 3.4968 |  | 16.7017 | 36.4113 | 6.7967 |  | 40.227 | 124.1735 | 13.7081 | 26.0356 | 2.8664 | 103 | 31.7465 | 1.2646 | 93.1472 | 0
11787 | 801.0199 | 2.4385 | 22.8783 | 87.977 | -9.8076 | 10.4471 | 76.9232 | 3.9257 |  | 17.2134 | 35.9551 | 6.7993 |  | 40.3434 | 121.7519 | 13.8137 | 25.9947 | 2.583 | 107 | 31.2628 | 1.2688 | 92.7119 | 0
11788 | 815.5352 | 2.9161 | 22.9317 | 88.4436 | -11.1173 | 11.3997 | 75.9149 | 3.9079 |  | 15.9554 | 35.4485 | 5.8324 |  | 38.9079 | 115.837 | 12.2141 | 26.9602 | 2.5427 | 99 | 31.4351 | 1.2614 | 94.5873 | 0
11789 | 816.7878 | 3.671 | 23.8477 | 86.8863 | -10.3052 | 10.4503 | 74.8557 | 3.9583 |  | 13.5685 | 34.4269 | 4.0965 |  | 36.6165 | 110.6589 | 9.231 | 27.7451 | 2.4245 | 94 | 30.9862 | 1.2638 | 89.8517 | 0.08992
11790 | 824.8593 | 2.8271 | 40.4748 | 85.4666 | -9.744 | 10.45 | 61.1254 | 2.1917 |  | 12.1509 | 33.3668 | 3.6522 |  | 35.6434 | 108.522 | 8.3568 | 25.8818 | 2.3656 | 98 | 28.5471 | 1.2675 | 90.3706 | 0.14471
11791 | 834.3136 | 2.7497 | 50.8558 | 85.8452 | -8.2114 | 9.5003 | 60.2647 | 2.5146 |  | 11.8242 | 32.9194 | 6.2546 |  | 37.0824 | 108.1824 | 8.4416 | 24.9941 | 2.3501 | 102 | 33.7361 | 1.2659 | 89.9186 | 0.2608
11792 | 831.6058 | 3.4016 | 60.8909 | 85.8725 | -8.7179 | 9.5 | 79.3002 | 1.9821 |  | 13.3018 | 33.7401 | 12.0843 |  | 40.8349 | 108.7351 | 8.3918 | 25.2811 | 2.6658 | 121 | 40.6042 | 1.2673 | 91.4453 | 0.2143
11793 | 867.2331 | 3.2745 | 81.978 | 87.9759 | -7.8292 | 8.5503 | 88.6378 | 1.4432 |  | 17.1074 | 41.0805 | 13.9101 |  | 44.6866 | 110.7095 | 8.2304 | 25.4342 | 5.0601 | 146 | 39.1213 | 1.2682 | 90.5865 | 0.32087
11794 | 892.5319 | 3.2469 | 95.2664 | 88.2636 | -7.8648 | 8.55 | 99.0452 | 1.4214 |  | 21.601 | 47.7182 | 13.8323 |  | 53.6475 | 118.5489 | 8.196 | 25.2793 | 10.7287 | 189 | 35.6589 | 1.2603 | 94.6956 | 0.28234
11795 | 910.839 | 4.0859 | 98.3665 | 88.4572 | -6.8849 | 7.6003 | 121.3518 | 2.0124 |  | 24.9406 | 49.3754 | 13.9851 |  | 57.8709 | 124.7339 | 8.3866 | 24.8757 | 13.0094 | 190 | 31.6562 | 1.2605 | 90.985 | 0.27107
11796 | 906.681 | 8.695 | 97.7794 | 88.0986 | -5.6136 | 6.6503 | 122.7043 | 1.7774 |  | 25.6244 | 55.2559 | 13.9414 |  | 61.4228 | 133.334 | 8.333 | 24.4805 | 13.5345 | 169 | 22.3825 | 1.2626 | 86.0588 | 0.25726
11797 | 887.155 | 8.1981 | 85.6883 | 87.9866 | -6.3939 | 7.5997 | 123.6412 | 1.2644 |  | 24.7779 | 57.4922 | 14.0645 |  | 61.7308 | 145.0581 | 8.3621 | 25.4854 | 13.4962 | 169 | 18.515 | 1.2609 | 88.9772 | 0.23512
11798 | 905.1493 | 4.3133 | 41.3552 | 89.3903 | -6.2967 | 7.6 | 136.223 | 1.3168 |  | 27.7842 | 57.441 | 14.8124 |  | 63.4939 | 154.4557 | 8.2441 | 25.9662 | 11.3832 | 209 | 20.0765 | 1.2557 | 86.2444 | 0.26237
11799 | 899.0285 | 3.1306 | 24.5127 | 89.4953 | -6.148 | 7.6 | 126.6242 | 1.1575 |  | 25.7619 | 57.2063 | 15.0125 |  | 66.6811 | 157.0819 | 8.1958 | 25.8754 | 6.5741 | 203 | 15.8092 | 1.2619 | 88.6382 | 0.24436
11800 | 880.3249 | 3.4258 | 23.0447 | 93.9394 | -6.1539 | 7.6 | 124.7566 | 1.0754 |  | 21.1249 | 57.0982 | 9.6472 |  | 63.3972 | 152.5912 | 8.2363 | 25.5177 | 4.7386 | 190 | 13.3986 | 1.249 | 84.7919 | 0.24008
11801 | 859.4465 | 7.595 | 24.655 | 96.1574 | -5.1513 | 6.6503 | 129.3582 | 1.301 |  | 18.3222 | 54.0382 | 5.2064 |  | 63.4575 | 153.8297 | 8.1396 | 25.8732 | 5.0701 | 188 | 18.9864 | 1.2601 | 82.6671 | 0.1507
11802 | 854.3063 | 13.7297 | 26.8541 | 94.8848 | -5.1859 | 6.65 | 129.6609 | 1.1609 |  | 16.5958 | 48.2707 | 4.2619 |  | 58.5201 | 150.2553 | 8.2011 | 25.3856 | 5.3621 | 228 | 24.6918 | 1.2489 | 78.5963 | 0.10391
11803 | 844.406 | 11.6613 | 26.7953 | 95.4001 | -6.0793 | 7.5997 | 133.6726 | 1.0843 |  | 14.3396 | 48.7648 | 4.0147 |  | 55.528 | 145.6897 | 7.924 | 25.1006 | 5.2021 | 218 | 26.5023 | 1.2491 | 79.7161 | 0.11398
11804 | 833.0983 | 13.1179 | 25.252 | 95.0398 | -5.0049 | 6.6503 | 112.0719 | 1.1127 |  | 12.7958 | 49.7839 | 3.7281 |  | 53.2123 | 143.646 | 8.1357 | 24.3889 | 5.143 | 265 | 27.9776 | 1.2609 | 78.9368 | 0.0042465
11805 | 824.6921 | 13.6361 | 25.2337 | 97.0568 | -6.0659 | 7.5997 | 104.0064 | 2.2651 |  | 12.9562 | 40.6819 | 5.2589 |  | 53.616 | 144.409 | 8.4756 | 24.5202 | 5.0398 | 228 | 28.0028 | 1.2523 | 72.5803 | 0
11806 | 825.3862 | 9.3854 | 25.4285 | 97.8558 | -7.0245 | 8.5497 | 94.305 | 2.3679 |  | 14.3868 | 34.8063 | 6.4683 |  | 54.5642 | 146.97 | 8.5727 | 25.0911 | 5.0419 | 212 | 27.7509 | 1.248 | 76.7042 | 0
11807 | 238.593 | 2.4836 | 6.7785 | 25.1604 | 0.73789 | 0.002376 | 26.3167 | 0.67141 |  | 4.5318 | 11.002 | 2.0131 |  | 14.6979 | 46.3569 | 2.2557 | 6.6079 | 1.5708 | 167 | 1.9834 | 0.14247 | 5.678 | 0
11808 | 849.0371 | 3.5897 | 23.4843 | 97.5187 | -7.2231 | 8.55 | 81.0518 | 2.4922 |  | 15.1227 | 35.0814 | 6.6911 |  | 50.138 | 141.3626 | 11.8851 | 25.9778 | 4.4241 | 167 | 32.795 | 1.2492 | 87.7652 | 0
11809 | 853.4417 | 3.2335 | 22.996 | 97.4928 | -7.9232 | 8.55 | 80.5453 | 2.9497 |  | 15.0288 | 35.9128 | 6.8408 |  | 52.8607 | 143.2932 | 12.8359 | 25.6829 | 4.4035 | 133 | 32.4944 | 1.2581 | 84.4865 | 0
11810 | 816.2213 | 2.5871 | 23.0101 | 95.8406 | -16.3652 | 16.1479 | 70.4708 | 2.2939 |  | 16.6166 | 36.1548 | 6.5139 |  | 49.9842 | 137.3212 | 13.03 | 25.5798 | 4.135 | 126 | 32.8962 | 1.2532 | 85.3562 | 0
11811 | 800.5317 | 2.4873 | 23.021 | 90.218 | -15.6 | 16.15 | 63.6637 | 2.8816 |  | 15.0485 | 34.9129 | 6.1655 |  | 46.9963 | 121.6174 | 12.9213 | 25.4702 | 4.2056 | 121 | 32.6713 | 1.2564 | 86.9341 | 0
11812 | 799.155 | 3.2989 | 22.9728 | 86.7597 | -12.0532 | 13.3008 | 56.865 | 2.5199 |  | 13.1015 | 33.3416 | 5.4168 |  | 40.9523 | 110.949 | 12.0517 | 26.8459 | 4.1765 | 97 | 34.7727 | 1.2603 | 85.1753 | 0
11813 | 804.6105 | 3.5485 | 22.5954 | 84.9423 | -9.1223 | 10.4508 | 57.4018 | 2.6693 |  | 11.6055 | 33.09 | 5.47 |  | 37.0621 | 108.7877 | 8.9889 | 27.6993 | 3.9702 | 96 | 40.916 | 1.2524 | 83.1033 | 0.011852
11814 | 817.6063 | 2.5109 | 22.4279 | 85.0017 | -7.9845 | 9.5003 | 75.7594 | 2.8369 |  | 11.0444 | 34.1609 | 4.0436 |  | 37.0938 | 106.4797 | 8.2601 | 25.6101 | 3.8823 | 92 | 29.2791 | 1.2587 | 82.5728 | 0.03171
11815 | 823.6667 | 1.9221 | 22.4883 | 84.5518 | -7.8545 | 9.5 | 73.2407 | 1.8051 |  | 11.0789 | 33.4816 | 3.3585 |  | 36.2665 | 107.1506 | 8.2558 | 24.6263 | 2.8342 | 97 | 28.1219 | 1.2584 | 83.5123 | 0.099593
11816 | 827.4136 | 2.4997 | 22.3917 | 84.4961 | -7.9265 | 8.5503 | 68.0546 | 1.4197 |  | 12.5829 | 35.0172 | 4.3598 |  | 38.1086 | 109.2192 | 8.3511 | 24.8698 | 2.6936 | 103 | 24.9724 | 1.2601 | 84.8265 | 0.18179
11817 | 843.0409 | 2.1764 | 22.3096 | 85.4807 | -8.1824 | 8.55 | 91.6 | 1.3904 |  | 16.645 | 37.4781 | 6.8326 |  | 41.3237 | 118.7442 | 8.3772 | 25.0078 | 3.1532 | 151 | 22.9871 | 1.2677 | 84.5944 | 0.14842
11818 | 870.4953 | 3.6439 | 22.3285 | 87.5828 | -7.8212 | 8.55 | 105.8916 | 1.3705 |  | 21.5183 | 43.1634 | 6.8002 |  | 47.9456 | 132.689 | 8.0825 | 25.3676 | 3.3566 | 141 | 23.1193 | 1.2555 | 88.3839 | 0.16821
11819 | 888.5244 | 5.6034 | 22.3242 | 88.3505 | -7.0309 | 7.6003 | 110.3207 | 1.5189 |  | 23.2556 | 47.4365 | 10.1035 |  | 59.5567 | 142.8903 | 8.2066 | 25.4591 | 3.3237 | 126 | 28.815 | 1.2666 | 84.3694 | 0.22947
11820 | 891.9167 | 3.6066 | 22.1473 | 89.3541 | -7.8464 | 8.5497 | 105.8325 | 1.4988 |  | 25.3443 | 53.7886 | 11.7993 |  | 66.2973 | 135.114 | 8.2949 | 25.426 | 3.8473 | 164 | 31.5604 | 1.2588 | 83.8166 | 0.21516
11821 | 890.5153 | 2.4623 | 22.2401 | 89.4593 | -7.9976 | 8.55 | 93.4469 | 1.2208 |  | 24.248 | 56.6177 | 7.1041 |  | 70.1227 | 132.2663 | 8.351 | 25.7608 | 4.2792 | 160 | 23.1343 | 1.265 | 84.3431 | 0.18116
11822 | 888.7459 | 3.2615 | 22.1475 | 89.7061 | -6.9905 | 7.6003 | 110.8013 | 1.0767 |  | 25.7578 | 57.4844 | 8.6349 |  | 73.2366 | 135.1461 | 8.2223 | 25.6961 | 4.1759 | 168 | 33.5026 | 1.2594 | 84.7408 | 0.16116
11823 | 920.5859 | 2.8932 | 22.4784 | 90.1907 | -8.1595 | 8.5497 | 120.3688 | 2.034 |  | 24.1094 | 64.8732 | 11.6468 |  | 63.6842 | 140.5123 | 8.1461 | 26.1793 | 4.3094 | 168 | 35.6812 | 1.258 | 85.2515 | 0.13969
11824 | 932.4804 | 4.4376 | 22.2497 | 92.1529 | -8.4547 | 8.55 | 102.8841 | 1.6965 |  | 17.826 | 74.1345 | 9.5145 |  | 63.8546 | 146.0659 | 8.1276 | 26.3037 | 5.2142 | 152 | 33.7599 | 1.2637 | 84.4413 | 0.11495
11825 | 924.1356 | 12.3754 | 22.1424 | 91.7188 | -8.4628 | 8.55 | 99.5502 | 2.2305 |  | 14.8808 | 61.6307 | 8.4853 |  | 63.3829 | 163.4535 | 8.3101 | 26.2732 | 5.6671 | 142 | 34.5222 | 1.2569 | 74.1845 | 0.10002
11826 | 908.6312 | 12.4758 | 22.1913 | 91.0859 | -9.1365 | 9.4997 | 94.6356 | 1.9564 |  | 14.5801 | 47.9922 | 8.2793 |  | 60.2243 | 164.0985 | 8.2574 | 25.8932 | 5.5173 | 109 | 37.5652 | 1.2608 | 75.8826 | 0.070186
11827 | 891.1941 | 6.9327 | 22.5154 | 87.0439 | -9.3028 | 9.5 | 103.7463 | 2.7798 |  | 14.8257 | 46.9614 | 8.014 |  | 56.2249 | 150.1611 | 8.3667 | 25.9192 | 5.0814 | 113 | 37.9607 | 1.2592 | 88.7384 | 0.021892
11828 | 867.1625 | 5.2621 | 22.8012 | 85.3416 | -10.4862 | 10.4497 | 94.9357 | 3.1366 |  | 14.2725 | 46.5538 | 6.122 |  | 53.5269 | 131.9361 | 8.1492 | 26.0182 | 4.9355 | 121 | 35.1803 | 1.2568 | 91.7358 | 0.0025936
11829 | 842.716 | 7.0633 | 23.296 | 86.8915 | -10.5837 | 10.45 | 93.4727 | 3.4246 |  | 15.9559 | 43.6642 | 6.2269 |  | 55.7633 | 129.7577 | 8.5237 | 26.3347 | 4.6394 | 117 | 37.0261 | 1.2643 | 93.1221 | 0
11830 | 823.6168 | 9.59 | 23.538 | 88.1924 | -10.5683 | 10.45 | 92.2371 | 3.0629 |  | 15.1027 | 37.967 | 6.6632 |  | 55.1211 | 128.2279 | 8.8812 | 26.1907 | 4.2288 | 111 | 35.0672 | 1.2581 | 94.7526 | 0
11831 | 235.6676 | 3.3932 | 6.2867 | 22.6966 | 0.17133 | 0.002903 | 26.5699 | 0.87055 |  | 4.361 | 11.536 | 2.0093 |  | 14.6646 | 39.6796 | 2.3519 | 6.8397 | 1.2706 | 99 | 2.4785 | 0.14147 | 6.3262 | 0
11832 | 816.4921 | 2.897 | 23.5417 | 87.6508 | -11.6377 | 11.3997 | 98.2807 | 3.6471 |  | 15.0785 | 34.9128 | 6.7214 |  | 49.3923 | 120.8547 | 9.4648 | 25.9717 | 4.1568 | 96 | 31.6506 | 1.2687 | 94.4653 | 0
11833 | 813.9939 | 3.0979 | 23.6755 | 87.0183 | -10.6375 | 10.4503 | 81.8465 | 4.1774 |  | 14.708 | 35.9694 | 6.4929 |  | 49.2282 | 117.2422 | 9.3854 | 25.7321 | 3.4433 | 94 | 31.8447 | 1.2646 | 95.4519 | 0
11834 | 781.9879 | 3.3104 | 23.6532 | 87.3115 | -11.6368 | 11.3997 | 76.0213 | 4.6159 |  | 14.6233 | 36.3323 | 6.4909 |  | 48.8882 | 120.6377 | 9.5322 | 25.5574 | 2.8134 | 105 | 32.9007 | 1.2623 | 97.9368 | 0
11835 | 776.4309 | 3.3047 | 24.2949 | 87.4677 | -11.6382 | 11.4 | 75.7063 | 4.6377 |  | 14.7483 | 35.8921 | 6.5462 |  | 48.2448 | 119.7223 | 9.57 | 25.6407 | 2.6652 | 101 | 33.5718 | 1.2626 | 101.5023 | 0
11836 | 785.9834 | 3.674 | 25.3355 | 88.2321 | -11.6397 | 11.4 | 75.2947 | 4.4623 |  | 13.6432 | 34.4986 | 5.6822 |  | 45.0885 | 113.5666 | 9.4912 | 26.3085 | 2.6136 | 93 | 31.7986 | 1.2637 | 115.3253 | 0
11837 | 798.8758 | 4.9175 | 36.3875 | 86.0869 | -11.6377 | 11.4 | 75.384 | 4.1301 |  | 15.0703 | 34.5905 | 6.5791 |  | 49.3225 | 114.9491 | 9.1771 | 27.3239 | 2.603 | 103 | 34.0984 | 1.2583 | 121.4147 | 0.013733
11838 | 831.2736 | 5.3936 | 54.2484 | 88.7423 | -13.64 | 13.2995 | 91.8852 | 3.5769 |  | 22.1346 | 40.6067 | 10.8072 |  | 76.386 | 135.9529 | 11.5681 | 25.6318 | 4.628 | 154 | 37.8846 | 1.2677 | 130.2416 | 0.039589
11839 | 891.75 | 9.0059 | 82.0829 | 96.8023 | -18.3569 | 18.0487 | 113.1871 | 3.5562 |  | 29.2186 | 61.1022 | 23.8711 |  | 103.3288 | 183.4102 | 26.8726 | 27.3968 | 7.8558 | 253 | 51.0816 | 1.521 | 150.3672 | 0.055606
11840 | 1001.2493 | 10.6626 | 102.4317 | 105.547 | -18.4593 | 18.03 | 132.0394 | 5.5308 |  | 33.5636 | 77.6959 | 32.1405 |  | 132.399 | 246.4781 | 35.5984 | 32.2727 | 14.9422 | 283 | 56.7016 | 1.772 | 180.6349 | 0.076858
11841 | 1106.074 | 8.1369 | 105.5989 | 119.7491 | -18.6643 | 18.07 | 149.5919 | 6.3883 |  | 43.7041 | 88.7948 | 33.4933 |  | 154.4396 | 286.5929 | 38.2551 | 37.3707 | 16.7833 | 322 | 62.1968 | 1.8053 | 197.2373 | 0.10799
11842 | 1175.81 | 5.9648 | 106.2018 | 124.238 | -19.6465 | 18.9997 | 153.1152 | 5.4965 |  | 44.9564 | 92.8121 | 32.0618 |  | 168.1328 | 306.9578 | 40.3638 | 40.6799 | 17.6522 | 281 | 57.0112 | 1.7763 | 197.1039 | 0.12423
11843 | 1206.5676 | 5.4273 | 109.0623 | 130.5325 | -20.5184 | 19.9497 | 155.4165 | 5.2379 |  | 45.4194 | 93.1447 | 32.7803 |  | 178.5004 | 315.8651 | 40.7374 | 41.8911 | 18.3157 | 300 | 63.9933 | 1.7605 | 199.3391 | 0.1329
11844 | 1194.6393 | 5.1953 | 109.6164 | 127.0621 | -21.5084 | 20.8997 | 156.5112 | 6.2598 |  | 43.4689 | 94.5534 | 37.0966 |  | 175.6983 | 316.6556 | 40.0501 | 40.0532 | 18.5995 | 329 | 59.0124 | 1.7715 | 203.9385 | 0.12998
11845 | 1199.5054 | 5.2155 | 111.8051 | 129.5995 | -19.6091 | 19.0005 | 157.341 | 5.2138 |  | 43.3341 | 95.8745 | 40.5972 |  | 176.5734 | 305.9514 | 41.0044 | 40.0392 | 19.468 | 280 | 60.6024 | 1.7646 | 208.4166 | 0.12617
11846 | 1215.0743 | 5.4222 | 110.7117 | 133.9105 | -18.6447 | 18.0503 | 156.9501 | 5.2674 |  | 43.4758 | 96.1324 | 39.1133 |  | 177.1648 | 302.0815 | 40.4936 | 39.7817 | 19.8704 | 259 | 59.7423 | 1.7639 | 203.6132 | 0.12633
11847 | 1182.493 | 8.9039 | 110.4133 | 132.8592 | -19.4542 | 19.005 | 149.9189 | 5.5139 |  | 40.8642 | 95.0947 | 36.511 |  | 175.1438 | 292.7938 | 38.4219 | 39.1236 | 19.3435 | 291 | 56.648 | 1.6168 | 202.5718 | 0.10668
11848 | 1151.9563 | 7.0264 | 106.9515 | 129.9372 | -13.7585 | 14.246 | 139.6085 | 4.1961 |  | 37.4822 | 94.3471 | 35.335 |  | 163.179 | 265.4797 | 30.8688 | 37.4401 | 18.6876 | 241 | 52.5995 | 1.2622 | 173.3422 | 0.094523
11849 | 1115.4147 | 5.0809 | 102.7023 | 112.109 | -12.0459 | 13.304 | 126.0577 | 4.1296 |  | 32.3143 | 85.1613 | 34.4383 |  | 125.113 | 234.742 | 16.8782 | 33.9263 | 18.1347 | 200 | 46.8119 | 1.2213 | 132.8076 | 0.075912
11850 | 1060.6221 | 4.5609 | 97.5285 | 99.5427 | -9.6724 | 11.3968 | 116.6449 | 4.5021 |  | 26.8613 | 67.2669 | 27.8778 |  | 99.0746 | 210.678 | 10.861 | 31.5668 | 14.6758 | 204 | 45.5751 | 1.2267 | 119.7561 | 0.059582
11851 | 1020.1156 | 4.0168 | 82.6844 | 98.5304 | -12.1565 | 13.2995 | 103.8002 | 4.4219 |  | 23.4238 | 60.4754 | 12.2059 |  | 91.0397 | 180.4166 | 9.4032 | 29.5384 | 7.651 | 193 | 43.664 | 1.2026 | 101.2908 | 0.020953
11852 | 991.6016 | 4.5383 | 39.4298 | 93.2383 | -11.2404 | 12.3503 | 110.3359 | 3.7293 |  | 20.4153 | 58.4419 | 6.3378 |  | 69.7001 | 156.4172 | 9.3057 | 27.6847 | 5.3804 | 170 | 42.7489 | 1.2179 | 98.2043 | 0.0032558
11853 | 975.2518 | 4.537 | 23.2696 | 90.4007 | -12.0818 | 12.35 | 108.0605 | 3.6056 |  | 17.5507 | 50.962 | 7.9113 |  | 55.8737 | 143.6665 | 9.1002 | 27.6886 | 5.3345 | 156 | 40.0951 | 1.2389 | 96.0625 | 0
11854 | 950.9035 | 3.6906 | 22.3632 | 88.7758 | -11.2933 | 11.4003 | 99.3012 | 4.1647 |  | 18.5456 | 41.1478 | 9.07 |  | 50.4728 | 136.5553 | 9.9026 | 27.1382 | 5.5234 | 134 | 36.5908 | 1.2157 | 97.1414 | 0
11855 | 266.59 | 1.0773 | 5.8583 | 22.3735 | 0.3188 | 0.003167 | 27.7585 | 1.3148 |  | 5.757 | 12.0412 | 2.7289 |  | 13.0435 | 41.4062 | 2.6715 | 6.9329 | 1.7101 | 114 | 2.82 | 0.13778 | 8.7097 | 0
11856 | 913.9524 | 2.4767 | 22.2281 | 91.1942 | -11.2631 | 11.4 | 92.4689 | 4.6867 |  | 17.3345 | 37.8169 | 9.2796 |  | 41.7794 | 116.962 | 10.6914 | 26.5924 | 4.4661 | 97 | 34.2279 | 1.2233 | 96.8291 | 0
11857 | 912.8813 | 2.339 | 22.2267 | 95.1103 | -11.4515 | 11.4 | 87.8498 | 5.1324 |  | 15.6076 | 39.0097 | 8.7334 |  | 39.9274 | 114.4881 | 10.462 | 26.842 | 4.0389 | 95 | 32.6761 | 1.2174 | 98.8754 | 0
11858 | 893.7445 | 2.4884 | 17.777 | 96.298 | -12.6313 | 12.3497 | 78.1625 | 5.2153 |  | 14.9581 | 39.6581 | 8.6986 |  | 39.4226 | 121.1882 | 10.2137 | 26.5131 | 3.3506 | 100 | -43.5574 | 1.2256 | 100.7223 | 0
11859 | 887.206 | 2.4216 | 16.0715 | 95.261 | -11.6309 | 11.4003 | 67.3201 | 5.1246 |  | 14.8948 | 40.3202 | 8.6763 |  | 39.0115 | 124.2022 | 10.403 | 26.294 | 2.6174 | 97 | 34.3164 | 1.2196 | 104.9835 | 0
11860 | 893.4173 | 2.7969 | 16.0451 | 88.8639 | -12.4993 | 12.3497 | 72.3048 | 4.9683 |  | 13.9238 | 39.2812 | 7.9417 |  | 39.131 | 118.2198 | 10.2187 | 27.1478 | 2.3659 | 95 | 31.952 | 1.2239 | 112.2098 | 0
11861 | 909.4135 | 3.3518 | 31.2231 | 86.344 | -11.5634 | 11.4003 | 80.8448 | 4.6488 |  | 18.6641 | 37.4438 | 7.3855 |  | 43.7309 | 116.2593 | 10.0565 | 28.0085 | 2.234 | 98 | 30.1133 | 1.2211 | 121.6736 | 0.016595
11862 | 948.3825 | 4.5443 | 51.0823 | 90.3839 | -15.3859 | 15.1989 | 87.62 | 2.9772 |  | 28.1884 | 43.1105 | 13.0253 |  | 77.6513 | 125.9166 | 12.4415 | 26.3646 | 2.2637 | 165 | 31.7387 | 1.2225 | 134.1289 | 0.030086
11863 | 989.3861 | 7.3929 | 76.2178 | 96.2308 | -17.5006 | 17.0995 | 109.4665 | 4.3133 |  | 33.0494 | 68.8349 | 28.3006 |  | 114.4058 | 167.4096 | 26.7892 | 28.5741 | 5.5965 | 229 | 47.4764 | 1.3765 | 143.139 | 0.11086
11864 | 1067.1904 | 11.658 | 95.3032 | 111.433 | -19.5812 | 18.9995 | 134.3598 | 6.3223 |  | 33.8027 | 86.7536 | 32.0421 |  | 144.409 | 235.0843 | 35.6546 | 33.1421 | 13.6924 | 283 | 55.1792 | 1.7243 | 174.152 | 0.25007
11865 | 1155.5975 | 14.2577 | 108.6815 | 124.3294 | -20.6096 | 19.9497 | 144.9047 | 7.0244 |  | 39.0926 | 94.1282 | 34.6518 |  | 163.2706 | 286.7222 | 40.2106 | 36.0402 | 17.2345 | 351 | 59.9135 | 1.7721 | 188.5866 | 0.22675
11866 | 1222.0198 | 12.7835 | 111.811 | 129.1785 | -17.643 | 17.1008 | 142.7756 | 6.325 |  | 42.8578 | 96.0908 | 38.908 |  | 172.9726 | 306.7321 | 42.2261 | 38.9332 | 18.2121 | 339 | 63.3863 | 1.9613 | 193.5469 | 0.2295
11867 | 1252.0213 | 14.8784 | 114.1057 | 129.3101 | -18.6393 | 18.0497 | 155.2698 | 6.6769 |  | 45.474 | 94.5329 | 38.696 |  | 180.7876 | 311.6831 | 42.8148 | 39.9096 | 18.6754 | 328 | 69.5892 | 2.7751 | 194.2584 | 0.2897
11868 | 1226.473 | 14.5592 | 113.1367 | 127.9674 | -18.6398 | 18.05 | 160.7187 | 6.1007 |  | 42.2323 | 95.3033 | 37.3449 |  | 177.2365 | 309.5966 | 42.9592 | 38.6654 | 19.0208 | 331 | 54.8435 | 2.8029 | 199.195 | 0.2871
11869 | 1223.0936 | 18.9208 | 113.1215 | 133.7871 | -20.6423 | 19.9495 | 155.99 | 6.6463 |  | 40.4771 | 98.0891 | 38.2616 |  | 177.1455 | 303.1821 | 43.7082 | 39.8571 | 19.1392 | 299 | 60.6062 | 2.9411 | 191.341 | 0.29595
11870 | 1244.7332 | 20.1662 | 111.3096 | 139.0643 | -21.6412 | 20.8997 | 154.9955 | 7.2439 |  | 40.7659 | 100.0907 | 38.4697 |  | 176.7879 | 303.5389 | 42.3138 | 40.0515 | 19.0284 | 290 | 60.7466 | 2.8236 | 192.3174 | 0.28056
11871 | 1219.8805 | 12.9071 | 107.6471 | 133.0172 | -19.4519 | 19.0005 | 154.8486 | 5.4082 |  | 39.2782 | 99.0658 | 36.1107 |  | 171.6671 | 291.6318 | 39.3074 | 39.6253 | 18.1874 | 254 | 56.4099 | 2.6746 | 189.6061 | 0.23977
11872 | 1193.4681 | 7.027 | 103.2401 | 128.3272 | -16.8334 | 17.1005 | 143.4848 | 5.2203 |  | 34.2707 | 95.8132 | 33.8427 |  | 159.6983 | 251.4759 | 31.4524 | 39.5389 | 17.6965 | 239 | 48.9631 | 1.8705 | 167.9976 | 0.21475
11873 | 1149.3371 | 5.3215 | 96.8949 | 113.1964 | -9.2208 | 10.4518 | 128.3065 | 4.4293 |  | 26.3372 | 84.2091 | 32.069 |  | 133.5524 | 214.8692 | 16.5571 | 34.9743 | 17.1183 | 203 | 40.6674 | 1.7288 | 119.3822 | 0.20982
11874 | 1108.7616 | 7.8225 | 93.7373 | 99.441 | -9.7561 | 10.45 | 118.2805 | 4.5773 |  | 20.6066 | 68.9784 | 27.9156 |  | 95.8754 | 191.1078 | 11.3682 | 31.9084 | 14.001 | 196 | 44.7268 | 1.7842 | 117.095 | 0.23285
11875 | 1042.7849 | 7.0886 | 77.2034 | 94.3132 | -11.4644 | 11.3997 | 110.1214 | 4.4736 |  | 18.9155 | 61.5658 | 18.2095 |  | 75.6497 | 172.7374 | 10.1064 | 28.6859 | 7.7715 | 180 | 43.3344 | 1.771 | 97.8576 | 0.15831
11876 | 993.1405 | 6.3325 | 33.0937 | 91.3991 | -11.6365 | 11.4 | 110.5883 | 3.632 |  | 16.8383 | 56.552 | 9.7415 |  | 65.4231 | 149.1971 | 9.5706 | 27.0545 | 5.1643 | 167 | 43.38 | 1.7582 | 96.4114 | 0.023559
11877 | 976.7703 | 4.9918 | 17.0809 | 88.7443 | -11.6371 | 11.4 | 102.8317 | 3.4783 |  | 14.3943 | 48.2659 | 9.6007 |  | 62.6598 | 144.2002 | 9.6359 | 26.7344 | 4.4851 | 158 | 40.7515 | 1.7684 | 91.3275 | 0
11878 | 965.2404 | 4.1667 | 16.6942 | 88.7597 | -12.631 | 12.3497 | 99.8934 | 3.4516 |  | 13.0621 | 40.8012 | 11.3516 |  | 63.1607 | 141.9745 | 9.9756 | 27.6397 | 4.0508 | 127 | 36.9581 | 1.7595 | 94.1074 | 0
11879 | 278.8754 | 1.3507 | 4.5148 | 23.1689 | 0.13663 | 0.003431 | 29.4468 | 1.0506 |  | 3.9041 | 12.5357 | 3.5491 |  | 17.2028 | 44.1325 | 2.6954 | 7.4009 | 1.2332 | 109 | 2.904 | 0.20907 | 8.5687 | 0
11880 | 932.3386 | 2.4063 | 16.5384 | 87.9117 | -10.6389 | 10.4505 | 85.1201 | 4.4835 |  | 12.2702 | 36.5911 | 6.0517 |  | 56.948 | 134.1379 | 10.6645 | 26.5957 | 2.9641 | 102 | 34.0753 | 1.7609 | 91.4558 | 0
11881 | 923.38 | 2.3776 | 16.5825 | 87.4058 | -12.6347 | 12.3495 | 79.1954 | 4.8378 |  | 12.2054 | 36.1346 | 5.9514 |  | 52.3762 | 127.3823 | 10.6943 | 26.6531 | 2.5581 | 99 | 33.2171 | 1.7656 | 94.2597 | 0
11882 | 905.8854 | 2.7245 | 16.6123 | 87.9085 | -11.6355 | 11.4003 | 70.0377 | 4.7184 |  | 12.2521 | 36.0962 | 5.934 |  | 51.2025 | 124.5795 | 10.6762 | 26.5673 | 2.5303 | 99 | 32.4927 | 1.7758 | 96.739 | 0
11883 | 897.6222 | 2.752 | 16.5732 | 88.8256 | -12.6359 | 12.3497 | 72.7913 | 4.688 |  | 12.1678 | 36.1033 | 5.9187 |  | 51.8254 | 121.0348 | 10.4516 | 26.2532 | 2.5247 | 99 | 31.6772 | 1.7669 | 99.0703 | 0
11884 | 900.0173 | 2.9755 | 16.4079 | 88.1691 | -11.6362 | 11.4003 | 76.9674 | 4.7198 |  | 14.5346 | 35.349 | 5.6771 |  | 51.316 | 115.632 | 10.4355 | 26.86 | 2.4978 | 107 | 31.5163 | 1.7765 | 104.2812 | 0
11885 | 901.4895 | 3.852 | 30.817 | 85.3757 | -11.636 | 11.4 | 79.3552 | 4.3903 |  | 19.7267 | 34.7144 | 7.3447 |  | 52.807 | 116.1748 | 10.1957 | 27.7409 | 2.3718 | 121 | 33.6609 | 1.774 | 118.8043 | 0.011586
11886 | 929.7988 | 7.1813 | 52.2698 | 85.9086 | -21.638 | 20.8974 | 86.2972 | 3.2124 |  | 30.5955 | 41.3063 | 11.3301 |  | 88.5406 | 127.6784 | 12.8371 | 26.5476 | 2.3059 | 185 | 38.1301 | 1.7801 | 131.2934 | 0.031787
11887 | 980.9224 | 14.7192 | 77.7364 | 92.2339 | -22.3285 | 21.8497 | 112.2381 | 4.0323 |  | 37.9245 | 67.0653 | 23.6431 |  | 116.576 | 173.0868 | 25.9496 | 28.9994 | 5.2311 | 271 | 47.2293 | 1.7674 | 132.9138 | 0.051528
11888 | 1063.4647 | 18.6466 | 101.2868 | 109.9946 | -21.8177 | 21.85 | 139.0649 | 5.5924 |  | 44.7267 | 85.7207 | 29.8008 |  | 139.2113 | 240.1648 | 35.2067 | 34.1017 | 13.3242 | 300 | 50.6195 | 1.7381 | 168.4737 | 0.077003
11889 | 1157.4957 | 16.6778 | 111.1274 | 121.9351 | -19.9464 | 19.9505 | 152.511 | 4.791 |  | 43.7507 | 93.3882 | 32.5731 |  | 158.0933 | 288.3754 | 37.8181 | 38.045 | 17.8811 | 327 | 59.2619 | 1.7325 | 182.0018 | 0.12731
11890 | 1200.9981 | 12.0892 | 109.5408 | 127.963 | -21.3209 | 21.8495 | 154.9689 | 5.2993 |  | 50.6502 | 97.1822 | 32.2376 |  | 170.5416 | 310.6417 | 39.6558 | 38.9716 | 17.4498 | 351 | 69.2858 | 1.7249 | 182.2823 | 0.14553
11891 | 1199.4114 | 7.1344 | 112.9688 | 131.4136 | -19.2576 | 19.9505 | 148.9666 | 4.6274 |  | 47.1336 | 96.6972 | 27.6819 |  | 181.5928 | 313.6369 | 40.2657 | 39.2548 | 17.7894 | 313 | 75.258 | 2.3941 | 188.4719 | 0.17309
11892 | 1201.2039 | 5.4882 | 111.0764 | 128.061 | -20.1977 | 20.8997 | 144.1245 | 5.4968 |  | 42.8338 | 95.7101 | 29.8656 |  | 177.6803 | 299.6271 | 40.9044 | 39.1504 | 17.9063 | 328 | 65.284 | 2.4688 | 196.8895 | 0.12279
11893 | 1212.0107 | 5.5622 | 106.9955 | 135.888 | -20.6891 | 21.8497 | 141.71 | 5.576 |  | 39.5083 | 96.4307 | 34.4462 |  | 177.465 | 302.319 | 42.4837 | 41.2515 | 18.1722 | 259 | 67.9637 | 3.0479 | 193.9948 | 0.1208
11894 | 1206.9749 | 5.5089 | 111.5204 | 138.1053 | -19.4098 | 20.9003 | 141.722 | 6.1894 |  | 37.5114 | 98.0776 | 35.6348 |  | 175.7366 | 303.3429 | 41.9412 | 43.4183 | 18.8566 | 249 | 72.5885 | 3.603 | 192.2055 | 0.11354
11895 | 1191.5488 | 7.7261 | 111.2009 | 134.8688 | -22.3873 | 23.7492 | 139.9853 | 5.3138 |  | 33.3158 | 97.0178 | 37.809 |  | 170.7251 | 298.5091 | 40.266 | 51.5831 | 18.9569 | 237 | 69.3387 | 3.309 | 191.2397 | 0.13745
11896 | 1154.8453 | 7.4456 | 106.3506 | 126.4787 | -14.5407 | 16.1521 | 135.4629 | 5.1571 |  | 34.5276 | 93.5949 | 37.1192 |  | 156.1415 | 270.2703 | 34.8455 | 46.9225 | 18.4495 | 237 | 59.9002 | 2.5343 | 170.5328 | 0.11236
11897 | 1115.8509 | 5.1444 | 103.3397 | 111.6647 | -12.7382 | 14.2505 | 129.8093 | 4.6532 |  | 35.2469 | 85.2473 | 36.2576 |  | 125.2632 | 233.3604 | 19.5886 | 37.5326 | 17.5871 | 184 | 49.8278 | 2.398 | 125.5022 | 0.059417
11898 | 1084.4961 | 4.4623 | 100.0807 | 96.7385 | -12.8956 | 14.25 | 123.3978 | 3.3481 |  | 31.8895 | 70.8955 | 32.0241 |  | 91.9725 | 205.8575 | 11.3287 | 33.8168 | 14.2948 | 177 | 51.2118 | 2.4709 | 127.8422 | 0.042527
11899 | 1030.3712 | 4.4413 | 79.9514 | 89.3626 | -13.4357 | 14.25 | 113.6869 | 3.4787 |  | 25.2286 | 63.9583 | 20.3583 |  | 71.5305 | 187.8678 | 10.0211 | 30.9702 | 8.2809 | 155 | 51.2092 | 2.4583 | 113.803 | 0.048291
11900 | 988.5364 | 4.9944 | 34.5757 | 86.7178 | -13.4672 | 14.25 | 109.693 | 3.6685 |  | 20.6802 | 60.5223 | 16.1767 |  | 54.5026 | 172.6561 | 9.9922 | 28.6807 | 5.6651 | 159 | 47.6077 | 2.4664 | 101.9915 | 0.0059465
11901 | 970.2457 | 4.8317 | 18.5853 | 86.3221 | -11.8105 | 12.3505 | 106.0758 | 3.9914 |  | 15.2158 | 54.2618 | 17.2278 |  | 48.8786 | 156.5838 | 10.2328 | 27.7561 | 5.4996 | 149 | 43.2902 | 2.464 | 108.7942 | 0
11902 | 946.184 | 4.051 | 17.9574 | 87.3177 | -11.7613 | 12.35 | 96.0976 | 4.4773 |  | 12.8271 | 46.5282 | 16.9107 |  | 48.1678 | 144.0305 | 10.197 | 27.0601 | 5.119 | 137 | 38.3994 | 2.4674 | 108.6372 | 0
11903 | 275.6585 | 1.2557 | 4.8796 | 23.0338 | 0.52435 | 0.003431 | 27.5734 | 1.4474 |  | 3.9238 | 14.4552 | 5.0848 |  | 13.1318 | 44.9343 | 2.7451 | 7.1728 | 1.5566 | 112 | 3.0704 | 0.29486 | 10.1254 | 0
11904 | 909.749 | 2.6476 | 17.9736 | 86.3321 | -10.9303 | 11.4 | 78.7909 | 4.563 |  | 12.0366 | 41.5371 | 12.7121 |  | 46.7207 | 136.4984 | 10.121 | 26.5163 | 4.1673 | 104 | 34.8224 | 2.469 | 107.2172 | 0
11905 | 910.759 | 3.3217 | 18.2741 | 86.3489 | -9.6088 | 10.4503 | 86.5402 | 4.418 |  | 12.2507 | 40.6597 | 12.0259 |  | 44.9546 | 131.7004 | 10.3398 | 26.496 | 3.1539 | 100 | 34.691 | 2.4768 | 106.0021 | 0
11906 | 901.4473 | 8.425 | 18.4685 | 86.5051 | -10.1045 | 10.45 | 92.7866 | 4.3239 |  | 12.5843 | 40.1631 | 12.0254 |  | 41.9967 | 133.2999 | 10.3392 | 26.8236 | 2.5707 | 97 | 39.6163 | 2.4752 | 105.461 | 0
11907 | 896.6234 | 10.2713 | 18.1428 | 86.3552 | -10.821 | 10.45 | 77.3795 | 4.6126 |  | 12.5516 | 39.9577 | 12.0371 |  | 42.2978 | 128.0877 | 10.4281 | 26.694 | 2.4205 | 98 | 38.3897 | 2.4812 | 106.9153 | 0
11908 | 264.9686 | 3.3535 | 4.9391 | 22.7348 | -0.003056 | 0.002903 | 21.1706 | 1.4922 |  | 3.8927 | 13.1824 | 3.7144 |  | 11.7933 | 40.138 | 2.8708 | 7.1702 | 0.7629 | 95 | 2.9944 | 0.29103 | 8.404 | 0
11909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0.025473
11910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0.060872
11911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 0.063387
11912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0.14386
11913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0.18173
11914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0.10897
11915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0.1432
11916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0.16905
11917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0.20264
11918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0.13954
11919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0.18712
11920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0.080633
11921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0.060134
11922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0.039293
11923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0.056156
11924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0.0079934
11925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0
11926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0
11927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0
11928 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0
11929 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0
11930 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0
11931 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0
11932 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0
11933 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0.018995
11934 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0.073094
11935 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0.087367
11936 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0.1316
11937 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0.098321
11938 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0.17537
11939 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0.12066
11940 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0.17916
11941 | 1057.1781 | 0 | 0 | 0 | -14.9744 | 14.2257 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0.12143
11942 | 1180.9595 | 7.8036 | 102.2252 | 131.2467 | -20.6614 | 21.8597 | 149.8391 | 4.5696 |  | 38.6157 | 90.9086 | 28.2084 |  | 153.7483 | 260.2038 | 30.2673 | 38.6733 | 16.5033 | 283 | 51.3765 | 3.7035 | 190.0483 | 0.13302
11943 | 1190.0931 | 5.9415 | 111.1875 | 129.7864 | -19.2903 | 19.9505 | 156.7254 | 5.4226 |  | 37.8262 | 98.781 | 28.8766 |  | 161.2986 | 277.4137 | 31.3604 | 39.5223 | 19.2399 | 260 | 49.6964 | 3.1819 | 178.4681 | 0.12359
11944 | 1127.5098 | 5.0468 | 105.7279 | 115.6433 | -11.4106 | 11.4024 | 144.3237 | 4.2376 |  | 33.0186 | 93.5807 | 23.6695 |  | 145.4035 | 238.2806 | 28.2911 | 37.4378 | 19.3397 | 242 | 43.2099 | 2.5417 | 156.6572 | 0.24146
11945 | 1095.5218 | 4.6964 | 91.3461 | 107.3316 | -8.6385 | 8.5508 | 144.0552 | 2.3539 |  | 30.7434 | 84.1435 | 22.4573 |  | 112.008 | 209.2624 | 18.4349 | 34.5661 | 19.0239 | 234 | 32.5425 | 2.4354 | 119.0344 | 0.27653
11946 | 1044.7762 | 4.2372 | 43.3012 | 96.0936 | -8.4934 | 8.55 | 134.1834 | 1.4242 |  | 23.0088 | 66.2355 | 23.1283 |  | 77.8741 | 194.656 | 14.5615 | 31.6059 | 15.7788 | 217 | 35.3698 | 2.4984 | 107.9162 | 0.26359
11947 | 1003.8815 | 8.2563 | 25.2125 | 89.7251 | -6.5633 | 6.6505 | 110.719 | 2.4353 |  | 19.1445 | 55.671 | 21.2424 |  | 63.6985 | 177.5659 | 13.9201 | 28.7802 | 9.511 | 207 | 35.9648 | 2.4673 | 93.5875 | 0.023425
11948 | 984.4714 | 8.4976 | 23.683 | 86.8333 | -7.642 | 7.6018 | 94.4238 | 1.8979 |  | 17.2543 | 42.9417 | 20.359 |  | 55.0503 | 158.4823 | 12.5611 | 27.1416 | 7.5766 | 206 | 40.6222 | 2.4703 | 91.0447 | 0.0035869
11949 | 947.2893 | 7.5609 | 23.763 | 86.4997 | -8.6355 | 8.5476 | 83.7199 | 2.6817 |  | 13.5496 | 38.1259 | 13.3363 |  | 50.9409 | 146.2665 | 21.9243 | 27.1564 | 7.2649 | 204 | 39.5134 | 2.4641 | 89.6156 | 0
11950 | 920.7172 | 12.8808 | 23.7532 | 86.0012 | -7.6406 | 7.6024 | 94.0447 | 3.6613 |  | 13.6551 | 37.9872 | 11.2013 |  | 50.632 | 141.1038 | 17.1691 | 27.3726 | 7.2065 | 179 | 37.485 | 2.4676 | 93.3862 | 0
11951 | 261.1619 | 4.9853 | 6.2947 | 21.8267 | 0.13414 | 0 | 28.7449 | 1.1668 |  | 4.2871 | 12.058 | 3.4393 |  | 13.5689 | 43.3407 | 3.723 | 7.1512 | 2.2199 | 158 | 2.7802 | 0.28392 | 5.5159 | 0
11952 | 902.704 | 14.3233 | 24.2947 | 85.8488 | -8.6352 | 8.5503 | 95.0847 | 2.4642 |  | 13.7245 | 37.2896 | 7.1372 |  | 47.4761 | 138.4115 | 10.0456 | 26.8594 | 5.7949 | 137 | 33.0564 | 2.4706 | 92.4936 | 0
11953 | 889.743 | 10.6754 | 24.3504 | 85.6764 | -9.6343 | 9.4997 | 95.534 | 3.2141 |  | 13.5188 | 37.1579 | 6.3817 |  | 43.2574 | 133.9092 | 9.394 | 26.205 | 5.035 | 133 | 35.4884 | 2.475 | 94.3198 | 0
11954 | 870.9846 | 9.6853 | 24.3598 | 85.3865 | -9.6319 | 9.5 | 86.1859 | 4.0597 |  | 12.8138 | 37.6114 | 6.3013 |  | 40.8012 | 129.3107 | 9.3172 | 26.0929 | 4.4429 | 130 | 34.6536 | 2.4718 | 94.8473 | 0
11955 | 871.8355 | 5.9852 | 24.1824 | 85.5835 | -10.6327 | 10.4497 | 81.5143 | 4.1142 |  | 12.5662 | 36.9488 | 6.3308 |  | 38.9557 | 126.5519 | 9.5736 | 26.0233 | 4.3214 | 125 | 34.5997 | 2.479 | 99.5144 | 0
11956 | 873.5979 | 3.4489 | 24.1629 | 84.7366 | -9.6349 | 9.5003 | 80.7431 | 3.9284 |  | 11.3485 | 35.2756 | 5.5099 |  | 38.1583 | 119.1183 | 9.2187 | 26.7439 | 4.2188 | 119 | 37.4986 | 2.4761 | 97.7908 | 0
11957 | 869.5361 | 3.5039 | 25.7218 | 83.1993 | -9.6372 | 9.5 | 79.7394 | 3.575 |  | 9.8293 | 34.2974 | 3.9839 |  | 35.9735 | 110.2551 | 8.9055 | 27.919 | 3.0607 | 105 | 34.8944 | 2.4761 | 98.2014 | 0.015126
11958 | 883.2246 | 2.6395 | 51.6917 | 82.8972 | -9.639 | 9.5 | 79.2612 | 2.6902 |  | 9.5148 | 34.417 | 3.4184 |  | 35.8264 | 109.5767 | 8.6782 | 25.8817 | 2.5732 | 110 | 32.2077 | 2.4866 | 100.9224 | 0.034646
11959 | 886.1454 | 2.9464 | 61.223 | 82.9233 | -8.6408 | 8.5503 | 84.1511 | 2.4687 |  | 9.4969 | 35.1013 | 5.3367 |  | 36.9684 | 110.3813 | 9.281 | 25.034 | 2.5885 | 108 | 40.7957 | 2.4791 | 100.2493 | 0.062643
11960 | 890.9767 | 3.6621 | 62.2917 | 82.5268 | -8.6416 | 8.55 | 91.4473 | 3.0887 |  | 13.4158 | 37.972 | 11.3282 |  | 39.3207 | 110.5254 | 12.157 | 25.0347 | 2.6378 | 126 | 58.3242 | 2.4861 | 100.2819 | 0.082268
11961 | 920.802 | 3.2914 | 75.4296 | 82.5072 | -9.6393 | 9.4997 | 98.9331 | 2.6813 |  | 21.2146 | 43.5591 | 13.5799 |  | 48.1935 | 120.2549 | 12.8033 | 25.5295 | 4.946 | 123 | 59.3591 | 2.496 | 102.2531 | 0.11241
11962 | 949.0075 | 2.9655 | 83.7382 | 83.2152 | -7.4483 | 7.6005 | 101.2996 | 3.0481 |  | 30.4685 | 47.3275 | 16.359 |  | 55.6023 | 131.8742 | 12.2616 | 25.582 | 10.3172 | 160 | 63.2934 | 2.4912 | 101.4693 | 0.22123
11963 | 958.3682 | 5.3896 | 84.744 | 83.5352 | -8.283 | 8.5497 | 101.7526 | 3.0868 |  | 32.0728 | 49.8559 | 17.8786 |  | 60.6454 | 139.5789 | 13.9015 | 25.8034 | 12.1326 | 157 | 64.4065 | 2.4928 | 99.0916 | 0.23441
11964 | 967.9068 | 8.3935 | 86.8726 | 84.2208 | -7.5005 | 7.6003 | 91.3619 | 2.1062 |  | 33.4323 | 55.2408 | 15.4217 |  | 71.9697 | 141.9421 | 20.3618 | 25.6733 | 12.0145 | 161 | 66.9675 | 2.5014 | 98.9094 | 0.15446
11965 | 965.7476 | 10.0926 | 80.708 | 83.4848 | -8.6441 | 8.5497 | 94.7097 | 2.9713 |  | 35.7135 | 58.1085 | 13.755 |  | 83.8693 | 139.5238 | 15.018 | 25.5836 | 12.5246 | 159 | 67.1773 | 2.4966 | 99.079 | 0.1348
11966 | 955.8042 | 10.736 | 49.3357 | 84.0805 | -8.3867 | 8.55 | 115.4354 | 3.0058 |  | 35.21 | 59.99 | 14.3572 |  | 81.1185 | 146.001 | 12.1999 | 25.8405 | 10.5036 | 186 | 63.8927 | 2.4882 | 95.9362 | 0.15869
11967 | 957.4302 | 10.3008 | 34.7647 | 85.4308 | -7.1691 | 7.6003 | 125.964 | 3.7226 |  | 29.5121 | 59.6749 | 14.1656 |  | 67.0123 | 148.8339 | 11.5874 | 26.131 | 5.4023 | 189 | 57.551 | 2.4878 | 92.8402 | 0.13916
11968 | 953.5566 | 10.6378 | 34.1087 | 84.7823 | -7.2868 | 7.6 | 109.2566 | 3.2887 |  | 21.726 | 58.8933 | 6.7369 |  | 61.7968 | 154.4135 | 9.8146 | 26.4499 | 3.3409 | 184 | 46.1691 | 2.4879 | 90.9416 | 0.11471
11969 | 931.7289 | 10.7011 | 33.8175 | 83.5212 | -6.1083 | 6.6503 | 108.9106 | 3.6899 |  | 19.3079 | 56.5593 | 3.5823 |  | 63.6011 | 155.0899 | 9.128 | 25.9411 | 3.7683 | 204 | 41.2907 | 2.4539 | 90.6604 | 0.062337
11970 | 938.279 | 9.8906 | 33.5728 | 83.983 | -6.9776 | 7.6018 | 110.3828 | 2.6863 |  | 17.5262 | 50.9304 | 4.2136 |  | 61.779 | 159.5559 | 9.3268 | 26.1236 | 4.2444 | 196 | 38.2072 | 2.497 | 96.8511 | 0.039461
11971 | 932.3682 | 6.1556 | 33.0373 | 83.6534 | -6.967 | 7.5979 | 102.8545 | 2.7825 |  | 15.4516 | 46.078 | 3.9188 |  | 56.8156 | 158.012 | 9.5227 | 25.8444 | 3.8317 | 192 | 34.7676 | 2.4885 | 92.4037 | 0.02107
11972 | 924.3469 | 9.9168 | 33.4566 | 82.9127 | -6.8906 | 7.6 | 95.1252 | 2.6797 |  | 13.5961 | 39.0268 | 3.6488 |  | 52.8843 | 140.0534 | 9.3413 | 25.2327 | 3.6115 | 199 | 33.0486 | 2.4702 | 90.9136 | 0.0046354
11973 | 923.1965 | 11.6352 | 34.1388 | 83.9886 | -6.5226 | 7.6 | 103.5967 | 2.3377 |  | 13.3168 | 37.356 | 5.15 |  | 49.0833 | 131.6361 | 9.4052 | 25.3377 | 3.6544 | 170 | 32.9078 | 2.4752 | 87.0913 | 0
11974 | 917.0271 | 9.5763 | 33.537 | 85.164 | -6.8194 | 7.6 | 96.1497 | 3.0055 |  | 14.748 | 37.764 | 6.2868 |  | 48.9706 | 132.2202 | 9.6001 | 25.8857 | 3.303 | 155 | 32.5588 | 2.4771 | 91.5453 | 0
11975 | 267.2999 | 2.9121 | 8.9812 | 22.2068 | 0.3345 | 0.002112 | 27.0088 | 1.038 |  | 4.7246 | 12.3327 | 1.9814 |  | 13.4181 | 42.1823 | 2.5851 | 6.9115 | 0.98585 | 117 | 2.512 | 0.2946 | 7.2933 | 0
11976 | 929.5409 | 2.4052 | 30.8887 | 86.0215 | -8.178 | 8.5497 | 74.9849 | 2.5506 |  | 13.4359 | 37.9017 | 6.5061 |  | 48.6499 | 125.2518 | 9.9202 | 25.9843 | 2.8187 | 117 | 31.7702 | 2.4697 | 98.122 | 0
11977 | 931.7174 | 2.294 | 30.7852 | 86.2013 | -8.5127 | 8.55 | 59.7252 | 3.3614 |  | 13.1789 | 37.9063 | 6.4218 |  | 48.0367 | 120.9139 | 9.8431 | 25.984 | 2.7548 | 115 | 31.4535 | 0 | 98.5402 | 0
11978 | 899.6445 | 2.2869 | 30.4299 | 85.9247 | -15.6328 | 15.1982 | 61.3013 | 3.6441 |  | 12.3517 | 37.5277 | 6.3187 |  | 47.2587 | 123.8303 | 9.7909 | 25.9546 | 2.761 | 113 | 32.1516 | 2.4793 | 98.1539 | 0
11979 | 879.1052 | 2.5299 | 30.4653 | 85.5931 | -13.6314 | 13.3005 | 64.7105 | 2.952 |  | 12.0454 | 37.6634 | 6.2947 |  | 48.0452 | 125.9346 | 9.7495 | 26.0348 | 2.7643 | 112 | 32.4498 | 2.4752 | 99.5632 | 0
11980 | 881.2601 | 2.8616 | 30.3741 | 84.3722 | -12.6312 | 12.3503 | 70.3352 | 2.6328 |  | 11.2664 | 37.3748 | 5.7584 |  | 46.1764 | 121.1595 | 9.6013 | 26.9969 | 2.7374 | 112 | 34.4703 | 2.4784 | 98.8408 | 0
11981 | 874.3916 | 3.6641 | 29.4889 | 82.6615 | -8.6336 | 8.5511 | 63.4888 | 3.0262 |  | 9.6286 | 35.6823 | 4.0318 |  | 41.2827 | 115.6218 | 9.4663 | 27.6404 | 2.6043 | 102 | 39.7464 | 2.479 | 96.0657 | 0.014601
11982 | 885.9824 | 2.7228 | 29.3893 | 81.9355 | -8.6378 | 8.55 | 60.7049 | 3.1699 |  | 8.9693 | 34.9516 | 3.3909 |  | 38.7858 | 111.2032 | 9.3126 | 25.7069 | 2.5428 | 106 | 31.039 | 2.4729 | 95.6547 | 0.038333
11983 | 894.1137 | 2.0202 | 29.3788 | 81.9522 | -8.6428 | 8.55 | 64.9762 | 1.997 |  | 8.9629 | 36.2182 | 3.3712 |  | 38.4309 | 106.1942 | 10.6171 | 25.044 | 2.5316 | 106 | 37.478 | 2.4848 | 95.2521 | 0.065217
11984 | 905.7247 | 2.4467 | 29.4478 | 82.6512 | -8.6404 | 8.55 | 75.1542 | 2.8654 |  | 11.2877 | 36.6022 | 3.3658 |  | 39.088 | 105.2599 | 11.808 | 24.9879 | 2.6756 | 123 | 36.0023 | 2.4893 | 95.2866 | 0.075484
11985 | 925.831 | 2.581 | 29.5798 | 84.7037 | -7.6369 | 7.6003 | 93.6094 | 3.203 |  | 16.7775 | 39.085 | 3.9045 |  | 42.5875 | 107.7454 | 11.8488 | 25.0878 | 2.8788 | 157 | 36.6279 | 2.4851 | 94.6841 | 0.095073
11986 | 947.9875 | 7.1198 | 29.0477 | 85.3176 | -8.5714 | 8.5497 | 99.351 | 2.1243 |  | 23.9196 | 44.9879 | 4.0842 |  | 49.6371 | 112.5561 | 11.5413 | 25.4085 | 4.0691 | 158 | 42.9984 | 2.4881 | 97.053 | 0.12621
11987 | 968.0149 | 6.8144 | 29.2111 | 85.0785 | -7.6018 | 7.6003 | 104.2228 | 2.4665 |  | 30.1874 | 49.0789 | 4.09 |  | 53.7631 | 119.4227 | 11.2949 | 26.0165 | 5.0433 | 182 | 46.9549 | 2.4953 | 100.3854 | 0.13396
11988 | 973.7673 | 3.2757 | 29.451 | 86.9896 | -8.5698 | 8.5497 | 98.0366 | 1.8442 |  | 30.4793 | 55.7095 | 5.5298 |  | 57.509 | 128.0585 | 11.3767 | 25.811 | 4.9122 | 184 | 36.8379 | 2.4889 | 99.8809 | 0.12419
11989 | 994.4407 | 2.6477 | 29.3718 | 91.2094 | -7.2883 | 7.6003 | 103.6562 | 1.4073 |  | 28.3493 | 58.993 | 4.6793 |  | 61.3663 | 135.8855 | 11.2098 | 25.9452 | 4.6765 | 180 | 38.9431 | 2.4739 | 99.3008 | 0.1342
11990 | 992.788 | 3.642 | 29.5503 | 91.606 | -6.1966 | 6.6503 | 107.445 | 1.3663 |  | 23.6349 | 59.9052 | 4.6976 |  | 62.3826 | 140.0954 | 11.2198 | 26.3239 | 4.8433 | 166 | 33.1751 | 2.4766 | 98.4584 | 0.1205
11991 | 991.5064 | 3.992 | 29.1885 | 89.0139 | -7.4877 | 7.5997 | 96.0176 | 1.5892 |  | 20.3569 | 60.2726 | 6.7801 |  | 58.1297 | 137.2416 | 10.9733 | 26.91 | 4.8164 | 160 | 30.1669 | 2.4745 | 102.6812 | 0.10409
11992 | 988.4471 | 9.2975 | 28.8304 | 87.058 | -6.6445 | 6.6503 | 105.7191 | 1.2939 |  | 15.5147 | 63.3393 | 8.5681 |  | 64.8775 | 134.0868 | 9.9287 | 27.8368 | 5.0681 | 157 | 34.4945 | 2.465 | 89.2801 | 0.092487
11993 | 998.8527 | 9.2807 | 29.1127 | 91.6164 | -6.6404 | 6.65 | 95.9468 | 1.1534 |  | 14.9006 | 70.6523 | 8.961 |  | 68.2314 | 142.8575 | 8.9517 | 28.2705 | 4.9102 | 152 | 35.8449 | 2.4299 | 85.6897 | 0.068682
11994 | 998.4818 | 5.9879 | 29.4162 | 92.4871 | -6.6336 | 6.65 | 92.1767 | 1.7803 |  | 15.5798 | 60.5736 | 9.6985 |  | 64.4731 | 150.9543 | 8.697 | 26.741 | 4.8545 | 137 | 40.2278 | 2.4895 | 92.1374 | 0.044511
11995 | 980.841 | 6.9725 | 29.2494 | 90.0472 | -7.6345 | 7.5997 | 95.8506 | 2.1791 |  | 13.0446 | 47.049 | 10.6573 |  | 65.593 | 147.3965 | 8.9675 | 26.1542 | 4.6865 | 140 | 39.6536 | 2.4533 | 92.6451 | 0.037481
11996 | 951.5407 | 15.8902 | 29.7333 | 89.1783 | -7.634 | 7.6 | 101.2625 | 2.6841 |  | 11.0441 | 39.9536 | 8.4436 |  | 57.9455 | 139.1727 | 8.8418 | 25.6335 | 4.5186 | 130 | 41.4771 | 2.4561 | 91.1329 | 0.0046354
11997 | 932.2834 | 21.2803 | 30.0209 | 89.0265 | -6.6301 | 6.6503 | 86.3778 | 2.0886 |  | 11.0835 | 39.6517 | 6.7396 |  | 49.3681 | 134.9038 | 8.9351 | 25.6329 | 4.0477 | 121 | 39.4192 | 2.4639 | 89.8796 | 0
11998 | 910.2033 | 18.2727 | 29.9893 | 88.4864 | 0.74787 | 0.001848 | 78.7869 | 3.1373 |  | 11.8252 | 39.0306 | 7.6455 |  | 46.768 | 132.7347 | 8.976 | 25.7476 | 3.2155 | 106 | 37.3218 | 2.4588 | 97.167 | 0
11999 | 264.6066 | 5.4445 | 8.0932 | 22.922 | 0.3571 | 0 | 23.365 | 1.1778 |  | 3.7329 | 12.5837 | 2.4995 |  | 12.6798 | 42.0694 | 2.3956 | 6.8438 | 0.92228 | 107 | 2.9473 | 0.29299 | 6.2471 | 0
12000 | 892.4992 | 7.6965 | 30.1381 | 88.3071 | -8.905 | 9.4996 | 72.9605 | 2.2978 |  | 11.8509 | 36.3474 | 7.3809 |  | 43.5932 | 130.0975 | 9.3216 | 26.0617 | 2.3718 | 107 | 34.7844 | 2.4485 | 97.0285 | 0
12001 | 897.936 | 3.6154 | 29.8877 | 88.1363 | -7.9855 | 8.5503 | 65.1298 | 2.936 |  | 11.8719 | 36.1317 | 7.1764 |  | 42.9242 | 120.7469 | 9.2116 | 26.3799 | 2.4183 | 106 | 34.2962 | 2.4621 | 97.4006 | 0
12002 | 871.3044 | 2.4579 | 30.1797 | 89.0589 | -8.4329 | 8.55 | 66.3454 | 3.4569 |  | 11.8974 | 36.0694 | 7.0643 |  | 42.8531 | 120.8242 | 9.2143 | 26.3242 | 2.4513 | 113 | 31.3219 | 2.4547 | 95.1333 | 0
12003 | 861.1583 | 2.4184 | 30.7083 | 88.2274 | -7.6304 | 7.6003 | 66.528 | 2.3378 |  | 11.8569 | 35.8784 | 7.0056 |  | 42.1076 | 119.6221 | 9.1454 | 26.4591 | 2.453 | 110 | 31.3619 | 2.4568 | 98.0511 | 0
12004 | 851.7919 | 3.0173 | 31.6152 | 90.296 | -9.6355 | 9.4995 | 61.918 | 2.9238 |  | 12.7811 | 35.1888 | 6.1943 |  | 39.0258 | 113.3675 | 8.9222 | 27.0164 | 2.401 | 101 | 30.9116 | 2.4573 | 105.2001 | 0
12005 | 857.2606 | 4.3098 | 30.4648 | 87.2213 | -8.6399 | 8.5503 | 78.6805 | 3.4998 |  | 18.3395 | 35.2013 | 5.9119 |  | 40.6335 | 108.8853 | 8.8368 | 27.5552 | 2.2659 | 104 | 33.1685 | 2.4551 | 108.7262 | 0.027422
12006 | 890.0503 | 4.914 | 40.0842 | 90.5948 | -9.6431 | 9.4997 | 95.0514 | 2.6766 |  | 24.849 | 41.8649 | 14.8284 |  | 76.3656 | 129.0839 | 11.5771 | 26.1007 | 2.3077 | 167 | 36.1063 | 2.4576 | 130.2933 | 0.17204
12007 | 945.3241 | 9.6436 | 70.8617 | 100.4071 | -15.0935 | 15.1984 | 110.8567 | 3.5624 |  | 29.6092 | 69.1604 | 27.2687 |  | 106.3733 | 182.3417 | 26.6959 | 28.249 | 6.6302 | 266 | 52.0909 | 2.5081 | 142.5271 | 0.26377
12008 | 1037.2863 | 9.5994 | 99.9266 | 110.9777 | -13.8665 | 14.2503 | 132.0905 | 4.6018 |  | 32.3005 | 89.5617 | 30.9146 |  | 135.4029 | 234.8225 | 34.7644 | 33.0254 | 12.6409 | 293 | 61.0855 | 2.5057 | 163.2054 | 0.27789
12009 | 1154.1759 | 10.8099 | 107.8392 | 122.3687 | -13.2599 | 14.25 | 149.7471 | 5.5848 |  | 36.9263 | 93.7221 | 29.8058 |  | 159.3058 | 282.0037 | 40.2105 | 36.6652 | 18.2604 | 323 | 62.9616 | 2.5024 | 185.4361 | 0.0963
12010 | 1208.846 | 9.0886 | 109.3505 | 133.7692 | -17.562 | 18.9987 | 156.3403 | 5.2858 |  | 43.7354 | 96.2777 | 31.3626 |  | 172.5622 | 300.0081 | 40.4247 | 38.4241 | 18.5543 | 310 | 53.6461 | 3.3117 | 189.1506 | 0.10977
12011 | 1231.1012 | 10.0027 | 111.4963 | 133.7417 | -15.1347 | 17.1005 | 154.8831 | 5.0049 |  | 44.115 | 95.7571 | 33.029 |  | 178.7811 | 300.4141 | 39.0555 | 40.7178 | 18.0709 | 275 | 60.6504 | 3.3686 | 190.2935 | 0.11905
12012 | 1228.2368 | 9.3083 | 112.2579 | 135.2456 | -15.2109 | 17.1 | 154.5552 | 5.2064 |  | 42.2529 | 95.8208 | 37.1628 |  | 177.2036 | 299.5383 | 41.2446 | 39.8915 | 18.6167 | 301 | 68.1558 | 2.8721 | 196.0612 | 0.12249
12013 | 1228.2153 | 10.9067 | 112.9986 | 138.3423 | -13.4285 | 15.2005 | 169.2682 | 5.7123 |  | 41.5059 | 95.9317 | 40.4338 |  | 175.6421 | 306.6588 | 41.7324 | 39.0487 | 19.4401 | 272 | 79.8327 | 2.545 | 193.0833 | 0.12019
12014 | 1230.1715 | 10.4366 | 114.6356 | 142.9296 | -14.627 | 16.1497 | 170.8221 | 5.8993 |  | 42.412 | 99.0494 | 40.4445 |  | 179.0694 | 310.1089 | 41.1744 | 41.6525 | 21.271 | 267 | 82.5068 | 2.7902 | 188.69 | 0.11305
12015 | 1210.2277 | 11.3083 | 112.5725 | 144.8426 | -15.688 | 17.0997 | 164.1287 | 4.5827 |  | 38.5121 | 101.4964 | 34.1754 |  | 172.9132 | 294.3384 | 40.5311 | 42.4195 | 19.9431 | 247 | 78.6419 | 2.6713 | 194.0256 | 0.23573
12016 | 1159.9221 | 8.4011 | 105.8612 | 133.0171 | -11.6176 | 13.3011 | 149.3289 | 3.7523 |  | 33.9648 | 95.4049 | 33.1866 |  | 152.2361 | 256.5869 | 32.7227 | 39.0753 | 18.212 | 227 | 58.4872 | 2.5272 | 170.9965 | 0.22307
12017 | 1130.02 | 5.1427 | 100.3174 | 117.3109 | -5.222 | 7.6016 | 142.5286 | 2.5234 |  | 34.8174 | 88.313 | 33.2741 |  | 117.0778 | 218.7907 | 17.7186 | 35.4652 | 17.3466 | 236 | 44.974 | 2.5031 | 135.0534 | 0.25166
12018 | 1081.6962 | 4.0427 | 95.6382 | 102.7254 | -5.1639 | 7.6 | 138.0053 | 1.5017 |  | 31.0822 | 72.9906 | 28.2403 |  | 78.0643 | 192.1679 | 11.5259 | 32.677 | 13.9792 | 210 | 44.8054 | 2.5031 | 121.1143 | 0.23304
12019 | 1052.6753 | 7.1533 | 75.3649 | 96.723 | -7.2968 | 9.4995 | 130.2405 | 2.45 |  | 23.2568 | 62.3285 | 14.0113 |  | 64.2609 | 167.0791 | 10.0914 | 30.0412 | 7.5254 | 183 | 46.7257 | 2.5012 | 100.4764 | 0.019756
12020 | 1009.3238 | 12.0309 | 32.7767 | 94.4111 | -4.415 | 6.6508 | 98.5982 | 1.8987 |  | 18.2677 | 54.7958 | 8.9002 |  | 59.5374 | 155.5367 | 9.2735 | 27.6438 | 4.5839 | 174 | 52.7781 | 2.5065 | 86.4178 | 0.0043595
12021 | 969.8657 | 14.4049 | 17.9206 | 90.3948 | -5.5659 | 7.5997 | 84.896 | 2.7147 |  | 13.8615 | 46.3517 | 9.3887 |  | 54.5132 | 146.4176 | 8.8179 | 26.7177 | 3.9977 | 181 | 48.0477 | 2.5023 | 87.001 | 0
12022 | 951.0735 | 7.4397 | 17.5078 | 87.8362 | -6.7124 | 8.5497 | 99.0452 | 3.5009 |  | 13.1465 | 38.9702 | 10.5003 |  | 50.4981 | 139.8904 | 9.0462 | 26.3013 | 4.1081 | 160 | 45.3106 | 2.512 | 93.8364 | 0
12023 | 279.7367 | 1.2285 | 4.7932 | 22.9965 | 0.82682 | 0.002376 | 31.5463 | 1.1281 |  | 4.1996 | 12.0907 | 3.3635 |  | 13.5709 | 44.3324 | 2.4988 | 7.0073 | 1.3359 | 126 | 3.6069 | 0.3031 | 9.1248 | 0
12024 | 922.0957 | 2.6454 | 17.7706 | 88.8947 | -7.3373 | 9.4995 | 78.5588 | 2.9786 |  | 13.9178 | 36.6103 | 11.1316 |  | 45.4523 | 122.7645 | 9.3664 | 26.2343 | 4.0181 | 108 | 43.5355 | 2.514 | 99.1562 | 0
12025 | 917.6603 | 2.292 | 17.8584 | 88.1886 | -5.6411 | 7.6005 | 81.49 | 3.4441 |  | 13.8656 | 37.5311 | 10.8074 |  | 45.1746 | 115.8565 | 9.1752 | 26.2939 | 3.4648 | 105 | 37.6837 | 2.5111 | 99.0742 | 0
12026 | 908.5254 | 2.391 | 17.9016 | 88.7007 | -6.257 | 8.5497 | 75.0642 | 2.6395 |  | 13.6145 | 38.6162 | 10.6808 |  | 45.2549 | 115.9594 | 9.0755 | 26.2876 | 2.7013 | 106 | 36.9933 | 2.5195 | 99.6659 | 0
12027 | 895.7067 | 2.5741 | 17.8742 | 88.2366 | -6.3476 | 8.55 | 66.9497 | 2.9742 |  | 13.1024 | 38.8803 | 10.6677 |  | 45.4479 | 116.0431 | 9.1514 | 26.3983 | 2.4642 | 102 | 38.4636 | 2.5226 | 99.5779 | 0
12028 | 899.8649 | 2.8487 | 17.6134 | 85.9454 | -5.522 | 7.6003 | 57.3705 | 3.2376 |  | 13.1747 | 37.4853 | 9.4703 |  | 44.5966 | 110.5191 | 9.0627 | 27.3834 | 2.4052 | 100 | 35.0562 | 2.5148 | 105.9559 | 0
12029 | 906.2436 | 3.6735 | 25.0874 | 85.8456 | -6.1791 | 8.5497 | 64.6205 | 2.7809 |  | 17.2619 | 37.0629 | 9.8357 |  | 48.2892 | 110.0809 | 8.7602 | 28.1724 | 2.2835 | 104 | 38.2658 | 2.5262 | 110.411 | 0.016834
12030 | 941.1347 | 4.5682 | 37.5627 | 87.8778 | -8.8795 | 11.3992 | 72.3036 | 2.1306 |  | 21.4312 | 43.8916 | 12.7999 |  | 80.4358 | 122.0347 | 11.5471 | 26.4528 | 2.2479 | 179 | 43.6557 | 2.5191 | 122.3422 | 0.048393
12031 | 1001.0897 | 8.9831 | 71.4279 | 94.327 | -11.2802 | 13.2995 | 97.5833 | 3.1705 |  | 20.6065 | 70.6579 | 23.1314 |  | 111.5974 | 176.1668 | 26.4974 | 28.1347 | 7.174 | 266 | 62.3034 | 2.5335 | 143.74 | 0.10252
12032 | 1075.7996 | 9.3082 | 93.8531 | 114.1728 | -12.4008 | 14.2497 | 123.1313 | 5.4955 |  | 24.9218 | 89.9583 | 31.9038 |  | 140.5696 | 233.9382 | 35.0741 | 33.5273 | 13.5775 | 264 | 71.9935 | 2.5194 | 167.4726 | 0.18289
12033 | 1161.6859 | 7.3554 | 108.1451 | 129.3121 | -12.5556 | 14.25 | 136.9477 | 5.7373 |  | 31.4577 | 99.4767 | 36.4329 |  | 159.6739 | 273.3273 | 39.8465 | 38.5706 | 17.4126 | 322 | 67.1986 | 2.5246 | 193.1859 | 0.25348
12034 | 1212.9513 | 5.6565 | 110.6901 | 134.279 | -15.4255 | 17.0992 | 138.4534 | 5.2055 |  | 35.5199 | 104.7317 | 41.3725 |  | 168.6002 | 298.3155 | 40.7572 | 40.9443 | 19.2214 | 368 | 68.2891 | 2.8428 | 201.4823 | 0.28314
12035 | 1238.2988 | 5.1425 | 114.6892 | 135.4488 | -12.1434 | 14.2508 | 135.3689 | 5.1554 |  | 40.4995 | 105.6903 | 41.4433 |  | 177.4507 | 306.0579 | 39.1556 | 41.3674 | 19.7083 | 316 | 80.8431 | 3.9492 | 207.8024 | 0.25495
12036 | 1232.198 | 6.0963 | 112.8423 | 136.6563 | -11.2263 | 13.3003 | 136.7662 | 5.2725 |  | 42.8051 | 105.7661 | 39.7369 |  | 177.6939 | 301.7293 | 39.2329 | 40.4859 | 19.3457 | 317 | 74.9318 | 4.6293 | 214.595 | 0.25385
12037 | 1221.4876 | 7.2967 | 116.0873 | 145.5917 | -12.5696 | 14.2497 | 153.3103 | 5.7637 |  | 42.9791 | 105.2469 | 40.5166 |  | 188.6211 | 298.0821 | 41.9001 | 44.7911 | 19.1383 | 286 | 78.1847 | 4.1178 | 214.0179 | 0.28724
12038 | 1210.5641 | 7.9583 | 119.2674 | 147.5792 | -15.5024 | 17.0992 | 159.2798 | 5.5416 |  | 46.4426 | 104.1087 | 39.3336 |  | 195.3211 | 302.2427 | 43.7782 | 51.6267 | 18.9603 | 238 | 86.291 | 5.2433 | 209.4893 | 0.27991
12039 | 1194.9777 | 7.1905 | 117.4709 | 141.3786 | -15.7875 | 17.1 | 162.7365 | 5.3772 |  | 46.2743 | 101.761 | 36.186 |  | 188.7408 | 299.5619 | 41.9849 | 51.875 | 18.925 | 261 | 84.2109 | 4.9757 | 210.1651 | 0.27113
12040 | 1171.6604 | 5.4198 | 113.0338 | 133.9832 | -17.5515 | 18.9995 | 149.9683 | 4.6824 |  | 43.9792 | 99.3024 | 34.335 |  | 172.6111 | 270.9567 | 33.4402 | 47.0536 | 18.5288 | 253 | 76.2299 | 3.9656 | 180.2089 | 0.1787
12041 | 1123.6994 | 6.0739 | 107.6802 | 118.4537 | -19.3478 | 20.8995 | 125.2019 | 2.7133 |  | 37.7155 | 90.8509 | 33.317 |  | 139.2953 | 221.1418 | 27.5628 | 38.4534 | 17.2674 | 242 | 62.0128 | 3.6849 | 134.0894 | 0.10187
12042 | 1082.1524 | 7.2768 | 103.8127 | 102.1426 | -7.34 | 9.5032 | 104.3581 | 2.3964 |  | 29.665 | 76.9281 | 26.9433 |  | 101.4237 | 191.3267 | 18.0939 | 33.3856 | 13.3241 | 202 | 57.4394 | 3.6858 | 118.1656 | 0.039796
12043 | 1057.2083 | 6.5907 | 85.87 | 96.4489 | -5.0184 | 7.6005 | 83.2646 | 2.679 |  | 25.8675 | 69.6894 | 14.4422 |  | 82.4212 | 173.4566 | 11.8817 | 30.8641 | 7.1924 | 177 | 61.8147 | 3.7319 | 109.7405 | 0.12171
12044 | 1016.2884 | 5.733 | 46.8735 | 92.9512 | -6.3132 | 8.5497 | 87.9545 | 2.1157 |  | 21.3731 | 64.4527 | 8.367 |  | 72.1354 | 156.7727 | 11.4437 | 28.3854 | 4.1105 | 162 | 61.0055 | 3.6993 | 101.131 | 0.016894
12045 | 987.22 | 5.2571 | 27.7162 | 92.1811 | -5.1187 | 7.6003 | 90.9128 | 2.7477 |  | 16.855 | 56.6083 | 9.8305 |  | 62.9538 | 147.7748 | 10.5779 | 27.4605 | 4.0931 | 146 | 52.7997 | 3.6992 | 96.4794 | 0
12046 | 962.1982 | 4.154 | 26.9446 | 91.7096 | -3.9154 | 6.6503 | 82.4093 | 2.5249 |  | 15.6242 | 49.9915 | 11.0366 |  | 58.6204 | 141.9806 | 9.9754 | 26.8623 | 4.1778 | 127 | 47.0772 | 3.6969 | 97.3189 | 0
12047 | 390.6995 | 1.5345 | 10.5186 | 34.6978 | 1.4325 | 0.001848 | 33.0939 | 0.792 |  | 6.7335 | 21.1781 | 4.7039 |  | 22.6606 | 61.1431 | 3.8554 | 10.2362 | 1.7768 | 116 | 9.0214 | 0.88599 | 21.0072 | 0
12048 | 914.2682 | 2.5119 | 26.7359 | 88.8139 | -5.0753 | 7.6 | 70.4046 | 2.5533 |  | 15.1491 | 44.2385 | 11.1279 |  | 52.2204 | 119.5757 | 9.8183 | 26.5474 | 3.6886 | 109 | 39.5406 | 3.704 | 98.5941 | 0
12049 | 906.9239 | 2.6905 | 26.7554 | 90.4156 | -5.055 | 7.6 | 59.6914 | 2.759 |  | 14.4872 | 43.8979 | 10.8708 |  | 50.1429 | 114.8588 | 9.8965 | 26.3838 | 2.9024 | 107 | 39.1301 | 3.6968 | 101.1501 | 0
12050 | 901.8161 | 2.5252 | 26.8881 | 91.0725 | -5.7253 | 8.5497 | 54.8054 | 3.2282 |  | 13.8836 | 43.4671 | 10.8199 |  | 49.9016 | 115.3768 | 9.7665 | 26.1035 | 2.4889 | 106 | 40.9672 | 3.6972 | 97.1211 | 0
12051 | 898.3505 | 2.4726 | 26.7956 | 89.5854 | -5.8345 | 8.55 | 56.4578 | 2.412 |  | 13.5192 | 43.0055 | 10.7938 |  | 50.1609 | 115.0966 | 9.5997 | 26.2396 | 2.4875 | 105 | 37.0183 | 3.7033 | 97.5458 | 0
12052 | 886.9549 | 2.8991 | 26.6191 | 89.5245 | -5.3978 | 7.6003 | 55.4425 | 2.6045 |  | 15.1542 | 42.0803 | 10.3971 |  | 51.3931 | 110.6142 | 9.5265 | 27.4481 | 2.3548 | 104 | 39.2973 | 3.6996 | 99.6234 | 0
12053 | 899.3691 | 3.7639 | 32.9638 | 87.6919 | -4.7582 | 6.6503 | 63.9622 | 2.4589 |  | 21.8945 | 42.411 | 10.3944 |  | 53.9645 | 111.8018 | 9.2929 | 27.9696 | 2.2133 | 108 | 40.4409 | 3.7058 | 109.2876 | 0.11706
12054 | 941.528 | 5.5051 | 51.7661 | 90.8909 | -15.8153 | 17.0971 | 75.2893 | 2.2738 |  | 24.3508 | 51.6995 | 15.17 |  | 78.1441 | 121.9518 | 12.8215 | 26.3821 | 2.1371 | 185 | 45.5356 | 3.7294 | 117.1774 | 0.19823
12055 | 1009.7075 | 12.1246 | 84.2022 | 98.0259 | -16.5409 | 18.0497 | 100.6866 | 4.1318 |  | 22.9434 | 74.0581 | 26.518 |  | 114.0204 | 173.2502 | 26.4616 | 27.9854 | 5.3122 | 236 | 64.5537 | 4.3614 | 140.0633 | 0.28031
12056 | 1084.0642 | 19.396 | 105.5504 | 114.0924 | -16.2687 | 18.05 | 125.8724 | 5.1831 |  | 25.3364 | 92.1745 | 33.3589 |  | 147.4469 | 233.8934 | 37.5677 | 33.1649 | 12.2626 | 303 | 73.7991 | 4.1915 | 174.2999 | 0.31257
12057 | 1168.2413 | 23.901 | 111.5419 | 132.1368 | -18.149 | 19.9495 | 131.0216 | 4.8435 |  | 28.4863 | 97.5434 | 35.1801 |  | 173.3556 | 273.2406 | 42.0552 | 39.0589 | 16.1161 | 323 | 81.6179 | 3.9944 | 194.9154 | 0.29831
12058 | 1226.744 | 21.9441 | 114.9062 | 143.5043 | -20.991 | 22.7992 | 136.5919 | 6.1255 |  | 32.2327 | 98.9252 | 35.9524 |  | 190.557 | 294.8656 | 43.5461 | 41.8516 | 17.2649 | 326 | 87.6983 | 4.3706 | 201.7547 | 0.31559
12059 | 1241.3346 | 14.5227 | 117.9476 | 147.7632 | -15.903 | 18.0513 | 145.1741 | 5.9179 |  | 34.6313 | 97.9727 | 36.7053 |  | 200.7376 | 303.6293 | 42.8162 | 42.0061 | 18.1347 | 315 | 88.2522 | 4.2497 | 205.9577 | 0.25554
12060 | 1231.6708 | 10.7039 | 116.6334 | 147.7454 | -19.9123 | 21.8489 | 150.4529 | 5.0469 |  | 32.9816 | 97.7165 | 38.5602 |  | 198.8937 | 303.8264 | 41.7093 | 40.8402 | 18.6126 | 393 | 84.075 | 4.1987 | 208.8627 | 0.26969
12061 | 1229.9332 | 9.7619 | 117.6101 | 146.8724 | -20.1234 | 21.8318 | 151.8031 | 4.905 |  | 33.3642 | 98.8248 | 38.4959 |  | 193.2116 | 303.4945 | 43.3499 | 40.9726 | 18.8726 | 323 | 86.3165 | 4.105 | 212.6615 | 0.21676
12062 | 1231.3609 | 7.4536 | 120.3192 | 147.7075 | -21.2373 | 22.8179 | 153.5846 | 5.2624 |  | 35.372 | 98.0574 | 37.331 |  | 189.0406 | 304.3838 | 43.2366 | 41.886 | 19.287 | 285 | 82.2021 | 4.3378 | 212.4431 | 0.13598
12063 | 1236.241 | 5.6415 | 117.2133 | 146.8496 | -18.5637 | 20.9005 | 151.7911 | 5.3373 |  | 35.1033 | 98.7841 | 35.6515 |  | 183.6807 | 300.7174 | 41.1642 | 42.5632 | 19.3074 | 268 | 81.2263 | 4.0205 | 208.0963 | 0.15601
12064 | 1210.7205 | 5.1826 | 110.889 | 138.6721 | -12.5664 | 15.2016 | 138.5886 | 4.1692 |  | 36.7777 | 99.312 | 32.1054 |  | 168.8622 | 279.1804 | 31.8496 | 40.9612 | 18.407 | 234 | 73.7459 | 3.6764 | 182.7207 | 0.14325
12065 | 1158.4535 | 5.2505 | 106.9198 | 124.5003 | -10.1187 | 12.3508 | 126.0626 | 3.4037 |  | 35.4673 | 91.6558 | 30.8992 |  | 127.1957 | 246.5909 | 20.9447 | 36.4782 | 17.8772 | 229 | 62.1117 | 3.6596 | 146.0115 | 0.067035
12066 | 1097.5704 | 5.3613 | 100.5892 | 108.586 | -10.3233 | 12.3534 | 114.3723 | 3.7629 |  | 27.8819 | 77.519 | 25.6139 |  | 85.1098 | 223.1514 | 14.8164 | 32.3735 | 14.2985 | 203 | 58.4739 | 3.6547 | 126.0581 | 0.092582
12067 | 1043.0664 | 4.1651 | 83.9417 | 101.5784 | -9.5571 | 11.3968 | 103.7456 | 3.1619 |  | 22.675 | 69.2714 | 15.7891 |  | 67.095 | 204.0851 | 11.9012 | 28.8028 | 7.8777 | 178 | 50.6674 | 3.6387 | 112.5903 | 0.06709
12068 | 1001.1923 | 6.8113 | 46.6233 | 98.413 | -8.5608 | 10.4503 | 99.4326 | 1.812 |  | 19.6904 | 64.7708 | 11.0479 |  | 59.7929 | 178.0721 | 11.4118 | 26.2197 | 4.9401 | 165 | 47.2009 | 3.6421 | 103.3679 | 0.012925
12069 | 971.6165 | 11.2038 | 24.385 | 97.7577 | -7.3847 | 9.5029 | 99.8377 | 2.2324 |  | 16.7244 | 54.9183 | 12.3831 |  | 54.779 | 158.2555 | 10.7299 | 25.6506 | 4.6791 | 167 | 42.5757 | 3.6425 | 94.1401 | 0
12070 | 945.8803 | 9.4482 | 22.1967 | 98.2415 | -6.9901 | 9.4974 | 92.0218 | 2.4357 |  | 15.8026 | 46.3656 | 15.5156 |  | 51.8441 | 148.0182 | 10.4098 | 26.2612 | 3.8011 | 146 | 45.5791 | 3.6442 | 90.8651 | 0
12071 | 396.0057 | 3.2376 | 8.8749 | 38.5687 | 1.6213 | 0.002639 | 36.7076 | 0.89959 |  | 7.0168 | 20.2843 | 7.378 |  | 20.6054 | 64.816 | 4.245 | 10.5682 | 1.4423 | 129 | 9.6348 | 0.91554 | 19.8546 | 0
12072 | 891.4327 | 2.3922 | 21.745 | 97.7119 | -7.0335 | 9.5003 | 69.7307 | 2.3289 |  | 14.4132 | 42.4994 | 11.5723 |  | 46.5677 | 139.54 | 10.0569 | 25.9799 | 2.8044 | 123 | 37.6966 | 3.636 | 95.3725 | 0
12073 | 881.0799 | 2.4366 | 21.9206 | 98.1762 | -5.9666 | 8.5503 | 58.3789 | 1.9151 |  | 13.8994 | 41.6381 | 10.6831 |  | 44.6041 | 134.3657 | 12.522 | 25.8697 | 3.0595 | 116 | 37.3787 | 3.6452 | 94.8636 | 0
12074 | 886.4461 | 2.4972 | 21.9407 | 97.2662 | -7.0605 | 9.4997 | 54.6956 | 2.5969 |  | 13.928 | 41.261 | 10.7103 |  | 42.8075 | 122.8198 | 14.5032 | 26.011 | 2.8288 | 118 | 38.1104 | 3.6329 | 95.8266 | 0
12075 | 884.6119 | 2.32 | 22.0112 | 95.7604 | -7.1923 | 9.5 | 55.7901 | 2.3197 |  | 14.6317 | 40.2881 | 10.5242 |  | 42.191 | 115.3179 | 14.5256 | 26.0698 | 2.4715 | 112 | 33.0763 | 3.6415 | 95.4421 | 0
12076 | 875.0397 | 2.924 | 21.3789 | 94.577 | -7.3557 | 9.5026 | 55.2991 | 1.5748 |  | 15.8741 | 38.3967 | 8.6891 |  | 40.9102 | 108.2962 | 12.9919 | 27.1571 | 2.2957 | 112 | 31.0533 | 3.6392 | 95.2454 | 0
12077 | 894.3959 | 3.1317 | 35.2512 | 92.5159 | -6.4883 | 8.5476 | 61.0405 | 2.1039 |  | 20.8981 | 37.3118 | 8.3463 |  | 46.0003 | 108.3559 | 10.7045 | 27.5639 | 2.2519 | 114 | 32.7411 | 3.6415 | 104.43 | 0.12404
12078 | 937.6819 | 3.8723 | 56.2415 | 95.4059 | -13.5903 | 15.1982 | 81.0915 | 2.0457 |  | 28.4356 | 42.525 | 12.5965 |  | 71.8433 | 118.0715 | 13.3313 | 26.1146 | 2.4126 | 180 | 37.4486 | 3.6348 | 117.1785 | 0.1186
12079 | 982.0951 | 6.7231 | 80.7163 | 104.2456 | -16.4335 | 18.0492 | 108.3281 | 2.4864 |  | 32.4042 | 66.1725 | 26.2309 |  | 110.2089 | 159.8228 | 26.0216 | 27.6225 | 5.2972 | 281 | 51.1513 | 3.635 | 131.4248 | 0.25813
12080 | 1047.3432 | 8.3118 | 100.1858 | 115.0918 | -15.1505 | 17.1003 | 135.2651 | 3.7489 |  | 35.0674 | 86.5006 | 37.0365 |  | 142.2707 | 221.922 | 35.5315 | 31.5278 | 12.7201 | 310 | 56.2313 | 3.6278 | 163.0947 | 0.31293
12081 | 1129.466 | 8.6967 | 112.8149 | 138.967 | -15.3103 | 17.1 | 161.9863 | 4.4885 |  | 37.2397 | 91.8777 | 39.6229 |  | 160.755 | 263.0047 | 38.61 | 35.0867 | 15.8789 | 343 | 58.7159 | 3.6265 | 188.9334 | 0.36206
12082 | 1204.5847 | 9.4069 | 117.712 | 150.6309 | -16.1478 | 18.0497 | 178.4934 | 4.5427 |  | 37.8708 | 93.25 | 39.1769 |  | 171.5445 | 280.5513 | 39.2418 | 36.9397 | 15.495 | 336 | 59.2188 | 3.7169 | 186.6703 | 0.33504
12083 | 1234.7416 | 9.9043 | 121.6784 | 147.5909 | -15.6687 | 18.05 | 192.8011 | 4.1786 |  | 38.1415 | 93.1335 | 38.2226 |  | 181.0752 | 290.6409 | 39.9143 | 38.9686 | 16.1958 | 306 | 61.3803 | 3.6789 | 185.0048 | 0.26149
12084 | 1231.0626 | 15.8056 | 125.7164 | 144.7449 | -17.9243 | 19.955 | 205.2674 | 3.9529 |  | 37.1783 | 94.5887 | 37.7141 |  | 183.3311 | 302.8341 | 39.1467 | 40.8966 | 16.5391 | 304 | 56.6055 | 4.1641 | 187.953 | 0.27699
12085 | 1232.341 | 16.0416 | 126.961 | 147.9843 | -15.7993 | 17.0953 | 207.809 | 4.0571 |  | 37.1351 | 96.1795 | 37.3544 |  | 183.5396 | 305.5927 | 39.2708 | 41.5457 | 17.145 | 287 | 62.7622 | 4.2232 | 184.4502 | 0.29932
12086 | 1231.2707 | 9.1369 | 126.0186 | 149.2144 | -14.4725 | 16.1503 | 210.6661 | 4.1439 |  | 36.7516 | 98.2628 | 38.656 |  | 182.6158 | 303.1783 | 39.9613 | 41.4647 | 17.5599 | 278 | 64.909 | 4.3666 | 188.6507 | 0.29121
12087 | 1200.3797 | 5.6606 | 123.0151 | 142.9861 | -17.0228 | 19.9489 | 200.9763 | 3.9775 |  | 34.9241 | 98.1995 | 38.9584 |  | 178.8557 | 294.213 | 38.562 | 41.1856 | 17.2078 | 271 | 63.9019 | 4.9676 | 188.3228 | 0.28326
12088 | 1154.9522 | 4.9523 | 120.1685 | 134.0762 | -10.1119 | 12.3521 | 183.632 | 4.0034 |  | 33.8665 | 95.4472 | 36.9654 |  | 165.6667 | 267.7235 | 31.5834 | 40.1475 | 16.6784 | 261 | 58.0931 | 4.3692 | 160.5939 | 0.17764
12089 | 1119.4628 | 5.8128 | 117.6603 | 121.97 | -9.6718 | 10.4505 | 171.9349 | 2.6491 |  | 30.4193 | 89.6336 | 35.0464 |  | 127.8015 | 226.5409 | 21.1084 | 38.2646 | 16.0117 | 232 | 46.4589 | 4.1905 | 122.4424 | 0.2366
12090 | 1050.8773 | 5.7242 | 112.3126 | 107.153 | -8.2341 | 9.5003 | 156.4168 | 1.4326 |  | 24.4561 | 74.9994 | 27.6649 |  | 84.7543 | 193.9798 | 15.5397 | 35.6136 | 12.831 | 202 | 46.1858 | 4.179 | 111.2759 | 0.25324
12091 | 988.9527 | 6.4319 | 93.5158 | 100.3875 | -7.7671 | 9.5 | 150.1677 | 1.2648 |  | 20.2049 | 63.4278 | 15.7557 |  | 65.1188 | 175.1998 | 13.5606 | 31.9812 | 7.5523 | 187 | 49.5884 | 4.1779 | 103.3261 | 0.20112
12092 | 966.6893 | 8.0019 | 53.2762 | 96.1142 | -7.6722 | 9.5 | 128.0872 | 1.1617 |  | 18.0824 | 58.0489 | 10.9423 |  | 60.4655 | 164.5212 | 12.4778 | 29.4877 | 4.957 | 172 | 43.0399 | 4.1767 | 95.4043 | 0.074743
12093 | 948.4187 | 8.0622 | 30.8932 | 96.3796 | -7.7691 | 9.5 | 106.8305 | 1.4934 |  | 14.8829 | 52.3055 | 10.5915 |  | 57.7893 | 159.4124 | 11.7688 | 28.644 | 4.6073 | 158 | 42.199 | 4.1761 | 94.8598 | 0
12094 | 924.1305 | 7.1229 | 26.6657 | 101.9172 | -4.9959 | 6.6508 | 95.859 | 1.5835 |  | 12.0962 | 47.408 | 10.5472 |  | 53.93 | 149.6991 | 11.346 | 28.4752 | 3.5966 | 147 | -33.3039 | 4.1814 | 94.6203 | 0
12095 | 388.8303 | 3.0157 | 10.1937 | 41.3225 | 0.93035 | 0.001848 | 38.5692 | 0.64916 |  | 5.0915 | 20.9741 | 4.7828 |  | 21.2529 | 64.8602 | 4.5756 | 11.4079 | 1.3077 | 130 | 8.5041 | 1.0588 | 20.7756 | 0
12096 | 901.6272 | 5.6202 | 23.4849 | 103.1574 | -6.4517 | 6.6497 | 80.2083 | 2.25 |  | 10.8947 | 43.1484 | 10.8764 |  | 47.7394 | 126.1739 | 14.5151 | 28.6193 | 2.4607 | 126 | 34.4871 | 4.1911 | 91.8362 | 0
12097 | 891.1891 | 4.098 | 23.3515 | 102.705 | -8.6376 | 8.5495 | 78.269 | 1.9142 |  | 10.8605 | 42.0911 | 10.6874 |  | 45.8249 | 125.7795 | 15.7757 | 28.4399 | 2.396 | 120 | 37.0652 | 4.1915 | 87.6267 | 0
12098 | 883.2181 | 3.3278 | 22.8432 | 102.9319 | -10.6374 | 10.4495 | 75.3349 | 2.479 |  | 10.8235 | 41.1758 | 13.0369 |  | 42.7526 | 130.9654 | 15.9352 | 28.114 | 2.3408 | 113 | 36.8456 | 4.1983 | 88.1207 | 0
12099 | 883.7836 | 3.5482 | 22.5007 | 102.9583 | -7.6379 | 7.6008 | 60.9208 | 2.2944 |  | 10.8809 | 40.6566 | 18.1855 |  | 40.7656 | 129.3588 | 15.6883 | 28.0806 | 2.3282 | 108 | 37.2726 | 4.2072 | 89.2301 | 0
12100 | 898.816 | 3.233 | 22.3451 | 100.9885 | -8.6386 | 8.5497 | 54.9588 | 1.6512 |  | 12.5247 | 39.3653 | 17.407 |  | 39.5832 | 125.113 | 14.3314 | 28.2555 | 2.2818 | 110 | 34.27 | 4.2076 | 92.7882 | 0
12101 | 930.3187 | 3.4289 | 38.8347 | 99.1456 | -10.6376 | 10.4495 | 59.1597 | 1.4317 |  | 16.8239 | 39.6649 | 13.4504 |  | 44.0478 | 122.9172 | 11.9004 | 28.0032 | 2.165 | 113 | 36.1684 | 4.2155 | 100.2285 | 0.016813
12102 | 972.4969 | 3.8809 | 57.6186 | 99.5922 | -3.1677 | 11.3997 | 74.3294 | 2.3117 |  | 21.0077 | 44.9081 | 18.0722 |  | 72.8142 | 133.4452 | 15.2588 | 27.8128 | 2.7764 | 185 | 42.0822 | 4.2632 | 108.7347 | 0.12635
12103 | 1018.7445 | 6.5977 | 82.7625 | 104.4286 | 13.7659 | 18.0482 | 98.4688 | 3.3972 |  | 24.2265 | 65.2675 | 30.7789 |  | 110.883 | 186.5101 | 27.9698 | 30.6338 | 5.4947 | 259 | 60.6867 | 4.8702 | 115.1066 | 0.23757
12104 | 1094.58 | 10.7956 | 108.4077 | 119.2563 | 29.0667 | 18.9997 | 119.3578 | 4.6632 |  | 28.0724 | 87.5269 | 36.208 |  | 139.2786 | 252.3692 | 38.2241 | 35.6499 | 11.1108 | 303 | 64.4281 | 5.0208 | 143.5489 | 0.21731
12105 | 1166.831 | 12.3317 | 120.8602 | 136.5135 | 34.9379 | 16.1508 | 135.6608 | 5.366 |  | 32.8703 | 96.0892 | 34.8674 |  | 158.4634 | 283.7391 | 39.6964 | 38.5745 | 15.0487 | 317 | 59.9655 | 4.8858 | 171.4222 | 0.27584
12106 | 1206.075 | 9.0396 | 122.2778 | 142.653 | 38.7202 | 18.0495 | 148.2939 | 4.4793 |  | 33.6549 | 98.1037 | 37.3193 |  | 170.7757 | 304.5286 | 39.5845 | 41.0477 | 16.1563 | 384 | 64.304 | 4.9406 | 180.3255 | 0.22023
12107 | 1229.5757 | 10.1921 | 123.4685 | 141.4601 | 45.5719 | 18.05 | 171.0262 | 4.077 |  | 34.9459 | 97.0555 | 38.5805 |  | 176.0014 | 314.8844 | 40.9572 | 41.3814 | 16.5848 | 333 | 63.605 | 5.0928 | 180.3279 | 0.18245
12108 | 1241.3062 | 16.0264 | 122.1011 | 143.9059 | 57.7127 | 16.1505 | 177.1406 | 4.2051 |  | 32.0492 | 96.8702 | 37.0973 |  | 173.1873 | 308.5927 | 41.7577 | 40.6592 | 16.9557 | 330 | 58.9348 | 5.6024 | 181.4162 | 0.15651
12109 | 1235.4124 | 19.2311 | 121.5625 | 147.9493 | 72.1056 | 13.3008 | 186.4546 | 4.2124 |  | 28.3538 | 98.5413 | 37.0052 |  | 175.0548 | 309.2512 | 41.7862 | 41.9718 | 17.6592 | 291 | 54.2346 | 5.4735 | 188.977 | 0.25506
12110 | 1211.5134 | 17.7969 | 124.5862 | 150.13 | 66.2522 | 25.6466 | 192.1761 | 4.7463 |  | 31.0553 | 99.0432 | 36.8895 |  | 174.4349 | 314.2032 | 40.8077 | 42.2343 | 18.1052 | 311 | 54.0071 | 5.6139 | 185.776 | 0.2755
12111 | 1184.2589 | 14.5068 | 123.6561 | 143.1014 | 70.3313 | 21.8511 | 184.8476 | 4.3638 |  | 32.5926 | 99.9854 | 33.9122 |  | 166.563 | 318.2139 | 37.5501 | 41.7631 | 18.0155 | 303 | 54.3228 | 4.5977 | 177.9349 | 0.17255
12112 | 1153.5815 | 13.7282 | 119.6118 | 126.4344 | 67.5283 | 14.2521 | 170.5836 | 2.8309 |  | 30.421 | 96.3837 | 32.3412 |  | 150.717 | 291.6522 | 28.9726 | 40.1279 | 17.2661 | 275 | 54.4097 | 4.1664 | 149.3547 | 0.086782
12113 | 1123.6573 | 12.5596 | 106.3676 | 114.3973 | 58.2359 | 9.5013 | 154.0661 | 1.7526 |  | 25.2262 | 84.8088 | 30.4013 |  | 118.1151 | 241.3138 | 19.7464 | 37.2077 | 16.2829 | 273 | 51.7745 | 4.1744 | 115.3184 | 0.18086
12114 | 1071.4823 | 7.311 | 83.2027 | 105.5032 | 40.786 | 10.4497 | 122.0414 | 1.1907 |  | 21.6821 | 70.8628 | 22.7849 |  | 89.4414 | 199.7654 | 15.7136 | 34.732 | 12.9938 | 239 | 46.4513 | 4.1898 | 104.3404 | 0.043179
12115 | 1028.1864 | 3.5459 | 63.6207 | 99.2739 | 28.2622 | 10.45 | 111.9571 | 1.0014 |  | 20.6983 | 61.7539 | 11.2945 |  | 76.7326 | 180.0569 | 14.1625 | 31.2612 | 7.247 | 215 | 44.748 | 4.2189 | 101.5503 | 0.042561
12116 | 988.7518 | 3.1768 | 38.5783 | 95.824 | 29.9259 | 6.6511 | 108.2458 | 1.1477 |  | 17.7086 | 50.8314 | 7.2617 |  | 65.5517 | 173.9149 | 14.3019 | 28.5872 | 4.1852 | 210 | 43.3262 | 4.2026 | 92.7757 | 0.029747
12117 | 969.7105 | 3.7873 | 24.6366 | 95.2522 | 28.8485 | 7.5997 | 81.3452 | 1.2599 |  | 13.8515 | 44.1645 | 7.3306 |  | 60.1369 | 171.5299 | 13.8312 | 27.8206 | 3.5603 | 211 | 38.3061 | 4.1808 | 90.1009 | 0
12118 | 958.7019 | 3.8301 | 23.1145 | 96.7271 | 27.7301 | 7.6 | 83.4504 | 1.3336 |  | 12.719 | 44.8987 | 7.3994 |  | 55.8525 | 162.1952 | 11.418 | 27.6995 | 3.0824 | 191 | 44.8883 | 4.1875 | 92.1556 | 0
12119 | 397.228 | 1.5662 | 9.08 | 37.8873 | 17.4496 | 0.002112 | 40.3067 | 0.60609 |  | 5.6497 | 20.5482 | 3.4915 |  | 21.2592 | 68.746 | 4.0622 | 10.9091 | 1.3009 | 184 | 9.9078 | 1.0399 | 20.6612 | 0
12120 | 917.4583 | 2.727 | 22.4702 | 96.6452 | 24.6034 | 8.5505 | 72.3232 | 2.1571 |  | 11.3335 | 42.0403 | 8.18 |  | 47.5579 | 143.908 | 12.3458 | 27.3822 | 2.5155 | 162 | 34.9646 | 4.1846 | 91.4664 | 0
12121 | 899.8492 | 2.5798 | 29.3596 | 98.0187 | 25.7243 | 6.6505 | 55.349 | 2.0256 |  | 11.2456 | 40.8085 | 8.0703 |  | 42.1556 | 146.8289 | 13.3277 | 27.1697 | 2.4883 | 153 | 34.7047 | 4.1904 | 89.8178 | 0
12122 | 882.1798 | 2.5116 | 38.748 | 101.9191 | 21.1552 | 10.4489 | 55.0582 | 1.6759 |  | 11.002 | 40.4226 | 7.9314 |  | 39.9445 | 139.2982 | 13.4074 | 27.0612 | 2.3517 | 154 | 32.7813 | 4.1979 | 87.0872 | 0
12123 | 879.0932 | 2.4539 | 40.8375 | 103.8483 | 24.4283 | 7.6008 | 52.007 | 1.7991 |  | 10.5865 | 40.185 | 7.8317 |  | 39.6308 | 130.2615 | 13.5228 | 27.4566 | 2.391 | 152 | 28.8159 | 4.1897 | 85.9154 | 0
12124 | 876.255 | 2.7963 | 31.6843 | 101.2684 | 29.5438 | 10.4492 | 52.1692 | 1.6372 |  | 9.1313 | 38.9264 | 6.3557 |  | 38.7539 | 121.0107 | 12.2919 | 27.3048 | 2.3748 | 162 | 27.8579 | 4.1998 | 82.4287 | 0
12125 | 879.7614 | 2.5857 | 26.3292 | 97.8769 | 38.8663 | 10.45 | 51.2492 | 1.7489 |  | 8.1255 | 38.3425 | 5.1339 |  | 37.2349 | 122.4646 | 9.9465 | 27.2031 | 2.2011 | 144 | 29.2562 | 4.2005 | 79.7655 | 0.017362
12126 | 891.9934 | 2.0406 | 38.9765 | 94.3241 | 45.2036 | 6.6511 | 52.4334 | 1.858 |  | 8.2881 | 38.6142 | 5.1279 |  | 36.6454 | 124.44 | 8.8721 | 27.1535 | 2.1127 | 134 | 22.6245 | 4.2047 | 82.4694 | 0.12896
12127 | 895.116 | 2.1594 | 50.3141 | 92.5577 | 44.7193 | 8.5495 | 65.1872 | 1.4551 |  | 8.9186 | 38.413 | 7.3156 |  | 37.7702 | 124.311 | 9.2111 | 26.7566 | 2.2245 | 138 | 32.2941 | 4.2025 | 84.3129 | 0.2888
12128 | 895.2542 | 2.5986 | 54.8006 | 92.6934 | 47.8679 | 8.55 | 98.6035 | 1.3872 |  | 9.4065 | 42.0351 | 12.4186 |  | 41.9049 | 123.0272 | 9.0238 | 26.4023 | 2.3767 | 138 | 29.8201 | 4.1928 | 88.2548 | 0.31976
12129 | 909.3601 | 2.826 | 71.4649 | 94.3761 | 55.6131 | 6.6505 | 134.2996 | 1.5319 |  | 10.9793 | 46.5131 | 15.0287 |  | 46.9447 | 124.7474 | 9.0826 | 26.2644 | 4.655 | 143 | 26.2544 | 4.194 | 90.8553 | 0.34827
12130 | 938.5739 | 3.0073 | 87.5453 | 94.7444 | 62.827 | 6.65 | 142.0403 | 1.5152 |  | 15.3442 | 48.8818 | 15.2148 |  | 53.9981 | 127.9 | 8.7574 | 26.5574 | 9.2519 | 173 | 30.6561 | 4.1844 | 92.3045 | 0.32638
12131 | 991.4277 | 3.3864 | 95.0935 | 94.8911 | 65.1518 | 7.5997 | 131.4571 | 1.2174 |  | 17.5247 | 52.1486 | 15.5294 |  | 58.2447 | 136.2838 | 8.5072 | 26.8895 | 11.4878 | 172 | 26.0056 | 4.184 | 92.3383 | 0.25336
12132 | 990.708 | 5.883 | 98.2521 | 95.3497 | 57.0416 | 8.5497 | 130.758 | 1.003 |  | 17.2226 | 57.6874 | 15.5743 |  | 62.3957 | 138.8105 | 9.2488 | 26.7282 | 11.4467 | 169 | 21.7114 | 4.1746 | 89.9423 | 0.26869
12133 | 964.4594 | 9.3328 | 89.9509 | 94.1543 | 39.1587 | 8.55 | 114.6302 | 1.1841 |  | 17.3138 | 60.3747 | 15.4751 |  | 70.4522 | 148.3051 | 9.4493 | 27.0455 | 11.398 | 222 | 23.4344 | 4.1766 | 87.401 | 0.2916
12134 | 960.292 | 7.2567 | 72.2147 | 92.4887 | 24.2361 | 10.4495 | 101.7798 | 1.1224 |  | 17.2279 | 60.7463 | 16.1873 |  | 72.7109 | 159.5253 | 9.1436 | 27.1969 | 9.4105 | 222 | 28.8439 | 4.1845 | 90.6854 | 0.29011
12135 | 975.0142 | 7.3752 | 56.1047 | 91.8766 | 24.0528 | 8.5505 | 98.9751 | 1.0063 |  | 15.3871 | 63.6645 | 15.8218 |  | 61.7021 | 167.0192 | 8.7623 | 27.1049 | 5.4174 | 208 | 34.5764 | 4.1799 | 87.5422 | 0.30177
12136 | 972.627 | 10.1922 | 36.0902 | 91.0753 | 22.1057 | 9.4997 | 96.0873 | 1.5662 |  | 12.8614 | 64.6049 | 12.1902 |  | 53.7572 | 164.8033 | 8.6373 | 27.6493 | 3.0301 | 196 | 28.3904 | 4.1368 | 76.3355 | 0.25354
12137 | 961.4864 | 8.6487 | 26.686 | 91.2368 | 26.6053 | 9.5 | 90.3826 | 1.82 |  | 13.2163 | 61.7483 | 8.9511 |  | 52.1839 | 160.8341 | 8.8781 | 27.9608 | 2.6297 | 203 | 32.912 | 4.1798 | 80.8411 | 0.27597
12138 | 959.3293 | 4.9865 | 26.5398 | 92.6394 | 37.6536 | 8.5503 | 92.7851 | 1.5196 |  | 14.4615 | 55.7525 | 6.8388 |  | 49.6043 | 157.9009 | 8.7241 | 27.8609 | 2.6328 | 208 | 39.2708 | 4.2278 | 82.2748 | 0.25862
12139 | 941.2874 | 3.2695 | 26.0547 | 92.6344 | 39.9914 | 9.4997 | 99.9625 | 1.3586 |  | 13.4955 | 49.0978 | 5.6924 |  | 47.3327 | 148.5444 | 8.4925 | 28.0943 | 2.4972 | 214 | 43.3133 | 4.2067 | 82.8974 | 0.2012
12140 | 920.1397 | 4.1198 | 25.6862 | 92.3909 | 36.8899 | 9.5 | 101.1242 | 1.9616 |  | 13.0885 | 43.1327 | 6.1744 |  | 46.4778 | 143.9694 | 8.7424 | 28.2716 | 2.2353 | 221 | 47.2615 | 4.2009 | 82.0845 | 0.091824
12141 | 907.5535 | 4.632 | 25.8994 | 92.5784 | 35.029 | 9.5 | 99.5161 | 1.9963 |  | 13.8137 | 40.9465 | 8.0205 |  | 49.1479 | 146.2382 | 8.9711 | 27.8294 | 2.1945 | 211 | 48.1693 | 4.2032 | 82.6551 | 0
12142 | 896.2605 | 5.9411 | 26.5822 | 93.3365 | 32.7394 | 10.4497 | 89.8343 | 2.4322 |  | 13.8137 | 41.6697 | 8.7447 |  | 49.5434 | 151.9302 | 8.9994 | 27.6912 | 2.2849 | 188 | 48.7825 | 4.2019 | 86.4072 | 0
12143 | 381.356 | 3.3539 | 10.9389 | 37.2531 | 22.141 | 0.002903 | 35.9972 | 1.3688 |  | 10.6963 | 19.3095 | 3.7286 |  | 19.8532 | 70.0303 | 3.6252 | 11.189 | 1.0432 | 158 | 10.5002 | 1.0681 | 18.7714 | 0
12144 | 879.3457 | 10.1159 | 26.4728 | 94.6954 | 30.1503 | 10.4497 | 68.3185 | 2.2036 |  | 10.6963 | 40.9358 | 8.4975 |  | 43.546 | 142.6875 | 12.2262 | 27.8473 | 2.9214 | 161 | 45.1661 | 4.2123 | 78.1803 | 0
12145 | 876.4078 | 8.5556 | 26.5926 | 93.5421 | 29.5036 | 9.5003 | 68.509 | 2.388 |  | 10.3912 | 40.1887 | 8.2378 |  | 42.9957 | 141.1868 | 13.1814 | 27.5252 | 3.0955 | 162 | 46.7066 | 4.2258 | 79.7764 | 0
12146 | 880.972 | 5.1626 | 26.657 | 93.7299 | 25.8533 | 11.3995 | 62.4938 | 2.8105 |  | 10.6617 | 40.0341 | 8.0558 |  | 42.4871 | 137.618 | 13.0305 | 27.6682 | 2.8973 | 153 | 47.5046 | 4.2232 | 79.1987 | 0
12147 | 875.773 | 2.9159 | 26.6879 | 93.5041 | 27.0377 | 9.5005 | 56.6952 | 2.3384 |  | 10.5545 | 40.5543 | 7.7826 |  | 42.0186 | 133.1762 | 13.5354 | 27.4943 | 2.5698 | 142 | 42.4372 | 4.2241 | 80.1289 | 0
12148 | 872.4908 | 3.046 | 26.5664 | 89.8262 | 23.1095 | 12.3492 | 59.2673 | 2.3245 |  | 9.0661 | 40.0113 | 6.08 |  | 38.8551 | 131.1004 | 12.1235 | 27.04 | 2.353 | 137 | 42.0741 | 4.2337 | 76.1091 | 0
12149 | 875.5491 | 2.8033 | 29.3001 | 88.0417 | 25.0161 | 9.5008 | 57.8167 | 2.0386 |  | 8.0457 | 39.3202 | 4.9488 |  | 37.5105 | 124.1077 | 9.8782 | 26.8906 | 2.2563 | 142 | 42.005 | 4.2312 | 78.2363 | 0.017641
12150 | 895.0899 | 2.2892 | 42.4495 | 89.3972 | 24.1817 | 9.5 | 48.8093 | 2.2859 |  | 9.5617 | 41.7787 | 5.3191 |  | 37.7357 | 116.5708 | 8.7402 | 27.1251 | 2.2368 | 141 | 38.0906 | 4.2329 | 76.4118 | 0.04417
12151 | 902.6752 | 2.1285 | 58.3331 | 89.1211 | 23.4822 | 9.5 | 51.3635 | 2.0298 |  | 12.6198 | 44.9827 | 5.5919 |  | 37.2449 | 112.1226 | 8.1893 | 26.8529 | 2.2197 | 139 | 25.8438 | 4.2376 | 76.1481 | 0.08196
12152 | 912.3415 | 2.0294 | 67.5604 | 90.6826 | 21.9734 | 10.4497 | 66.5988 | 1.3566 |  | 11.7194 | 41.5945 | 5.7289 |  | 38.644 | 116.2273 | 8.257 | 26.5746 | 2.8193 | 135 | 20.368 | 4.2349 | 79.5969 | 0.12306
12153 | 935.9968 | 2.7972 | 67.6876 | 90.5426 | 20.8435 | 11.3997 | 89.2539 | 1.4167 |  | 10.4674 | 38.6759 | 6.0947 |  | 43.4508 | 123.8653 | 8.6892 | 26.8015 | 3.9832 | 193 | 14.8922 | 4.2379 | 83.5286 | 0.25778
12154 | 964.2767 | 2.8741 | 65.0549 | 91.7328 | 22.3891 | 10.4503 | 96.0172 | 1.3331 |  | 14.6648 | 40.4117 | 6.1272 |  | 49.986 | 129.0966 | 8.7904 | 27.4406 | 4.5375 | 174 | 12.0157 | 4.2403 | 87.0592 | 0.29315
12155 | 985.3228 | 3.2372 | 64.5978 | 93.3716 | 25.4419 | 8.5505 | 82.5383 | 1.2869 |  | 16.9926 | 50.5905 | 5.8314 |  | 62.4229 | 129.3448 | 8.3765 | 27.5832 | 4.687 | 168 | 11.0832 | 4.23 | 88.8995 | 0.26098
12156 | 994.6638 | 7.2324 | 65.6406 | 92.2306 | 25.4997 | 9.4997 | 86.0526 | 1.3182 |  | 16.5582 | 69.3414 | 8.3635 |  | 73.5585 | 129.6374 | 8.2183 | 27.5441 | 4.8853 | 193 | 20.7511 | 4.2353 | 88.3156 | 0.27298
12157 | 1006.5247 | 8.1261 | 66.2625 | 90.5988 | 26.1743 | 10.4497 | 100.8531 | 1.5184 |  | 16.7774 | 72.2563 | 10.6597 |  | 71.7029 | 143.8799 | 8.6122 | 27.6195 | 5.0997 | 185 | 17.5601 | 4.2351 | 90.9564 | 0.29511
12158 | 1014.9895 | 8.577 | 66.302 | 90.0497 | 28.8344 | 9.5003 | 104.2908 | 1.4725 |  | 16.3297 | 64.2598 | 15.132 |  | 74.7407 | 159.7635 | 8.5858 | 27.4352 | 5.1364 | 185 | 19.1163 | 4.2293 | 87.7574 | 0.2923
12159 | 1016.4216 | 7.3778 | 57.7546 | 92.509 | 29.7511 | 9.5 | 106.4417 | 1.3132 |  | 14.2305 | 66.305 | 22.2389 |  | 78.568 | 163.2244 | 8.4005 | 27.9984 | 5.2367 | 181 | 25.7332 | 4.2259 | 84.9622 | 0.30124
12160 | 1001.756 | 7.7887 | 36.7105 | 93.9237 | 31.3695 | 8.5503 | 97.1166 | 1.1587 |  | 10.8387 | 75.3844 | 19.2389 |  | 70.4062 | 166.407 | 8.5096 | 27.8793 | 4.9846 | 179 | 29.5441 | 4.1772 | 84.3104 | 0.2513
12161 | 1000.6705 | 14.1797 | 25.9466 | 93.4982 | 30.1139 | 10.4495 | 84.9365 | 1.0603 |  | 9.2928 | 71.2801 | 11.9191 |  | 63.3809 | 171.5767 | 8.4735 | 27.7442 | 4.4402 | 169 | 27.0391 | 4.2121 | 74.439 | 0.27194
12162 | 1004.6555 | 17.3175 | 25.7501 | 92.1933 | 33.5675 | 7.6008 | 92.2691 | 1.3322 |  | 9.3226 | 57.7248 | 10.2037 |  | 62.836 | 166.9021 | 8.9224 | 27.679 | 4.1572 | 160 | 29.5019 | 4.2588 | 67.7329 | 0.25833
12163 | 988.2766 | 17.2716 | 25.605 | 90.8584 | 30.4399 | 9.4995 | 101.0844 | 1.7011 |  | 9.428 | 50.6665 | 10.4611 |  | 61.709 | 153.9512 | 8.8778 | 27.5864 | 3.9042 | 144 | 35.1346 | 4.2325 | 65.6769 | 0.023547
12164 | 967.8096 | 14.8275 | 25.263 | 90.1581 | 29.7299 | 9.5 | 101.2873 | 2.1591 |  | 9.8446 | 46.0534 | 9.2103 |  | 53.2825 | 149.6638 | 8.5313 | 27.5925 | 3.6873 | 143 | 39.569 | 4.2241 | 67.4086 | 0.018357
12165 | 950.4203 | 12.4248 | 25.4454 | 89.7457 | 29.6971 | 9.5 | 95.4996 | 2.2897 |  | 10.0518 | 44.3316 | 9.7412 |  | 49.088 | 142.1276 | 8.3295 | 27.5709 | 3.3622 | 120 | 40.4286 | 0 | 70.9519 | 0
12166 | 927.009 | 11.6407 | 25.9496 | 95.761 | -7.7895 | 10.4497 | 80.9479 | 2.7363 |  | 11.3995 | 45.2843 | 10.0814 |  | 53.1759 | 134.9747 | 8.3931 | 27.6537 | 2.6777 | 124 | 44.2958 | 4.2284 | 74.5189 | 0
12167 | 385.6595 | 5.0605 | 10.4465 | 38.968 | 20.1407 | 0.002903 | 31.0349 | 1.3924 |  | 5.453 | 20.8934 | 4.1283 |  | 22.3282 | 60.4142 | 3.3674 | 10.9396 | 1.0209 | 118 | 9.6519 | 1.0541 | 15.0074 | 0
12168 | 901.2299 | 4.4742 | 26.2156 | 97.8982 | 26.631 | 10.4503 | 79.6242 | 2.553 |  | 12.0132 | 46.0134 | 8.8562 |  | 47.3141 | 125.7644 | 12.4936 | 27.8474 | 2.3119 | 118 | 35.8386 | 4.2407 | 76.7286 | 0
12169 | 896.6803 | 2.3538 | 28.7943 | 97.3618 | 23.1802 | 13.2992 | 83.9447 | 2.3662 |  | 11.5456 | 44.5951 | 8.4748 |  | 41.7728 | 123.3471 | 13.5508 | 27.6628 | 2.3325 | 108 | 36.1658 | 4.2413 | 79.6003 | 0
12170 | 899.9265 | 2.4711 | 28.0197 | 96.9546 | 27.2689 | 8.5513 | 73.7684 | 2.5728 |  | 11.4999 | 42.7678 | 8.3808 |  | 40.4571 | 121.6723 | 12.9527 | 27.6045 | 2.3277 | 110 | 37.1009 | 4.2407 | 80.4921 | 0
12171 | 885.7089 | 2.5084 | 26.0596 | 94.1837 | 23.5109 | 11.3992 | 79.8999 | 3.4918 |  | 11.3706 | 40.6031 | 8.3978 |  | 39.987 | 119.5901 | 12.9295 | 27.826 | 2.3268 | 108 | 37.5648 | 4.2393 | 82.378 | 0
12172 | 885.4158 | 2.9575 | 25.5284 | 90.0404 | 24.7293 | 9.5005 | 94.1937 | 2.4276 |  | 11.9324 | 9.9371 | 6.8373 |  | 38.4843 | 114.8184 | 11.555 | 27.3957 | 2.208 | 109 | 33.9569 | 4.2489 | 94.8518 | 0
12173 | 896.6543 | 3.0516 | 34.0642 | 88.2522 | 23.0981 | 10.4497 | 78.7729 | 2.2267 |  | 17.0447 | 38.8393 | 6.7043 |  | 43.9452 | 116.5974 | 9.2624 | 26.8647 | 2.317 | 107 | 33.631 | 4.2493 | 101.7205 | 0.13239
12174 | 926.2715 | 3.6981 | 52.4316 | 90.1881 | 20.7554 | 12.3495 | 69.8119 | 2.2498 |  | 21.249 | 43.0979 | 14.2169 |  | 66.9414 | 130.6281 | 11.7809 | 26.3989 | 3.3047 | 182 | 41.5187 | 4.2483 | 113.4451 | 0.17521
12175 | 1000.0881 | 8.3833 | 85.4138 | 101.4031 | 14.7701 | 18.0484 | 93.4173 | 2.9608 |  | 23.0304 | 62.9812 | 25.7425 |  | 100.724 | 180.0023 | 25.235 | 29.2772 | 7.7389 | 241 | 52.956 | 4.2478 | 140.1459 | 0.25273
12176 | 1111.3261 | 14.7492 | 106.8975 | 114.1573 | 14.2605 | 19.9495 | 123.6045 | 4.4049 |  | 26.7448 | 80.4968 | 31.0723 |  | 135.8103 | 238.9843 | 36.3816 | 36.1398 | 14.0463 | 283 | 59.3989 | 4.3526 | 168.6285 | 0.2759
12177 | 1199.5919 | 16.2835 | 116.9341 | 134.1074 | 17.1901 | 19.95 | 139.1272 | 4.8242 |  | 32.2744 | 87.1627 | 35.3466 |  | 161.8869 | 281.8618 | 41.6083 | 40.8346 | 17.7584 | 347 | 64.6927 | 4.4606 | 180.8919 | 0.31752
12178 | 1245.6474 | 14.3729 | 118.9017 | 142.1916 | 20.5601 | 21.8495 | 143.4893 | 4.7101 |  | 35.9721 | 87.9696 | 39.0564 |  | 170.9323 | 307.0998 | 42.953 | 43.4317 | 18.7865 | 372 | 65.5794 | 5.1153 | 188.3469 | 0.2951
12179 | 1261.7738 | 10.9456 | 119.1305 | 141.6068 | 24.8284 | 22.7997 | 145.3195 | 4.6579 |  | 38.16 | 88.2308 | 39.4875 |  | 177.8087 | 313.4176 | 42.575 | 45.5636 | 18.904 | 368 | 64.2022 | 5.3446 | 191.3348 | 0.25886
12180 | 1257.7136 | 8.6402 | 119.4471 | 142.5371 | 28.8373 | 20.9005 | 141.2843 | 4.5371 |  | 37.244 | 92.1856 | 40.9978 |  | 176.7919 | 315.6035 | 43.8643 | 44.475 | 18.866 | 342 | 65.4781 | 5.0979 | 190.0374 | 0.26851
12181 | 1246.0789 | 8.3899 | 117.6587 | 147.9187 | 27.9296 | 22.7995 | 137.6382 | 4.5247 |  | 38.5559 | 97.2529 | 42.8701 |  | 174.4856 | 317.9347 | 44.5269 | 43.938 | 19.184 | 305 | 69.5742 | 4.767 | 194.8406 | 0.28405
12182 | 1262.7388 | 9.5373 | 117.3379 | 149.4474 | 29.633 | 22.8 | 139.7983 | 4.8223 |  | 40.0185 | 101.5613 | 41.8554 |  | 176.9476 | 314.8352 | 42.9838 | 44.5872 | 19.4173 | 324 | 69.9114 | 5.8899 | 195.3867 | 0.2777
12183 | 1266.3461 | 11.1148 | 116.791 | 144.394 | 32.9493 | 21.8503 | 138.6417 | 4.9977 |  | 37.934 | 101.1108 | 38.7102 |  | 170.2186 | 298.3751 | 42.2105 | 44.7832 | 19.4133 | 288 | 66.733 | 5.5963 | 187.5523 | 0.29713
12184 | 1219.9938 | 9.3124 | 113.4488 | 136.288 | 43.8768 | 14.2521 | 131.3352 | 4.3865 |  | 34.9792 | 97.7024 | 35.9785 |  | 151.0672 | 263.7545 | 34.1468 | 43.2694 | 19.0152 | 263 | 53.8111 | 5.151 | 157.3496 | 0.22824
12185 | 1158.1683 | 5.9464 | 109.6463 | 123.9404 | 50.2822 | 11.404 | 129.9019 | 3.5904 |  | 30.4019 | 91.2916 | 35.7835 |  | 115.2226 | 216.9266 | 19.8359 | 40.7651 | 18.2062 | 231 | 47.9981 | 5.0351 | 132.3679 | 0.26957
12186 | 1103.5059 | 3.9184 | 105.4815 | 109.222 | 50.419 | 11.3968 | 115.5812 | 2.8152 |  | 26.3879 | 77.8742 | 31.0691 |  | 78.3834 | 184.8447 | 14.0139 | 37.7142 | 14.2409 | 218 | 47.3569 | 4.3387 | 119.0699 | 0.19111
12187 | 1053.6134 | 3.6938 | 84.7119 | 101.9495 | 47.9733 | 11.4032 | 88.0599 | 2.4454 |  | 23.5254 | 68.9952 | 16.9797 |  | 61.0068 | 172.7617 | 12.0971 | 33.9622 | 8.0972 | 216 | 44.7984 | 3.0051 | 100.3485 | 0.045936
12188 | 1010.1017 | 3.6793 | 46.3194 | 99.3125 | 44.831 | 12.3466 | 70.9233 | 1.8464 |  | 20.0295 | 65.806 | 11.272 |  | 55.0689 | 156.9792 | 10.1498 | 30.5377 | 5.0251 | 197 | 47.285 | 2.6267 | 90.7453 | 0.057243
12189 | 986.3216 | 3.9191 | 27.2659 | 97.5646 | 41.6736 | 13.2997 | 81.42 | 2.338 |  | 15.8072 | 56.9633 | 15.0427 |  | 51.9869 | 140.2083 | 10.0969 | 28.9474 | 4.3214 | 184 | 50.8818 | 2.6211 | 87.9155 | 0
12190 | 948.8477 | 3.9436 | 26.2689 | 96.884 | 44.0166 | 7.6037 | 89.4941 | 2.5145 |  | 14.8539 | 47.2133 | 15.6809 |  | 48.5989 | 136.235 | 10.4728 | 29.5102 | 3.4655 | 148 | 45.7076 | 2.6232 | 91.0809 | 0
12191 | 396.0676 | 1.6801 | 10.6795 | 38.2706 | 25.1775 | 0 | 37.719 | 0.90592 |  | 6.9651 | 20.4061 | 6.5624 |  | 19.1527 | 62.5484 | 4.2692 | 12.0203 | 1.3693 | 122 | 9.3789 | 0.657 | 20.7824 | 0
12192 | 880.8856 | 2.756 | 26.4332 | 97.0752 | 35.4147 | 8.55 | 78.7178 | 3.0462 |  | 14.8385 | 42.7681 | 7.8512 |  | 42.1496 | 133.8279 | 10.2459 | 30.3327 | 2.9208 | 115 | 41.0624 | 2.6235 | 89.2802 | 0
12193 | 869.7201 | 2.7468 | 26.5056 | 96.9796 | 31.417 | 10.4495 | 86.3611 | 2.6158 |  | 14.838 | 42.1658 | 7.2916 |  | 42.1059 | 127.2667 | 10.8426 | 30.327 | 3.2245 | 112 | 38.8309 | 2.6307 | 88.9518 | 0
12194 | 876.7793 | 2.3239 | 26.4987 | 97.1888 | 30.4232 | 9.5003 | 88.2635 | 2.7483 |  | 14.8721 | 41.4124 | 8.3382 |  | 42.2368 | 122.3941 | 10.8017 | 30.4141 | 3.4217 | 116 | 39.7788 | 2.6276 | 87.0407 | 0
12195 | 882.5668 | 2.2491 | 26.4667 | 96.364 | 27.853 | 10.4497 | 91.9018 | 3.3058 |  | 14.316 | 41.3697 | 7.7661 |  | 42.4033 | 119.7934 | 10.3297 | 30.7611 | 3.3058 | 107 | 40.0613 | 2.6252 | 86.9318 | 0
12196 | 881.5337 | 2.833 | 26.2452 | 94.3093 | 26.4335 | 10.45 | 88.7909 | 2.436 |  | 14.8434 | 39.6663 | 5.2859 |  | 40.5985 | 114.1621 | 9.8712 | 31.2887 | 3.1832 | 108 | 35.4309 | 2.6266 | 95.8996 | 0
12197 | 903.1728 | 3.4202 | 34.8679 | 93.5562 | 24.3655 | 11.3997 | 83.4127 | 2.2131 |  | 18.7023 | 39.6694 | 6.0606 |  | 44.6681 | 112.1731 | 9.9746 | 29.9336 | 3.0896 | 110 | 34.7313 | 2.6267 | 105.8824 | 0.14156
12198 | 954.3949 | 7.485 | 50.1033 | 98.8812 | 22.7529 | 12.3497 | 76.3578 | 3.1624 |  | 21.5076 | 46.7587 | 11.8172 |  | 69.0956 | 123.6974 | 14.0341 | 29.1137 | 3.0816 | 197 | 44.0592 | 2.7054 | 117.7493 | 0.23001
12199 | 1029.381 | 12.0622 | 80.2077 | 109.5076 | 17.505 | 17.0987 | 83.8871 | 3.3297 |  | 24.3171 | 68.3963 | 23.4422 |  | 107.1713 | 175.267 | 26.9342 | 32.7203 | 6.6395 | 242 | 58.6283 | 3.9164 | 132.7916 | 0.29232
12200 | 1135.4093 | 12.0463 | 104.3248 | 124.2466 | 17.2924 | 18.0497 | 113.9608 | 3.7322 |  | 27.1006 | 88.0001 | 32.9231 |  | 142.8211 | 249.0014 | 35.0081 | 38.397 | 13.077 | 249 | 67.3468 | 4.6694 | 168.5925 | 0.32249
12201 | 1229.3355 | 8.0376 | 114.8287 | 138.8508 | 18.131 | 18.05 | 135.3928 | 4.7151 |  | 31.6329 | 94.1125 | 35.1065 |  | 163.7023 | 294.8289 | 37.641 | 42.8529 | 16.8016 | 324 | 62.0976 | 4.6896 | 191.4905 | 0.32048
12202 | 1276.6065 | 5.1761 | 116.4534 | 142.6526 | 15.7914 | 20.905 | 141.7591 | 5.3109 |  | 40.0883 | 95.7559 | 35.5352 |  | 171.244 | 307.6576 | 39.8868 | 45.8559 | 17.7575 | 364 | 65.5905 | 4.8125 | 193.6394 | 0.32379
12203 | 1304.3872 | 5.1196 | 118.316 | 142.1879 | 17.0735 | 20.8942 | 141.2334 | 5.0309 |  | 39.9295 | 97.187 | 36.8718 |  | 179.5062 | 314.8422 | 40.9891 | 45.9939 | 18.0494 | 324 | 68.3171 | 5.146 | 194.2464 | 0.2508
12204 | 1297.2397 | 5.7649 | 122.1086 | 141.8319 | 23.0903 | 19.9503 | 145.1685 | 5.0573 |  | 31.4701 | 98.0037 | 38.1586 |  | 177.7566 | 320.744 | 42.784 | 44.4011 | 17.8346 | 371 | 60.1501 | 6.0635 | 197.7708 | 0.26697
12205 | 1277.1989 | 9.3967 | 120.9111 | 142.1422 | 32.8019 | 18.0505 | 163.437 | 5.1302 |  | 25.7804 | 101.3202 | 39.2826 |  | 176.0487 | 317.5933 | 42.7014 | 45.7578 | 18.0724 | 334 | 65.643 | 6.896 | 201.6843 | 0.29065
12206 | 1272.0963 | 12.1607 | 120.8633 | 144.318 | 36.9154 | 20.905 | 167.3692 | 4.5953 |  | 26.5297 | 105.417 | 38.9355 |  | 178.5471 | 317.6123 | 40.9575 | 43.8758 | 18.5104 | 322 | 63.1764 | 7.5781 | 197.6187 | 0.2882
12207 | 1234.6576 | 9.5007 | 119.7508 | 148.0851 | 45.9825 | 20.8942 | 157.7857 | 4.1553 |  | 32.9634 | 105.0565 | 38.4101 |  | 174.921 | 320.3198 | 39.4809 | 41.9875 | 18.586 | 266 | 62.1781 | 7.3109 | 192.329 | 0.29887
12208 | 1186.0086 | 6.0605 | 114.5397 | 140.6823 | 60.1577 | 13.3021 | 154.5014 | 4.0236 |  | 34.4847 | 101.6632 | 35.9724 |  | 161.7588 | 288.0345 | 32.8754 | 40.3182 | 18.1667 | 254 | 47.652 | 6.7301 | 164.6142 | 0.25257
12209 | 1139.784 | 5.1045 | 110.2052 | 120.1526 | 57.9769 | 11.4005 | 156.3324 | 3.5395 |  | 29.3532 | 92.4621 | 29.5615 |  | 131.8905 | 240.7219 | 21.3685 | 37.4372 | 16.944 | 240 | 44.4517 | 6.0422 | 132.3449 | 0.26902
12210 | 1079.7295 | 4.2015 | 107.4249 | 103.9098 | 49.3158 | 11.4 | 135.1442 | 2.7349 |  | 23.491 | 83.9263 | 21.3157 |  | 96.9778 | 206.2237 | 12.7614 | 34.6033 | 13.2209 | 217 | 42.8615 | 5.2558 | 113.8674 | 0.24545
12211 | 1050.113 | 5.8499 | 90.6984 | 97.6079 | 40.4379 | 7.6011 | 109.6674 | 2.1841 |  | 20.307 | 87.3733 | 12.9758 |  | 76.0469 | 190.2954 | 10.4817 | 32.0358 | 7.5967 | 198 | 40.218 | 4.6398 | 97.9078 | 0.18271
12212 | 1022.2601 | 6.2351 | 50.163 | 92.877 | 29.6809 | 8.5497 | 96.2047 | 2.256 |  | 17.485 | 78.0723 | 8.9805 |  | 67.5237 | 172.3155 | 10.2377 | 30.2739 | 4.5401 | 188 | 40.9723 | 3.8332 | 87.5959 | 0.07168
12213 | 993.182 | 4.532 | 28.3827 | 93.0277 | 26.8103 | 10.4495 | 94.9748 | 2.0386 |  | 12.7958 | 59.38 | 8.8033 |  | 64.2751 | 158.2274 | 10.093 | 29.3792 | 3.4498 | 179 | 41.8877 | 3.6114 | 84.4499 | 0
12214 | 985.3079 | 4.4246 | 26.986 | 99.6835 | 26.6885 | 8.5505 | 89.1226 | 2.3532 |  | 11.7475 | 49.235 | 8.8842 |  | 64.1259 | 149.109 | 10.5388 | 29.1303 | 2.8562 | 161 | 38.8645 | 3.6187 | 86.4576 | 0
12215 | 415.497 | 2.0679 | 10.7655 | 40.2997 | 17.7804 | 0.002376 | 35.1458 | 1.2605 |  | 5.5811 | 20.8757 | 3.8923 |  | 26.0162 | 63.7669 | 4.3157 | 11.5122 | 1.274 | 141 | 8.0377 | 0.90475 | 19.2434 | 0
12216 | 936.0668 | 2.602 | 26.4604 | 101.6862 | 21.4585 | 10.4503 | 70.327 | 2.4608 |  | 12.2976 | 44.647 | 6.8323 |  | 58.8742 | 131.0723 | 10.3745 | 29.4293 | 3.0165 | 119 | 37.6077 | 3.62 | 84.1573 | 0
12217 | 922.3609 | 2.318 | 33.091 | 99.7345 | 28.394 | 10.45 | 64.7538 | 2.461 |  | 12.2836 | 44.8946 | 6.8171 |  | 55.9113 | 129.3182 | 10.8825 | 29.3827 | 2.6329 | 118 | 37.5594 | 3.616 | 83.4727 | 0
12218 | 910.4752 | 2.3622 | 42.1956 | 98.632 | 40.4841 | 8.5505 | 59.5236 | 2.5439 |  | 12.0995 | 44.8429 | 8.9784 |  | 55.5831 | 125.6443 | 10.9462 | 29.1685 | 2.3355 | 126 | 36.6879 | 3.6246 | 82.8761 | 0
12219 | 910.1477 | 2.4386 | 45.1475 | 99.9272 | 40.0555 | 9.4997 | 55.1256 | 2.2709 |  | 11.5068 | 44.3481 | 14.1285 |  | 56.3395 | 121.3336 | 10.8228 | 29.0968 | 2.3388 | 124 | 32.7922 | 3.6145 | 85.0919 | 0
12220 | 913.9318 | 2.3578 | 37.106 | 98.7172 | 36.0034 | 10.4497 | 54.9377 | 2.2561 |  | 12.0337 | 42.7415 | 13.0357 |  | 54.8115 | 115.6883 | 10.3083 | 28.9815 | 2.2558 | 130 | 34.642 | 3.619 | 87.9422 | 0
12221 | 925.1021 | 3.1312 | 42.2059 | 97.3723 | 33.6572 | 9.5003 | 56.7126 | 1.9371 |  | 16.1341 | 42.8839 | 9.3311 |  | 56.8429 | 117.6892 | 10.1369 | 28.2718 | 2.1463 | 117 | 36.5825 | 3.8281 | 95.2536 | 0.11633
12222 | 971.0432 | 8.3529 | 63.1153 | 98.2854 | 27.7852 | 13.2989 | 73.5535 | 2.2771 |  | 21.0406 | 51.4254 | 18.1602 |  | 81.0823 | 132.6237 | 14.3793 | 28.3286 | 2.1072 | 169 | 43.6377 | 5.6924 | 106.8445 | 0.2104
12223 | 1035.8297 | 13.6077 | 89.3562 | 101.38 | 20.9851 | 18.0487 | 99.6142 | 3.4987 |  | 21.4025 | 73.0092 | 32.5353 |  | 117.2027 | 178.369 | 26.5705 | 30.9909 | 3.0612 | 269 | 55.5937 | 7.1435 | 125.5769 | 0.27651
12224 | 1131.7022 | 16.9222 | 106.4886 | 116.3632 | 18.8005 | 18.9997 | 121.2355 | 5.1889 |  | 22.9829 | 90.7722 | 39.5214 |  | 147.7713 | 243.3884 | 36.3458 | 36.1752 | 5.7739 | 300 | 68.444 | 8.5874 | 164.8535 | 0.3136
12225 | 1242.3251 | 17.4849 | 114.233 | 132.8957 | 18.5469 | 19 | 135.6595 | 6.2948 |  | 29.7582 | 95.7568 | 40.2289 |  | 168.1371 | 294.896 | 39.9583 | 40.3626 | 7.2026 | 330 | 69.1173 | 8.7698 | 189.8373 | 0.32024
12226 | 1285.3949 | 15.832 | 116.8936 | 148.8831 | 16.7441 | 20.8995 | 140.053 | 5.6159 |  | 35.2487 | 97.1046 | 40.0221 |  | 176.5265 | 319.5636 | 42.5122 | 51.1343 | 7.3369 | 340 | 58.8638 | 10.4868 | 195.4183 | 0.32748
12227 | 1288.1396 | 12.461 | 118.9806 | 152.0466 | 20.7441 | 19.0005 | 142.7587 | 4.9193 |  | 37.1458 | 98.1859 | 40.8664 |  | 181.9627 | 327.5861 | 42.8171 | 54.4626 | 7.9097 | 302 | 60.764 | 10.1897 | 202.1838 | 0.25919
12228 | 1288.9666 | 7.9281 | 117.7125 | 145.2928 | 26.3352 | 17.1005 | 150.0986 | 4.774 |  | 37.3805 | 99.5467 | 41.5228 |  | 180.2018 | 325.1974 | 42.712 | 52.1419 | 8.4858 | 303 | 52.183 | 10.0579 | 202.5518 | 0.27672
12229 | 1293.135 | 5.7928 | 117.1706 | 146.8344 | 31.3556 | 18.0497 | 161.1873 | 4.8162 |  | 39.9447 | 101.3137 | 41.9339 |  | 181.8543 | 318.4842 | 41.9586 | 52.9141 | 8.6976 | 302 | 54.2746 | 10.0161 | 202.1485 | 0.30027
12230 | 1277.8979 | 6.2791 | 120.5304 | 146.9542 | 40.1712 | 18.9997 | 169.0355 | 4.2326 |  | 41.592 | 102.0627 | 41.113 |  | 186.3246 | 315.6558 | 40.0728 | 52.5767 | 8.5051 | 275 | 58.1072 | 10.0661 | 202.4555 | 0.29637
12231 | 1247.0579 | 5.7711 | 118.6145 | 141.5855 | 47.5726 | 19.0053 | 161.6006 | 3.1949 |  | 38.4354 | 101.9468 | 37.141 |  | 175.6812 | 304.8824 | 40.0538 | 47.5313 | 8.3126 | 295 | 53.0658 | 8.6915 | 194.3377 | 0.30257
12232 | 1197.2322 | 4.8198 | 114.4587 | 133.9225 | 54.9532 | 13.2963 | 148.0929 | 2.0978 |  | 35.4306 | 99.1626 | 32.0645 |  | 157.5888 | 267.6908 | 34.5023 | 40.9835 | 7.9512 | 246 | 46.2395 | 6.9984 | 165.8097 | 0.25494
12233 | 1133.9116 | 4.4918 | 112.6435 | 117.2581 | 53.1291 | 12.3503 | 141.6636 | 1.3778 |  | 31.4287 | 88.179 | 29.5944 |  | 124.3261 | 229.6184 | 22.2008 | 36.3923 | 7.0924 | 225 | 43.342 | 6.7974 | 124.938 | 0.27694
12234 | 1086.3645 | 3.6204 | 108.2535 | 102.8269 | 40.7295 | 10.4505 | 130.1053 | 1.1588 |  | 26.6149 | 71.8868 | 24.0063 |  | 86.9213 | 210.2953 | 14.5312 | 34.3648 | 5.5408 | 243 | 41.0821 | 6.6452 | 110.531 | 0.26314
12235 | 1048.6618 | 2.8315 | 85.6934 | 98.5542 | 29.7502 | 7.6008 | 116.7635 | 1.693 |  | 22.0403 | 64.7947 | 20.3209 |  | 75.7995 | 197.416 | 11.5891 | 33.5336 | 4.8214 | 200 | 41.6781 | 6.6098 | 97.6427 | 0.20353
12236 | 1025.6422 | 2.7763 | 46.5544 | 94.886 | 27.1839 | 7.6 | 104.4588 | 1.8117 |  | 17.0568 | 62.131 | 22.4755 |  | 68.8996 | 183.1092 | 10.3213 | 31.1568 | 5.2476 | 206 | 42.4915 | 6.5793 | 88.9144 | 0.091646
12237 | 997.2887 | 2.9859 | 27.5693 | 93.2626 | 23.0191 | 11.3989 | 89.278 | 1.4861 |  | 12.1842 | 54.1454 | 15.584 |  | 56.6198 | 166.1773 | 10.2344 | 29.3549 | 5.347 | 203 | 40.6947 | 6.557 | 87.5343 | 0
12238 | 965.4145 | 2.8814 | 26.6517 | 94.7608 | 22.7938 | 10.4503 | 80.0618 | 2.2985 |  | 11.4208 | 46.4756 | 8.1499 |  | 52.4347 | 151.8066 | 10.0845 | 29.9049 | 4.0138 | 184 | 41.5107 | 6.5621 | 90.3495 | 0
12239 | 405.1584 | 1.2807 | 10.7898 | 37.5979 | 16.5969 | 0.002903 | 33.5108 | 1.319 |  | 5.5211 | 20.233 | 3.2235 |  | 21.4554 | 65.943 | 4.0329 | 12.1503 | 1.3597 | 171 | 8.837 | 1.6361 | 20.4341 | 0
12240 | 909.4639 | 2.4487 | 26.6843 | 95.4313 | 33.4252 | 9.5003 | 75.334 | 2.578 |  | 12.2656 | 42.7202 | 7.1059 |  | 41.4779 | 145.4195 | 10.0331 | 25.7391 | 2.8389 | 159 | 42.3837 | 6.5693 | 84.5025 | 0
12241 | 890.1029 | 2.3336 | 26.0885 | 95.4457 | 37.1758 | 9.5 | 81.2318 | 2.8541 |  | 12.1474 | 42.0682 | 7.0917 |  | 37.8567 | 142.2162 | 9.5758 | 24.261 | 2.9576 | 138 | 40.5428 | 6.5664 | 82.1586 | 0
12242 | 883.2728 | 2.4348 | 25.8457 | 95.0776 | 32.7924 | 10.4497 | 80.3987 | 2.3356 |  | 11.5312 | 42.1014 | 7.0575 |  | 36.0265 | 137.5045 | 9.7855 | 24.3866 | 2.9146 | 118 | 38.7995 | 6.5721 | 82.9513 | 0
12243 | 887.0454 | 2.4033 | 25.8769 | 94.3171 | 29.2544 | 11.3997 | 80.9224 | 2.5412 |  | 10.6138 | 43.5088 | 6.7805 |  | 35.5472 | 137.7907 | 10.0335 | 24.5394 | 2.7691 | 109 | 36.119 | 6.5793 | 83.1062 | 0
12244 | 888.9542 | 2.8517 | 25.3073 | 92.916 | 28.2401 | 10.4503 | 84.9982 | 2.9854 |  | 10.99 | 46.889 | 5.1203 |  | 35.7099 | 130.8706 | 10.3709 | 24.7858 | 2.6438 | 107 | 33.1223 | 6.5775 | 83.6716 | 0
12245 | 893.7041 | 2.633 | 24.8793 | 93.2041 | 26.8092 | 10.4529 | 68.4739 | 1.9638 |  | 14.2391 | 48.9886 | 4.137 |  | 40.0574 | 122.7516 | 9.1611 | 25.0206 | 2.5457 | 105 | 33.041 | 6.575 | 84.4303 | 0.085922
12246 | 912.0228 | 2.7039 | 24.5686 | 96.7013 | 24.9227 | 11.3968 | 53.5904 | 2.2114 |  | 14.3256 | 52.8645 | 4.5954 |  | 59.2511 | 123.8701 | 8.6827 | 25.3696 | 2.5552 | 125 | 34.4589 | 6.5745 | 86.7882 | 0.17414
12247 | 923.1453 | 2.9553 | 51.7885 | 96.7276 | 23.4776 | 12.3497 | 60.2468 | 2.0676 |  | 10.8952 | 60.8797 | 7.1471 |  | 77.4296 | 144.6311 | 9.3078 | 25.7003 | 2.8752 | 152 | 37.6371 | 6.5719 | 87.0195 | 0.094596
12248 | 945.6887 | 2.9899 | 75.8389 | 93.6916 | 22.0355 | 14.2495 | 67.473 | 1.4046 |  | 9.9013 | 66.3965 | 9.5704 |  | 94.0992 | 177.7477 | 9.1997 | 26.6801 | 4.1306 | 147 | 38.9038 | 7.2838 | 90.9155 | 0.079321
12249 | 982.7042 | 3.2063 | 84.7171 | 96.5859 | 25.0007 | 13.3003 | 80.8623 | 1.3806 |  | 10.8142 | 67.684 | 10.2701 |  | 106.8653 | 202.671 | 9.2719 | 27.782 | 5.4381 | 145 | 45.4501 | 6.9318 | 97.5109 | 0.13396
12250 | 1009.6341 | 3.0424 | 93.5607 | 97.1464 | 28.6443 | 12.3503 | 105.3751 | 1.2782 |  | 11.3304 | 69.905 | 11.2481 |  | 116.7939 | 215.7317 | 9.1006 | 28.2548 | 6.5152 | 153 | 44.9711 | 6.7947 | 99.9134 | 0.11112
12251 | 1034.867 | 3.0779 | 95.6806 | 100.2707 | 32.4871 | 12.35 | 121.3344 | 1.1664 |  | 13.8621 | 70.8483 | 14.65 |  | 127.2648 | 226.2236 | 8.8335 | 29.2758 | 7.3012 | 152 | 46.2911 | 7.0265 | 95.2839 | 0.1498
12252 | 1067.4703 | 3.2179 | 95.1278 | 102.5446 | 35.578 | 14.2495 | 128.2591 | 1.0881 |  | 15.2295 | 69.6764 | 15.7453 |  | 130.2394 | 226.8191 | 9.2412 | 29.9974 | 7.7332 | 160 | 41.0547 | 7.0349 | 96.3552 | 0.16566
12253 | 1056.318 | 3.3001 | 95.727 | 101.4394 | 45.1581 | 12.3505 | 127.3649 | 1.3124 |  | 14.2958 | 69.3015 | 21.6806 |  | 131.4701 | 224.7786 | 9.5321 | 29.6103 | 8.0151 | 156 | 40.0084 | 6.8343 | 100.892 | 0.3014
12254 | 1024.417 | 4.3982 | 96.0703 | 102.9834 | 52.3653 | 12.35 | 114.2754 | 1.2607 |  | 14.4065 | 69.5713 | 27.2025 |  | 131.1799 | 223.9694 | 9.0255 | 28.4478 | 8.2124 | 162 | 41.0815 | 6.6173 | 97.677 | 0.27972
12255 | 1021.5389 | 7.3172 | 89.2726 | 99.3297 | 56.8687 | 12.35 | 124.2689 | 1.0389 |  | 15.0621 | 69.9394 | 26.9499 |  | 128.3806 | 225.7843 | 8.8951 | 28.2966 | 8.162 | 153 | 40.1023 | 6.5564 | 98.4815 | 0.2659
12256 | 1022.498 | 9.4057 | 70.1921 | 95.1042 | 56.9797 | 11.4003 | 119.4634 | 1.0106 |  | 16.4824 | 68.2073 | 24.2323 |  | 121.0798 | 208.038 | 8.8939 | 28.1794 | 7.4018 | 155 | 35.5613 | 6.4911 | 95.1404 | 0.20979
12257 | 1010.8048 | 8.3274 | 60.0845 | 95.0906 | 54.0781 | 8.5508 | 104.5816 | 1.0311 |  | 16.1376 | 64.7498 | 18.3796 |  | 98.972 | 192.0498 | 8.9631 | 27.7874 | 6.5835 | 165 | 33.4694 | 6.5276 | 91.7755 | 0.1349
12258 | 980.0978 | 4.5533 | 60.0272 | 96.7198 | 48.5124 | 8.55 | 116.5928 | 1.0647 |  | 13.2132 | 62.8724 | 16.3 |  | 78.2885 | 187.7548 | 9.2779 | 27.5613 | 6.0111 | 159 | 37.5563 | 6.6042 | 89.5004 | 0.079134
12259 | 961.7184 | 2.1928 | 55.851 | 96.0471 | 36.5029 | 10.4495 | 114.7802 | 1.0702 |  | 11.0409 | 59.9136 | 18.7779 |  | 66.4649 | 177.2633 | 9.1734 | 26.1081 | 5.3091 | 148 | 40.5499 | 6.5565 | 85.0067 | 0.043662
12260 | 946.0879 | 5.9696 | 44.5696 | 94.4108 | 32.5301 | 6.6511 | 99.1462 | 1.8848 |  | 10.7263 | 52.9241 | 19.2993 |  | 57.7651 | 159.5927 | 8.9541 | 24.7803 | 4.5448 | 138 | 40.0073 | 6.5407 | 78.9931 | 0.03269
12261 | 944.6558 | 11.9408 | 39.0404 | 95.54 | 28.9108 | 8.5495 | 96.1031 | 1.9765 |  | 10.4356 | 45.5181 | 19.8301 |  | 54.0751 | 153.0185 | 8.9359 | 24.5219 | 3.6811 | 129 | 41.2937 | 6.5414 | 77.3158 | 0
12262 | 933.1831 | 11.6302 | 38.9061 | 99.3942 | 25.4396 | 9.4997 | 98.9613 | 2.3315 |  | 10.9791 | 42.173 | 20.8053 |  | 54.3245 | 144.5013 | 9.3632 | 24.8146 | 3.1483 | 127 | 40.8116 | 6.5375 | 77.6028 | 0
12263 | 392.3822 | 4.3966 | 15.7087 | 40.0623 | 17.6907 | 0.00264 | 43.0339 | 1.3202 |  | 5.1767 | 19.2873 | 9.2009 |  | 22.3267 | 61.0256 | 3.8867 | 10.016 | 1.3741 | 117 | 8.5952 | 1.6491 | 16.3878 | 0
12264 | 897.5952 | 6.7604 | 39.1815 | 102.0108 | 32.0355 | 8.5508 | 80.2125 | 2.2534 |  | 11.087 | 41.1514 | 20.1534 |  | 46.8321 | 125.4824 | 13.1875 | 29.2153 | 2.4341 | 119 | 39.17 | 6.5545 | 72.7003 | 0
12265 | 891.8962 | 4.41 | 39.1561 | 102.0302 | 40.19 | 9.4997 | 73.1624 | 2.3186 |  | 11.1047 | 40.9603 | 15.3699 |  | 44.1883 | 124.7129 | 13.7974 | 29.8912 | 2.3668 | 113 | 38.8754 | 6.5545 | 74.8524 | 0
12266 | 883.5059 | 3.6215 | 38.9159 | 102.222 | 40.1629 | 10.4497 | 74.1193 | 1.865 |  | 11.1012 | 41.108 | 12.4894 |  | 43.8316 | 128.3354 | 14.008 | 29.5861 | 2.4465 | 118 | 40.4717 | 6.5518 | 77.5193 | 0
12267 | 880.9744 | 2.8334 | 38.7557 | 101.1657 | 40.3408 | 9.5003 | 77.9018 | 2.3993 |  | 10.4022 | 40.3934 | 16.3721 |  | 43.4742 | 130.2111 | 13.5257 | 29.3546 | 2.4726 | 116 | 36.7041 | 6.5523 | 75.6626 | 0
12268 | 876.3263 | 3.1325 | 38.5619 | 98.8445 | 38.758 | 9.5 | 76.1662 | 2.2959 |  | 11.4329 | 38.7764 | 15.0481 |  | 41.7747 | 121.5299 | 12.0744 | 28.9735 | 2.2822 | 113 | 34.9547 | 6.5466 | 80.5178 | 0
12269 | 891.4954 | 3.0131 | 38.3032 | 99.455 | 37.2023 | 8.5503 | 79.0389 | 2.2067 |  | 16.2334 | 38.9701 | 9.9474 |  | 46.3724 | 115.854 | 10.5102 | 28.5976 | 2.1402 | 109 | 34.7766 | 6.5568 | 87.3062 | 0.024551
12270 | 922.8268 | 3.1369 | 41.5411 | 97.9804 | 33.0306 | 12.3489 | 85.4805 | 1.8457 |  | 18.4871 | 45.6101 | 12.3913 |  | 69.2351 | 122.4615 | 12.116 | 28.6446 | 2.1287 | 128 | 35.4782 | 6.5548 | 94.1907 | 0.051504
12271 | 943.9289 | 3.3457 | 60.8013 | 98.5482 | 34.3893 | 12.35 | 99.8083 | 1.6831 |  | 17.4348 | 67.4 | 19.3763 |  | 89.8478 | 148.6468 | 21.7469 | 31.2232 | 4.8955 | 149 | 41.9445 | 6.6611 | 101.5666 | 0.068983
12272 | 963.6562 | 3.3273 | 83.3954 | 107.2087 | 36.8401 | 13.2997 | 120.3183 | 3.0288 |  | 17.1502 | 83.709 | 22.7595 |  | 103.5928 | 181.6326 | 27.9265 | 34.0132 | 10.7886 | 154 | 44.8755 | 7.2376 | 114.1337 | 0.091637
12273 | 987.7412 | 3.2183 | 97.0265 | 116.5735 | 51.2135 | 12.3503 | 137.0037 | 3.8571 |  | 18.0986 | 85.7536 | 24.6309 |  | 115.3016 | 205.3029 | 29.1984 | 35.5543 | 14.9665 | 160 | -38.0911 | 7.3552 | 117.2079 | 0.10573
12274 | 1037.5761 | 2.9996 | 100.9162 | 120.4333 | 68.1535 | 11.4003 | 148.3481 | 3.0551 |  | 19.0761 | 87.5504 | 28.1315 |  | 125.3901 | 217.5254 | 30.1126 | 36.0178 | 16.6921 | 159 | 48.0222 | 7.2364 | 117.8734 | 0.13406
12275 | 1056.1303 | 3.0983 | 103.3097 | 120.8388 | 73.3497 | 13.2995 | 156.0677 | 2.451 |  | 19.8258 | 91.9424 | 29.9432 |  | 134.2499 | 222.9529 | 30.4011 | 36.8845 | 17.2983 | 164 | 49.1981 | 7.1814 | 119.4938 | 0.13771
12276 | 1051.7794 | 3.6525 | 105.5131 | 119.3437 | 73.0797 | 13.3 | 159.5808 | 2.722 |  | 20.4386 | 95.5755 | 29.9239 |  | 136.3266 | 222.9588 | 29.791 | 36.6539 | 17.5 | 163 | 45.1847 | 7.2985 | 120.7855 | 0.13598
12277 | 1058.7215 | 7.1491 | 107.0564 | 121.1436 | 69.55 | 14.2497 | 162.5116 | 2.573 |  | 19.8187 | 95.2507 | 30.7438 |  | 138.0967 | 230.554 | 29.2142 | 35.7535 | 17.7819 | 168 | 41.8781 | 7.2127 | 122.2563 | 0.26861
12278 | 1054.0403 | 11.1008 | 107.7671 | 121.9473 | 68.9314 | 13.3003 | 172.0564 | 2.6962 |  | 19.5183 | 94.8023 | 31.5701 |  | 140.4414 | 240.7262 | 28.8716 | 35.1571 | 17.814 | 168 | 47.9359 | 7.7433 | 118.8215 | 0.21891
12279 | 1049.4004 | 11.3998 | 105.8526 | 120.5715 | 67.6958 | 13.3 | 174.0091 | 2.3922 |  | 20.4406 | 94.3793 | 31.0291 |  | 137.901 | 238.6713 | 28.9101 | 34.0424 | 18.0822 | 164 | 45.8035 | 7.3235 | 111.3391 | 0.13617
12280 | 1032.2714 | 6.8836 | 81.7828 | 109.4478 | 74.8759 | 5.7021 | 156.495 | 1.5055 |  | 20.4825 | 92.557 | 30.4106 |  | 134.4419 | 220.9932 | 23.4947 | 33.1067 | 17.833 | 170 | 41.6084 | 6.6008 | 95.3737 | 0.11276
12281 | 1015.5412 | 6.811 | 60.0088 | 104.8544 | 73.4946 | 6.6516 | 150.7301 | 1.2656 |  | 20.0022 | 86.2019 | 29.5153 |  | 107.1966 | 204.9593 | 14.0027 | 32.2859 | 16.9101 | 169 | 40.6411 | 6.5634 | 83.1365 | 0.06577
12282 | 984.5731 | 9.6035 | 40.6564 | 99.1321 | 69.9717 | 7.5979 | 129.1368 | 1.1617 |  | 19.5948 | 75.4493 | 25.5958 |  | 76.3316 | 187.8981 | 10.4423 | 31.1621 | 12.9391 | 159 | 38.8566 | 6.5445 | 78.4636 | 0.044477
12283 | 950.3186 | 5.8215 | 29.0737 | 93.3811 | 66.48 | 7.6 | 121.979 | 1.0494 |  | 19.6076 | 62.7344 | 19.7924 |  | 66.8889 | 172.958 | 11.0504 | 29.8332 | 7.0639 | 146 | 42.3111 | 6.5153 | 71.3773 | 0.048337
12284 | 915.2539 | 3.2447 | 27.3888 | 92.3256 | 61.0775 | 8.5497 | 117.2917 | 1.0487 |  | 17.5406 | 50.1106 | 9.8427 |  | 62.3817 | 159.9399 | 10.5363 | 29.4197 | 4.3707 | 150 | -37.1182 | 6.5141 | 70.3809 | 0.010242
12285 | 903.9199 | 8.0475 | 27.4089 | 91.4862 | 55.1269 | 7.6003 | 80.6745 | 1.519 |  | 12.8477 | 44.6657 | 3.9486 |  | 58.2115 | 148.8663 | 9.4841 | 28.8301 | 4.1214 | 143 | 43.9907 | 6.5206 | 63.6536 | 0
12286 | 888.2193 | 11.0111 | 27.4985 | 97.4162 | 44.4945 | 8.5497 | 61.5571 | 2.1243 |  | 11.9544 | 44.1944 | 5.7371 |  | 61.2931 | 142.762 | 9.8107 | 28.7891 | 4.0772 | 140 | 37.6343 | 6.5091 | 59.6685 | 0
12287 | 369.3019 | 4.7887 | 11.016 | 39.7996 | 23.6681 | 0.002376 | 26.5063 | 1.0178 |  | 5.7267 | 20.144 | 3.1417 |  | 25.9406 | 62.7344 | 4.1143 | 11.5418 | 1.814 | 131 | 7.4603 | 1.6302 | 11.6016 | 0
12288 | 887.4875 | 3.4905 | 28.0927 | 101.3939 | 24.7587 | 11.3995 | 61.0214 | 2.0358 |  | 12.9878 | 44.5443 | 6.8161 |  | 57.8449 | 136.7314 | 9.9654 | 29.5614 | 2.8862 | 129 | 37.5949 | 6.5293 | 68.0368 | 0
12289 | 877.5848 | 2.4129 | 30.264 | 101.3912 | 26.1859 | 8.5508 | 58.0051 | 2.3161 |  | 12.3897 | 45.0317 | 6.7166 |  | 55.8565 | 137.1122 | 10.1503 | 29.3733 | 2.4116 | 117 | 45.5417 | 6.5227 | 68.835 | 0
12290 | 887.2433 | 2.4523 | 40.7638 | 100.6166 | 23.5101 | 9.4997 | 57.3136 | 1.9939 |  | 11.7536 | 44.7254 | 6.5468 |  | 55.59 | 131.5719 | 10.1919 | 29.2762 | 2.4164 | 108 | 40.9161 | 6.5209 | 71.108 | 0
12291 | 892.6118 | 2.3712 | 46.454 | 97.6238 | 25.0798 | 9.5 | 55.1511 | 2.3535 |  | 10.9205 | 43.1875 | 5.9597 |  | 54.2445 | 126.7552 | 9.974 | 29.0558 | 2.4056 | 109 | 42.5127 | 6.5263 | 70.0599 | 0
12292 | 900.9347 | 2.7153 | 42.9702 | 96.7583 | 31.6859 | 11.3995 | 56.4119 | 1.9686 |  | 9.5698 | 41.378 | 4.3964 |  | 52.6079 | 123.7692 | 9.2657 | 28.8167 | 2.2895 | 120 | 43.3502 | 6.5289 | 66.1927 | 0
12293 | 908.2408 | 2.6181 | 37.2163 | 95.7912 | 43.9962 | 7.6011 | 51.8527 | 2.1844 |  | 8.9647 | 40.9343 | 3.6143 |  | 51.8159 | 123.0615 | 9.7036 | 28.3922 | 2.2066 | 107 | 37.5551 | 6.5257 | 65.3924 | 0.017837
12294 | 916.5695 | 1.991 | 54.7162 | 93.0241 | 44.6058 | 8.5497 | 52.1023 | 2.0266 |  | 8.9025 | 43.39 | 3.6157 |  | 46.8691 | 120.2598 | 9.7014 | 28.2744 | 2.1913 | 103 | 34.1707 | 6.5245 | 67.3335 | 0.042419
12295 | 918.8564 | 1.9304 | 66.7701 | 91.2919 | 45.4854 | 9.4997 | 57.0266 | 1.3058 |  | 9.1984 | 47.524 | 8.3021 |  | 46.8273 | 115.7821 | 9.0962 | 28.2614 | 2.4941 | 109 | 37.4559 | 6.5232 | 70.1664 | 0.06
12296 | 910.3088 | 2.2974 | 68.0948 | 93.046 | 47.1835 | 11.3995 | 79.1203 | 1.3165 |  | 10.3657 | 46.0285 | 17.2963 |  | 53.332 | 119.0708 | 9.0628 | 28.5227 | 3.4306 | 111 | 39.5955 | 6.6509 | 72.184 | 0.07977
12297 | 921.942 | 2.9812 | 80.3075 | 93.3478 | 52.3638 | 10.4503 | 89.0332 | 1.3149 |  | 13.1625 | 45.91 | 21.5784 |  | 61.9816 | 130.9442 | 9.436 | 28.7158 | 7.3291 | 138 | 37.3301 | 6.9367 | 74.5352 | 0.098322
12298 | 964.126 | 5.1768 | 96.5366 | 93.1056 | 55.1755 | 9.5003 | 84.4956 | 1.4862 |  | 17.208 | 52.1835 | 25.2209 |  | 69.8451 | 139.97 | 9.8411 | 29.6567 | 13.4402 | 164 | 39.8803 | 6.8707 | 74.9356 | 0.12936
12299 | 985.9663 | 4.4441 | 103.0254 | 94.3423 | 56.7329 | 5.7011 | 98.8668 | 1.3211 |  | 19.509 | 60.4747 | 27.8625 |  | 75.9453 | 151.4405 | 9.3544 | 29.0118 | 16.4559 | 178 | 38.48 | 6.5829 | 73.5086 | 0.12229
12300 | 987.7709 | 2.9942 | 103.7555 | 97.0154 | 52.7481 | 7.5995 | 124.6484 | 1.3207 |  | 19.5446 | 64.0269 | 24.0975 |  | 79.6874 | 155.6314 | 9.0368 | 28.3252 | 17.3102 | 180 | 34.6929 | 6.6377 | 75.091 | 0.15818
12301 | 974.0445 | 3.0859 | 100.9961 | 99.4398 | 52.3653 | 9.4995 | 133.0536 | 1.2676 |  | 19.1026 | 65.7117 | 21.7463 |  | 81.6799 | 157.9503 | 9.3318 | 28.574 | 17.8124 | 184 | 34.5822 | 6.5862 | 74.9654 | 0.14775
12302 | 976.3736 | 5.5844 | 84.1185 | 100.6347 | 55.9837 | 7.6005 | 133.8657 | 1.0533 |  | 19.013 | 64.8859 | 26.0006 |  | 82.1052 | 163.0392 | 9.49 | 28.2278 | 15.5195 | 205 | 36.8742 | 6.5168 | 73.7584 | 0.2116
12303 | 996.4008 | 5.5146 | 64.834 | 100.1065 | 56.2178 | 8.5497 | 109.6935 | 1.0212 |  | 17.3937 | 63.0372 | 29.3133 |  | 81.3763 | 160.7477 | 9.6703 | 28.579 | 10.8975 | 218 | 32.3377 | 6.5053 | 71.6712 | 0.12221
12304 | 978.6396 | 8.4411 | 40.8277 | 97.6685 | 57.1454 | 7.6003 | 96.8165 | 0.96999 |  | 13.9117 | 62.8238 | 25.4701 |  | 80.6765 | 156.2512 | 9.2303 | 28.6886 | 7.6453 | 186 | 28.7443 | 6.4625 | 68.2694 | 0.1009
12305 | 967.1399 | 14.9775 | 28.5919 | 97.3995 | 57.3205 | 7.6 | 94.2561 | 0.95222 |  | 11.9404 | 66.7334 | 21.637 |  | 76.5158 | 153.5962 | 8.9035 | 28.281 | 6.3907 | 186 | 28.6361 | 0 | 66.2204 | 0.11042
12306 | 963.7467 | 14.9692 | 28.5275 | 97.5664 | 58.2947 | 8.5497 | 84.4818 | 1.0047 |  | 11.536 | 69.6122 | 23.5633 |  | 70.7395 | 151.6246 | 9.0229 | 28.4256 | 5.4665 | 177 | 31.7372 | 6.4926 | 66.2199 | 0.19025
12307 | 951.2976 | 11.6009 | 28.9782 | 97.6354 | 57.7419 | 9.4997 | 97.8443 | 1.2261 |  | 11.6657 | 58.1182 | 21.8642 |  | 69.1011 | 160.6756 | 9.5571 | 28.3146 | 4.8867 | 184 | 37.4744 | 6.5564 | 67.577 | 0.20652
12308 | 936.7687 | 8.7895 | 28.4586 | 96.3025 | 54.528 | 9.5 | 114.9273 | 1.2844 |  | 10.9924 | 44.3674 | 15.4251 |  | 67.6939 | 157.2997 | 10.4386 | 28.2571 | 4.5251 | 190 | 35.1895 | 6.5161 | 69.4384 | 0.10677
12309 | 917.859 | 7.7695 | 27.9648 | 93.4441 | 43.4689 | 10.4497 | 99.8328 | 1.2036 |  | 10.5279 | 40.4851 | 10.9676 |  | 63.7572 | 148.1694 | 9.4678 | 28.0661 | 4.0585 | 177 | 37.1148 | 6.4952 | 68.9847 | 0
12310 | 913.547 | 6.3499 | 27.6412 | 93.3573 | 34.2433 | 8.5505 | 81.1397 | 1.3374 |  | 11.6023 | 41.6691 | 14.6758 |  | 64.6897 | 148.9621 | 9.3768 | 28.1932 | 3.294 | 169 | 39.7487 | 6.4986 | 70.3325 | 0
12311 | 392.9703 | 2.3562 | 11.1234 | 37.1428 | 20.3391 | 0.002376 | 33.6755 | 0.64911 |  | 5.4616 | 19.7684 | 8.1723 |  | 27.132 | 67.9731 | 4.0027 | 11.3941 | 1.2882 | 134 | 8.487 | 1.6164 | 15.4625 | 0
12312 | 886.2401 | 2.5977 | 27.1072 | 97.825 | 46.425 | 8.5503 | 80.0141 | 2.0251 |  | 11.6216 | 42.2457 | 10.3898 |  | 59.4986 | 146.4818 | 12.9019 | 28.2054 | 2.3823 | 117 | 38.5533 | 6.4939 | 71.3581 | 0
12313 | 876.8873 | 2.561 | 27.4381 | 100.396 | 51.3022 | 6.6505 | 78.5279 | 1.6763 |  | 11.0081 | 42.3392 | 8.5015 |  | 57.5594 | 148.0398 | 14.2594 | 28.3615 | 2.4553 | 116 | 37.1838 | 6.4945 | 71.8136 | 0
12314 | 881.4949 | 2.5001 | 27.4147 | 100.79 | 42.4305 | 5.7003 | 67.4004 | 1.7037 |  | 10.6164 | 42.557 | 8.2436 |  | 56.0419 | 143.302 | 13.6328 | 28.4121 | 2.3831 | 118 | 38.6305 | 6.502 | 71.9279 | 0
12315 | 888.5896 | 2.3477 | 27.1413 | 100.4388 | 33.2255 | 6.6497 | 52.9438 | 1.9247 |  | 9.7225 | 41.5904 | 6.7095 |  | 54.7901 | 131.7433 | 13.472 | 28.1058 | 2.2699 | 109 | 39.0628 | 6.5018 | 71.0773 | 0
12316 | 891.3133 | 2.8105 | 31.5596 | 96.9544 | 38.3775 | 8.5495 | 51.3559 | 1.6419 |  | 8.3744 | 40.3483 | 5.1886 |  | 53.5234 | 123.2076 | 12.5853 | 28.4563 | 2.1522 | 111 | 37.6891 | 6.5009 | 68.0916 | 0
12317 | 881.4218 | 2.8719 | 30.6462 | 92.7849 | 42.1645 | 6.6505 | 50.2532 | 1.8443 |  | 7.7097 | 40.2407 | 4.4369 |  | 52.3058 | 125.8579 | 10.3463 | 28.5923 | 2.0622 | 103 | 38.9967 | 6.5111 | 66.5245 | 0.021043
12318 | 876.1682 | 2.1994 | 35.7391 | 91.4651 | 33.2821 | 8.5495 | 51.2329 | 1.7375 |  | 7.7408 | 44.255 | 4.7662 |  | 47.363 | 126.1746 | 9.5627 | 28.0712 | 2.0754 | 105 | 27.8781 | 6.507 | 66.9588 | 0.038802
12319 | 880.6272 | 2.1009 | 50.3258 | 93.4244 | 42.4763 | 7.6003 | 56.1763 | 1.2407 |  | 8.245 | 46.6858 | 6.6109 |  | 47.7679 | 123.9076 | 9.5136 | 27.7877 | 2.2071 | 113 | 23.1298 | 6.5005 | 68.0837 | 0.060503
12320 | 901.985 | 2.5409 | 64.0059 | 96.9861 | 52.8631 | 7.6 | 77.3278 | 1.1715 |  | 9.4393 | 42.7616 | 13.309 |  | 54.7406 | 128.9926 | 9.3716 | 27.9564 | 3.0115 | 115 | 23.8194 | 6.5032 | 70.7575 | 0.08374
12321 | 915.9771 | 3.1946 | 68.0867 | 96.1766 | 51.7395 | 8.5497 | 86.3732 | 1.1462 |  | 12.2506 | 40.698 | 21.7461 |  | 63.3432 | 137.8954 | 9.3657 | 28.4438 | 4.6708 | 146 | 30.0664 | 6.5018 | 68.5696 | 0.15902
12322 | 934.1153 | 2.6102 | 68.9559 | 95.8099 | 52.8586 | 7.6003 | 90.0952 | 1.0717 |  | 17.4583 | 47.6601 | 26.578 |  | 72.1117 | 145.2394 | 9.3617 | 28.4004 | 6.4459 | 169 | 44.2921 | 6.5022 | 73.1185 | 0.23279
12323 | 958.8585 | 3.6403 | 70.4173 | 96.5922 | 51.7767 | 8.5497 | 88.2353 | 1.2943 |  | 21.2048 | 58.5357 | 24.1602 |  | 79.2974 | 155.497 | 9.4804 | 28.459 | 7.3124 | 163 | 56.4186 | 6.4931 | 74.8576 | 0.22913
12324 | 984.4167 | 3.8243 | 71.0748 | 98.7769 | 49.2268 | 10.4495 | 85.5161 | 1.3301 |  | 21.0529 | 66.3637 | 24.434 |  | 83.6656 | 161.9588 | 9.6787 | 28.7859 | 7.805 | 177 | 55.2551 | 6.4894 | 75.4703 | 0.26043
12325 | 991.141 | 3.2029 | 70.7292 | 100.2887 | 50.8829 | 9.5003 | 97.0034 | 1.0957 |  | 19.799 | 75.5006 | 25.3165 |  | 92.1105 | 168.0992 | 9.6993 | 28.8984 | 8.1007 | 175 | 40.9713 | 6.4946 | 74.0463 | 0.26232
12326 | 982.9486 | 6.282 | 69.3992 | 99.7582 | 55.2669 | 7.6005 | 122.7628 | 1.0355 |  | 20.9232 | 79.3848 | 26.2067 |  | 93.1947 | 179.9524 | 9.042 | 28.4597 | 8.048 | 166 | 35.6292 | 6.4936 | 71.3938 | 0.28466
12327 | 982.2287 | 7.1188 | 66.0079 | 102.0455 | 58.245 | 6.6503 | 122.4805 | 1.0291 |  | 20.3381 | 70.1006 | 28.395 |  | 83.5553 | 190.1988 | 9.1309 | 28.5156 | 8.1973 | 167 | 38.2061 | 6.4927 | 71.5304 | 0.29987
12328 | 977.452 | 5.3642 | 52.3517 | 99.5525 | 57.6177 | 6.65 | 105.1953 | 1.0187 |  | 16.4339 | 62.6695 | 31.1547 |  | 76.7543 | 188.584 | 9.4678 | 28.9425 | 7.8693 | 167 | 45.1214 | 6.4222 | 71.1337 | 0.087947
12329 | 974.8819 | 7.478 | 44.1949 | 96.8822 | 55.8858 | 7.5997 | 102.0839 | 1.0025 |  | 13.5404 | 61.8177 | 32.8258 |  | 74.0849 | 182.7911 | 8.7487 | 28.6422 | 6.8696 | 150 | 47.284 | 6.4719 | 69.2775 | 0.17727
12330 | 974.4311 | 9.7898 | 44.309 | 97.0802 | 53.7814 | 9.4995 | 106.9316 | 1.1942 |  | 12.3888 | 58.8592 | 29.6815 |  | 69.0729 | 173.8809 | 8.8125 | 28.7556 | 6.0808 | 127 | 43.2062 | 6.5152 | 70.5972 | 0.19685
12331 | 960.4076 | 8.6263 | 43.696 | 96.9378 | 53.8597 | 8.5503 | 106.4061 | 1.2286 |  | 11.132 | 54.4033 | 17.9428 |  | 67.939 | 162.344 | 9.6332 | 28.9175 | 6.008 | 121 | 41.0442 | 6.5483 | 71.5768 | 0.1648
12332 | 934.8871 | 5.9052 | 43.8544 | 95.0226 | 52.0942 | 8.55 | 109.136 | 1.3291 |  | 9.9409 | 49.665 | 8.8505 |  | 66.6171 | 156.6893 | 8.8337 | 28.6155 | 5.643 | 131 | 38.3352 | 6.5041 | 72.8497 | 0.091445
12333 | 929.3197 | 6.8704 | 43.8885 | 96.7756 | 46.9319 | 7.6003 | 93.7226 | 1.9279 |  | 10.7276 | 47.6095 | 12.9891 |  | 65.6816 | 151.5928 | 9.542 | 29.3586 | 4.9226 | 130 | 36.9722 | 6.5034 | 72.3234 | 0
12334 | 927.842 | 9.3261 | 43.6526 | 101.0468 | 34.7313 | 8.5497 | 79.6131 | 1.9593 |  | 12.1644 | 46.3665 | 16.7166 |  | 66.8824 | 146.0431 | 9.3981 | 29.8696 | 3.9662 | 123 | 40.2197 | 6.5001 | 72.4866 | 0
12335 | 392.3545 | 4.4345 | 17.5181 | 40.1179 | 19.2567 | 0.002376 | 34.1875 | 0.75794 |  | 5.5495 | 20.7147 | 7.0555 |  | 27.1684 | 64.8613 | 3.4395 | 11.8236 | 1.5267 | 117 | 8.6644 | 1.6049 | 14.5816 | 0
12336 | 900.3425 | 3.0112 | 44.2636 | 107.5802 | 25.2784 | 8.5503 | 81.983 | 2.3015 |  | 11.5136 | 41.2438 | 6.6585 |  | 61.4763 | 129.0768 | 12.5539 | 29.8685 | 2.7946 | 117 | 40.0332 | 6.5021 | 73.5018 | 0
12337 | 889.749 | 2.9855 | 46.5022 | 109.5192 | 29.8235 | 10.4495 | 76.5275 | 2.2004 |  | 11.0561 | 41.7535 | 6.6468 |  | 57.1648 | 125.2262 | 13.7018 | 29.6149 | 2.4372 | 113 | 42.01 | 6.5053 | 74.8008 | 0
12338 | 897.665 | 2.7718 | 58.5771 | 110.1047 | 39.8537 | 9.5003 | 62.5791 | 1.9672 |  | 11.1225 | 42.0387 | 9.0978 |  | 56.0334 | 124.5606 | 13.9955 | 29.5729 | 2.2832 | 116 | 38.7293 | 6.5099 | 74.5052 | 0
12339 | 905.109 | 2.6059 | 65.7152 | 109.5455 | 41.8341 | 9.5 | 63.0546 | 2.5434 |  | 11.0436 | 42.6743 | 14.292 |  | 55.3363 | 122.5321 | 13.2388 | 29.5422 | 2.285 | 112 | 39.1675 | 6.5162 | 78.7344 | 0
12340 | 914.7568 | 2.9934 | 60.9527 | 105.8449 | 39.6685 | 10.4497 | 60.3889 | 2.1732 |  | 11.7684 | 41.73 | 13.253 |  | 53.3815 | 118.9145 | 12.4879 | 28.803 | 2.2143 | 109 | 39.4876 | 6.5093 | 85.6243 | 0
12341 | 935.7783 | 4.1983 | 50.6961 | 100.8675 | 38.4135 | 9.5003 | 66.089 | 1.6759 |  | 15.7207 | 41.6924 | 8.5313 |  | 59.3944 | 120.0178 | 10.5901 | 28.2403 | 2.1177 | 118 | 36.1277 | 6.5172 | 92.8847 | 0.12893
12342 | 981.7338 | 4.994 | 57.3142 | 100.7765 | 35.4518 | 11.3995 | 79.0687 | 1.858 |  | 19.789 | 47.4011 | 14.7226 |  | 82.5281 | 136.9166 | 12.4021 | 28.3661 | 2.0666 | 172 | 48.2978 | 6.8042 | 104.9903 | 0.19772
12343 | 1035.8282 | 8.2599 | 84.4371 | 110.7933 | 31.8607 | 15.1989 | 94.559 | 2.5506 |  | 30.5286 | 68.2262 | 30.4755 |  | 105.1975 | 181.8231 | 25.6326 | 31.6094 | 5.9795 | 241 | 70.6084 | 8.3411 | 127.2443 | 0.2034
12344 | 1123.8719 | 10.7769 | 111.8248 | 125.3639 | 28.646 | 18.0492 | 117.815 | 4.5863 |  | 39.864 | 88.8578 | 39.0069 |  | 125.011 | 244.0832 | 36.1429 | 36.8566 | 12.7813 | 244 | 88.0809 | 9.2327 | 157.826 | 0.32293
12345 | 1223.7865 | 13.8464 | 122.2885 | 135.6629 | 28.3079 | 18.05 | 138.0628 | 5.4023 |  | 41.6813 | 97.6997 | 40.4582 |  | 140.1394 | 291.287 | 40.4134 | 41.8366 | 16.7515 | 296 | 87.3981 | 8.6838 | 178.4681 | 0.33102
12346 | 1280.5498 | 17.8548 | 121.8776 | 142.0415 | 27.0522 | 18.9997 | 142.6752 | 4.704 |  | 42.0499 | 101.0051 | 42.1562 |  | 149.1414 | 313.1201 | 42.6629 | 46.3409 | 18.2475 | 319 | 88.3575 | 9.0718 | 188.0423 | 0.33545
12347 | 1306.0358 | 16.138 | 121.8191 | 143.7084 | 29.1675 | 17.1005 | 141.1566 | 4.9257 |  | 42.9913 | 102.0432 | 42.9887 |  | 155.6515 | 319.7311 | 42.1459 | 54.1449 | 18.6807 | 309 | 90.4257 | 8.8478 | 195.7372 | 0.26
12348 | 1289.639 | 10.5336 | 121.4056 | 150.7571 | 28.5579 | 18.0497 | 143.4384 | 5.4711 |  | 42.8394 | 100.7693 | 41.4027 |  | 158.6722 | 331.1461 | 42.3295 | 57.9512 | 18.8362 | 339 | 89.4468 | 9.193 | 194.3575 | 0.27597
12349 | 1303.8711 | 8.0889 | 121.2317 | 155.6802 | 27.9837 | 18.9997 | 144.3746 | 6.1959 |  | 42.5356 | 101.055 | 38.8161 |  | 158.9214 | 333.9995 | 44.2318 | 57.8918 | 19.27 | 333 | 88.5553 | 9.4966 | 202.3594 | 0.29993
12350 | 1319.8437 | 6.6728 | 120.7515 | 155.5104 | 26.3636 | 20.8995 | 146.6681 | 6.251 |  | 42.4439 | 103.7291 | 37.7487 |  | 159.1399 | 325.8196 | 42.8651 | 57.8873 | 19.358 | 280 | 88.8451 | 10.2511 | 213.5866 | 0.29721
12351 | 1291.1389 | 4.8179 | 119.8709 | 151.5023 | 25.7946 | 21.8497 | 141.9776 | 5.7157 |  | 42.3575 | 104.9651 | 38.0583 |  | 155.9747 | 305.8677 | 39.9053 | 56.6323 | 19.1907 | 266 | 84.689 | 10.0214 | 212.9161 | 0.30945
12352 | 1269.0616 | 4.7261 | 118.2487 | 141.1754 | 36.2387 | 12.3526 | 129.4854 | 4.8791 |  | 41.1622 | 103.028 | 35.1612 |  | 147.6927 | 269.1205 | 31.8649 | 50.4316 | 18.63 | 253 | 74.059 | 9.054 | 187.7846 | 0.24509
12353 | 1192.4389 | 4.6243 | 115.3759 | 128.1206 | 36.1628 | 12.35 | 118.1294 | 2.9471 |  | 36.702 | 91.6747 | 30.7792 |  | 114.5506 | 228.4257 | 18.6072 | 40.4508 | 17.6325 | 244 | 59.0189 | 8.3515 | 149.8805 | 0.26172
12354 | 1113.7179 | 4.2974 | 113.6617 | 116.6049 | 35.738 | 12.35 | 106.9215 | 2.182 |  | 26.7109 | 76.3937 | 23.4049 |  | 81.2864 | 213.5195 | 12.8712 | 34.2616 | 13.7076 | 227 | 53.5649 | 8.5498 | 126.4371 | 0.28158
12355 | 1070.9641 | 4.5976 | 96.1537 | 106.3236 | 34.4726 | 13.2997 | 90.7407 | 1.847 |  | 18.8582 | 68.024 | 11.4475 |  | 67.247 | 202.9293 | 12.0486 | 31.469 | 7.5199 | 230 | 49.7617 | 8.4068 | 101.7859 | 0.2245
12356 | 1044.8379 | 6.9106 | 53.0243 | 98.1388 | 38.0313 | 9.5011 | 81.4536 | 1.6791 |  | 15.5769 | 62.5193 | 5.634 |  | 60.0118 | 184.2647 | 10.4006 | 29.6823 | 4.2315 | 198 | 46.5783 | 8.33 | 89.134 | 0.12502
12357 | 1009.0189 | 8.5065 | 29.8864 | 95.2279 | 38.814 | 8.5503 | 78.0932 | 2.1946 |  | 12.3156 | 53.9215 | 6.1029 |  | 53.6973 | 164.2652 | 9.6309 | 28.9538 | 3.0135 | 186 | 45.0536 | 8.3258 | 83.8476 | 0
12358 | 977.5707 | 5.5677 | 29.2127 | 96.4474 | 35.4201 | 10.4495 | 83.8746 | 2.0051 |  | 11.7759 | 46.071 | 7.2286 |  | 57.5943 | 146.8432 | 9.7857 | 28.7919 | 2.5307 | 168 | 39.2137 | 8.4215 | 90.4588 | 0
12359 | 410.9957 | 1.4395 | 11.8757 | 38.1012 | 22.8506 | 0.002903 | 38.2724 | 0.74834 |  | 5.4691 | 19.8282 | 3.3415 |  | 24.9452 | 63.6859 | 3.9781 | 11.3985 | 1.1462 | 140 | 7.9249 | 2.0906 | 20.931 | 0
12360 | 939.3425 | 2.3256 | 28.9747 | 97.6222 | 33.9915 | 11.3995 | 81.2988 | 2.3803 |  | 11.7316 | 42.3128 | 7.6257 |  | 56.2335 | 139.8598 | 10.0266 | 28.9508 | 2.5636 | 134 | 42.9117 | 8.3323 | 91.5325 | 0
12361 | 932.271 | 2.233 | 30.6541 | 96.6658 | 35.2641 | 9.5005 | 76.6382 | 1.7904 |  | 11.6662 | 41.6132 | 7.4589 |  | 53.1528 | 134.0884 | 9.7464 | 28.4693 | 2.5629 | 121 | 37.9491 | 8.3386 | 93.7732 | 0
12362 | 928.0144 | 2.2292 | 41.2081 | 95.892 | 35.9136 | 8.5503 | 70.619 | 2.3939 |  | 11.6328 | 41.0224 | 7.3254 |  | 52.1087 | 130.0111 | 10.3548 | 28.2512 | 2.5433 | 122 | 39.2606 | 8.326 | 91.7102 | 0
12363 | 919.6204 | 2.3347 | 46.5269 | 96.2445 | 31.3713 | 12.3489 | 70.2357 | 2.2435 |  | 11.6147 | 40.9 | 7.3145 |  | 51.4812 | 125.155 | 10.0625 | 28.2473 | 2.5584 | 115 | 36.1563 | 8.3296 | 87.8031 | 0
12364 | 916.9002 | 2.7986 | 42.3035 | 95.4064 | 35.4857 | 8.5511 | 63.9944 | 2.431 |  | 13.0952 | 40.0573 | 6.8501 |  | 50.498 | 119.2582 | 9.7598 | 27.9688 | 2.53 | 115 | 39.3972 | 8.3282 | 93.6649 | 0
12365 | 938.4713 | 4.401 | 43.0343 | 93.5814 | 34.2065 | 9.4997 | 61.1485 | 2.184 |  | 16.7095 | 40.925 | 7.5643 |  | 56.1755 | 120.334 | 9.9405 | 27.9565 | 2.4086 | 138 | 38.1191 | 8.3309 | 102.458 | 0.032207
12366 | 971.4126 | 8.3533 | 54.1072 | 96.2552 | 29.8706 | 13.2989 | 72.2394 | 1.9375 |  | 21.0664 | 47.4597 | 15.3541 |  | 77.8004 | 130.2296 | 13.5018 | 27.8444 | 2.3347 | 183 | 47.4371 | 8.6619 | 118.8273 | 0.042757
12367 | 1030.9024 | 13.4056 | 81.9082 | 104.3633 | 21.3042 | 21.8476 | 93.0917 | 3.4098 |  | 30.864 | 65.909 | 29.6132 |  | 104.5611 | 171.3561 | 24.8118 | 29.971 | 5.5367 | 223 | 73.8599 | 10.2516 | 137.7614 | 0.061443
12368 | 1141.5462 | 11.8288 | 109.4825 | 122.5431 | 25.6122 | 18.0511 | 115.5948 | 4.9117 |  | 39.2177 | 81.7975 | 34.6333 |  | 130.8096 | 239.569 | 34.6038 | 35.437 | 12.5675 | 252 | 86.2549 | 11.1027 | 173.2739 | 0.084579
12369 | 1238.6053 | 8.1553 | 121.1471 | 138.313 | 22.3764 | 20.8992 | 132.4233 | 5.7633 |  | 41.2834 | 90.6652 | 33.348 |  | 149.0245 | 286.9084 | 40.745 | 44.1859 | 16.9504 | 306 | 90.7474 | 11.6433 | 204.2694 | 0.10835
12370 | 1291.7901 | 8.8196 | 123.6965 | 149.0129 | 26.6225 | 17.1011 | 140.0948 | 5.3274 |  | 41.9616 | 98.5563 | 35.0037 |  | 161.8607 | 310.7124 | 42.7754 | 53.8637 | 17.9932 | 360 | 97.1511 | 12.1033 | 215.2602 | 0.134
12371 | 1309.6656 | 13.087 | 125.8407 | 152.4961 | 26.1531 | 18.0497 | 142.4031 | 4.8474 |  | 43.7242 | 101.5232 | 36.7795 |  | 172.2587 | 324.3674 | 42.6408 | 50.2811 | 18.6306 | 336 | 103.2248 | 11.7331 | 222.756 | 0.1269
12372 | 1306.8879 | 15.8053 | 126.4496 | 153.1118 | 23.3217 | 20.8992 | 142.0622 | 5.2161 |  | 41.1243 | 101.803 | 37.4765 |  | 177.4213 | 332.6072 | 42.587 | 43.5333 | 18.8983 | 356 | 92.1169 | 11.4055 | 221.4966 | 0.12894
12373 | 1317.8252 | 11.8673 | 125.8261 | 160.5155 | 22.2432 | 21.8497 | 144.2729 | 5.7563 |  | 40.8185 | 100.3208 | 38.2268 |  | 178.9298 | 335.984 | 44.3723 | 45.5434 | 18.9091 | 301 | 87.6057 | 10.6348 | 225.005 | 0.15136
12374 | 1310.0714 | 7.9138 | 125.494 | 162.0246 | 20.9584 | 22.7997 | 148.3901 | 5.6178 |  | 43.8785 | 101.3679 | 38.9875 |  | 179.4245 | 330.8754 | 44.5754 | 46.8943 | 18.9673 | 286 | 93.0848 | 11.3059 | 224.2997 | 0.12292
12375 | 1290.1612 | 5.8645 | 120.2134 | 153.0522 | 21.6913 | 21.8503 | 139.7333 | 5.2544 |  | 44.0712 | 102.7897 | 38.2428 |  | 174.609 | 324.4546 | 42.3047 | 46.0112 | 19.0271 | 281 | 87.8953 | 12.2052 | 210.3 | 0.11632
12376 | 1256.9155 | 4.6799 | 114.0378 | 140.9344 | 31.3636 | 12.3526 | 124.4114 | 4.513 |  | 41.1981 | 99.7338 | 34.4611 |  | 163.5985 | 281.2305 | 34.8591 | 42.123 | 18.5326 | 280 | 70.511 | 11.1942 | 187.1075 | 0.088279
12377 | 1196.6321 | 4.3845 | 112.9011 | 126.3973 | 32.0555 | 12.35 | 113.1282 | 3.3196 |  | 37.2302 | 92.408 | 30.7399 |  | 137.4825 | 232.2845 | 21.4319 | 37.7938 | 17.6313 | 227 | 57.1797 | 10.8381 | 150.3951 | 0.13349
12378 | 1139.8453 | 7.8596 | 110.1908 | 109.1471 | 35.138 | 10.4505 | 97.393 | 2.6948 |  | 28.2252 | 78.875 | 24.7523 |  | 104.8267 | 209.9761 | 13.2132 | 34.4262 | 13.7664 | 227 | 56.6719 | 10.1283 | 124.6894 | 0.047048
12379 | 1086.1427 | 7.7284 | 92.1485 | 100.8364 | 33.8842 | 12.3495 | 85.3541 | 2.2725 |  | 20.8814 | 70.68 | 12.5205 |  | 88.2072 | 189.0667 | 11.8786 | 31.4356 | 7.7377 | 218 | 47.9252 | 10.106 | 101.024 | 0.08231
12380 | 1046.9735 | 4.2805 | 48.2352 | 98.4128 | 36.0832 | 10.4505 | 83.2056 | 2.2572 |  | 17.886 | 64.6986 | 5.2509 |  | 79.4572 | 168.8016 | 10.732 | 30.383 | 4.8056 | 196 | 48.279 | 10.0437 | 93.927 | 0.015254
12381 | 1009.6783 | 5.7955 | 22.2665 | 95.8191 | 34.5741 | 11.3997 | 85.9742 | 2.0987 |  | 14.1638 | 55.7077 | 5.4388 |  | 73.5569 | 152.5101 | 10.102 | 30.1901 | 4.566 | 187 | 53.5281 | 9.926 | 88.0476 | 0
12382 | 981.1195 | 9.4376 | 19.5503 | 94.7875 | 36.1785 | 8.5508 | 87.7836 | 2.4744 |  | 13.3105 | 47.8402 | 7.4791 |  | 65.8117 | 147.3928 | 10.3506 | 29.7783 | 4.2729 | 167 | 48.9758 | 9.9059 | 86.9219 | 0
12383 | 419.9295 | 5.1731 | 7.9158 | 37.9405 | 22.8396 | 0.002376 | 38.1409 | 1.3537 |  | 6.3002 | 20.6769 | 3.8528 |  | 25.3106 | 67.985 | 4.2836 | 11.9654 | 1.8404 | 127 | 10.1135 | 2.4968 | 17.6154 | 0
12384 | 898.87 | 8.5449 | 19.2602 | 95.9357 | 79.083 | 12.3489 | 81.2853 | 2.3083 |  | 13.6509 | 41.8726 | 8.0986 |  | 56.7819 | 136.6855 | 10.0279 | 28.4184 | 2.9816 | 118 | 45.1435 | 9.922 | 78.4999 | 0
12385 | 892.78 | 4.6359 | 19.1474 | 96.1542 | 77.8687 | 12.35 | 63.6012 | 2.5384 |  | 12.8216 | 41.21 | 7.8471 |  | 55.6561 | 138.6781 | 10.3962 | 28.3986 | 2.3809 | 116 | 44.8494 | 9.9223 | 84.353 | 0
12386 | 896.5193 | 2.3693 | 18.9898 | 96.0286 | 78.1242 | 11.4003 | 54.8523 | 2.4921 |  | 12.5117 | 40.9512 | 7.6776 |  | 54.8341 | 135.1667 | 10.5173 | 28.346 | 2.383 | 121 | 43.6828 | 9.912 | 86.5104 | 0
12387 | 888.4167 | 2.3517 | 18.9164 | 95.465 | 77.576 | 11.4 | 52.9683 | 2.6328 |  | 12.3963 | 41.6294 | 7.7386 |  | 54.2413 | 127.2181 | 9.8207 | 28.2497 | 2.3834 | 117 | 42.779 | 9.8968 | 88.2125 | 0
12388 | 887.2729 | 2.7321 | 18.7068 | 93.6864 | 80.1468 | 8.5508 | 55.7701 | 2.3208 |  | 13.4191 | 41.1075 | 7.9962 |  | 53.2955 | 120.632 | 10.3801 | 27.9418 | 2.3686 | 118 | 42.1789 | 9.9098 | 92.6314 | 0
12389 | 911.7567 | 3.9804 | 30.7653 | 92.6965 | 81.1186 | 7.6003 | 61.4822 | 2.2805 |  | 17.462 | 40.917 | 8.4312 |  | 55.0318 | 121.2 | 9.8089 | 27.7164 | 2.262 | 125 | 42.3204 | 9.9052 | 104.4465 | 0.024191
12390 | 956.0756 | 7.1293 | 47.1005 | 94.9452 | 77.9209 | 10.4492 | 76.8064 | 1.9356 |  | 22.0264 | 47.2272 | 16.7642 |  | 75.0537 | 129.8138 | 14.4727 | 27.7374 | 2.1678 | 181 | 52.1877 | 10.0475 | 124.9504 | 0.053084
12391 | 1018.8271 | 11.9896 | 74.9013 | 100.4657 | 70.0582 | 18.0479 | 95.03 | 2.8532 |  | 33.2337 | 69.5537 | 27.7476 |  | 106.7195 | 178.6322 | 26.4293 | 31.2033 | 4.7747 | 261 | 73.2818 | 11.9518 | 139.8685 | 0.1468
12392 | 1091.7175 | 17.459 | 102.9973 | 116.4798 | 67.0845 | 20.8992 | 109.1579 | 4.1216 |  | 41.3158 | 87.9493 | 32.6022 |  | 139.0084 | 237.4459 | 35.4597 | 35.8346 | 11.235 | 271 | 84.7318 | 13.0224 | 163.974 | 0.11969
12393 | 1193.586 | 17.6383 | 115.1567 | 134.4939 | 64.5948 | 23.7492 | 127.1114 | 4.9918 |  | 44.0908 | 92.1919 | 34.6323 |  | 164.641 | 281.4706 | 40.7482 | 38.7819 | 15.2907 | 348 | 82.5862 | 12.8593 | 196.4469 | 0.21096
12394 | 1255.0838 | 13.444 | 117.9614 | 148.0382 | 67.876 | 20.9066 | 133.9997 | 4.9409 |  | 43.9893 | 92.9674 | 38.0932 |  | 172.3679 | 308.5227 | 40.8747 | 40.0489 | 16.1991 | 359 | 71.1616 | 13.0358 | 187.3167 | 0.22501
12395 | 1254.0979 | 7.8311 | 119.306 | 162.0741 | 69.2365 | 19.9445 | 132.4121 | 4.8979 |  | 44.6251 | 93.0911 | 40.2386 |  | 179.8863 | 313.6843 | 41.9192 | 46.8052 | 17.1269 | 337 | 74.231 | 12.7692 | 186.3195 | 0.20983
12396 | 1246.1497 | 5.1997 | 120.0114 | 164.3056 | 68.209 | 21.8495 | 129.6396 | 4.868 |  | 38.6469 | 95.1173 | 41.214 |  | 178.9905 | 317.3546 | 40.6795 | 53.4235 | 17.6392 | 336 | 66.3837 | 12.4379 | 190.2258 | 0.26355
12397 | 1268.0876 | 4.3988 | 120.1525 | 167.4343 | 71.5931 | 20.9003 | 132.6987 | 5.4474 |  | 27.4449 | 97.27 | 41.2685 |  | 174.6032 | 324.9275 | 40.0498 | 54.0137 | 17.9689 | 310 | 58.9908 | 12.0834 | 193.3945 | 0.27429
12398 | 1254.0904 | 4.6811 | 119.7288 | 162.0915 | 73.5016 | 21.8497 | 143.2856 | 4.9646 |  | 25.5275 | 98.046 | 39.5204 |  | 173.1724 | 317.8873 | 40.0804 | 52.6259 | 18.4301 | 275 | 53.5272 | 13.1409 | 189.207 | 0.26445
12399 | 1236.3453 | 4.8451 | 118.6164 | 148.6561 | 79.6724 | 18.0511 | 140.3519 | 4.3138 |  | 25.9926 | 96.8664 | 38.1334 |  | 171.8324 | 313.8168 | 39.0453 | 50.619 | 18.9206 | 267 | 61.6206 | 12.3209 | 190.3016 | 0.20289
12400 | 1205.2776 | 4.8388 | 112.7671 | 140.5373 | 88.6694 | 11.4018 | 125.3998 | 3.8264 |  | 26.9391 | 94.6553 | 36.1082 |  | 161.1695 | 291.2238 | 33.595 | 49.5819 | 18.6927 | 247 | 42.1738 | 10.278 | 170.0003 | 0.18945
12401 | 1117.8034 | 5.3477 | 106.7731 | 125.3596 | 92.3815 | 9.5005 | 114.2979 | 2.9584 |  | 26.7428 | 86.0777 | 32.0224 |  | 124.9811 | 251.2924 | 21.4908 | 44.927 | 17.6958 | 216 | 39.6097 | 9.6039 | 125.0976 | 0.068583
12402 | 1073.3546 | 3.9339 | 105.08 | 111.1336 | 91.1142 | 11.3995 | 100.6985 | 3.3226 |  | 24.2738 | 73.8475 | 26.531 |  | 93.3461 | 231.0482 | 15.5298 | 41.3444 | 14.8773 | 216 | 43.8474 | 9.5535 | 110.7102 | 0.050287
12403 | 1054.2323 | 2.6456 | 94.8564 | 102.5382 | 91.6137 | 11.4 | 74.7226 | 2.4471 |  | 21.6374 | 75.2594 | 16.5184 |  | 84.31 | 205.6133 | 12.1533 | 40.3719 | 9.3991 | 199 | 43.7421 | 9.7669 | 94.8847 | 0.029101
12404 | 995.7924 | 2.9004 | 49.1037 | 97.0112 | 89.9305 | 13.2995 | 54.195 | 1.543 |  | 17.3358 | 77.6478 | 17.5342 |  | 80.0348 | 188.034 | 10.5318 | 38.2193 | 6.7421 | 193 | 44.5229 | 9.6181 | 84.2548 | 0.0096951
12405 | 957.074 | 6.0818 | 27.788 | 93.1858 | 89.4928 | 11.4005 | 57.0722 | 2.0983 |  | 12.367 | 60.1061 | 17.1893 |  | 69.1854 | 167.1863 | 9.8823 | 36.4339 | 5.5031 | 177 | 42.1857 | 9.5307 | 81.4523 | 0
12406 | 932.3103 | 7.198 | 25.8626 | 93.6527 | 87.3228 | 11.4 | 54.4993 | 2.1545 |  | 11.9755 | 45.801 | 11.8829 |  | 61.8068 | 151.4987 | 9.8228 | 36.2482 | 4.8249 | 153 | 40.0615 | 9.6324 | 83.7815 | 0
12407 | 904.8717 | 3.8218 | 25.7244 | 95.547 | 89.1211 | 8.5508 | 57.5654 | 2.6258 |  | 13.225 | 42.4513 | 10.3546 |  | 57.4178 | 136.1132 | 10.4487 | 36.7581 | 4.1941 | 136 | 38.4667 | 9.5194 | 85.3424 | 0
12408 | 910.643 | 2.5359 | 25.872 | 100.7894 | 54.0986 | 7.6003 | 63.0426 | 2.1418 |  | 13.5395 | 42.1796 | 10.8172 |  | 54.5339 | 128.4966 | 11.0048 | 36.5735 | 3.5829 | 127 | 38.3931 | 9.5073 | 97.6067 | 0
12409 | 920.0205 | 2.7433 | 25.9226 | 103.0803 | 51.8565 | 9.4995 | 62.7019 | 2.7234 |  | 12.6153 | 42.1375 | 10.5472 |  | 52.1267 | 125.2902 | 11.4031 | 36.401 | 2.9816 | 125 | 36.6157 | 9.5065 | 96.9663 | 0
12410 | 909.8829 | 2.4904 | 25.7038 | 105.0575 | 51.8296 | 9.5 | 58.9515 | 2.1934 |  | 11.6792 | 41.7331 | 10.2626 |  | 49.3167 | 126.9176 | 10.1346 | 36.4697 | 2.7886 | 130 | 39.3683 | 9.5041 | 90.1743 | 0
12411 | 913.1829 | 2.2172 | 25.8935 | 103.3103 | 51.1625 | 9.5 | 58.4845 | 1.9593 |  | 11.218 | 40.8279 | 9.966 |  | 49.6895 | 121.6847 | 10.7963 | 36.2992 | 2.668 | 116 | 36.1947 | 9.5161 | 87.613 | 0
12412 | 918.3181 | 2.7392 | 25.4174 | 100.0765 | 50.5418 | 9.5 | 60.5143 | 2.2281 |  | 11.3993 | 38.5979 | 7.9721 |  | 48.0468 | 115.3518 | 10.7629 | 35.8387 | 2.4184 | 114 | 35.2916 | 9.511 | 89.0443 | 0
12413 | 928.9574 | 3.2781 | 33.58 | 100.0849 | 47.1517 | 11.3995 | 66.1109 | 2.5233 |  | 17.1804 | 38.8913 | 8.3024 |  | 51.3231 | 115.7053 | 9.8694 | 35.0926 | 2.6725 | 119 | 34.5721 | 9.4881 | 103.4389 | 0.073182
12414 | 982.6619 | 8.324 | 45.3325 | 100.4681 | 45.2785 | 11.4 | 75.6276 | 1.9806 |  | 22.3753 | 46.012 | 15.953 |  | 81.7778 | 129.2435 | 12.8151 | 35.63 | 3.1383 | 164 | 39.3687 | 9.4929 | 117.4809 | 0.054395
12415 | 1041.2374 | 11.7064 | 77.7676 | 106.0236 | 37.0222 | 18.0482 | 95.4397 | 3.0733 |  | 31.6016 | 68.0166 | 26.9053 |  | 104.3687 | 176.6044 | 25.1985 | 37.3364 | 5.4306 | 232 | 51.5164 | 10.9781 | 127.7446 | 0.081433
12416 | 1099.2986 | 11.3238 | 106.232 | 120.0915 | 34.7599 | 19.9495 | 116.5936 | 3.7781 |  | 37.6251 | 85.3564 | 30.6537 |  | 127.711 | 235.4075 | 30.538 | 42.0661 | 12.2191 | 256 | 58.4872 | 13.6041 | 159.8578 | 0.083503
12417 | 1199.2316 | 8.1839 | 114.5194 | 132.7215 | 37.804 | 18.0505 | 131.4912 | 3.7411 |  | 41.3852 | 91.5829 | 34.3369 |  | 143.9632 | 269.2004 | 30.3016 | 45.0382 | 15.8046 | 295 | 53.9778 | 12.8862 | 173.3464 | 0.12669
12418 | 1235.2111 | 5.9459 | 113.8498 | 139.2222 | 40.0572 | 17.1003 | 132.4976 | 3.9562 |  | 41.8046 | 95.445 | 36.9058 |  | 151.6783 | 292.5886 | 29.9319 | 48.3038 | 17.1505 | 326 | 53.4257 | 15.0806 | 170.674 | 0.22145
12419 | 1229.1842 | 9.8433 | 115.3975 | 142.7533 | 40.9978 | 18.0547 | 137.4357 | 4.0645 |  | 42.9964 | 99.145 | 38.3565 |  | 155.6616 | 291.2487 | 29.8116 | 43.1295 | 17.589 | 324 | 53.6245 | 14.0377 | 165.0646 | 0.13763
12420 | 1233.5672 | 12.8479 | 116.1422 | 138.6856 | 39.9141 | 21.8439 | 134.3096 | 4.5296 |  | 41.7763 | 98.6869 | 39.772 |  | 142.7649 | 299.3623 | 30.6012 | 39.125 | 17.5656 | 320 | 51.3526 | 13.5101 | 158.0332 | 0.25839
12421 | 1228.9826 | 12.7849 | 117.3847 | 142.2486 | 45.9907 | 19.9505 | 145.6027 | 4.9064 |  | 34.5665 | 99.1115 | 38.5214 |  | 147.4503 | 302.3579 | 30.7248 | 41.9319 | 17.9195 | 285 | 49.4151 | 13.5659 | 173.668 | 0.14476
12422 | 1235.9143 | 8.3509 | 115.9501 | 148.2734 | 52.9228 | 19.95 | 151.7806 | 4.8801 |  | 27.4126 | 100.551 | 36.6252 |  | 156.47 | 293.9673 | 32.0678 | 44.0968 | 18.3357 | 261 | 42.6375 | 13.9631 | 177.639 | 0.14353
12423 | 1202.6102 | 6.1719 | 116.4487 | 144.1908 | 57.2895 | 20.8997 | 148.2522 | 4.1406 |  | 23.0691 | 96.4182 | 36.0933 |  | 156.3469 | 288.1306 | 31.7813 | 42.9691 | 18.0992 | 258 | 55.6652 | 13.352 | 175.3433 | 0.10645
12424 | 1168.8785 | 5.5487 | 110.5686 | 132.8456 | 66.688 | 13.3021 | 140.8633 | 4.5181 |  | 21.5331 | 90.2299 | 34.6642 |  | 145.9233 | 259.7677 | 27.619 | 38.7018 | 17.4744 | 238 | 41.1947 | 11.3763 | 151.8326 | 0.098828
12425 | 1122.9534 | 4.8195 | 106.8729 | 117.8044 | 69.2131 | 11.4005 | 130.369 | 3.4894 |  | 21.343 | 83.1881 | 32.5128 |  | 118.6332 | 242.1645 | 16.5182 | 35.0597 | 17.0077 | 216 | 42.8772 | 10.8678 | 110.4882 | 0.073556
12426 | 1092.0349 | 3.7861 | 104.9579 | 103.4663 | 69.1332 | 10.4503 | 118.6307 | 2.4632 |  | 20.8912 | 71.8517 | 26.4413 |  | 96.7261 | 220.3273 | 9.9583 | 33.094 | 14.0197 | 205 | 34.2772 | 10.9612 | 101.2316 | 0.052813
12427 | 1045.358 | 3.8222 | 90.5104 | 98.8928 | 67.2933 | 8.5505 | 84.7388 | 2.4311 |  | 19.4584 | 67.7367 | 14.8925 |  | 87.1245 | 204.0233 | 9.452 | 30.521 | 7.7225 | 183 | 39.4627 | 11.1168 | 85.7877 | 0.031129
12428 | 1012.9454 | 3.7262 | 41.1415 | 97.2122 | 60.6772 | 6.6505 | 66.522 | 2.6172 |  | 17.0402 | 63.5174 | 9.5332 |  | 79.6298 | 182.1009 | 9.2502 | 28.5168 | 4.4254 | 172 | 43.5794 | 11.0192 | 80.0466 | 0.0223
12429 | 978.2726 | 4.0383 | 21.061 | 94.8135 | 46.6782 | 9.4992 | 68.7147 | 1.9822 |  | 12.6037 | 54.4858 | 8.7175 |  | 69.7504 | 168.2321 | 9.1651 | 27.6063 | 4.0243 | 167 | 46.15 | 10.9929 | 80.1732 | 0.00033094
12430 | 942.8394 | 3.7359 | 19.7902 | 97.8151 | 48.7155 | 10.4497 | 61.9373 | 2.5695 |  | 11.7315 | 47.0818 | 10.0858 |  | 58.3605 | 153.2551 | 9.5069 | 27.5767 | 4.1199 | 157 | 43.3183 | 12.5277 | 77.5116 | 0
12431 | 915.1358 | 2.7254 | 19.697 | 98.4474 | 53.1253 | 10.45 | 61.4587 | 3.0463 |  | 12.7366 | 44.4152 | 11.1704 |  | 55.1378 | 140.2916 | 10.0896 | 27.0817 | 3.3786 | 131 | 42.0808 | 11.4902 | 79.2638 | 0
12432 | 914.1839 | 2.4336 | 19.4414 | 98.5392 | 34.8472 | 9.5003 | 54.8769 | 2.3674 |  | 13.0208 | 43.2813 | 11.3309 |  | 53.8843 | 129.3522 | 10.143 | 27.0169 | 2.5729 | 121 | 44.83 | 11.0471 | 81.7897 | 0
12433 | 912.1973 | 2.272 | 19.2722 | 99.7993 | 32.7694 | 9.5 | 57.735 | 2.7252 |  | 13.0136 | 43.7968 | 11.2027 |  | 51.2883 | 124.969 | 9.733 | 26.5451 | 2.3737 | 118 | 42.0401 | 10.9893 | 82.3279 | 0
12434 | 908.269 | 2.6337 | 19.453 | 100.1682 | 30.5717 | 10.4497 | 60.1234 | 2.1555 |  | 12.9531 | 43.0555 | 11.4975 |  | 48.4785 | 122.6456 | 9.3572 | 27.116 | 2.3589 | 114 | 41.7577 | 11.0035 | 80.3878 | 0
12435 | 910.4418 | 2.5268 | 19.5641 | 100.7237 | 27.6331 | 12.3529 | 58.4019 | 2.6615 |  | 12.9081 | 42.4378 | 11.2043 |  | 48.3748 | 122.669 | 9.8032 | 26.8995 | 2.3559 | 108 | 41.0799 | 10.9989 | 84.1307 | 0
12436 | 924.666 | 2.6415 | 19.362 | 98.7481 | 28.6229 | 10.4471 | 60.57 | 2.746 |  | 13.024 | 41.011 | 9.6897 |  | 47.5503 | 114.1677 | 9.5729 | 26.4659 | 2.2755 | 108 | 39.497 | 10.9891 | 86.9853 | 0
12437 | 932.7901 | 3.5733 | 28.538 | 96.0577 | 26.8824 | 11.3997 | 64.4987 | 2.1502 |  | 17.7582 | 41.2202 | 9.5435 |  | 51.3101 | 114.6066 | 9.435 | 26.7495 | 2.1762 | 125 | 38.0042 | 11.0051 | 99.9431 | 0.13705
12438 | 977.95 | 10.6479 | 42.9011 | 98.7224 | 25.2736 | 12.3497 | 74.7276 | 2.3859 |  | 21.2355 | 46.4241 | 17.7693 |  | 81.7388 | 130.9507 | 11.7487 | 26.7899 | 2.5638 | 166 | 43.1018 | 11.2646 | 106.6352 | 0.17996
12439 | 1028.8665 | 14.67 | 76.3671 | 105.592 | 18.2238 | 18.9982 | 99.6455 | 2.5684 |  | 29.4207 | 69.7648 | 32.2304 |  | 105.1908 | 173.598 | 25.4159 | 28.1418 | 5.8809 | 202 | 61.4606 | 13.4127 | 124.6669 | 0.17239
12440 | 1094.9017 | 9.9743 | 99.9096 | 123.6579 | 18.5174 | 19.0053 | 118.0143 | 3.836 |  | 38.0662 | 88.6944 | 39.3531 |  | 124.6735 | 219.13 | 34.7184 | 32.5741 | 11.0691 | 237 | 72.9443 | 14.1449 | 154.6274 | 0.28977
12441 | 1154.3382 | 7.0117 | 106.6502 | 135.2421 | 19.3027 | 18.9947 | 130.563 | 5.1448 |  | 42.6297 | 95.9143 | 40.9115 |  | 137.0897 | 256.5906 | 37.1518 | 35.572 | 13.393 | 291 | 67.847 | 14.2521 | 152.2605 | 0.33213
12442 | 1216.6364 | 5.6322 | 105.7757 | 142.4544 | 19.7016 | 19.9497 | 130.833 | 4.896 |  | 42.2889 | 99.2569 | 42.5922 |  | 144.491 | 278.5112 | 39.0351 | 40.0596 | 16.8195 | 313 | 73.4206 | 15.8798 | 159.4914 | 0.32209
12443 | 1234.6762 | 6.5271 | 104.1898 | 148.7005 | 22.3946 | 18.0505 | 127.1753 | 5.5229 |  | 41.3286 | 96.9031 | 41.5829 |  | 149.7498 | 283.6536 | 40.6038 | 41.7228 | 16.0422 | 317 | 74.414 | 19.0318 | 170.7422 | 0.25441
12444 | 1248.5209 | 10.9427 | 106.127 | 151.5125 | 23.8188 | 18.05 | 128.2691 | 5.1526 |  | 40.6359 | 96.2451 | 38.1714 |  | 153.3194 | 287.3089 | 41.1682 | 41.9677 | 14.998 | 320 | 73.605 | 18.8411 | 176.7526 | 0.27278
12445 | 1232.3696 | 13.8997 | 114.9985 | 154.9815 | 24.6624 | 18.9997 | 136.1963 | 5.1695 |  | 42.0707 | 97.9666 | 37.0495 |  | 155.2206 | 290.5045 | 42.7056 | 40.5808 | 15.7178 | 292 | 71.5143 | 16.5722 | 181.9861 | 0.29271
12446 | 1214.0173 | 13.4032 | 113.1029 | 150.2439 | 21.2431 | 24.6984 | 135.5333 | 5.3074 |  | 42.9906 | 98.891 | 33.9697 |  | 153.198 | 290.1256 | 41.0906 | 39.1359 | 16.136 | 286 | 68.81 | 17.6161 | 181.2434 | 0.22968
12447 | 1184.2037 | 8.5387 | 105.8774 | 140.8043 | 21.5054 | 28.4989 | 139.6086 | 4.4821 |  | 43.0234 | 102.1284 | 28.2093 |  | 143.2539 | 286.9027 | 39.0667 | 38.9769 | 16.3605 | 289 | 63.061 | 16.6618 | 178.6362 | 0.18139
12448 | 1142.8708 | 5.0034 | 101.4326 | 125.9529 | 40.3249 | 17.1032 | 138.0684 | 4.3158 |  | 41.2624 | 99.7743 | 22.9396 |  | 132.8759 | 259.1892 | 31.0181 | 37.0785 | 16.2849 | 251 | 62.9759 | 12.4454 | 152.5454 | 0.0941
12449 | 1063.7917 | 3.606 | 89.8571 | 112.8855 | 48.3203 | 12.3513 | 126.2363 | 3.288 |  | 35.6573 | 87.8334 | 21.2334 |  | 93.4264 | 206.0059 | 17.6958 | 34.482 | 15.5983 | 225 | 50.4836 | 11.6487 | 115.6795 | 0.13762
12450 | 1009.6733 | 3.0052 | 44.2767 | 103.3748 | 48.1046 | 11.4034 | 106.1886 | 2.8774 |  | 24.4211 | 74.8451 | 20.4044 |  | 61.3272 | 189.1641 | 16.9525 | 31.0981 | 12.337 | 217 | 46.5149 | 11.8945 | 101.1115 | 0.082933
12451 | 967.2668 | 2.4107 | 20.1984 | 94.2267 | 48.0745 | 10.4471 | 74.2844 | 2.0618 |  | 18.7819 | 64.4161 | 13.2736 |  | 52.9565 | 172.2386 | 15.7924 | 28.29 | 6.4859 | 191 | 41.7952 | 11.8479 | 87.5891 | 0.068951
12452 | 957.9621 | 3.415 | 17.3638 | 93.5028 | 49.573 | 8.5529 | 59.8155 | 1.4471 |  | 16.7061 | 50.7614 | 11.1869 |  | 50.4403 | 159.9658 | 13.4486 | 27.5847 | 4.2357 | 192 | 40.9665 | 11.9116 | 88.5128 | 0.011948
12453 | 954.5306 | 4.1231 | 17.3452 | 96.4809 | 48.4089 | 8.55 | 58.4277 | 2.4724 |  | 12.32 | 45.4487 | 13.8596 |  | 49.0187 | 150.9326 | 11.3682 | 27.1884 | 4.0469 | 196 | 39.1367 | 11.8224 | 84.1635 | 0.00033095
12454 | 926.783 | 3.9725 | 17.5583 | 97.1695 | 45.9503 | 10.4471 | 62.2075 | 2.1921 |  | 12.6542 | 45.8649 | 16.8599 |  | 49.7503 | 148.1575 | 12.3544 | 27.6849 | 4.189 | 180 | 39.6145 | 13.4907 | 89.444 | 0
12455 | 906.9787 | 3.7266 | 17.6696 | 98.2896 | 45.545 | 10.45 | 64.2163 | 2.5489 |  | 13.8283 | 45.8503 | 12.819 |  | 56.0312 | 143.9417 | 10.8766 | 26.6925 | 4.2549 | 155 | 39.1851 | 12.3546 | 93.5105 | 0
12456 | 888.5777 | 3.3657 | 17.7727 | 97.8419 | 41.2924 | 10.45 | 58.6344 | 2.1299 |  | 13.6189 | 44.6134 | 8.9562 |  | 52.8754 | 146.6468 | 10.5013 | 23.6739 | 3.7096 | 152 | 38.845 | 11.8458 | 92.2966 | 0
12457 | 886.5072 | 2.5658 | 17.6787 | 99.2555 | 44.6485 | 8.5505 | 56.5668 | 2.7826 |  | 13.1291 | 44.0869 | 8.1851 |  | 51.6142 | 141.7041 | 11.0887 | 23.1301 | 3.2999 | 150 | 39.3861 | 11.8054 | 91.0577 | 0
12458 | 864.0178 | 2.9304 | 17.586 | 98.3135 | 44.6367 | 10.4495 | 56.3916 | 2.2556 |  | 11.7759 | 43.9779 | 8.4689 |  | 47.8549 | 138.4132 | 11.4914 | 22.9099 | 3.0299 | 150 | 37.9177 | 11.8213 | 93.0745 | 0
12459 | 863.9986 | 2.634 | 17.2707 | 99.3078 | 41.0229 | 11.3997 | 49.4206 | 2.5846 |  | 11.2434 | 43.2303 | 8.2782 |  | 44.4493 | 135.1341 | 10.3779 | 22.5807 | 2.9929 | 136 | 40.7866 | 11.8175 | 86.5227 | 0
12460 | 870.8515 | 2.6551 | 17.121 | 95.554 | 40.138 | 10.4503 | 48.7508 | 2.0846 |  | 9.6942 | 41.2958 | 6.9979 |  | 40.9983 | 131.4616 | 11.9036 | 22.9545 | 2.6879 | 137 | 38.8703 | 11.8051 | 81.9604 | 0
12461 | 877.181 | 3.1169 | 19.2365 | 95.1501 | 40.3547 | 9.5003 | 52.2734 | 2.2832 |  | 8.7469 | 40.5483 | 5.5241 |  | 38.3438 | 124.0019 | 10.1423 | 24.1868 | 2.3572 | 123 | 37.6138 | 11.8037 | 80.8406 | 0.021178
12462 | 860.1848 | 2.2981 | 43.9833 | 95.1541 | 38.2165 | 10.4497 | 59.3518 | 2.0153 |  | 10.4767 | 43.1289 | 5.053 |  | 38.1452 | 120.4985 | 10.2575 | 22.5516 | 2.2601 | 117 | 37.5833 | 11.8086 | 78.2919 | 0.074789
12463 | 859.046 | 2.5565 | 50.9523 | 96.2354 | 38.6512 | 9.5003 | 60.7628 | 2.3213 |  | 19.9796 | 47.7084 | 5.2569 |  | 40.9303 | 117.4117 | 10.5506 | 21.6898 | 2.9726 | 124 | 50.8751 | 11.7957 | 78.859 | 0.16813
12464 | 864.2951 | 2.6416 | 52.6133 | 95.0325 | 39.6195 | 9.5 | 67.6794 | 2.979 |  | 27.8622 | 44.8425 | 5.2373 |  | 44.0353 | 119.5786 | 10.5576 | 21.6679 | 2.7052 | 117 | 52.0152 | 11.796 | 82.0839 | 0.3316
12465 | 876.1388 | 2.0373 | 67.3884 | 91.1783 | 44.0678 | 8.5503 | 65.5675 | 2.2091 |  | 28.9256 | 43.901 | 6.0053 |  | 48.7249 | 120.9302 | 10.5511 | 21.8397 | 4.3447 | 169 | 46.0119 | 11.7932 | 85.7577 | 0.32916
12466 | 896.5905 | 2.346 | 82.9533 | 92.696 | 48.5108 | 9.4997 | 71.1614 | 1.4923 |  | 26.9102 | 51.3489 | 6.1305 |  | 58.0774 | 128.653 | 11.0055 | 21.6176 | 9.4982 | 169 | 45.7163 | 11.7917 | 88.0902 | 0.32921
12467 | 897.9777 | 2.6518 | 87.9308 | 93.3336 | 54.3479 | 8.5503 | 74.8299 | 1.3779 |  | 29.7333 | 54.2088 | 5.6134 |  | 59.9299 | 126.1426 | 10.1807 | 21.8586 | 12.4411 | 183 | 41.5904 | 11.7921 | 90.7251 | 0.26273
12468 | 890.3252 | 6.2028 | 89.0606 | 93.3904 | 47.4938 | 8.55 | 58.7945 | 1.1826 |  | 31.4383 | 53.5865 | 5.2935 |  | 59.2087 | 130.4573 | 11.3819 | 21.0529 | 13.4022 | 190 | 28.1106 | 11.8106 | 80.9287 | 0.26946
12469 | 892.6832 | 4.573 | 82.1852 | 93.2938 | 39.2679 | 7.6003 | 68.3499 | 1.0503 |  | 30.3934 | 53.705 | 5.176 |  | 61.675 | 143.7697 | 10.3287 | 21.1721 | 13.4762 | 194 | 31.827 | 11.7818 | 83.7278 | 0.2781
12470 | 895.4371 | 5.8525 | 38.7285 | 92.4565 | 38.1151 | 9.4995 | 92.1165 | 1.0109 |  | 26.947 | 54.7978 | 5.0113 |  | 61.7662 | 161.135 | 10.5836 | 21.0906 | 10.9811 | 181 | 29.0465 | 11.7995 | 82.6763 | 0.12902
12471 | 894.5168 | 9.2739 | 18.8721 | 91.1413 | 55.1586 | 6.6508 | 72.4136 | 1.1073 |  | 23.9085 | 55.8691 | 5.0193 |  | 62.5684 | 160.2699 | 10.7929 | 20.9764 | 5.9586 | 186 | 26.0708 | 11.7833 | 81.8893 | 0.10748
12472 | 906.1323 | 9.1261 | 17.3345 | 98.1369 | 60.6887 | 7.5997 | 57.5536 | 1.2802 |  | 24.8955 | 55.9794 | 5.0928 |  | 62.3212 | 159.0243 | 9.8187 | 24.4328 | 4.4365 | 184 | 28.0683 | 11.783 | 77.7353 | 0.15063
12473 | 903.5291 | 9.0798 | 17.0089 | 103.1066 | 49.3857 | 9.4995 | 58.1185 | 1.1559 |  | 28.0145 | 53.2523 | 5.2669 |  | 67.1408 | 157.01 | 11.6893 | 26.6694 | 4.8434 | 177 | 38.7727 | 11.7975 | 70.6195 | 0.071588
12474 | 898.629 | 9.6608 | 16.7621 | 101.453 | 36.1606 | 7.6005 | 59.6245 | 1.0563 |  | 23.4171 | 47.7007 | 6.3678 |  | 69.2376 | 155.2003 | 10.2681 | 26.8864 | 4.8019 | 176 | 36.5361 | 11.7828 | 69.0506 | 0.04859
12475 | 872.8241 | 10.1565 | 16.4561 | 99.9862 | 27.3018 | 9.4995 | 57.5337 | 1.077 |  | 17.0085 | 44.4932 | 9.1016 |  | 63.9306 | 151.9218 | 9.9434 | 26.3274 | 4.5513 | 177 | 35.3572 | 11.6386 | 68.9024 | 0.067393
12476 | 871.9503 | 11.5899 | 16.3177 | 100.3118 | 27.2151 | 7.6026 | 53.8896 | 2.0092 |  | 15.0635 | 44.3982 | 12.6963 |  | 56.2481 | 158.8559 | 10.8746 | 26.1664 | 4.6254 | 184 | 35.3023 | 11.902 | 69.2687 | 0.025212
12477 | 859.4089 | 9.0881 | 16.5689 | 97.7034 | 24.4287 | 8.55 | 52.3796 | 1.8988 |  | 16.0658 | 44.1437 | 12.7449 |  | 53.955 | 150.6132 | 9.9101 | 24.1648 | 4.4574 | 201 | 35.9202 | 11.8173 | 71.2334 | 0.00055158
12478 | 869.869 | 8.8901 | 16.8259 | 97.3108 | 28.1722 | 9.4974 | 57.2497 | 1.9556 |  | 16.23 | 44.323 | 11.8766 |  | 54.5104 | 150.4897 | 11.9182 | 22.3977 | 4.3573 | 193 | 37.3905 | 13.5481 | 78.1957 | 0
12479 | 867.7841 | 10.5539 | 16.8586 | 95.4355 | 38.5296 | 8.5503 | 58.0227 | 2.5779 |  | 15.5711 | 44.6703 | 9.2284 |  | 51.1947 | 149.9813 | 10.8379 | 21.9686 | 4.1651 | 163 | 39.0498 | 12.3401 | 78.3532 | 0
12480 | 870.6217 | 6.9853 | 16.8827 | 94.7816 | 42.8307 | 9.4997 | 56.1336 | 2.0782 |  | 16.7015 | 43.485 | 7.97 |  | 48.5429 | 150.5648 | 9.9321 | 21.9722 | 4.1681 | 157 | 36.8057 | 12.2316 | 80.9063 | 0
12481 | 878.9388 | 3.2011 | 17.01 | 94.2324 | 43.0903 | 9.5 | 59.9033 | 1.7519 |  | 15.6835 | 42.4933 | 7.7697 |  | 46.4757 | 145.533 | 11.7654 | 21.992 | 4.3102 | 158 | 37.484 | 11.9983 | 80.978 | 0
12482 | 870.5729 | 2.4731 | 16.9944 | 95.3225 | 40.4082 | 9.5 | 58.8484 | 2.5132 |  | 13.9263 | 42.3777 | 7.7266 |  | 44.8853 | 139.6342 | 10.7629 | 21.863 | 3.673 | 167 | 38.592 | 11.8216 | 81.6354 | 0
12483 | 861.4746 | 2.7274 | 17.4842 | 94.6991 | 39.0597 | 8.5503 | 53.7834 | 2.0983 |  | 13.5024 | 42.4806 | 7.8384 |  | 44.5931 | 136.5968 | 9.9336 | 21.675 | 3.1174 | 155 | 41.5016 | 11.7967 | 82.4018 | 0
12484 | 871.4479 | 2.8216 | 17.0368 | 91.9063 | 35.8417 | 9.4997 | 51.2493 | 2.2798 |  | 11.9988 | 41.7114 | 6.1592 |  | 45.0272 | 131.7511 | 11.8449 | 22.0824 | 2.585 | 147 | 45.1132 | 11.7878 | 78.1327 | 0
12485 | 864.6858 | 2.2199 | 16.372 | 91.2107 | 34.5989 | 9.5 | 54.8335 | 2.0386 |  | 10.843 | 41.0645 | 5.046 |  | 45.1516 | 128.4249 | 10.2304 | 23.4163 | 2.4633 | 137 | 43.464 | 11.7892 | 75.9014 | 0.03307
12486 | 875.7112 | 1.8192 | 16.2853 | 91.7598 | 33.1714 | 10.4497 | 51.5778 | 2.2548 |  | 10.8107 | 43.6423 | 4.8421 |  | 45.187 | 124.2272 | 9.1711 | 21.7556 | 2.4358 | 132 | 30.6025 | 11.7846 | 76.0061 | 0.044522
12487 | 888.3032 | 1.7684 | 16.1876 | 91.2229 | 33.7135 | 9.5003 | 46.3434 | 1.6922 |  | 10.5686 | 45.7543 | 4.8247 |  | 47.1937 | 121.5769 | 10.865 | 20.9643 | 2.4173 | 127 | 28.5 | 11.7609 | 75.0591 | 0.076606
12488 | 896.5332 | 1.8405 | 16.1949 | 91.3256 | 32.8544 | 9.5 | 49.2867 | 1.4259 |  | 11.2631 | 42.2364 | 5.0028 |  | 53.7591 | 115.1414 | 10.0201 | 21.6037 | 2.5665 | 125 | 32.5297 | 11.7881 | 79.2142 | 0.099408
12489 | 918.3105 | 2.0216 | 16.2653 | 92.936 | 33.201 | 8.5503 | 67.9778 | 2.2022 |  | 11.4988 | 40.4989 | 4.9466 |  | 58.9247 | 117.5944 | 11.1308 | 21.4191 | 2.4403 | 137 | 39.025 | 11.788 | 83.222 | 0.14686
12490 | 936.4612 | 2.636 | 16.3456 | 93.4462 | 33.1069 | 8.55 | 75.7243 | 1.7405 |  | 12.3354 | 43.3638 | 4.9074 |  | 61.558 | 124.4397 | 9.97 | 21.3874 | 2.3401 | 142 | 31.4111 | 11.7725 | 84.6096 | 0.17555
12491 | 940.7329 | 2.6007 | 16.094 | 93.1501 | 32.2833 | 9.4997 | 82.5831 | 1.3024 |  | 15.4515 | 50.9503 | 5.2355 |  | 61.5744 | 133.5369 | 10.0401 | 21.3587 | 2.4687 | 145 | 30.5631 | 11.7812 | 87.4274 | 0.14654
12492 | 936.7821 | 5.8701 | 15.8622 | 93.6058 | 31.8459 | 10.4497 | 82.8692 | 1.6248 |  | 18.5914 | 60.489 | 8.2714 |  | 63.5361 | 132.8957 | 9.8849 | 21.584 | 3.2065 | 145 | 35.6149 | 11.7829 | 80.9358 | 0.16184
12493 | 949.8503 | 5.8636 | 16.2541 | 98.0404 | 32.0022 | 10.45 | 66.9715 | 2.2526 |  | 16.5665 | 64.0542 | 10.0143 |  | 68.7203 | 142.1854 | 10.4242 | 21.9579 | 3.9786 | 137 | 38.6818 | 11.7864 | 84.2786 | 0.22642
12494 | 956.0596 | 3.1724 | 16.2997 | 97.8593 | 31.6481 | 10.45 | 59.4564 | 1.6886 |  | 17.2039 | 64.7008 | 9.9218 |  | 73.5934 | 145.2463 | 9.6496 | 21.5228 | 4.414 | 142 | 41.82 | 11.7633 | 85.4028 | 0.2158
12495 | 967.2094 | 2.2509 | 16.0113 | 97.192 | 32.491 | 9.5003 | 55.545 | 1.3049 |  | 18.6791 | 66.11 | 9.8209 |  | 74.2264 | 149.4546 | 10.7909 | 21.4133 | 4.7799 | 144 | 42.7811 | 11.7743 | 86.9533 | 0.18934
12496 | 965.7909 | 6.6126 | 15.9433 | 97.3885 | 34.6419 | 6.6508 | 53.0004 | 2.1055 |  | 18.3996 | 65.249 | 10.1823 |  | 68.3199 | 156.7135 | 9.544 | 21.2531 | 4.217 | 145 | 42.3465 | 11.7765 | 82.7329 | 0.25248
12497 | 970.988 | 10.021 | 15.983 | 99.698 | 31.9888 | 8.5495 | 56.1603 | 1.7492 |  | 18.2013 | 61.9734 | 10.1159 |  | 66.963 | 170.2201 | 10.4802 | 21.347 | 4.142 | 143 | 40.0234 | 11.6152 | 70.752 | 0.14494
12498 | 957.3278 | 9.4895 | 16.2185 | 100.4022 | 30.3738 | 9.4997 | 55.9351 | 2.1331 |  | 18.6533 | 56.2604 | 8.0623 |  | 67.9999 | 173.5806 | 10.3098 | 21.6976 | 4.0536 | 142 | 42.7014 | 11.9022 | 78.961 | 0.091419
12499 | 933.9964 | 10.0124 | 16.1804 | 100.6513 | 30.4075 | 8.5503 | 51.7883 | 2 |  | 19.6963 | 53.3811 | 6.1847 |  | 62.2554 | 173.3716 | 10.5197 | 21.4751 | 4.1309 | 144 | 37.2257 | 11.82 | 84.7356 | 0.030256
12500 | 922.6172 | 11.1157 | 16.1159 | 99.7295 | 26.4355 | 11.3992 | 57.1675 | 2.3441 |  | 18.5844 | 47.4863 | 5.4942 |  | 54.2821 | 165.6661 | 10.4777 | 21.364 | 4.2891 | 134 | 35.5825 | 11.7916 | 81.0196 | 0.011565
12501 | 909.3276 | 7.2801 | 15.9031 | 96.002 | 25.8703 | 10.4503 | 61.6385 | 1.8142 |  | 16.2867 | 44.1094 | 5.1595 |  | 50.0513 | 159.4669 | 9.8795 | 21.5504 | 3.9386 | 129 | 35.0128 | 11.7864 | 78.9731 | 0.00055158
12502 | 902.3508 | 3.9254 | 16.592 | 94.9161 | 26.6837 | 8.5505 | 62.034 | 2.506 |  | 17.9542 | 44.2953 | 6.8726 |  | 49.5006 | 146.2598 | 10.8114 | 21.869 | 3.7061 | 134 | 36.3202 | 13.6045 | 86.0681 | 0
12503 | 891.6709 | 2.6352 | 16.9544 | 94.8456 | 23.9234 | 10.4495 | 57.3513 | 3.082 |  | 19.8653 | 44.1663 | 7.8098 |  | 50.696 | 137.5084 | 10.1311 | 23.756 | 3.8889 | 129 | 35.8267 | 12.3151 | 83.6173 | 0
12504 | 877.2547 | 2.3317 | 16.9814 | 93.8883 | 25.3442 | 8.5505 | 55.9813 | 2.2307 |  | 20.2314 | 43.8252 | 8.0899 |  | 50.6201 | 131.2945 | 10.9129 | 27.1216 | 4.3036 | 122 | 34.9729 | 11.8562 | 86.3788 | 0
12505 | 876.5508 | 2.3635 | 17.0919 | 93.2996 | 24.0192 | 9.4997 | 56.3493 | 2.6817 |  | 19.3051 | 43.7532 | 7.943 |  | 51.7304 | 128.4392 | 10.788 | 28.4344 | 3.3885 | 125 | 30.5822 | 11.8178 | 86.2877 | 0
12506 | 870.329 | 2.3686 | 16.9675 | 93.3298 | 22.622 | 10.4497 | 56.9656 | 2.8648 |  | 16.9716 | 43.4769 | 7.8021 |  | 50.3697 | 132.3392 | 10.2222 | 27.9231 | 2.6383 | 129 | 36.0634 | 11.834 | 85.0534 | 0
12507 | 856.1526 | 2.3678 | 16.8047 | 92.8929 | 21.3901 | 11.3997 | 54.6072 | 2.6041 |  | 14.8732 | 42.4326 | 7.3336 |  | 48.9711 | 125.5146 | 10.6379 | 27.176 | 2.4878 | 115 | 35.5977 | 11.8307 | 86.2578 | 0
12508 | 870.5474 | 2.4152 | 16.0249 | 91.0287 | 18.4935 | 12.3497 | 52.6576 | 2.6862 |  | 14.2887 | 41.0628 | 6.0586 |  | 46.1013 | 118.1677 | 10.4162 | 26.5036 | 2.3693 | 112 | 32.3428 | 11.8502 | 98.6658 | 0
12509 | 883.1242 | 2.2309 | 29.4685 | 90.3513 | 17.4307 | 10.4505 | 53.2047 | 1.9619 |  | 18.1065 | 41.3543 | 6.5933 |  | 51.4211 | 118.0895 | 10.257 | 26.2471 | 2.326 | 111 | 39.8443 | 11.8442 | 104.077 | 0.035662
12510 | 919.0527 | 3.3239 | 44.1584 | 93.9101 | 9.936 | 12.3495 | 56.4462 | 2.1603 |  | 19.8779 | 45.9643 | 13.0724 |  | 79.9738 | 129.3354 | 13.5624 | 25.9241 | 2.3499 | 180 | 40.6522 | 12.3546 | 114.2131 | 0.042714
12511 | 947.1122 | 3.6673 | 71.9308 | 103.6594 | 7.5185 | 17.0987 | 59.6226 | 3.1022 |  | 18.855 | 63.2927 | 19.2157 |  | 101.3798 | 162.3165 | 25.9612 | 26.8298 | 6.1591 | 220 | 49.7021 | 15.7173 | 132.9773 | 0.10211
12512 | 999.9366 | 3.8232 | 89.3411 | 114.3945 | 13.4835 | 17.1 | 62.5008 | 4.7229 |  | 19.2576 | 75.1378 | 20.7585 |  | 116.0132 | 217.2373 | 34.5254 | 29.8539 | 11.0982 | 202 | 45.9021 | 16.5329 | 148.4564 | 0.12557
12513 | 1070.2379 | 3.9474 | 94.3096 | 124.0813 | 9.5256 | 22.7984 | 68.3397 | 4.8361 |  | 18.796 | 81.3779 | 19.0892 |  | 127.3257 | 256.1172 | 34.555 | 33.3249 | 13.3644 | 201 | 31.1143 | 14.9156 | 160.7275 | 0.17768
12514 | 1100.329 | 6.4789 | 97.0851 | 125.902 | 11.5623 | 21.8503 | 71.9015 | 4.5361 |  | 14.8739 | 86.9268 | 19.8357 |  | 136.1166 | 277.4321 | 33.7406 | 37.137 | 14.0502 | 206 | 40.8359 | 14.8254 | 161.8097 | 0.18277
12515 | 1112.6868 | 8.048 | 99.9856 | 128.6463 | 15.4889 | 19.0008 | 72.4677 | 4.5785 |  | 13.2607 | 90.1304 | 19.4431 |  | 137.6172 | 278.7512 | 31.5514 | 36.3343 | 14.2469 | 220 | 30.0995 | 13.4062 | 166.7722 | 0.16295
12516 | 1118.1043 | 5.1971 | 99.5203 | 132.5717 | 18.0983 | 18.0503 | 82.2765 | 4.8353 |  | 14.618 | 91.8975 | 18.8082 |  | 141.2218 | 276.6328 | 31.5117 | 34.7372 | 14.294 | 212 | 31.9742 | 13.223 | 167.3826 | 0.13397
12517 | 1150.7535 | 3.6751 | 101.8663 | 130.1866 | 19.0693 | 19.9495 | 103.1945 | 4.6544 |  | 15.1039 | 92.0042 | 19.5524 |  | 137.1275 | 272.206 | 30.4208 | 37.4426 | 14.0981 | 205 | 30.151 | 15.0802 | 162.3629 | 0.1712
12518 | 1140.5367 | 3.8965 | 102.296 | 130.0885 | 23.426 | 19.95 | 100.5284 | 4.9581 |  | 16.8049 | 91.8718 | 19.847 |  | 136.016 | 264.7142 | 31.2888 | 37.4368 | 13.8855 | 198 | 30.4164 | 13.8987 | 165.8711 | 0.18843
12519 | 1104.3101 | 4.0845 | 99.5319 | 127.8438 | 29.9869 | 19.95 | 102.0095 | 5.0139 |  | 15.5492 | 91.6022 | 21.7857 |  | 133.5089 | 259.015 | 29.868 | 37.1323 | 13.8632 | 180 | 36.7752 | 13.8202 | 161.2085 | 0.24158
12520 | 1077.7038 | 3.6019 | 96.9613 | 119.2593 | 44.3883 | 12.3521 | 75.959 | 4.1598 |  | 16.4749 | 88.6802 | 21.2737 |  | 128.098 | 233.516 | 25.7451 | 35.2226 | 13.5109 | 166 | 33.4673 | 12.6449 | 144.0028 | 0.24956
12521 | 1062.8003 | 7.4899 | 97.3278 | 110.7698 | 51.0104 | 12.3534 | 64.1292 | 2.6899 |  | 17.2317 | 82.2275 | 20.4551 |  | 102.6532 | 207.7967 | 15.1304 | 33.3103 | 14.1907 | 185 | 36.6824 | 11.1703 | 106.2238 | 0.28417
12522 | 1035.1705 | 10.281 | 95.8869 | 99.654 | 50.7423 | 10.4471 | 62.1153 | 2.3614 |  | 15.0586 | 69.3721 | 14.8689 |  | 75.3252 | 173.5451 | 9.7694 | 31.589 | 12.5255 | 171 | 35.4796 | 11.0157 | 96.7571 | 0.27329
12523 | 1016.4829 | 7.0073 | 84.4407 | 95.2629 | 46.7328 | 10.45 | 74.1247 | 2.0026 |  | 13.1825 | 63.6908 | 6.4804 |  | 65.3072 | 153.8462 | 12.4247 | 29.6018 | 6.3201 | 150 | 37.2312 | 11.0098 | 86.0047 | 0.20722
12524 | 992.073 | 3.8741 | 42.8169 | 93.7828 | 45.7919 | 11.3997 | 67.144 | 1.6512 |  | 12.7937 | 59.946 | 3.7802 |  | 56.9337 | 135.685 | 10.4806 | 28.3515 | 3.4573 | 138 | 36.506 | 11.0018 | 78.9681 | 0.13626
12525 | 959.1887 | 3.7772 | 23.7633 | 92.5478 | 47.6617 | 9.5005 | 70.205 | 2.4021 |  | 12.4462 | 52.0261 | 4.0418 |  | 48.0638 | 131.165 | 8.7066 | 27.3361 | 3.0067 | 128 | 31.1384 | 11.0134 | 78.5337 | 0.00049642
12526 | 936.1116 | 3.4851 | 22.2875 | 93.8809 | 47.3657 | 9.5 | 74.2898 | 2.4154 |  | 13.7762 | 44.7087 | 5.7617 |  | 44.8932 | 134.0218 | 9.5899 | 26.6534 | 2.9974 | 128 | 42.8668 | 12.7101 | 82.0458 | 0
12527 | 917.0399 | 2.738 | 22.187 | 95.2675 | 45.0273 | 9.5 | 61.6415 | 2.8676 |  | 14.5908 | 42.0041 | 6.6021 |  | 43.7894 | 132.3079 | 9.162 | 25.3275 | 2.6006 | 140 | 37.5042 | 11.5566 | 81.7053 | 0
12528 | 903.7883 | 2.374 | 22.1917 | 94.1263 | 40.51 | 10.4497 | 53.5319 | 2.3822 |  | 14.0029 | 42.2008 | 6.3649 |  | 41.4237 | 126.3411 | 9.9927 | 23.0273 | 2.3307 | 149 | 35.9227 | 11.0443 | 80.8309 | 0
12529 | 902.741 | 2.2119 | 22.4182 | 93.7832 | 40.0476 | 8.5505 | 49.8398 | 2.8291 |  | 12.9726 | 41.8028 | 6.1513 |  | 40.284 | 126.3027 | 9.2792 | 22.1967 | 2.3069 | 124 | 44.4093 | 11.0151 | 81.3589 | 0
12530 | 898.751 | 2.1704 | 22.4021 | 94.5904 | 36.0324 | 10.4495 | 51.4036 | 2.5964 |  | 12.8132 | 41.5373 | 6.0879 |  | 39.2975 | 127.8927 | 10.6253 | 22.0596 | 2.3032 | 119 | 32.5838 | 11.0211 | 80.626 | 0
12531 | 887.0073 | 2.1693 | 22.4298 | 92.8214 | 34.1784 | 10.45 | 51.1226 | 2.8691 |  | 12.0072 | 41.0617 | 5.5866 |  | 39.5039 | 126.409 | 9.2144 | 21.9078 | 2.2799 | 116 | 33.161 | 11.0206 | 80.3675 | 0
12532 | 892.2406 | 2.5135 | 22.1575 | 91.1039 | 33.0807 | 10.45 | 49.7437 | 2.2004 |  | 12.7036 | 40.1651 | 4.0011 |  | 40.222 | 119.3248 | 9.5456 | 22.563 | 2.162 | 113 | 38.0875 | 11.0282 | 84.3306 | 0
12533 | 905.2905 | 2.2396 | 22.0152 | 90.5987 | 32.2022 | 10.45 | 58.601 | 2.4165 |  | 17.1691 | 40.0075 | 3.3758 |  | 44.1088 | 113.9774 | 8.7164 | 24.4443 | 2.1048 | 111 | 29.5029 | 11.0338 | 86.3091 | 0.022217
12534 | 914.3203 | 2.1149 | 21.6835 | 91.4375 | 33.6496 | 8.5505 | 71.6369 | 1.9288 |  | 18.3568 | 43.9653 | 3.3846 |  | 66.338 | 112.407 | 10.0911 | 24.7646 | 2.1206 | 131 | 36.4192 | 11.0166 | 87.0003 | 0.072545
12535 | 917.3679 | 2.3309 | 29.9072 | 90.4384 | 27.0378 | 16.1479 | 83.978 | 1.5328 |  | 16.3546 | 53.3452 | 3.3009 |  | 77.3723 | 126.1268 | 9.2765 | 24.167 | 4.4408 | 158 | 35.4001 | 11.0112 | 89.5241 | 0.069765
12536 | 941.2067 | 2.1345 | 37.1429 | 90.1947 | 32.5122 | 13.3008 | 101.5354 | 1.913 |  | 16.4241 | 56.9368 | 3.4192 |  | 84.1505 | 149.9864 | 8.1067 | 24.722 | 10.163 | 157 | 29.8587 | 10.9995 | 91.4013 | 0.11388
12537 | 972.8111 | 2.256 | 39.0199 | 91.9858 | 39.5212 | 13.3 | 114.7146 | 1.7393 |  | 17.5456 | 62.4654 | 3.9753 |  | 93.0363 | 162.7949 | 9.7564 | 25.5794 | 12.8147 | 159 | 31.7657 | 11.0149 | 92.8506 | 0.1089
12538 | 996.5662 | 3.1809 | 39.3549 | 92.9953 | 50.5877 | 14.2497 | 120.3738 | 1.3901 |  | 19.2204 | 66.0287 | 4.9595 |  | 103.4504 | 173.8243 | 8.8983 | 25.3324 | 13.3318 | 163 | 38.1981 | 11.0093 | 90.9462 | 0.11721
12539 | 1005.3504 | 2.9995 | 40.1155 | 91.8556 | 58.6847 | 13.3003 | 122.3754 | 1.2667 |  | 20.1689 | 66.3928 | 7.3578 |  | 112.0143 | 176.7523 | 9.531 | 26.1698 | 13.7575 | 165 | 33.6442 | 10.9876 | 89.1468 | 0.18215
12540 | 999.8404 | 2.5363 | 39.5508 | 94.8796 | 58.9217 | 10.4508 | 126.6184 | 1.3004 |  | 20.2761 | 65.8896 | 9.953 |  | 115.3994 | 176.3561 | 8.8234 | 26.5687 | 14.615 | 177 | 43.8494 | 10.9991 | 91.8718 | 0.12979
12541 | 1001.1397 | 2.3853 | 40.097 | 96.7109 | 60.3207 | 11.4029 | 134.3379 | 1.3069 |  | 20.327 | 69.5806 | 11.0968 |  | 114.0785 | 187.1855 | 8.7375 | 26.604 | 15.4383 | 166 | 39.7098 | 10.9809 | 92.0994 | 0.12715
12542 | 992.6734 | 3.2703 | 40.8819 | 96.8665 | 65.1011 | 12.3466 | 141.4341 | 1.2903 |  | 20.3355 | 78.9914 | 15.1319 |  | 113.0662 | 193.1528 | 9.0876 | 26.6137 | 15.7788 | 166 | 38.2087 | 10.9752 | 91.9654 | 0.1522
12543 | 987.5809 | 3.4558 | 41.0784 | 95.5085 | 67.8553 | 11.4003 | 144.0335 | 1.6335 |  | 23.523 | 75.2959 | 17.1038 |  | 109.382 | 193.0389 | 8.8339 | 26.6553 | 15.7544 | 164 | 46.7292 | 10.9846 | 89.7469 | 0.21373
12544 | 972.2201 | 3.137 | 40.324 | 90.4006 | 68.0699 | 8.5508 | 137.3775 | 1.6423 |  | 23.6076 | 66.5604 | 18.6753 |  | 105.7498 | 185.886 | 9.3797 | 27.4752 | 15.5051 | 167 | 38.9934 | 10.9861 | 88.4021 | 0.2234
12545 | 974.1319 | 3.1089 | 40.1535 | 91.3671 | 63.6265 | 9.4997 | 128.7119 | 1.5873 |  | 22.2637 | 62.574 | 15.9523 |  | 94.6926 | 176.831 | 8.4762 | 27.6578 | 15.21 | 170 | 38.7231 | 10.8257 | 83.2801 | 0.17854
12546 | 972.5596 | 2.7514 | 39.4323 | 92.6822 | 63.6331 | 8.5503 | 108.9393 | 1.4739 |  | 20.999 | 60.5737 | 12.2388 |  | 81.5626 | 180.1159 | 9.4562 | 28.1738 | 12.7276 | 165 | 32.6734 | 10.9627 | 82.4791 | 0.07028
12547 | 947.2069 | 6.0161 | 36.3056 | 93.248 | 64.253 | 8.5524 | 73.0765 | 1.3927 |  | 20.1448 | 59.5564 | 7.9687 |  | 75.7913 | 173.4498 | 8.856 | 27.7123 | 7.2005 | 150 | 33.1914 | 11.1022 | 75.1139 | 0.11554
12548 | 926.3673 | 14.626 | 26.1161 | 90.4186 | 63.3103 | 7.5979 | 55.484 | 1.4464 |  | 17.8185 | 52.0169 | 6.2018 |  | 75.1526 | 149.3494 | 9.8678 | 24.2079 | 4.8036 | 148 | 34.6214 | 11.0086 | 64.074 | 0.038317
12549 | 916.6656 | 19.2404 | 22.421 | 90.3141 | 50.263 | 8.5497 | 48.83 | 1.6126 |  | 13.6824 | 43.3112 | 5.0722 |  | 71.0283 | 137.5077 | 8.9435 | 22.5777 | 4.4533 | 128 | 30.9309 | 10.9839 | 63.5412 | 0.00093769
12550 | 900.5687 | 14.4876 | 22.6415 | 90.7155 | 42.6292 | 6.6505 | 52.2772 | 1.9934 |  | 12.732 | 40.0339 | 6.3831 |  | 66.9825 | 130.1152 | 9.62 | 22.5474 | 4.2365 | 134 | 36.9823 | 12.664 | 67.7081 | 0
12551 | 876.8604 | 10.3357 | 22.8543 | 92.0928 | 36.6577 | 9.4992 | 49.2428 | 1.9685 |  | 12.711 | 39.03 | 7.5003 |  | 62.0633 | 122.6825 | 8.9214 | 23.5751 | 4.1129 | 128 | 30.4084 | 11.4595 | 67.5079 | 0
12552 | 882.6966 | 7.4715 | 22.79 | 92.8163 | 33.8068 | 9.5 | 55.3036 | 1.5726 |  | 12.1064 | 38.9688 | 7.4178 |  | 61.6172 | 124.2035 | 12.0326 | 26.9362 | 3.3373 | 125 | 26.9597 | 11.0382 | 73.1884 | 0
12553 | 875.6666 | 3.7955 | 22.6377 | 92.7502 | 30.3765 | 8.5503 | 59.1761 | 1.4346 |  | 12.0379 | 38.9684 | 7.2928 |  | 60.4413 | 122.1908 | 13.0404 | 27.6891 | 2.5929 | 122 | 35.1983 | 10.9839 | 79.9506 | 0
12554 | 867.0469 | 2.2508 | 22.5308 | 93.3373 | 27.7293 | 8.55 | 60.7744 | 2.3316 |  | 12.064 | 38.9579 | 7.1988 |  | 59.6348 | 120.6546 | 13.9621 | 27.4085 | 2.3469 | 116 | 29.9475 | 10.98 | 81.8049 | 0
12555 | 885.5384 | 2.166 | 22.313 | 93.3297 | 26.6414 | 8.55 | 55.3906 | 2.0643 |  | 11.9838 | 38.7725 | 7.2007 |  | 58.1412 | 118.6977 | 13.2563 | 27.5077 | 2.3127 | 113 | 28.5785 | 11.004 | 84.6615 | 0
12556 | 902.8991 | 2.7386 | 22.0237 | 92.109 | 24.1147 | 10.4495 | 49.36 | 2.4257 |  | 13.1059 | 37.4224 | 6.5842 |  | 57.5841 | 115.4463 | 12.9693 | 27.8652 | 2.2756 | 118 | 40.1938 | 10.9904 | 82.9055 | 0
12557 | 929.9839 | 3.926 | 33.7814 | 90.6095 | 24.3614 | 9.5003 | 59.1814 | 1.7723 |  | 17.4531 | 37.3865 | 6.0601 |  | 58.9582 | 114.0661 | 9.5955 | 26.5033 | 2.1503 | 108 | 31.474 | 10.9845 | 93.9031 | 0.041604
12558 | 965.5315 | 5.8806 | 54.5516 | 91.4516 | 21.6198 | 11.3995 | 71.506 | 1.5566 |  | 20.8217 | 42.4005 | 11.0388 |  | 82.0981 | 125.1007 | 12.7379 | 26.3611 | 2.1263 | 154 | 46.6071 | 11.0108 | 105.3796 | 0.071305
12559 | 1023.7789 | 10.1396 | 81.5303 | 98.6558 | 20.0353 | 17.0984 | 86.6721 | 3.758 |  | 30.9304 | 60.6934 | 19.7212 |  | 103.6602 | 158.4826 | 25.8878 | 29.4543 | 4.433 | 236 | 70.4387 | 15.2536 | 121.1243 | 0.11068
12560 | 1102.7906 | 18.2589 | 97.3795 | 119.49 | 25.2203 | 18.9995 | 98.9585 | 4.9171 |  | 38.7505 | 74.9708 | 23.672 |  | 126.2216 | 226.2004 | 35.6537 | 33.8702 | 9.878 | 248 | 71.2805 | 16.6376 | 149.8368 | 0.29961
12561 | 1165.1892 | 20.2369 | 104.6809 | 135.5216 | 23.742 | 22.7989 | 115.727 | 5.9555 |  | 40.0946 | 82.7591 | 20.6705 |  | 148.9108 | 268.7968 | 36.3578 | 39.6985 | 12.197 | 291 | 81.3138 | 15.8761 | 166.9366 | 0.27467
12562 | 1194.7285 | 13.3602 | 103.7422 | 145.2225 | 21.0079 | 24.6995 | 124.47 | 5.785 |  | 39.9565 | 88.4828 | 20.2471 |  | 157.9432 | 286.1683 | 38.5711 | 44.084 | 12.7114 | 286 | 77.7656 | 18.07 | 179.1441 | 0.32406
12563 | 1226.8169 | 7.2493 | 103.1761 | 148.9479 | 24.3247 | 20.9011 | 123.7616 | 5.3963 |  | 40.6044 | 92.1569 | 24.0553 |  | 162.3076 | 289.2522 | 36.6165 | 45.5299 | 12.5934 | 276 | 76.5065 | 17.3543 | 238.7817 | 0.25905
12564 | 1234.078 | 5.1351 | 104.0053 | 145.7411 | 24.9737 | 20.8826 | 122.4759 | 5.2314 |  | 38.941 | 94.5492 | 26.8688 |  | 159.9351 | 296.0028 | 35.9187 | 44.1373 | 12.8613 | 291 | 73.9029 | 16.2775 | 268.8455 | 0.27495
12565 | 1239.0031 | 5.1406 | 105.1706 | 147.5409 | 23.6978 | 22.8169 | 127.1228 | 5.0501 |  | 30.7356 | 95.4552 | 30.0458 |  | 159.7523 | 293.4463 | 38.6832 | 45.535 | 13.5215 | 270 | 66.8028 | 15.2627 | 268.4558 | 0.29877
12566 | 1220.5658 | 5.1281 | 103.0753 | 153.0002 | 25.9338 | 20.9005 | 129.7943 | 4.8884 |  | 29.0696 | 95.3917 | 30.1637 |  | 158.8315 | 290.2933 | 38.5536 | 44.9068 | 14.7119 | 291 | 68.1478 | 16.5226 | 264.5186 | 0.28946
12567 | 1189.0862 | 5.9539 | 100.0652 | 146.9541 | 26.0437 | 21.8497 | 125.1716 | 4.5339 |  | 27.1479 | 94.9777 | 30.2207 |  | 153.6335 | 285.4881 | 36.2466 | 45.582 | 13.5951 | 260 | 56.9736 | 17.7653 | 263.6397 | 0.23188
12568 | 1159.7597 | 5.3636 | 98.9081 | 138.8573 | 34.5131 | 15.2018 | 112.4276 | 5.0406 |  | 27.4228 | 92.8265 | 26.53 |  | 147.9189 | 259.056 | 30.8276 | 44.0153 | 12.8198 | 226 | 55.2351 | 13.0137 | 233.011 | 0.18159
12569 | 1117.31 | 5.3826 | 94.6422 | 120.4367 | 34.2119 | 16.1497 | 110.0741 | 3.7599 |  | 22.7677 | 83.184 | 23.2535 |  | 115.1576 | 220.885 | 18.77 | 38.4492 | 12.5318 | 203 | 46.0689 | 11.9666 | 182.9798 | 0.11599
12570 | 1078.2838 | 4.7305 | 91.3553 | 103.3097 | 39.545 | 12.3511 | 95.6126 | 2.673 |  | 19.2635 | 69.2798 | 18.1009 |  | 80.8224 | 190.6276 | 12.8991 | 33.827 | 9.8597 | 200 | 45.0081 | 11.7669 | 155.7725 | 0.11323
12571 | 1042.71 | 5.0716 | 81.5757 | 99.8479 | 39.6151 | 13.2997 | 72.0152 | 3.0528 |  | 18.8071 | 64.52 | 9.2452 |  | 69.971 | 173.6178 | 11.6036 | 31.0245 | 4.847 | 178 | 40.7782 | 12.0552 | 136.1004 | 0.10472
12572 | 994.6938 | 5.0417 | 42.4849 | 95.6325 | 36.8858 | 13.3 | 56.8206 | 2.8743 |  | 17.001 | 61.4748 | 5.9886 |  | 63.5223 | 155.6653 | 11.1638 | 29.1312 | 3.3504 | 156 | 42.9702 | 11.9736 | 133.8433 | 0.10809
12573 | 980.9728 | 4.4654 | 24.9102 | 98.3369 | 36.9579 | 10.4508 | 54.8819 | 2.7907 |  | 13.0112 | 52.8946 | 6.4692 |  | 51.6349 | 139.447 | 10.3897 | 28.8279 | 3.6282 | 140 | 37.9512 | 11.9677 | 127.8443 | 0.0074759
12574 | 965.4115 | 3.7366 | 23.7088 | 98.4338 | 34.4825 | 11.3997 | 53.15 | 2.2689 |  | 12.2835 | 44.7051 | 7.5176 |  | 47.4522 | 129.7054 | 10.3492 | 28.497 | 3.329 | 129 | 33.5147 | 13.7417 | 127.5512 | 0
12575 | 923.9917 | 2.8053 | 23.6214 | 95.953 | 32.8532 | 12.3497 | 47.3022 | 2.5971 |  | 12.1249 | 42.8972 | 7.9122 |  | 45.8674 | 127.3665 | 11.5417 | 27.8115 | 2.6354 | 125 | 40.2965 | 12.4705 | 128.6115 | 0
12576 | 909.9512 | 2.3525 | 23.3807 | 95.4134 | 34.7113 | 9.5008 | 53.3077 | 2.1436 |  | 12.2353 | 42.6554 | 7.9127 |  | 43.6893 | 126.05 | 10.1361 | 27.2276 | 2.3813 | 122 | 32.5555 | 12.0333 | 125.8586 | 0
12577 | 905.8165 | 3.113 | 23.4757 | 95.7175 | 32.5428 | 10.4497 | 57.2407 | 2.7936 |  | 12.8645 | 41.507 | 7.7718 |  | 42.2688 | 124.4146 | 10.6688 | 26.8155 | 2.3959 | 121 | 37.6945 | 11.9802 | 128.8617 | 0
12578 | 905.7969 | 2.7037 | 22.7773 | 95.0792 | 32.1666 | 10.45 | 54.2519 | 2.2305 |  | 13.0661 | 40.7601 | 7.6763 |  | 42.0379 | 124.2653 | 9.9797 | 27.214 | 2.384 | 115 | 38.0241 | 11.9854 | 129.8625 | 0
12579 | 908.4686 | 2.5701 | 18.8289 | 94.3825 | 31.6134 | 10.45 | 57.5378 | 2.5577 |  | 12.6482 | 40.1627 | 7.7148 |  | 42.782 | 122.1842 | 11.4601 | 26.9001 | 2.3992 | 111 | 31.1518 | 12.004 | 126.1765 | 0
12580 | 910.62 | 2.8899 | 16.923 | 92.1355 | 25.5319 | 11.3997 | 57.0862 | 1.9545 |  | 12.9076 | 38.6335 | 6.1364 |  | 41.0677 | 115.2197 | 9.8751 | 25.775 | 2.286 | 112 | 39.7483 | 11.9865 | 131.8506 | 0
12581 | 933.5658 | 4.1661 | 35.1696 | 91.8434 | 21.1049 | 11.4 | 54.8455 | 2.2217 |  | 17.812 | 38.5428 | 5.7256 |  | 45.0413 | 114.2438 | 10.1548 | 25.6085 | 2.19 | 110 | 31.7154 | 11.9602 | 149.4014 | 0.021025
12582 | 954.2107 | 4.9947 | 49.8389 | 93.5259 | 20.9367 | 11.4 | 66.8757 | 1.9933 |  | 21.6851 | 44.0503 | 11.0564 |  | 73.1668 | 123.8544 | 12.3971 | 26.5667 | 2.1981 | 159 | 41.7557 | 12.0376 | 172.9134 | 0.10123
12583 | 1005.3559 | 8.6023 | 74.3756 | 100.8696 | 15.3712 | 18.0482 | 89.3478 | 3.6538 |  | 21.3715 | 64.7232 | 18.5397 |  | 104.381 | 167.4351 | 27.2119 | 28.9262 | 5.8681 | 212 | 68.5986 | 15.2692 | 194.1637 | 0.17453
12584 | 1081.2022 | 9.661 | 95.3486 | 120.9514 | 19.2109 | 18.9997 | 105.8865 | 5.2854 |  | 21.3656 | 82.0897 | 19.7126 |  | 131.1202 | 233.8969 | 33.8476 | 33.8047 | 10.9333 | 262 | 70.6455 | 21.1458 | 232.6728 | 0.10478
12585 | 1145.622 | 10.5316 | 99.2741 | 135.522 | 19.7739 | 20.8995 | 118.0202 | 5.0985 |  | 21.5177 | 88.7393 | 18.8701 |  | 146.449 | 270.4263 | 39.2483 | 40.1121 | 12.5979 | 274 | 73.5092 | 20.1511 | 250.8053 | 0.15516
12586 | 1197.451 | 11.853 | 98.786 | 141.088 | 20.9674 | 19.9392 | 124.5703 | 4.9894 |  | 22.155 | 90.6716 | 21.4025 |  | 154.0132 | 280.1761 | 40.4191 | 43.6979 | 12.5279 | 274 | 60.5761 | 21.7364 | 258.8252 | 0.11495
12587 | 1201.2604 | 16.5764 | 103.0613 | 140.4919 | 19.2601 | 24.7097 | 125.36 | 5.1957 |  | 22.3289 | 91.1193 | 20.369 |  | 159.6464 | 284.17 | 43.1853 | 43.5936 | 7.7408 | 283 | 64.8875 | 19.5487 | 271.2859 | 0.18021
12588 | 1188.5201 | 15.3355 | 103.9592 | 141.4184 | 25.4974 | 22.8005 | 121.8215 | 5.6083 |  | 23.5852 | 91.1437 | 18.663 |  | 162.6126 | 280.3939 | 41.7853 | 40.9913 | 4.9131 | 296 | 57.8554 | 19.8862 | 271.2205 | 0.19787
12589 | 1196.9531 | 9.394 | 102.6192 | 144.3912 | 27.8428 | 23.7497 | 120.5548 | 5.4711 |  | 23.7358 | 91.6719 | 18.577 |  | 165.867 | 278.3128 | 41.26 | 42.9579 | 5.2606 | 260 | 62.8145 | 18.5074 | 274.9182 | 0.15398
12590 | 1198.2409 | 7.4844 | 102.441 | 147.8026 | 28.9801 | 23.75 | 130.6631 | 5.3584 |  | 21.5284 | 92.2926 | 19.5583 |  | 164.504 | 280.2216 | 40.7539 | 44.3856 | 10.8019 | 244 | 48.4734 | 18.2747 | 282.6968 | 0.12539
12591 | 1176.272 | 5.8034 | 100.6761 | 142.2504 | 28.1002 | 24.6997 | 128.3589 | 4.9609 |  | 18.8798 | 90.956 | 20.0554 |  | 155.8532 | 273.5018 | 39.2784 | 44.2717 | 13.6496 | 244 | 57.103 | 18.167 | 267.4746 | 0.15848
12592 | 1141.931 | 4.9075 | 96.8681 | 132.0142 | 37.7684 | 16.1524 | 113.9181 | 5.0035 |  | 18.1958 | 88.5591 | 19.266 |  | 143.6386 | 250.7018 | 32.5196 | 42.9077 | 13.5562 | 193 | 43.7479 | 15.2753 | 235.5935 | 0.13005
12593 | 1100.6933 | 4.1243 | 96.1341 | 115.5194 | 47.0416 | 12.3511 | 103.2799 | 3.8076 |  | 17.286 | 81.226 | 18.2696 |  | 110.1007 | 218.4634 | 19.2148 | 38.4765 | 13.3354 | 171 | 41.6422 | 13.8847 | 188.7856 | 0.083982
12594 | 1058.718 | 3.2448 | 93.3196 | 99.698 | 52.9576 | 12.35 | 94.0538 | 2.7115 |  | 16.2567 | 68.0314 | 15.4177 |  | 68.6504 | 187.8595 | 13.2944 | 33.4512 | 10.6103 | 160 | 31.5109 | 13.7333 | 166.3178 | 0.073225
12595 | 1015.1555 | 2.5149 | 81.6487 | 94.5195 | 51.4981 | 10.4505 | 71.972 | 2.0643 |  | 15.7598 | 64.4002 | 8.9212 |  | 50.3416 | 160.7371 | 10.5683 | 30.3579 | 4.5373 | 152 | 33.4997 | 13.736 | 141.7409 | 0.03665
12596 | 988.5637 | 3.0275 | 40.9171 | 92.9118 | 45.1871 | 8.5505 | 61.9456 | 1.9714 |  | 14.4196 | 70.8274 | 6.319 |  | 48.0345 | 142.7726 | 9.3997 | 28.8768 | 2.1546 | 150 | 40.9753 | 13.7632 | 133.1562 | 0.011346
12597 | 957.1936 | 4.3709 | 22.9972 | 92.5762 | 28.3236 | 11.3992 | 71.2305 | 1.5748 |  | 10.8917 | 61.6868 | 6.3515 |  | 50.6082 | 135.4754 | 9.4676 | 27.6876 | 2.1206 | 147 | 33.9598 | 13.7485 | 131.0392 | 0.0006619
12598 | 937.0214 | 4.0562 | 22.05 | 95.2199 | 27.9769 | 8.5508 | 72.5719 | 2.3678 |  | 11.1483 | 46.702 | 8.1267 |  | 51.7228 | 129.9194 | 10.0194 | 27.5114 | 2.2394 | 137 | 36.6484 | 15.4392 | 130.4967 | 0
12599 | 908.8719 | 2.911 | 22.1354 | 95.7357 | 37.6703 | 9.4997 | 62.6176 | 2.3157 |  | 11.9696 | 41.2158 | 9.0121 |  | 52.0571 | 126.7142 | 10.0952 | 26.9631 | 2.3054 | 126 | 38.9978 | 14.2907 | 133.6277 | 0
12600 | 896.5097 | 2.3558 | 22.0791 | 95.9895 | 43.9154 | 9.5 | 58.1856 | 2.5887 |  | 11.5295 | 41.2004 | 8.8972 |  | 50.909 | 125.4763 | 10.4121 | 26.6683 | 2.3148 | 125 | 33.6949 | 13.7896 | 131.6644 | 0
12601 | 895.7633 | 2.2592 | 21.9341 | 96.5327 | 45.3919 | 10.4497 | 59.3965 | 2.0795 |  | 11.7729 | 41.498 | 8.6671 |  | 49.8955 | 125.4038 | 10.7309 | 26.4756 | 2.3261 | 120 | 37.6796 | 13.7673 | 132.436 | 0
12602 | 896.5891 | 2.3187 | 21.8903 | 97.0572 | 45.9213 | 9.5003 | 61.0551 | 2.0413 |  | 12.2386 | 40.2867 | 8.6023 |  | 48.8748 | 122.6832 | 10.1813 | 26.5235 | 2.3304 | 117 | 35.4075 | 13.753 | 134.2947 | 0
12603 | 898.046 | 2.4115 | 19.6196 | 95.8535 | 42.4304 | 9.5 | 54.9673 | 2.3532 |  | 12.327 | 39.5665 | 8.5699 |  | 49.117 | 121.3055 | 10.5478 | 26.4907 | 2.3387 | 114 | 33.7246 | 13.7628 | 134.3204 | 0
12604 | 901.4328 | 2.7708 | 16.5371 | 94.6424 | 39.5628 | 10.4497 | 51.2634 | 2.0866 |  | 13.1534 | 38.2365 | 7.5303 |  | 48.9201 | 113.6981 | 10.187 | 26.0573 | 2.2566 | 115 | 39.8385 | 13.7713 | 141.8726 | 0
12605 | 915.5152 | 4.8655 | 29.8542 | 94.1878 | 40.1581 | 10.45 | 60.6707 | 2.3212 |  | 17.3558 | 37.9787 | 6.944 |  | 53.3206 | 115.7542 | 9.7412 | 25.6792 | 2.1547 | 112 | 30.8972 | 13.75 | 152.4502 | 0.086633
12606 | 965.2226 | 10.1656 | 47.7049 | 97.3036 | 39.4672 | 11.3997 | 76.5715 | 1.9383 |  | 20.2254 | 43.0284 | 10.815 |  | 84.0446 | 124.11 | 12.5079 | 25.8155 | 2.1397 | 160 | 38.7019 | 13.7653 | 178.7184 | 0.087945
12607 | 1027.2113 | 15.066 | 76.5117 | 102.5054 | 29.9505 | 18.9979 | 93.9824 | 3.6827 |  | 29.2012 | 60.696 | 16.2016 |  | 109.2096 | 171.2468 | 26.5218 | 28.2131 | 4.498 | 224 | 71.9283 | 17.4258 | 206.6169 | 0.075972
12608 | 1083.8882 | 18.2482 | 91.9468 | 121.3542 | 27.3272 | 19.9497 | 112.4631 | 4.8507 |  | 37.0633 | 78.9078 | 18.83 |  | 127.9445 | 228.7338 | 32.2085 | 33.193 | 9.8942 | 249 | 68.9995 | 19.3688 | 245.5798 | 0.15078
12609 | 1163.787 | 13.5822 | 96.2796 | 137.8275 | 25.9236 | 20.8997 | 120.5897 | 5.4412 |  | 39.1084 | 88.441 | 21.62 |  | 140.8438 | 259.7337 | 34.3118 | 39.5551 | 12.0479 | 277 | 72.4555 | 18.7863 | 274.6273 | 0.12296
12610 | 1233.651 | 8.6113 | 99.8213 | 145.8557 | 32.7561 | 19.0005 | 120.5872 | 4.9657 |  | 39.4918 | 91.0349 | 22.0101 |  | 147.1221 | 271.456 | 33.2202 | 41.7797 | 12.4371 | 288 | 65.3956 | 19.5122 | 275.6891 | 0.18322
12611 | 1226.3448 | 11.2633 | 98.658 | 143.8718 | 42.7079 | 19 | 137.7661 | 4.5679 |  | 39.0016 | 90.1916 | 21.9796 |  | 149.2414 | 268.6719 | 33.0019 | 41.6628 | 12.692 | 265 | 64.5693 | 17.9014 | 279.8783 | 0.12757
12612 | 1226.0588 | 11.1126 | 104.4318 | 144.8945 | 43.317 | 19.9497 | 149.3261 | 4.8006 |  | 37.18 | 91.5342 | 21.5892 |  | 149.4448 | 264.6163 | 33.7366 | 41.1642 | 12.7431 | 303 | 61.6089 | 20.308 | 269.2989 | 0.20049
12613 | 1204.6585 | 9.4608 | 102.5873 | 147.7652 | 36.068 | 16.1511 | 150.3412 | 4.7375 |  | 33.6247 | 92.1637 | 19.9384 |  | 152.8339 | 269.1844 | 34.354 | 40.2349 | 12.5831 | 259 | 53.6089 | 21.7453 | 265.102 | 0.15094
12614 | 1188.2409 | 6.1595 | 98.9356 | 145.8866 | 34.8785 | 17.0997 | 148.8881 | 4.5648 |  | 26.4496 | 90.9023 | 18.889 |  | 146.5257 | 281.9528 | 33.9018 | 40.5377 | 12.2468 | 259 | 57.408 | 20.2637 | 260.0189 | 0.13258
12615 | 1154.144 | 4.6636 | 98.1707 | 136.503 | 35.1284 | 19.9492 | 143.663 | 3.9371 |  | 20.5411 | 90.7776 | 18.4178 |  | 141.0537 | 276.6221 | 32.9498 | 41.0149 | 12.1081 | 260 | 51.0836 | 17.981 | 256.4705 | 0.17207
12616 | 1110.0964 | 4.1935 | 95.6154 | 125.5011 | 44.1749 | 12.3521 | 134.5914 | 2.9307 |  | 18.7354 | 89.1543 | 17.8247 |  | 135.7512 | 246.0966 | 25.9813 | 37.7385 | 12.1528 | 214 | 40.7419 | 13.6947 | 224.6453 | 0.14679
12617 | 1070.5136 | 3.7114 | 82.6345 | 117.5109 | 48.1205 | 8.5511 | 125.2574 | 2.0715 |  | 18.5485 | 83.0269 | 17.5296 |  | 103.3561 | 196.833 | 14.8536 | 34.1103 | 12.106 | 191 | 32.6453 | 13.1052 | 181.2145 | 0.077607
12618 | 1032.44 | 3.1892 | 40.7516 | 104.9834 | 38.6436 | 8.55 | 108.1324 | 1.4389 |  | 18.2923 | 68.2662 | 15.012 |  | 73.5813 | 178.9724 | 11.459 | 32.0747 | 9.8608 | 170 | 31.2578 | 13.1087 | 159.7142 | 0.049968
12619 | 989.904 | 8.6452 | 22.7103 | 97.0087 | 37.7354 | 8.55 | 73.9918 | 1.1091 |  | 16.8945 | 58.2712 | 8.6312 |  | 62.1049 | 171.4458 | 9.7949 | 29.1514 | 5.0162 | 146 | 35.3323 | 13.0964 | 134.6618 | 0.11432
12620 | 957.3558 | 11.1282 | 21.4356 | 94.6449 | 35.7784 | 7.6003 | 57.136 | 1.0511 |  | 14.7426 | 47.4488 | 6.2854 |  | 63.2769 | 154.8472 | 9.9593 | 27.1139 | 2.994 | 143 | 31.2365 | 13.0985 | 125.1709 | 0.096448
12621 | 929.3288 | 11.308 | 21.3552 | 94.3675 | 35.5275 | 7.6 | 52.7338 | 1.3294 |  | 11.008 | 42.3932 | 6.2923 |  | 61.2767 | 139.9292 | 8.5981 | 26.0397 | 2.5638 | 145 | 37.5565 | 13.0888 | 124.9131 | 0.0018754
12622 | 916.7002 | 6.3449 | 21.595 | 96.3478 | 33.7192 | 8.5497 | 54.9408 | 1.4361 |  | 10.9449 | 44.2496 | 8.1493 |  | 54.5478 | 134.6562 | 9.8981 | 26.1166 | 2.4765 | 138 | 31.9872 | 14.7167 | 130.0153 | 0
12623 | 897.615 | 2.7675 | 21.3702 | 97.0653 | 33.6379 | 8.55 | 56.7601 | 1.4675 |  | 11.272 | 43.5741 | 9.1011 |  | 46.5722 | 135.0842 | 9.2305 | 26.1941 | 2.5009 | 131 | 25.5416 | 23.4379 | 126.8364 | 0
12624 | 884.6115 | 2.7344 | 21.4986 | 96.2658 | 38.0529 | 7.6003 | 57.9804 | 2.2832 |  | 11.257 | 42.0107 | 9.1252 |  | 42.8642 | 127.0792 | 9.6022 | 26.2057 | 2.4855 | 129 | 35.0879 | 24.5836 | 126.8303 | 0
12625 | 881.2456 | 3.2679 | 21.6933 | 96.4513 | 40.7998 | 10.4492 | 54.283 | 2.0103 |  | 11.429 | 41.9742 | 9.0986 |  | 42.1793 | 122.4689 | 10.3412 | 27.1244 | 2.4001 | 127 | 26.6162 | 24.5639 | 129.329 | 0
12626 | 883.1764 | 2.7746 | 21.5317 | 96.3902 | 41.7247 | 10.45 | 50.3084 | 1.9158 |  | 11.2062 | 42.1667 | 8.9278 |  | 46.49 | 121.2597 | 9.2983 | 26.722 | 2.3694 | 135 | 25.5338 | 24.6412 | 127.1423 | 0
12627 | 879.4537 | 2.3078 | 21.5092 | 96.1579 | 42.0775 | 8.5505 | 52.2827 | 2.5565 |  | 10.9901 | 41.6358 | 8.8378 |  | 47.8936 | 121.2088 | 9.5568 | 26.5156 | 2.3556 | 136 | 34.9786 | 24.6865 | 126.3676 | 0
12628 | 893.9751 | 2.7147 | 21.0745 | 94.358 | 41.0132 | 9.4997 | 55.2855 | 2.0275 |  | 9.4143 | 39.913 | 6.9185 |  | 41.855 | 116.0299 | 8.8027 | 26.1342 | 2.248 | 129 | 30.8644 | 24.9065 | 124.276 | 0
12629 | 901.6671 | 3.6184 | 21.3291 | 93.5416 | 39.9706 | 9.5 | 57.4784 | 1.392 |  | 8.5748 | 39.5195 | 6.0662 |  | 38.2258 | 115.6526 | 10.0003 | 25.8508 | 2.1639 | 111 | 33.2411 | 20.2658 | 123.3931 | 0.13654
12630 | 927.1273 | 3.6907 | 38.7081 | 93.3008 | 36.089 | 10.4497 | 56.7786 | 2.0391 |  | 8.6466 | 42.0047 | 6.1045 |  | 37.8248 | 117.7482 | 9.459 | 25.6521 | 2.1953 | 114 | 37.5981 | 13.9992 | 125.9923 | 0.2054
12631 | 944.1343 | 2.4586 | 53.6517 | 93.5733 | 36.4212 | 8.5505 | 57.7148 | 1.6784 |  | 8.6517 | 46.4128 | 5.9792 |  | 37.8378 | 120.8686 | 8.1848 | 25.7251 | 2.299 | 110 | 28.8985 | 13.1329 | 125.1931 | 0.27647
12632 | 950.4277 | 2.2459 | 61.137 | 93.1513 | 37.1219 | 8.55 | 65.9595 | 1.6384 |  | 8.6451 | 42.9115 | 6.3858 |  | 39.459 | 127.148 | 9.6337 | 25.6495 | 2.3219 | 115 | 30.4849 | 13.116 | 129.1983 | 0.32672
12633 | 946.5816 | 2.2046 | 68.7069 | 93.0927 | 36.8741 | 9.4997 | 77.4683 | 1.4902 |  | 9.9973 | 44.5336 | 6.6749 |  | 44.5427 | 124.0439 | 8.7812 | 26.1299 | 4.2971 | 123 | 25.9075 | 13.1193 | 132.8395 | 0.32793
12634 | 947.6286 | 2.0362 | 83.4821 | 93.1395 | 38.3475 | 8.5503 | 90.0957 | 1.2645 |  | 13.8973 | 49.9477 | 6.5476 |  | 47.4732 | 125.4905 | 9.2715 | 26.5079 | 9.2926 | 122 | 20.6599 | 13.1192 | 130.9924 | 0.3336
12635 | 958.4773 | 2.2471 | 87.004 | 93.5555 | 38.2263 | 9.4997 | 108.476 | 1.5616 |  | 15.6082 | 53.3928 | 6.4999 |  | 48.37 | 123.5006 | 8.6791 | 27.2107 | 11.263 | 130 | 28.3123 | 13.1025 | 131.2665 | 0.26605
12636 | 966.1596 | 4.4915 | 88.3615 | 94.0291 | 40.7008 | 9.5 | 115.6505 | 1.9903 |  | 16.2773 | 60.2894 | 6.5616 |  | 47.739 | 129.2669 | 8.7526 | 27.2408 | 10.9909 | 138 | 13.6088 | 13.1079 | 129.586 | 0.2822
12637 | 956.683 | 8.6705 | 85.8163 | 93.3475 | 45.6032 | 8.5503 | 98.6551 | 1.6379 |  | 17.6152 | 62.6468 | 7.0003 |  | 48.6395 | 134.9815 | 9.2777 | 26.9397 | 10.7617 | 140 | 8.2814 | 13.1217 | 132.418 | 0.3038
12638 | 965.2307 | 6.2962 | 65.7006 | 93.5582 | 49.1055 | 9.4997 | 75.2945 | 1.1758 |  | 18.1574 | 63.9587 | 6.4423 |  | 50.8475 | 141.9091 | 8.3107 | 27.1724 | 8.703 | 166 | 18.0289 | 13.1244 | 132.6748 | 0.29974
12639 | 963.3421 | 3.7104 | 44.8253 | 93.9106 | 52.4276 | 8.5503 | 68.5623 | 1.2654 |  | 16.7871 | 65.2033 | 5.3176 |  | 49.3113 | 147.8615 | 9.7676 | 27.5018 | 4.1762 | 176 | 10.633 | 13.1143 | 132.1583 | 0.30833
12640 | 952.0439 | 2.799 | 39.4675 | 95.8055 | 49.3003 | 9.4997 | 61.6887 | 1.129 |  | 13.4673 | 64.7337 | 4.8023 |  | 48.182 | 149.699 | 8.6367 | 27.4321 | 2.5279 | 162 | 20.4175 | 13.1111 | 131.572 | 0.25975
12641 | 946.6667 | 2.3889 | 39.0021 | 95.4737 | 45.3631 | 9.5 | 62.6539 | 1.0231 |  | 11.8371 | 62.4051 | 4.9186 |  | 49.558 | 138.6077 | 8.7894 | 27.275 | 2.7406 | 147 | 23.119 | 13.1101 | 133.1007 | 0.28121
12642 | 916.2041 | 2.4416 | 38.7774 | 94.0187 | 49.916 | 7.6005 | 61.3686 | 1.0666 |  | 12.2533 | 56.8901 | 4.9708 |  | 44.2704 | 134.8398 | 8.3642 | 26.5663 | 2.8015 | 141 | 19.6299 | 13.0935 | 129.4084 | 0.25804
12643 | 910.5591 | 2.5443 | 38.4977 | 94.5068 | 50.0515 | 8.5497 | 61.4275 | 1.2966 |  | 11.6553 | 52.1019 | 4.8405 |  | 41.4599 | 129.7806 | 9.631 | 26.5737 | 2.6851 | 150 | 26.7248 | 13.0625 | 127.2547 | 0.15946
12644 | 907.8982 | 2.9508 | 37.6816 | 95.7703 | 47.6248 | 9.4997 | 62.9584 | 1.382 |  | 10.3144 | 44.9793 | 5.1239 |  | 41.5535 | 130.1666 | 8.5937 | 26.3927 | 2.5718 | 147 | 27.167 | 13.085 | 129.3466 | 0.12648
12645 | 904.2975 | 4.5287 | 37.6877 | 94.7277 | 46.4369 | 8.5503 | 64.266 | 1.8263 |  | 9.0326 | 42.1419 | 5.2055 |  | 41.778 | 127.9983 | 9.3312 | 26.2117 | 2.4191 | 151 | 23.8156 | 13.1064 | 129.8466 | 0.0097232
12646 | 911.3531 | 5.2474 | 37.8047 | 95.1323 | 44.8553 | 7.6003 | 59.991 | 1.8029 |  | 8.8461 | 41.9308 | 5.9824 |  | 42.4172 | 127.978 | 8.4323 | 26.1636 | 2.2831 | 155 | 34.8043 | 14.7211 | 128.0296 | 0
12647 | 898.9607 | 3.9803 | 37.5238 | 96.4704 | 39.6808 | 10.4492 | 72.5641 | 2.4543 |  | 10.3635 | 42.7825 | 7.2155 |  | 40.9858 | 123.2307 | 10.1735 | 26.5672 | 2.3057 | 129 | 31.1228 | 23.6764 | 129.7685 | 0
12648 | 889.75 | 2.6292 | 38.3085 | 96.404 | 39.8885 | 8.5505 | 73.2021 | 2.071 |  | 11.0402 | 43.0505 | 8.4668 |  | 40.0657 | 126.7311 | 12.3925 | 26.7916 | 2.3669 | 131 | 29.3237 | 24.9745 | 132.3682 | 0
12649 | 889.9758 | 2.2418 | 37.9783 | 95.8561 | 36.2793 | 9.4997 | 57.8393 | 2.6721 |  | 11.0967 | 41.8871 | 8.0761 |  | 40.3972 | 127.6124 | 14.1358 | 27.061 | 2.5057 | 130 | 38.8615 | 21.0708 | 134.1272 | 0
12650 | 889.2972 | 2.321 | 37.391 | 96.055 | 34.9626 | 9.5 | 58.5579 | 2.2882 |  | 11.0496 | 41.3119 | 7.482 |  | 40.611 | 131.1001 | 13.4249 | 26.8931 | 2.4129 | 127 | 32.9046 | 14.1376 | 133.8129 | 0
12651 | 892.1823 | 2.3846 | 37.4163 | 96.196 | 35.0173 | 9.5 | 62.2694 | 1.7349 |  | 10.5282 | 40.6683 | 7.1174 |  | 40.0098 | 129.2724 | 13.6338 | 26.7456 | 2.3345 | 115 | 30.0128 | 13.1228 | 134.2448 | 0
12652 | 895.8074 | 2.8877 | 37.2008 | 94.0405 | 35.0338 | 9.5 | 58.6921 | 2.1878 |  | 8.9581 | 39.4029 | 5.3688 |  | 38.8941 | 123.2618 | 12.2042 | 26.5414 | 2.1825 | 115 | 41.1423 | 13.1207 | 128.3923 | 0
12653 | 898.8408 | 2.3253 | 38.5818 | 92.8355 | 34.2034 | 10.4497 | 55.3382 | 1.6855 |  | 8.282 | 39.255 | 4.6232 |  | 38.7999 | 121.7017 | 9.8548 | 25.995 | 2.1101 | 111 | 32.9941 | 13.1287 | 129.1157 | 0.15888
12654 | 912.0347 | 1.87 | 39.2625 | 92.456 | 36.2416 | 8.5505 | 55.453 | 1.2995 |  | 8.1494 | 41.478 | 4.5607 |  | 39.6734 | 123.3285 | 9.4932 | 25.6432 | 2.1297 | 112 | 24.862 | 13.0945 | 129.0049 | 0.21591
12655 | 916.2774 | 1.9764 | 38.484 | 93.6873 | 34.8389 | 10.4495 | 57.7103 | 1.2756 |  | 8.0535 | 46.3309 | 4.4986 |  | 39.0426 | 117.7868 | 8.8229 | 25.6618 | 2.2464 | 113 | 24.3549 | 13.1001 | 125.9119 | 0.27353
12656 | 917.4365 | 1.9305 | 38.0312 | 92.8547 | 36.8306 | 9.5003 | 58.7165 | 1.5143 |  | 8.4943 | 43.1197 | 4.6058 |  | 38.7776 | 117.4326 | 8.8676 | 25.7926 | 2.2663 | 112 | 32.9002 | 13.1112 | 129.432 | 0.32121
12657 | 937.0678 | 1.8882 | 38.1349 | 92.1461 | 36.6301 | 8.5503 | 60.5139 | 2.331 |  | 10.2221 | 40.6018 | 4.57 |  | 41.65 | 114.3976 | 9.0439 | 25.6168 | 2.2617 | 116 | 25.8268 | 13.1009 | 131.0136 | 0.26299
12658 | 947.1925 | 2.2406 | 38.2807 | 92.8404 | 37.1468 | 8.55 | 75.3767 | 1.6462 |  | 14.3864 | 41.542 | 7.2492 |  | 47.5058 | 119.3244 | 9.474 | 26.0382 | 2.233 | 120 | 20.5528 | 13.1046 | 132.2953 | 0.32769
12659 | 974.3736 | 2.238 | 38.8998 | 92.5321 | 37.4219 | 9.4997 | 96.2416 | 1.0797 |  | 17.089 | 50.4924 | 9.2746 |  | 49.5012 | 121.0692 | 9.0615 | 25.9859 | 2.1562 | 136 | 32.1137 | 13.0913 | 135.118 | 0.24292
12660 | 979.4803 | 2.427 | 38.9259 | 92.8046 | 39.6689 | 8.5503 | 112.603 | 1.076 |  | 17.3493 | 61.3918 | 7.7548 |  | 51.4686 | 121.9821 | 8.6373 | 26.4264 | 2.1175 | 135 | 25.0213 | 13.1174 | 136.0595 | 0.13648
12661 | 978.4791 | 2.1626 | 38.4751 | 93.0408 | 37.6499 | 10.4495 | 96.6209 | 1.0675 |  | 17.2297 | 65.129 | 9.1332 |  | 55.4227 | 123.5956 | 8.2218 | 26.3884 | 2.1424 | 137 | 26.6669 | 13.1076 | 129.4242 | 0.2573
12662 | 946.5726 | 4.708 | 38.2597 | 95.2164 | 39.4187 | 8.5505 | 75.8364 | 1.036 |  | 17.2499 | 65.6085 | 10.5969 |  | 57.365 | 134.913 | 8.8138 | 26.9578 | 2.2597 | 140 | 32.7792 | 13.1205 | 130.1646 | 0.29231
12663 | 960.0425 | 8.5169 | 38.5042 | 97.7475 | 37.7888 | 9.4997 | 60.7335 | 1.0611 |  | 15.9536 | 65.8585 | 11.0821 |  | 55.6871 | 140.5753 | 9.9229 | 27.6428 | 2.2883 | 149 | 26.2308 | 13.1046 | 124.7498 | 0.2985
12664 | 963.205 | 6.9294 | 38.5353 | 95.5441 | 39.4864 | 8.5503 | 54.188 | 1.3863 |  | 12.1524 | 65.8169 | 11.0443 |  | 54.3118 | 141.8863 | 9.0334 | 27.2876 | 2.2988 | 146 | 27.3731 | 13.1233 | 126.5968 | 0.15658
12665 | 969.4682 | 3.5754 | 38.0552 | 94.6259 | 39.0088 | 8.55 | 55.0752 | 1.1897 |  | 10.3819 | 62.6294 | 7.618 |  | 53.6397 | 137.6436 | 9.5083 | 27.9594 | 2.28 | 142 | 27.9992 | 13.1191 | 128.77 | 0.22728
12666 | 965.6472 | 2.9568 | 37.9942 | 94.139 | 37.2538 | 9.4997 | 56.8291 | 1.0494 |  | 10.1882 | 61.6152 | 5.6418 |  | 53.0541 | 144.3685 | 8.7805 | 27.3848 | 2.2715 | 137 | 24.6118 | 13.1104 | 127.602 | 0.25439
12667 | 953.5096 | 11.054 | 38.0762 | 93.2994 | 37.0681 | 9.5 | 57.1011 | 1.9492 |  | 10.4081 | 61.7214 | 5.6562 |  | 51.8864 | 138.1256 | 8.7427 | 27.559 | 2.2526 | 126 | 32.1499 | 13.087 | 121.9259 | 0.21338
12668 | 930.0637 | 17.2312 | 38.2093 | 93.2161 | 37.6353 | 9.5 | 57.9323 | 1.6536 |  | 10.4026 | 50.6687 | 5.4297 |  | 51.0934 | 128.1575 | 9.1783 | 26.9593 | 2.3103 | 130 | 27.2635 | 13.1112 | 116.8563 | 0.11844
12669 | 910.9055 | 14.941 | 38.549 | 92.6058 | 37.0368 | 10.4497 | 52.4968 | 1.4417 |  | 10.1463 | 44.1138 | 5.8898 |  | 50.1621 | 133.8348 | 8.8265 | 26.6743 | 2.3247 | 121 | 25.2709 | 13.1155 | 119.5704 | 0.0080195
12670 | 906.2014 | 9.7896 | 39.0337 | 94.5975 | 39.7062 | 7.6008 | 51.0129 | 2.3789 |  | 11.4728 | 43.9432 | 7.5509 |  | 48.5985 | 136.8582 | 9.1093 | 27.0273 | 2.4226 | 114 | 37.9671 | 14.7886 | 125.1325 | 0
12671 | 870.2363 | 4.273 | 38.8761 | 95.3476 | 37.2672 | 8.5497 | 54.0788 | 2.1606 |  | 11.5075 | 42.0839 | 8.4143 |  | 49.3125 | 133.5489 | 10.2247 | 26.3059 | 2.4449 | 116 | 28.4953 | 23.2304 | 123.8973 | 0
12672 | 849.2884 | 2.2385 | 38.7435 | 96.0914 | 37.5463 | 7.6003 | 71.8406 | 1.9751 |  | 11.0232 | 40.2943 | 8.2482 |  | 49.0711 | 126.1075 | 9.092 | 26.355 | 2.4183 | 121 | 28.7083 | 24.5915 | 124.6344 | 0
12673 | 839.9488 | 2.2536 | 37.5554 | 95.5475 | 36.1618 | 8.5497 | 74.5751 | 2.6211 |  | 11.0371 | 39.8431 | 7.9238 |  | 47.9766 | 121.3599 | 9.7351 | 26.5577 | 2.3414 | 113 | 36.0261 | 24.5957 | 126.6556 | 0
12674 | 840.9382 | 2.3355 | 36.8673 | 96.9206 | 32.4078 | 11.3992 | 65.0008 | 2.1304 |  | 11.0631 | 39.7302 | 7.9711 |  | 47.3412 | 120.0205 | 8.9452 | 26.3986 | 2.3171 | 113 | 36.5903 | 16.0467 | 127.8112 | 0
12675 | 844.4428 | 2.3411 | 37.2995 | 96.229 | 31.6552 | 8.5508 | 59.7871 | 2.4989 |  | 10.956 | 39.5658 | 7.9529 |  | 47.8872 | 119.7702 | 9.9803 | 26.5271 | 2.3239 | 110 | 35.9092 | 13.3481 | 130.7304 | 0
12676 | 852.9368 | 2.7235 | 38.0574 | 93.4466 | 25.6193 | 9.4997 | 59.8243 | 1.8237 |  | 11.134 | 37.998 | 6.0321 |  | 47.0473 | 113.5663 | 8.5692 | 26.076 | 2.1911 | 113 | 36.1698 | 13.1244 | 141.8669 | 0
12677 | 878.4906 | 2.9353 | 38.3627 | 93.0686 | 23.5598 | 9.5 | 60.2903 | 1.3338 |  | 15.6585 | 38.0313 | 5.7731 |  | 51.5507 | 115.7856 | 9.0449 | 26.111 | 2.121 | 116 | 33.1528 | 13.1475 | 146.129 | 0.052158
12678 | 921.0241 | 4.1781 | 40.0898 | 98.4326 | 22.356 | 10.4497 | 69.2185 | 2.5758 |  | 19.6632 | 45.0892 | 10.4157 |  | 79.3938 | 132.0983 | 11.4621 | 25.9668 | 2.1284 | 157 | 38.8864 | 13.1435 | 169.6363 | 0.041786
12679 | 963.7377 | 8.4291 | 64.7261 | 109.3436 | 16.5173 | 18.0479 | 89.5208 | 3.483 |  | 17.0259 | 64.2437 | 16.7093 |  | 99.0453 | 175.4718 | 26.1738 | 28.6632 | 2.4603 | 215 | 49.5903 | 16.8552 | 205.3956 | 0.10236
12680 | 1047.2273 | 11.7545 | 88.4423 | 124.3456 | 18.3338 | 18.9997 | 109.9645 | 4.2086 |  | 16.1957 | 80.9547 | 18.8695 |  | 117.9138 | 221.0806 | 32.1686 | 34.0574 | 4.064 | 251 | 50.0118 | 19.4841 | 245.5393 | 0.13539
12681 | 1146.2132 | 9.9433 | 94.5711 | 137.7838 | 17.0887 | 20.8995 | 121.372 | 4.7191 |  | 16.0242 | 87.314 | 18.957 |  | 135.1652 | 250.4718 | 34.5191 | 39.5612 | 9.6844 | 266 | 50.9115 | 18.5853 | 268.4643 | 0.23232
12682 | 1174.975 | 9.4709 | 92.2357 | 138.9463 | 16.6891 | 20.9 | 125.1783 | 4.6836 |  | 15.2166 | 88.4058 | 20.579 |  | 139.8956 | 262.656 | 35.5176 | 42.7652 | 12.2522 | 324 | 51.1667 | 20.2595 | 270.0793 | 0.11695
12683 | 1195.9296 | 12.9338 | 94.8594 | 139.0818 | 16.8018 | 20.9 | 132.7788 | 4.6106 |  | 15.5352 | 89.3732 | 21.614 |  | 146.8139 | 262.9005 | 34.9208 | 51.7632 | 12.2106 | 275 | 45.439 | 19.9893 | 271.768 | 0.26019
12684 | 1203.957 | 14.0475 | 94.6855 | 144.5358 | 18.6141 | 19.9503 | 129.5865 | 5.6977 |  | 16.5094 | 91.0799 | 20.6803 |  | 148.4456 | 262.3646 | 35.3117 | 52.993 | 12.1339 | 293 | 42.4124 | 18.9129 | 263.4504 | 0.27025
12685 | 1199.1474 | 11.5505 | 97.2233 | 148.3472 | 19.7484 | 19.95 | 137.1669 | 5.7372 |  | 15.8846 | 90.8301 | 19.6749 |  | 146.2363 | 272.3257 | 36.1138 | 52.3094 | 12.6845 | 256 | 44.2804 | 18.9358 | 273.1917 | 0.29222
12686 | 1194.5616 | 11.2311 | 97.6748 | 150.658 | 18.9373 | 21.8495 | 147.6782 | 5.0533 |  | 16.135 | 90.6301 | 19.4258 |  | 142.1441 | 278.0369 | 36.1022 | 49.8039 | 13.0474 | 234 | 42.806 | 20.6563 | 263.7154 | 0.21935
12687 | 1187.4088 | 10.6833 | 94.8763 | 141.4924 | 10.1916 | 30.3976 | 146.4764 | 4.5408 |  | 16.7064 | 90.1304 | 17.8376 |  | 137.6368 | 268.1347 | 35.4582 | 49.7773 | 12.8312 | 233 | 43.2742 | 19.5758 | 253.8041 | 0.14512
12688 | 1167.4276 | 6.7609 | 92.4996 | 132.2558 | 24.4664 | 16.154 | 133.1244 | 3.9101 |  | 16.6531 | 86.8871 | 17.0349 |  | 129.7918 | 237.6788 | 29.5725 | 49.6605 | 13.1115 | 202 | 38.8999 | 15.7457 | 237.8693 | 0.25806
12689 | 1113.5515 | 7.0732 | 89.374 | 116.5734 | 27.3452 | 12.3511 | 113.9429 | 3.5819 |  | 16.5544 | 79.1419 | 16.6604 |  | 101.4288 | 198.1565 | 16.1227 | 47.7447 | 13.1395 | 184 | 31.2441 | 14.9564 | 187.4664 | 0.27068
12690 | 1058.6691 | 9.8551 | 90.588 | 102.6706 | 28.1551 | 10.4505 | 90.8124 | 2.7829 |  | 16.5727 | 66.0506 | 14.1783 |  | 68.7522 | 180.542 | 11.747 | 44.5627 | 10.085 | 178 | 32.6614 | 14.8726 | 161.4656 | 0.21522
12691 | 1022.4154 | 10.1271 | 80.6509 | 97.1438 | 26.6952 | 11.3997 | 67.8625 | 1.7834 |  | 16.1821 | 60.9416 | 8.3592 |  | 54.3269 | 162.1371 | 10.0843 | 40.5654 | 4.367 | 151 | 32.8431 | 14.9227 | 135.481 | 0.029604
12692 | 989.1329 | 6.548 | 39.8375 | 95.923 | 27.3536 | 10.4503 | 61.0346 | 2.1296 |  | 14.5637 | 58.7331 | 6.0197 |  | 50.3663 | 144.83 | 9.4853 | 37.0464 | 2.2931 | 137 | 34.4758 | 14.9276 | 129.4777 | 0.012007
12693 | 963.0101 | 4.3505 | 22.1115 | 94.1385 | 25.788 | 11.3997 | 65.5131 | 1.939 |  | 10.886 | 50.5816 | 5.9695 |  | 48.2097 | 136.0237 | 9.4022 | 35.7109 | 2.4266 | 128 | 34.0088 | 14.9302 | 129.2378 | 0.002096
12694 | 933.3127 | 3.7691 | 18.7129 | 94.9611 | 25.2789 | 11.4 | 68.7941 | 1.7195 |  | 10.9432 | 43.0283 | 7.5032 |  | 48.0201 | 135.8529 | 10.5676 | 36.059 | 2.578 | 126 | 36.3156 | 15.2812 | 128.95 | 0
12695 | 908.7965 | 2.8511 | 15.8767 | 95.8481 | 22.6709 | 13.2995 | 64.5677 | 2.4954 |  | 11.4032 | 40.8066 | 8.3452 |  | 49.0019 | 127.936 | 9.8428 | 36.5681 | 2.528 | 116 | 34.94 | 15.004 | 130.1689 | 0
12696 | 897.9232 | 2.3435 | 15.0314 | 96.7102 | 27.2106 | 8.5513 | 54.4077 | 2.1271 |  | 11.15 | 40.9388 | 8.2236 |  | 48.813 | 122.916 | 9.2365 | 36.2175 | 2.5051 | 114 | 33.4277 | 14.9189 | 132.7271 | 0
12697 | 895.1349 | 2.4012 | 14.958 | 96.7282 | 24.8923 | 10.4495 | 52.1384 | 2.6517 |  | 11.0762 | 41.168 | 8.1044 |  | 48.1172 | 119.8146 | 10.2278 | 36.1666 | 2.4592 | 113 | 40.0299 | 14.9048 | 134.1223 | 0
12698 | 894.0426 | 2.324 | 14.9144 | 95.9718 | 25.4661 | 9.5003 | 55.6095 | 2.3212 |  | 11.0365 | 40.8941 | 7.8081 |  | 48.6662 | 123.8289 | 10.0238 | 36.3494 | 2.3907 | 111 | 37.2702 | 14.922 | 131.9703 | 0
12699 | 896.7068 | 2.2604 | 14.7586 | 95.3889 | 25.0469 | 8.5503 | 50.3178 | 2.532 |  | 10.1544 | 39.9229 | 7.2029 |  | 48.8541 | 123.1577 | 9.4996 | 36.0479 | 2.3209 | 109 | 37.5524 | 14.9236 | 131.9018 | 0
12700 | 902.8271 | 2.5426 | 14.155 | 93.344 | 19.1537 | 11.3992 | 48.4353 | 1.8237 |  | 10.8991 | 38.9921 | 5.6206 |  | 47.8408 | 115.7132 | 9.9484 | 35.6156 | 2.2119 | 110 | 37.5227 | 14.9355 | 139.0851 | 0
12701 | 918.4548 | 2.7017 | 28.0197 | 92.48 | 16.9123 | 11.4 | 61.9046 | 2.1539 |  | 15.8893 | 39.0065 | 5.8089 |  | 53.3341 | 114.4943 | 8.5842 | 35.4865 | 2.163 | 125 | 35.4956 | 14.9204 | 156.6128 | 0.05422
12702 | 954.0474 | 8.4965 | 47.8228 | 96.0109 | 19.7432 | 11.4 | 74.3912 | 2.0304 |  | 18.6476 | 44.4943 | 10.9284 |  | 80.625 | 123.1333 | 11.9056 | 36.1451 | 2.1707 | 173 | 40.4708 | 15.7838 | 181.2906 | 0.043452
12703 | 1006.12 | 15.6916 | 73.604 | 102.1978 | 19.1817 | 14.2492 | 95.1978 | 2.829 |  | 19.6727 | 63.5991 | 16.2327 |  | 103.4253 | 174.2187 | 24.6231 | 38.565 | 4.4661 | 256 | 49.6347 | 18.6365 | 208.5728 | 0.15618
12704 | 1061.6387 | 11.7141 | 86.9138 | 120.827 | 16.7614 | 17.0992 | 117.6345 | 3.8533 |  | 19.4553 | 78.8735 | 21.2729 |  | 125.4705 | 229.5855 | 29.881 | 43.6521 | 9.878 | 284 | 42.2673 | 18.5682 | 243.2222 | 0.14174
12705 | 1143.1613 | 8.2716 | 90.4121 | 134.1732 | 18.0928 | 18.0497 | 132.4024 | 4.1364 |  | 20.9633 | 85.7616 | 24.3138 |  | 139.0838 | 254.2109 | 31.2161 | 48.4256 | 11.9467 | 294 | 37.1451 | 18.4584 | 263.0427 | 0.1082
12706 | 1174.1848 | 8.0701 | 90.2186 | 138.5134 | 19.9401 | 19.9495 | 131.9273 | 4.3885 |  | 19.7695 | 88.6677 | 21.9614 |  | 142.2473 | 259.4522 | 33.138 | 52.4031 | 12.0166 | 288 | 41.8445 | 21.1474 | 257.5018 | 0.12137
12707 | 1191.6469 | 6.7182 | 92.5156 | 139.4784 | 29.3959 | 16.1511 | 132.5018 | 5.0051 |  | 17.2052 | 90.2721 | 19.7921 |  | 147.2341 | 257.8687 | 33.8211 | 52.4573 | 12.0785 | 272 | 31.3125 | 21.624 | 259.8404 | 0.13276
12708 | 1202.6749 | 6.8744 | 96.0261 | 141.1022 | 35.3916 | 19.9489 | 137.1976 | 6.0519 |  | 17.078 | 90.7874 | 19.8746 |  | 148.3655 | 264.273 | 33.1444 | 53.5837 | 12.1947 | 317 | 29.2093 | 22.0081 | 266.402 | 0.20604
12709 | 1199.2836 | 11.0837 | 99.3023 | 142.7749 | 43.8876 | 18.0505 | 143.6118 | 5.1603 |  | 19.4263 | 91.519 | 18.5756 |  | 146.6374 | 262.9637 | 33.3096 | 54.6409 | 12.1351 | 269 | 30.0924 | 20.263 | 265.5922 | 0.1897
12710 | 1184.1367 | 10.1476 | 99.998 | 143.692 | 45.4887 | 20.8992 | 147.7581 | 4.4093 |  | 19.0164 | 90.1129 | 17.5613 |  | 142.2886 | 265.5424 | 33.8958 | 54.7306 | 12.1263 | 253 | 30.4118 | 21.7259 | 264.2684 | 0.21407
12711 | 1160.7958 | 10.4585 | 96.9001 | 139.1928 | 47.2479 | 23.7492 | 143.1414 | 4.0226 |  | 18.5194 | 89.8962 | 17.3529 |  | 136.2975 | 257.605 | 31.963 | 54.3235 | 12.0804 | 258 | 29.4216 | 18.9416 | 255.1307 | 0.25772
12712 | 1127.0612 | 10.4356 | 93.0073 | 130.3427 | 52.1597 | 12.3532 | 135.0709 | 3.4866 |  | 19.134 | 88.3294 | 16.9058 |  | 132.3491 | 221.5943 | 28.1092 | 53.787 | 12.0202 | 209 | 23.2122 | 0 | 224.9555 | 0.24159
12713 | 1074.909 | 8.6155 | 89.4566 | 115.9388 | 40.9389 | 9.5008 | 125.1518 | 3.0149 |  | 18.7082 | 80.4775 | 16.6565 |  | 107.8461 | 193.4302 | 15.9483 | 49.8966 | 12.1436 | 181 | 20.37 | 15.9606 | 184.2702 | 0.2317
12714 | 1024.5253 | 14.0893 | 86.495 | 103.5297 | 28.3201 | 9.5 | 106.4688 | 2.1509 |  | 17.7181 | 68.834 | 14.4414 |  | 74.1348 | 172.6209 | 10.2144 | 44.8479 | 9.8493 | 173 | 25.8841 | 15.3614 | 142.6945 | 0.1268
12715 | 977.3682 | 18.1355 | 81.3643 | 97.037 | 30.9056 | 12.3492 | 70.5061 | 1.4693 |  | 16.2223 | 64.1245 | 8.0678 |  | 61.2598 | 157.0422 | 10.108 | 39.3586 | 4.5412 | 148 | 28.7565 | 15.2955 | 119.9062 | 0.029001
12716 | 963.9096 | 14.091 | 39.3781 | 97.275 | 40.3564 | 10.4505 | 53.0028 | 1.1365 |  | 13.6739 | 61.1321 | 5.5536 |  | 57.9278 | 143.9261 | 11.0808 | 37.0362 | 2.546 | 127 | 34.3413 | 15.2662 | 112.7497 | 0.023454
12717 | 960.4699 | 7.1869 | 18.6848 | 97.3467 | 44.8913 | 7.6008 | 48.017 | 1.9913 |  | 9.7415 | 53.5906 | 5.5645 |  | 54.66 | 133.513 | 9.9566 | 36.619 | 2.5249 | 127 | 34.9893 | 15.3148 | 120.515 | 0.0011583
12718 | 939.2133 | 4.376 | 16.4954 | 99.4816 | 43.9843 | 7.6 | 50.4268 | 2.0064 |  | 8.7956 | 45.5583 | 6.3241 |  | 54.8882 | 125.9011 | 11.2546 | 36.4974 | 2.3959 | 122 | 35.7844 | 15.677 | 121.5151 | 0
12719 | 288.7553 | 1.4509 | 4.7037 | 28.0746 | 20.3033 | 0.002112 | 16.3967 | 0.58755 |  | 2.9452 | 14.833 | 2.1601 |  | 16.0789 | 41.4221 | 3.4611 | 10.3458 | 0.77484 | 123 | 3.4546 | 2.1111 | 12.6528 | 0
12720 | 898.0646 | 2.1726 | 16.1196 | 103.5168 | 39.4132 | 9.5 | 54.7624 | 2.2184 |  | 11.0899 | 43.3853 | 8.0871 |  | 58.9812 | 125.2885 | 10.5441 | 36.3432 | 2.3289 | 114 | 39.811 | 15.3138 | 125.1078 | 0
12721 | 895.1615 | 2.1339 | 15.8075 | 102.8752 | 37.2801 | 9.5 | 51.1911 | 2.0891 |  | 11.2369 | 42.4159 | 8.1346 |  | 54.0324 | 132.5684 | 10.6757 | 36.4267 | 2.33 | 113 | 38.9846 | 15.3065 | 125.0397 | 0
12722 | 897.3099 | 2.2292 | 16.0166 | 103.5387 | 33.5241 | 10.4497 | 49.6063 | 2.6405 |  | 11.3031 | 41.5507 | 8.1246 |  | 52.528 | 133.7703 | 10.684 | 36.4012 | 2.3345 | 116 | 39.2113 | 15.3006 | 129.6317 | 0
12723 | 900.6823 | 2.3232 | 16.0602 | 102.965 | 32.2653 | 9.5003 | 50.3298 | 1.9905 |  | 9.9946 | 40.0714 | 7.1665 |  | 51.7967 | 127.6855 | 10.988 | 36.1689 | 2.2908 | 110 | 39.2613 | 15.3323 | 126.1293 | 0
12724 | 909.4628 | 2.3262 | 15.5848 | 100.3524 | 31.0531 | 10.4497 | 48.6633 | 2.1555 |  | 10.7584 | 38.9941 | 5.6965 |  | 49.6516 | 116.8999 | 9.8024 | 36.0755 | 2.1779 | 109 | 39.4752 | 15.3358 | 130.5136 | 0
12725 | 915.4942 | 3.7508 | 21.6149 | 101.2368 | 30.5301 | 10.45 | 49.8904 | 1.717 |  | 16.0291 | 39.2531 | 6.0861 |  | 51.9911 | 115.7309 | 10.3754 | 35.912 | 2.1443 | 107 | 37.513 | 15.3174 | 136.2015 | 0.10814
12726 | 946.4659 | 8.6683 | 29.839 | 100.4288 | 29.8696 | 10.45 | 68.3813 | 2.0436 |  | 18.6966 | 44.6122 | 10.998 |  | 75.2055 | 124.1264 | 14.1644 | 36.0007 | 2.16 | 160 | 36.5337 | 15.3884 | 157.1653 | 0.20649
12727 | 989.2687 | 12.4261 | 60.6202 | 101.3558 | 23.7232 | 17.0982 | 107.4978 | 2.5053 |  | 21.5808 | 61.7282 | 16.2301 |  | 98.2327 | 158.3775 | 24.34 | 38.3476 | 4.4502 | 239 | 41.1551 | 17.952 | 184.8489 | 0.27663
12728 | 1051.3033 | 12.4737 | 89.0997 | 121.1842 | 22.8569 | 18.9995 | 124.4331 | 3.2717 |  | 22.3471 | 74.375 | 17.6517 |  | 118.3799 | 212.3796 | 30.7608 | 42.3946 | 9.9927 | 269 | 41.1016 | 18.1895 | 227.8333 | 0.32687
12729 | 1131.6677 | 12.3829 | 95.2851 | 134.6666 | 21.5107 | 22.7989 | 129.6935 | 3.8315 |  | 18.4882 | 81.8335 | 17.3554 |  | 132.9343 | 241.226 | 31.3975 | 45.138 | 13.9254 | 299 | 34.3101 | 19.5136 | 253.4386 | 0.32287
12730 | 1173.2505 | 13.1195 | 95.9063 | 136.1883 | 28.3111 | 20.9005 | 129.0864 | 3.8918 |  | 22.6757 | 85.8301 | 18.0401 |  | 142.1089 | 253.6876 | 31.4745 | 48.6346 | 14.3965 | 274 | 31.0088 | 24.1222 | 256.0382 | 0.32928
12731 | 1183.9421 | 9.8448 | 99.6834 | 133.2846 | 39.1789 | 19.0005 | 127.5777 | 3.6037 |  | 26.8433 | 87.3812 | 18.3022 |  | 145.2444 | 253.8238 | 32.7482 | 51.6592 | 13.0549 | 262 | 31.8455 | 23.4318 | 260.8721 | 0.25683
12732 | 1164.2504 | 5.057 | 102.6808 | 136.6471 | 37.8078 | 20.8995 | 130.538 | 4.6029 |  | 22.9882 | 86.9635 | 18.6608 |  | 145.1025 | 255.5274 | 32.9021 | 52.1082 | 12.4765 | 273 | 31.421 | 22.8046 | 258.1026 | 0.27303
12733 | 1182.2967 | 3.8464 | 101.9958 | 143.8222 | 37.4959 | 19.9503 | 136.2756 | 4.5803 |  | 21.9924 | 87.9305 | 17.863 |  | 147.4816 | 254.3431 | 33.3248 | 53.5893 | 12.7518 | 256 | 31.9921 | 23.1166 | 265.9026 | 0.29734
12734 | 1170.6658 | 3.8739 | 101.5236 | 145.3399 | 42.2995 | 18.0505 | 138.2375 | 4.3922 |  | 21.2689 | 88.4866 | 17.5425 |  | 146.8869 | 247.8784 | 34.2267 | 54.0733 | 12.9974 | 253 | 27.7926 | 24.0365 | 261.2542 | 0.2959
12735 | 1163.2123 | 3.909 | 103.9949 | 141.7581 | 45.7195 | 19.9495 | 133.2922 | 4.3307 |  | 18.5112 | 88.8413 | 17.4083 |  | 139.8583 | 243.6695 | 33.915 | 53.3447 | 13.4755 | 248 | 29.003 | 22.8529 | 255.6049 | 0.30797
12736 | 1137.257 | 3.9674 | 101.7523 | 136.4063 | 57.2205 | 10.4526 | 126.9257 | 4.3103 |  | 16.7685 | 87.6081 | 16.7669 |  | 127.8558 | 215.2118 | 29.2224 | 51.4729 | 13.8517 | 227 | 24.1536 | 21.3186 | 229.8583 | 0.25548
12737 | 1089.9136 | 3.7772 | 99.0771 | 121.4786 | 52.5049 | 9.5003 | 118.3084 | 3.1182 |  | 17.181 | 79.2977 | 16.5414 |  | 94.4081 | 177.9248 | 16.5286 | 48.8331 | 13.6403 | 200 | 19.5048 | 18.0024 | 188.0423 | 0.19566
12738 | 1025.1541 | 3.6919 | 96.6868 | 103.8825 | 46.9223 | 8.5503 | 101.1693 | 2.1274 |  | 17.7559 | 65.6785 | 14.126 |  | 59.8539 | 165.4184 | 11.7887 | 46.1309 | 10.5902 | 168 | 23.9233 | 16.8054 | 167.8398 | 0.2029
12739 | 988.6451 | 3.2551 | 86.6303 | 98.5169 | 44.7162 | 8.55 | 67.2808 | 1.8643 |  | 17.1246 | 59.9288 | 7.9434 |  | 46.5459 | 159.1751 | 10.6496 | 43.1311 | 4.929 | 138 | 26.7902 | 16.2313 | 138.2858 | 0.063721
12740 | 964.9744 | 3.0015 | 42.584 | 97.8353 | 44.6799 | 9.4997 | 51.6784 | 1.411 |  | 14.788 | 64.0111 | 5.5071 |  | 42.6393 | 144.6363 | 11.0062 | 38.0883 | 2.7581 | 131 | 28.6521 | 16.1784 | 133.4734 | 0.10042
12741 | 953.455 | 3.4135 | 23.1877 | 99.4863 | 42.9179 | 10.4497 | 55.3638 | 1.8833 |  | 11.1956 | 62.5794 | 5.4938 |  | 40.4404 | 133.8187 | 9.9281 | 36.2242 | 2.741 | 140 | 27.9408 | 16.1984 | 126.5573 | 0.014158
12742 | 936.3238 | 3.6146 | 22.1978 | 102.9878 | 42.3564 | 9.5003 | 50.2481 | 2.0219 |  | 10.2555 | 46.8371 | 6.3573 |  | 41.0808 | 123.5544 | 10.5454 | 36.3882 | 2.6458 | 140 | 30.3191 | 16.5526 | 125.1924 | 0
12743 | 288.1766 | 1.2574 | 6.4287 | 29.0065 | 20.6723 | 0.00264 | 14.7196 | 0.63406 |  | 3.4056 | 13.7143 | 2.1886 |  | 12.042 | 40.2143 | 3.1328 | 10.3314 | 0.86212 | 128 | 3.0287 | 2.2472 | 13.5964 | 0
12744 | 896.0153 | 2.2132 | 22.3174 | 105.7982 | 42.0986 | 7.6008 | 54.0246 | 2.457 |  | 12.8522 | 42.4316 | 8.1981 |  | 42.102 | 123.744 | 11.2159 | 36.6929 | 2.6774 | 117 | 35.8326 | 16.2791 | 130.2942 | 0
12745 | 897.2071 | 2.2714 | 22.3609 | 105.4875 | 40.3267 | 8.5497 | 53.1816 | 2.0933 |  | 12.6628 | 42.2979 | 8.0592 |  | 41.604 | 127.4835 | 10.289 | 36.8453 | 2.6952 | 118 | 35.8391 | 16.1916 | 131.5133 | 0
12746 | 889.9456 | 2.3264 | 22.6681 | 105.991 | 36.8301 | 9.4997 | 47.8374 | 1.7378 |  | 12.2706 | 41.7414 | 7.9263 |  | 41.5309 | 121.1163 | 10.3804 | 36.554 | 2.6974 | 117 | 37.9171 | 16.1909 | 130.2711 | 0
12747 | 888.9664 | 2.2143 | 22.0305 | 104.9074 | 34.6191 | 9.5 | 48.0943 | 2.6159 |  | 11.0528 | 40.8046 | 7.2893 |  | 41.4569 | 116.1243 | 12.269 | 36.2849 | 2.661 | 108 | 38.5989 | 16.2092 | 132.3143 | 0
12748 | 278.5879 | 0.75872 | 6.3285 | 29.4809 | 17.6476 | 0.00264 | 15.6421 | 1.0104 |  | 3.4705 | 14.0546 | 2.2903 |  | 12.1413 | 39.1919 | 3.7457 | 10.3912 | 0.88601 | 109 | 3.7809 | 2.1802 | 14.6048 | 0
12749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0.076015
12750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0.10996
12751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0.091049
12752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0.25462
12753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0.3032
12754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0.31352
12755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0.26319
12756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0.26954
12757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 0.28746
12758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0.28578
12759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0.29847
12760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | 0.25314
12761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0.2808
12762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0.26369
12763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0.22738
12764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0.13899
12765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0.017128
12766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0
12767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0
12768 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0
12769 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0
12770 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0
12771 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0
12772 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 0
12773 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0.15704
12774 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0.21541
12775 | 1015.402 | 0 | 0 | 0 | -13.2533 | 12.5906 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0.27761
12776 | 1058.7097 | 7.5438 | 93.809 | 124.7641 | 38.7668 | 16.1595 | 97.0394 | 4.0869 |  | 16.7723 | 79.6122 | 15.966 |  | 110.3249 | 204.6131 | 27.7763 | 43.4211 | 10.4922 | 249 | 44.5404 | 26.162 | 217.3807 | 0.32466
12777 | 1111.4785 | 10.4173 | 106.9394 | 137.2863 | 41.086 | 17.0997 | 114.2825 | 4.4567 |  | 16.0155 | 90.4988 | 18.0279 |  | 132.3736 | 248.5041 | 31.5259 | 47.0124 | 12.4697 | 298 | 49.7653 | 24.0354 | 271.7112 | 0.31712
12778 | 1170.6256 | 11.4886 | 106.4712 | 139.0072 | 36.3348 | 20.8989 | 111.7426 | 4.5984 |  | 15.6592 | 93.8899 | 18.4123 |  | 140.1325 | 270.3438 | 31.6405 | 49.3075 | 12.6551 | 297 | 52.1177 | 26.5583 | 275.6438 | 0.31792
12779 | 1199.5131 | 15.4296 | 102.6864 | 137.8105 | 39.8576 | 19.0005 | 108.9641 | 4.7547 |  | 15.3206 | 96.7203 | 18.0176 |  | 141.0036 | 278.7145 | 33.1912 | 49.8407 | 12.5893 | 276 | 48.5244 | 24.2279 | 278.1354 | 0.25309
12780 | 1197.4447 | 17.5264 | 101.6267 | 137.4544 | 48.4493 | 16.1508 | 109.1305 | 4.6998 |  | 15.6599 | 98.6641 | 17.1562 |  | 139.4073 | 279.3247 | 32.1971 | 48.4543 | 12.4571 | 273 | 45.1209 | 23.5602 | 253.3995 | 0.27107
12781 | 1203.1575 | 10.6306 | 104.2252 | 138.8348 | 51.1207 | 16.15 | 118.0148 | 4.7636 |  | 16.223 | 100.7793 | 11.9415 |  | 139.3609 | 282.1824 | 33.7853 | 48.9672 | 12.4945 | 248 | 44.3244 | 24.129 | 270.4385 | 0.2892
12782 | 1188.8793 | 4.733 | 104.8419 | 138.2794 | 44.1709 | 20.8987 | 116.2402 | 4.5483 |  | 16.4721 | 101.2122 | 9.1392 |  | 137.3585 | 284.8406 | 33.2439 | 50.2805 | 12.618 | 246 | 47.0861 | 24.853 | 264.1279 | 0.28624
12783 | 1152.5874 | 3.3262 | 103.2697 | 132.6481 | 32.8694 | 29.4476 | 115.0149 | 4.2301 |  | 16.3729 | 100.3057 | 9.0222 |  | 128.3337 | 261.9408 | 33.4847 | 48.7092 | 12.6099 | 216 | 40.861 | 22.5065 | 230.89 | 0.2568
12784 | 1102.7408 | 3.3273 | 99.6999 | 120.3506 | 36.316 | 19.9526 | 113.0226 | 3.514 |  | 15.2602 | 92.9208 | 8.8513 |  | 120.5398 | 227.5091 | 26.2527 | 47.1315 | 12.3148 | 214 | 38.7332 | 18.3952 | 195.5383 | 0.22959
12785 | 1055.4262 | 3.5616 | 87.1068 | 113.8517 | 39.2269 | 13.3018 | 106.6448 | 2.0623 |  | 13.9129 | 83.2781 | 8.7158 |  | 91.0009 | 191.8376 | 13.8542 | 44.317 | 12.5727 | 169 | 25.1882 | 17.2116 | 157.2144 | 0.27438
12786 | 1020.08 | 2.9718 | 40.0666 | 105.4284 | 46.9096 | 8.5513 | 84.8387 | 1.4009 |  | 10.1122 | 71.1159 | 7.9804 |  | 62.0307 | 175.7241 | 8.9418 | 42.117 | 10.2747 | 159 | 29.0641 | 17.5306 | 139.7853 | 0.25402
12787 | 979.5091 | 7.5895 | 19.7325 | 101.5626 | 47.1782 | 9.4997 | 54.5705 | 1.1698 |  | 7.9571 | 62.2987 | 8.9282 |  | 53.0158 | 152.5928 | 8.4173 | 39.5018 | 4.5771 | 146 | 32.8989 | 17.4947 | 120.1672 | 0.13816
12788 | 957.392 | 10.1068 | 17.8308 | 100.4754 | 49.2942 | 8.5503 | 37.5305 | 1.0668 |  | 7.8046 | 50.5408 | 9.6723 |  | 52.4845 | 144.1336 | 8.5283 | 38.414 | 2.5217 | 135 | 33.3919 | 17.4444 | 113.7908 | 0.034853
12789 | 942.1266 | 6.4982 | 17.3398 | 97.4656 | 50.5412 | 9.5024 | 40.8452 | 1.1399 |  | 7.8839 | 45.21 | 5.9856 |  | 46.4675 | 134.638 | 8.1781 | 36.9739 | 2.4411 | 128 | 30.6868 | 17.4331 | 114.9577 | 0.0020409
12790 | 922.998 | 4.3433 | 17.9453 | 96.9076 | 53.6448 | 7.5979 | 38.9053 | 2.3369 |  | 9.5771 | 45.633 | 5.9285 |  | 41.6787 | 134.06 | 8.91 | 36.4805 | 2.5233 | 119 | 33.4366 | 17.8062 | 114.9728 | 0
12791 | 286.5347 | 1.483 | 5.2743 | 27.1466 | 24.763 | 0.002111 | 11.5851 | 0.95925 |  | 3.4104 | 15.9472 | 2.1954 |  | 11.8743 | 46.0642 | 2.6501 | 10.382 | 0.86304 | 112 | 3.1824 | 2.3826 | 11.983 | 0
12792 | 885.4611 | 11.8239 | 18.2817 | 97.7659 | 51.8067 | 8.5503 | 36.5457 | 1.7212 |  | 10.7017 | 45.5669 | 6.8362 |  | 39.5977 | 125.1807 | 8.7759 | 36.3848 | 2.5562 | 111 | 33.9378 | 20.2986 | 115.8472 | 0
12793 | 888.5134 | 11.7737 | 18.1762 | 97.7264 | 50.4085 | 8.55 | 38.2798 | 1.6783 |  | 10.6051 | 44.9122 | 6.5799 |  | 39.9822 | 121.6134 | 9.2684 | 36.2458 | 2.5861 | 106 | 34.2179 | 20.3237 | 118.9761 | 0
12794 | 879.9724 | 5.641 | 17.8069 | 97.8212 | 48.3941 | 8.55 | 35.6311 | 1.9386 |  | 10.6535 | 44.296 | 6.4879 |  | 41.0816 | 125.5662 | 8.7203 | 36.435 | 2.5913 | 111 | 33.1103 | 19.9279 | 118.5194 | 0
12795 | 881.359 | 2.4444 | 17.9173 | 97.5264 | 47.0224 | 9.4997 | 38.7086 | 1.8455 |  | 10.2571 | 43.5611 | 6.4881 |  | 40.1087 | 124.968 | 9.129 | 36.5555 | 2.6151 | 110 | 31.2923 | 17.7508 | 116.3677 | 0
12796 | 893.5341 | 2.0651 | 17.7056 | 95.7511 | 49.0648 | 7.6005 | 36.2394 | 1.4435 |  | 8.5815 | 41.9348 | 4.6124 |  | 37.4925 | 120.2427 | 8.3043 | 36.0269 | 2.4491 | 101 | 31.4067 | 17.4115 | 113.581 | 0
12797 | 889.9307 | 1.841 | 16.9192 | 94.2682 | 46.5773 | 9.4995 | 40.916 | 1.9676 |  | 7.8491 | 42.2213 | 3.6266 |  | 36.3699 | 113.7613 | 8.6293 | 35.6192 | 2.3795 | 103 | 29.4295 | 17.4027 | 109.7131 | 0.03529
12798 | 889.1089 | 2.0837 | 16.4001 | 94.073 | 47.7326 | 8.5503 | 38.6504 | 1.6436 |  | 7.8592 | 46.5379 | 4.5576 |  | 36.9692 | 111.2888 | 8.6514 | 35.4251 | 2.386 | 107 | 21.6365 | 17.3713 | 112.9927 | 0.22338
12799 | 904.0399 | 2.3203 | 16.4661 | 95.5322 | 47.9598 | 10.4495 | 43.2387 | 1.2939 |  | 8.4277 | 45.8804 | 4.5626 |  | 37.5323 | 110.9917 | 7.6997 | 35.3365 | 2.5109 | 103 | 19.4687 | 17.4138 | 115.7163 | 0.28981
12800 | 906.8477 | 2.2915 | 16.0399 | 95.3963 | 52.5312 | 8.5505 | 56.4393 | 1.2803 |  | 8.9649 | 42.986 | 4.311 |  | 38.152 | 113.9521 | 8.3383 | 35.119 | 2.5274 | 105 | 32.2976 | 17.7188 | 118.0543 | 0.33868
12801 | 928.5619 | 2.4869 | 36.5434 | 94.853 | 49.8265 | 10.4495 | 63.7747 | 1.7413 |  | 10.4199 | 45.7731 | 4.1957 |  | 39.6142 | 119.135 | 8.4972 | 35.5835 | 4.6126 | 113 | 23.4034 | 17.667 | 118.9914 | 0.32794
12802 | 943.6546 | 5.0271 | 66.8242 | 95.1728 | 41.7033 | 7.6008 | 68.9645 | 1.4135 |  | 13.8154 | 50.2692 | 4.0343 |  | 42.1311 | 130.043 | 7.8544 | 35.2601 | 9.6506 | 112 | 16.6295 | 0 | 119.8404 | 0.31574
12803 | 958.8693 | 5.5722 | 76.3546 | 94.7856 | 43.5837 | 7.6 | 68.8589 | 1.517 |  | 15.0427 | 54.4587 | 4.1771 |  | 44.5249 | 133.5193 | 8.5747 | 34.9307 | 11.753 | 120 | 14.3871 | 17.4124 | 120.4632 | 0.2537
12804 | 964.3969 | 3.5383 | 76.9067 | 94.8445 | 50.3979 | 7.6 | 72.571 | 1.2289 |  | 15.0516 | 59.5019 | 4.3428 |  | 47.4926 | 129.0626 | 7.6665 | 35.0816 | 11.955 | 124 | 11.1132 | 17.3825 | 114.8111 | 0.27072
12805 | 962.2969 | 2.8059 | 67.4018 | 95.5912 | 49.9309 | 8.5497 | 72.8273 | 1.484 |  | 15.0793 | 67.661 | 4.0628 |  | 45.4325 | 129.946 | 8.4415 | 35.2911 | 11.9752 | 125 | 9.2593 | 17.3864 | 116.9967 | 0.29557
12806 | 952.4587 | 3.3415 | 34.8236 | 95.5444 | 50.8202 | 8.55 | 64.5968 | 1.4634 |  | 15.0519 | 75.8625 | 4.199 |  | 45.7003 | 133.8815 | 8.6138 | 35.8934 | 9.7945 | 139 | 5.6132 | 17.3729 | 118.1441 | 0.29096
12807 | 955.9211 | 5.114 | 19.8029 | 94.8278 | 53.0533 | 7.6003 | 44.502 | 1.1554 |  | 13.6732 | 68.9287 | 3.8609 |  | 44.9183 | 130.5402 | 8.6094 | 35.4098 | 5.1353 | 143 | 7.8888 | 17.3737 | 117.2429 | 0.30892
12808 | 948.7452 | 3.6311 | 17.9009 | 95.5671 | 49.61 | 7.6 | 35.3344 | 1.2252 |  | 9.8555 | 63.5054 | 3.8046 |  | 50.476 | 129.7612 | 7.6802 | 35.5752 | 3.3367 | 142 | 9.2456 | 17.3676 | 113.0912 | 0.25688
12809 | 937.4579 | 2.4711 | 17.678 | 94.9904 | 35.7327 | 9.4995 | 39.9286 | 1.1157 |  | 8.5535 | 64.9882 | 3.9491 |  | 52.4019 | 138.918 | 8.0271 | 35.7814 | 3.2947 | 140 | 16.0872 | 17.3943 | 109.6436 | 0.29212
12810 | 921.9223 | 3.1268 | 17.4752 | 94.9814 | 34.7083 | 7.6005 | 40.5473 | 1.0808 |  | 8.741 | 68.8646 | 3.9366 |  | 49.7523 | 142.3301 | 8.9597 | 35.4788 | 3.2887 | 144 | 19.5034 | 17.3831 | 110.0903 | 0.28024
12811 | 907.6729 | 6.3809 | 17.345 | 95.1014 | 39.6421 | 6.6503 | 41.0421 | 1.0994 |  | 8.7949 | 62.1296 | 4.0997 |  | 43.7257 | 138.1862 | 8.0779 | 35.8667 | 3.3292 | 146 | 27.1264 | 17.4086 | 106.535 | 0.24953
12812 | 900.6466 | 9.234 | 16.9772 | 93.3282 | 29.503 | 9.4992 | 42.9935 | 1.2876 |  | 8.1032 | 48.7107 | 3.9883 |  | 41.4193 | 127.3244 | 7.9681 | 35.803 | 3.1076 | 136 | 27.5326 | 17.146 | 105.7012 | 0.15728
12813 | 905.8636 | 8.6371 | 16.3012 | 94.3281 | 28.0629 | 6.6508 | 36.4025 | 1.7679 |  | 7.5463 | 43.7664 | 3.9004 |  | 41.066 | 127.0727 | 8.0589 | 35.5573 | 2.9298 | 139 | 27.4119 | 17.3188 | 106.9211 | 0.027345
12814 | 911.5883 | 7.4242 | 16.1812 | 95.179 | 33.9521 | 10.4489 | 40.8509 | 1.7502 |  | 8.0177 | 43.0878 | 4.7271 |  | 47.8493 | 122.0227 | 8.2036 | 35.8243 | 3.2942 | 140 | 29.9534 | 17.6924 | 107.5777 | 0
12815 | 288.1292 | 2.5376 | 4.7475 | 27.0133 | 20.7696 | 0.002903 | 14.2715 | 0.54956 |  | 2.7622 | 15.0283 | 1.6929 |  | 14.9895 | 40.3626 | 2.3913 | 10.3513 | 1.1845 | 111 | 2.9009 | 2.3568 | 10.394 | 0
12816 | 891.1241 | 9.7067 | 15.5119 | 97.8704 | 47.5834 | 7.6008 | 41.9414 | 1.7312 |  | 10.5021 | 43.7843 | 6.8782 |  | 49.6986 | 124.7657 | 11.9914 | 36.6058 | 3.296 | 115 | 30.5257 | 17.7485 | 107.9871 | 0
12817 | 906.6952 | 9.4281 | 15.3459 | 98.1773 | 48.62 | 9.4995 | 43.7887 | 1.7205 |  | 10.4912 | 43.9089 | 6.7017 |  | 49.5325 | 124.0571 | 12.166 | 36.5348 | 3.2503 | 120 | 27.7948 | 17.6182 | 111.5398 | 0
12818 | 903.5731 | 9.6241 | 15.0423 | 97.8336 | 50.9256 | 8.5503 | 36.4371 | 2.0053 |  | 10.444 | 43.4754 | 6.7081 |  | 50.3615 | 120.2244 | 14.0452 | 36.428 | 3.0999 | 119 | 38.2512 | 17.4183 | 111.8796 | 0
12819 | 886.8758 | 9.756 | 14.9623 | 96.9477 | 49.2588 | 10.4495 | 38.9673 | 1.8791 |  | 9.6937 | 42.4992 | 6.3524 |  | 51.4492 | 118.8886 | 12.588 | 36.1724 | 2.9204 | 114 | 27.8126 | 17.4166 | 110.524 | 0
12820 | 888.0761 | 5.6509 | 14.2103 | 95.1694 | 52.1572 | 7.6008 | 34.6957 | 2.1467 |  | 8.1642 | 41.0234 | 4.4341 |  | 48.8401 | 111.0728 | 11.8487 | 35.6137 | 2.5148 | 113 | 29.0325 | 17.3705 | 108.6752 | 0
12821 | 894.7862 | 2.5267 | 14.2059 | 94.3959 | 50.989 | 8.5497 | 37.9677 | 1.6352 |  | 7.5822 | 42.6387 | 3.5723 |  | 46.8816 | 113.0142 | 8.5521 | 35.3629 | 2.3239 | 104 | 32.6525 | 17.3664 | 107.3165 | 0.17077
12822 | 913.5363 | 2.0947 | 14.1768 | 94.0634 | 51.1068 | 8.55 | 37.0381 | 1.325 |  | 7.6085 | 47.2039 | 3.6215 |  | 39.1952 | 109.7387 | 8.0698 | 35.6066 | 2.3374 | 111 | 29.3683 | 17.3458 | 109.1807 | 0.22787
12823 | 917.7588 | 2.0007 | 14.2938 | 94.1005 | 52.6038 | 8.55 | 41.3779 | 1.2969 |  | 7.7816 | 45.3863 | 3.8957 |  | 36.9616 | 112.1125 | 7.5312 | 35.5882 | 2.4537 | 106 | 29.7335 | 17.3731 | 107.8895 | 0.29037
12824 | 927.0562 | 1.8894 | 14.2366 | 95.7833 | 52.7426 | 9.4997 | 44.0039 | 1.202 |  | 8.6442 | 40.7827 | 4.4155 |  | 39.5576 | 112.4395 | 8.7144 | 35.2466 | 2.4832 | 109 | 26.4726 | 17.6449 | 113.3315 | 0.33627
12825 | 932.2522 | 1.8396 | 14.331 | 95.2107 | 47.0834 | 10.4497 | 40.6253 | 1.4374 |  | 10.0771 | 40.1755 | 3.9691 |  | 40.821 | 114.4884 | 7.7363 | 35.1045 | 2.4622 | 115 | 16.9954 | 17.4942 | 111.8819 | 0.33037
12826 | 937.1259 | 2.0318 | 14.1928 | 94.8403 | 35.1241 | 9.5003 | 66.8348 | 1.2235 |  | 13.7281 | 42.2884 | 3.9615 |  | 41.0249 | 122.5825 | 7.9977 | 35.3668 | 2.6015 | 117 | 10.0938 | 17.2604 | 114.8968 | 0.33382
12827 | 963.9922 | 1.9682 | 14.5591 | 95.2863 | 32.7828 | 10.4497 | 68.8175 | 1.056 |  | 14.6819 | 53.1824 | 4.1035 |  | 41.4943 | 125.4577 | 8.336 | 35.1179 | 2.5924 | 121 | 13.9137 | 17.4314 | 114.7211 | 0.25721
12828 | 959.7442 | 2.1033 | 14.9402 | 94.9352 | 43.0373 | 9.5003 | 73.9925 | 1.9836 |  | 14.3163 | 69.7267 | 4.0838 |  | 43.2279 | 118.99 | 7.5871 | 35.1069 | 2.5445 | 125 | 13.0446 | 17.1651 | 113.2107 | 0.27338
12829 | 957.3518 | 2.479 | 15.5932 | 97.1086 | 49.0257 | 8.5503 | 67.0977 | 2.4476 |  | 14.3992 | 68.7558 | 4.2349 |  | 44.2796 | 126.4419 | 8.3879 | 34.7997 | 2.5384 | 129 | 12.2351 | 17.3864 | 114.6947 | 0.29819
12830 | 959.4061 | 4.2674 | 16.1352 | 97.9837 | 52.4812 | 6.6505 | 50.2253 | 2.4231 |  | 14.6344 | 63.5837 | 4.2771 |  | 44.2487 | 129.4569 | 8.3943 | 34.5001 | 2.5391 | 128 | 10.2707 | 17.7959 | 111.1904 | 0.29049
12831 | 940.5921 | 8.1755 | 15.9248 | 98.1168 | 55.9602 | 5.7003 | 38.3217 | 2.4111 |  | 13.4529 | 63.1064 | 4.1582 |  | 48.2545 | 130.8209 | 7.6611 | 34.9118 | 2.5344 | 126 | 14.2642 | 17.2087 | 112.7377 | 0.30919
12832 | 932.6037 | 8.9771 | 15.2245 | 97.0912 | 54.8258 | 6.6497 | 39.3228 | 2.3362 |  | 9.7563 | 62.0626 | 3.9221 |  | 49.3312 | 129.1905 | 8.0384 | 34.4341 | 2.5076 | 127 | 10.6369 | 17.0124 | 110.1861 | 0.26276
12833 | 950.4565 | 4.7698 | 15.7141 | 98.9529 | 53.6584 | 7.5997 | 41.0946 | 2.6287 |  | 7.9995 | 60.2474 | 3.8235 |  | 48.557 | 136.5252 | 8.3403 | 35.3323 | 2.5573 | 122 | 14.8743 | 16.9568 | 110.6917 | 0.28972
12834 | 955.5658 | 2.4747 | 15.7684 | 98.257 | 55.6088 | 6.6503 | 35.7481 | 1.8706 |  | 7.7942 | 54.9355 | 3.6757 |  | 45.0668 | 139.8806 | 8.6552 | 35.5363 | 2.5618 | 116 | 22.7519 | 17.0014 | 111.8133 | 0.27139
12835 | 942.7137 | 2.1406 | 15.6866 | 95.4862 | 51.6022 | 9.4992 | 41.5144 | 1.1728 |  | 7.7883 | 50.9932 | 3.6736 |  | 44.9404 | 130.2426 | 7.61 | 35.0344 | 2.5667 | 122 | 26.8207 | 17.0046 | 111.041 | 0.18871
12836 | 928.1097 | 2.1547 | 15.7875 | 95.2586 | 40.8911 | 8.5503 | 44.552 | 1.0352 |  | 8.3467 | 46.2118 | 3.6457 |  | 44.1998 | 126.7651 | 8.9444 | 34.8673 | 2.5637 | 119 | 28.4492 | 17.0044 | 110.8841 | 0.012941
12837 | 907.2109 | 5.5391 | 15.7239 | 95.1914 | 34.1461 | 6.6505 | 40.1693 | 1.0202 |  | 8.4117 | 43.6911 | 4.6944 |  | 45.7345 | 126.3217 | 7.9573 | 35.2053 | 2.5822 | 122 | 29.117 | 17.0165 | 109.3941 | 0.002427
12838 | 895.4245 | 9.4197 | 15.2948 | 100.4878 | 31.34 | 8.5495 | 42.0787 | 1.2187 |  | 8.33 | 42.8139 | 8.0277 |  | 54.4814 | 125.8593 | 8.3381 | 35.0911 | 2.6043 | 116 | 32.5727 | 17.3559 | 108.0441 | 0
12839 | 286.9881 | 3.815 | 4.5298 | 29.7741 | 16.6017 | 0.002376 | 14.255 | 0.44871 |  | 2.8157 | 15.1071 | 3.1386 |  | 17.3864 | 43.6488 | 2.6048 | 10.3053 | 0.89551 | 118 | 3.2214 | 2.3797 | 9.6951 | 0
12840 | 876.629 | 9.6355 | 15.2371 | 105.5677 | 29.6663 | 9.4995 | 43.0721 | 2.087 |  | 12.2199 | 44.3087 | 11.2527 |  | 57.8497 | 125.5322 | 11.9407 | 35.7923 | 2.589 | 119 | 33.8323 | 19.9773 | 109.4907 | 0
12841 | 880.989 | 6.019 | 17.7753 | 105.495 | 35.1853 | 8.5503 | 41.6972 | 2.2164 |  | 12.7996 | 43.7885 | 11.0573 |  | 52.9887 | 121.6471 | 12.55 | 35.4526 | 2.5455 | 112 | 31.5775 | 19.9842 | 112.072 | 0
12842 | 886.5195 | 2.9671 | 29.7074 | 106.3799 | 35.0725 | 7.6003 | 39.8301 | 1.8194 |  | 12.9317 | 43.396 | 12.0627 |  | 50.6726 | 120.37 | 12.9323 | 35.7618 | 2.5433 | 116 | 31.2571 | 19.9711 | 115.7438 | 0
12843 | 879.3603 | 2.2395 | 33.8523 | 104.1571 | 35.776 | 8.5497 | 42.9256 | 1.6334 |  | 11.7554 | 42.2643 | 13.6742 |  | 49.9946 | 115.5962 | 11.9779 | 35.6244 | 2.5014 | 111 | 31.0019 | 20.0121 | 114.1166 | 0
12844 | 881.8051 | 2.2205 | 35.2571 | 102.4519 | 45.7602 | 8.55 | 39.1948 | 1.4062 |  | 11.1915 | 41.0141 | 9.1271 |  | 48.2738 | 111.658 | 11.3297 | 35.3521 | 2.3877 | 111 | 31.4243 | 19.9948 | 117.9648 | 0
12845 | 893.061 | 2.3518 | 31.0294 | 103.4757 | 47.1709 | 10.4495 | 46.1616 | 1.2801 |  | 13.5739 | 41.3089 | 5.4804 |  | 55.2483 | 114.7027 | 9.6413 | 35.1991 | 2.334 | 125 | 32.2304 | 19.5729 | 133.9712 | 0.042601
12846 | 936.6924 | 4.0078 | 32.0787 | 102.5 | 45.6447 | 12.3495 | 65.7395 | 1.9028 |  | 17.7729 | 46.174 | 11.3714 |  | 80.1273 | 133.1113 | 10.046 | 35.141 | 2.3621 | 148 | 43.5586 | 17.3449 | 158.6889 | 0.081813
12847 | 966.3124 | 16.5994 | 61.7188 | 102.2492 | 48.0182 | 14.2495 | 93.4243 | 3.2057 |  | 17.0435 | 64.8118 | 18.6295 |  | 96.1961 | 171.159 | 22.5036 | 37.0416 | 6.1471 | 218 | -19.5863 | 20.5263 | 193.8037 | 0.07915
12848 | 1040.2635 | 20.2621 | 86.6705 | 119.7603 | 53.0407 | 17.0992 | 105.575 | 4.5029 |  | 17.1965 | 80.5252 | 15.3314 |  | 111.6225 | 222.6031 | 29.1791 | 41.8236 | 10.9502 | 242 | 42.2722 | 21.7413 | 216.7847 | 0.096517
12849 | 1117.2675 | 13.4987 | 96.3968 | 128.8069 | 56.2512 | 17.1 | 119.5659 | 4.2297 |  | 18.0388 | 89.8956 | 12.0132 |  | 123.8302 | 253.7921 | 29.1994 | 46.616 | 13.3524 | 256 | 39.3266 | 20.9103 | 243.033 | 0.11321
12850 | 1145.9846 | 8.7162 | 96.4336 | 134.4198 | 51.7368 | 17.1 | 128.3567 | 3.9198 |  | 17.3181 | 89.595 | 12.0572 |  | 132.4346 | 258.7562 | 31.032 | 48.057 | 12.0293 | 270 | 37.6833 | 23.7386 | 245.1493 | 0.16778
12851 | 1153.7152 | 9.4255 | 97.6653 | 133.0697 | 45.8135 | 18.0497 | 123.435 | 4.5021 |  | 16.2883 | 93.1562 | 11.5079 |  | 135.3608 | 259.7339 | 31.099 | 49.8403 | 7.2707 | 237 | 31.8182 | 23.2926 | 247.1443 | 0.12922
12852 | 1136.5389 | 8.3832 | 99.1591 | 134.5222 | 44.432 | 18.05 | 124.9572 | 4.5509 |  | 15.8172 | 95.6658 | 12.2152 |  | 132.8702 | 259.9183 | 30.3588 | 47.8942 | 5.1728 | 244 | 25.6617 | 22.3116 | 246.8045 | 0.13
12853 | 1165.1796 | 5.1703 | 102.0012 | 138.3873 | 46.7814 | 18.05 | 132.4395 | 4.3664 |  | 16.1691 | 96.8647 | 13.2597 |  | 137.5349 | 255.9008 | 31.6052 | 47.6343 | 4.5715 | 218 | 29.1429 | 22.841 | 249.7177 | 0.18784
12854 | 1162.7761 | 4.7082 | 103.4365 | 138.1681 | 49.6225 | 18.05 | 133.275 | 4.6581 |  | 16.3973 | 98.7445 | 14.4076 |  | 139.3153 | 257.9836 | 32.0374 | 48.1772 | 5.1341 | 205 | 33.0969 | 23.3638 | 246.928 | 0.13131
12855 | 1162.2177 | 7.1414 | 95.3908 | 136.9409 | 51.6762 | 18.9997 | 129.0776 | 4.3676 |  | 15.7668 | 97.1078 | 16.5029 |  | 120.3411 | 235.9253 | 33.5539 | 47.8227 | 5.496 | 211 | 35.3294 | 21.1989 | 241.8008 | 0.11626
12856 | 1138.8918 | 5.1759 | 64.6372 | 127.1217 | 54.7766 | 17.1005 | 131.4532 | 3.8727 |  | 15.7143 | 91.9129 | 17.2499 |  | 97.6061 | 209.6949 | 27.7743 | 45.5105 | 5.32 | 182 | 25.871 | 18.6964 | 213.4353 | 0.13466
12857 | 1084.6676 | 3.5754 | 52.1001 | 113.4561 | 56.5385 | 11.4016 | 122.6696 | 2.8031 |  | 14.0868 | 83.5747 | 12.8885 |  | 85.5851 | 177.5091 | 14.5783 | 42.4975 | 4.6919 | 153 | 19.183 | 17.4219 | 171.6511 | 0.071681
12858 | 1055.7449 | 12.3971 | 51.5541 | 105.1274 | 51.4843 | 13.2995 | 104.077 | 1.7236 |  | 10.0462 | 73.2383 | 9.6025 |  | 77.755 | 165.7457 | 9.6151 | 41.195 | 3.8527 | 151 | 26.2533 | 17.5558 | 147.6855 | 0.050358
12859 | 1002.4688 | 13.7458 | 46.5263 | 99.9303 | 53.4282 | 9.5011 | 64.7438 | 1.1796 |  | 8.3784 | 67.5234 | 6.8081 |  | 65.8963 | 151.7227 | 9.1987 | 38.1872 | 3.062 | 132 | 28.0615 | 17.3702 | 118.6977 | 0.1131
12860 | 977.635 | 7.7942 | 27.9158 | 97.1742 | 56.6215 | 7.6005 | 42.0295 | 1.0602 |  | 8.7145 | 63.6385 | 5.6814 |  | 53.5313 | 142.5095 | 9.0086 | 36.2763 | 2.7993 | 133 | 29.5775 | 17.3467 | 115.364 | 0.03049
12861 | 945.7524 | 4.2214 | 18.0635 | 95.9634 | 56.2212 | 7.6 | 41.403 | 1.0542 |  | 8.743 | 51.3545 | 5.906 |  | 44.8286 | 134.6108 | 8.3552 | 35.3394 | 2.7998 | 134 | 30.1702 | 17.3331 | 120.4529 | 0.0025373
12862 | 926.9625 | 3.1774 | 16.6009 | 97.9116 | 51.6911 | 8.5497 | 44.4347 | 1.5038 |  | 10.3138 | 45.5422 | 7.4523 |  | 51.1824 | 128.4581 | 9.0699 | 35.5854 | 2.8963 | 129 | 35.6795 | 17.6733 | 120.5486 | 0
12863 | 292.4653 | 1.077 | 4.8549 | 28.0809 | 24.1306 | 0.002376 | 14.4951 | 0.5802 |  | 3.7014 | 16.0104 | 2.6838 |  | 16.1918 | 43.4411 | 2.7499 | 10.3323 | 0.9957 | 118 | 3.4744 | 2.3788 | 12.7965 | 0
12864 | 881.2676 | 2.3815 | 17.6102 | 99.5349 | 44.2361 | 8.55 | 41.1961 | 1.4519 |  | 12.8908 | 45.0657 | 8.4535 |  | 52.6182 | 123.4693 | 8.5901 | 35.0856 | 2.9641 | 116 | 33.8113 | 20.2933 | 120.3037 | 0
12865 | 877.8821 | 2.3191 | 17.7753 | 103.2072 | 31.1563 | 9.4997 | 38.4348 | 1.4573 |  | 12.9514 | 44.4615 | 8.3313 |  | 56.2755 | 121.3205 | 8.9875 | 34.9612 | 2.8322 | 116 | 32.267 | 20.3107 | 120.4659 | 0
12866 | 872.1792 | 2.406 | 17.9734 | 104.6045 | 32.9943 | 8.5503 | 38.5501 | 2.19 |  | 12.8666 | 43.7716 | 10.1253 |  | 61.1606 | 123.1772 | 9.4972 | 35.3932 | 2.762 | 111 | 31.6104 | 20.333 | 121.2698 | 0
12867 | 872.211 | 2.4577 | 17.9866 | 103.7169 | 42.3174 | 7.6003 | 40.8982 | 2.1987 |  | 12.1532 | 42.4629 | 14.7477 |  | 61.143 | 127.7519 | 9.2174 | 35.5258 | 2.7688 | 113 | -12.6576 | 20.3335 | 124.9725 | 0
12868 | 879.5041 | 2.2764 | 23.2664 | 101.8265 | 44.7678 | 9.4995 | 34.5171 | 1.5419 |  | 11.4583 | 40.5884 | 13.0956 |  | 58.5138 | 121.6408 | 8.732 | 35.166 | 2.6144 | 107 | 31.7482 | 20.3338 | 124.9679 | 0
12869 | 879.1217 | 2.2977 | 37.846 | 100.6324 | 48.74 | 8.5503 | 46.6393 | 1.2968 |  | 13.6777 | 40.8129 | 8.1713 |  | 60.935 | 114.7848 | 9.0413 | 34.8778 | 2.5636 | 105 | 28.783 | 19.8973 | 134.6999 | 0.025733
12870 | 905.66 | 3.5103 | 53.6777 | 99.4669 | 46.0131 | 11.3992 | 67.337 | 1.6797 |  | 16.1087 | 45.3535 | 13.1895 |  | 82.677 | 127.8106 | 10.8173 | 34.7621 | 2.5689 | 145 | 31.8593 | 17.6556 | 164.1134 | 0.060976
12871 | 955.9052 | 10.0209 | 76.1686 | 101.6274 | 42.9847 | 15.1989 | 87.2343 | 3.082 |  | 17.3573 | 62.108 | 21.8215 |  | 99.4297 | 164.5983 | 23.3898 | 36.9863 | 2.9354 | 200 | 46.1022 | 20.8839 | 194.1665 | 0.11073
12872 | 1032.0035 | 10.5377 | 93.6292 | 122.5568 | 44.555 | 16.1497 | 105.045 | 5.1361 |  | 18.3472 | 78.2517 | 17.4877 |  | 115.8787 | 213.4753 | 29.5657 | 41.2808 | 3.5697 | 223 | 45.9995 | 25.42 | 231.6708 | 0.11927
12873 | 1090.564 | 9.666 | 100.7496 | 133.5587 | 40.4699 | 18.9992 | 111.945 | 5.3261 |  | 16.8824 | 86.5401 | 13.955 |  | 126.2317 | 241.4013 | 31.7642 | 45.7032 | 3.8046 | 259 | 38.3334 | 27.1307 | 247.2822 | 0.1467
12874 | 1139.1176 | 11.1647 | 102.8425 | 135.917 | 38.8557 | 19.9497 | 115.436 | 4.9856 |  | 17.7283 | 88.4454 | 14.2202 |  | 132.86 | 258.4258 | 32.2798 | 49.2439 | 3.9092 | 256 | 35.4877 | 28.7938 | 245.974 | 0.24068
12875 | 1176.4953 | 7.5645 | 102.0993 | 136.1354 | 39.148 | 19.95 | 116.581 | 4.7205 |  | 17.9638 | 89.3694 | 14.2857 |  | 135.175 | 257.8018 | 33.6457 | 52.7947 | 4.1544 | 241 | 35.1291 | 28.0185 | 253.9963 | 0.23776
12876 | 1165.0286 | 4.999 | 102.5448 | 139.2573 | 36.1798 | 19.95 | 115.0933 | 5.0211 |  | 16.0682 | 93.8948 | 14.7033 |  | 135.2313 | 261.3758 | 34.5626 | 52.5442 | 4.1532 | 254 | 38.7753 | 27.5047 | 251.3381 | 0.16497
12877 | 1151.9575 | 7.9848 | 105.4093 | 144.7102 | 36.788 | 17.1008 | 117.4192 | 5.2653 |  | 15.3836 | 96.7125 | 15.0976 |  | 134.9347 | 254.6055 | 33.1691 | 54.2504 | 4.3393 | 220 | 35.5562 | 27.6281 | 254.7352 | 0.18101
12878 | 1170.7338 | 12.4539 | 107.0892 | 140.1005 | 37.5323 | 18.0497 | 116.4269 | 4.9067 |  | 15.2511 | 95.6929 | 14.2708 |  | 133.5798 | 263.0487 | 32.1649 | 53.5001 | 4.451 | 222 | 31.1456 | 26.4791 | 241.3217 | 0.17821
12879 | 1173.8773 | 8.6601 | 103.9923 | 131.0731 | 38.9892 | 18.9997 | 121.0715 | 5.1361 |  | 14.8602 | 95.6854 | 13.2538 |  | 125.9995 | 255.3665 | 30.7586 | 51.9255 | 4.376 | 216 | 27.2523 | 24.9355 | 234.8975 | 0.11446
12880 | 1139.9122 | 4.6813 | 73.9283 | 113.5533 | 45.8306 | 14.2513 | 111.8448 | 5.605 |  | 15.1809 | 97.3888 | 11.6036 |  | 110.5832 | 220.9434 | 25.7722 | 43.0483 | 4.3576 | 198 | 21.4451 | 23.3117 | 210.598 | 0.19165
12881 | 1096.4049 | 4.1821 | 60.1449 | 104.4684 | 49.9846 | 11.4008 | 108.072 | 5.4967 |  | 14.1445 | 88.3469 | 11.2642 |  | 99.0618 | 181.4952 | 15.4315 | 34.4743 | 4.4478 | 155 | 18.0536 | 22.0468 | 164.7379 | 0.10992
12882 | 1045.1755 | 3.569 | 57.4042 | 98.5425 | 39.3501 | 9.5005 | 90.1803 | 5.4524 |  | 9.1813 | 74.0991 | 10.6166 |  | 77.4634 | 166.8764 | 11.2621 | 30.5556 | 4.2842 | 147 | 24.776 | 22.6224 | 147.2986 | 0.085055
12883 | 1008.8242 | 3.3157 | 47.0537 | 95.9965 | 30.6192 | 8.5503 | 57.2592 | 4.7196 |  | 7.0019 | 66.6977 | 8.1617 |  | 62.0594 | 156.3512 | 9.8061 | 27.5864 | 3.3827 | 136 | 27.4534 | 21.9827 | 121.7065 | 0.054099
12884 | 985.0247 | 3.2824 | 28.4197 | 95.2065 | 31.6298 | 9.4997 | 41.1253 | 3.2328 |  | 7.3028 | 59.9234 | 7.3433 |  | 56.3984 | 147.7 | 9.8898 | 26.7746 | 2.9647 | 137 | 29.6974 | 21.0312 | 112.014 | 0.022707
12885 | 959.8545 | 4.0939 | 19.1199 | 95.4004 | 30.9158 | 8.5503 | 40.4674 | 3.2081 |  | 7.412 | 48.1001 | 7.0992 |  | 53.7732 | 130.0686 | 9.6866 | 26.2584 | 2.8668 | 137 | 29.5893 | 20.8918 | 109.5325 | 0.0025925
12886 | 942.2035 | 3.6832 | 18.1142 | 99.702 | 36.0423 | 8.55 | 43.5418 | 2.8488 |  | 7.7145 | 43.8156 | 7.539 |  | 60.1924 | 122.2677 | 9.7831 | 26.0583 | 2.778 | 129 | 33.9786 | 21.3452 | 109.2561 | 0
12887 | 294.7968 | 1.1255 | 5.3203 | 28.5741 | 20.2456 | 0.002376 | 14.1908 | 0.8407 |  | 2.6028 | 15.4547 | 2.5653 |  | 18.5373 | 41.6603 | 2.8633 | 7.4762 | 0.92732 | 118 | 3.3563 | 2.7967 | 11.3198 | 0
12888 | 891.326 | 2.4986 | 18.8501 | 103.0357 | 47.6061 | 9.5 | 41.9093 | 1.8559 |  | 12.1924 | 44.2864 | 9.9711 |  | 63.2227 | 129.2577 | 10.163 | 26.503 | 2.9427 | 114 | 33.4421 | 23.829 | 113.2125 | 0
12889 | 893.0471 | 2.4664 | 18.5747 | 102.7717 | 47.5997 | 9.5 | 40.6304 | 2.4232 |  | 12.9416 | 44.2385 | 9.7429 |  | 64.8569 | 126.2053 | 10.5409 | 26.7655 | 2.9689 | 109 | 31.2428 | 23.8162 | 117.4897 | 0
12890 | 903.3966 | 2.4785 | 18.5842 | 102.5962 | 45.1857 | 9.5 | 40.2541 | 2.2074 |  | 13.0482 | 44.4166 | 12.0894 |  | 68.8579 | 121.3731 | 10.7076 | 26.4731 | 2.8504 | 108 | 33.0615 | 23.8513 | 114.7867 | 0
12891 | 897.1126 | 2.4592 | 17.6634 | 101.4693 | 43.788 | 9.5 | 41.2383 | 2.4198 |  | 11.4706 | 43.0971 | 17.2202 |  | 68.7927 | 113.5671 | 9.3104 | 25.8103 | 2.7154 | 109 | 35.8669 | 23.8538 | 119.9063 | 0
12892 | 899.4295 | 2.211 | 16.4949 | 98.9668 | 41.9812 | 9.5 | 33.4462 | 1.7909 |  | 11.0566 | 41.505 | 15.6008 |  | 67.5252 | 109.7357 | 10.1707 | 25.4347 | 2.6024 | 107 | 35.805 | 23.7987 | 120.9163 | 0
12893 | 903.7613 | 2.3164 | 30.9263 | 97.9919 | 39.5446 | 10.4497 | 44.9773 | 1.3451 |  | 13.9001 | 41.7703 | 10.2607 |  | 66.6663 | 110.0526 | 9.304 | 25.5423 | 2.5503 | 100 | 34.1829 | 22.3177 | 132.3759 | 0.021783
12894 | 943.3439 | 3.5753 | 48.8084 | 98.6851 | 38.5672 | 10.45 | 60.564 | 1.877 |  | 18.7685 | 45.5408 | 13.9347 |  | 78.153 | 127.481 | 12.8458 | 25.6365 | 2.5859 | 151 | 33.9622 | 0 | 158.2971 | 0.059818
12895 | 988.4695 | 7.6221 | 70.3 | 97.8326 | 30.9979 | 17.0982 | 87.6584 | 3.0551 |  | 21.4163 | 65.2282 | 20.8194 |  | 92.5072 | 158.8227 | 24.182 | 27.9894 | 2.9312 | 187 | 40.2865 | 23.1411 | 187.4039 | 0.11082
12896 | 1040.7935 | 10.0348 | 81.9961 | 114.3087 | 27.3689 | 22.7984 | 108.2887 | 3.7904 |  | 19.4842 | 83.7148 | 16.1557 |  | 111.5272 | 209.6935 | 31.3782 | 31.2003 | 3.5713 | 213 | 40.464 | 25.0069 | 219.201 | 0.19148
12897 | 1104.8789 | 9.2039 | 89.0725 | 125.1125 | 35.3643 | 20.9005 | 112.203 | 4.3075 |  | 15.7805 | 93.0706 | 12.5606 |  | 128.8947 | 238.7176 | 32.2001 | 44.95 | 3.7944 | 260 | 32.3761 | 25.2906 | 247.1573 | 0.24193
12898 | 1130.398 | 8.9586 | 92.6499 | 131.7272 | 47.2038 | 19.9503 | 119.3179 | 4.1163 |  | 15.0411 | 94.5559 | 12.5866 |  | 136.7321 | 253.7515 | 34.8991 | 51.7985 | 3.8929 | 249 | 32.5887 | 25.5733 | 246.3984 | 0.32031
12899 | 1159.038 | 10.6166 | 96.3725 | 131.7075 | 56.5448 | 16.1511 | 119.8868 | 4.5893 |  | 15.5789 | 93.0151 | 12.6729 |  | 139.3736 | 253.1718 | 34.1551 | 52.2954 | 3.9011 | 234 | 28.7789 | 26.3189 | 255.6285 | 0.25491
12900 | 1199.2838 | 8.8275 | 99.9452 | 131.4284 | 47.2739 | 19.9489 | 126.7853 | 4.9422 |  | 15.6089 | 94.6457 | 13.6555 |  | 138.3997 | 253.6306 | 33.9214 | 51.9051 | 3.8786 | 241 | 22.2905 | 24.8205 | 241.7392 | 0.27303
12901 | 1197.8983 | 5.6463 | 101.5541 | 132.7571 | 46.0434 | 16.1511 | 121.6673 | 4.9543 |  | 15.4179 | 96.2765 | 16.9699 |  | 140.9618 | 248.6003 | 33.3694 | 53.1374 | 3.8654 | 226 | 22.9091 | 24.0051 | 248.799 | 0.28302
12902 | 1184.6453 | 4.7314 | 98.2788 | 136.3336 | 43.4803 | 18.0495 | 119.2577 | 4.6765 |  | 15.3514 | 96.8193 | 18.2128 |  | 140.4336 | 243.8515 | 33.2867 | 53.8896 | 3.9878 | 215 | 25.4073 | 25.193 | 234.5708 | 0.26239
12903 | 1165.1553 | 4.8692 | 96.1781 | 129.9747 | 42.7953 | 19.9495 | 119.1214 | 4.1498 |  | 15.401 | 98.3061 | 17.3815 |  | 128.1684 | 231.152 | 33.1752 | 52.9599 | 4.0477 | 211 | 19.955 | 24.1341 | 222.5365 | 0.26405
12904 | 1137.4242 | 4.7607 | 73.7547 | 117.3539 | 47.6699 | 15.2013 | 112.1533 | 3.4031 |  | 15.4086 | 98.0659 | 16.5534 |  | 114.5364 | 210.1274 | 26.3958 | 51.2922 | 4.0539 | 180 | 13.2891 | 22.617 | 186.1957 | 0.094146
12905 | 1099.9549 | 4.4511 | 63.2518 | 108.9378 | 47.5518 | 10.4542 | 113.7061 | 3.067 |  | 14.2519 | 88.4088 | 14.9829 |  | 102.8103 | 179.087 | 14.5997 | 47.7612 | 4.0194 | 167 | 13.097 | 22.1591 | 145.377 | 0.17742
12906 | 1048.8622 | 3.2702 | 60.6333 | 99.3843 | 45.8091 | 11.3968 | 95.2477 | 1.7901 |  | 9.5633 | 70.1328 | 12.1991 |  | 83.5133 | 166.7868 | 8.9509 | 39.4529 | 3.7472 | 162 | 20.5608 | 21.4313 | 132.5211 | 0.2047
12907 | 1017.9577 | 6.7291 | 49.9023 | 94.4591 | 39.4787 | 10.4503 | 64.0613 | 1.7131 |  | 7.5133 | 62.5422 | 9.3588 |  | 63.5065 | 157.3234 | 9.3478 | 29.9836 | 3.0654 | 144 | 24.2297 | 21.0335 | 110.7622 | 0.2486
12908 | 978.8365 | 5.1586 | 31.4723 | 93.0599 | 26.9589 | 11.3997 | 48.9767 | 2.1126 |  | 8.9279 | 57.8893 | 8.1589 |  | 52.1661 | 134.1012 | 9.0702 | 27.2515 | 2.7814 | 133 | 25.8628 | 20.9399 | 106.182 | 0.15721
12909 | 957.8979 | 3.2343 | 22.6501 | 93.172 | 31.5898 | 6.6513 | 60.6129 | 1.8298 |  | 9.7311 | 47.8212 | 8.109 |  | 46.4119 | 120.5455 | 8.6097 | 26.4312 | 2.9196 | 128 | 27.7808 | 20.9619 | 111.004 | 0.027636
12910 | 932.5742 | 7.5402 | 21.5398 | 97.1295 | 36.8881 | 10.4489 | 61.2917 | 1.6164 |  | 9.1791 | 41.21 | 8.7995 |  | 44.5922 | 114.2422 | 9.2279 | 25.5128 | 2.9529 | 121 | 28.5124 | 21.3624 | 106.5994 | 0
12911 | 292.2775 | 3.5098 | 6.3469 | 28.121 | 21.4411 | 0.002903 | 18.735 | 0.53778 |  | 2.9604 | 14.0427 | 3.0096 |  | 13.1861 | 38.3498 | 2.7835 | 7.3254 | 0.99407 | 116 | 2.7216 | 2.8513 | 9.3547 | 0
12912 | 903.6239 | 6.2161 | 20.7264 | 101.1885 | 42.575 | 10.4503 | 44.1941 | 2.1463 |  | 12.3108 | 40.9445 | 10.8676 |  | 43.5319 | 118.7069 | 9.0701 | 26.0895 | 2.6318 | 116 | 36.0325 | 0 | 104.8705 | 0
12913 | 882.7034 | 3.062 | 20.121 | 101.6845 | 42.5418 | 8.5505 | 40.6717 | 1.6952 |  | 12.9478 | 41.0782 | 10.7926 |  | 44.9842 | 119.8994 | 10.1729 | 26.0658 | 2.7505 | 114 | 33.9307 | 21.0586 | 107.8517 | 0
12914 | 885.6974 | 2.859 | 20.1553 | 101.5039 | 38.9565 | 8.55 | 43.1254 | 2.5055 |  | 13.0773 | 41.1465 | 13.0358 |  | 49.198 | 116.6799 | 9.238 | 26.1177 | 2.7063 | 109 | 33.8887 | 20.9796 | 108.8469 | 0
12915 | 880.5187 | 2.7176 | 20.1714 | 100.5068 | 36.1928 | 8.55 | 38.3599 | 2.216 |  | 12.5412 | 40.4754 | 19.071 |  | 50.5895 | 115.2369 | 10.042 | 25.9108 | 2.577 | 116 | 32.7145 | 20.9657 | 113.6076 | 0
12916 | 879.8725 | 2.7031 | 19.7171 | 99.1009 | 34.9661 | 9.4997 | 42.4533 | 2.0511 |  | 11.6448 | 39.0103 | 17.4356 |  | 48.1509 | 108.4134 | 8.7654 | 25.6142 | 2.4223 | 108 | 32.6796 | 20.9784 | 114.9085 | 0
12917 | 913.7103 | 5.7573 | 33.8115 | 97.3473 | 33.2888 | 11.3995 | 45.3114 | 1.7553 |  | 13.7398 | 39.0099 | 11.204 |  | 51.0032 | 111.5879 | 9.5781 | 25.563 | 2.3333 | 111 | 28.1293 | 20.9608 | 122.4264 | 0.026453
12918 | 971.1371 | 12.019 | 51.841 | 95.9532 | 31.6276 | 12.3497 | 61.6762 | 2.1986 |  | 16.1248 | 45.4181 | 14.4891 |  | 76.7602 | 122.7542 | 11.6507 | 25.3875 | 2.3554 | 151 | 29.4987 | 20.9253 | 145.5397 | 0.057466
12919 | 1007.398 | 19.9854 | 74.7886 | 97.5205 | 28.8542 | 15.1992 | 82.211 | 0 |  | 15.3182 | 68.4587 | 22.9039 |  | 99.6731 | 159.1869 | 24.3542 | 28.0453 | 4.7251 | 185 | 46.5589 | 25.0514 | 172.4356 | 0.12864
12920 | 1048.5324 | 14.2004 | 92.4449 | 119.2039 | 30.5665 | 14.2503 | 89.0167 | 4.5471 |  | 14.5825 | 85.324 | 19.0523 |  | 119.2771 | 202.9847 | 30.0956 | 32.7543 | 8.2718 | 210 | 51.4845 | 26.9843 | 212.6107 | 0.20067
12921 | 1108.3716 | 6.9933 | 96.4295 | 130.9109 | 26.311 | 18.0489 | 98.2811 | 5.8154 |  | 14.3766 | 92.6837 | 16.6554 |  | 132.32 | 243.9803 | 31.7498 | 36.8795 | 5.7703 | 241 | 48.6935 | 27.1931 | 234.083 | 0.17062
12922 | 1149.839 | 4.6867 | 95.9435 | 139.0367 | 24.5997 | 18.9997 | 110.2325 | 5.4457 |  | 14.5001 | 95.8789 | 17.5892 |  | 137.5205 | 255.2546 | 31.6811 | 42.6832 | 3.9107 | 269 | 46.7061 | 26.5991 | 242.2298 | 0.11824
12923 | 1163.2894 | 8.5133 | 94.5249 | 137.8929 | 26.017 | 18.0503 | 118.7253 | 5.0801 |  | 14.6398 | 96.819 | 16.9227 |  | 139.4506 | 251.2838 | 32.3293 | 49.2822 | 3.6994 | 243 | 46.1164 | 26.0058 | 237.9172 | 0.20855
12924 | 1171.0075 | 11.2631 | 96.2658 | 132.6662 | 25.7334 | 18.9997 | 123.3227 | 5.205 |  | 14.7221 | 97.8609 | 14.0904 |  | 137.3514 | 249.8235 | 33.7188 | 49.7082 | 3.4957 | 269 | 44.4332 | 25.7933 | 221.2003 | 0.23867
12925 | 1166.9758 | 10.1368 | 94.3031 | 133.8219 | 27.5605 | 17.1005 | 117.972 | 4.996 |  | 14.5232 | 98.7738 | 13.2919 |  | 137.1672 | 245.6588 | 32.4777 | 50.3112 | 3.4305 | 229 | 46.2867 | 25.5139 | 222.1461 | 0.28817
12926 | 1172.9838 | 10.277 | 90.4622 | 135.403 | 19.6365 | 24.6979 | 108.054 | 4.3471 |  | 14.2712 | 98.3586 | 17.1386 |  | 137.3813 | 242.9801 | 32.9629 | 50.6744 | 3.763 | 201 | 44.6229 | 25.6925 | 209.8998 | 0.27176
12927 | 1151.7999 | 6.3188 | 87.0027 | 131.7116 | 17.7222 | 26.5995 | 103.2035 | 2.7375 |  | 14.2329 | 96.4106 | 15.864 |  | 117.2625 | 229.0209 | 30.9041 | 50.9773 | 3.7037 | 201 | 34.4919 | 24.379 | 205.2785 | 0.24049
12928 | 1100.7513 | 3.8221 | 62.4274 | 114.1863 | 32.1297 | 12.354 | 89.3137 | 1.5855 |  | 14.0677 | 91.933 | 11.7151 |  | 97.4193 | 202.2143 | 25.4875 | 49.0457 | 3.6647 | 182 | 26.5938 | 23.9412 | 174.1839 | 0.23301
12929 | 1081.0885 | 3.8246 | 50.7322 | 106.6598 | 34.5323 | 9.5008 | 74.8054 | 1.2017 |  | 12.7339 | 83.9241 | 10.8319 |  | 80.5521 | 170.5609 | 14.9923 | 45.9716 | 3.8304 | 160 | 25.7286 | 22.6073 | 141.4202 | 0.15811
12930 | 1057.3609 | 3.2106 | 48.8361 | 102.9115 | 32.2034 | 10.4497 | 63.965 | 1.1315 |  | 9.1375 | 71.2504 | 10.0406 |  | 56.0311 | 157.8407 | 10.2394 | 42.9101 | 3.6259 | 152 | 27.035 | 22.7297 | 127.0485 | 0.15093
12931 | 1034.222 | 2.4546 | 44.4176 | 98.478 | 31.7868 | 10.45 | 46.5576 | 2.0691 |  | 7.8055 | 65.9568 | 7.5821 |  | 45.1499 | 144.7333 | 9.7417 | 41.0463 | 3.0654 | 131 | 27.5444 | 23.033 | 108.2347 | 0.071839
12932 | 987.9217 | 2.4091 | 28.9935 | 94.3182 | 31.7205 | 10.45 | 44.3532 | 1.7545 |  | 7.7512 | 59.7502 | 6.7678 |  | 43.4347 | 131.5655 | 10.0955 | 37.8243 | 2.7537 | 125 | 28.6488 | 22.8469 | 103.4771 | 0.038133
12933 | 958.6138 | 3.518 | 20.5861 | 92.9782 | 34.1751 | 8.5505 | 38.8893 | 1.3776 |  | 7.8197 | 47.4929 | 6.5142 |  | 41.0729 | 124.2719 | 9.8181 | 36.2144 | 2.5019 | 125 | 28.9928 | 22.7378 | 99.8915 | 0.0012135
12934 | 933.5916 | 3.5607 | 19.7311 | 93.3152 | 34.2217 | 8.55 | 42.1101 | 1.8642 |  | 8.6851 | 43.1323 | 7.8898 |  | 42.0048 | 121.9277 | 10.1664 | 36.2382 | 2.4433 | 108 | 30.3513 | 23.1037 | 103.5087 | 0
12935 | 291.7757 | 1.1636 | 5.7951 | 26.3645 | 17.3092 | 0.002376 | 14.4559 | 0.70431 |  | 3.0128 | 15.2228 | 2.8378 |  | 12.5709 | 41.4997 | 2.9956 | 10.4275 | 0.83223 | 106 | 2.9034 | 3.0568 | 10.6966 | 0
12936 | 874.6889 | 2.8889 | 19.9246 | 95.9198 | 31.0106 | 9.4995 | 42.882 | 1.9976 |  | 12.6775 | 42.9446 | 9.2151 |  | 41.0275 | 115.5584 | 10.2694 | 33.0571 | 2.5369 | 105 | 37.2268 | 22.9189 | 103.4092 | 0
12937 | 870.131 | 2.346 | 20.2404 | 95.7276 | 30.9616 | 9.5 | 38.4149 | 2.4532 |  | 13.3979 | 43.1165 | 9.0008 |  | 39.0535 | 113.6919 | 10.6412 | 32.2283 | 2.5438 | 103 | 35.5821 | 22.7624 | 106.5338 | 0
12938 | 870.9295 | 2.4068 | 20.0311 | 96.0928 | 31.1726 | 9.5 | 42.034 | 2.0955 |  | 13.3396 | 43.3577 | 9.8675 |  | 39.7355 | 115.0885 | 9.7754 | 32.5115 | 2.5543 | 100 | -7.4098 | 22.7535 | 105.7505 | 0
12939 | 869.5001 | 2.3201 | 19.8915 | 95.1779 | 31.1183 | 9.5 | 39.6608 | 2.3014 |  | 12.7341 | 42.3072 | 12.1022 |  | 40.0586 | 110.0645 | 10.4503 | 32.0945 | 2.553 | 100 | 30.5363 | 22.7406 | 107.8842 | 0
12940 | 875.644 | 2.3221 | 19.5427 | 92.9346 | 30.9707 | 9.5 | 39.9601 | 1.9278 |  | 11.7825 | 40.2365 | 10.2516 |  | 39.1224 | 105.4618 | 9.4541 | 32.1917 | 2.3886 | 102 | 30.8538 | 22.7623 | 106.4193 | 0
12941 | 892.93 | 2.035 | 18.9973 | 91.8771 | 28.6417 | 11.3995 | 34.1327 | 1.5531 |  | 13.5352 | 39.4449 | 7.1782 |  | 44.66 | 104.8712 | 10.2204 | 33.4649 | 2.3279 | 96 | 28.7319 | 22.7251 | 109.8592 | 0.033227
12942 | 896.5825 | 2.0052 | 19.0446 | 92.4554 | 32.0678 | 8.5508 | 38.4736 | 1.5672 |  | 13.831 | 40.7575 | 6.1976 |  | 65.2707 | 112.3658 | 9.6587 | 33.7376 | 2.3571 | 120 | 27.4122 | 22.6975 | 106.3367 | 0.1945
12943 | 907.3763 | 1.9039 | 29.673 | 94.1632 | 28.6847 | 13.2987 | 40.3913 | 1.3917 |  | 9.7503 | 43.6676 | 6.4421 |  | 73.4406 | 125.932 | 10.7267 | 33.8018 | 2.4759 | 138 | 32.8508 | 22.749 | 109.8362 | 0.25773
12944 | 925.9611 | 1.853 | 37.4756 | 108.571 | 31.864 | 12.3503 | 44.5802 | 1.2794 |  | 8.4244 | 44.9345 | 6.2983 |  | 76.6312 | 135.9059 | 9.7287 | 33.5098 | 2.4796 | 133 | 31.429 | 22.7291 | 107.8868 | 0.31867
12945 | 948.6789 | 1.9172 | 38.8764 | 114.2901 | 35.4037 | 13.2997 | 40.7506 | 1.177 |  | 8.9222 | 45.9226 | 6.0385 |  | 77.8153 | 140.2332 | 10.2643 | 33.2998 | 2.4557 | 133 | 27.8222 | 22.7398 | 106.2623 | 0.30263
12946 | 959.5955 | 2.068 | 39.0314 | 114.5864 | 51.1681 | 11.4005 | 43.0562 | 1.1001 |  | 8.9289 | 46.1374 | 6.0482 |  | 80.5323 | 151.4014 | 9.4975 | 33.4681 | 2.4876 | 132 | 23.2619 | 22.8233 | 110.5386 | 0.26038
12947 | 960.7469 | 2.5264 | 39.9426 | 114.7481 | 56.2367 | 11.4 | 45.4591 | 1.1742 |  | 9.2488 | 46.178 | 6.0319 |  | 83.9672 | 149.3583 | 10.1654 | 33.5372 | 2.5242 | 136 | 17.5485 | 22.7203 | 107.7193 | 0.26185
12948 | 953.5918 | 2.784 | 40.0577 | 115.2969 | 47.4837 | 14.2492 | 38.6268 | 1.1972 |  | 9.6806 | 46.4642 | 6.1456 |  | 85.422 | 153.2711 | 9.3629 | 33.5518 | 2.5405 | 139 | 23.494 | 22.73 | 112.1105 | 0.27903
12949 | 939.261 | 4.3861 | 39.7118 | 114.5407 | 50.732 | 11.4008 | 41.644 | 1.5883 |  | 10.0167 | 51.1093 | 5.9298 |  | 85.2914 | 153.9927 | 10.6908 | 33.7016 | 2.7154 | 139 | 29.6492 | 22.8318 | 111.6779 | 0.30127
12950 | 944.1378 | 5.3947 | 39.1973 | 115.1662 | 38.7041 | 10.4503 | 38.9363 | 1.3861 |  | 10.7587 | 54.7916 | 5.8278 |  | 86.3533 | 154.4468 | 9.3532 | 34.4381 | 2.7437 | 143 | 33.2682 | 22.7227 | 109.7091 | 0.2988
12951 | 959.9581 | 5.6137 | 38.3724 | 111.0536 | 29.7668 | 14.2489 | 40.6242 | 1.1364 |  | 10.2155 | 50.5896 | 6.0386 |  | 75.4527 | 151.0525 | 9.4065 | 35.8923 | 2.7002 | 137 | 38.1878 | 22.7197 | 110.0848 | 0.26878
12952 | 942.3546 | 9.9503 | 37.7013 | 97.0628 | 41.5775 | 8.5516 | 38.6717 | 1.3154 |  | 10.1744 | 46.6364 | 5.771 |  | 59.7748 | 141.4739 | 9.2581 | 35.2224 | 2.6795 | 149 | 28.3864 | 22.7381 | 109.3142 | 0.26371
12953 | 922.605 | 11.1329 | 33.777 | 92.994 | 46.3 | 6.6505 | 39.8167 | 2.1976 |  | 11.0904 | 44.1594 | 5.881 |  | 53.8029 | 124.5544 | 8.7057 | 34.7194 | 2.6943 | 145 | 25.2174 | 22.374 | 104.5399 | 0.28647
12954 | 913.8313 | 10.5829 | 23.1635 | 93.5336 | 44.4162 | 8.5495 | 38.878 | 2.2451 |  | 11.7346 | 42.5551 | 6.0788 |  | 53.3374 | 125.8247 | 9.4932 | 34.8757 | 2.5688 | 143 | 26.6969 | 22.6747 | 105.4066 | 0.26607
12955 | 928.7827 | 6.3319 | 19.3838 | 94.4653 | 41.1402 | 10.4495 | 36.4395 | 2.3768 |  | 10.1333 | 46.3153 | 6.0644 |  | 50.4137 | 126.2732 | 10.1987 | 33.7903 | 2.4019 | 115 | 27.2933 | 23.0415 | 106.0075 | 0.033759
12956 | 915.3844 | 7.2053 | 19.0056 | 94.0572 | 40.2449 | 10.45 | 41.9828 | 1.7507 |  | 9.4617 | 47.9063 | 5.9991 |  | 48.8707 | 129.9679 | 9.4282 | 31.6261 | 2.3416 | 109 | 28.4891 | 22.7834 | 103.4671 | 0.034234
12957 | 920.133 | 9.3808 | 19.2137 | 93.1967 | 38.4945 | 10.45 | 40.9948 | 1.42 |  | 9.6753 | 43.1099 | 6.9864 |  | 46.0155 | 121.2572 | 9.3898 | 31.2309 | 2.3849 | 107 | 28.2881 | 22.7068 | 99.4049 | 0.0062433
12958 | 907.0556 | 9.715 | 19.7232 | 94.1603 | 37.8019 | 8.5505 | 44.0454 | 2.4533 |  | 11.4204 | 40.9547 | 8.455 |  | 45.3416 | 119.9409 | 9.6894 | 31.2837 | 2.492 | 111 | 28.6418 | 23.1216 | 105.6833 | 0
12959 | 286.112 | 3.4919 | 5.8763 | 27.1432 | 18.5725 | 0.002376 | 14.952 | 0.99958 |  | 4.1045 | 14.5279 | 2.9659 |  | 13.564 | 42.1055 | 2.8624 | 9.1015 | 0.86237 | 99 | 2.7255 | 3.1119 | 9.7831 | 0
12960 | 876.0978 | 4.4172 | 20.1881 | 96.1824 | 36.6633 | 8.5497 | 41.8815 | 1.6176 |  | 10.7621 | 41.1212 | 8.9485 |  | 46.2238 | 131.5585 | 9.9716 | 31.8284 | 2.5473 | 103 | 31.3683 | 25.7118 | 108.9648 | 0
12961 | 881.8149 | 3.2535 | 20.1607 | 95.6285 | 35.0796 | 9.4997 | 39.7351 | 2.4319 |  | 10.7334 | 40.6138 | 8.7433 |  | 46.1394 | 128.1354 | 10.1664 | 31.662 | 2.5486 | 99 | 29.7954 | 25.7473 | 108.8933 | 0
12962 | 869.849 | 2.672 | 19.8286 | 96.0911 | 34.7005 | 9.5 | 42.7885 | 2.1019 |  | 10.7668 | 40.6001 | 8.5807 |  | 45.8787 | 126.0143 | 9.5933 | 31.6194 | 2.5532 | 102 | 29.562 | 25.7318 | 106.1738 | 0
12963 | 859.0428 | 2.4048 | 19.8275 | 95.5301 | 35.9249 | 8.5503 | 40.1122 | 1.6737 |  | 10.2006 | 40.4344 | 8.6178 |  | 45.0104 | 126.5076 | 10.2787 | 31.4401 | 2.5461 | 95 | 29.4048 | 25.7695 | 105.4325 | 0
12964 | 859.8579 | 2.2839 | 19.6304 | 93.2757 | 34.6763 | 9.4997 | 38.4197 | 1.4947 |  | 8.4917 | 38.9701 | 7.0432 |  | 45.0549 | 122.4543 | 9.1145 | 31.6765 | 2.4497 | 98 | 28.4011 | 24.3309 | 100.1468 | 0
12965 | 849.9216 | 2.0244 | 19.4061 | 92.3508 | 36.5543 | 7.6005 | 38.6712 | 2.0527 |  | 7.8713 | 39.1954 | 5.9078 |  | 45.0838 | 120.1547 | 9.7445 | 32.6975 | 2.3401 | 93 | 27.4275 | 22.8881 | 99.0625 | 0.16546
12966 | 853.2233 | 1.8864 | 19.1995 | 92.382 | 34.6721 | 9.4995 | 36.0673 | 1.6877 |  | 7.8696 | 42.0227 | 5.818 |  | 44.8921 | 111.6823 | 8.9972 | 31.5155 | 2.3592 | 98 | 26.3127 | 22.6953 | 97.1228 | 0.2253
12967 | 852.0632 | 2.457 | 19.349 | 94.9273 | 34.3331 | 9.5 | 42.4519 | 1.5615 |  | 7.8054 | 46.2235 | 5.7726 |  | 44.3418 | 107.702 | 9.8659 | 30.6075 | 2.4546 | 97 | 27.1817 | 22.727 | 101.0321 | 0.28997
12968 | 869.3767 | 2.1902 | 19.3553 | 108.5353 | 35.645 | 8.5503 | 38.9682 | 1.4982 |  | 7.887 | 42.9577 | 5.7021 |  | 45.0664 | 109.1418 | 9.0815 | 30.6002 | 2.4905 | 96 | 23.8199 | 23.1411 | 100.791 | 0.23694
12969 | 873.2548 | 1.8584 | 28.9075 | 113.6322 | 35.4743 | 9.4997 | 42.9439 | 1.3694 |  | 8.1295 | 39.9615 | 5.921 |  | 46.0149 | 114.4193 | 9.3712 | 30.6447 | 2.4827 | 98 | 17.7307 | 23.3309 | 102.7016 | 0.33199
12970 | 872.3366 | 2.3121 | 36.337 | 114.6011 | 37.1141 | 8.5503 | 42.7831 | 1.3089 |  | 8.0938 | 40.7802 | 6.0334 |  | 48.9123 | 114.2869 | 9.5611 | 30.961 | 2.471 | 99 | 8.6162 | 22.8223 | 99.9182 | 0.33426
12971 | 861.5755 | 2.5569 | 37.6309 | 113.4214 | 37.6377 | 9.4997 | 40.8964 | 1.2086 |  | 8.0385 | 44.4337 | 6.1078 |  | 49.2742 | 108.373 | 9.2602 | 30.9474 | 2.4811 | 103 | 7.8402 | 22.8973 | 102.5223 | 0.25577
12972 | 860.4963 | 2.4219 | 37.6298 | 113.5237 | 41.3535 | 9.5 | 43.402 | 1.1126 |  | 8.359 | 50.0294 | 6.1935 |  | 48.594 | 109.1492 | 9.1165 | 30.9927 | 2.5273 | 108 | 7.3472 | 23.0712 | 99.4561 | 0.25871
12973 | 862.6723 | 2.4021 | 33.9202 | 114.3778 | 45.4103 | 8.5503 | 40.5053 | 1.0719 |  | 9.0108 | 51.872 | 6.0814 |  | 48.4054 | 116.8976 | 10.5194 | 30.9024 | 2.5708 | 109 | 17.177 | 22.7772 | 100.9704 | 0.22853
12974 | 874.8085 | 2.3632 | 23.1041 | 114.6548 | 45.9701 | 8.55 | 38.7776 | 1.3465 |  | 8.4383 | 51.5894 | 5.9798 |  | 48.3574 | 125.0801 | 9.2133 | 30.9086 | 2.552 | 126 | 23.6711 | 22.6986 | 99.8194 | 0.28143
12975 | 890.0192 | 2.5229 | 19.5715 | 109.2098 | 47.4241 | 8.55 | 40.8286 | 1.2155 |  | 8.1686 | 52.2126 | 6.0046 |  | 50.0766 | 122.8345 | 9.5936 | 30.882 | 2.5615 | 120 | 11.2007 | 22.7239 | 101.2771 | 0.30624
12976 | 885.456 | 7.2583 | 19.596 | 96.8878 | 51.0271 | 8.55 | 36.6781 | 1.0529 |  | 8.6182 | 52.1683 | 6.1865 |  | 48.7634 | 119.0213 | 8.8593 | 30.2203 | 2.5583 | 128 | 10.2801 | 22.7171 | 96.6979 | 0.20047
12977 | 862.5467 | 9.726 | 19.3093 | 91.1928 | 52.1269 | 8.55 | 39.0685 | 1.0429 |  | 8.2061 | 50.7068 | 6.4004 |  | 48.3046 | 117.8929 | 10.1153 | 30.4052 | 2.5168 | 122 | 12.0218 | 22.377 | 92.2709 | 0.29304
12978 | 884.099 | 9.9747 | 19.3446 | 92.2201 | 46.4976 | 12.3524 | 45.3813 | 1.0595 |  | 8.2268 | 50.9717 | 6.4045 |  | 49.5133 | 115.638 | 9.2319 | 30.8887 | 2.562 | 126 | 20.0761 | 22.9549 | 92.5615 | 0.16272
12979 | 895.4338 | 7.1076 | 19.4884 | 91.5323 | 47.7482 | 8.5476 | 39.3482 | 1.0308 |  | 8.3279 | 48.836 | 6.3473 |  | 48.2473 | 115.0279 | 9.2418 | 31.1212 | 2.5818 | 128 | 23.8215 | 22.7491 | 95.4728 | 0.032288
12980 | 899.2116 | 3.5293 | 19.3817 | 91.2186 | 45.2865 | 9.4997 | 42.0446 | 1.8103 |  | 8.1605 | 43.8441 | 6.4278 |  | 46.8349 | 112.5492 | 9.5103 | 31.3652 | 2.5654 | 132 | 26.9176 | 22.7072 | 97.9794 | 0.013875
12981 | 903.4016 | 5.0565 | 19.3133 | 91.098 | 44.7495 | 8.5503 | 39.1255 | 1.8811 |  | 8.1926 | 41.2843 | 6.4292 |  | 46.8779 | 113.2066 | 8.9583 | 30.9888 | 2.4042 | 126 | 28.9218 | 22.7111 | 94.674 | 0.0011583
12982 | 907.8332 | 11.7814 | 19.4214 | 92.0226 | 41.4087 | 9.4997 | 41.5171 | 1.6074 |  | 9.1914 | 39.6449 | 7.0919 |  | 46.8908 | 112.0577 | 9.6394 | 31.3286 | 2.3972 | 118 | 35.574 | 23.0828 | 96.5709 | 0
12983 | 286.5664 | 5.2104 | 5.6689 | 26.096 | 20.3809 | 0.00264 | 14.0324 | 0.51882 |  | 3.2036 | 13.6424 | 2.4396 |  | 13.743 | 37.8224 | 2.8689 | 9.0444 | 0.82089 | 102 | 3.4565 | 3.0731 | 7.1008 | 0
12984 | 900.5351 | 15.2874 | 19.9198 | 94.7772 | 34.568 | 11.3995 | 42.2321 | 2.0531 |  | 11.3628 | 39.9913 | 8.9985 |  | 48.0972 | 115.9552 | 12.7122 | 36.8709 | 2.5641 | 101 | 37.5542 | 22.9875 | 98.417 | 0
12985 | 881.7893 | 11.4005 | 20.0641 | 94.9937 | 32.7137 | 11.4 | 45.0166 | 2.4339 |  | 11.372 | 40.1466 | 8.8585 |  | 47.6433 | 118.673 | 14.7638 | 37.9732 | 2.5446 | 103 | 35.9695 | 22.7262 | 100.9138 | 0
12986 | 878.9773 | 10.0555 | 19.6776 | 94.9845 | 35.3349 | 8.5508 | 39.4407 | 2.0637 |  | 11.4086 | 40.1236 | 8.7581 |  | 47.7824 | 119.7826 | 13.7612 | 37.5434 | 2.5606 | 103 | 35.9575 | 22.7561 | 100.084 | 0
12987 | 879.3833 | 9.7534 | 19.9088 | 94.451 | 34.4039 | 8.55 | 40.2351 | 2.2196 |  | 11.3716 | 40.0909 | 8.8088 |  | 47.9971 | 120.9741 | 14.6746 | 36.6663 | 2.5579 | 95 | 36.8653 | 22.7437 | 101.4754 | 0
12988 | 886.7664 | 10.0091 | 19.7156 | 93.0105 | 32.4447 | 9.4997 | 34.491 | 2.0027 |  | 9.8218 | 38.8903 | 7.908 |  | 47.4538 | 113.6965 | 12.5982 | 36.1955 | 2.5088 | 99 | 35.901 | 22.7648 | 99.7442 | 0
12989 | 892.2606 | 7.0059 | 19.4176 | 91.3423 | 29.9211 | 10.4497 | 40.9032 | 1.8077 |  | 8.7381 | 38.2395 | 6.3369 |  | 46.7435 | 110.8125 | 10.1755 | 35.4854 | 2.3849 | 96 | 35.6381 | 22.7547 | 100.7549 | 0.022315
12990 | 922.3555 | 3.0795 | 19.2078 | 91.1218 | 29.6938 | 9.5003 | 39.7522 | 2.2008 |  | 8.5999 | 40.072 | 5.9423 |  | 45.9597 | 107.7646 | 8.7423 | 35.09 | 2.3617 | 103 | 30.71 | 22.6965 | 99.4366 | 0.06364
12991 | 942.6725 | 1.8655 | 19.1496 | 93.7029 | 27.985 | 10.4497 | 43.2026 | 1.6759 |  | 8.5629 | 44.2799 | 6.1015 |  | 44.1933 | 107.2507 | 10.9347 | 34.8884 | 2.4418 | 98 | 28.7955 | 22.7112 | 101.2969 | 0.13458
12992 | 952.4982 | 2.3211 | 19.2013 | 107.6263 | 28.3179 | 9.5003 | 38.5799 | 1.4169 |  | 8.4622 | 41.0714 | 6.1671 |  | 44.0975 | 107.3699 | 9.4908 | 35.2249 | 2.4957 | 100 | 23.3062 | 22.7192 | 101.7456 | 0.084001
12993 | 941.2396 | 2.2487 | 18.9185 | 112.5831 | 27.7666 | 10.4497 | 42.9767 | 1.4436 |  | 9.8341 | 38.5208 | 5.9163 |  | 47.5788 | 108.8714 | 8.3981 | 35.3729 | 2.4858 | 100 | 25.8567 | 22.7397 | 101.0473 | 0.28529
12994 | 927.9338 | 2.2767 | 19.0509 | 116.9439 | 28.0061 | 10.45 | 49.5151 | 2.2864 |  | 13.6323 | 39.7696 | 6.1372 |  | 51.172 | 109.315 | 10.3454 | 35.3106 | 2.4542 | 101 | 33.5357 | 22.7029 | 104.9665 | 0.11699
12995 | 928.3556 | 2.4285 | 19.074 | 116.3065 | 28.2081 | 9.5003 | 41.8136 | 2.5703 |  | 15.3442 | 46.7912 | 6.1882 |  | 50.2315 | 110.6984 | 9.2178 | 35.0992 | 2.3604 | 100 | 25.3297 | 22.6924 | 105.0238 | 0.1641
12996 | 937.8641 | 5.8511 | 19.2302 | 113.8372 | 27.6473 | 9.5 | 42.3075 | 2.6298 |  | 15.0782 | 56.7404 | 6.0191 |  | 48.0708 | 107.343 | 8.6668 | 35.2228 | 2.3262 | 109 | 21.0028 | 22.738 | 101.2628 | 0.15398
12997 | 958.992 | 8.324 | 18.9335 | 114.5831 | 26.0223 | 10.4497 | 37.3623 | 2.4295 |  | 14.8816 | 61.4946 | 5.8446 |  | 45.4271 | 113.6879 | 10.251 | 35.467 | 2.4892 | 112 | 21.7113 | 22.7443 | 100.2583 | 0.21953
12998 | 951.6406 | 4.7655 | 19.3126 | 113.717 | 27.0224 | 9.5003 | 39.5411 | 1.8914 |  | 14.7567 | 62.6036 | 5.8622 |  | 45.4322 | 125.5368 | 9.1515 | 35.6653 | 2.8636 | 107 | 16.5161 | 22.7592 | 99.8577 | 0.27243
12999 | 938.0013 | 3.0487 | 19.325 | 108.5936 | 27.8848 | 9.5 | 42.9523 | 2.1624 |  | 13.2941 | 62.9708 | 5.8835 |  | 52.5875 | 132.2733 | 9.4385 | 35.6494 | 3.0689 | 114 | -6.5186 | 22.7671 | 103.5923 | 0.24575
13000 | 927.3971 | 2.6337 | 18.8366 | 94.8713 | 27.7792 | 9.5 | 36.8027 | 1.8825 |  | 9.7333 | 62.1223 | 5.7774 |  | 48.7628 | 132.4681 | 9.9144 | 35.2361 | 3.0241 | 111 | 18.7526 | 22.7479 | 105.3997 | 0.17361
13001 | 952.0304 | 6.5301 | 19.0817 | 92.4327 | 27.8758 | 9.5026 | 41.1139 | 1.4624 |  | 8.4827 | 60.24 | 5.8035 |  | 47.4093 | 139.4043 | 8.931 | 35.8051 | 2.7017 | 112 | 23.7849 | 22.6754 | 102.2859 | 0.14223
13002 | 949.3954 | 6.5648 | 19.2363 | 93.5545 | 28.468 | 9.4974 | 41.7501 | 2.1229 |  | 8.5822 | 54.306 | 5.9249 |  | 45.7394 | 143.5921 | 9.835 | 35.437 | 2.4255 | 104 | 26.5539 | 22.7689 | 98.2466 | 0.07707
13003 | 958.6694 | 4.1685 | 19.0748 | 91.8684 | 27.9257 | 9.5 | 43.742 | 1.8249 |  | 8.5976 | 47.4816 | 5.901 |  | 44.4659 | 133.8354 | 10.1271 | 34.8058 | 2.3809 | 104 | 31.851 | 22.7554 | 101.9319 | 0.032836
13004 | 960.3353 | 3.6071 | 18.8801 | 90.7558 | 26.1552 | 10.4497 | 43.3425 | 2.2907 |  | 8.6118 | 42.3241 | 6.2168 |  | 43.1101 | 119.2055 | 8.8189 | 34.4936 | 2.3513 | 106 | 34.3552 | 22.752 | 102.3987 | 0.018394
13005 | 955.7242 | 4.2571 | 19.4626 | 90.9558 | 22.6434 | 10.45 | 41.0777 | 1.7751 |  | 8.6027 | 40.4752 | 7.2384 |  | 43.3447 | 117.131 | 8.8065 | 34.3901 | 2.3439 | 100 | 34.2545 | 22.7247 | 104.0416 | 0.0012135
13006 | 950.8206 | 4.1939 | 19.6864 | 92.2096 | 20.226 | 9.5003 | 38.8229 | 2.3216 |  | 9.995 | 40.7445 | 10.4273 |  | 43.5341 | 118.1497 | 10.0395 | 34.8436 | 2.4618 | 107 | 34.3475 | 23.1051 | 107.4328 | 0
13007 | 293.9393 | 1.3832 | 5.6406 | 25.6602 | 11.6818 | 0.00264 | 11.9234 | 0.93037 |  | 3.4857 | 14.1247 | 3.8093 |  | 12.5649 | 39.5105 | 2.9759 | 9.89 | 0.83566 | 109 | 3.3003 | 2.9414 | 10.5957 | 0
13008 | 899.2786 | 2.6932 | 20.0199 | 93.523 | 17.7964 | 10.45 | 44.2539 | 2.7108 |  | 13.367 | 40.8394 | 11.0998 |  | 43.5571 | 115.5055 | 10.8541 | 35.1641 | 2.5673 | 111 | 35.8949 | 22.861 | 105.1407 | 0
13009 | 892.3455 | 2.4081 | 19.7053 | 93.6043 | 17.7199 | 9.5003 | 37.4867 | 2.2233 |  | 14.0259 | 40.7636 | 9.9013 |  | 43.4032 | 116.2386 | 9.7659 | 35.2567 | 2.5653 | 103 | 33.8276 | 22.7367 | 109.6791 | 0
13010 | 879.9223 | 2.3405 | 20.0614 | 94.0214 | 15.7075 | 11.3995 | 40.4316 | 2.5349 |  | 14.1287 | 40.7346 | 9.6842 |  | 43.9152 | 114.7029 | 8.9329 | 35.3982 | 2.569 | 106 | 34.3727 | 22.7811 | 106.2494 | 0
13011 | 887.571 | 2.3903 | 20.1098 | 93.7789 | 17.9122 | 9.5005 | 39.3801 | 2.8362 |  | 13.8791 | 40.3341 | 9.3011 |  | 43.6204 | 114.2726 | 11.6247 | 35.2752 | 2.5775 | 94 | 34.5962 | 22.7728 | 109.643 | 0
13012 | 882.7503 | 2.92 | 19.8132 | 91.6712 | 15.4783 | 11.3995 | 42.343 | 2.1226 |  | 12.8402 | 38.7849 | 7.8633 |  | 42.346 | 108.4473 | 9.7475 | 34.8259 | 2.472 | 97 | 33.8153 | 22.7816 | 123.8333 | 0
13013 | 904.8718 | 3.623 | 32.2139 | 90.5693 | 16.4526 | 10.4503 | 37.1402 | 2.298 |  | 14.5803 | 39.2382 | 7.656 |  | 48.7417 | 111.9322 | 8.3636 | 36.2106 | 2.379 | 93 | 34.2211 | 22.7762 | 130.7618 | 0.021227
13014 | 958.5722 | 4.185 | 56.2188 | 93.3119 | 16.2971 | 10.45 | 52.8327 | 1.7808 |  | 17.633 | 45.2522 | 13.2641 |  | 74.5458 | 120.3796 | 12.6805 | 35.9625 | 2.3718 | 133 | 34.561 | 22.7525 | 156.607 | 0.041331
13015 | 314.4669 | 7.4876 | 78.3465 | 98.4834 | 12.5297 | 17.0982 | 73.2355 | 2.8208 |  | 16.5458 | 64.6563 | 20.3135 |  | 92.9559 | 151.7069 | 22.7963 | 37.2883 | 4.7668 | 155 | 35.2025 | 25.427 | 185.6333 | 0.14622
13016 | 0 | 11.1616 | 91.2718 | 116.7999 | 14.2071 | 19.9492 | 90.2566 | 4.11 |  | 15.8312 | 78.5179 | 16.081 |  | 104.6851 | 178.9625 | 29.0728 | 39.7933 | 7.9245 | 166 | 34.0516 | 26.181 | 212.372 | 0.14114
13017 | 0 | 11.2298 | 93.8829 | 126.8289 | 17.9297 | 19.0003 | 102.7921 | 4.4853 |  | 15.4347 | 88.1237 | 13.5022 |  | 115.6045 | 198.7018 | 31.0663 | 42.9807 | 5.5829 | 164 | 30.4847 | 25.73 | 229.915 | 0.10928
13018 | 0 | 8.7244 | 96.9883 | 134.1818 | 18.5834 | 19 | 105.3611 | 5.6078 |  | 15.4981 | 93.5745 | 13.8966 |  | 121.6043 | 214.8081 | 29.6876 | 46.8021 | 3.8442 | 168 | 27.1336 | 26.316 | 230.1467 | 0.11498
13019 | 0 | 12.4052 | 98.7126 | 133.2888 | 22.3889 | 17.1053 | 107.2725 | 5.9929 |  | 15.3733 | 94.5476 | 13.9001 |  | 123.3709 | 216.5888 | 31.109 | 47.175 | 3.8003 | 147 | 22.478 | 25.7114 | 234.7119 | 0.1253
13020 | 0 | 12.1763 | 101.1117 | 134.1481 | 24.3496 | 18.045 | 114.7823 | 5.4004 |  | 15.338 | 94.034 | 12.9628 |  | 119.5528 | 223.843 | 29.6227 | 45.5733 | 3.8919 | 158 | 18.7371 | 27.4024 | 225.9862 | 0.12961
13021 | 0 | 7.0942 | 101.784 | 136.3446 | 29.7537 | 17.1003 | 114.8948 | 5.3134 |  | 15.1488 | 93.1948 | 12.4726 |  | 121.3652 | 228.7702 | 30.7131 | 46.6093 | 4.013 | 162 | 18.5561 | 28.2365 | 218.3947 | 0.18727
13022 | 0 | 5.0015 | 101.0346 | 137.4363 | 34.1662 | 17.1 | 118.4132 | 5.0176 |  | 14.9019 | 93.1277 | 13.3794 |  | 123.6964 | 227.8272 | 30.0968 | 47.2066 | 4.0426 | 163 | 21.0654 | 28.7553 | 214.9296 | 0.20639
13023 | 0 | 4.6596 | 96.8068 | 130.5092 | 34.1736 | 20.8989 | 104.5149 | 4.5465 |  | 14.9391 | 93.5221 | 12.7884 |  | 110.9601 | 220.4228 | 28.7873 | 47.2604 | 3.8298 | 148 | 20.565 | 28.0109 | 215.0957 | 0.13374
13024 | 0 | 4.7118 | 68.8797 | 111.9882 | 44.966 | 11.4026 | 88.466 | 3.9046 |  | 14.7596 | 90.5855 | 11.8006 |  | 92.4876 | 193.6279 | 25.7919 | 45.1774 | 3.7295 | 145 | 14.7341 | 26.6139 | 189.7211 | 0.22125
13025 | 0 | 4.4253 | 56.3486 | 103.9951 | 42.7156 | 13.2995 | 78.5489 | 2.3039 |  | 13.546 | 82.8904 | 12.1617 |  | 78.2916 | 172.0487 | 13.79 | 42.8568 | 3.7718 | 155 | 13.5809 | 25.8427 | 152.6145 | 0.19954
13026 | 0 | 3.9479 | 54.3254 | 100.7586 | 45.0136 | 9.5011 | 68.2987 | 1.3149 |  | 10.1833 | 69.2835 | 11.2412 |  | 56.6893 | 155.929 | 9.9049 | 40.8857 | 3.5211 | 151 | 21.6917 | 25.8824 | 130.203 | 0.085385
13027 | 0 | 5.1361 | 49.7392 | 98.4999 | 43.9893 | 8.5503 | 48.7974 | 1.8335 |  | 8.7853 | 62.3966 | 8.6827 |  | 45.938 | 146.8591 | 10.4254 | 38.7631 | 2.932 | 132 | 25.017 | 26.1412 | 111.1519 | 0.078227
13028 | 0 | 8.995 | 35.3039 | 95.6548 | 40.5616 | 10.4495 | 45.4264 | 1.7554 |  | 8.7524 | 56.9255 | 7.5214 |  | 44.0093 | 141.896 | 8.9304 | 36.0825 | 2.6413 | 127 | 26.9254 | 25.8069 | 102.5691 | 0.016453
13029 | 0 | 11.0401 | 27.0216 | 93.2124 | 37.7427 | 11.3997 | 38.6103 | 1.4276 |  | 8.7173 | 45.4852 | 7.4769 |  | 42.7592 | 130.8436 | 10.4393 | 35.0594 | 2.4326 | 119 | 30.9602 | 25.7106 | 97.6331 | 0.001048
13030 | 0 | 6.2151 | 26.1376 | 93.1445 | 38.9104 | 8.5508 | 42.1452 | 2.2416 |  | 9.1074 | 39.8219 | 8.2111 |  | 40.845 | 126.2221 | 9.1375 | 35.3282 | 2.3936 | 114 | 41.4752 | 26.0693 | 101.9852 | 0
13031 | 0 | 1.2099 | 7.5102 | 25.7719 | 18.996 | 0.002376 | 14.7504 | 0.90181 |  | 3.0981 | 13.8118 | 2.8275 |  | 11.5695 | 43.2141 | 2.2941 | 9.9734 | 0.81906 | 105 | 4.0186 | 3.4118 | 10.7187 | 0
13032 |  | 2.6036 | 26.5794 | 96.8634 | 34.6408 | 9.5 | 42.6335 | 2.4257 |  | 13.59 | 40.4841 | 10.3042 |  | 39.6339 | 126.2619 | 10.2919 | 35.5372 | 2.572 | 108 | 41.9401 | 25.8345 | 106.5216 | 0
13033 |  | 2.3798 | 26.3403 | 96.4027 | 33.8221 | 8.5503 | 39.6727 | 2.2356 |  | 14.2855 | 40.1194 | 10.142 |  | 40.1039 | 127.6242 | 9.2675 | 35.3424 | 2.5617 | 107 | 40.981 | 25.7561 | 108.9475 | 0
13034 |  | 2.2611 | 24.9136 | 95.9022 | 29.3927 | 12.3489 | 42.1899 | 2.4505 |  | 14.3561 | 39.7192 | 10.1953 |  | 40.404 | 120.2182 | 9.9858 | 35.4358 | 2.5735 | 104 | 40.3253 | 25.7544 | 106.5302 | 0
13035 |  | 2.2599 | 21.3147 | 94.4053 | 30.7078 | 10.4505 | 40.985 | 2.1078 |  | 13.2535 | 38.5949 | 9.2349 |  | 39.5239 | 115.614 | 9.1758 | 35.3867 | 2.5371 | 102 | 40.6715 | 25.7392 | 105.0716 | 0
13036 |  | 2.1941 | 19.7352 | 93.0205 | 32.4296 | 8.5505 | 35.1107 | 2.1901 |  | 12.6855 | 37.1905 | 7.7706 |  | 37.5993 | 109.9413 | 10.3081 | 34.8916 | 2.4041 | 104 | 40.4805 | 25.7298 | 113.413 | 0
13037 |  | 5.0683 | 35.1137 | 93.5854 | 34.4822 | 6.6505 | 39.4224 | 1.9708 |  | 14.9834 | 37.2275 | 8.0759 |  | 43.2647 | 110.3434 | 8.9926 | 34.5786 | 2.3378 | 98 | 38.8422 | 25.7075 | 125.2481 | 0.048798
13038 |  | 7.6577 | 57.5782 | 94.9935 | 30.1264 | 10.4489 | 52.7269 | 2.9021 |  | 17.5872 | 43.6303 | 14.195 |  | 69.5011 | 123.4547 | 12.4146 | 34.5819 | 2.3771 | 125 | 36.6156 | 25.7983 | 153.2909 | 0.048358
13039 |  | 6.1781 | 79.2564 | 99.4555 | 25.0607 | 15.1987 | 78.7791 | 3.5869 |  | 17.5767 | 65.0196 | 21.6386 |  | 89.5527 | 146.8603 | 22.4505 | 36.5303 | 2.7505 | 150 | 38.6676 | 28.7379 | 180.1183 | 0.059507
13040 |  | 10.9459 | 92.4326 | 116.7769 | 23.963 | 17.0995 | 95.324 | 4.2267 |  | 17.9425 | 81.2111 | 17.2771 |  | 102.3353 | 173.083 | 28.5785 | 39.7843 | 3.3601 | 156 | 32.8729 | 29.8786 | 220.5928 | 0.1422
13041 |  | 15.494 | 101.3877 | 127.8329 | 26.3042 | 17.1 | 107.3208 | 4.6655 |  | 17.9312 | 90.8419 | 15.1866 |  | 112.0279 | 191.4922 | 31.1879 | 43.1844 | 3.6511 | 154 | 26.5455 | 29.1898 | 229.736 | 0.19722
13042 |  | 15.3391 | 101.1293 | 127.7578 | 28.4429 | 18.9995 | 119.7023 | 4.8425 |  | 17.4611 | 93.6258 | 15.6689 |  | 118.0064 | 214.7491 | 30.7361 | 45.0703 | 3.7611 | 155 | 23.4402 | 29.2289 | 229.9258 | 0.11428
13043 |  | 14.1175 | 100.2318 | 127.6821 | 37.2803 | 16.1508 | 121.2878 | 5.3087 |  | 17.6757 | 93.1904 | 15.462 |  | 122.6919 | 218.1005 | 31.6861 | 45.8822 | 3.8892 | 158 | 26.726 | 29.4705 | 231.7289 | 0.25831
13044 |  | 11.3742 | 101.1509 | 128.0593 | 43.4396 | 18.0495 | 115.6715 | 4.8705 |  | 17.1912 | 90.2623 | 13.6126 |  | 122.2104 | 221.1593 | 30.9687 | 45.4853 | 3.9276 | 159 | 21.1301 | 28.7582 | 224.9549 | 0.22842
13045 |  | 9.0695 | 100.334 | 130.3749 | 50.1141 | 18.9997 | 125.1819 | 4.383 |  | 16.3354 | 88.3377 | 13.7709 |  | 121.4701 | 235.8873 | 31.2684 | 46.1886 | 4.2024 | 163 | -18.9015 | 28.8521 | 228.0776 | 0.17434
13046 |  | 6.3363 | 97.9 | 133.0338 | 55.1964 | 19 | 132.4852 | 5.295 |  | 16.0402 | 90.2203 | 13.9504 |  | 123.3508 | 235.2145 | 30.9261 | 46.0856 | 4.4112 | 172 | 18.2327 | 28.8355 | 221.478 | 0.15655
13047 |  | 5.0062 | 92.2926 | 125.0144 | 60.7922 | 18.0503 | 117.6952 | 5.532 |  | 16.0801 | 89.0776 | 13.0134 |  | 111.7876 | 223.4203 | 31.3573 | 45.882 | 4.585 | 167 | 20.518 | 28.2805 | 217.7811 | 0.10712
13048 |  | 4.9741 | 65.0243 | 109.4772 | 66.5027 | 14.2511 | 97.1798 | 4.1169 |  | 16.1756 | 86.1267 | 11.8885 |  | 92.1763 | 197.3809 | 25.6825 | 43.9124 | 4.6022 | 162 | 15.1349 | 27.3353 | 193.6459 | 0.12705
13049 |  | 6.5093 | 52.305 | 104.3359 | 59.4189 | 12.3505 | 83.699 | 2.655 |  | 14.969 | 78.1652 | 11.0003 |  | 79.3629 | 192.5047 | 14.0413 | 41.9582 | 4.4394 | 145 | 14.8513 | 26.5932 | 151.4406 | 0.10204
13050 |  | 8.8989 | 48.7312 | 100.9939 | 47.8593 | 8.5511 | 73.7955 | 2.063 |  | 12.3712 | 64.1114 | 9.7149 |  | 63.8561 | 176.7863 | 10.4617 | 39.4089 | 4.2835 | 142 | 22.3954 | 27.115 | 133.098 | 0.071106
13051 |  | 5.6009 | 42.7358 | 95.2825 | 32.8634 | 10.4495 | 52.2428 | 1.6745 |  | 9.4603 | 57.7159 | 7.2515 |  | 57.3868 | 154.5506 | 9.2512 | 37.5088 | 3.4618 | 123 | 24.7635 | 27.438 | 111.2664 | 0.063126
13052 |  | 2.4675 | 28.985 | 91.3669 | 31.4268 | 7.6008 | 36.4872 | 1.5398 |  | 8.4615 | 52.1238 | 6.1501 |  | 60.8746 | 132.5168 | 9.9524 | 35.6421 | 2.8919 | 119 | 26.4519 | 26.8434 | 105.0713 | 0.024848
13053 |  | 3.6268 | 21.3494 | 88.2835 | 26.9923 | 9.4995 | 40.6343 | 1.7509 |  | 8.475 | 41.3916 | 6.0278 |  | 60.5946 | 130.3488 | 9.8843 | 35.1926 | 2.8014 | 110 | 28.3851 | 26.7673 | 104.0732 | 0.0022615
13054 |  | 3.674 | 20.4379 | 97.7456 | 26.5358 | 7.6005 | 46.6479 | 1.7254 |  | 9.6223 | 36.9203 | 7.3256 |  | 57.6954 | 131.213 | 9.3813 | 35.5174 | 2.8231 | 113 | 30.6366 | 28.3793 | 102.8651 | 0
13055 |  | 1.1313 | 5.8901 | 28.3104 | 13.7743 | 0.002112 | 15.479 | 0.55937 |  | 3.416 | 13.0046 | 2.6578 |  | 16.4042 | 44.6433 | 2.6207 | 10.0579 | 0.96363 | 108 | 2.9146 | 3.7308 | 10.598 | 0
13056 |  | 2.4684 | 21.7145 | 98.3815 | 36.0962 | 9.5 | 39.2216 | 2.3297 |  | 13.3058 | 37.3891 | 8.9001 |  | 51.1332 | 120.4715 | 9.6034 | 35.581 | 2.5921 | 104 | 30.3232 | 41.5135 | 103.2771 | 0
13057 |  | 2.6504 | 20.3074 | 97.4746 | 42.8995 | 9.5 | 37.7567 | 1.9307 |  | 14.0713 | 37.1184 | 8.8044 |  | 49.8194 | 118.1276 | 10.4772 | 35.5862 | 2.5964 | 101 | 33.9782 | 41.3974 | 105.1626 | 0
13058 |  | 2.5705 | 20.2484 | 99.9062 | 45.899 | 8.5503 | 39.8126 | 2.4183 |  | 14.151 | 36.8251 | 10.1996 |  | 50.4391 | 115.6496 | 9.726 | 35.4821 | 2.5859 | 104 | 35.6005 | 41.4657 | 107.9923 | 0
13059 |  | 2.4645 | 20.0353 | 99.2118 | 44.0929 | 11.3992 | 40.7906 | 2.0757 |  | 13.6956 | 36.2708 | 13.8438 |  | 50.6332 | 113.443 | 11.7048 | 35.4145 | 2.6047 | 100 | 34.8281 | 41.4081 | 108.9849 | 0
13060 |  | 2.4838 | 25.5545 | 97.9815 | 44.7676 | 9.5005 | 40.7854 | 1.7763 |  | 12.8319 | 34.5417 | 11.9669 |  | 48.9377 | 106.5804 | 9.7224 | 34.8279 | 2.4569 | 103 | 34.6422 | 41.4096 | 113.1003 | 0
13061 |  | 3.0666 | 40.4642 | 97.711 | 44.3691 | 8.5503 | 41.5487 | 2.1842 |  | 14.7718 | 34.5497 | 8.2049 |  | 49.1848 | 109.6178 | 8.4595 | 34.4028 | 2.3711 | 94 | 32.9672 | 39.3164 | 120.5719 | 0.15421
13062 |  | 8.6603 | 55.8641 | 98.8154 | 42.8043 | 10.4495 | 57.6392 | 2.2235 |  | 16.9394 | 40.4629 | 12.6616 |  | 55.6598 | 117.2522 | 12.9838 | 35.0929 | 2.5578 | 129 | 31.7109 | 28.4123 | 147.2241 | 0.21782
13063 |  | 13.9596 | 74.6071 | 99.1008 | 40.2277 | 14.2489 | 88.1991 | 2.7764 |  | 19.482 | 60.7242 | 19.7629 |  | 74.8658 | 143.0154 | 22.7439 | 36.724 | 5.3399 | 146 | 31.8688 | 28.0698 | 171.7328 | 0.28181
13064 |  | 11.165 | 85.832 | 113.0542 | 39.8226 | 18.0489 | 98.9676 | 4.1052 |  | 20.8075 | 76.5517 | 14.7022 |  | 98.3026 | 170.1701 | 28.659 | 39.4033 | 6.4191 | 158 | 30.9371 | 28.4838 | 202.6395 | 0.32968
13065 |  | 9.8204 | 89.3381 | 123.5142 | 49.461 | 15.2008 | 111.7989 | 4.446 |  | 20.2001 | 82.1626 | 11.6597 |  | 120.568 | 196.7292 | 30.3196 | 41.5874 | 7.2515 | 155 | 24.733 | 28.2304 | 221.1026 | 0.32732
13066 |  | 7.7602 | 93.8925 | 126.9808 | 55.7168 | 16.1497 | 112.812 | 4.3292 |  | 17.2757 | 89.5963 | 11.847 |  | 126.3438 | 217.3565 | 29.387 | 43.8543 | 6.2754 | 157 | 20.9386 | 28.5153 | 225.0874 | 0.329
13067 |  | 7.2676 | 98.4615 | 128.6629 | 59.554 | 18.0495 | 121.6035 | 4.252 |  | 17.1011 | 90.5421 | 11.8846 |  | 127.7294 | 218.723 | 30.0625 | 45.554 | 4.4642 | 153 | 24.7753 | 28.9396 | 236.7757 | 0.25383
13068 |  | 8.4345 | 98.831 | 128.4574 | 62.9083 | 17.1003 | 129.7214 | 4.2812 |  | 17.54 | 86.4457 | 11.5996 |  | 127.8796 | 217.4735 | 29.2503 | 44.8023 | 4.1688 | 158 | 17.3957 | 29.2634 | 227.008 | 0.27116
13069 |  | 11.8191 | 99.1973 | 132.8656 | 58.0602 | 16.1503 | 134.0985 | 4.7273 |  | 16.7866 | 85.1408 | 11.0867 |  | 127.4205 | 222.9445 | 28.6041 | 44.7433 | 4.2416 | 157 | 24.179 | 29.7687 | 225.1328 | 0.29591
13070 |  | 13.0359 | 99.0149 | 132.0492 | 56.8867 | 15.2003 | 132.7906 | 4.7363 |  | 16.516 | 86.0465 | 11.4604 |  | 128.5531 | 224.9409 | 29.9537 | 44.8826 | 4.2881 | 164 | 20.0041 | 29.2822 | 216.5373 | 0.29452
13071 |  | 7.519 | 91.3321 | 126.3002 | 58.0672 | 18.0492 | 129.7588 | 4.1523 |  | 16.5366 | 86.4084 | 11.1291 |  | 109.3282 | 213.684 | 28.8805 | 45.3624 | 4.2109 | 151 | 20.6404 | 29.3326 | 209.6728 | 0.30798
13072 |  | 4.5758 | 70.3816 | 111.5383 | 61.4824 | 13.3013 | 114.4362 | 3.2271 |  | 16.5134 | 84.5477 | 10.928 |  | 93.1203 | 194.051 | 23.5902 | 44.4928 | 3.9086 | 153 | 15.3472 | 28.1028 | 185.0944 | 0.21588
13073 |  | 4.1233 | 61.5779 | 103.4726 | 58.7838 | 10.4508 | 94.2783 | 1.9178 |  | 14.6875 | 75.782 | 9.693 |  | 90.776 | 171.5657 | 13.9914 | 41.4103 | 3.7372 | 141 | 14.2407 | 27.3419 | 154.4672 | 0.22159
13074 |  | 4.9796 | 60.9258 | 98.2978 | 53.7739 | 10.45 | 81.088 | 1.2642 |  | 10.7829 | 64.8256 | 8.2865 |  | 75.1552 | 158.5366 | 8.993 | 40.0904 | 3.526 | 143 | 20.0481 | 28.2453 | 137.5193 | 0.26745
13075 |  | 9.8045 | 54.3228 | 91.8176 | 56.4096 | 5.7013 | 50.0257 | 1.5759 |  | 9.1334 | 59.3605 | 5.854 |  | 57.8394 | 146.8341 | 9.7846 | 38.0842 | 2.9765 | 122 | 21.7047 | 28.0176 | 110.2314 | 0.25392
13076 |  | 13.9832 | 37.4318 | 88.6571 | 52.3816 | 9.4989 | 38.399 | 1.3154 |  | 9.1277 | 54.3193 | 5.0271 |  | 50.6009 | 129.77 | 8.8597 | 35.9714 | 2.8212 | 130 | 21.5012 | 27.7853 | 99.2707 | 0.15542
13077 |  | 8.7663 | 28.6463 | 89.8468 | 50.543 | 8.5503 | 35.2161 | 1.1674 |  | 9.0434 | 44.3799 | 4.798 |  | 47.1323 | 118.3397 | 9.5513 | 34.9732 | 2.8131 | 127 | 23.2081 | 27.7656 | 99.774 | 0.023576
13078 |  | 4.1733 | 27.6593 | 94.4776 | 37.8999 | 9.4997 | 40.6021 | 1.3486 |  | 10.2867 | 38.2012 | 6.3827 |  | 47.4326 | 112.487 | 8.9672 | 35.3013 | 2.7369 | 125 | 23.8255 | 29.432 | 104.51 | 0
13079 |  | 1.3135 | 8.069 | 26.9257 | 17.2416 | 0.00264 | 14.5805 | 0.48522 |  | 3.732 | 13.3752 | 2.4646 |  | 14.0475 | 38.7455 | 2.4251 | 10.1625 | 0.93922 | 117 | 2.2745 | 3.9426 | 10.7707 | 0
13080 |  | 2.8987 | 27.6448 | 93.4414 | 30.7585 | 9.4997 | 38.6638 | 1.6976 |  | 12.6074 | 36.8612 | 7.5541 |  | 48.0229 | 117.69 | 9.1746 | 35.5875 | 2.5361 | 115 | 24.3003 | 42.2076 | 104.6302 | 0
13081 |  | 2.7936 | 27.1049 | 91.0837 | 28.9239 | 9.5 | 41.0836 | 2.3037 |  | 13.3273 | 37.2557 | 7.3764 |  | 47.618 | 115.3925 | 10.4525 | 35.6224 | 2.5584 | 108 | 23.7573 | 42.2309 | 103.8767 | 0
13082 |  | 2.6891 | 27.2961 | 91.9543 | 26.8335 | 10.4497 | 43.1577 | 1.9516 |  | 13.3753 | 37.1475 | 8.2396 |  | 46.9477 | 112.9875 | 9.4058 | 35.4864 | 2.5569 | 102 | 23.5777 | 42.2135 | 104.4819 | 0
13083 |  | 2.726 | 27.4349 | 90.8342 | 30.3991 | 5.7013 | 42.3724 | 1.6435 |  | 13.0938 | 36.9943 | 10.5723 |  | 47.185 | 111.9342 | 10.9263 | 35.7797 | 2.5512 | 103 | 24.5077 | 42.2459 | 107.8282 | 0
13084 |  | 2.7596 | 32.8223 | 88.4229 | 29.3515 | 6.6497 | 39.9439 | 1.4764 |  | 12.1342 | 36.1498 | 8.9141 |  | 45.5989 | 105.8344 | 9.5193 | 35.5253 | 2.4315 | 100 | 22.7142 | 0 | 109.3792 | 0
13085 |  | 3.0874 | 47.1041 | 87.6351 | 30.0611 | 5.7003 | 41.7999 | 1.8585 |  | 14.023 | 35.6407 | 6.3329 |  | 48.3862 | 108.229 | 8.2241 | 35.3224 | 2.3505 | 100 | 21.1737 | 40.1902 | 118.5803 | 0.081088
13086 |  | 8.1652 | 63.8351 | 91.7638 | 28.9895 | 7.5995 | 64.8006 | 2.1656 |  | 18.0485 | 39.877 | 11.1505 |  | 62.1831 | 117.094 | 12.3791 | 36.2708 | 2.3628 | 123 | 25.6123 | 29.4008 | 138.9636 | 0.061754
13087 |  | 10.8821 | 82.9411 | 98.1815 | 23.7594 | 13.2984 | 95.0345 | 3.5901 |  | 18.4619 | 62.2594 | 18.164 |  | 81.5576 | 144.0903 | 22.8923 | 38.2069 | 4.8899 | 152 | 33.4485 | 28.5238 | 166.5848 | 0.061653
13088 |  | 15.2505 | 95.6892 | 115.5321 | 21.9098 | 15.1995 | 103.2435 | 4.5087 |  | 17.622 | 75.1834 | 14.879 |  | 102.6496 | 170.5049 | 28.7503 | 40.3925 | 7.8618 | 154 | 42.4597 | 29.0198 | 208.7573 | 0.082149
13089 |  | 11.328 | 100.4064 | 122.0762 | 29.0547 | 17.0995 | 110.0045 | 4.8147 |  | 16.0768 | 80.9666 | 11.6568 |  | 119.4722 | 194.7333 | 29.5106 | 43.3314 | 5.4244 | 161 | 40.1031 | 28.494 | 238.603 | 0.10654
13090 |  | 7.6594 | 103.4404 | 126.4689 | 36.8468 | 17.1047 | 119.8165 | 4.925 |  | 15.4929 | 85.0874 | 12.7743 |  | 123.8156 | 214.472 | 29.7788 | 45.101 | 3.6071 | 159 | 25.58 | 27.3512 | 240.4743 | 0.11666
13091 |  | 12.1558 | 103.1524 | 125.6276 | 42.813 | 15.1958 | 125.7431 | 5.0742 |  | 15.3799 | 86.2676 | 12.5592 |  | 128.0317 | 224.5074 | 30.4865 | 45.3141 | 3.6249 | 162 | 30.4374 | 28.1265 | 232.9675 | 0.25024
13092 |  | 16.3786 | 103.0893 | 131.151 | 44.7021 | 17.1042 | 136.2475 | 5.0006 |  | 14.617 | 86.5529 | 11.585 |  | 130.9639 | 222.731 | 28.9182 | 45.4672 | 3.5258 | 177 | 38.1093 | 28.7677 | 223.9705 | 0.27715
13093 |  | 16.9337 | 101.183 | 129.8236 | 48.2496 | 16.1455 | 137.1663 | 5.1419 |  | 14.7947 | 87.013 | 11.1777 |  | 130.6948 | 221.7072 | 30.0977 | 46.8378 | 3.4659 | 180 | 3.6621 | 3.7825 | 232.7309 | 0.2935
13094 |  | 10.1768 | 100.8038 | 131.551 | 51.0517 | 16.15 | 132.2729 | 5.3634 |  | 14.6175 | 87.098 | 11.7979 |  | 132.1516 | 218.0478 | 28.9685 | 47.2711 | 3.441 | 176 | 0 | 0 | 227.8977 | 0.27213
13095 |  | 5.0726 | 92.4117 | 128.4262 | 49.8089 | 19.9489 | 120.0664 | 4.9147 |  | 14.3249 | 86.3393 | 11.1453 |  | 119.1783 | 206.2372 | 29.834 | 46.7004 | 3.4569 | 165 | 0 | 0 | 223.2214 | 0.26138
13096 |  | 4.4571 | 67.9037 | 110.8442 | 59.7885 | 14.2516 | 103.6487 | 3.7696 |  | 14.0684 | 83.6631 | 10.3748 |  | 98.5571 | 195.0335 | 24.7251 | 44.6856 | 3.4889 | 165 | 0 | 0 | 206.5051 | 0.20883
13097 |  | 4.0816 | 59.9268 | 100.7305 | 64.6795 | 10.454 | 91.0608 | 2.3565 |  | 12.8966 | 77.2991 | 10.0258 |  | 80.7468 | 171.3562 | 16.1171 | 42.5342 | 3.7076 | 157 | 0 | 0 | 168.8486 | 0.2014
13098 |  | 3.6023 | 57.8898 | 101.3524 | 61.1408 | 6.6482 | 76.9043 | 1.285 |  | 9.2385 | 64.2414 | 8.4405 |  | 68.6272 | 146.2655 | 9.7105 | 39.5823 | 3.5595 | 171 | 0 | 0 | 143.3725 | 0.10961
13099 |  | 3.0817 | 51.8877 | 96.4038 | 52.649 | 6.65 | 50.2274 | 1.0018 |  | 7.7611 | 57.6064 | 5.7753 |  | 63.8422 | 129.7244 | 8.1028 | 36.6805 | 2.8875 | 156 | 0 | 0 | 123.1155 | 0.092783
13100 |  | 2.3414 | 36.555 | 92.1959 | 47.4017 | 7.5997 | 40.712 | 1.174 |  | 7.8039 | 53.1287 | 4.7353 |  | 54.2658 | 123.9901 | 9.6702 | 35.4567 | 2.547 | 150 | 0 | 0 | 118.1972 | 0.074578
13101 |  | 2.9942 | 28.8346 | 90.5737 | 47.1568 | 6.6503 | 39.2716 | 1.1813 |  | 7.8214 | 43.3755 | 5.0005 |  | 49.3967 | 123.573 | 8.6547 | 35.0588 | 2.4398 | 131 | 0 | 0 | 119.8383 | 0.0034302
13102 |  | 3.5647 | 27.7649 | 92.3 | 44.2489 | 8.5495 | 39.3113 | 1.3027 |  | 8.8606 | 39.1497 | 6.6808 |  | 50.8141 | 126.4241 | 8.9669 | 35.1999 | 2.5865 | 128 | 0 | 0 | 118.6342 | 0
13103 |  | 1.3414 | 8.4357 | 27.5129 | 22.5599 | 0.002376 | 13.6406 | 0.49665 |  | 3.3304 | 14.646 | 2.6289 |  | 15.831 | 46.479 | 2.8323 | 10.5935 | 0.96711 | 119 | 0 | 0 | 13 | 0
13104 | 994.2712 | 2.4766 | 27.2556 | 93.1918 | 35.1216 | 7.6005 | 35.8356 | 1.4937 |  | 11.3179 | 37.77 | 7.5278 |  | 47.9395 | 115.6304 | 8.9698 | 35.6305 | 3.0708 | 121 |  |  | 115.7904 | 0
13105 | 994.2712 | 2.6054 | 27.2091 | 92.6708 | 37.1685 | 6.6503 | 38.5842 | 1.5512 |  | 11.9852 | 37.5212 | 7.3692 |  | 47.4016 | 114.1383 | 9.4428 | 35.5959 | 2.5634 | 116 |  |  | 115.8934 | 0
13106 | 994.2712 | 2.898 | 27.1345 | 92.995 | 34.021 | 8.5495 | 37.2429 | 2.1085 |  | 12.041 | 37.7224 | 8.2908 |  | 47.2617 | 115.3463 | 9.6012 | 35.5282 | 2.5536 | 112 |  |  | 117.1559 | 0
13107 | 994.2712 | 2.7735 | 27.0879 | 91.9985 | 34.6482 | 8.55 | 41.8451 | 1.8316 |  | 11.1134 | 36.8924 | 9.982 |  | 46.6458 | 110.5615 | 8.5098 | 35.4482 | 2.5214 | 107 |  |  | 121.0358 | 0
13108 | 994.2712 | 2.4341 | 32.3434 | 89.9347 | 34.3244 | 8.55 | 39.7192 | 1.3408 |  | 10.4776 | 35.4551 | 8.452 |  | 45.0914 | 106.7875 | 9.2484 | 35.9412 | 2.3941 | 108 |  |  | 121.3998 | 0
13109 | 994.2712 | 2.2604 | 43.286 | 89.42 | 34.6219 | 7.6003 | 41.7035 | 1.2686 |  | 13.7107 | 35.1074 | 6.4041 |  | 48.3992 | 107.405 | 8.4015 | 35.4174 | 2.3351 | 104 |  |  | 132.0854 | 0.12102
13110 | 994.2712 | 3.3305 | 58.781 | 91.4312 | 34.2334 | 8.5497 | 52.0755 | 1.4446 |  | 17.7656 | 39.9349 | 11.4331 |  | 60.5827 | 117.2801 | 12.4636 | 35.2678 | 2.3678 | 132 |  |  | 149.3799 | 0.1801
13111 | 994.2712 | 7.7502 | 80.853 | 94.4715 | 30.4746 | 13.2987 | 88.0302 | 3.3099 |  | 17.645 | 61.5303 | 19.1203 |  | 79.3999 | 138.4065 | 22.1091 | 37.4337 | 4.5991 | 152 |  |  | 176.2564 | 0.25533
13112 | 994.2712 | 9.8369 | 93.5174 | 108.7647 | 29.9435 | 17.0989 | 98.5046 | 4.6496 |  | 16.4994 | 77.6781 | 14.625 |  | 100.9683 | 166.8548 | 26.6945 | 40.2807 | 6.3173 | 157 |  |  | 211.9524 | 0.32386
13113 | 994.2712 | 12.7427 | 97.1425 | 122.5435 | 36.6133 | 17.1 | 110.2973 | 4.4136 |  | 16.2738 | 84.0368 | 12.5253 |  | 113.4769 | 188.4383 | 29.06 | 42.7181 | 6.0004 | 151 |  |  | 224.2207 | 0.32582
13114 | 994.2712 | 14.3957 | 97.9751 | 125.0068 | 43.4388 | 16.1503 | 115.1467 | 4.3873 |  | 16.3641 | 85.8613 | 13.2107 |  | 118.7021 | 209.9572 | 28.4907 | 44.1447 | 5.6766 | 155 |  |  | 225.1942 | 0.31545
13115 | 994.2712 | 13.1675 | 98.0734 | 125.2907 | 48.8318 | 16.1545 | 118.1027 | 4.4641 |  | 17.0359 | 84.73 | 13.0156 |  | 124.5075 | 214.4444 | 29.5181 | 44.7514 | 5.5314 | 157 |  |  | 228.2493 | 0.27232
13116 | 994.2712 | 9.1906 | 97.915 | 128.0956 | 56.3572 | 16.1455 | 126.1781 | 4.5869 |  | 17.1626 | 84.6064 | 12.4921 |  | 124.2717 | 206.6292 | 30.3772 | 44.5056 | 4.7314 | 168 |  |  | 219.758 | 0.29118
13117 | 994.2712 | 5.3155 | 98.5659 | 131.3615 | 62.4313 | 16.15 | 130.4784 | 4.6567 |  | 16.9153 | 85.563 | 12.6702 |  | 125.1697 | 211.6812 | 29.4293 | 45.1713 | 4.265 | 186 |  |  | 222.7436 | 0.31741
13118 | 1050.0618 | 4.1534 | 98.2157 | 134.8234 | 65.8541 | 15.2003 | 130.8508 | 4.7266 |  | 16.8843 | 88.8145 | 11.9614 |  | 124.8623 | 218.4866 | 28.8236 | 45.4464 | 4.2274 | 170 |  |  | 220.5461 | 0.30591
13119 | 1050.66 | 4.2521 | 95.1599 | 129.1963 | 64.0723 | 16.1497 | 121.2305 | 4.141 |  | 16.9738 | 90.8588 | 11.5488 |  | 107.5839 | 218.3022 | 27.8211 | 45.1864 | 4.3853 | 162 |  |  | 208.432 | 0.26555
13120 | 1014.3457 | 4.0493 | 70.7718 | 111.0825 | 67.4 | 10.4516 | 98.0194 | 3.6965 |  | 16.8094 | 84.027 | 10.4533 |  | 95.8586 | 200.105 | 21.9185 | 43.1959 | 4.416 | 166 |  |  | 185.8446 | 0.090675
13121 | 983.3644 | 3.4235 | 56.3466 | 110.3114 | 62.3416 | 9.5003 | 86.889 | 2.4676 |  | 15.5418 | 74.6677 | 10.009 |  | 87.1169 | 167.2764 | 12.5247 | 40.6837 | 4.4481 | 158 |  |  | 149.2395 | 0.070415
13122 | 964.156 | 2.741 | 38.0991 | 103.6126 | 54.0907 | 8.5503 | 70.3787 | 1.5603 |  | 11.9531 | 60.5899 | 9.1316 |  | 70.3986 | 144.2534 | 8.7891 | 38.1942 | 4.2429 | 160 |  |  | 134.7844 | 0.11352
13123 | 929.5291 | 2.7443 | 28.2369 | 99.9449 | 53.0211 | 7.6003 | 49.4658 | 1.1922 |  | 10.5771 | 51.9256 | 6.631 |  | 60.3719 | 138.7843 | 7.8086 | 36.555 | 3.5373 | 134 |  |  | 113.8394 | 0.13577
13124 | 887.67 | 2.8655 | 26.3946 | 98.6499 | 47.456 | 7.6 | 39.4372 | 1.0931 |  | 10.4987 | 45.1382 | 5.4184 |  | 50.7848 | 133.4072 | 7.7369 | 34.9499 | 3.1569 | 120 |  |  | 110.4446 | 0.029531
13125 | 883.9021 | 4.3942 | 25.9044 | 97.3532 | 42.3747 | 9.4995 | 39.0414 | 1.0916 |  | 9.9383 | 39.2707 | 5.4706 |  | 46.5852 | 127.3333 | 7.9375 | 34.3152 | 3.1024 | 115 |  |  | 106.8434 | 0.0014893
13126 | 876.2426 | 3.9487 | 26.6807 | 99.8745 | 41.8121 | 8.5503 | 37.3716 | 1.4593 |  | 10.7259 | 34.8577 | 7.0013 |  | 47.3673 | 123.6893 | 9.2049 | 34.3877 | 3.4464 | 119 |  |  | 112.0552 | 0
13127 | 280.0968 | 1.1535 | 8.0925 | 29.2244 | 20.2902 | 0.002376 | 11.8059 | 0.56427 |  | 3.8064 | 11.8839 | 2.5949 |  | 14.4292 | 42.6231 | 2.8864 | 10.1357 | 1.2492 | 118 |  |  | 12.8479 | 0
13128 | 902.115 | 3.7743 | 26.7623 | 100.5188 | 34.4751 | 9.5 | 43.4294 | 2.0297 |  | 12.1353 | 32.4753 | 8.1942 |  | 47.4981 | 119.5299 | 8.3264 | 34.9631 | 4.9349 | 125 |  |  | 111.9192 | 0
13129 | 875.1972 | 3.1992 | 26.6185 | 101.857 | 41.5606 | 5.7011 | 44.9459 | 1.8989 |  | 12.1089 | 32.2278 | 8.071 |  | 46.0171 | 117.2115 | 7.8988 | 34.8642 | 4.9423 | 120 |  |  | 111.1529 | 0
13130 | 868.6564 | 2.395 | 26.3542 | 101.8125 | 40.6325 | 7.5995 | 44.5934 | 1.6318 |  | 12.0005 | 31.8865 | 8.0203 |  | 45.7488 | 114.5359 | 8.1553 | 34.8061 | 5.1966 | 115 |  |  | 113.7076 | 0
13131 | 848.8974 | 2.2981 | 26.2587 | 99.7049 | 39.7123 | 7.6 | 45.3721 | 1.8164 |  | 10.8903 | 30.7104 | 7.2847 |  | 45.0706 | 114.3458 | 7.7971 | 34.5737 | 4.6568 | 112 |  |  | 109.7346 | 0
13132 | 881.9382 | 2.1105 | 31.367 | 98.548 | 35.6775 | 7.6 | 45.5135 | 1.5233 |  | 9.5347 | 29.5596 | 5.8614 |  | 43.8183 | 109.0334 | 7.5456 | 34.6475 | 3.5267 | 109 |  |  | 107.9614 | 0
13133 | 890.8028 | 2.1012 | 31.2557 | 97.6656 | 37.4012 | 8.5497 | 44.5626 | 1.2864 |  | 9.0987 | 30.1589 | 5.1604 |  | 42.8177 | 110.5527 | 8.0728 | 34.5669 | 3.1 | 102 |  |  | 107.2765 | 0.12876
13134 | 886.3816 | 2.1381 | 32.3721 | 96.8205 | 37.672 | 7.6003 | 46.6245 | 1.2777 |  | 9.0944 | 34.4996 | 6.1404 |  | 43.1237 | 106.883 | 7.7021 | 34.6123 | 3.1405 | 99 |  |  | 106.3778 | 0.19646
13135 | 896.9001 | 2.1175 | 54.2394 | 97.0789 | 34.3075 | 7.6 | 52.747 | 1.2615 |  | 9.2168 | 35.6229 | 6.0912 |  | 43.0814 | 108.3286 | 8.0793 | 34.7856 | 3.2299 | 97 |  |  | 109.1103 | 0.26619
13136 | 917.0097 | 1.9688 | 62.4401 | 97.5333 | 36.5679 | 7.6 | 63.7302 | 1.2404 |  | 10.0708 | 31.5293 | 5.5593 |  | 45.3011 | 108.0526 | 7.6118 | 34.2016 | 3.2619 | 104 |  |  | 107.3061 | 0.3172
13137 | 931.6709 | 2.2523 | 74.7414 | 97.5536 | 44.8378 | 7.6 | 58.17 | 1.1471 |  | 11.9616 | 33.2749 | 5.473 |  | 47.1568 | 109.3839 | 7.4581 | 33.9072 | 3.3059 | 99 |  |  | 108.697 | 0.32051
13138 | 942.6843 | 2.5274 | 89.1603 | 98.5349 | 50.6613 | 7.6 | 49.983 | 1.3426 |  | 15.5553 | 38.6258 | 5.2679 |  | 48.6189 | 111.007 | 8.3556 | 34.0044 | 3.4368 | 106 |  |  | 109.8439 | 0.30429
13139 | 899.5597 | 2.4808 | 95.5317 | 97.5099 | 52.7669 | 7.6 | 47.2967 | 2.0642 |  | 17.102 | 41.6973 | 5.1876 |  | 49.3633 | 111.7316 | 7.5897 | 34.3749 | 3.3566 | 108 |  |  | 110.1819 | 0.26719
13140 | 887.5285 | 7.1975 | 83.9284 | 97.744 | 55.4702 | 9.4995 | 48.9487 | 2.3725 |  | 16.8972 | 47.441 | 5.4325 |  | 50.2023 | 109.2934 | 7.3451 | 34.5152 | 3.3267 | 115 |  |  | 106.7295 | 0.28085
13141 | 874.4275 | 9.7945 | 60.485 | 97.7277 | 62.8434 | 7.6005 | 48.8133 | 1.579 |  | 16.9288 | 49.9553 | 5.5121 |  | 51.2434 | 118.6419 | 7.5885 | 34.3727 | 3.3334 | 111 |  |  | 104.1432 | 0.30569
13142 | 878.386 | 5.3263 | 37.6076 | 98.8583 | 66.7346 | 5.7005 | 47.835 | 1.0886 |  | 17.1685 | 50.6507 | 6.2356 |  | 51.1184 | 130.7457 | 7.912 | 34.4217 | 3.3529 | 130 |  |  | 105.6586 | 0.30241
13143 | 921.1654 | 3.3704 | 28.7147 | 99.7977 | 61.856 | 7.5995 | 47.9917 | 1.6579 |  | 15.3933 | 51.9372 | 6.1048 |  | 50.4025 | 135.9422 | 7.3793 | 34.3025 | 3.3417 | 128 |  |  | 106.9816 | 0.3115
13144 | 928.9964 | 6.2423 | 27.4705 | 100.1241 | 57.6504 | 7.6 | 53.7701 | 2.0641 |  | 11.569 | 50.3538 | 5.579 |  | 50.6629 | 134.0988 | 7.6856 | 34.3213 | 3.5114 | 130 |  |  | 101.3236 | 0.2651
13145 | 894.5895 | 6.4201 | 26.7199 | 100.7246 | 57.8372 | 5.7005 | 53.139 | 2.112 |  | 10.0546 | 44.764 | 5.5193 |  | 49.1197 | 132.5203 | 6.906 | 33.9064 | 3.4876 | 126 |  |  | 100.2955 | 0.2859
13146 | 856.8918 | 6.9058 | 26.4872 | 101.0739 | 58.5026 | 7.5995 | 52.1848 | 2.3964 |  | 10.1085 | 42.8869 | 5.6454 |  | 48.6532 | 129.5471 | 7.7525 | 34.2104 | 3.4854 | 130 |  |  | 99.1712 | 0.26017
13147 | 855.1818 | 6.7961 | 27.194 | 101.0144 | 61.8471 | 7.6 | 49.6868 | 1.6662 |  | 10.3329 | 40.5801 | 5.7394 |  | 48.2464 | 127.0584 | 8.1643 | 34.6708 | 3.5378 | 121 |  |  | 104.0313 | 0.22243
13148 | 882.5744 | 6.6988 | 27.0845 | 98.0916 | 58.4309 | 7.6 | 47.6684 | 1.0944 |  | 10.3374 | 34.2637 | 5.501 |  | 46.1399 | 127.1628 | 7.0882 | 34.4988 | 3.4902 | 123 |  |  | 100.3507 | 0.12205
13149 | 855.3752 | 6.9785 | 26.8734 | 94.3466 | 54.9159 | 6.6503 | 47.8795 | 1.0416 |  | 9.8027 | 32.1673 | 5.4499 |  | 44.8101 | 135.7277 | 7.2336 | 34.2435 | 3.3739 | 124 |  |  | 104.7898 | 0.010132
13150 | 847.5939 | 6.7955 | 26.7563 | 91.6046 | 53.2202 | 6.65 | 49.1442 | 1.7776 |  | 9.6265 | 31.9082 | 6.1195 |  | 45.5322 | 134.2906 | 8.4371 | 34.3446 | 3.3961 | 121 |  |  | 104.0902 | 0
13151 | 271.6497 | 2.378 | 7.898 | 25.9817 | 24.4588 | 0.001848 | 15.9978 | 0.72543 |  | 3.233 | 11.1632 | 2.132 |  | 13.6821 | 45.1414 | 2.5763 | 10.0008 | 1.1682 | 110 |  |  | 10.5626 | 0
13152 | 865.1897 | 3.7884 | 26.6289 | 97.9147 | 43.0219 | 7.6 | 50.2035 | 1.6204 |  | 12.0086 | 33.3946 | 8.2403 |  | 46.7403 | 121.6363 | 11.1648 | 35.1917 | 3.6844 | 109 |  |  | 109.0542 | 0
13153 | 873.7358 | 3.1891 | 26.4604 | 95.6204 | 45.7027 | 7.6 | 46.533 | 1.611 |  | 11.9648 | 33.6608 | 8.1645 |  | 46.4795 | 127.6435 | 13.3085 | 35.4919 | 3.3964 | 106 |  |  | 106.9455 | 0
13154 | 857.1838 | 2.5399 | 25.8754 | 94.2065 | 43.6997 | 8.5497 | 42.1648 | 1.8485 |  | 11.9014 | 33.0257 | 8.2014 |  | 46.1015 | 125.8112 | 12.0202 | 35.8204 | 3.3397 | 111 |  |  | 110.0334 | 0
13155 | 857.2043 | 2.5403 | 26.1194 | 97.6818 | 40.0356 | 9.4997 | 44.6837 | 1.6864 |  | 11.4547 | 32.2631 | 7.7054 |  | 45.1638 | 119.1576 | 12.8232 | 35.685 | 3.339 | 105 |  |  | 107.869 | 0
13156 | 858.4959 | 2.6564 | 25.8969 | 93.8785 | 35.4196 | 8.5503 | 48.2177 | 2.0576 |  | 9.8143 | 30.9216 | 6.062 |  | 43.8401 | 111.0125 | 10.9577 | 35.0778 | 3.2012 | 100 |  |  | 106.3691 | 0
13157 | 869.4277 | 2.5355 | 25.6559 | 90.6892 | 29.7577 | 9.4997 | 52.3067 | 1.661 |  | 9.0594 | 30.3878 | 5.2217 |  | 42.9966 | 109.7206 | 7.8544 | 35.0632 | 3.1481 | 100 |  |  | 102.2865 | 0.13511
13158 | 876.3031 | 2.2125 | 25.6294 | 93.8161 | 30.8845 | 8.5503 | 48.0646 | 1.2969 |  | 9.0874 | 32.3192 | 5.13 |  | 42.6531 | 106.6573 | 7.9811 | 34.7777 | 3.1552 | 100 |  |  | 105.7999 | 0.19055
13159 | 890.6612 | 2.299 | 25.532 | 94.1409 | 30.4549 | 7.6003 | 46.2746 | 1.3185 |  | 9.1207 | 36.9591 | 5.1942 |  | 43.3527 | 109.3857 | 7.1765 | 34.3715 | 3.2675 | 99 |  |  | 104.2801 | 0.14233
13160 | 882.0072 | 2.3091 | 25.5468 | 95.7382 | 30.8652 | 7.6 | 49.4522 | 1.4 |  | 9.024 | 33.9737 | 5.3128 |  | 42.4477 | 107.4976 | 7.8737 | 34.2627 | 3.269 | 106 |  |  | 105.8277 | 0.32853
13161 | 880.0119 | 4.845 | 25.4132 | 99.4679 | 31.0243 | 8.5497 | 52.7517 | 1.5125 |  | 10.3531 | 31.3847 | 5.4778 |  | 42.9602 | 107.5702 | 7.304 | 34.0549 | 3.2635 | 105 |  |  | 103.7029 | 0.32525
13162 | 901.0619 | 5.1416 | 25.4208 | 107.0341 | 37.2001 | 7.6003 | 59.0219 | 1.5568 |  | 14.0151 | 32.5096 | 5.4776 |  | 44.3095 | 108.6934 | 7.4691 | 34.2757 | 3.2902 | 108 |  |  | 109.7592 | 0.32917
13163 | 905.8256 | 3.3662 | 25.3442 | 104.1672 | 40.1506 | 10.4492 | 51.0118 | 1.2798 |  | 15.7964 | 38.3997 | 5.6019 |  | 47.0051 | 110.9257 | 8.5968 | 34.5785 | 3.2159 | 107 |  |  | 106.7852 | 0.25546
13164 | 910.7672 | 5.433 | 25.4262 | 96.4452 | 43.6463 | 9.5003 | 44.5616 | 1.0573 |  | 17.1685 | 47.0618 | 5.8563 |  | 48.9567 | 105.4562 | 7.57 | 34.5093 | 3.143 | 112 |  |  | 110.5724 | 0.2722
13165 | 913.3357 | 4.5253 | 25.7287 | 92.9093 | 41.8753 | 9.5 | 45.1327 | 1.0137 |  | 17.8888 | 50.2436 | 5.6653 |  | 49.29 | 105.9936 | 7.1182 | 34.7989 | 3.2913 | 119 |  |  | 110.0764 | 0.29647
13166 | 896.5244 | 5.8461 | 25.9141 | 91.136 | 39.1591 | 5.7011 | 44.025 | 1.0477 |  | 17.6604 | 50.2737 | 5.8351 |  | 49.7785 | 113.3472 | 8.4511 | 34.2 | 3.3529 | 113 |  |  | 107.0619 | 0.29564
13167 | 903.5478 | 5.3411 | 25.8384 | 91.9618 | 32.8681 | 7.5995 | 47.0106 | 1.0769 |  | 15.1466 | 50.3507 | 5.8437 |  | 49.5994 | 120.5822 | 7.3604 | 33.9125 | 3.3771 | 119 |  |  | 106.3768 | 0.30813
13168 | 907.7261 | 7.6319 | 25.3146 | 89.8943 | 32.6735 | 6.6503 | 51.4309 | 1.0458 |  | 11.361 | 50.1198 | 5.5124 |  | 49.2011 | 117.3014 | 7.6989 | 33.1401 | 3.3249 | 114 |  |  | 104.4281 | 0.26194
13169 | 920.983 | 11.8963 | 25.2502 | 93.9899 | 32.6998 | 7.5997 | 51.7865 | 1.2607 |  | 9.6694 | 49.0656 | 5.4449 |  | 49.0813 | 117.1911 | 7.1114 | 33.7392 | 3.3714 | 111 |  |  | 102.2459 | 0.28797
13170 | 924.132 | 16.0964 | 25.7299 | 93.7564 | 33.0299 | 8.5497 | 49.2061 | 1.2859 |  | 9.2456 | 43.1531 | 5.5492 |  | 51.1945 | 121.7944 | 8.0584 | 35.1037 | 3.4405 | 107 |  |  | 101.3185 | 0.27241
13171 | 906.423 | 17.3691 | 25.7294 | 90.9465 | 31.261 | 8.55 | 46.1907 | 1.8282 |  | 9.0876 | 35.4296 | 5.5671 |  | 49.3452 | 122.1382 | 7.227 | 34.7928 | 3.7417 | 99 |  |  | 99.114 | 0.24485
13172 | 895.596 | 9.4876 | 25.5955 | 91.4667 | 36.5561 | 7.6003 | 44.8426 | 1.5793 |  | 8.9886 | 32.992 | 5.6601 |  | 44.6541 | 120.4252 | 8.1042 | 34.6557 | 3.7942 | 120 |  |  | 104.4486 | 0.14783
13173 | 891.0284 | 4.6576 | 25.4233 | 92.313 | 32.1688 | 8.5497 | 47.7325 | 1.2809 |  | 9.0272 | 32.0948 | 6.684 |  | 43.3459 | 122.6971 | 7.2576 | 34.655 | 4.0184 | 116 |  |  | 106.8919 | 0.018944
13174 | 892.4974 | 4.2747 | 25.5841 | 99.6568 | 31.6763 | 7.6003 | 48.6332 | 2.141 |  | 10.1427 | 31.3282 | 10.3132 |  | 46.8847 | 122.1142 | 7.654 | 35.0608 | 3.8418 | 111 |  |  | 107.719 | 0
13175 | 287.5502 | 1.5136 | 7.6272 | 29.5446 | 17.263 | 0.002112 | 15.7347 | 0.87939 |  | 3.6078 | 11.104 | 3.9755 |  | 14.4728 | 41.973 | 2.362 | 10.3103 | 1.2615 | 105 |  |  | 11.6875 | 0
13176 | 873.4663 | 3.062 | 25.985 | 106.8974 | 45.0079 | 7.6005 | 45.3779 | 1.6078 |  | 13.7751 | 31.8488 | 12.8386 |  | 45.5761 | 118.3483 | 8.2133 | 35.5625 | 3.493 | 103 |  |  | 109.5705 | 0
13177 | 863.4783 | 3.0865 | 25.6667 | 105.9448 | 42.5036 | 9.4995 | 45.4975 | 2.6275 |  | 14.4496 | 31.7861 | 12.7293 |  | 48.5398 | 122.0188 | 8.7331 | 35.3951 | 3.4389 | 101 |  |  | 111.2374 | 0
13178 | 866.5127 | 3.1285 | 26.0695 | 101.6617 | 40.5839 | 9.5 | 47.1647 | 2.1792 |  | 14.4698 | 31.7714 | 13.5738 |  | 52.9283 | 127.7241 | 8.3001 | 35.3497 | 3.37 | 101 |  |  | 112.5716 | 0
13179 | 867.4656 | 3.0103 | 26.1629 | 99.6751 | 39.0636 | 9.5 | 50.7637 | 2.3756 |  | 13.7816 | 30.9886 | 13.6482 |  | 53.7728 | 124.1192 | 7.4063 | 35.04 | 3.3397 | 101 |  |  | 116.0119 | 0
13180 | 871.756 | 3.0045 | 25.7596 | 97.5555 | 35.9521 | 11.3995 | 51.686 | 1.8136 |  | 13.0415 | 29.5072 | 9.944 |  | 51.847 | 120.8486 | 8.2134 | 34.7486 | 3.2046 | 100 |  |  | 127.168 | 0
13181 | 872.677 | 2.7164 | 44.5764 | 96.493 | 39.2104 | 7.6011 | 49.6671 | 1.2985 |  | 15.0573 | 29.1242 | 7.0406 |  | 50.8527 | 120.7773 | 7.2617 | 34.3802 | 3.121 | 95 |  |  | 135.454 | 0.13883
13182 | 926.5484 | 3.2888 | 60.5647 | 95.0625 | 35.5707 | 11.3989 | 65.6074 | 1.9964 |  | 18.2291 | 34.7957 | 12.4254 |  | 58.2353 | 139.0089 | 8.0272 | 34.9037 | 3.1359 | 124 |  |  | 149.9537 | 0.20689
13183 | 964.435 | 6.2825 | 78.3934 | 95.4359 | 33.7476 | 14.2492 | 85.9025 | 2.9942 |  | 21.0933 | 54.1875 | 21.389 |  | 76.9152 | 160.3542 | 8.285 | 36.9554 | 5.5879 | 147 |  |  | 184.6636 | 0.28333
13184 | 1015.4507 | 11.518 | 93.2869 | 111.6605 | 32.6371 | 16.1495 | 97.1048 | 4.0134 |  | 21.4088 | 69.0147 | 16.5611 |  | 98.7447 | 180.7142 | 13.0408 | 40.1402 | 9.3107 | 148 |  |  | 213.486 | 0.32935
13185 | 1069.6409 | 13.9016 | 98.4648 | 125.6208 | 33.463 | 15.2003 | 101.5309 | 4.4269 |  | 16.2254 | 80.5684 | 12.5378 |  | 111.8302 | 192.467 | 19.0727 | 43.4933 | 6.6649 | 155 |  |  | 230.4078 | 0.3097
13186 | 1114.3514 | 16.8304 | 98.9299 | 128.065 | 28.854 | 19.9487 | 103.1163 | 4.5146 |  | 13.9493 | 89.0907 | 12.2435 |  | 121.0688 | 206.1462 | 22.4681 | 44.9651 | 6.1332 | 162 |  |  | 230.8011 | 0.32196
13187 | 1143.0318 | 16.3259 | 100.7445 | 129.0637 | 33.8482 | 16.1511 | 108.6849 | 4.6003 |  | 13.689 | 88.0602 | 12.5371 |  | 125.9573 | 213.0368 | 21.4285 | 45.6421 | 4.9615 | 159 |  |  | 229.7857 | 0.25983
13188 | 1140.4164 | 10.8335 | 101.3849 | 128.9235 | 35.8417 | 17.0997 | 125.3419 | 4.5855 |  | 13.942 | 86.6046 | 11.9102 |  | 125.237 | 205.3597 | 22.0455 | 45.0059 | 3.6614 | 158 |  |  | 232.0858 | 0.27651
13189 | 1148.868 | 6.4661 | 102.0827 | 129.4475 | 41.4542 | 16.1503 | 133.978 | 4.7208 |  | 14.9965 | 96.1885 | 11.8136 |  | 124.8214 | 207.6978 | 19.2087 | 46.2797 | 3.7753 | 161 |  |  | 228.7338 | 0.29038
13190 | 1157.5374 | 4.6735 | 100.6088 | 133.6276 | 46.5103 | 18.0495 | 132.9027 | 4.4241 |  | 15.4664 | 93.5341 | 11.8873 |  | 122.8589 | 206.8438 | 12.2498 | 45.513 | 3.9003 | 156 |  |  | 221.1138 | 0.27853
13191 | 1106.3123 | 4.7699 | 93.1177 | 129.5541 | 52.6706 | 17.1003 | 124.1217 | 4.144 |  | 14.4407 | 90.9002 | 10.9706 |  | 101.8614 | 193.6 | 9.504 | 43.8421 | 3.9413 | 150 |  |  | 220.1532 | 0.25341
13192 | 1064.186 | 4.5807 | 65.9804 | 110.2195 | 51.8755 | 13.3011 | 105.3206 | 3.8373 |  | 12.9226 | 94.0461 | 9.6848 |  | 87.1687 | 185.4584 | 7.7676 | 41.9943 | 3.8898 | 152 |  |  | 198.6749 | 0.24796
13193 | 1007.8049 | 4.0137 | 55.5375 | 105.0015 | 49.9073 | 8.5513 | 94.9939 | 3.1462 |  | 10.4391 | 81.5456 | 9.4991 |  | 79.5132 | 163.8162 | 8.2857 | 41.202 | 3.903 | 152 |  |  | 163.4265 | 0.2618
13194 | 1008.0732 | 3.2188 | 54.3174 | 103.1964 | 42.974 | 11.3992 | 81.6854 | 2.008 |  | 6.3414 | 63.7758 | 8.7967 |  | 62.5463 | 152.7774 | 7.2683 | 39.4029 | 3.684 | 154 |  |  | 148.0209 | 0.17351
13195 | 988.4133 | 3.5783 | 47.8613 | 96.5694 | 47.2777 | 8.5508 | 61.4652 | 1.5817 |  | 4.822 | 57.4051 | 6.3103 |  | 51.6783 | 149.6458 | 7.6574 | 36.8332 | 3.0418 | 125 |  |  | 128.5398 | 0.099136
13196 | 966.5629 | 3.251 | 31.4355 | 94.4301 | 43.2744 | 9.4997 | 53.5023 | 2.4492 |  | 4.8037 | 52.0736 | 5.3227 |  | 47.9351 | 137.0362 | 7.2417 | 35.8904 | 2.7552 | 119 |  |  | 116.5482 | 0.015409
13197 | 939.7805 | 8.0016 | 22.6168 | 96.0569 | 34.6871 | 9.5 | 47.559 | 1.9463 |  | 4.8013 | 40.994 | 5.3674 |  | 47.5028 | 132.7307 | 7.6851 | 35.6429 | 2.7079 | 110 |  |  | 118.875 | 0.00088254
13198 | 931.5605 | 11.1125 | 21.3628 | 96.1708 | 30.1428 | 10.4497 | 48.2881 | 1.8154 |  | 6.5292 | 36.434 | 7.1548 |  | 50.2717 | 130.6111 | 8.0778 | 35.6691 | 2.6537 | 108 |  |  | 116.3425 | 0
13199 | 299.894 | 4.0718 | 6.3708 | 27.7248 | 17.0326 | 0.002903 | 16.24 | 0.68592 |  | 2.5009 | 13.1075 | 2.6919 |  | 15.4356 | 45.1777 | 2.3848 | 10.478 | 0.91304 | 103 |  |  | 9.1321 | 0
13200 | 937.3805 | 3.8402 | 21.9525 | 96.5059 | 36.0449 | 11.4 | 52.5476 | 2.0757 |  | 9.5589 | 37.1091 | 8.2166 |  | 48.7048 | 113.5315 | 12.3716 | 35.7301 | 2.5633 | 106 |  |  | 123.5663 | 0
13201 | 919.778 | 2.4124 | 21.9715 | 95.6064 | 36.6597 | 8.5508 | 46.0388 | 2.4375 |  | 10.1937 | 36.6785 | 8.7709 |  | 48.5037 | 115.0354 | 12.2585 | 36.0607 | 2.5693 | 102 |  |  | 125.3393 | 0
13202 | 897.0617 | 2.4646 | 21.8987 | 96.5374 | 33.7914 | 9.4997 | 46.7741 | 1.9629 |  | 10.1766 | 36.0523 | 10.6734 |  | 52.7372 | 114.4826 | 11.2322 | 35.6601 | 2.5642 | 100 |  |  | 124.89 | 0
13203 | 893.4815 | 2.5679 | 21.8595 | 94.8785 | 25.8857 | 11.3995 | 47.67 | 2.3536 |  | 9.7173 | 35.4192 | 15.5067 |  | 55.7517 | 111.9644 | 11.2693 | 36.4511 | 2.5682 | 102 |  |  | 126.6176 | 0
13204 | 900.3379 | 2.7376 | 21.3869 | 93.2907 | 22.6742 | 10.4503 | 48.3636 | 1.8487 |  | 8.7333 | 34.0162 | 13.6467 |  | 55.0608 | 105.6799 | 7.923 | 35.5004 | 2.4465 | 101 |  |  | 133.2346 | 0
13205 | 894.7723 | 2.3663 | 32.7794 | 94.0351 | 25.1252 | 7.6008 | 50.0124 | 2.1142 |  | 10.6702 | 33.3703 | 8.8294 |  | 54.0175 | 108.2945 | 7.9358 | 34.5718 | 2.3629 | 96 |  |  | 144.5444 | 0.018535
13206 | 919.7546 | 7.2777 | 39.828 | 93.4679 | 21.6515 | 10.4492 | 66.9895 | 2.3656 |  | 14.2409 | 38.0907 | 12.8428 |  | 61.8826 | 118.7109 | 7.2884 | 35.0464 | 2.3709 | 124 |  |  | 162.9399 | 0.038017
13207 | 959.2 | 15.7673 | 66.0878 | 98.2838 | 19.0265 | 16.1484 | 86.8466 | 2.6663 |  | 16.9394 | 59.5958 | 19.7588 |  | 81.2002 | 138.3285 | 8.305 | 36.995 | 2.7905 | 150 |  |  | 189.0939 | 0.057786
13208 | 999.068 | 13.2584 | 91.9621 | 115.4069 | 27.2194 | 14.2505 | 106.7581 | 3.7658 |  | 17.7869 | 77.704 | 15.6394 |  | 102.9927 | 166.4286 | 11.4095 | 41.4828 | 3.7199 | 151 |  |  | 223.7668 | 0.078647
13209 | 1066.7634 | 6.4053 | 100.0915 | 126.9605 | 30.0577 | 16.1495 | 114.9713 | 3.9031 |  | 15.8901 | 84.8334 | 11.864 |  | 116.0544 | 184.1493 | 17.6551 | 45.7391 | 4.041 | 155 |  |  | 240.0743 | 0.18219
13210 | 1131.8632 | 5.4446 | 98.406 | 132.5253 | 35.0944 | 18.0495 | 123.036 | 4.7033 |  | 18.8856 | 86.3663 | 11.5298 |  | 120.1945 | 201.0424 | 21.831 | 41.7018 | 4.1509 | 155 |  |  | 237.8901 | 0.23891
13211 | 1152.7038 | 7.5938 | 97.9972 | 133.9964 | 44.3379 | 17.1003 | 128.5502 | 4.301 |  | 18.1781 | 87.0013 | 11.6021 |  | 123.4269 | 199.3656 | 20.3307 | 38.5808 | 3.9436 | 158 |  |  | 234.6604 | 0.21915
13212 | 1140.2463 | 7.8333 | 98.0086 | 131.6205 | 50.7223 | 18.0497 | 130.5506 | 4.0499 |  | 14.8048 | 85.7049 | 11.6251 |  | 124.8831 | 196.7795 | 20.7612 | 40.5501 | 3.798 | 156 |  |  | 236.0403 | 0.25863
13213 | 1140.5852 | 10.1172 | 100.7305 | 135.2335 | 61.416 | 18.05 | 134.1211 | 3.9374 |  | 15.4692 | 87.1564 | 12.6456 |  | 125.0254 | 204.5696 | 17.7729 | 44.6326 | 3.7565 | 157 |  |  | 224.6746 | 0.14497
13214 | 1129.6031 | 10.6886 | 100.0882 | 135.6877 | 62.2993 | 18.05 | 137.393 | 3.8094 |  | 14.3948 | 87.4484 | 12.2201 |  | 123.5631 | 205.7304 | 10.3825 | 46.1502 | 3.7922 | 156 |  |  | 215.2497 | 0.16267
13215 | 1098.9528 | 6.8134 | 100.6392 | 126.7124 | 59.9138 | 14.2511 | 128.4909 | 3.7272 |  | 13.2741 | 86.3952 | 11.3538 |  | 110.1606 | 197.4383 | 8.19 | 45.0496 | 3.7677 | 149 |  |  | 219.4001 | 0.18853
13216 | 1047.5828 | 4.7929 | 94.9007 | 108.0966 | 60.6709 | 10.4511 | 97.9727 | 3.4285 |  | 12.9589 | 83.0066 | 9.6433 |  | 90.4683 | 184.9704 | 8.0842 | 42.6635 | 3.9745 | 139 |  |  | 200.1563 | 0.088818
13217 | 1018.5713 | 4.1821 | 67.7209 | 101.383 | 58.2964 | 8.5505 | 70.6579 | 3.2227 |  | 11.6886 | 76.2574 | 9.3905 |  | 81.6419 | 167.0141 | 7.8903 | 40.4783 | 3.9111 | 147 |  |  | 158.2563 | 0.070138
13218 | 983.8599 | 3.3277 | 54.2642 | 96.1788 | 54.5401 | 8.55 | 59.9196 | 2.3344 |  | 7.8827 | 62.8477 | 8.2947 |  | 68.5548 | 149.4156 | 7.0885 | 38.2511 | 3.498 | 144 |  |  | 138.793 | 0.096769
13219 | 943.7809 | 2.9136 | 47.3049 | 92.8795 | 52.7129 | 8.55 | 54.5129 | 1.5178 |  | 5.6925 | 55.8656 | 5.6855 |  | 57.2543 | 139.5417 | 7.752 | 36.9526 | 2.8489 | 130 |  |  | 119.5978 | 0.1241
13220 | 934.3852 | 2.4481 | 30.8038 | 91.4843 | 44.3047 | 8.55 | 53.3326 | 1.1226 |  | 5.3658 | 50.5621 | 4.6771 |  | 53.691 | 129.8892 | 7.2318 | 36.312 | 2.6114 | 123 |  |  | 113.3181 | 0.028715
13221 | 924.3679 | 3.0968 | 22.36 | 92.8838 | 41.4119 | 9.4997 | 55.7913 | 1.9021 |  | 5.593 | 40.0147 | 4.7233 |  | 51.3499 | 124.9401 | 7.666 | 36.394 | 2.5974 | 120 |  |  | 113.5857 | 0.00088254
13222 | 904.517 | 3.4398 | 21.3501 | 97.8308 | 40.7621 | 8.5503 | 58.9798 | 1.9038 |  | 6.0002 | 34.9255 | 5.5841 |  | 51.6434 | 119.2825 | 7.5799 | 36.4185 | 2.5237 | 121 |  |  | 112.5744 | 0
13223 | 288.11 | 1.2098 | 6.3774 | 28.7357 | 19.2412 | 0.002376 | 19.5017 | 0.56978 |  | 2.0717 | 12.3141 | 2.0022 |  | 15.6564 | 40.4434 | 2.1719 | 10.677 | 0.85521 | 115 |  |  | 12.5364 | 0
13224 | 908.9072 | 2.4847 | 21.0737 | 103.3905 | 27.3934 | 8.5503 | 56.6665 | 2.1344 |  | 10.1038 | 35.5061 | 7.4788 |  | 51.1295 | 111.4583 | 10.9865 | 36.3459 | 2.5752 | 109 |  |  | 116.8382 | 0
13225 | 915.471 | 2.3283 | 21.1814 | 102.4955 | 27.4689 | 10.4495 | 55.8365 | 1.6245 |  | 10.6555 | 35.4884 | 7.3664 |  | 53.2146 | 111.6205 | 12.7465 | 36.2751 | 2.5601 | 110 |  |  | 121.3847 | 0
13226 | 902.5137 | 2.3994 | 21.3659 | 103.2107 | 37.5768 | 8.5505 | 48.2186 | 2.3196 |  | 10.6697 | 35.3254 | 8.2155 |  | 57.3444 | 110.9357 | 11.8159 | 36.0292 | 2.5615 | 102 |  |  | 119.896 | 0
13227 | 892.6012 | 2.3371 | 21.2934 | 105.374 | 34.6783 | 10.4495 | 51.1118 | 1.9356 |  | 9.9658 | 34.3859 | 10.2081 |  | 58.0489 | 110.1387 | 12.1246 | 35.9512 | 2.5615 | 101 |  |  | 124.4778 | 0
13228 | 887.0066 | 2.6397 | 20.8877 | 102.2233 | 34.7268 | 8.5505 | 50.7704 | 2.1456 |  | 9.1768 | 32.8869 | 8.5456 |  | 56.2566 | 103.5901 | 10.863 | 35.7052 | 2.4242 | 99 |  |  | 128.0048 | 0
13229 | 902.706 | 2.4706 | 30.505 | 98.9978 | 33.8244 | 9.4997 | 56.1565 | 1.9734 |  | 11.2866 | 32.4237 | 6.2012 |  | 51.2624 | 107.048 | 8.107 | 35.4165 | 2.3479 | 95 |  |  | 133.8826 | 0.032563
13230 | 945.126 | 7.0329 | 37.528 | 98.5538 | 32.0921 | 10.4497 | 68.6956 | 1.4608 |  | 13.3399 | 37.3361 | 12.0685 |  | 56.2163 | 121.4111 | 7.3343 | 35.9055 | 2.3722 | 123 |  |  | 150.7562 | 0.063159
13231 | 996.1232 | 14.3431 | 56.5896 | 102.0684 | 25.0837 | 17.0982 | 94.9868 | 2.411 |  | 12.3293 | 57.6672 | 19.6457 |  | 73.8796 | 149.4104 | 8.7258 | 37.6248 | 2.7425 | 148 |  |  | 179.4349 | 0.061255
13232 | 1038.792 | 13.245 | 85.0022 | 114.3853 | 29.5146 | 15.2005 | 112.1454 | 4.0181 |  | 11.6863 | 76.0799 | 14.7188 |  | 95.9773 | 171.2044 | 10.9342 | 40.6201 | 3.8734 | 150 |  |  | 216.104 | 0.15555
13233 | 1090.3818 | 7.0617 | 96.9663 | 123.5732 | 30.0047 | 18.0492 | 120.319 | 4.5904 |  | 11.7165 | 84.9776 | 10.6249 |  | 108.2057 | 187.3457 | 18.6557 | 42.79 | 4.261 | 148 |  |  | 237.9991 | 0.15358
13234 | 1117.7786 | 4.9273 | 89.6202 | 127.7187 | 34.4603 | 18.05 | 128.2273 | 4.4092 |  | 11.725 | 88.5981 | 11.649 |  | 113.4855 | 195.3153 | 20.8203 | 44.331 | 4.2754 | 151 |  |  | 236.4092 | 0.18121
13235 | 1126.9851 | 8.4798 | 94.5656 | 133.216 | 42.9654 | 16.1505 | 130.1589 | 4.1204 |  | 11.7117 | 89.5284 | 12.4929 |  | 116.1156 | 198.173 | 21.6482 | 44.6839 | 4.2614 | 145 |  |  | 234.3833 | 0.16773
13236 | 1110.8723 | 10.6718 | 101.095 | 130.6002 | 49.7342 | 15.2003 | 127.69 | 4.3593 |  | 12.4237 | 88.3234 | 12.2317 |  | 116.6408 | 196.3506 | 20.805 | 44.1477 | 4.2228 | 135 |  |  | 223.6188 | 0.21469
13237 | 1101.3463 | 10.176 | 101.4625 | 131.0739 | 52.9728 | 18.9989 | 129.4099 | 4.6693 |  | 12.9518 | 90.0033 | 12.0645 |  | 121.4431 | 205.0525 | 18.9178 | 44.2598 | 4.1654 | 144 |  |  | 226.669 | 0.23622
13238 | 1101.6828 | 12.3029 | 100.9501 | 134.7325 | 55.5178 | 18.0503 | 133.6735 | 4.4987 |  | 13.076 | 90.6951 | 11.9636 |  | 118.1256 | 202.7149 | 11.2504 | 44.5474 | 4.2522 | 135 |  |  | 225.4155 | 0.1599
13239 | 1073.7516 | 9.0572 | 94.6833 | 119.2643 | 52.8507 | 16.1505 | 130.6673 | 4.0312 |  | 13.1 | 90.9016 | 11.698 |  | 96.403 | 190.1962 | 8.3622 | 44.5707 | 4.321 | 139 |  |  | 221.077 | 0.20171
13240 | 1028.0399 | 5.4527 | 68.0722 | 105.5953 | 58.6534 | 10.4516 | 104.268 | 3.4147 |  | 12.9438 | 89.6541 | 9.5085 |  | 72.8943 | 176.4713 | 8.4911 | 42.4499 | 4.3081 | 142 |  |  | 198.4955 | 0.24863
13241 | 1022.9656 | 4.211 | 58.6126 | 101.2964 | 59.4309 | 7.6008 | 71.6066 | 2.1722 |  | 11.6405 | 81.578 | 8.4411 |  | 68.76 | 165.7529 | 8.0334 | 38.9849 | 4.3457 | 131 |  |  | 158.9169 | 0.28677
13242 | 998.1092 | 2.8841 | 56.8824 | 97.2605 | 54.7532 | 7.6 | 54.9281 | 1.2747 |  | 8.0134 | 66.5452 | 7.2082 |  | 60.5765 | 157.5508 | 6.6997 | 36.3784 | 3.9036 | 136 |  |  | 148.753 | 0.2676
13243 | 975.7924 | 2.3672 | 50.5275 | 95.8697 | 54.7875 | 7.6021 | 49.5273 | 1.5263 |  | 6.267 | 61.338 | 4.9833 |  | 49.8366 | 150.9043 | 7.9213 | 35.6052 | 3.1284 | 115 |  |  | 127.0611 | 0.21762
13244 | 954.3263 | 2.3337 | 31.9371 | 94.1464 | 53.3114 | 9.4974 | 58.7535 | 1.2761 |  | 5.1855 | 55.8802 | 3.8387 |  | 46.2642 | 140.4156 | 6.8386 | 34.512 | 2.8232 | 108 |  |  | 118.0108 | 0.051595
13245 | 926.8295 | 3.0855 | 22.6961 | 94.6737 | 47.0966 | 8.5503 | 52.1614 | 1.8804 |  | 4.7585 | 45.2693 | 3.6781 |  | 44.7368 | 118.9801 | 6.6258 | 34.2289 | 2.8044 | 113 |  |  | 118.1341 | 0.00077222
13246 | 911.7977 | 3.4189 | 21.7892 | 99.2041 | 35.8242 | 8.5524 | 52.968 | 1.8438 |  | 5.3253 | 40.5408 | 4.7383 |  | 42.7437 | 111.7055 | 7.6484 | 34.5722 | 2.8561 | 104 |  |  | 119.7064 | 0
13247 | 286.1588 | 1.1936 | 6.3822 | 28.4851 | 16.3948 | 0 | 17.7697 | 0.54258 |  | 1.8525 | 14.06 | 1.7217 |  | 12.3854 | 38.3213 | 2.3033 | 9.967 | 0.97122 | 105 |  |  | 12.8878 | 0
13248 | 894.0306 | 2.3529 | 21.4842 | 103.7443 | 30.5217 | 8.5503 | 52.8667 | 2.4905 |  | 9.576 | 40.4446 | 6.6342 |  | 42.0386 | 121.4726 | 11.2904 | 35.876 | 2.6819 | 101 | 0 | 0 | 117.4328 | 0
13249 | 894.1322 | 2.2664 | 21.7709 | 103.7065 | 26.5556 | 9.4997 | 50.1114 | 2.0498 |  | 10.1917 | 39.4855 | 6.5167 |  | 44.8718 | 116.0911 | 11.4118 | 35.9076 | 2.6365 | 96 | 0 | 0 | 118.2339 | 0
13250 | 885.531 | 2.257 | 21.7522 | 103.2449 | 28.985 | 9.5 | 53.6718 | 1.9015 |  | 10.1769 | 38.3339 | 8.1285 |  | 48.3542 | 113.5044 | 12.4135 | 35.3595 | 2.6427 | 98 | 0 | 0 | 115.5298 | 0
13251 | 885.5651 | 2.2522 | 21.5214 | 101.5009 | 32.2414 | 8.5503 | 49.7118 | 2.4267 |  | 9.1913 | 36.8827 | 12.6067 |  | 48.4156 | 110.4634 | 11.3876 | 35.0086 | 2.6084 | 97 | 0 | 0 | 120.3368 | 0
13252 | 884.6992 | 2.3197 | 21.1788 | 99.5306 | 31.3483 | 11.3992 | 49.3942 | 1.798 |  | 8.4501 | 35.2727 | 10.9828 |  | 46.8006 | 108.5724 | 10.8552 | 34.6305 | 2.4799 | 95 | 0 | 0 | 122.3988 | 0
13253 | 894.714 | 3.6658 | 34.9019 | 99.0099 | 29.2344 | 10.4503 | 49.2878 | 2.0393 |  | 10.6556 | 35.0557 | 6.1361 |  | 45.618 | 109.0622 | 7.5004 | 34.5833 | 2.4141 | 95 | 0 | 0 | 135.7958 | 0.12244
13254 | 919.6872 | 5.7517 | 48.7515 | 98.2263 | 28.5134 | 10.45 | 67.2939 | 1.6782 |  | 14.1687 | 39.9164 | 10.4165 |  | 54.1553 | 119.2222 | 7.3781 | 34.7759 | 2.4498 | 122 | 0 | 0 | 156.6763 | 0.17446
13255 | 955.3542 | 8.5171 | 70.2204 | 99.4679 | 28.5895 | 13.2992 | 102.4586 | 2.2502 |  | 16.0245 | 62.234 | 19.0133 |  | 72.8571 | 139.7509 | 7.1069 | 36.8569 | 4.8331 | 139 | 0 | 0 | 177.5723 | 0.22397
13256 | 1002.4202 | 6.6294 | 83.6619 | 112.1242 | 29.5431 | 16.1492 | 120.0357 | 3.4804 |  | 14.8235 | 78.2081 | 15.0455 |  | 94.4632 | 170.5588 | 10.4242 | 40.4466 | 8.3058 | 143 | 26.7868 | 23.5555 | 208.0155 | 0.29013
13257 | 1058.2707 | 6.9149 | 90.0783 | 121.952 | 31.6012 | 18.0495 | 126.0443 | 3.7669 |  | 14.1802 | 85.6032 | 17.3688 |  | 106.3841 | 187.7441 | 18.0005 | 42.7749 | 5.6259 | 148 | 27.063 | 26.3713 | 221.0938 | 0.32315
13258 | 1110.9939 | 6.9642 | 92.5879 | 126.792 | 37.2537 | 16.1505 | 132.5955 | 4.6092 |  | 14.1705 | 89.4025 | 19.837 |  | 111.5738 | 198.4384 | 21.917 | 44.1885 | 3.8461 | 149 | 21.7941 | 24.1111 | 220.553 | 0.31423
13259 | 1130.2908 | 5.1743 | 98.2235 | 126.532 | 38.3006 | 18.0495 | 134.1723 | 4.2224 |  | 14.2107 | 89.9014 | 19.6673 |  | 114.2932 | 203.8252 | 20.8929 | 48.5736 | 3.8114 | 151 | 16.8444 | 25.859 | 219.3715 | 0.25981
13260 | 1128.6946 | 9.1849 | 104.4885 | 129.8807 | 44.9998 | 16.1505 | 131.2292 | 4.5417 |  | 15.0141 | 78.4885 | 20.7004 |  | 115.3633 | 196.3516 | 20.857 | 49.2013 | 5.2632 | 148 | 14.0299 | 28.7246 | 211.0095 | 0.27985
13261 | 1112.6115 | 9.6391 | 105.2585 | 129.5296 | 48.4624 | 18.9992 | 130.2541 | 4.4296 |  | 14.7746 | 64.5451 | 20.7422 |  | 119.6038 | 203.568 | 17.8266 | 49.5498 | 5.885 | 152 | 16.2057 | 27.7982 | 218.5342 | 0.29177
13262 | 1109.9311 | 8.8667 | 105.2692 | 130.6257 | 53.9216 | 18.0503 | 130.3517 | 3.7327 |  | 14.3607 | 71.9968 | 20.2453 |  | 118.2299 | 206.7417 | 11.1848 | 49.8193 | 5.2535 | 147 | 20.9293 | 21.6618 | 202.5784 | 0.27554
13263 | 1078.7995 | 10.9726 | 95.9053 | 117.8969 | 51.8642 | 17.1003 | 128.1698 | 3.6502 |  | 14.3593 | 86.6098 | 17.5402 |  | 95.0122 | 201.8098 | 7.9714 | 47.5863 | 4.7547 | 142 | 14.6134 | 25.7364 | 201.3188 | 0.30488
13264 | 1018.9706 | 8.2564 | 70.4229 | 105.7317 | 56.0207 | 8.5524 | 106.8162 | 3.7781 |  | 14.194 | 87.6417 | 10.8957 |  | 73.8224 | 190.0711 | 8.628 | 42.8019 | 4.2523 | 144 | 16.2669 | 27.3406 | 183.5951 | 0.2488
13265 | 981.4645 | 4.7135 | 60.9624 | 102.3158 | 54.629 | 8.55 | 72.9034 | 2.9284 |  | 13.082 | 80.0875 | 8.5642 |  | 63.5087 | 167.7003 | 7.0151 | 37.4321 | 4.1256 | 145 | 14.1615 | 20.9747 | 153.3085 | 0.24734
13266 | 973.9151 | 7.315 | 58.79 | 98.7947 | 55.2446 | 6.6505 | 58.8993 | 2.3913 |  | 8.6375 | 65.4928 | 7.7792 |  | 51.6175 | 149.9414 | 6.8198 | 30.0028 | 3.8999 | 151 | 16.6437 | 25.9099 | 138.2817 | 0.21446
13267 | 954.811 | 5.0755 | 52.3932 | 96.8148 | 45.6664 | 9.4992 | 53.8413 | 2.0616 |  | 7.3752 | 59.4913 | 5.4323 |  | 45.8836 | 139.4983 | 8.1207 | 27.0195 | 3.3328 | 138 | 20.8384 | 26.7077 | 123.8649 | 0.20859
13268 | 916.0172 | 2.7139 | 35.057 | 95.2417 | 45.6507 | 7.6005 | 50.4895 | 1.7317 |  | 7.76 | 54.5031 | 4.3833 |  | 43.8255 | 119.4538 | 7.0307 | 26.2276 | 3.0321 | 123 | 21.2361 | 19.0746 | 109.3339 | 0.10775
13269 | 898.8867 | 3.4954 | 26.0006 | 94.6008 | 43.7621 | 6.6503 | 54.0369 | 2.1474 |  | 7.8713 | 42.7685 | 4.4311 |  | 41.6205 | 113.9038 | 7.1917 | 26.2036 | 3.0346 | 120 | 21.9161 | 22.9647 | 111.5402 | 0.0057002
13270 | 887.9605 | 3.4511 | 25.2035 | 95.7208 | 34.2436 | 9.4992 | 53.6001 | 1.9082 |  | 9.4713 | 39.1248 | 6.2535 |  | 40.844 | 115.245 | 6.8301 | 26.3354 | 3.1274 | 110 | 24.9998 | 23.1246 | 109.7094 | 0
13271 | 277.2278 | 0 | 7.2534 | 0 | 16.83 | 0.00264 | 16.6938 | 0.55559 |  | 3.3855 | 13.9111 | 2.3266 |  | 0 | 0 | 1.8293 | 0 | 1.0647 | 110 | 2.4529 | 3.0586 | 11.3844 | 0
13272 | 887.9882 | 2.4203 | 25.1847 | 96.7408 | 35.1929 | 10.4489 | 53.0482 | 1.5898 |  | 12.2627 | 37.9811 | 6.4368 |  | 41.8986 | 116.0088 | 11.1673 | 26.8392 | 2.9989 | 109 | 26.1505 | 23.1125 | 112.4003 | 0
13273 | 902.9704 | 2.3627 | 25.2592 | 96.4655 | 33.977 | 9.5003 | 52.3311 | 1.747 |  | 12.265 | 39.8811 | 6.3143 |  | 43.8301 | 117.1616 | 11.6509 | 26.3739 | 2.9947 | 103 | 25.1117 | 18.9119 | 111.8476 | 0
13274 | 873.7689 | 2.2962 | 25.3089 | 96.2258 | 30.5087 | 7.6005 | 48.6462 | 2.4286 |  | 12.0853 | 45.1299 | 7.0441 |  | 46.9993 | 115.2423 | 12.171 | 26.4594 | 2.9691 | 105 | 25.0632 | 22.6677 | 113.1536 | 0
13275 | 875.4926 | 2.5174 | 25.1928 | 96.9584 | 28.5967 | 9.4995 | 50.6626 | 2.0046 |  | 12.1015 | 43.6705 | 9.5223 |  | 47.8729 | 111.9433 | 11.2974 | 26.4675 | 2.9745 | 105 | 24.4102 | 24.1291 | 113.1308 | 0
13276 | 872.4242 | 2.4402 | 30.6565 | 94.5404 | 33.1458 | 7.6005 | 49.5741 | 1.5133 |  | 10.9619 | 36.077 | 8.0009 |  | 46.5762 | 103.2224 | 8.6423 | 25.818 | 2.8843 | 103 | 24.9303 | 18.3349 | 120.169 | 0
13277 | 896.4067 | 5.1201 | 45.5814 | 93.434 | 39.1754 | 7.6 | 60.0058 | 1.3491 |  | 12.75 | 33.4652 | 5.3411 |  | 45.8893 | 106.7361 | 7.3217 | 25.6638 | 2.8027 | 100 | 24.0223 | 29.4626 | 123.7704 | 0.13822
13278 | 934.8228 | 6.9705 | 54.3396 | 95.9911 | 43.7555 | 8.5497 | 80.6036 | 1.9877 |  | 14.9096 | 38.4806 | 10.8193 |  | 56.0667 | 119.4171 | 7.2318 | 26.3178 | 2.7769 | 125 | 24.184 | 19.805 | 145.5343 | 0.20977
13279 | 968.7468 | 9.113 | 82.0113 | 97.786 | 37.6478 | 17.0976 | 110.4016 | 2.3019 |  | 14.0816 | 58.2974 | 21.3466 |  | 73.5582 | 143.7376 | 8.1079 | 28.3286 | 3.0637 | 144 | 31.6379 | 20.1702 | 172.8704 | 0.264
13280 | 1019.1405 | 6.7792 | 98.5049 | 111.6682 | 42.422 | 18.9995 | 122.0333 | 3.2084 |  | 12.9901 | 70.5514 | 21.7733 |  | 93.4454 | 162.5676 | 10.3459 | 31.1261 | 3.6716 | 159 | 33.5009 | 24.6897 | 208.765 | 0.29816
13281 | 1048.2592 | 4.9982 | 101.842 | 122.4599 | 49.2167 | 19 | 133.4829 | 3.5865 |  | 12.7131 | 80.331 | 20.8116 |  | 104.6943 | 180.4483 | 17.5625 | 33.3754 | 3.8273 | 155 | 27.9678 | 26.6507 | 223.4012 | 0.26412
13282 | 1055.5686 | 4.2547 | 101.231 | 128.807 | 49.4343 | 18.0503 | 138.5243 | 3.7605 |  | 12.6098 | 86.8642 | 16.8744 |  | 108.9214 | 194.9143 | 20.906 | 42.6863 | 3.8118 | 160 | 23.369 | 21.575 | 223.7184 | 0.25794
13283 | 1053.2619 | 4.3874 | 103.411 | 130.293 | 48.0412 | 17.1003 | 140.3326 | 3.6695 |  | 12.8335 | 87.8079 | 16.2099 |  | 109.1583 | 195.9419 | 20.0051 | 45.5299 | 3.7639 | 158 | 20.2611 | 26.495 | 225.0209 | 0.26647
13284 | 1032.5003 | 7.0302 | 104.4861 | 136.0353 | 52.5152 | 18.0497 | 141.8835 | 4.0282 |  | 13.2089 | 85.6449 | 18.709 |  | 110.1592 | 190.27 | 19.9078 | 45.7877 | 3.7738 | 149 | 15.2821 | 23.6735 | 220.0444 | 0.28125
13285 | 1037.3669 | 8.2572 | 103.6717 | 134.2711 | 59.2663 | 18.05 | 146.5582 | 4.3098 |  | 13.2285 | 85.839 | 15.2115 |  | 110.1325 | 194.9841 | 17.027 | 46.5881 | 3.7761 | 152 | 12.5035 | 24.1304 | 217.6032 | 0.19796
13286 | 1041.7324 | 6.9264 | 104.033 | 130.5983 | 59.7987 | 17.1003 | 139.6596 | 4.2334 |  | 13.1977 | 87.9035 | 17.9506 |  | 109.8795 | 200.084 | 9.8799 | 46.1621 | 3.7695 | 153 | 25.4412 | 26.7076 | 205.8949 | 0.2168
13287 | 1051.996 | 5.1055 | 96.719 | 114.3007 | 56.7989 | 15.2005 | 130.4897 | 3.9865 |  | 13.1753 | 89.0418 | 17.4323 |  | 91.099 | 192.6637 | 7.2395 | 48.7653 | 3.851 | 143 | 29.3168 | 20.9242 | 196.2784 | 0.23517
13288 | 1023.0324 | 3.9905 | 71.6358 | 103.0226 | 54.3559 | 11.4011 | 108.5904 | 2.9106 |  | 13.0245 | 86.3511 | 15.0702 |  | 68.6829 | 183.7482 | 7.0807 | 48.6692 | 4.0196 | 142 | 22.5432 | 24.8938 | 173.7822 | 0.11524
13289 | 966.559 | 3.4222 | 56.7 | 102.0222 | 54.1425 | 8.5508 | 76.7427 | 1.6875 |  | 11.3533 | 76.948 | 14.6116 |  | 60.7309 | 162.3512 | 6.9054 | 46.7778 | 3.9592 | 133 | 19.0035 | 22.6223 | 137.7814 | 0.071622
13290 | 941.9728 | 2.625 | 38.684 | 100.1451 | 51.6898 | 6.6505 | 59.8709 | 1.3065 |  | 7.6654 | 60.7694 | 9.615 |  | 51.6309 | 155.694 | 7.1783 | 44.702 | 3.6608 | 137 | 22.7955 | 20.3117 | 129.2824 | 0.049748
13291 | 902.4381 | 2.128 | 28.8259 | 99.5596 | 44.4876 | 7.5997 | 58.4185 | 1.0985 |  | 6.3506 | 47.9479 | 5.4269 |  | 46.6612 | 143.5729 | 7.0694 | 43.3852 | 3.0133 | 118 | 23.5921 | 24.1497 | 112.9727 | 0.08812
13292 | 875.786 | 2.1198 | 27.2723 | 97.6464 | 40.7249 | 7.6 | 58.1418 | 0.99369 |  | 5.5387 | 40.4758 | 4.1573 |  | 44.6546 | 132.0751 | 6.4798 | 41.3577 | 2.7053 | 118 | 23.5598 | 20.6183 | 107.3389 | 0.013542
13293 | 869.5638 | 3.2258 | 27.1932 | 94.5735 | 32.6054 | 9.4995 | 53.5285 | 1.2868 |  | 5.0282 | 38.0871 | 4.2065 |  | 41.6355 | 118.1576 | 6.5557 | 40.6818 | 2.6132 | 120 | 24.3749 | 22.6188 | 104.1421 | 0.00038611
13294 | 874.2688 | 3.5378 | 27.5742 | 95.8686 | 31.7511 | 7.6005 | 55.3222 | 1.3925 |  | 6.7934 | 38.5777 | 6.069 |  | 41.4886 | 118.6862 | 7.3907 | 41.1204 | 2.7457 | 119 | 27.33 | 25.4495 | 106.591 | 0
13295 | 274.7285 | 1.1959 | 7.9884 | 26.8381 | 16.1412 | 0.002112 | 18.0797 | 0.45618 |  | 2.5251 | 13.5306 | 2.2486 |  | 12.1445 | 41.2567 | 2.1629 | 11.7015 | 0.94766 | 109 | 2.6919 | 3.451 | 11.1725 | 0
13296 | 879.7941 | 3.1586 | 27.6146 | 96.2961 | 39.1696 | 8.5497 | 54.197 | 1.9124 |  | 7.7587 | 38.9829 | 6.9043 |  | 38.8337 | 115.6024 | 10.8872 | 41.8698 | 2.6761 | 109 | 31.5541 | 23.7073 | 110.6849 | 0
13297 | 877.561 | 3.0042 | 27.7842 | 96.7591 | 36.4262 | 10.4495 | 50.6734 | 1.6182 |  | 7.9386 | 38.3955 | 7.0631 |  | 39.2499 | 115.7301 | 11.0207 | 42.2761 | 2.7103 | 103 | 30.0601 | 22.9348 | 111.0804 | 0
13298 | 861.5685 | 2.4978 | 27.7331 | 96.4302 | 34.248 | 10.45 | 46.7753 | 1.8301 |  | 7.7806 | 38.2874 | 7.1429 |  | 39.6398 | 115.2798 | 11.7851 | 42.0669 | 2.6246 | 102 | 28.503 | 20.2715 | 111.2024 | 0
13299 | 866.3402 | 2.2647 | 27.3024 | 96.5041 | 35.3192 | 9.5003 | 55.4297 | 1.6922 |  | 7.5582 | 38.2338 | 7.0122 |  | 38.3542 | 110.9783 | 11.3505 | 41.419 | 2.5375 | 98 | 28.3538 | 23.7857 | 109.4184 | 0
13300 | 865.6761 | 2.6837 | 32.832 | 95.422 | 33.5825 | 9.5 | 53.9712 | 1.5113 |  | 6.496 | 36.7841 | 6.0692 |  | 37.8858 | 110.0221 | 9.4643 | 40.8889 | 2.481 | 96 | 27.8944 | 21.6562 | 110.0075 | 0
13301 | 871.6324 | 3.2268 | 32.5239 | 94.3782 | 37.3128 | 5.7011 | 55.5519 | 2.0228 |  | 5.1924 | 35.4151 | 4.2825 |  | 36.7712 | 106.1872 | 6.7499 | 40.978 | 2.3617 | 90 | 27.1929 | 21.4629 | 110.0913 | 0.11828
13302 | 888.6965 | 2.9367 | 28.5649 | 94.3743 | 35.0428 | 6.6497 | 53.3484 | 1.6388 |  | 4.75 | 37.7004 | 3.6252 |  | 36.258 | 108.5987 | 6.9773 | 40.87 | 2.3569 | 93 | 25.7031 | 23.9713 | 111.114 | 0.14381
13303 | 897.3489 | 2.1469 | 27.1937 | 93.3187 | 31.7248 | 7.5997 | 50.8299 | 1.324 |  | 4.7794 | 42.2693 | 3.6727 |  | 37.5713 | 106.1305 | 6.9567 | 40.8566 | 2.4575 | 88 | 27.1916 | 21.33 | 108.5831 | 0.21428
13304 | 899.0257 | 2.1326 | 26.9835 | 103.0941 | 31.0386 | 9.4995 | 53.9407 | 1.3867 |  | 4.7993 | 38.5803 | 3.6928 |  | 37.2074 | 108.1776 | 9.1391 | 40.6938 | 2.5382 | 90 | 31.4704 | 22.5855 | 108.5165 | 0.2931
13305 | 938.5478 | 2.3767 | 36.1425 | 113.3075 | 32.7535 | 8.5503 | 55.7734 | 1.8888 |  | 6.0682 | 39.0594 | 3.6486 |  | 38.8257 | 108.2792 | 16.1874 | 40.484 | 2.9874 | 95 | 33.0546 | 24.4995 | 107.778 | 0.19406
13306 | 943.4929 | 2.4791 | 49.8586 | 116.2372 | 37.4555 | 9.4997 | 52.2472 | 2.0102 |  | 9.6732 | 43.3765 | 3.632 |  | 38.9889 | 112.4594 | 18.744 | 40.4691 | 3.0217 | 98 | 30.3325 | 21.1196 | 110.5183 | 0.32251
13307 | 940.7313 | 3.3718 | 53.2677 | 116.0807 | 36.8991 | 9.5 | 51.7836 | 2.2716 |  | 11.5402 | 46.5485 | 3.6669 |  | 42.7075 | 113.2032 | 19.0477 | 41.5701 | 2.789 | 99 | 27.9935 | 21.0707 | 109.6047 | 0.2689
13308 | 947.5819 | 3.3245 | 52.8265 | 115.5882 | 39.064 | 10.4497 | 49.7183 | 1.8743 |  | 11.6234 | 52.3457 | 3.6159 |  | 46.2977 | 111.4497 | 19.738 | 41.7423 | 2.7208 | 100 | 24.5074 | 23.1708 | 111.866 | 0.2842
13309 | 934.6073 | 2.5645 | 47.5083 | 115.8188 | 47.1569 | 6.6511 | 52.5506 | 1.5739 |  | 12.5766 | 55.5495 | 3.8715 |  | 46.2709 | 103.3949 | 16.1643 | 41.7404 | 2.7059 | 101 | 19.6675 | 18.1376 | 112.1461 | 0.23797
13310 | 909.4175 | 4.7083 | 30.8906 | 116.4397 | 42.2414 | 6.65 | 54.1043 | 1.5881 |  | 13.1638 | 56.2014 | 4.0347 |  | 44.6465 | 109.3072 | 9.3751 | 41.3909 | 2.7264 | 128 | 21.9358 | 21.4832 | 111.2652 | 0.14597
13311 | 913.2895 | 5.9378 | 22.3098 | 103.5185 | 33.3938 | 9.4992 | 63.1738 | 1.6042 |  | 11.9844 | 56.2822 | 3.9597 |  | 43.9822 | 121.2805 | 6.3226 | 41.7769 | 2.8515 | 121 | 17.1699 | 22.8975 | 110.3898 | 0.1861
13312 | 905.8301 | 5.2536 | 20.8365 | 96.0823 | 38.8966 | 6.6508 | 55.013 | 1.3874 |  | 7.8546 | 55.0809 | 9.911 |  | 42.5508 | 130.0293 | 7.1413 | 41.0748 | 2.9441 | 119 | 10.8318 | 17.6293 | 106.6185 | 0.13186
13313 | 878.3478 | 5.6229 | 20.585 | 92.9485 | 40.5442 | 8.5495 | 49.2122 | 1.438 |  | 6.0503 | 49.1195 | 12.9783 |  | 41.1311 | 129.1681 | 6.5676 | 40.342 | 2.9148 | 121 | 8.5289 | 20.7929 | 103.3239 | 0.094557
13314 | 886.0218 | 6.0224 | 21.1432 | 94.2563 | 45.7705 | 5.7008 | 55.4819 | 1.2136 |  | 5.7886 | 46.6664 | 12.9159 |  | 40.2156 | 134.3101 | 6.8646 | 41.3481 | 2.983 | 124 | 15.1794 | 22.8713 | 106.9444 | 0.066142
13315 | 873.8077 | 4.9162 | 21.0037 | 94.6552 | 44.1943 | 5.7 | 59.1686 | 1.04 |  | 5.0193 | 44.1494 | 11.4838 |  | 39.7097 | 126.0224 | 7.0257 | 41.5677 | 3.0064 | 120 | 20.1877 | 17.1406 | 107.8787 | 0.041882
13316 | 871.899 | 3.2774 | 21.14 | 94.1884 | 37.1354 | 8.5492 | 57.4625 | 1.7955 |  | 5.3159 | 38.2456 | 6.7082 |  | 37.3269 | 123.5404 | 6.8342 | 40.9781 | 2.971 | 129 | 22.0554 | 21.7449 | 108.4904 | 0.015022
13317 | 865.9851 | 3.9943 | 21.3522 | 94.601 | 40.9896 | 9.4997 | 55.6211 | 1.5878 |  | 5.3536 | 35.6845 | 4.3616 |  | 37.6822 | 134.644 | 6.998 | 41.1475 | 2.893 | 137 | 23.6028 | 23.1279 | 103.7142 | 0.00038611
13318 | 860.648 | 6.1479 | 21.3577 | 97.5973 | 38.1747 | 8.5503 | 50.5708 | 1.5586 |  | 6.4417 | 35.8166 | 6.2381 |  | 39.1663 | 123.6661 | 7.3156 | 41.0849 | 2.8937 | 140 | 27.7612 | 18.4798 | 111.9402 | 0
13319 | 268.6089 | 2.4402 | 6.1676 | 27.6519 | 16.6219 | 0.002376 | 15.3064 | 0.55844 |  | 2.3148 | 12.4802 | 2.3656 |  | 11.5114 | 39.0229 | 2.0888 | 11.6662 | 0.97296 | 108 | 2.7808 | 2.3645 | 11.0688 | 0
13320 | 830.4555 | 4.2723 | 21.7755 | 97.1174 | 30.8864 | 8.55 | 53.8981 | 2.3733 |  | 7.6321 | 36.8245 | 7.2479 |  | 39.9703 | 113.9482 | 7.273 | 42.0827 | 2.948 | 109 | 35.641 | 22.4237 | 110.3969 | 0
13321 | 832.3045 | 3.1463 | 21.803 | 96.6988 | 26.647 | 11.3992 | 55.0368 | 2.3333 |  | 7.6268 | 37.5642 | 6.9919 |  | 39.3867 | 113.8744 | 7.5694 | 42.0223 | 2.9396 | 107 | 33.4378 | 17.0969 | 112.2182 | 0
13322 | 821.6927 | 2.6835 | 21.7076 | 97.9712 | 34.0876 | 8.5508 | 53.4878 | 2.0644 |  | 7.6069 | 37.8245 | 6.9622 |  | 39.074 | 118.9234 | 6.8287 | 41.8631 | 2.9505 | 108 | 32.2776 | 21.7925 | 114.1337 | 0
13323 | 823.3321 | 2.3329 | 21.7039 | 97.0941 | 39.6922 | 8.55 | 56.6431 | 2.2199 |  | 6.8555 | 37.3656 | 6.4541 |  | 38.2828 | 120.7594 | 7.1834 | 41.6283 | 2.9328 | 101 | 32.0706 | 22.4394 | 114.5349 | 0
13324 | 819.84 | 2.3992 | 21.055 | 94.2419 | 42.7318 | 7.6003 | 56.646 | 1.6376 |  | 5.3022 | 35.9714 | 4.7682 |  | 36.7933 | 117.0712 | 7.4516 | 41.5147 | 2.8115 | 100 | 32.1371 | 16.9935 | 109.6234 | 0
13325 | 826.6507 | 2.6757 | 21.2114 | 93.1242 | 41.0596 | 8.5497 | 50.6774 | 2.0668 |  | 4.7666 | 35.2842 | 4.3078 |  | 36.4019 | 112.1817 | 6.3807 | 41.6721 | 2.7641 | 98 | 30.1278 | 27.6038 | 108.0534 | 0.049858
13326 | 833.2617 | 2.3883 | 21.1763 | 92.9935 | 38.4397 | 10.4495 | 53.4206 | 1.7008 |  | 4.7613 | 37.7048 | 4.1819 |  | 37.4683 | 108.8718 | 6.8986 | 41.6022 | 2.7726 | 95 | 25.944 | 17.8861 | 109.1214 | 0.084689
13327 | 842.3939 | 2.123 | 21.0899 | 92.9887 | 37.8856 | 10.45 | 52.9119 | 1.3477 |  | 4.7439 | 42.1566 | 4.1916 |  | 38.7831 | 107.5184 | 7.0341 | 41.3231 | 2.8891 | 90 | 22.4015 | 18.8054 | 108.1799 | 0.13892
13328 | 844.1251 | 1.9491 | 21.0833 | 102.6427 | 42.3992 | 6.6511 | 53.3118 | 1.5166 |  | 4.7405 | 38.6098 | 5.0338 |  | 38.2435 | 107.2083 | 9.3924 | 41.0591 | 2.8991 | 93 | 16.5287 | 18.3282 | 109.4241 | 0.23774
13329 | 852.1659 | 1.8576 | 20.8749 | 111.4879 | 39.982 | 9.4992 | 53.952 | 1.6899 |  | 6.3883 | 35.5583 | 4.6164 |  | 38.6684 | 112.0212 | 16.54 | 40.8317 | 2.8933 | 96 | 9.4353 | 22.2464 | 110.4166 | 0.21616
13330 | 870.3122 | 2.4034 | 20.704 | 113.7097 | 42.7445 | 8.5503 | 48.8922 | 1.4829 |  | 10.1743 | 35.8517 | 4.0997 |  | 40.6489 | 120.181 | 18.7021 | 40.4433 | 2.8764 | 97 | 5.6597 | 19.853 | 109.899 | 0.32546
13331 | 869.3731 | 3.5793 | 20.8782 | 114.4664 | 45.0848 | 8.55 | 48.7978 | 1.2346 |  | 11.5838 | 43.7859 | 4.3127 |  | 41.8813 | 120.7591 | 19.2042 | 40.5536 | 2.9341 | 96 | 7.3217 | 19.2929 | 107.9254 | 0.26417
13332 | 870.3315 | 7.76 | 21.095 | 114.5846 | 47.558 | 8.55 | 49.4439 | 1.0905 |  | 12.3858 | 54.8294 | 4.1357 |  | 44.0185 | 120.2421 | 19.3576 | 40.7867 | 2.9745 | 106 | 9.459 | 22.1076 | 106.0899 | 0.27585
13333 | 874.0803 | 7.1568 | 21.1009 | 114.8965 | 49.5271 | 8.55 | 52.018 | 1.0586 |  | 12.3744 | 58.6985 | 4.0313 |  | 45.2226 | 117.1145 | 16.0342 | 41.2458 | 3.1053 | 102 | 15.32 | 20.168 | 108.9879 | 0.30166
13334 | 872.7567 | 3.8315 | 21.4023 | 116.0847 | 51.1433 | 7.6003 | 55.3124 | 1.0408 |  | 12.1083 | 59.4195 | 4.0906 |  | 45.349 | 134.0157 | 9.3678 | 40.9448 | 3.1426 | 107 | 8.2573 | 18.9362 | 106.1488 | 0.30935
13335 | 861.775 | 3.0532 | 21.3604 | 102.4791 | 51.0104 | 7.6 | 57.8025 | 1.0407 |  | 11.1413 | 60.7252 | 4.023 |  | 43.7069 | 135.6925 | 7.0162 | 40.2674 | 3.1146 | 106 | 9.4896 | 21.9744 | 110.4669 | 0.31329
13336 | 853.4213 | 7.1735 | 20.9863 | 92.6426 | 44.275 | 8.5497 | 53.0561 | 1.3466 |  | 7.5732 | 59.3005 | 4.8211 |  | 43.1965 | 131.6848 | 6.5988 | 39.6429 | 3.0814 | 109 | 4.8882 | 21.0646 | 108.8292 | 0.2617
13337 | 865.4116 | 8.3875 | 21.1274 | 92.9839 | 43.6943 | 6.6505 | 49.6328 | 1.225 |  | 6.1006 | 55.8536 | 4.9816 |  | 43.909 | 128.8802 | 6.4156 | 40.0606 | 3.0188 | 107 | 10.3674 | 17.8146 | 104.5905 | 0.28416
13338 | 850.3348 | 8.4415 | 21.4864 | 94.8285 | 48.3052 | 7.5997 | 54.0986 | 1.1041 |  | 6.1568 | 48.6998 | 5.0373 |  | 42.2223 | 129.5119 | 6.9439 | 40.987 | 2.999 | 101 | 16.77 | 21.9438 | 108.0237 | 0.25903
13339 | 842.7236 | 9.3652 | 21.3352 | 93.7809 | 41.3541 | 7.6 | 57.6492 | 1.0892 |  | 5.4656 | 41.4692 | 5.0478 |  | 39.8982 | 120.847 | 6.7281 | 40.6434 | 2.9812 | 98 | 20.7467 | 21.4675 | 107.7435 | 0.21498
13340 | 861.5665 | 9.5898 | 21.2855 | 94.0619 | 45.8766 | 6.6503 | 51.6946 | 1.0707 |  | 5.3088 | 38.5526 | 4.2612 |  | 39.0214 | 121.9205 | 6.8059 | 40.2782 | 2.9597 | 99 | 23.4767 | 17.6579 | 106.3608 | 0.10158
13341 | 865.6883 | 10.3979 | 21.3781 | 93.4795 | 48.5617 | 8.5495 | 49.566 | 1.8206 |  | 4.9917 | 37.9936 | 6.1212 |  | 38.55 | 120.8142 | 6.6178 | 40.7556 | 2.9658 | 94 | 25.9885 | 21.722 | 104.8756 | 0.0036237
13342 | 860.1037 | 8.0145 | 21.426 | 94.7023 | 40.2602 | 7.6003 | 51.0876 | 1.7915 |  | 5.6457 | 38.174 | 13.3923 |  | 39.4911 | 123.3641 | 6.9363 | 41.2622 | 2.9631 | 97 | 28.1928 | 23.6772 | 106.6928 | 0
13343 | 263.788 | 2.2462 | 6.0864 | 26.1838 | 16.9929 | 0.002112 | 16.079 | 0.51995 |  | 1.9591 | 13.1244 | 5.2412 |  | 11.4183 | 41.8484 | 1.9711 | 11.5665 | 0.9748 | 96 | 2.7044 | 3.1703 | 10.4584 | 0
13344 | 870.7723 | 2.543 | 21.7285 | 97.6935 | 34.8458 | 10.4497 | 53.711 | 2.5494 |  | 9.4782 | 38.7125 | 17.038 |  | 38.5531 | 126.731 | 10.555 | 42.3619 | 2.9561 | 99 | 37.6862 | 21.9411 | 111.0472 | 0
13345 | 876.0993 | 2.7355 | 25.7445 | 97.3112 | 31.91 | 7.6008 | 52.7687 | 2.0566 |  | 10.1356 | 38.7495 | 10.4006 |  | 42.145 | 127.3967 | 11.3087 | 42.1345 | 2.9535 | 93 | 31.9957 | 20.9556 | 110.0381 | 0
13346 | 868.0076 | 2.5568 | 37.1754 | 97.6711 | 30.097 | 9.4995 | 56.502 | 2.4063 |  | 10.1348 | 38.48 | 8.9824 |  | 46.2382 | 126.4373 | 11.6878 | 42.0122 | 2.9558 | 96 | 31.6333 | 18.2431 | 112.0882 | 0
13347 | 863.3886 | 2.2911 | 41.1797 | 96.8993 | 36.0864 | 8.5503 | 56.4835 | 2.0349 |  | 9.6267 | 38.0913 | 14.4313 |  | 48.1853 | 119.7799 | 11.75 | 42.1816 | 2.9705 | 95 | 32.0989 | 22.1128 | 113.6736 | 0
13348 | 860.7275 | 2.2155 | 35.2507 | 95.5046 | 36.5013 | 10.4495 | 52.6494 | 2.2068 |  | 8.6782 | 36.451 | 12.6803 |  | 45.815 | 114.9745 | 9.8241 | 41.4361 | 2.8158 | 95 | 31.3387 | 20.4641 | 122.3038 | 0
13349 | 857.7499 | 2.2965 | 41.6676 | 95.1366 | 36.135 | 9.5003 | 63.0287 | 1.679 |  | 10.5223 | 35.3085 | 6.9265 |  | 44.9435 | 111.3182 | 7.4773 | 41.2102 | 2.7325 | 92 | 30.0716 | 26.3564 | 129.7402 | 0.11608
13350 | 858.5034 | 3.3368 | 58.9442 | 96.2157 | 38.2573 | 7.6005 | 77.3237 | 1.2773 |  | 12.6336 | 39.8336 | 12.6006 |  | 51.6287 | 126.3592 | 6.9012 | 41.6959 | 2.7451 | 141 | 27.6112 | 17.5314 | 148.347 | 0.18979
13351 | 906.9856 | 4.2884 | 79.3604 | 99.7709 | 31.7185 | 15.1979 | 103.9861 | 1.9912 |  | 11.7002 | 59.4639 | 21.6902 |  | 67.8384 | 147.1096 | 8.3531 | 42.5901 | 5.2405 | 169 | 31.7464 | 18.7856 | 179.1559 | 0.25976
13352 | 942.6288 | 6.0122 | 93.2136 | 110.7707 | 32.2631 | 18.0492 | 119.8452 | 3.5046 |  | 11.3113 | 73.8627 | 15.5882 |  | 85.9505 | 164.9146 | 10.8415 | 44.1561 | 8.8612 | 166 | 29.8587 | 26.2747 | 196.6431 | 0.31625
13353 | 1000.7465 | 5.5419 | 99.0887 | 120.109 | 40.9566 | 16.1505 | 124.8281 | 4.3301 |  | 12.4457 | 82.062 | 11.0505 |  | 95.3168 | 174.0508 | 18.6683 | 47.8608 | 6.2901 | 161 | 21.5659 | 20.7678 | 204.3007 | 0.35562
13354 | 1073.5247 | 4.7947 | 101.3007 | 124.9551 | 47.7181 | 17.0997 | 129.3693 | 4.0345 |  | 13.1478 | 85.6157 | 11.9258 |  | 99.5839 | 192.5901 | 20.838 | 44.4349 | 5.5124 | 157 | 15.9672 | 17.16 | 199.1644 | 0.33109
13355 | 1090.7396 | 4.0889 | 100.1199 | 125.703 | 58.5502 | 15.2005 | 133.3521 | 3.6357 |  | 13.3794 | 86.3707 | 11.3382 |  | 105.029 | 195.2133 | 21.4129 | 39.1638 | 5.1634 | 155 | 17.1803 | 21.0794 | 197.2777 | 0.26424
13356 | 1075.5208 | 3.8553 | 102.0992 | 126.7565 | 58.6106 | 15.2 | 135.1631 | 3.6234 |  | 13.3263 | 85.1895 | 10.6589 |  | 103.9216 | 191.7621 | 21.9834 | 34.6835 | 4.4875 | 161 | 20.6253 | 29.2402 | 194.4163 | 0.27535
13357 | 1058.3438 | 3.9298 | 102.2291 | 124.9797 | 57.0784 | 13.3005 | 134.4768 | 3.5221 |  | 13.1481 | 83.9816 | 10.3968 |  | 102.7948 | 196.1448 | 18.221 | 35.0361 | 4.4606 | 159 | 26.3638 | 25.8872 | 189.897 | 0.29542
13358 | 1059.2145 | 6.0727 | 96.8092 | 126.7837 | 56.6328 | 15.1995 | 134.0678 | 3.6269 |  | 13.0742 | 83.9888 | 9.9465 |  | 110.1678 | 199.137 | 11.774 | 42.1319 | 4.4891 | 165 | 24.5236 | 0 | 193.9068 | 0.29477
13359 | 1053.5778 | 9.9433 | 67.9591 | 113.2043 | 51.9582 | 17.0995 | 131.7627 | 3.5794 |  | 12.8115 | 85.1242 | 10.5387 |  | 94.4011 | 191.8762 | 9.1111 | 44.146 | 4.2801 | 153 | 22.6145 | 26.252 | 186.9185 | 0.30841
13360 | 1016.1334 | 7.8017 | 55.7063 | 101.4803 | 57.3049 | 11.4016 | 110.5737 | 3.1845 |  | 12.3581 | 83.3427 | 9.7054 |  | 80.2678 | 176.6735 | 8.4718 | 42.3325 | 4.0362 | 142 | 21.2777 | 22.1887 | 175.714 | 0.2628
13361 | 1006.5435 | 3.9673 | 55.5386 | 101.0521 | 61.8577 | 8.5532 | 74.3021 | 2.6575 |  | 11.1194 | 76.7249 | 8.7112 |  | 75.7184 | 164.0121 | 7.9951 | 40.8612 | 4.0322 | 135 | 20.7457 | 25.7617 | 146.3594 | 0.28756
13362 | 986.115 | 2.7741 | 53.3075 | 97.6636 | 55.8557 | 8.5476 | 55.9196 | 1.5623 |  | 7.5277 | 62.6781 | 7.5119 |  | 59.4219 | 149.8252 | 7.5529 | 39.6062 | 3.5695 | 133 | 20.8785 | 21.2477 | 131.8259 | 0.26334
13363 | 960.7155 | 2.9451 | 46.0201 | 94.8271 | 53.4244 | 7.6003 | 51.6118 | 1.1545 |  | 6.063 | 57.3225 | 5.0027 |  | 51.4572 | 141.6464 | 7.4192 | 38.3121 | 2.8384 | 120 | 21.8821 | 21.8473 | 117.9542 | 0.22052
13364 | 922.1848 | 2.5384 | 30.1187 | 97.8322 | 51.0957 | 8.5497 | 52.0847 | 1.2496 |  | 5.9991 | 53.0954 | 3.945 |  | 47.2098 | 128.9602 | 7.9724 | 37.0637 | 2.5773 | 104 | 22.3419 | 21.7084 | 110.3096 | 0.11142
13365 | 906.2741 | 3.3878 | 22.0237 | 99.2763 | 47.5512 | 8.55 | 49.0274 | 1.2063 |  | 5.1445 | 42.1658 | 3.9823 |  | 46.5276 | 119.8025 | 7.5377 | 36.7616 | 2.5668 | 104 | 26.0152 | 15.966 | 110.586 | 0
13366 | 883.4062 | 3.5668 | 21.2686 | 101.9263 | 47.6328 | 8.55 | 47.6107 | 1.3223 |  | 6.4513 | 37.644 | 6.4039 |  | 47.0844 | 114.9936 | 8.0704 | 37.5114 | 2.676 | 117 | 26.2913 | 22.0311 | 110.4332 | 0
13367 | 277.8525 | 1.1918 | 6.2497 | 29.0826 | 23.6652 | 0.002376 | 15.3564 | 0.47065 |  | 2.4288 | 13.2752 | 2.497 |  | 13.8879 | 38.9456 | 2.4212 | 10.8705 | 0.92752 | 112 | 2.5174 | 3.1191 | 11.8826 | 0
13368 | 877.6865 | 2.2336 | 20.9057 | 100.2916 | 52.5972 | 7.6 | 49.1425 | 2.2342 |  | 9.3105 | 37.6436 | 6.8364 |  | 48.5832 | 112.5284 | 11.476 | 37.4057 | 2.5348 | 116 | 30.883 | 16.0872 | 112.4187 | 0
13369 | 882.7877 | 2.2273 | 20.8678 | 97.1412 | 47.5891 | 9.4995 | 43.8847 | 1.8785 |  | 9.9682 | 37.0017 | 6.825 |  | 50.9111 | 112.8027 | 12.8074 | 37.5117 | 2.5541 | 100 | 28.8314 | 20.3358 | 112.9972 | 0
13370 | 875.5606 | 2.2276 | 20.9762 | 96.7957 | 49.4867 | 7.6005 | 49.7907 | 1.6108 |  | 9.9802 | 36.6883 | 8.4796 |  | 54.5541 | 114.9703 | 11.7229 | 37.8117 | 2.5415 | 98 | 27.9264 | 21.9429 | 112.4442 | 0
13371 | 879.8802 | 2.2451 | 21.1181 | 95.8103 | 43.5462 | 9.4995 | 50.2425 | 2.369 |  | 9.6023 | 36.1606 | 13.9221 |  | 55.8135 | 112.9699 | 11.3672 | 37.8407 | 2.5389 | 100 | 27.6188 | 15.9144 | 113.3836 | 0
13372 | 889.1828 | 2.4164 | 21.0359 | 94.3741 | 33.1027 | 8.5503 | 49.6757 | 1.8035 |  | 8.7131 | 34.7455 | 12.3323 |  | 53.6083 | 107.8556 | 9.1742 | 37.6746 | 2.4257 | 95 | 31.4265 | 20.8239 | 115.3729 | 0
13373 | 918.2788 | 2.1752 | 29.3448 | 94.8318 | 28.2358 | 9.4997 | 54.8725 | 1.5951 |  | 10.6725 | 34.1966 | 6.7303 |  | 53.0928 | 107.9507 | 7.1168 | 37.662 | 2.345 | 95 | 29.1313 | 20.4636 | 122.7533 | 0.12626
13374 | 940.6171 | 3.4694 | 48.9601 | 98.6096 | 36.1075 | 8.5503 | 71.9696 | 2.1608 |  | 12.7628 | 39.0528 | 11.6393 |  | 58.327 | 116.5294 | 8.2282 | 37.5538 | 2.3317 | 126 | 27.5196 | 16.7503 | 144.3141 | 0.080567
13375 | 879.5986 | 4.4635 | 76.6336 | 99.0103 | 36.6299 | 14.2484 | 104.4483 | 2.51 |  | 12.4034 | 59.5837 | 21.7553 |  | 74.408 | 137.8056 | 8.5145 | 39.8121 | 4.7616 | 170 | 27.1078 | 24.0393 | 173.3455 | 0.092062
13376 | 843.1869 | 6.4105 | 94.4 | 107.3212 | 47.382 | 13.3003 | 121.2297 | 3.1624 |  | 12.4093 | 78.6294 | 15.774 |  | 91.8109 | 164.6532 | 11.0635 | 41.593 | 10.2367 | 159 | 25.66 | 25.7308 | 189.271 | 0.23547
13377 | 893.5681 | 7.6051 | 102.037 | 120.3528 | 55.8468 | 16.1492 | 126.3067 | 3.6625 |  | 12.7305 | 85.572 | 10.7668 |  | 101.3055 | 177.0156 | 18.915 | 43.9248 | 12.4903 | 155 | 30.1334 | 26.2115 | 194.012 | 0.27652
13378 | 925.1445 | 7.6944 | 102.6407 | 125.8949 | 58.9157 | 18.0495 | 130.6859 | 3.7003 |  | 12.5413 | 87.6367 | 10.3543 |  | 105.6886 | 188.1178 | 21.3623 | 45.5877 | 12.7293 | 162 | 23.9256 | 27.9757 | 199.0749 | 0.27303
13379 | 930.9005 | 7.9792 | 105.1996 | 127.6253 | 56.7409 | 17.1003 | 137.934 | 3.5028 |  | 12.4193 | 88.9047 | 10.3947 |  | 109.7469 | 192.407 | 20.7158 | 46.0219 | 12.7647 | 158 | 21.6511 | 27.9927 | 195.5542 | 0.2385
13380 | 953.9475 | 7.8831 | 104.907 | 131.257 | 55.6406 | 19.9492 | 142.6117 | 3.509 |  | 13.9967 | 87.5244 | 10.6001 |  | 111.8154 | 194.548 | 21.1816 | 44.7716 | 12.7195 | 162 | 22.1188 | 28.2639 | 195.9572 | 0.2372
13381 | 982.3606 | 6.3267 | 104.443 | 137.31 | 60.3872 | 18.0505 | 140.0145 | 3.4291 |  | 13.5741 | 87.879 | 10.5622 |  | 113.9112 | 197.303 | 17.2263 | 46.0319 | 12.749 | 158 | 23.7549 | 26.2969 | 193.0137 | 0.29029
13382 | 1003.4046 | 6.9471 | 99.0264 | 139.4721 | 59.3978 | 15.2008 | 135.9218 | 3.808 |  | 12.7688 | 90.2047 | 10.3138 |  | 114.6644 | 199.4239 | 10.7381 | 47.1078 | 10.6592 | 155 | 32.5965 | 27.5031 | 190.578 | 0.28574
13383 | 996.8703 | 6.0447 | 84.8821 | 123.459 | 56.2947 | 13.3005 | 131.2349 | 3.8683 |  | 12.5011 | 91.7859 | 10.1136 |  | 103.706 | 189.1188 | 8.2527 | 48.0738 | 11.0193 | 141 | 38.6659 | 26.4696 | 188.5043 | 0.27456
13384 | 983.452 | 4.5027 | 79.0502 | 108.9319 | 57.9578 | 10.4508 | 112.6156 | 3.2248 |  | 12.4512 | 89.435 | 9.0743 |  | 95.1111 | 181.0951 | 7.6776 | 46.6677 | 12.9636 | 136 | 24.3559 | 24.9088 | 170.4276 | 0.25595
13385 | 955.9495 | 3.3398 | 77.7402 | 100.9655 | 60.331 | 8.5505 | 72.9689 | 2.1489 |  | 10.9721 | 78.588 | 8.322 |  | 83.1826 | 156.166 | 7.4281 | 43.1012 | 10.8935 | 134 | 17.4051 | 27.3678 | 143.1234 | 0.27515
13386 | 956.6759 | 2.7989 | 77.1494 | 97.5873 | 56.3057 | 7.6003 | 54.8546 | 1.2897 |  | 7.4291 | 64.055 | 7.3504 |  | 64.9124 | 145.5672 | 7.051 | 40.8588 | 5.4441 | 132 | 23.2048 | 21.5245 | 131.927 | 0.25579
13387 | 948.4952 | 3.9191 | 71.9303 | 98.3208 | 50.4635 | 10.4492 | 53.4927 | 1.0505 |  | 6.1527 | 58.4681 | 4.8116 |  | 56.646 | 143.0456 | 7.079 | 38.8396 | 2.9398 | 113 | 23.728 | 25.484 | 117.1439 | 0.17277
13388 | 931.4355 | 3.7135 | 54.788 | 99.2138 | 52.4959 | 6.6511 | 52.5493 | 1.2895 |  | 5.9384 | 53.6637 | 3.731 |  | 54.8693 | 135.992 | 7.3081 | 36.9043 | 2.6462 | 122 | 23.3464 | 20.4637 | 109.2326 | 0.11988
13389 | 913.1628 | 5.0102 | 45.7053 | 99.5045 | 46.0554 | 6.65 | 54.1025 | 1.2239 |  | 5.0575 | 42.1479 | 3.7054 |  | 53.7149 | 126.7127 | 7.6825 | 36.7858 | 2.634 | 116 | -5.5079 | 23.4792 | 107.5375 | 0
13390 | 901.1319 | 4.9123 | 45.7115 | 100.3508 | 41.0085 | 7.5997 | 48.4917 | 1.3014 |  | 6.548 | 37.0837 | 5.5053 |  | 54.3423 | 126.4657 | 6.9819 | 36.5054 | 2.657 | 108 | 27.1188 | 23.1346 | 109.1463 | 0
13391 | 281.3297 | 1.5343 | 13.4146 | 28.0983 | 19.7259 | 0.002112 | 14.4256 | 0.45949 |  | 2.4523 | 12.892 | 2.0746 |  | 16.0011 | 43.4148 | 1.8935 | 10.3795 | 0.89457 | 98 | 2.6817 | 3.1045 | 11.3809 | 0
13392 | 855.4098 | 5.797 | 47.408 | 99.5966 | 39.1826 | 7.6 | 48.174 | 2.1327 |  | 9.4598 | 37.1647 | 6.4909 |  | 51.5293 | 122.3411 | 11.6057 | 36.9937 | 2.5939 | 95 | 27.0117 | 23.6174 | 112.741 | 0
13393 | 848.758 | 6.0412 | 51.5203 | 99.3597 | 37.0138 | 8.5497 | 49.1084 | 1.8911 |  | 9.9946 | 37.0966 | 6.424 |  | 55.3591 | 117.0979 | 11.9598 | 37.2585 | 2.6121 | 95 | 25.3237 | 21.7739 | 113.6332 | 0
13394 | 832.9652 | 6.0826 | 62.4237 | 99.4835 | 34.2549 | 11.3992 | 52.4903 | 1.8531 |  | 9.99 | 37.0514 | 9.1141 |  | 59.8373 | 121.7826 | 11.6551 | 37.2619 | 2.5972 | 90 | 25.2585 | 21.1351 | 113.8724 | 0
13395 | 840.7391 | 5.1225 | 66.2454 | 100.0313 | 36.0017 | 8.5508 | 50.2724 | 1.7235 |  | 10.002 | 36.8804 | 17.1503 |  | 60.8166 | 124.8877 | 11.2742 | 36.9525 | 2.5846 | 89 | 25.1673 | 23.1706 | 115.9337 | 0
13396 | 843.2971 | 3.52 | 66.3687 | 97.969 | 37.2095 | 8.55 | 48.8779 | 2.1788 |  | 9.048 | 35.2975 | 15.9005 |  | 59.5351 | 124.592 | 8.4663 | 36.6681 | 2.4892 | 90 | 25.0348 | 20.8969 | 111.7539 | 0
13397 | 851.8721 | 2.8904 | 57.835 | 101.9443 | 32.3643 | 8.55 | 57.6988 | 1.6966 |  | 10.7324 | 35.3307 | 7.6472 |  | 52.9619 | 115.0291 | 6.613 | 36.6058 | 2.3943 | 92 | 24.3808 | 27.4197 | 121.3816 | 0.13606
13398 | 894.1724 | 3.8295 | 57.3416 | 109.13 | 33.4715 | 10.4495 | 73.8452 | 1.6021 |  | 12.7062 | 42.6686 | 11.4103 |  | 53.5706 | 119.9688 | 8.3637 | 36.5087 | 2.3924 | 124 | 27.2876 | 18.2438 | 141.1282 | 0.20838
13399 | 945.18 | 4.2366 | 85.0699 | 107.2869 | 32.5771 | 16.1484 | 98.5928 | 2.3574 |  | 11.6714 | 65.7944 | 20.7911 |  | 68.6678 | 138.2106 | 7.6924 | 37.9965 | 4.7651 | 144 | 36.5721 | 26.221 | 168.9815 | 0.26777
13400 | 988.2718 | 7.2428 | 100.6416 | 116.3107 | 31.3241 | 18.0495 | 113.7894 | 3.3787 |  | 10.9461 | 82.2321 | 14.9551 |  | 86.3969 | 156.0492 | 11.0059 | 40.8561 | 10.2764 | 146 | 37.723 | 23.3948 | 185.4112 | 0.31435
13401 | 1042.6226 | 8.6764 | 104.7217 | 129.6419 | 33.9189 | 16.1505 | 118.5442 | 3.9251 |  | 11.0228 | 87.2569 | 10.4602 |  | 94.0467 | 168.9986 | 17.4164 | 43.0629 | 12.4334 | 170 | 33.3635 | 26.9484 | 195.7877 | 0.34955
13402 | 1087.4766 | 10.5098 | 105.002 | 130.5791 | 33.6339 | 17.0997 | 122.5026 | 3.8524 |  | 11.0797 | 88.3957 | 11.1787 |  | 97.5613 | 189.0629 | 20.3831 | 46.6697 | 12.4361 | 165 | 31.8769 | 23.5181 | 191.599 | 0.323
13403 | 1100.1813 | 9.2138 | 104.5554 | 128.2449 | 35.8293 | 16.1503 | 124.7699 | 3.5654 |  | 11.1142 | 88.7865 | 11.6146 |  | 100.5087 | 193.6826 | 19.6348 | 48.5987 | 12.4234 | 163 | 34.3387 | 26.4703 | 193.2707 | 0.25051
13404 | 1087.6596 | 7.2643 | 101.6315 | 126.3779 | 37.1688 | 16.15 | 124.1803 | 3.6918 |  | 11.0649 | 88.4795 | 10.4299 |  | 101.5097 | 192.2645 | 21.1487 | 46.5857 | 12.4962 | 181 | 28.681 | 24.2948 | 190.1097 | 0.26717
13405 | 1074.1934 | 8.3759 | 101.6642 | 126.7292 | 38.0843 | 17.0997 | 126.511 | 3.6675 |  | 11.0381 | 89.2837 | 9.9324 |  | 103.4482 | 190.8684 | 19.1786 | 45.6668 | 12.562 | 157 | 34.1518 | 25.9564 | 188.5257 | 0.29192
13406 | 1087.0107 | 11.0876 | 90.5604 | 128.9334 | 42.0307 | 17.1 | 125.4608 | 3.9455 |  | 12.2127 | 89.5723 | 10.8001 |  | 103.3042 | 191.0872 | 11.5975 | 45.369 | 12.684 | 159 | 24.0324 | 23.2389 | 186.1571 | 0.29063
13407 | 1085.2327 | 12.0587 | 54.7648 | 113.7298 | 48.912 | 17.1 | 123.4418 | 3.6279 |  | 13.1111 | 90.2804 | 10.3733 |  | 84.5424 | 184.8307 | 9.3628 | 45.1654 | 12.7587 | 141 | 13.6592 | 27.4702 | 185.6452 | 0.30188
13408 | 1067.8607 | 10.214 | 40.8309 | 104.0588 | 55.4704 | 14.2508 | 108.2598 | 3.3837 |  | 12.8337 | 89.363 | 8.8449 |  | 72.7712 | 172.7568 | 7.8885 | 44.5793 | 12.8173 | 135 | 7.1579 | 22.6564 | 162.9491 | 0.25672
13409 | 1016.68 | 10.2887 | 35.2773 | 100.8478 | 55.7117 | 9.5013 | 70.3847 | 2.2796 |  | 11.0636 | 80.9268 | 8.5174 |  | 65.0321 | 160.534 | 7.0694 | 40.8031 | 10.6304 | 134 | 8.2756 | 25.2027 | 141.1448 | 0.28054
13410 | 967.8933 | 8.1666 | 31.0608 | 96.6537 | 46.5003 | 10.4497 | 52.1525 | 1.9128 |  | 6.8628 | 66.2136 | 7.5457 |  | 48.5378 | 149.8167 | 7.2966 | 37.9271 | 5.5364 | 132 | 14.2245 | 21.2 | 125.218 | 0.25348
13411 | 951.8921 | 5.005 | 30.1379 | 97.4851 | 50.0179 | 9.5003 | 56.9329 | 1.9281 |  | 5.0007 | 61.1357 | 5.1909 |  | 43.0607 | 150.4704 | 6.8006 | 36.8924 | 3.0516 | 110 | 20.3375 | 23.5896 | 121.2984 | 0.22806
13412 | 926.6644 | 2.9594 | 28.9809 | 101.3206 | 51.2353 | 8.5503 | 56.0397 | 2.0356 |  | 4.8403 | 55.4712 | 4.1901 |  | 42.0846 | 132.2978 | 7.0407 | 35.9268 | 2.7763 | 104 | 22.3762 | 18.9817 | 114.1001 | 0.12523
13413 | 904.5937 | 3.2334 | 28.3006 | 103.3425 | 43.2975 | 5.7008 | 55.7603 | 1.768 |  | 4.7989 | 43.7367 | 4.0988 |  | 40.0617 | 117.1846 | 7.6537 | 35.4549 | 2.7544 | 107 | 24.286 | 20.1044 | 118.6324 | 0
13414 | 892.9434 | 6.222 | 28.4937 | 108.1575 | 35.8051 | 7.5995 | 56.9018 | 1.79 |  | 5.5541 | 38.5508 | 5.1104 |  | 38.6172 | 111.007 | 6.7511 | 35.8791 | 2.6034 | 102 | 23.6688 | 20.3443 | 115.1814 | 0
13415 | 274.708 | 2.6313 | 8.1549 | 30.2175 | 17.3632 | 0.002112 | 17.8706 | 0.61639 |  | 1.9253 | 13.1387 | 1.8034 |  | 11.001 | 36.5326 | 1.7615 | 10.1225 | 0.83745 | 95 | 2.3034 | 2.7349 | 11.0083 | 0
13416 | 891.406 | 3.9888 | 28.0887 | 112.1044 | 25.6195 | 10.4495 | 52.6879 | 1.997 |  | 9.4932 | 39.8928 | 6.9638 |  | 39.4567 | 114.5936 | 6.8497 | 37.2485 | 2.5708 | 99 | 28.4719 | 19.771 | 110.2843 | 0
13417 | 894.3387 | 2.5128 | 31.4945 | 111.8364 | 24.1697 | 11.3997 | 53.3173 | 1.6407 |  | 10.1037 | 39.7581 | 6.7475 |  | 42.939 | 114.065 | 7.8861 | 37.1513 | 2.5738 | 98 | 27.4636 | 18.5864 | 112.7655 | 0
13418 | 882.0251 | 2.2621 | 42.664 | 112.1063 | 34.9305 | 7.6011 | 51.5842 | 2.6322 |  | 10.1002 | 39.3661 | 8.4559 |  | 46.4653 | 112.1797 | 7.3202 | 37.0465 | 2.5717 | 94 | 28.7849 | 20.1355 | 114.7404 | 0
13419 | 884.738 | 2.3794 | 46.4776 | 110.862 | 38.1409 | 8.5497 | 48.9254 | 2.9029 |  | 9.5218 | 38.4445 | 14.0648 |  | 47.5108 | 111.4336 | 7.6396 | 36.6622 | 2.5771 | 93 | 28.3609 | 19.1561 | 109.8645 | 0
13420 | 279.2349 | 0.85934 | 13.4998 | 31.0358 | 19.1546 | 0.002376 | 15.2654 | 0.93042 |  | 3.0543 | 13.2705 | 5.3362 |  | 13.9354 | 37.8916 | 2.2911 | 10.4633 | 0.86574 | 93 | 2.8407 | 2.6044 | 12.0114 | 0
13421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0.060536
13422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0.082626
13423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0.13361
13424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0.078767
13425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0.14083
13426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0.12226
13427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0.16993
13428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0.18488
13429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0.17785
13430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0.16917
13431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0.18932
13432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0.23005
13433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0.24893
13434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0.26435
13435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 0.23937
13436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 0.13314
13437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0
13438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 0
13439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 0
13440 | [18 empty] | 104 |  |  |  | 0
13441 | [18 empty] | 97 |  |  |  | 0
13442 | [18 empty] | 98 |  |  |  | 0
13443 | [18 empty] | 93 |  |  |  | 0
13444 | [18 empty] | 91 |  |  |  | 0
13445 | [18 empty] | 89 |  |  |  | 0.15085
13446 | [18 empty] | 118 |  |  |  | 0.21944
13447 | [18 empty] | 144 |  |  |  | 0.15839
13448 | [18 empty] | 149 |  |  |  | 0.21856
13449 | [18 empty] | 158 |  |  |  | 0.29362
13450 | [18 empty] | 154 |  |  |  | 0.28552
13451 | [18 empty] | 158 |  |  |  | 0.24825
13452 | [18 empty] | 161 |  |  |  | 0.26527
13453 | [18 empty] | 154 |  |  |  | 0.29044
13454 | [18 empty] | 159 |  |  |  | 0.28672
13455 | [18 empty] | 137 |  |  |  | 0.30472
13456 | [18 empty] | 132 |  |  |  | 0.25832
13457 | [18 empty] | 131 |  |  |  | 0.23194
13458 | [18 empty] | 138 |  |  |  | 0.22867
13459 | [18 empty] | 120 |  |  |  | 0.19875
13460 | [18 empty] | 116 |  |  |  | 0.092719
13461 | [18 empty] | 119 |  |  |  | 0
13462 | [18 empty] | 118 |  |  |  | 0
13463 | [18 empty] | 103 |  |  |  | 0
13464 | [18 empty] | 107 |  |  |  | 0
13465 | [18 empty] | 100 |  |  |  | 0
13466 | [18 empty] | 93 |  |  |  | 0
13467 | [18 empty] | 95 |  |  |  | 0
13468 | [18 empty] | 89 |  |  |  | 0
13469 | [18 empty] | 90 |  |  |  | 0.136
13470 | [18 empty] | 90 |  |  |  | 0.19904
13471 | [18 empty] | 89 |  |  |  | 0.23597
13472 | [18 empty] | 88 |  |  |  | 0.30624
13473 | [18 empty] | 92 |  |  |  | 0.33783
13474 | [18 empty] | 99 |  |  |  | 0.31207
13475 | [18 empty] | 103 |  |  |  | 0.25165
13476 | [18 empty] | 110 |  |  |  | 0.26873
13477 | [18 empty] | 107 |  |  |  | 0.29298
13478 | [18 empty] | 125 |  |  |  | 0.28962
13479 | [18 empty] | 120 |  |  |  | 0.30073
13480 | [18 empty] | 123 |  |  |  | 0.24796
13481 | [18 empty] | 123 |  |  |  | 0.28281
13482 | [18 empty] | 134 |  |  |  | 0.26372
13483 | [18 empty] | 127 |  |  |  | 0.22177
13484 | [18 empty] | 125 |  |  |  | 0.074789
13485 | [18 empty] | 123 |  |  |  | 0
13486 | [18 empty] | 118 |  |  |  | 0
13487 | [18 empty] | 111 |  |  |  | 0
13488 | [18 empty] | 112 |  |  |  | 0
13489 | [18 empty] | 101 |  |  |  | 0
13490 | [18 empty] | 101 |  |  |  | 0
13491 | [18 empty] | 103 |  |  |  | 0
13492 | [18 empty] | 95 |  |  |  | 0
13493 | [18 empty] | 90 |  |  |  | 0.14339
13494 | [18 empty] | 94 |  |  |  | 0.21264
13495 | [18 empty] | 92 |  |  |  | 0.27354
13496 | [18 empty] | 91 |  |  |  | 0.32097
13497 | [18 empty] | 98 |  |  |  | 0.35349
13498 | [18 empty] | 92 |  |  |  | 0.32243
13499 | [18 empty] | 98 |  |  |  | 0.2489
13500 | [18 empty] | 101 |  |  |  | 0.26537
13501 | [18 empty] | 101 |  |  |  | 0.28998
13502 | [18 empty] | 106 |  |  |  | 0.28741
13503 | [18 empty] | 105 |  |  |  | 0.29997
13504 | [18 empty] | 113 |  |  |  | 0.25492
13505 | [18 empty] | 119 |  |  |  | 0.2795
13506 | [18 empty] | 113 |  |  |  | 0.26947
13507 | [18 empty] | 111 |  |  |  | 0.22315
13508 | [18 empty] | 103 |  |  |  | 0.11414
13509 | [18 empty] | 102 |  |  |  | 0
13510 | [18 empty] | 107 |  |  |  | 0
13511 | [18 empty] | 96 |  |  |  | 0
13512 | [18 empty] | 92 |  |  |  | 0
13513 | [18 empty] | 94 |  |  |  | 0
13514 | [18 empty] | 95 |  |  |  | 0
13515 | [18 empty] | 93 |  |  |  | 0
13516 | [18 empty] | 90 |  |  |  | 0
13517 | [18 empty] | 88 |  |  |  | 0.14175
13518 | [18 empty] | 116 |  |  |  | 0.21387
13519 | [18 empty] | 167 |  |  |  | 0.2748
13520 | [18 empty] | 154 |  |  |  | 0.32218
13521 | [18 empty] | 161 |  |  |  | 0.35173
13522 | [18 empty] | 161 |  |  |  | 0.32481
13523 | [18 empty] | 158 |  |  |  | 0.30802
13524 | [18 empty] | 153 |  |  |  | 0.26701
13525 | [18 empty] | 153 |  |  |  | 0.28792
13526 | [18 empty] | 167 |  |  |  | 0.17127
13527 | [18 empty] | 151 |  |  |  | 0.15104
13528 | [18 empty] | 144 |  |  |  | 0.25187
13529 | [18 empty] | 138 |  |  |  | 0.28018
13530 | [18 empty] | 133 |  |  |  | 0.26902
13531 | [18 empty] | 123 |  |  |  | 0.21542
13532 | [18 empty] | 117 |  |  |  | 0.10181
13533 | [18 empty] | 112 |  |  |  | 0
13534 | [18 empty] | 103 |  |  |  | 0
13535 | [18 empty] | 97 |  |  |  | 0
13536 | [18 empty] | 93 |  |  |  | 0
13537 | [18 empty] | 95 |  |  |  | 0
13538 | [18 empty] | 92 |  |  |  | 0
13539 | [18 empty] | 93 |  |  |  | 0
13540 | [18 empty] | 91 |  |  |  | 0
13541 | [18 empty] | 89 |  |  |  | 0.018099
13542 | [18 empty] | 110 |  |  |  | 0.037787
13543 | [18 empty] | 151 |  |  |  | 0.060688
13544 | [18 empty] | 149 |  |  |  | 0.09574
13545 | [18 empty] | 159 |  |  |  | 0.15284
13546 | [18 empty] | 164 |  |  |  | 0.11582
13547 | [18 empty] | 172 |  |  |  | 0.27177
13548 | [18 empty] | 161 |  |  |  | 0.16057
13549 | [18 empty] | 173 |  |  |  | 0.1753
13550 | [18 empty] | 152 |  |  |  | 0.13276
13551 | [18 empty] | 139 |  |  |  | 0.10908
13552 | [18 empty] | 132 |  |  |  | 0.085943
13553 | [18 empty] | 134 |  |  |  | 0.066655
13554 | [18 empty] | 129 |  |  |  | 0.045412
13555 | [18 empty] | 119 |  |  |  | 0.025857
13556 | [18 empty] | 117 |  |  |  | 0.047612
13557 | [18 empty] | 124 |  |  |  | 0
13558 | [18 empty] | 122 |  |  |  | 0
13559 | [18 empty] | 106 |  |  |  | 0
13560 | [18 empty] | 105 |  |  |  | 0
13561 | [18 empty] | 101 |  |  |  | 0
13562 | [18 empty] | 100 |  |  |  | 0
13563 | [18 empty] | 99 |  |  |  | 0
13564 | [18 empty] | 95 |  |  |  | 0
13565 | [18 empty] | 90 |  |  |  | 0.013711
13566 | [18 empty] | 113 |  |  |  | 0.039373
13567 | [18 empty] | 159 |  |  |  | 0.21652
13568 | [18 empty] | 150 |  |  |  | 0.075413
13569 | [18 empty] | 164 |  |  |  | 0.094793
13570 | [18 empty] | 148 |  |  |  | 0.11013
13571 | [18 empty] | 144 |  |  |  | 0.28398
13572 | [18 empty] | 145 |  |  |  | 0.27011
13573 | [18 empty] | 160 |  |  |  | 0.12392
13574 | [18 empty] | 159 |  |  |  | 0.27172
13575 | [18 empty] | 133 |  |  |  | 0.26726
13576 | [18 empty] | 137 |  |  |  | 0.1998
13577 | [18 empty] | 125 |  |  |  | 0.25703
13578 | [18 empty] | 125 |  |  |  | 0.24946
13579 | [18 empty] | 113 |  |  |  | 0.10639
13580 | [18 empty] | 102 |  |  |  | 0.0071086
13581 | [18 empty] | 97 |  |  |  | 0
13582 | [18 empty] | 103 |  |  |  | 0
13583 | [18 empty] | 95 |  |  |  | 0
13584 | [18 empty] | 95 |  |  |  | 0
13585 | [18 empty] | 97 |  |  |  | 0
13586 | [18 empty] | 92 |  |  |  | 0
13587 | [18 empty] | 94 |  |  |  | 0
13588 | [18 empty] | 91 |  |  |  | 0
13589 | [18 empty] | 91 |  |  |  | 0.10231
13590 | [18 empty] | 108 |  |  |  | 0.15764
13591 | [18 empty] | 149 |  |  |  | 0.19537
13592 | [18 empty] | 155 |  |  |  | 0.25755
13593 | [18 empty] | 165 |  |  |  | 0.33505
13594 | [18 empty] | 150 |  |  |  | 0.12367
13595 | [18 empty] | 142 |  |  |  | 0.11991
13596 | [18 empty] | 149 |  |  |  | 0.12409
13597 | [18 empty] | 158 |  |  |  | 0.12195
13598 | [18 empty] | 166 |  |  |  | 0.11892
13599 | [18 empty] | 138 |  |  |  | 0.10403
13600 | [18 empty] | 132 |  |  |  | 0.084895
13601 | [18 empty] | 134 |  |  |  | 0.13369
13602 | [18 empty] | 128 |  |  |  | 0.10399
13603 | [18 empty] | 115 |  |  |  | 0.024867
13604 | [18 empty] | 105 |  |  |  | 0.0079881
13605 | [18 empty] | 104 |  |  |  | 0
13606 | [18 empty] | 103 |  |  |  | 0
13607 | [18 empty] | 100 |  |  |  | 0
13608 | [18 empty] | 103 |  |  |  | 0
13609 | [18 empty] | 98 |  |  |  | 0
13610 | [18 empty] | 99 |  |  |  | 0
13611 | [18 empty] | 93 |  |  |  | 0
13612 | [18 empty] | 94 |  |  |  | 0
13613 | [18 empty] | 90 |  |  |  | 0.018996
13614 | [18 empty] | 113 |  |  |  | 0.055218
13615 | [18 empty] | 146 |  |  |  | 0.052343
13616 | [18 empty] | 143 |  |  |  | 0.0842
13617 | [18 empty] | 158 |  |  |  | 0.20607
13618 | [18 empty] | 152 |  |  |  | 0.23001
13619 | [18 empty] | 148 |  |  |  | 0.19212
13620 | [18 empty] | 150 |  |  |  | 0.14587
13621 | [18 empty] | 152 |  |  |  | 0.12913
13622 | [18 empty] | 161 |  |  |  | 0.11499
13623 | [18 empty] | 134 |  |  |  | 0.10584
13624 | [18 empty] | 132 |  |  |  | 0.098359
13625 | [18 empty] | 138 |  |  |  | 0.079138
13626 | [18 empty] | 131 |  |  |  | 0.045682
13627 | [18 empty] | 124 |  |  |  | 0.022288
13628 | [18 empty] | 117 |  |  |  | 0.0061727
13629 | [18 empty] | 112 |  |  |  | 0
13630 | [18 empty] | 117 |  |  |  | 0
13631 | [18 empty] | 118 |  |  |  | 0
13632 | [18 empty] | 111 |  |  |  | 0
13633 | [18 empty] | 102 |  |  |  | 0
13634 | [18 empty] | 97 |  |  |  | 0
13635 | [18 empty] | 95 |  |  |  | 0
13636 | [18 empty] | 93 |  |  |  | 0
13637 | [18 empty] | 85 |  |  |  | 0.040666
13638 | [18 empty] | 89 |  |  |  | 0.057781
13639 | [18 empty] | 97 |  |  |  | 0.08978
13640 | [18 empty] | 87 |  |  |  | 0.22814
13641 | [18 empty] | 88 |  |  |  | 0.28507
13642 | [18 empty] | 95 |  |  |  | 0.20289
13643 | [18 empty] | 96 |  |  |  | 0.20625
13644 | [18 empty] | 102 |  |  |  | 0.22913
13645 | [18 empty] | 103 |  |  |  | 0.14599
13646 | [18 empty] | 125 |  |  |  | 0.27245
13647 | [18 empty] | 118 |  |  |  | 0.24198
13648 | [18 empty] | 118 |  |  |  | 0.22821
13649 | [18 empty] | 116 |  |  |  | 0.22566
13650 | [18 empty] | 118 |  |  |  | 0.082405
13651 | [18 empty] | 115 |  |  |  | 0.055469
13652 | [18 empty] | 111 |  |  |  | 0.0079321
13653 | [18 empty] | 111 |  |  |  | 0
13654 | [18 empty] | 129 |  |  |  | 0
13655 | [18 empty] | 108 |  |  |  | 0
13656 | [18 empty] | 111 |  |  |  | 0
13657 | [18 empty] | 117 |  |  |  | 0
13658 | [18 empty] | 113 |  |  |  | 0
13659 | [18 empty] | 97 |  |  |  | 0
13660 | [18 empty] | 100 |  |  |  | 0
13661 | [18 empty] | 99 |  |  |  | 0.028174
13662 | [18 empty] | 95 |  |  |  | 0.15901
13663 | [18 empty] | 105 |  |  |  | 0.24814
13664 | [18 empty] | 94 |  |  |  | 0.17394
13665 | [18 empty] | 92 |  |  |  | 0.15746
13666 | [18 empty] | 94 |  |  |  | 0.15921
13667 | [18 empty] | 96 |  |  |  | 0.14484
13668 | [18 empty] | 101 |  |  |  | 0.13576
13669 | [18 empty] | 109 |  |  |  | 0.19022
13670 | [18 empty] | 103 |  |  |  | 0.21966
13671 | [18 empty] | 108 |  |  |  | 0.15492
13672 | [18 empty] | 105 |  |  |  | 0.13634
13673 | [18 empty] | 106 |  |  |  | 0.20786
13674 | [18 empty] | 105 |  |  |  | 0.17429
13675 | [18 empty] | 94 |  |  |  | 0.03791
13676 | [18 empty] | 94 |  |  |  | 0.065721
13677 | [18 empty] | 95 |  |  |  | 0
13678 | [18 empty] | 94 |  |  |  | 0
13679 | [18 empty] | 95 |  |  |  | 0
13680 | [18 empty] | 96 |  |  |  | 0
13681 | [18 empty] | 95 |  |  |  | 0
13682 | [18 empty] | 94 |  |  |  | 0
13683 | [18 empty] | 91 |  |  |  | 0
13684 | [18 empty] | 89 |  |  |  | 0
13685 | [18 empty] | 91 |  |  |  | 0.035988
13686 | [18 empty] | 113 |  |  |  | 0.18786
13687 | [18 empty] | 135 |  |  |  | 0.079696
13688 | [18 empty] | 149 |  |  |  | 0.18213
13689 | [18 empty] | 163 |  |  |  | 0.11086
13690 | [18 empty] | 156 |  |  |  | 0.11399
13691 | [18 empty] | 149 |  |  |  | 0.15951
13692 | [18 empty] | 160 |  |  |  | 0.18244
13693 | [18 empty] | 160 |  |  |  | 0.14362
13694 | [18 empty] | 157 |  |  |  | 0.17234
13695 | [18 empty] | 147 |  |  |  | 0.25479
13696 | [18 empty] | 141 |  |  |  | 0.20624
13697 | [18 empty] | 136 |  |  |  | 0.08468
13698 | [18 empty] | 129 |  |  |  | 0.047477
13699 | [18 empty] | 128 |  |  |  | 0.035749
13700 | [18 empty] | 122 |  |  |  | 0.011856
13701 | [18 empty] | 109 |  |  |  | 0
13702 | [18 empty] | 104 |  |  |  | 0
13703 | [18 empty] | 100 |  |  |  | 0
13704 | [18 empty] | 96 |  |  |  | 0
13705 | [18 empty] | 100 |  |  |  | 0
13706 | [18 empty] | 98 |  |  |  | 0
13707 | [18 empty] | 92 |  |  |  | 0
13708 | [18 empty] | 95 |  |  |  | 0
13709 | [18 empty] | 91 |  |  |  | 0.10617
13710 | [18 empty] | 115 |  |  |  | 0.18628
13711 | [18 empty] | 145 |  |  |  | 0.23984
13712 | [18 empty] | 141 |  |  |  | 0.3098
13713 | [18 empty] | 173 |  |  |  | 0.33568
13714 | [18 empty] | 143 |  |  |  | 0.3143
13715 | [18 empty] | 142 |  |  |  | 0.29848
13716 | [18 empty] | 163 |  |  |  | 0.26094
13717 | [18 empty] | 151 |  |  |  | 0.28689
13718 | [18 empty] | 156 |  |  |  | 0.28429
13719 | [18 empty] | 137 |  |  |  | 0.29196
13720 | [18 empty] | 137 |  |  |  | 0.21181
13721 | [18 empty] | 137 |  |  |  | 0.22486
13722 | [18 empty] | 138 |  |  |  | 0.20335
13723 | [18 empty] | 130 |  |  |  | 0.040939
13724 | [18 empty] | 118 |  |  |  | 0.027803
13725 | [18 empty] | 110 |  |  |  | 0
13726 | [18 empty] | 107 |  |  |  | 0
13727 | [18 empty] | 100 |  |  |  | 0
13728 | [18 empty] | 99 |  |  |  | 0
13729 | [18 empty] | 100 |  |  |  | 0
13730 | [18 empty] | 96 |  |  |  | 0
13731 | [18 empty] | 99 |  |  |  | 0
13732 | [18 empty] | 94 |  |  |  | 0
13733 | [18 empty] | 90 |  |  |  | 0.035908
13734 | [18 empty] | 112 |  |  |  | 0.10149
13735 | [18 empty] | 137 |  |  |  | 0.15571
13736 | [18 empty] | 153 |  |  |  | 0.11705
13737 | [18 empty] | 158 |  |  |  | 0.13737
13738 | [18 empty] | 156 |  |  |  | 0.1479
13739 | [18 empty] | 153 |  |  |  | 0.20451
13740 | [18 empty] | 164 |  |  |  | 0.17792
13741 | [18 empty] | 163 |  |  |  | 0.16948
13742 | [18 empty] | 174 |  |  |  | 0.11316
13743 | [18 empty] | 155 |  |  |  | 0.10397
13744 | [18 empty] | 146 |  |  |  | 0.08274
13745 | [18 empty] | 143 |  |  |  | 0.070344
13746 | [18 empty] | 128 |  |  |  | 0.049529
13747 | [18 empty] | 116 |  |  |  | 0.082292
13748 | [18 empty] | 108 |  |  |  | 0.025475
13749 | [18 empty] | 103 |  |  |  | 0
13750 | [18 empty] | 103 |  |  |  | 0
13751 | [18 empty] | 96 |  |  |  | 0
13752 | [18 empty] | 95 |  |  |  | 0
13753 | [18 empty] | 97 |  |  |  | 0
13754 | [18 empty] | 96 |  |  |  | 0
13755 | [18 empty] | 92 |  |  |  | 0
13756 | [18 empty] | 91 |  |  |  | 0
13757 | [18 empty] | 88 |  |  |  | 0.05625
13758 | [18 empty] | 111 |  |  |  | 0.0335
13759 | [18 empty] | 145 |  |  |  | 0.15288
13760 | [18 empty] | 154 |  |  |  | 0.16346
13761 | [18 empty] | 168 |  |  |  | 0.16457
13762 | [18 empty] | 173 |  |  |  | 0.10403
13763 | [18 empty] | 165 |  |  |  | 0.11466
13764 | [18 empty] | 175 |  |  |  | 0.19474
13765 | [18 empty] | 167 |  |  |  | 0.25237
13766 | [18 empty] | 161 |  |  |  | 0.18196
13767 | [18 empty] | 141 |  |  |  | 0.27732
13768 | [18 empty] | 139 |  |  |  | 0.15888
13769 | [18 empty] | 129 |  |  |  | 0.059706
13770 | [18 empty] | 132 |  |  |  | 0.059183
13771 | [18 empty] | 131 |  |  |  | 0.03777
13772 | [18 empty] | 113 |  |  |  | 0.032093
13773 | [18 empty] | 110 |  |  |  | 0
13774 | [18 empty] | 102 |  |  |  | 0
13775 | [18 empty] | 100 |  |  |  | 0
13776 | [18 empty] | 104 |  |  |  | 0
13777 | [18 empty] | 99 |  |  |  | 0
13778 | [18 empty] | 98 |  |  |  | 0
13779 | [18 empty] | 98 |  |  |  | 0
13780 | [18 empty] | 94 |  |  |  | 0
13781 | [18 empty] | 87 |  |  |  | 0.086096
13782 | [18 empty] | 113 |  |  |  | 0.17832
13783 | [18 empty] | 172 |  |  |  | 0.12065
13784 | [18 empty] | 163 |  |  |  | 0.25865
13785 | [18 empty] | 153 |  |  |  | 0.30212
13786 | [18 empty] | 151 |  |  |  | 0.3148
13787 | [18 empty] | 151 |  |  |  | 0.29863
13788 | [18 empty] | 164 |  |  |  | 0.26123
13789 | [18 empty] | 148 |  |  |  | 0.27767
13790 | [18 empty] | 150 |  |  |  | 0.22576
13791 | [18 empty] | 136 |  |  |  | 0.24546
13792 | [18 empty] | 132 |  |  |  | 0.19938
13793 | [18 empty] | 132 |  |  |  | 0.21638
13794 | [18 empty] | 128 |  |  |  | 0.15062
13795 | [18 empty] | 113 |  |  |  | 0.1985
13796 | [18 empty] | 103 |  |  |  | 0.031346
13797 | [18 empty] | 102 |  |  |  | 0
13798 | [18 empty] | 116 |  |  |  | 0
13799 | [18 empty] | 107 |  |  |  | 0
13800 | [18 empty] | 96 |  |  |  | 0
13801 | [18 empty] | 100 |  |  |  | 0
13802 | [18 empty] | 93 |  |  |  | 0
13803 | [18 empty] | 93 |  |  |  | 0
13804 | [18 empty] | 93 |  |  |  | 0
13805 | [18 empty] | 86 |  |  |  | 0
13806 | [18 empty] | 87 |  |  |  | 0.17283
13807 | [18 empty] | 92 |  |  |  | 0.17684
13808 | [18 empty] | 87 |  |  |  | 0.2419
13809 | [18 empty] | 89 |  |  |  | 0.3429
13810 | [18 empty] | 93 |  |  |  | 0.31657
13811 | [18 empty] | 96 |  |  |  | 0.30246
13812 | [18 empty] | 98 |  |  |  | 0.26441
13813 | [18 empty] | 103 |  |  |  | 0.14189
13814 | [18 empty] | 118 |  |  |  | 0.27288
13815 | [18 empty] | 119 |  |  |  | 0.24741
13816 | [18 empty] | 116 |  |  |  | 0.081799
13817 | [18 empty] | 117 |  |  |  | 0.1477
13818 | [18 empty] | 115 |  |  |  | 0.051632
13819 | [18 empty] | 117 |  |  |  | 0.029418
13820 | [18 empty] | 115 |  |  |  | 0.0046355
13821 | [18 empty] | 125 |  |  |  | 0
13822 | [18 empty] | 130 |  |  |  | 0
13823 | [18 empty] | 117 |  |  |  | 0
13824 | [18 empty] | 110 |  |  |  | 0
13825 | [18 empty] | 103 |  |  |  | 0
13826 | [18 empty] | 104 |  |  |  | 0
13827 | [18 empty] | 102 |  |  |  | 0
13828 | [18 empty] | 99 |  |  |  | 0
13829 | [18 empty] | 91 |  |  |  | 0
13830 | [18 empty] | 92 |  |  |  | 0.096991
13831 | [18 empty] | 95 |  |  |  | 0.14125
13832 | [18 empty] | 92 |  |  |  | 0.22414
13833 | [18 empty] | 96 |  |  |  | 0.32887
13834 | [18 empty] | 93 |  |  |  | 0.31525
13835 | [18 empty] | 97 |  |  |  | 0.29338
13836 | [18 empty] | 103 |  |  |  | 0.26392
13837 | [18 empty] | 103 |  |  |  | 0.28176
13838 | [18 empty] | 107 |  |  |  | 0.28491
13839 | [18 empty] | 106 |  |  |  | 0.15238
13840 | [18 empty] | 104 |  |  |  | 0.22427
13841 | [18 empty] | 113 |  |  |  | 0.1848
13842 | [18 empty] | 111 |  |  |  | 0.14895
13843 | [18 empty] | 111 |  |  |  | 0.14408
13844 | [18 empty] | 105 |  |  |  | 0.022981
13845 | [18 empty] | 109 |  |  |  | 0
13846 | [18 empty] | 105 |  |  |  | 0
13847 | [18 empty] | 93 |  |  |  | 0
13848 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0
13849 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0
13850 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0
13851 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0
13852 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0
13853 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 0
13854 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0.16745
13855 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0.057576
13856 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0.11901
13857 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0.14614
13858 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0.19037
13859 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0.20659
13860 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0.13075
13861 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0.17341
13862 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0.1135
13863 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0.13816
13864 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0.078
13865 | 883.6679 | 0 | 0 | 0 | -10.7496 | 10.2121 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0.064598
13866 | 888.3525 | 2.7826 | 26.5702 | 96.0943 | 47.6597 | 8.5561 | 45.4045 | 1.453 |  | 7.0061 | 49.3922 | 5.8778 |  | 53.0412 | 132.832 | 8.5331 | 39.7197 | 4.23 | 129 | 20.8895 | 76.449 | 124.4452 | 0.046882
13867 | 869.259 | 2.1101 | 21.302 | 93.1833 | 47.9984 | 8.55 | 46.2892 | 1.3563 |  | 6.0528 | 46.6456 | 4.0969 |  | 45.2162 | 131.6612 | 7.233 | 39.6835 | 3.3059 | 128 | 21.4361 | 71.8572 | 104.535 | 0.051109
13868 | 831.948 | 2.6233 | 21.2422 | 91.9596 | 46.632 | 9.4997 | 50.1566 | 1.1954 |  | 5.5943 | 44.209 | 4.0971 |  | 40.8503 | 129.8071 | 7.583 | 38.2779 | 3.3336 | 121 | 25.9189 | 78.0151 | 98.0182 | 0.0045803
13869 | 808.3919 | 3.5796 | 21.3375 | 92.7425 | 43.9339 | 10.4497 | 48.523 | 1.2275 |  | 5.2225 | 39.0894 | 4.6577 |  | 38.6164 | 126.1553 | 7.7204 | 37.641 | 3.3102 | 118 | 27.2527 | 75.9053 | 93.8161 | 0
13870 | 799.3982 | 3.4537 | 21.5083 | 95.1469 | 47.3422 | 7.6008 | 44.035 | 2.0722 |  | 6.5933 | 36.9701 | 6.3312 |  | 39.535 | 126.5277 | 7.9271 | 38.0336 | 3.3239 | 115 | 30.5671 | 74.2262 | 94.0233 | 0
13871 | 244.8738 | 0 | 6.1141 | 0 | 22.0742 | 0.002112 | 13.131 | 0.79678 |  | 2.3489 | 12.6296 | 2.2417 |  | 0 | 0 | 2.2346 | 0 | 1.1055 | 105 | 2.9947 | 9.7929 | 9.6835 | 0
13872 | 790.283 | 2.3961 | 21.0825 | 96.9902 | 34.7829 | 7.5997 | 46.4366 | 1.7945 |  | 9.0118 | 37.4691 | 6.9967 |  | 38.0824 | 116.7051 | 7.6559 | 38.2184 | 2.917 | 99 | 27.0394 | 74.7389 | 94.2435 | 0
13873 | 787.6835 | 2.289 | 21.6572 | 96.9067 | 41.3934 | 7.6 | 51.3082 | 1.6808 |  | 9.6298 | 36.8478 | 6.9543 |  | 37.8548 | 114.0762 | 7.6904 | 38.1656 | 3.2299 | 95 | 25.5739 | 75.7219 | 95.1542 | 0
13874 | 774.3616 | 2.3801 | 33.5638 | 96.4407 | 39.0264 | 7.6 | 53.5167 | 2.3697 |  | 9.6458 | 36.3069 | 8.9195 |  | 37.8784 | 119.2913 | 7.6542 | 38.002 | 3.5737 | 94 | 25.0642 | 78.6751 | 93.8253 | 0
13875 | 764.8131 | 2.3189 | 38.286 | 96.3336 | 28.9658 | 8.5497 | 57.9574 | 1.9956 |  | 9.6559 | 36.2679 | 14.6413 |  | 37.8647 | 120.051 | 8.0702 | 38.6166 | 3.5176 | 94 | 24.6025 | 74.3157 | 95.5002 | 0
13876 | 762.7257 | 2.6906 | 36.2638 | 94.8583 | 24.4064 | 10.4495 | 59.4539 | 1.5749 |  | 9.2864 | 36.542 | 13.8135 |  | 38.3587 | 112.4315 | 7.5589 | 38.0485 | 2.8396 | 93 | 25.1567 | 76.4811 | 97.8965 | 0
13877 | 769.1227 | 2.7671 | 39.8044 | 94.1484 | 25.5822 | 9.5003 | 60.6262 | 1.6769 |  | 10.6414 | 40.7166 | 8.1684 |  | 42.0879 | 103.724 | 7.5156 | 37.368 | 2.429 | 90 | 23.8934 | 80.0562 | 104.2164 | 0
13878 | 789.7084 | 3.5685 | 52.8899 | 95.9993 | 32.41 | 8.5503 | 75.1894 | 2.2288 |  | 12.3401 | 43.5557 | 14.5429 |  | 51.5553 | 108.5586 | 7.5467 | 37.0797 | 2.3661 | 117 | 20.4272 | 72.4154 | 126.1781 | 0.02532
13879 | 823.8139 | 4.0294 | 64.666 | 95.3994 | 30.949 | 15.1982 | 99.8916 | 3.11 |  | 15.1856 | 43.4755 | 23.7453 |  | 64.1381 | 129.1572 | 9.3299 | 38.8404 | 4.6405 | 149 | 26.6733 | 84.4291 | 149.3545 | 0.046139
13880 | 847.6898 | 3.6991 | 70.7227 | 103.2337 | 39.2324 | 12.3508 | 110.9811 | 3.6981 |  | 12.6539 | 47.7951 | 17.0229 |  | 84.6051 | 150.4824 | 13.7327 | 41.9245 | 10.1844 | 146 | 35.4866 | 85.5327 | 178.8435 | 0.067694
13881 | 882.5338 | 3.8234 | 83.2153 | 114.5328 | 33.611 | 16.1489 | 113.7493 | 3.9626 |  | 11.2465 | 51.0064 | 11.9035 |  | 94.2644 | 164.4618 | 22.4868 | 44.2463 | 12.793 | 193 | 36.8874 | 66.4505 | 184.4011 | 0.092949
13882 | 925.9411 | 3.7868 | 92.6766 | 121.6068 | 39.1856 | 12.3511 | 115.9119 | 3.6433 |  | 12.1257 | 51.7654 | 11.6886 |  | 97.6003 | 181.66 | 25.9926 | 45.4393 | 13.3128 | 165 | 29.4099 | 62.0328 | 184.7792 | 0.21169
13883 | 954.1542 | 3.8834 | 82.3803 | 120.0931 | 42.7732 | 14.2495 | 121.5078 | 3.7037 |  | 13.4362 | 52.6709 | 11.6431 |  | 99.3158 | 185.7396 | 26.4346 | 39.9399 | 14.2323 | 166 | 23.716 | 69.8512 | 185.9161 | 0.17752
13884 | 981.2976 | 3.8522 | 89.4212 | 121.174 | 47.3083 | 13.3003 | 126.4904 | 3.6509 |  | 14.0876 | 52.8604 | 13.8501 |  | 100.6857 | 183.0604 | 26.5262 | 36.9419 | 14.7603 | 168 | 22.3709 | 50.4266 | 181.2702 | 0.23537
13885 | 976.4187 | 4.1112 | 96.7065 | 121.6148 | 49.7963 | 14.2497 | 124.801 | 3.7291 |  | 14.2271 | 53.6258 | 17.0123 |  | 105.384 | 187.1191 | 23.0708 | 35.8934 | 14.6287 | 155 | 21.4885 | 56.1351 | 183.8824 | 0.11649
13886 | 973.4825 | 4.081 | 90.7088 | 125.235 | 54.9545 | 13.3003 | 123.4547 | 3.5307 |  | 14.6835 | 54.6745 | 14.9475 |  | 105.8278 | 190.0396 | 15.8797 | 35.1606 | 14.181 | 170 | 24.7689 | 50.8341 | 181.6054 | 0.18698
13887 | 982.7602 | 3.6377 | 63.4224 | 117.2048 | 59.5127 | 13.3 | 124.5911 | 3.5661 |  | 13.6036 | 55.4371 | 10.2612 |  | 99.0166 | 182.8177 | 13.1556 | 35.1043 | 13.9452 | 156 | 25.6297 | 53.4382 | 182.5107 | 0.12594
13888 | 962.655 | 3.0828 | 50.3753 | 109.2168 | 60.4913 | 10.4508 | 109.2395 | 3.2533 |  | 12.2637 | 43.6305 | 6.3756 |  | 86.0016 | 164.5254 | 11.1993 | 33.4014 | 13.5059 | 138 | 21.0038 | 48.6738 | 159.0399 | 0.23862
13889 | 958.8897 | 2.6679 | 43.3389 | 106.5336 | 54.5642 | 9.5003 | 75.899 | 2.6257 |  | 10.8079 | 49.771 | 4.8109 |  | 79.0521 | 149.1843 | 8.6796 | 31.207 | 11.4172 | 133 | 20.4454 | 41.309 | 132.1008 | 0.14271
13890 | 930.2849 | 4.1716 | 41.1893 | 105.8231 | 53.4031 | 7.6005 | 63.9923 | 2.131 |  | 7.2629 | 48.0142 | 3.9277 |  | 64.3618 | 153.3264 | 7.7316 | 29.8102 | 6.2362 | 131 | 22.4676 | 46.1504 | 121.0507 | 0.1015
13891 | 914.0301 | 4.7493 | 40.8091 | 104.1097 | 53.7017 | 7.6 | 64.2986 | 1.9259 |  | 5.8986 | 48.1058 | 3.3321 |  | 57.8247 | 149.5356 | 8.2547 | 27.4393 | 3.8295 | 113 | 24.5652 | 41.3122 | 108.0835 | 0.048435
13892 | 880.6618 | 5.4628 | 39.3521 | 100.4218 | 46.7082 | 8.5497 | 55.7404 | 1.8508 |  | 5.9013 | 46.4034 | 3.2018 |  | 54.4792 | 138.0446 | 7.9526 | 25.7817 | 3.6658 | 115 | 26.9407 | 43.2467 | 99.7564 | 0.0066609
13893 | 856.1771 | 7.1791 | 38.8289 | 101.6169 | 41.6769 | 7.6003 | 57.6331 | 1.7705 |  | 6.0351 | 40.7474 | 4.2341 |  | 53.0528 | 130.0642 | 8.2698 | 25.3133 | 3.6157 | 117 | 26.8151 | 45.7051 | 99.8656 | 0
13894 | 856.1394 | 6.26 | 39.1351 | 111.4355 | 40.4125 | 9.4995 | 58.7741 | 2.2905 |  | 6.9683 | 37.6834 | 5.5845 |  | 50.895 | 127.2549 | 8.4612 | 25.8878 | 4.0129 | 114 | 29.8636 | 40.5203 | 101.8118 | 0
13895 | 260.3793 | 1.8832 | 11.3374 | 32.0007 | 20.7762 | 0.00264 | 18.3231 | 0.8455 |  | 2.4179 | 12.9397 | 1.9445 |  | 14.5782 | 42.7688 | 2.4162 | 7.4315 | 1.4075 | 111 | 2.9465 | 5.4002 | 9.6481 | 0
13896 | 861.692 | 2.4074 | 41.3417 | 109.5389 | 36.5757 | 8.55 | 53.8189 | 1.7242 |  | 9.2045 | 37.1271 | 5.9498 |  | 47.7598 | 116.3727 | 11.9569 | 25.6048 | 4.1632 | 118 | 28.7474 | 50.0389 | 103.1933 | 0
13897 | 854.4292 | 2.2899 | 42.0088 | 108.6325 | 32.6113 | 8.55 | 54.3178 | 1.7883 |  | 9.6561 | 37.0394 | 6.0881 |  | 49.1759 | 115.818 | 12.7971 | 25.8754 | 3.6399 | 110 | 26.0513 | 44.7403 | 105.574 | 0
13898 | 843.6806 | 2.2434 | 53.4173 | 109.406 | 34.5082 | 8.55 | 59.9309 | 1.9016 |  | 9.6387 | 37.077 | 8.0656 |  | 55.6579 | 119.2794 | 12.5577 | 25.2866 | 2.9758 | 104 | 26.0483 | 50.5461 | 106.615 | 0
13899 | 844.2581 | 2.2534 | 57.3928 | 108.7342 | 31.7697 | 9.4997 | 57.7048 | 2.328 |  | 9.6839 | 37.0199 | 13.6052 |  | 58.8336 | 117.8507 | 12.8032 | 25.4653 | 2.7244 | 95 | 26.2456 | 47.1059 | 108.0536 | 0
13900 | 832.5583 | 2.6963 | 60.8678 | 108.0045 | 30.4108 | 8.5503 | 58.8829 | 2.0338 |  | 10.0973 | 36.8877 | 13.3216 |  | 58.4222 | 112.4686 | 11.7571 | 25.9534 | 2.7018 | 94 | 26.8207 | 47.3737 | 109.7586 | 0
13901 | 844.825 | 3.0314 | 51.0734 | 107.497 | 30.8212 | 8.55 | 67.7666 | 1.4798 |  | 11.3037 | 39.4404 | 7.4846 |  | 55.5041 | 106.3979 | 8.849 | 25.7613 | 2.5502 | 90 | 26.6354 | 50.9722 | 117.4845 | 0
13902 | 878.0975 | 3.5129 | 42.4276 | 108.7698 | 35.3004 | 8.55 | 75.0364 | 1.3192 |  | 12.723 | 39.0183 | 12.3451 |  | 54.3347 | 112.9122 | 7.9458 | 26.2565 | 2.4881 | 120 | 21.6892 | 45.5806 | 130.918 | 0.14019
13903 | 916.9024 | 3.8883 | 45.5361 | 104.9661 | 35.2572 | 14.2484 | 101.1794 | 1.7815 |  | 12.2053 | 43.0675 | 21.9028 |  | 62.8828 | 135.191 | 9.9514 | 27.4072 | 4.7728 | 146 | 32.6547 | 53.3308 | 159.1602 | 0.10553
13904 | 934.6067 | 3.4734 | 53.7178 | 116.6184 | 39.3219 | 15.1997 | 112.835 | 3.4162 |  | 12.0043 | 50.2477 | 14.9737 |  | 84.0491 | 156.9711 | 14.212 | 28.7108 | 10.2318 | 155 | 39.1244 | 57.4788 | 183.6357 | 0.13091
13905 | 966.6601 | 3.5451 | 73.4044 | 128.0394 | 44.8843 | 14.2503 | 114.4068 | 3.5951 |  | 12.3743 | 53.3736 | 11.9941 |  | 99.0941 | 173.6472 | 22.9649 | 31.7395 | 12.4596 | 177 | 36.2838 | 68.6145 | 191.6535 | 0.17759
13906 | 1022.9364 | 3.8305 | 88.1936 | 131.4251 | 48.7409 | 15.1997 | 117.0109 | 3.2626 |  | 12.7543 | 54.695 | 11.4125 |  | 110.4984 | 185.3294 | 25.5602 | 36.0744 | 12.7614 | 170 | 33.0483 | 83.433 | 188.8163 | 0.24709
13907 | 1045.052 | 3.982 | 89.8168 | 133.1206 | 47.8508 | 16.1497 | 121.2746 | 3.5164 |  | 12.9728 | 55.7138 | 10.6587 |  | 117.6165 | 191.5774 | 24.9914 | 38.3121 | 13.5231 | 170 | 34.1404 | 85.304 | 193.3431 | 0.27792
13908 | 1035.6459 | 4.037 | 95.0629 | 136.3558 | 46.7643 | 16.15 | 122.9393 | 3.2925 |  | 13.091 | 55.8815 | 10.4319 |  | 118.9267 | 186.4709 | 26.1031 | 45.5853 | 14.014 | 178 | 30.7211 | 77.6502 | 187.9214 | 0.24863
13909 | 1022.1674 | 3.9789 | 96.4886 | 135.82 | 47.1083 | 17.0997 | 122.8299 | 3.3017 |  | 14.5534 | 55.6513 | 12.9983 |  | 118.7698 | 190.095 | 23.4683 | 40.0156 | 14.1057 | 177 | 35.4166 | 80.8674 | 186.918 | 0.26166
13910 | 1031.3066 | 3.3935 | 88.7727 | 137.4828 | 49.9375 | 16.1503 | 124.3325 | 3.6216 |  | 13.7648 | 57.1854 | 12.1888 |  | 120.1068 | 187.6866 | 15.9917 | 35.437 | 14.1809 | 188 | 28.0445 | 81.9217 | 185.5274 | 0.20815
13911 | 1035.1546 | 3.51 | 52.0825 | 120.0116 | 51.6924 | 15.2003 | 126.6063 | 3.4189 |  | 13.1779 | 58.3011 | 8.4898 |  | 108.8103 | 192.9668 | 13.4195 | 34.8669 | 14.2142 | 176 | 23.3115 | 80.1272 | 179.5225 | 0.24006
13912 | 1001.1076 | 3.5152 | 36.7865 | 109.3038 | 53.0666 | 11.4011 | 109.0257 | 3.2751 |  | 12.716 | 53.3219 | 4.6013 |  | 90.774 | 169.1797 | 11.6657 | 33.6757 | 13.9397 | 152 | 20.7855 | 83.5003 | 165.6741 | 0.26194
13913 | 996.5338 | 3.9466 | 28.4929 | 110.9085 | 56.5539 | 9.5032 | 75.913 | 2.2635 |  | 11.259 | 48.8686 | 3.5423 |  | 76.5475 | 149.7947 | 9.2036 | 33.2701 | 12.3489 | 149 | 30.8684 | 85.4454 | 135.8532 | 0.24873
13914 | 978.242 | 6.169 | 24.2716 | 103.6381 | 47.0233 | 9.4974 | 58.3657 | 1.6424 |  | 6.8248 | 45.6104 | 3.504 |  | 55.401 | 139.4027 | 7.8857 | 30.9332 | 7.3151 | 158 | 27.8011 | 75.4298 | 127.8299 | 0.23153
13915 | 942.2964 | 6.1851 | 24.0219 | 100.0283 | 46.48 | 8.5503 | 58.7647 | 1.3154 |  | 4.6506 | 44.4172 | 3.5271 |  | 46.134 | 136.6529 | 7.8873 | 28.4006 | 4.5237 | 134 | 26.6693 | 81.0201 | 109.3642 | 0.17653
13916 | 925.0577 | 3.8639 | 23.8462 | 100.6676 | 48.3575 | 7.6003 | 58.3532 | 1.3279 |  | 4.4839 | 42.3874 | 3.5627 |  | 42.6387 | 129.4424 | 7.9736 | 26.2781 | 4.493 | 121 | 28.3282 | 82.0268 | 101.579 | 0.0040296
13917 | 904.9654 | 3.6533 | 23.8396 | 101.5526 | 38.9254 | 7.6 | 57.2509 | 2.0606 |  | 5.0522 | 37.9527 | 4.2138 |  | 43.1332 | 119.4458 | 7.7402 | 25.7429 | 4.7099 | 127 | 27.2351 | 76.5634 | 101.2316 | 0
13918 | 898.4558 | 3.5946 | 23.9391 | 106.9025 | 35.5224 | 8.5497 | 54.8741 | 1.8666 |  | 6.6266 | 36.6727 | 5.4394 |  | 43.8613 | 114.5949 | 8.3913 | 25.5448 | 4.7141 | 123 | 29.2103 | 79.8651 | 105.6036 | 0
13919 | 276.7677 | 1.1604 | 6.8257 | 30.0399 | 18.3452 | 0.002376 | 16.7906 | 0.52843 |  | 2.3583 | 12.6855 | 1.8912 |  | 12.5913 | 37.9462 | 2.4513 | 7.1374 | 1.556 | 111 | 2.8525 | 10.6658 | 10.9676 | 0
13920 | 886.5806 | 2.4204 | 23.9694 | 109.9683 | 33.2937 | 8.5505 | 53.6743 | 1.7269 |  | 9.0224 | 35.874 | 6.0413 |  | 40.5308 | 113.7446 | 11.5699 | 25.8556 | 3.5262 | 111 | 28.4971 | 75.1124 | 107.8132 | 0
13921 | 879.2099 | 2.3063 | 24.2818 | 109.2102 | 29.1001 | 9.4997 | 54.7841 | 2.374 |  | 9.6341 | 35.4363 | 5.996 |  | 39.4226 | 112.8381 | 12.5195 | 26.1562 | 3.2106 | 109 | 27.9838 | 81.146 | 109.4432 | 0
13922 | 868.1742 | 2.2536 | 35.2545 | 111.0372 | 28.8915 | 8.5503 | 51.554 | 2.038 |  | 9.6158 | 35.5826 | 8.0345 |  | 44.5683 | 112.3575 | 12.6362 | 26.3097 | 3.2875 | 101 | 24.6886 | 80.7009 | 104.5421 | 0
13923 | 863.2964 | 2.2604 | 39.7099 | 109.5281 | 33.6885 | 8.55 | 51.7889 | 2.1984 |  | 9.6058 | 35.8363 | 13.6808 |  | 46.888 | 114.0057 | 12.7596 | 26.2808 | 3.4817 | 104 | 24.0486 | 76.265 | 108.1584 | 0
13924 | 862.792 | 2.6997 | 37.4801 | 107.7159 | 36.8142 | 9.4997 | 59.6326 | 2.3348 |  | 9.4363 | 38.3604 | 13.0154 |  | 46.473 | 108.4534 | 11.0469 | 26.1786 | 3.021 | 104 | 24.1645 | 82.1412 | 113.2226 | 0
13925 | 869.1427 | 2.9105 | 26.5282 | 107.0088 | 36.3204 | 9.5 | 62.5461 | 1.679 |  | 10.6945 | 35.8911 | 8.2303 |  | 49.5688 | 108.3166 | 8.9126 | 25.805 | 2.6668 | 100 | 24.4771 | 79.5733 | 117.3321 | 0
13926 | 895.1123 | 3.4128 | 22.6118 | 107.5926 | 34.8657 | 9.5 | 73.5188 | 2.0633 |  | 12.3501 | 35.9865 | 16.3886 |  | 53.9605 | 119.5466 | 8.402 | 25.9204 | 2.6027 | 119 | 21.3091 | 78.4332 | 141.2904 | 0.063727
13927 | 922.3959 | 3.9645 | 28.5719 | 103.2609 | 30.7579 | 14.2487 | 97.5798 | 2.417 |  | 12.6899 | 40.8309 | 25.514 |  | 66.5979 | 146.0957 | 9.5869 | 28.0712 | 5.002 | 158 | 27.0904 | 91.109 | 167.3386 | 0.11048
13928 | 959.8285 | 4.5522 | 35.5251 | 116.3081 | 35.0558 | 13.3003 | 110.9946 | 3.5059 |  | 11.5382 | 46.8303 | 19.177 |  | 88.3949 | 164.363 | 14.0839 | 30.7941 | 10.7596 | 180 | 38.2007 | 94.282 | 188.3748 | 0.099832
13929 | 999.8987 | 5.8063 | 70.9583 | 128.8195 | 37.6893 | 14.2497 | 117.4034 | 4.3648 |  | 13.3636 | 49.4929 | 13.705 |  | 99.539 | 183.7831 | 25.0905 | 33.3109 | 13.5643 | 184 | 37.1325 | 89.5448 | 182.6885 | 0.13738
13930 | 1019.2869 | 5.1095 | 86.0943 | 133.3145 | 42.0698 | 15.204 | 123.9701 | 4.097 |  | 13.2401 | 50.9814 | 19.0843 |  | 103.3926 | 196.282 | 28.4934 | 35.3033 | 13.9454 | 167 | 38.6359 | 87.7457 | 186.7087 | 0.24665
13931 | 1042.5891 | 6.3922 | 83.5009 | 134.7624 | 47.5557 | 15.1958 | 127.3272 | 3.7569 |  | 12.4714 | 52.1632 | 18.5873 |  | 109.0591 | 202.5788 | 28.6804 | 35.9244 | 14.2263 | 163 | 41.2197 | 83.7857 | 196.509 | 0.23305
13932 | 1046.7197 | 9.2691 | 91.0539 | 140.5893 | 45.976 | 18.0492 | 128.5939 | 3.9197 |  | 12.1908 | 52.0922 | 21.6059 |  | 114.9346 | 198.5965 | 29.1578 | 36.2414 | 14.6835 | 168 | 44.3131 | 84.4215 | 184.8074 | 0.20424
13933 | 1076.3295 | 8.2911 | 96.6229 | 139.6731 | 42.8269 | 18.05 | 127.1502 | 4.8498 |  | 13.1177 | 52.0446 | 20.5684 |  | 121.6874 | 200.3011 | 25.6244 | 47.2494 | 17.7261 | 170 | 49.3275 | 106.7558 | 186.9068 | 0.18044
13934 | 1079.114 | 7.012 | 91.924 | 139.1062 | 30.8256 | 18.9997 | 118.4267 | 4.5809 |  | 14.3267 | 52.1048 | 19.6725 |  | 124.679 | 201.8094 | 17.9124 | 49.3523 | 16.959 | 172 | 49.2751 | 101.6863 | 189.909 | 0.28264
13935 | 1054.0976 | 7.9422 | 52.2654 | 123.2895 | 28.7224 | 17.1005 | 110.2653 | 4.2887 |  | 12.5143 | 52.1657 | 13.6511 |  | 111.1681 | 205.4935 | 14.4883 | 48.3908 | 15.3744 | 155 | 43.933 | 103.4694 | 183.826 | 0.26674
13936 | 1028.0577 | 10.937 | 35.5114 | 111.5545 | 32.7423 | 9.5021 | 93.7029 | 3.6501 |  | 11.2061 | 50.7155 | 6.9825 |  | 88.7046 | 187.4532 | 12.0834 | 46.7625 | 15.346 | 151 | 36.9531 | 95.1448 | 158.2568 | 0.16159
13937 | 1021.2221 | 11.748 | 27.6827 | 111.5686 | 29.8962 | 10.4497 | 68.9678 | 2.3928 |  | 10.0492 | 49.7122 | 5.5084 |  | 78.4374 | 168.0676 | 9.7834 | 45.2621 | 13.7838 | 165 | 29.6181 | 94.0608 | 129.6345 | 0.17904
13938 | 987.5749 | 7.3995 | 23.4253 | 104.8777 | 32.5051 | 8.5505 | 62.6202 | 1.5708 |  | 6.4977 | 47.3933 | 4.8364 |  | 61.1538 | 150.4267 | 8.7378 | 43.0384 | 8.5537 | 156 | 28.3592 | 96.9498 | 120.9528 | 0.21417
13939 | 938.7195 | 4.9212 | 22.5862 | 100.6098 | 35.778 | 9.4997 | 62.8771 | 1.3719 |  | 5.8149 | 45.1072 | 4.5206 |  | 50.7725 | 140.204 | 8.1073 | 40.0883 | 5.488 | 141 | 29.3679 | 89.094 | 103.8024 | 0.10452
13940 | 909.9448 | 4.3053 | 22.4019 | 102.1032 | 39.201 | 7.6005 | 63.1737 | 1.5517 |  | 5.4565 | 44.0619 | 4.4463 |  | 46.4673 | 125.6894 | 8.5276 | 33.1782 | 5.1845 | 128 | 30.2178 | 94.4349 | 99.3055 | 0.023653
13941 | 893.0636 | 4.2736 | 22.7729 | 101.5879 | 36.6986 | 6.6503 | 63.1612 | 1.5981 |  | 6.1048 | 43.7915 | 5.4535 |  | 45.4351 | 118.014 | 8.7339 | 27.7872 | 5.4068 | 129 | 29.3648 | 91.0801 | 100.5914 | 0
13942 | 878.7753 | 3.8109 | 22.8838 | 102.5164 | 30.2417 | 8.5495 | 62.6493 | 1.6161 |  | 7.5612 | 39.345 | 6.8198 |  | 45.5081 | 115.9656 | 8.679 | 26.3666 | 5.5944 | 128 | 25.5575 | 90.854 | 102.9882 | 0
13943 | 271.1513 | 1.2213 | 6.5574 | 28.6362 | 14.8482 | 0.002376 | 19.6061 | 0.53878 |  | 2.6186 | 12.7628 | 2.3357 |  | 13.1566 | 38.6557 | 2.454 | 7.417 | 1.8765 | 120 | 2.4594 | 12.2526 | 10.8462 | 0
13944 | [18 empty] | 122 |  |  |  | 0
13945 | [18 empty] | 123 |  |  |  | 0
13946 | [18 empty] | 120 |  |  |  | 0
13947 | [18 empty] | 105 |  |  |  | 0
13948 | [18 empty] | 105 |  |  |  | 0
13949 | [18 empty] | 100 |  |  |  | 0
13950 | [18 empty] | 123 |  |  |  | 0.18417
13951 | [18 empty] | 176 |  |  |  | 0.096665
13952 | [18 empty] | 177 |  |  |  | 0.13507
13953 | [18 empty] | 176 |  |  |  | 0.20293
13954 | [18 empty] | 183 |  |  |  | 0.24625
13955 | [18 empty] | 176 |  |  |  | 0.23627
13956 | [18 empty] | 171 |  |  |  | 0.20853
13957 | [18 empty] | 182 |  |  |  | 0.17226
13958 | [18 empty] | 181 |  |  |  | 0.18818
13959 | [18 empty] | 187 |  |  |  | 0.19645
13960 | [18 empty] | 153 |  |  |  | 0.1141
13961 | [18 empty] | 145 |  |  |  | 0.12835
13962 | [18 empty] | 145 |  |  |  | 0.038189
13963 | [18 empty] | 129 |  |  |  | 0.01272
13964 | [18 empty] | 118 |  |  |  | 0.0012144
13965 | [18 empty] | 121 |  |  |  | 0
13966 | [18 empty] | 134 |  |  |  | 0
13967 | [18 empty] | 121 |  |  |  | 0
13968 | [18 empty] | 118 |  |  |  | 0
13969 | [18 empty] | 118 |  |  |  | 0
13970 | [18 empty] | 109 |  |  |  | 0
13971 | [18 empty] | 100 |  |  |  | 0
13972 | [18 empty] | 103 |  |  |  | 0
13973 | [18 empty] | 97 |  |  |  | 0
13974 | [18 empty] | 98 |  |  |  | 0.048688
13975 | [18 empty] | 106 |  |  |  | 0.053711
13976 | [18 empty] | 101 |  |  |  | 0.065321
13977 | [18 empty] | 123 |  |  |  | 0.20792
13978 | [18 empty] | 126 |  |  |  | 0.2729
13979 | [18 empty] | 111 |  |  |  | 0.29225
13980 | [18 empty] | 116 |  |  |  | 0.18592
13981 | [18 empty] | 125 |  |  |  | 0.28664
13982 | [18 empty] | 130 |  |  |  | 0.23388
13983 | [18 empty] | 143 |  |  |  | 0.19225
13984 | [18 empty] | 143 |  |  |  | 0.091527
13985 | [18 empty] | 139 |  |  |  | 0.077664
13986 | [18 empty] | 143 |  |  |  | 0.11542
13987 | [18 empty] | 140 |  |  |  | 0.025925
13988 | [18 empty] | 127 |  |  |  | 0.0024288
13989 | [18 empty] | 125 |  |  |  | 0
13990 | [18 empty] | 128 |  |  |  | 0
13991 | [18 empty] | 108 |  |  |  | 0
13992 | 819.6675 | 3.3851 | 31.8662 | 104.7059 | 29.3608 | 10.4495 | 58.7485 | 1.705 |  | 7.3768 | 37.8269 | 6.8697 |  | 37.8234 | 117.1799 | 8.4948 | 35.6893 | 3.3697 | 110 | 27.5971 | 52.5601 | 98.0749 | 0
13993 | 815.2888 | 3.1617 | 31.9704 | 103.6443 | 34.0311 | 7.6008 | 54.9939 | 1.8163 |  | 7.3547 | 36.9553 | 6.9337 |  | 37.1817 | 116.1181 | 8.7366 | 35.9277 | 3.0735 | 112 | 26.785 | 57.2865 | 98.4855 | 0
13994 | 802.0369 | 2.9097 | 32.2405 | 103.7053 | 31.942 | 8.5497 | 54.6751 | 2.3457 |  | 7.3414 | 36.8123 | 6.8915 |  | 36.54 | 116.6724 | 8.9522 | 35.9297 | 3.1179 | 106 | 23.6435 | 58.0437 | 100.0979 | 0
13995 | 792.1914 | 2.4814 | 32.0378 | 103.307 | 29.626 | 7.6003 | 58.913 | 1.8956 |  | 7.3586 | 36.7671 | 6.9285 |  | 36.8986 | 115.0245 | 8.4999 | 36.1274 | 2.7905 | 101 | 22.6904 | 52.6716 | 98.9702 | 0
13996 | 799.0406 | 2.8188 | 36.7197 | 103.283 | 26.5668 | 8.5497 | 57.0683 | 1.5497 |  | 7.0443 | 36.5167 | 6.919 |  | 36.7272 | 111.7542 | 8.998 | 35.9936 | 2.667 | 100 | 22.2578 | 59.2075 | 96.7516 | 0
13997 | 800.2205 | 3.4942 | 37.4345 | 100.762 | 32.1766 | 8.55 | 57.1917 | 1.407 |  | 5.2641 | 35.1679 | 5.4345 |  | 34.8439 | 107.4348 | 8.9319 | 35.4562 | 2.5835 | 100 | 22.489 | 60.0288 | 96.1533 | 0
13998 | 814.2288 | 2.7807 | 32.7508 | 99.3272 | 39.3224 | 8.55 | 58.4972 | 1.9525 |  | 4.4594 | 35.075 | 4.2955 |  | 33.8849 | 105.328 | 7.8147 | 35.5093 | 2.4751 | 98 | 22.4199 | 51.3697 | 94.8346 | 0.046299
13999 | 821.4302 | 2.0231 | 31.0953 | 99.9255 | 38.9638 | 8.55 | 56.894 | 1.5909 |  | 4.4499 | 37.032 | 4.0795 |  | 33.92 | 106.986 | 8.239 | 35.2626 | 2.4421 | 101 | 26.3833 | 57.151 | 95.6903 | 0.088529
14000 | 823.5304 | 2.1944 | 31.1331 | 109.8924 | 39.8433 | 9.4997 | 60.5748 | 1.5176 |  | 5.2453 | 40.5469 | 4.0236 |  | 36.5264 | 109.1491 | 11.4676 | 34.9678 | 2.4479 | 100 | 28.0461 | 52.5144 | 95.2501 | 0.077476
14001 | 840.4552 | 2.1147 | 31.0852 | 119.0168 | 43.7865 | 7.6005 | 62.1736 | 1.55 |  | 6.1201 | 37.4408 | 4.2405 |  | 38.44 | 113.482 | 17.6918 | 35.2643 | 2.4362 | 105 | 26.8775 | 58.7103 | 96.1373 | 0.13914
14002 | 842.469 | 1.9615 | 31.1145 | 121.0165 | 42.8663 | 8.5497 | 63.0105 | 1.2863 |  | 6.4876 | 36.5053 | 4.8976 |  | 40.0504 | 118.2602 | 20.0407 | 35.6746 | 2.4707 | 116 | 22.8876 | 57.4442 | 96.3117 | 0.17639
14003 | 845.533 | 2.1561 | 31.1874 | 122.72 | 45.6364 | 7.6003 | 58.4391 | 1.0339 |  | 7.3539 | 42.9877 | 4.7348 |  | 42.8124 | 114.8236 | 20.6666 | 35.6217 | 2.5097 | 116 | 17.2169 | 54.61 | 98.5421 | 0.1306
14004 | 854.7654 | 2.4744 | 31.1859 | 122.7232 | 46.2804 | 8.5497 | 57.3736 | 0.95998 |  | 7.8132 | 47.6276 | 4.1994 |  | 46.8093 | 108.9535 | 19.5095 | 35.5241 | 2.7033 | 126 | 17.9936 | 58.7794 | 98.2674 | 0.12793
14005 | 850.622 | 2.417 | 31.14 | 123.0125 | 48.7443 | 7.6003 | 56.3556 | 0.97469 |  | 7.5867 | 47.5055 | 3.9877 |  | 49.6367 | 113.9654 | 17.4105 | 35.6026 | 2.9172 | 123 | 13.7988 | 52.5829 | 95.3812 | 0.11448
14006 | 843.7953 | 2.6303 | 31.3888 | 125.1755 | 48.7396 | 8.5497 | 60.8596 | 0.99899 |  | 7.4261 | 47.0611 | 4.0603 |  | 50.2102 | 128.8977 | 10.5044 | 35.4682 | 3.3541 | 117 | 13.2705 | 57.0487 | 95.8166 | 0.23807
14007 | 850.8443 | 4.4873 | 31.3713 | 115.0737 | 49.7959 | 7.6003 | 57.7672 | 1.0183 |  | 8.3128 | 47.458 | 4.053 |  | 47.9073 | 142.1973 | 7.8145 | 35.7802 | 3.77 | 121 | 13.9802 | 60.1243 | 95.8823 | 0.2642
14008 | 834.6326 | 7.9445 | 30.9444 | 104.1955 | 43.2052 | 8.5497 | 49.9844 | 1.281 |  | 8.3092 | 46.6425 | 3.9113 |  | 45.2979 | 150.7097 | 7.3379 | 34.3571 | 4.3734 | 116 | 13.7749 | 56.0682 | 94.7209 | 0.14669
14009 | 867.2798 | 8.6703 | 31.445 | 104.6349 | 38.489 | 7.6024 | 58.5829 | 1.1278 |  | 6.9769 | 46.496 | 3.919 |  | 45.4594 | 156.652 | 7.9253 | 35.1964 | 4.8525 | 119 | 14.3767 | 0 | 94.8619 | 0.18288
14010 | 856.0036 | 4.325 | 31.3838 | 103.7551 | 40.5145 | 7.5979 | 60.4118 | 0.96861 |  | 6.7027 | 44.1995 | 3.7438 |  | 45.0262 | 156.7786 | 8.355 | 35.4032 | 4.4542 | 114 | 18.5691 | 56.2443 | 93.8031 | 0.13107
14011 | 850.2992 | 2.4186 | 31.1481 | 101.8321 | 34.6355 | 7.6 | 62.0944 | 0.96276 |  | 7.1505 | 39.9284 | 3.8448 |  | 41.8383 | 137.6795 | 7.7931 | 35.2941 | 4.1824 | 126 | 20.6498 | 53.503 | 96.4442 | 0.10235
14012 | 846.2726 | 3.3407 | 31.1069 | 101.0261 | 30.0484 | 8.5497 | 66.8076 | 1.8756 |  | 6.8592 | 38.4402 | 3.8291 |  | 39.6646 | 121.7433 | 7.4942 | 36.1621 | 3.9512 | 116 | 22.9893 | 59.0114 | 98.7182 | 0.0046883
14013 | 831.6375 | 4.109 | 31.431 | 101.6968 | 29.2845 | 10.4495 | 62.1111 | 1.7886 |  | 7.2402 | 38.1317 | 4.7952 |  | 39.1129 | 116.0801 | 7.8967 | 36.0443 | 3.7838 | 118 | 27.0288 | 53.3301 | 99.5888 | 0
14014 | 830.5665 | 4.6679 | 32.0172 | 104.5103 | 30.1179 | 6.6511 | 53.2506 | 1.5743 |  | 8.5881 | 38.9536 | 6.2222 |  | 38.2614 | 118.2457 | 8.9942 | 36.464 | 3.5886 | 118 | 28.9169 | 55.9322 | 100.7893 | 0
14015 | 259.2227 | 1.7049 | 9.288 | 29.4504 | 13.9806 | 0.001848 | 15.8859 | 0.52616 |  | 2.9807 | 13.6593 | 2.1668 |  | 11.0144 | 40.3441 | 2.6513 | 10.4219 | 1.1661 | 107 | 2.8576 | 7.629 | 10.2392 | 0
14016 | 814.2394 | 3.3834 | 31.8092 | 103.8542 | 34.3875 | 7.6008 | 64.9729 | 2.1712 |  | 9.7335 | 37.8859 | 6.456 |  | 37.1922 | 115.8906 | 8.5005 | 35.7628 | 2.6183 | 102 | 27.4731 | 51.8728 | 103.6981 | 0
14017 | 818.6022 | 2.9467 | 31.6468 | 103.5484 | 37.3199 | 8.5497 | 64.373 | 2.4074 |  | 10.2536 | 38.7312 | 6.5207 |  | 36.5061 | 113.5429 | 8.6091 | 35.7585 | 2.6029 | 100 | 26.0386 | 57.9041 | 104.9561 | 0
14018 | 813.3324 | 2.3657 | 31.6599 | 104.4968 | 38.1148 | 9.4997 | 58.495 | 1.9022 |  | 10.253 | 38.9931 | 8.439 |  | 36.919 | 116.1779 | 8.1632 | 35.8179 | 2.6088 | 102 | 25.5748 | 57.7894 | 101.1499 | 0
14019 | 803.0895 | 2.2525 | 32.0198 | 104.1837 | 38.6177 | 9.5 | 60.0674 | 1.5673 |  | 10.2834 | 38.6533 | 13.9898 |  | 37.0346 | 113.8705 | 7.9951 | 36.2824 | 2.6088 | 95 | 28.6369 | 52.3544 | 102.9057 | 0
14020 | 805.853 | 2.7725 | 31.6521 | 103.6298 | 37.5518 | 8.5503 | 61.4793 | 2.3261 |  | 10.3922 | 40.7901 | 13.754 |  | 36.3304 | 110.832 | 8.3531 | 35.7988 | 2.6241 | 93 | 30.2877 | 60.1448 | 111.346 | 0
14021 | 813.7375 | 3.0105 | 31.7154 | 102.6081 | 37.1271 | 8.55 | 63.8499 | 1.7227 |  | 15.374 | 36.6193 | 8.0235 |  | 40.4271 | 105.072 | 8.0567 | 35.1034 | 2.6969 | 105 | 27.1271 | 55.7189 | 119.7881 | 0
14022 | 857.7066 | 3.6796 | 39.9352 | 105.0686 | 35.337 | 10.4495 | 77.3496 | 1.9656 |  | 23.3401 | 39.6521 | 12.5099 |  | 49.3531 | 116.7377 | 8.0494 | 35.0894 | 2.8262 | 136 | 25.1974 | 0 | 137.6376 | 0.074862
14023 | 899.8922 | 7.4418 | 59.5222 | 103.3874 | 29.8796 | 15.1987 | 104.4009 | 3.2745 |  | 22.2482 | 55.2075 | 22.2265 |  | 65.9737 | 138.1811 | 14.5535 | 37.6456 | 5.534 | 173 | 35.068 | 66.3927 | 179.7496 | 0.082843
14024 | 945.3174 | 16.9676 | 80.0763 | 115.7969 | 31.0868 | 14.2503 | 124.9954 | 3.9725 |  | 24.2217 | 65.9543 | 16.1232 |  | 92.1442 | 160.2519 | 21.6248 | 40.9287 | 11.3593 | 182 | 37.2377 | 65.7075 | 195.9136 | 0.064708
14025 | 1000.2415 | 16.4573 | 89.1854 | 129.9758 | 31.2511 | 14.25 | 131.8015 | 4.2316 |  | 23.1174 | 66.4638 | 11.6332 |  | 107.7174 | 185.552 | 25.4066 | 44.7081 | 13.7545 | 247 | 37.8726 | 68.9608 | 210.3058 | 0.24365
14026 | 1031.6985 | 10.7386 | 88.6416 | 137.9357 | 29.1528 | 17.0992 | 131.5735 | 3.9559 |  | 20.9779 | 64.9921 | 11.6293 |  | 114.821 | 208.369 | 25.8248 | 47.7535 | 14.4518 | 239 | 31.7092 | 73.9576 | 207.5516 | 0.2571
14027 | 1065.759 | 6.1631 | 90.0023 | 135.6709 | 33.6531 | 15.2005 | 132.2938 | 3.9742 |  | 23.7271 | 65.1684 | 13.6974 |  | 118.9896 | 212.7332 | 26.1922 | 48.5315 | 14.4674 | 221 | 31.8792 | 64.4673 | 209.6849 | 0.28135
14028 | 1081.8111 | 4.1544 | 94.5155 | 134.6209 | 35.3916 | 15.2 | 134.2324 | 4.3778 |  | 18.4567 | 66.8442 | 16.8561 |  | 119.6045 | 217.2984 | 27.0308 | 48.5904 | 14.4741 | 241 | 33.2558 | 68.7392 | 207.3782 | 0.28899
14029 | 1080.6457 | 4.0247 | 98.9367 | 140.0449 | 32.6749 | 18.9989 | 137.8246 | 3.9389 |  | 14.5769 | 67.9892 | 16.1248 |  | 124.1398 | 216.4973 | 25.0303 | 49.9666 | 14.7999 | 211 | 35.9338 | 66.589 | 210.1572 | 0.3187
14030 | 1081.2576 | 6.2195 | 96.9191 | 142.6705 | 36.8728 | 16.1508 | 139.8515 | 3.7461 |  | 13.8474 | 66.5043 | 17.0873 |  | 122.5787 | 215.7004 | 19.9207 | 50.3398 | 13.6414 | 202 | 42.3048 | 60.5294 | 210.4842 | 0.32081
14031 | 1081.347 | 10.3794 | 90.2894 | 125.3808 | 38.342 | 16.15 | 141.0157 | 3.7413 |  | 13.7276 | 63.8363 | 14.9884 |  | 106.4876 | 209.5578 | 17.7963 | 48.9869 | 8.0613 | 191 | 35.7973 | 64.2362 | 198.3299 | 0.28287
14032 | 1042.9799 | 9.691 | 71.0688 | 113.1964 | 46.7434 | 11.4013 | 123.1329 | 3.3847 |  | 14.7129 | 57.104 | 7.4577 |  | 87.7054 | 187.5968 | 15.8559 | 45.5106 | 5.439 | 192 | 28.8013 | 56.4735 | 183.2467 | 0.26892
14033 | 1023.796 | 9.9508 | 62.1655 | 111.7172 | 54.4063 | 6.6513 | 90.8814 | 2.4933 |  | 12.416 | 47.4738 | 5.5555 |  | 74.9538 | 164.9909 | 15.0645 | 43.4169 | 5.6814 | 157 | 27.0543 | 57.4241 | 147.0983 | 0.25029
14034 | 987.6929 | 9.4078 | 46.7483 | 107.5583 | 50.5942 | 8.5495 | 72.5376 | 1.5751 |  | 9.0092 | 43.692 | 4.4592 |  | 58.9039 | 150.5883 | 15.2407 | 41.694 | 5.2636 | 155 | 28.8843 | 56.4284 | 128.8316 | 0.23383
14035 | 951.0863 | 6.5188 | 34.0455 | 108.3228 | 47.6328 | 8.55 | 73.0155 | 1.0783 |  | 7.4183 | 42.7022 | 3.7663 |  | 48.0458 | 145.2923 | 14.0871 | 39.9621 | 4.7907 | 140 | 27.539 | 48.0021 | 106.8674 | 0.14182
14036 | 915.2974 | 5.829 | 30.5056 | 109.1591 | 43.8677 | 6.6505 | 74.1284 | 1.1394 |  | 6.7767 | 40.3531 | 3.9613 |  | 45.0682 | 134.3121 | 13.3603 | 38.2585 | 4.6244 | 130 | 24.4588 | 53.4038 | 103.0623 | 0.0079485
14037 | 882.414 | 4.7577 | 29.6897 | 104.4892 | 31.4126 | 8.5495 | 75.8531 | 1.3798 |  | 8.8021 | 34.4376 | 5.9476 |  | 45.1563 | 128.2029 | 13.2548 | 37.6037 | 4.5126 | 124 | 25.3447 | 52.7542 | 104.4204 | 0
14038 | 869.9376 | 4.1105 | 29.4972 | 99.249 | 27.4416 | 7.6003 | 75.6633 | 1.3695 |  | 8.7938 | 31.6217 | 6.6148 |  | 41.8761 | 120.8794 | 13.0927 | 37.538 | 4.4866 | 107 | 25.8602 | 47.3244 | 106.9086 | 0
14039 | 269.063 | 0 | 8.4431 | 0 | 14.1179 | 0.002112 | 23.5806 | 0.4357 |  | 2.6929 | 10.8759 | 2.098 |  | 0 | 0 | 3.6998 | 0 | 1.4913 | 107 | 2.5318 | 6.1024 | 10.9153 | 0
14040 | 867.4498 | 2.4605 | 28.9913 | 98.5209 | 30.053 | 8.5497 | 70.7962 | 1.833 |  | 8.9867 | 31.6605 | 7.2947 |  | 40.3078 | 116.8176 | 12.1994 | 37.07 | 4.6584 | 106 | 27.1205 | 51.9947 | 99.9373 | 0
14041 | 858.5236 | 2.3586 | 28.0355 | 103.5672 | 35.1399 | 8.55 | 72.9787 | 1.7521 |  | 9.5755 | 32.1174 | 6.4917 |  | 39.775 | 113.2925 | 12.0606 | 36.9013 | 4.7571 | 97 | 25.9302 | 48.4713 | 100.7583 | 0
14042 | 851.8548 | 2.3028 | 28.0739 | 99.82 | 34.9072 | 8.55 | 62.5588 | 1.6635 |  | 9.6196 | 32.2172 | 8.3459 |  | 40.2743 | 112.4954 | 12.2817 | 37.0413 | 4.4084 | 101 | 25.1539 | 53.549 | 99.6934 | 0
14043 | 847.1357 | 2.2338 | 29.0605 | 97.1177 | 34.6123 | 7.6003 | 64.7551 | 1.5696 |  | 9.6651 | 31.7791 | 14.1113 |  | 40.1353 | 116.2194 | 12.692 | 37.3018 | 3.2716 | 102 | 24.1506 | 49.6217 | 100.0445 | 0
14044 | 846.6473 | 2.7743 | 33.8333 | 99.5272 | 36.085 | 9.4995 | 67.5758 | 1.7003 |  | 10.3868 | 31.5587 | 14.4667 |  | 39.84 | 112.1245 | 12.0605 | 37.5736 | 2.8147 | 101 | 24.2181 | 50.6437 | 104.7258 | 0
14045 | 856.0938 | 3.2131 | 35.0389 | 99.649 | 35.7522 | 8.5503 | 75.5311 | 1.9888 |  | 12.9349 | 35.4165 | 9.8268 |  | 44.5712 | 106.9894 | 11.8457 | 37.4568 | 2.7187 | 102 | 24.5432 | 54.1927 | 111.9415 | 0
14046 | 876.0835 | 4.2379 | 32.2017 | 103.4548 | 37.4159 | 10.4495 | 91.1749 | 1.4978 |  | 14.8923 | 43.0279 | 13.4456 |  | 54.1539 | 110.0602 | 12.3153 | 36.6694 | 3.3843 | 143 | 25.4053 | 47.9587 | 147.6535 | 0.11113
14047 | 915.1821 | 6.4503 | 51.2161 | 106.2754 | 39.7057 | 12.3392 | 120.3188 | 2.6257 |  | 13.2844 | 51.9242 | 22.4155 |  | 69.2262 | 133.0951 | 18.879 | 38.2403 | 9.0711 | 203 | 33.3038 | 62.1933 | -9.0332 | 0.25425
14048 | 955.1238 | 9.1791 | 76.8611 | 115.509 | 40.5637 | 14.2597 | 136.393 | 3.8673 |  | 12.9787 | 59.7109 | 18.7585 |  | 94.6503 | 167.6111 | 24.938 | 40.8992 | 12.4442 | 200 | 40.8177 | 65.1628 | 194.6006 | 0.2161
14049 | 1002.5212 | 10.3834 | 90.0482 | 123.0034 | 46.4537 | 14.25 | 141.7348 | 4.125 |  | 14.3006 | 64.6202 | 15.93 |  | 115.2091 | 187.6312 | 29.739 | 44.2518 | 12.7293 | 249 | 35.7675 | 62.206 | 206.13 | 0.21381
14050 | 1042.2068 | 9.3949 | 90.9068 | 123.4622 | 51.6927 | 16.1495 | 146.8354 | 3.8459 |  | 16.112 | 69.1763 | 16.6452 |  | 125.4198 | 198.1533 | 31.7395 | 46.384 | 13.2433 | 256 | 33.6486 | 68.983 | 207.7921 | 0.24796
14051 | 1068.3381 | 14.8735 | 90.7643 | 122.966 | 57.1602 | 15.2003 | 152.2419 | 4.0339 |  | 15.4615 | 70.0395 | 16.2763 |  | 128.6184 | 198.7131 | 32.038 | 47.9175 | 14.1322 | 223 | 32.9295 | 64.0446 | 215.9308 | 0.22653
14052 | 1034.0758 | 16.454 | 91.9528 | 130.2108 | 58.7672 | 13.3005 | 155.2862 | 3.9195 |  | 13.2889 | 69.6234 | 18.3816 |  | 128.6991 | 198.2548 | 32.7875 | 47.5282 | 14.416 | 235 | 34.1445 | 65.6778 | 207.0559 | 0.15195
14053 | 1045.5251 | 11.9637 | 93.566 | 137.2882 | 60.4546 | 16.1358 | 163.8955 | 4.3817 |  | 12.8358 | 70.855 | 20.6016 |  | 130.3785 | 207.6329 | 29.9011 | 48.6901 | 14.6143 | 206 | 31.112 | 69.4958 | 214.8267 | 0.20417
14054 | 1061.9545 | 10.9204 | 96.8384 | 143.3099 | 63.1231 | 16.1634 | 167.1255 | 4.366 |  | 14.2639 | 72.2208 | 22.7563 |  | 130.9278 | 212.763 | 21.642 | 48.8823 | 15.0588 | 195 | 37.7073 | 61.8677 | 216.3072 | 0.21357
14055 | 1060.0028 | 12.1024 | 96.6756 | 127.5086 | 59.335 | 15.2003 | 161.803 | 4.0608 |  | 12.7998 | 72.0188 | 15.044 |  | 127.3007 | 213.8979 | 18.545 | 49.1375 | 15.6287 | 202 | 44.5627 | 69.0449 | 197.3959 | 0.25597
14056 | 1027.9771 | 9.9127 | 80.0973 | 117.0942 | 55.4284 | 15.2 | 136.3293 | 3.5901 |  | 12.0359 | 65.3137 | 6.8173 |  | 109.9249 | 197.0092 | 17.2398 | 48.1383 | 15.8864 | 179 | 42.9695 | 63.5429 | 180.3559 | 0.23734
14057 | 1002.391 | 7.1223 | 70.4265 | 111.873 | 63.0501 | 8.5518 | 94.9822 | 2.4983 |  | 11.2125 | 44.3496 | 4.6549 |  | 96.0254 | 174.6727 | 14.2147 | 44.6438 | 16.5618 | 158 | 35.1472 | 58.7926 | 143.7065 | 0.224
14058 | 981.859 | 4.2138 | 53.1906 | 110.0312 | 55.9076 | 10.4495 | 80.6392 | 1.3129 |  | 7.0763 | 47.5652 | 4.2633 |  | 81.0162 | 164.0161 | 13.1079 | 42.8186 | 14.6239 | 144 | 36.9802 | 68.0256 | 137.1565 | 0.10131
14059 | 934.8292 | 3.9224 | 40.6331 | 107.053 | 53.1445 | 8.5505 | 79.3788 | 0.97189 |  | 5.133 | 45.4146 | 4.0574 |  | 67.0313 | 149.948 | 13.1223 | 35.9642 | 9.411 | 128 | 34.3795 | 57.4365 | 114.9936 | 0.06479
14060 | 894.179 | 5.5523 | 36.0567 | 104.461 | 50.1484 | 7.6003 | 78.0177 | 1.2458 |  | 5.2291 | 43.2068 | 4.4274 |  | 60.8688 | 137.7996 | 13.1014 | 28.0963 | 6.7414 | 114 | 31.7452 | 57.5795 | 111.2864 | 0.00071759
14061 | 865.8154 | 4.8108 | 35.6465 | 105.4254 | 40.3271 | 8.5497 | 78.592 | 1.3576 |  | 7.3584 | 38.2726 | 6.5021 |  | 59.3061 | 130.0988 | 13.3574 | 26.6315 | 6.3297 | 120 | 31.9281 | 58.7569 | 111.1371 | 0
14062 | 846.9837 | 3.4538 | 35.9084 | 105.7756 | 40.7027 | 7.6003 | 80.5333 | 1.3423 |  | 8.0588 | 35.2758 | 6.9731 |  | 59.6225 | 126.61 | 14.2896 | 26.3825 | 6.5972 | 127 | 30.587 | 52.3968 | 108.7502 | 0
14063 | 259.2698 | 0 | 10.2557 | 0 | 20.3567 | 0.002112 | 25.3082 | 0.43785 |  | 2.5615 | 11.9483 | 2.1694 |  | 0 | 0 | 4.1611 | 0 | 2.2257 | 119 | 2.9338 | 6.7987 | 11.1314 | 0
14064 | 810.9513 | 2.6636 | 37.0346 | 105.5052 | 34.0652 | 8.55 | 72.1441 | 1.3474 |  | 9.7044 | 33.7296 | 6.6866 |  | 57.0188 | 112.297 | 16.6728 | 25.8179 | 3.7306 | 105 | 30.5001 | 65.1233 | 110.2392 | 0
14065 | 824.578 | 2.2993 | 37.3055 | 104.8807 | 31.4066 | 9.4997 | 72.1835 | 1.5104 |  | 10.35 | 34.3728 | 6.7294 |  | 55.3079 | 111.2282 | 17.9033 | 26.6019 | 3.0587 | 106 | 29.5038 | 66.1527 | 109.7189 | 0
14066 | 822.1477 | 2.2325 | 37.0537 | 104.3525 | 27.9261 | 9.5 | 66.4819 | 1.386 |  | 9.9805 | 34.0123 | 8.7724 |  | 55.7442 | 111.5686 | 17.9829 | 26.1073 | 2.8723 | 98 | 28.2505 | 69.7627 | 112.1291 | 0
14067 | 820.1799 | 2.2313 | 36.9067 | 104.5341 | 27.8379 | 7.6005 | 64.9622 | 1.3111 |  | 9.2731 | 33.7854 | 14.5924 |  | 55.1726 | 113.1536 | 17.5993 | 25.8057 | 2.8629 | 96 | 27.881 | 62.0659 | 111.2805 | 0
14068 | 817.7851 | 2.9487 | 42.8335 | 105.1143 | 26.4597 | 8.5521 | 69.6498 | 1.3298 |  | 9.7789 | 37.2225 | 14.3527 |  | 55.685 | 108.6596 | 16.6951 | 25.7697 | 2.8692 | 103 | 27.6164 | 68.1863 | 111.552 | 0
14069 | 836.1775 | 3.8355 | 42.8393 | 105.2038 | 25.2172 | 9.4974 | 67.0829 | 1.258 |  | 12.0465 | 34.9612 | 10.6584 |  | 55.231 | 108.1396 | 14.5849 | 25.2941 | 2.8983 | 84 | 27.5712 | 65.6668 | 119.3515 | 0
14070 | 883.9983 | 4.5639 | 41.0975 | 106.0503 | 27.1152 | 9.5 | 92.7464 | 1.082 |  | 13.5073 | 38.8068 | 14.0352 |  | 60.1069 | 113.7065 | 13.3216 | 24.975 | 5.8816 | 77 | 26.4035 | 56.5891 | 135.0352 | 0.037116
14071 | 924.6939 | 7.5515 | 61.2685 | 106.0625 | 25.6455 | 12.3492 | 126.9257 | 2.4504 |  | 11.9743 | 52.7235 | 21.8522 |  | 76.1192 | 137.0128 | 14.7013 | 27.0156 | 10.2251 | 183 | 38.7736 | 70.2213 | 162.8444 | 0.042203
14072 | 967.6603 | 15.6553 | 85.821 | 117.3569 | 21.1572 | 17.0987 | 143.2814 | 4.579 |  | 11.7074 | 61.6723 | 15.3206 |  | 105.4754 | 162.4143 | 20.6749 | 30.6191 | 13.3344 | 185 | 53.4337 | 66.0488 | 197.3073 | 0.077
14073 | 1026.7126 | 17.2807 | 97.5463 | 133.4862 | 22.9067 | 16.1503 | 150.0863 | 4.6571 |  | 12.01 | 70.9334 | 12.6739 |  | 125.7455 | 186.7275 | 29.6764 | 36.5684 | 15.4058 | 216 | 55.2966 | 63.7832 | 208.9555 | 0.12829
14074 | 1063.8646 | 10.3625 | 100.5482 | 139.4371 | 19.9002 | 14.2505 | 150.893 | 4.7785 |  | 12.222 | 75.0493 | 12.4422 |  | 135.427 | 204.1581 | 32.5406 | 40.1162 | 16.6467 | 262 | 53.8459 | 72.12 | 205.308 | 0.11634
14075 | 1098.6827 | 5.3532 | 99.0507 | 146.0008 | 24.1211 | 17.0992 | 149.5638 | 4.7106 |  | 11.9121 | 76.4358 | 12.2521 |  | 140.9019 | 216.3026 | 32.8693 | 41.3555 | 16.967 | 241 | 54.6222 | 65.5904 | 213.6207 | 0.20693
14076 | 1089.9202 | 4.577 | 97.14 | 144.7821 | 37.006 | 16.1503 | 152.9849 | 4.7198 |  | 12.0237 | 77.6403 | 11.6777 |  | 143.8497 | 214.9355 | 33.1458 | 40.5538 | 16.7327 | 254 | 54.7369 | 0 | 205.9162 | 0.16375
14077 | 1088.7395 | 6.6555 | 99.8864 | 142.0988 | 43.5876 | 17.0997 | 157.5355 | 4.7832 |  | 12.6491 | 79.966 | 12.2636 |  | 143.1691 | 221.3909 | 32.082 | 40.5778 | 18.6149 | 233 | 51.6871 | 65.2374 | 208.896 | 0.18402
14078 | 1081.3997 | 5.3753 | 99.8227 | 145.5745 | 56.5971 | 13.3011 | 162.3147 | 4.7038 |  | 14.4872 | 80.269 | 14.339 |  | 135.4473 | 220.9524 | 24.4703 | 39.877 | 16.9768 | 220 | 44.7351 | 64.452 | 214.621 | 0.19612
14079 | 1074.7148 | 4.2872 | 93.3629 | 128.3561 | 57.6049 | 16.1492 | 165.6725 | 3.9973 |  | 13.4193 | 80.0556 | 13.7728 |  | 119.1279 | 214.644 | 20.0552 | 38.3831 | 15.8335 | 241 | 36.8245 | 66.0772 | 202.4135 | 0.13093
14080 | 1050.258 | 4.2924 | 66.3395 | 117.6523 | 55.9918 | 11.4013 | 155.3124 | 3.0871 |  | 12.6555 | 75.0377 | 14.2891 |  | 107.2147 | 196.2909 | 17.7414 | 36.7384 | 16.1957 | 207 | 24.0776 | 57.1524 | 175.1227 | 0.078269
14081 | 981.1627 | 3.7572 | 52.2067 | 111.3768 | 49.6639 | 7.6011 | 110.8449 | 2.6009 |  | 11.0387 | 59.8521 | 15.0122 |  | 96.5251 | 166.8139 | 13.8309 | 33.9444 | 16.0752 | 167 | 32.331 | 57.156 | 142.0427 | 0.056816
14082 | 950.1587 | 3.0705 | 37.8454 | 104.9399 | 49.1268 | 7.6 | 93.2528 | 1.9096 |  | 7.5054 | 51.7269 | 10.3745 |  | 68.7032 | 151.3583 | 11.6105 | 31.4972 | 13.639 | 154 | 32.2328 | 61.1984 | 135.3561 | 0.034172
14083 | 939.676 | 2.539 | 28.3873 | 101.5934 | 49.3262 | 7.6 | 91.0999 | 1.3212 |  | 6.1557 | 49.4358 | 9.3779 |  | 53.0647 | 144.2606 | 11.5877 | 28.3811 | 13.7115 | 125 | 34.0464 | 51.5529 | 114.6989 | 0.014653
14084 | 924.6906 | 4.4704 | 26.5776 | 102.0106 | 42.1526 | 8.5497 | 82.8462 | 1.2395 |  | 5.373 | 47.1144 | 5.9296 |  | 48.5818 | 138.4699 | 11.9005 | 26.9888 | 15.2816 | 113 | 35.8322 | 55.9435 | 110.2473 | 0.0001104
14085 | 899.194 | 7.35 | 26.5982 | 102.2479 | 34.2497 | 10.4495 | 78.0625 | 1.2751 |  | 6.0311 | 41.8008 | 10.8549 |  | 47.6556 | 124.754 | 12.0652 | 26.9786 | 15.7476 | 121 | 31.946 | 54.6915 | 108.5892 | 0
14086 | 876.0472 | 7.8772 | 26.7014 | 104.0728 | 33.1902 | 7.6008 | 78.4128 | 1.2817 |  | 7.3352 | 39.6239 | 11.0853 |  | 45.7402 | 117.9153 | 12.1255 | 26.9089 | 15.9076 | 119 | 32.4117 | 50.1616 | 109.433 | 0
14087 | 275.2798 | 0 | 7.8679 | 0 | 16.0209 | 0.002112 | 25.2562 | 0.43071 |  | 2.5659 | 13.9892 | 3.1462 |  | 0 | 0 | 3.5571 | 0 | 5.4041 | 116 | 3.2425 | 6.9614 | 11.1285 | 0
14088 | 848.417 | 6.0534 | 26.4414 | 102.1587 | 31.9954 | 7.6 | 74.3605 | 1.4292 |  | 8.658 | 38.4011 | 6.8866 |  | 46.7718 | 124.7419 | 15.461 | 25.8109 | 14.6486 | 106 | 29.6075 | 60.7388 | 109.4836 | 0
14089 | 851.2733 | 4.2228 | 26.4388 | 103.53 | 30.2633 | 8.5497 | 76.0671 | 1.3274 |  | 9.0351 | 37.9818 | 6.8105 |  | 42.3524 | 127.3621 | 16.2415 | 25.8391 | 14.4597 | 102 | 28.2535 | 59.4231 | 108.7801 | 0
14090 | 852.8781 | 3.5678 | 26.3918 | 103.3328 | 30.8233 | 7.6003 | 78.4146 | 1.4129 |  | 9.015 | 37.7798 | 8.8643 |  | 41.4263 | 124.5782 | 16.2433 | 25.9414 | 13.6225 | 103 | 28.5687 | 63.926 | 107.8605 | 0
14091 | 856.4192 | 3.1092 | 26.4582 | 102.6436 | 29.375 | 8.5497 | 74.5396 | 1.434 |  | 9.1141 | 37.5496 | 14.1349 |  | 42.1144 | 122.5808 | 16.6188 | 26.157 | 12.7221 | 99 | 27.468 | 60.3648 | 108.3345 | 0
14092 | 876.8574 | 4.3375 | 45.4985 | 103.9934 | 28.2686 | 9.4984 | 90.2483 | 1.511 |  | 11.1407 | 43.5729 | 16.7725 |  | 53.4512 | 121.5348 | 14.9558 | 26.3713 | 12.7988 | 96 | 29.0785 | 60.4396 | 129.8564 | 0
14093 | 885.742 | 0 | 0 | 0 | -10.0014 | 9.5013 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0
14094 | 885.742 | 0 | 0 | 0 | -10.0014 | 9.5013 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0.11675
14095 | 885.742 | 0 | 0 | 0 | -10.0014 | 9.5013 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 0.042308
14096 | 954.0895 | 9.084 | 82.9562 | 117.5786 | 28.6631 | 15.2079 | 135.4042 | 3.9112 |  | 11.698 | 60.1523 | 20.0654 |  | 93.8339 | 154.5778 | 27.0733 | 30.2339 | 13.7248 | 218 | 49.9464 | 68.921 | 194.0313 | 0.16911
14097 | 1042.6979 | 10.116 | 100.1966 | 130.7646 | 31.316 | 15.1958 | 153.1888 | 4.7066 |  | 11.3128 | 71.6128 | 20.6536 |  | 119.3047 | 186.3333 | 34.1474 | 34.75 | 14.8634 | 239 | 47.7863 | 66.338 | 209.5586 | 0.10735
14098 | 1087.4741 | 6.2984 | 101.3359 | 133.0562 | 33.5964 | 17.0995 | 151.7895 | 4.4104 |  | 11.7385 | 75.5971 | 18.0034 |  | 134.5925 | 203.2563 | 33.6194 | 38.6201 | 15.2946 | 254 | 3.6918 | 74.453 | 211.4377 | 0.22973
14099 | 1099.2071 | 6.793 | 104.1314 | 138.1472 | 38.1968 | 17.1 | 144.5454 | 4.494 |  | 12.6623 | 78.2938 | 14.8227 |  | 140.2056 | 214.1906 | 32.6137 | 39.9728 | 15.1403 | 256 | 38.3873 | 69.9325 | 211.7244 | 0.27578
14100 | 1093.3147 | 7.369 | 105.9833 | 135.2742 | 39.5411 | 17.1 | 143.9432 | 4.5116 |  | 12.8729 | 78.4425 | 14.8461 |  | 140.0438 | 216.3316 | 32.3875 | 40.4357 | 15.5394 | 251 | 40.236 | 0 | 211.933 | 0.29222
14101 | 1078.2085 | 4.7755 | 106.5165 | 134.2015 | 42.8474 | 16.1503 | 146.5842 | 4.465 |  | 14.9694 | 82.3627 | 13.4091 |  | 139.7126 | 220.3262 | 30.6661 | 40.2918 | 16.0626 | 215 | 37.4611 | 70.0939 | 205.8083 | 0.31567
14102 | 1094.9383 | 4.2095 | 99.6526 | 139.9068 | 46.8151 | 14.2545 | 146.8796 | 4.2377 |  | 15.1061 | 82.795 | 16.5113 |  | 137.8314 | 217.2372 | 23.513 | 39.1075 | 16.22 | 197 | 37.9614 | 0 | 209.4188 | 0.31875
14103 | 1062.5702 | 4.9735 | 90.9488 | 124.2431 | 46.2456 | 16.1455 | 146.7475 | 4.167 |  | 12.9703 | 77.6991 | 18.2873 |  | 128.9789 | 219.6684 | 20.6086 | 44.1913 | 16.5879 | 221 | 39.4004 | 69.654 | 196.639 | 0.26703
14104 | 1024.8438 | 9.2499 | 62.8366 | 112.5701 | 52.3221 | 11.4045 | 130.5938 | 3.7112 |  | 12.0186 | 70.2873 | 12.052 |  | 113.2531 | 208.9299 | 16.8584 | 39.8915 | 16.7842 | 196 | 35.252 | 67.1437 | 173.226 | 0.25839
14105 | 989.9984 | 10.0666 | 48.4948 | 109.0627 | 56.3678 | 7.5979 | 91.4393 | 2.7902 |  | 10.9153 | 56.0674 | 5.1069 |  | 91.3777 | 187.143 | 12.5201 | 35.4594 | 16.2683 | 183 | 29.2606 | 59.7898 | 137.6585 | 0.25788
14106 | 962.619 | 5.2535 | 32.5595 | 104.7938 | 53.9104 | 8.5521 | 71.6973 | 2.3911 |  | 7.8677 | 49.709 | 3.4012 |  | 68.718 | 174.6738 | 11.3642 | 32.7921 | 15.7102 | 174 | 37.1631 | 63.0689 | 129.4358 | 0.246
14107 | 927.9041 | 2.9931 | 23.5299 | 101.2236 | 52.4984 | 9.4974 | 73.6407 | 2.2374 |  | 6.5491 | 48.1063 | 3.6079 |  | 57.5168 | 160.0512 | 11.4182 | 29.2279 | 14.9306 | 155 | 42.0143 | 0 | 109.5465 | 0.15985
14108 | 891.2944 | 3.6895 | 20.7432 | 101.1959 | 50.3591 | 8.5503 | 69.7255 | 1.5729 |  | 5.1635 | 46.5075 | 3.2993 |  | 50.8783 | 147.9138 | 11.0778 | 27.6483 | 15.1732 | 137 | -0.14876 | 56.9223 | 104.875 | 0
14109 | 877.9841 | 4.4785 | 19.5241 | 103.7401 | 46.4031 | 7.6003 | 62.6857 | 2.0541 |  | 5.5252 | 40.7727 | 4.7175 |  | 47.7052 | 141.0367 | 11.771 | 26.9722 | 15.2973 | 138 | 37.534 | 61.6357 | 105.4207 | 0
14110 | 882.327 | 4.6807 | 19.6742 | 111.704 | 40.5259 | 8.5497 | 65.2065 | 1.857 |  | 6.5073 | 37.1692 | 5.8619 |  | 47.7409 | 138.9017 | 11.9695 | 26.9197 | 14.4315 | 126 | 35.6316 | 59.4606 | 109.2545 | 0
14111 | 280.4892 | 0 | 5.8222 | 0 | 19.2456 | 0.002376 | 21.5825 | 0.52827 |  | 2.249 | 12.91 | 1.9959 |  | 0 | 0 | 3.4947 | 0 | 4.7472 | 112 | 3.5482 | 8.1111 | 11.4738 | 0
14112 | 870.7056 | 3.6444 | 19.5139 | 111.4357 | 34.0235 | 9.4997 | 65.5017 | 1.7322 |  | 8.2867 | 36.688 | 5.9754 |  | 43.292 | 118.9665 | 15.9197 | 26.7912 | 12.9653 | 114 | 32.8752 | 78.3574 | 108.0425 | 0
14113 | 878.8923 | 3.2496 | 19.0626 | 109.304 | 30.4955 | 8.5503 | 65.1234 | 2.3124 |  | 8.8838 | 36.5122 | 5.962 |  | 41.4663 | 114.3947 | 16.9182 | 26.6841 | 12.5072 | 112 | 33.7165 | 71.2928 | 106.5084 | 0
14114 | 877.6963 | 2.9486 | 19.1647 | 109.1522 | 29.6228 | 8.55 | 62.2924 | 1.8948 |  | 8.942 | 36.2758 | 8.0749 |  | 40.796 | 116.0878 | 15.723 | 26.7653 | 12.3833 | 109 | 35.1769 | 75.6481 | 108.1956 | 0
14115 | 876.3221 | 2.5025 | 18.954 | 110.621 | 33.6547 | 9.4997 | 64.1193 | 1.5793 |  | 8.9858 | 36.5932 | 13.6653 |  | 40.682 | 114.6248 | 15.9981 | 26.8545 | 12.3997 | 107 | 34.7249 | 78.0048 | 110.522 | 0
14116 | 868.7036 | 2.2453 | 18.8752 | 109.457 | 31.91 | 8.5503 | 60.9362 | 2.3018 |  | 9.4035 | 36.64 | 13.4232 |  | 40.7784 | 112.4544 | 15.4393 | 26.7853 | 12.3235 | 110 | 35.2189 | 70.416 | 112.2494 | 0
14117 | 875.7836 | 2.7022 | 28.1003 | 106.6339 | 35.0234 | 9.4997 | 56.9906 | 1.8132 |  | 10.7917 | 36.6442 | 8.4233 |  | 45.8909 | 107.3686 | 11.9026 | 26.2949 | 12.1735 | 111 | 34.3522 | 74.8554 | 119.9031 | 0
14118 | 919.7676 | 4.2906 | 40.2098 | 107.9503 | 37.9396 | 11.3995 | 82.4863 | 1.4502 |  | 13.2523 | 45.5239 | 13.5139 |  | 57.1173 | 113.7308 | 11.9056 | 26.3384 | 13.289 | 144 | 31.9631 | 63.937 | 133.852 | 0.18543
14119 | 964.7153 | 10.539 | 59.6276 | 104.9442 | 37.8693 | 12.3497 | 119.5165 | 2.8468 |  | 11.3341 | 58.5805 | 25.7182 |  | 75.9956 | 137.1717 | 14.1275 | 28.8191 | 15.1214 | 216 | 39.5607 | 64.1595 | 170.257 | 0.27483
14120 | 1016.4364 | 18.4954 | 83.181 | 115.234 | 37.7797 | 15.1992 | 133.5606 | 4.1145 |  | 10.2093 | 63.9328 | 25.0641 |  | 104.9452 | 175.3688 | 17.5597 | 32.8245 | 14.1947 | 215 | 51.5747 | 70.6536 | 191.9098 | 0.31828
14121 | 1058.441 | 13.1244 | 95.46 | 128.2675 | 46.0576 | 12.3508 | 134.5882 | 4.1205 |  | 11.2634 | 67.3997 | 22.7204 |  | 121.7212 | 199.0005 | 26.366 | 35.9227 | 14.1198 | 246 | 44.3767 | 63.9285 | 200.8683 | 0.2912
14122 | 1074.6182 | 5.6222 | 98.1085 | 134.9227 | 51.3896 | 14.2495 | 135.6941 | 4.2406 |  | 12.0902 | 71.5383 | 23.1042 |  | 128.8972 | 219.6523 | 29.9807 | 37.4019 | 15.4921 | 266 | 39.6156 | 76.7173 | 203.7918 | 0.26105
14123 | 1093.3447 | 3.8884 | 98.0049 | 136.0488 | 53.8209 | 14.25 | 137.1424 | 4.5456 |  | 14.3364 | 72.3427 | 23.9203 |  | 130.7674 | 228.4401 | 30.9156 | 38.9008 | 16.4794 | 256 | 43.5629 | 75.0182 | 207.2771 | 0.28761
14124 | 1079.1574 | 5.6163 | 97.9287 | 134.2422 | 48.4452 | 14.25 | 138.5332 | 4.8621 |  | 13.2665 | 73.303 | 16.101 |  | 132.1562 | 230.6597 | 30.6928 | 38.1694 | 17.1285 | 235 | 50.7023 | 80.092 | 203.6016 | 0.2918
14125 | 1076.8764 | 7.3215 | 100.1256 | 135.1578 | 42.2966 | 17.0992 | 140.9582 | 4.9122 |  | 15.0373 | 73.8476 | 14.8174 |  | 132.0981 | 231.3641 | 27.3684 | 38.9425 | 17.4321 | 216 | 48.355 | 76.9033 | 201.7209 | 0.31727
14126 | 1082.6321 | 7.3901 | 100.9424 | 138.3734 | 46.3846 | 13.3011 | 141.9253 | 4.5938 |  | 13.7549 | 75.1799 | 15.3887 |  | 129.5958 | 226.0001 | 19.6776 | 37.9992 | 17.0813 | 239 | 46.8309 | 74.779 | 197.641 | 0.30471
14127 | 1041.6603 | 5.1274 | 99.0506 | 124.9118 | 40.4296 | 18.9984 | 140.9205 | 3.9555 |  | 12.2338 | 75.0469 | 9.9855 |  | 120.1201 | 216.0073 | 16.1379 | 37.2209 | 16.7109 | 216 | 36.3351 | 69.9114 | 189.3527 | 0.28275
14128 | 1007.4705 | 3.7292 | 82.9963 | 115.1344 | 41.9327 | 18.0553 | 130.2134 | 2.379 |  | 12.5259 | 68.5556 | 4.8917 |  | 106.0826 | 199.9843 | 14.3676 | 35.6726 | 16.5687 | 188 | 26.814 | 69.6338 | 166.984 | 0.27036
14129 | 948.3863 | 3.0776 | 69.9524 | 109.8623 | 50.9611 | 9.4974 | 93.0677 | 1.3848 |  | 11.1186 | 55.3973 | 4.0453 |  | 88.4381 | 174.7643 | 12.4808 | 32.8108 | 16.3028 | 156 | 21.6994 | 67.1367 | 135.6378 | 0.25628
14130 | 905.5695 | 3.0264 | 54.7256 | 104.9997 | 47.8578 | 7.6005 | 75.1643 | 1.0839 |  | 9.227 | 48.2056 | 3.5879 |  | 69.098 | 153.4338 | 11.5981 | 30.6141 | 13.5762 | 148 | 25.9055 | 62.9893 | 124.5806 | 0.23052
14131 | 888.1246 | 3.628 | 44.879 | 103.4784 | 45.2544 | 7.6 | 73.5498 | 0.96517 |  | 6.9126 | 42.5491 | 3.2372 |  | 55.1353 | 147.4393 | 10.8367 | 28.6211 | 7.6222 | 126 | 29.7752 | 67.354 | 105.4348 | 0.011848
14132 | 878.3799 | 4.4474 | 42.7645 | 103.031 | 36.8761 | 7.6 | 67.3647 | 1.1488 |  | 5.1266 | 39.6364 | 3.2005 |  | 48.8055 | 138.3588 | 11.6835 | 28.0876 | 4.0506 | 118 | 30.4914 | 63.8232 | 102.2473 | 0
14133 | 875.6221 | 4.8587 | 42.4816 | 103.3317 | 29.7517 | 8.5497 | 70.3264 | 2.0078 |  | 6.9989 | 38.7155 | 4.8221 |  | 48.7071 | 138.5876 | 10.7311 | 27.7904 | 4.0431 | 120 | 31.6825 | 61.216 | 105.1484 | 0
14134 | 868.6022 | 4.6147 | 38.4731 | 104.578 | 36.3328 | 7.6003 | 73.2019 | 1.8469 |  | 7.1765 | 37.9157 | 6.5564 |  | 48.6801 | 137.2057 | 11.8745 | 27.0226 | 4.4279 | 115 | 36.8524 | 67.8134 | 106.0575 | 0
14135 | 270.2284 | 1.5607 | 10.6594 | 29.3114 | 19.4203 | 0.002112 | 23.1516 | 0.52202 |  | 2.1988 | 13.095 | 2.2832 |  | 14.1154 | 45.6232 | 3.6461 | 7.6151 | 1.4931 | 111 | 3.6884 | 9.2653 | 10.8165 | 0
14136 | 843.1812 | 3.8226 | 36.8836 | 103.3358 | 29.7122 | 10.4497 | 69.9761 | 1.7796 |  | 6.6348 | 37.4639 | 6.2291 |  | 43.279 | 124.8542 | 11.3777 | 26.3077 | 3.6957 | 108 | 32.8311 | 76.9215 | 104.2445 | 0
14137 | 838.1846 | 2.9629 | 36.4881 | 102.9732 | 30.583 | 9.5003 | 71.0508 | 1.6489 |  | 6.5374 | 36.9175 | 6.0777 |  | 43.1123 | 120.0157 | 12.0557 | 26.3329 | 3.1762 | 103 | 31.8448 | 81.4741 | 103.732 | 0
14138 | 832.505 | 3.4664 | 47.2443 | 104.8748 | 31.4372 | 7.6005 | 65.862 | 1.5193 |  | 6.5085 | 36.9384 | 6.0957 |  | 41.0361 | 119.5037 | 12.3272 | 26.3483 | 3.0344 | 102 | 31.1097 | 79.1172 | 103.7523 | 0
14139 | 847.2993 | 3.3228 | 52.8559 | 103.3088 | 32.0222 | 6.6503 | 67.9182 | 2.1793 |  | 6.5158 | 37.2182 | 6.1152 |  | 40.4268 | 120.2113 | 11.1345 | 26.6704 | 2.9924 | 101 | 30.0696 | 76.4446 | 103.5631 | 0
14140 | 836.7939 | 3.0005 | 55.6879 | 102.4272 | 29.6897 | 8.5495 | 71.6078 | 1.8652 |  | 6.5075 | 37.0957 | 6.0991 |  | 40.672 | 115.9257 | 11.3568 | 26.7629 | 2.9879 | 101 | 30.5141 | 81.6769 | 102.3194 | 0
14141 | 846.7698 | 3.5152 | 46.6968 | 101.5022 | 29.4998 | 8.55 | 75.0007 | 1.4218 |  | 4.7948 | 40.9042 | 4.6438 |  | 39.3891 | 110.7169 | 11.1444 | 26.4007 | 2.9005 | 95 | 30.8573 | 77.2517 | 102.2781 | 0
14142 | 862.298 | 2.8904 | 37.9121 | 100.5356 | 33.2353 | 9.4997 | 77.895 | 1.5434 |  | 3.8522 | 42.0285 | 3.4512 |  | 37.6437 | 111.239 | 10.6719 | 26.0965 | 2.8338 | 97 | 29.4757 | 65.026 | 97.435 | 0.18434
14143 | 875.405 | 2.2521 | 35.7383 | 100.0202 | 41.1924 | 7.6005 | 73.3358 | 1.3711 |  | 3.8251 | 37.9651 | 3.25 |  | 37.2327 | 110.1563 | 10.4584 | 25.9454 | 2.8625 | 105 | 32.9405 | 67.2406 | 99.8329 | 0.26802
14144 | 884.9224 | 2.0731 | 35.9118 | 109.9337 | 42.9611 | 8.5497 | 69.2866 | 1.2829 |  | 4.3893 | 35.9327 | 3.2483 |  | 41.0244 | 113.1731 | 12.9124 | 25.9839 | 3.1324 | 105 | 41.4855 | 60.4041 | 100.1698 | 0.16921
14145 | 898.4338 | 2.5546 | 36.0086 | 118.802 | 44.0719 | 8.55 | 73.4764 | 1.2781 |  | 4.5987 | 38.0689 | 3.3417 |  | 49.3548 | 117.3602 | 20.3939 | 25.7335 | 6.3479 | 110 | 37.4607 | 66.6959 | 98.6484 | 0.3323
14146 | 898.535 | 2.4395 | 35.8937 | 123.9231 | 46.5523 | 7.6003 | 75.0048 | 1.0898 |  | 6.8496 | 43.94 | 3.3107 |  | 58.7093 | 125.3201 | 23.1719 | 25.9429 | 12.2751 | 121 | 33.627 | 66.6431 | 102.8893 | 0.26148
14147 | 892.6203 | 2.8862 | 35.5429 | 122.2602 | 48.1801 | 7.6 | 78.5737 | 0.99068 |  | 9.7898 | 46.777 | 3.2331 |  | 62.0269 | 129.6294 | 23.5054 | 26.2122 | 14.269 | 125 | 33.6401 | 60.8276 | 105.0976 | 0.28318
14148 | 887.8737 | 2.8609 | 34.4443 | 122.4919 | 49.2048 | 7.6 | 89.9204 | 1.5497 |  | 12.2244 | 46.7409 | 3.3221 |  | 63.8575 | 134.2488 | 22.3778 | 26.0668 | 14.0199 | 130 | 32.6649 | 66.5463 | 106.6899 | 0.19618
14149 | 888.9382 | 2.6431 | 34.1498 | 123.8259 | 48.6104 | 8.5497 | 108.936 | 1.2761 |  | 12.1802 | 47.003 | 3.1996 |  | 65.2499 | 137.4122 | 20.1348 | 26.0567 | 14.3931 | 133 | 28.6011 | 63.4866 | 105.2845 | 0.26437
14150 | 887.9411 | 2.6698 | 34.4406 | 124.0782 | 46.8858 | 9.4997 | 95.3392 | 0.99073 |  | 11.1174 | 48.8846 | 3.4739 |  | 66.0898 | 145.545 | 13.2473 | 26.286 | 15.111 | 143 | 31.9015 | 64.3142 | 105.7713 | 0.15241
14151 | 887.2016 | 2.6404 | 34.6008 | 109.9273 | 45.4065 | 9.5 | 79.6133 | 1.0459 |  | 8.1332 | 49.2075 | 3.321 |  | 67.4936 | 158.6347 | 10.7536 | 27.1639 | 15.4441 | 147 | 35.7981 | 68.7094 | 105.2063 | 0.24212
14152 | 909.8648 | 2.2175 | 34.8965 | 101.6038 | 46.3753 | 7.6005 | 82.861 | 1.1323 |  | 5.6349 | 47.5615 | 3.2419 |  | 69.4115 | 161.4524 | 10.8231 | 27.6108 | 15.827 | 151 | 36.6212 | 64.5146 | 102.2558 | 0.14071
14153 | 924.9993 | 2.1921 | 35.4334 | 100.8795 | 41.3491 | 8.5497 | 79.4787 | 1.0188 |  | 4.8038 | 42.4701 | 3.2705 |  | 64.1591 | 158.9341 | 11.1208 | 28.0564 | 14.3779 | 137 | 39.4755 | 65.107 | 98.2956 | 0.10241
14154 | 912.866 | 3.2584 | 35.5529 | 99.1063 | 34.7272 | 8.55 | 74.5686 | 1.8332 |  | 4.6438 | 39.2702 | 3.1596 |  | 58.7892 | 149.508 | 10.7849 | 27.2748 | 9.0444 | 137 | 39.3809 | 70.9416 | 103.9428 | 0.030104
14155 | 904.7531 | 4.1266 | 35.3166 | 101.5618 | 31.9776 | 7.6003 | 75.2861 | 1.6118 |  | 4.5579 | 38.6321 | 3.389 |  | 55.0545 | 132.3811 | 11.3509 | 26.9022 | 6.2465 | 144 | 35.3013 | 63.3172 | 105.0341 | 0.011847
14156 | 898.8474 | 4.6095 | 36.0047 | 104.4095 | 28.8872 | 8.5497 | 77.4259 | 1.4252 |  | 4.9694 | 39.5735 | 3.9327 |  | 53.307 | 130.9555 | 10.4025 | 26.4988 | 5.9301 | 141 | 35.4469 | 68.1128 | 107.068 | 0
14157 | 876.1081 | 4.496 | 37.4052 | 103.2652 | 34.6441 | 8.55 | 77.5052 | 1.7789 |  | 7.1745 | 39.1376 | 5.4763 |  | 52.5308 | 129.9386 | 11.3282 | 26.7598 | 5.5959 | 139 | 33.9991 | 70.174 | 113.0874 | 0
14158 | 867.4521 | 4.4258 | 37.8447 | 101.5049 | 33.8457 | 8.55 | 75.8433 | 1.6414 |  | 7.4898 | 37.3462 | 5.9973 |  | 50.4585 | 132.8002 | 10.7708 | 26.7735 | 5.5199 | 134 | 32.618 | 63.9735 | 113.4942 | 0
14159 | 272.9026 | 0 | 10.9969 | 28.3394 | 15.6864 | 0.002376 | 23.961 | 0.49861 |  | 2.361 | 12.8226 | 1.942 |  | 14.5525 | 46.0081 | 2.9763 | 7.6368 | 1.875 | 116 | 3.1852 | 8.4999 | 11.6552 | 0
14160 | 849.9026 | 4.0749 | 36.2978 | 102.5294 | 35.8447 | 9.4997 | 69.9001 | 1.8799 |  | 6.8265 | 36.4354 | 6.0395 |  | 47.2515 | 127.9992 | 10.9773 | 26.4805 | 5.6592 | 117 | 32.7156 | 81.293 | 112.9734 | 0
14161 | 852.6183 | 3.7636 | 36.9181 | 101.1876 | 36.1624 | 8.5503 | 73.9282 | 1.5553 |  | 6.6884 | 35.7809 | 5.9635 |  | 45.8461 | 121.1556 | 11.2949 | 26.4342 | 4.8242 | 117 | 31.4469 | 76.4182 | 115.2364 | 0
14162 | 843.9113 | 3.3039 | 37.7544 | 102.6467 | 41.0793 | 8.55 | 74.7319 | 2.2691 |  | 6.5765 | 35.5383 | 6.0869 |  | 46.1138 | 124.1679 | 11.4845 | 26.5296 | 3.7375 | 116 | 30.6263 | 81.8376 | 113.7198 | 0
14163 | 835.0367 | 3.4021 | 37.5939 | 102.8577 | 42.8009 | 8.55 | 76.8131 | 1.9028 |  | 6.5372 | 35.3597 | 6.0596 |  | 46.5672 | 123.1978 | 11.1704 | 26.6811 | 2.9297 | 107 | 29.7969 | 78.7996 | 111.0471 | 0
14164 | 835.8167 | 3.3598 | 36.305 | 102.4326 | 41.5401 | 9.4997 | 73.2591 | 2.639 |  | 6.4381 | 35.4831 | 6.1181 |  | 46.8317 | 123.2641 | 11.8504 | 26.7469 | 2.7103 | 106 | 32.3993 | 77.577 | 105.8326 | 0
14165 | 844.2129 | 3.5281 | 35.4447 | 99.9383 | 41.6062 | 8.5503 | 76.6496 | 1.9307 |  | 4.5952 | 35.5299 | 4.4562 |  | 44.7839 | 120.6795 | 11.2864 | 25.943 | 2.626 | 105 | 34.0674 | 82.5859 | 101.6199 | 0
14166 | 854.9783 | 2.497 | 35.1979 | 98.5831 | 40.0395 | 9.4997 | 72.5929 | 1.2265 |  | 3.6873 | 35.3194 | 3.3266 |  | 43.8058 | 117.2821 | 10.1468 | 25.5265 | 2.5376 | 101 | 31.0362 | 61.7936 | 98.3474 | 0.06977
14167 | 851.3368 | 1.8642 | 35.5026 | 98.6396 | 41.1719 | 8.5503 | 74.8655 | 1.2264 |  | 3.7022 | 39.2143 | 3.3555 |  | 44.5081 | 111.2017 | 10.7066 | 25.72 | 2.532 | 100 | 30.136 | 65.2421 | 100.5846 | 0.048961
14168 | 851.6288 | 1.9927 | 35.3203 | 109.3757 | 43.183 | 7.6003 | 77.8309 | 1.3172 |  | 5.1578 | 40.0932 | 3.5985 |  | 46.6552 | 111.6012 | 13.3539 | 25.7227 | 2.5033 | 105 | 31.8055 | 60.9109 | 102.394 | 0.071323
14169 | 856.7596 | 2.1931 | 35.2768 | 120.1608 | 42.6826 | 8.5497 | 80.0992 | 1.3276 |  | 8.2195 | 36.6247 | 3.5842 |  | 51.0424 | 116.5763 | 19.6075 | 25.6038 | 2.503 | 114 | 40.1672 | 68.357 | 106.3654 | 0.22578
14170 | 875.4014 | 2.7074 | 35.7769 | 121.1751 | 41.5235 | 9.4997 | 81.0244 | 1.2502 |  | 10.8828 | 40.656 | 6.332 |  | 55.1738 | 132.8594 | 22.931 | 25.6636 | 2.5793 | 117 | 36.644 | 69.7288 | 110.8015 | 0.28319
14171 | 894.9997 | 2.8611 | 35.6909 | 123.2229 | 41.9519 | 9.5 | 104.7715 | 1.1968 |  | 11.6214 | 44.6866 | 4.9587 |  | 62.1122 | 139.4088 | 23.0191 | 25.8432 | 2.9362 | 120 | 33.7895 | 62.533 | 110.9968 | 0.29385
14172 | 897.7306 | 3.1988 | 35.5241 | 123.5182 | 43.0979 | 9.5 | 107.3688 | 1.1555 |  | 10.4523 | 45.5619 | 4.2773 |  | 70.6585 | 139.3977 | 22.8814 | 25.978 | 3.7586 | 130 | 24.6871 | 67.7269 | 107.3555 | 0.30258
14173 | 897.2798 | 3.5303 | 35.5287 | 123.2233 | 43.8147 | 10.4497 | 107.0195 | 1.0419 |  | 10.0008 | 46.1745 | 4.7284 |  | 77.0524 | 142.5205 | 20.722 | 25.6576 | 5.6336 | 132 | 20.1874 | 68.578 | 104.0742 | 0.32242
14174 | 888.3285 | 3.345 | 35.96 | 123.4617 | 49.9543 | 6.6511 | 109.9616 | 1.3041 |  | 10.6935 | 46.722 | 11.6753 |  | 79.186 | 145.4434 | 12.9028 | 25.6006 | 6.8963 | 152 | 24.1386 | 64.8352 | 110.8457 | 0.32358
14175 | 894.8849 | 3.4421 | 35.988 | 109.8654 | 51.4762 | 6.65 | 88.9457 | 1.1465 |  | 12.6464 | 47.9449 | 18.047 |  | 79.5356 | 138.353 | 10.7092 | 25.5547 | 7.355 | 148 | 28.1588 | 70.4639 | 106.8437 | 0.28722
14176 | 899.0906 | 3.0013 | 36.5367 | 105.0122 | 50.1586 | 7.5997 | 83.7681 | 0.9788 |  | 10.7525 | 48.992 | 17.5741 |  | 74.9517 | 142.5766 | 10.9987 | 25.7546 | 7.3067 | 135 | 27.4993 | 69.4632 | 103.5951 | 0.25276
14177 | 891.2024 | 2.8751 | 35.9703 | 104.8842 | 47.9441 | 8.5497 | 89.5318 | 0.95308 |  | 8.7969 | 49.2159 | 12.0464 |  | 68.5424 | 149.0624 | 10.462 | 25.7288 | 7.1989 | 127 | 26.1369 | 65.0589 | 99.3716 | 0.2387
14178 | 884.4742 | 2.9565 | 35.523 | 103.1204 | 38.0421 | 13.2987 | 90.1573 | 0.9486 |  | 7.5492 | 46.0709 | 6.5945 |  | 65.3447 | 153.2731 | 10.3789 | 25.7801 | 12.1643 | 118 | 30.6818 | 63.4558 | 100.1862 | 0.20811
14179 | 885.5734 | 2.4691 | 35.5437 | 101.2371 | 30.057 | 11.4005 | 86.5753 | 1.051 |  | 6.2093 | 40.8114 | 3.833 |  | 64.2219 | 142.4645 | 10.8428 | 26.1872 | 15.3334 | 107 | 36.7337 | 67.9309 | 101.3675 | 0.08574
14180 | 883.0629 | 5.6059 | 36.0757 | 100.535 | 31.4548 | 7.6011 | 84.8307 | 1.9021 |  | 5.7961 | 38.0079 | 3.1917 |  | 56.5984 | 132.1378 | 12.5322 | 27.0356 | 10.6434 | 107 | 35.682 | 63.679 | 103.6605 | 0
14181 | 871.8662 | 7.8112 | 38.0696 | 101.8016 | 29.7097 | 9.4995 | 79.9327 | 1.8194 |  | 7.5901 | 36.4623 | 5.1794 |  | 53.9217 | 129.9788 | 11.0622 | 27.9867 | 6.9583 | 106 | 32.4526 | 62.8967 | 105.133 | 0
14182 | 863.8912 | 5.9576 | 38.3126 | 103.6488 | 28.8796 | 8.5503 | 81.3682 | 2.5951 |  | 8.069 | 35.2734 | 6.7683 |  | 54.5719 | 125.7408 | 10.8407 | 28.1934 | 6.0618 | 111 | 31.9555 | 69.5048 | 107.7433 | 0
14183 | 267.8376 | 0 | 10.9209 | 28.8407 | 14.9279 | 0.002376 | 26.0884 | 1.018 |  | 2.5737 | 12.1229 | 2.2892 |  | 15.8148 | 41.5541 | 3.1629 | 7.9449 | 1.9642 | 109 | 3.1228 | 9.5058 | 11.0146 | 0
14184 | 839.0325 | 2.7723 | 37.9438 | 105.7631 | 35.5277 | 8.5503 | 79.1924 | 1.5171 |  | 8.6675 | 34.3477 | 7.098 |  | 41.3928 | 119.2228 | 11.5845 | 27.0348 | 5.4795 | 104 | 31.3147 | 66.1426 | 104.475 | 0
14185 | 839.3217 | 2.3216 | 38.0969 | 103.0495 | 41.3013 | 8.55 | 78.1806 | 2.2662 |  | 9.2839 | 33.7901 | 6.2139 |  | 39.3382 | 118.3192 | 11.5776 | 27.0302 | 4.7728 | 103 | 34.902 | 66.7325 | 104.4914 | 0
14186 | 827.5928 | 2.387 | 37.9563 | 102.8206 | 42.1325 | 8.55 | 83.2012 | 1.924 |  | 9.2507 | 33.8534 | 6.053 |  | 39.7337 | 117.4825 | 10.6636 | 26.9451 | 3.3381 | 105 | 34.3072 | 58.8245 | 103.6741 | 0
14187 | 819.9628 | 2.3855 | 38.4592 | 102.9045 | 40.8534 | 9.4997 | 79.7311 | 2.3659 |  | 9.2185 | 33.8017 | 6.1415 |  | 39.9004 | 116.919 | 11.8897 | 26.9072 | 2.7297 | 102 | 34.3625 | 63.2139 | 104.6957 | 0
14188 | 821.9896 | 2.8298 | 37.9134 | 102.0645 | 39.7306 | 9.5 | 81.5611 | 1.9497 |  | 9.7669 | 33.8224 | 6.0589 |  | 39.7157 | 113.1551 | 10.9319 | 26.8475 | 2.7386 | 100 | 33.5856 | 66.5615 | 111.4931 | 0
14189 | 836.555 | 3.6854 | 38.1623 | 100.3311 | 39.5845 | 8.5503 | 82.5183 | 2.3013 |  | 13.5126 | 38.0884 | 5.3159 |  | 44.3768 | 113.0003 | 10.7701 | 26.273 | 2.6272 | 114 | 33.3777 | 59.4091 | 123.3479 | 0
14190 | 879.37 | 4.7752 | 44.5994 | 102.9561 | 36.7724 | 10.4495 | 97.1173 | 1.8401 |  | 19.7316 | 42.3648 | 12.5942 |  | 55.4323 | 127.5769 | 11.3363 | 26.0223 | 4.5777 | 149 | 34.5119 | 67.8317 | 141.6383 | 0.16691
14191 | 928.0171 | 8.5072 | 63.1794 | 103.9014 | 33.0512 | 13.2992 | 126.3965 | 2.6409 |  | 23.1665 | 53.0085 | 22.2909 |  | 78.5313 | 172.6108 | 12.605 | 28.2787 | 9.8241 | 246 | 46.5386 | 79.3643 | 177.102 | 0.25211
14192 | 992.4347 | 11.4643 | 86.9804 | 120.6787 | 29.4501 | 17.0989 | 144.6148 | 4.8374 |  | 23.7468 | 59.9469 | 17.1271 |  | 113.8451 | 208.4081 | 21.6176 | 33.1399 | 12.6713 | 255 | 48.9872 | 76.2738 | 200.0554 | 0.29063
14193 | 1026.3088 | 11.7721 | 100.8554 | 136.1185 | 34.1839 | 15.2005 | 155.6581 | 4.8076 |  | 27.109 | 62.7296 | 21.1242 |  | 134.5806 | 245.4353 | 30.1821 | 38.6753 | 13.9581 | 265 | 46.6318 | 81.3519 | 204.3754 | 0.32664
14194 | 1068.1606 | 8.4966 | 101.832 | 139.9608 | 33.424 | 18.0492 | 160.4672 | 4.2326 |  | 25.7376 | 62.9599 | 24.9974 |  | 143.1195 | 268.6016 | 29.6582 | 40.9334 | 14.9459 | 315 | 40.5644 | 82.7675 | 210.1235 | 0.21033
14195 | 1101.9533 | 5.6522 | 98.8575 | 143.6973 | 37.8473 | 17.1003 | 158.4055 | 4.3942 |  | 23.757 | 70.9972 | 24.2516 |  | 149.1778 | 276.9004 | 33.456 | 41.2858 | 15.8754 | 276 | 42.6339 | 81.8392 | 210.9648 | 0.2728
14196 | 1109.0077 | 4.8209 | 99.9743 | 143.159 | 41.0347 | 18.0497 | 156.3224 | 4.7165 |  | 17.5579 | 78.8676 | 25.1739 |  | 149.679 | 277.0134 | 34.0425 | 39.4014 | 16.8688 | 289 | 37.0488 | 80.8205 | 198.8589 | 0.29141
14197 | 1109.9673 | 4.4119 | 100.719 | 149.9529 | 47.379 | 18.05 | 157.3582 | 4.6248 |  | 19.9273 | 81.7348 | 26.9883 |  | 146.8621 | 266.9837 | 30.7372 | 42.0494 | 17.6024 | 278 | 38.3017 | 81.3179 | 205.3466 | 0.24192
14198 | 1116.4642 | 6.8238 | 99.147 | 149.7673 | 52.7315 | 16.1505 | 160.7432 | 4.2949 |  | 22.3223 | 84.7743 | 27.466 |  | 151.9038 | 265.5686 | 23.8304 | 51.0209 | 17.3469 | 255 | 48.9473 | 85.5667 | 200.1482 | 0.11363
14199 | 1095.6712 | 10.3189 | 102.0888 | 131.6447 | 48.3914 | 16.15 | 159.2579 | 3.942 |  | 21.0945 | 84.7511 | 26.1372 |  | 148.9664 | 254.7737 | 20.9831 | 52.6182 | 17.2399 | 234 | 56.8435 | 79.6548 | 188.9999 | 0.22579
14200 | 1052.1917 | 11.847 | 99.6994 | 120.3485 | 46.2604 | 13.3008 | 146.3025 | 3.4216 |  | 20.1984 | 78.428 | 20.7581 |  | 138.8685 | 230.5656 | 17.0712 | 51.1146 | 17.6618 | 205 | 59.3967 | 77.8063 | 171.4949 | 0.17244
14201 | 1014.759 | 8.9702 | 94.6229 | 114.6991 | 37.6737 | 13.3 | 123.3329 | 1.8034 |  | 18.9574 | 64.3364 | 17.9806 |  | 115.0481 | 195.2086 | 13.187 | 45.7245 | 17.798 | 189 | 53.3671 | 75.8761 | 136.5608 | 0.14017
14202 | 988.2638 | 4.8513 | 79.5346 | 106.6448 | 35.2584 | 8.5513 | 89.8129 | 1.1019 |  | 12.0775 | 56.3967 | 15.96 |  | 81.5665 | 171.8356 | 12.074 | 37.4921 | 14.2197 | 183 | 49.3001 | 73.6891 | 123.4211 | 0.034731
14203 | 952.9155 | 3.2356 | 60.8436 | 103.3726 | 35.7504 | 9.4997 | 71.8569 | 1.1356 |  | 7.7973 | 53.7463 | 7.9734 |  | 70.9595 | 161.1977 | 12.167 | 30.4039 | 8.7338 | 153 | 41.9012 | 63.862 | 108.1396 | 0.010251
14204 | 930.8048 | 4.5177 | 33.956 | 106.869 | 36.2179 | 8.5503 | 69.2915 | 1.9688 |  | 7.7234 | 52.5152 | 6.3456 |  | 69.3386 | 153.8964 | 11.4451 | 27.7161 | 6.6209 | 156 | 42.5343 | 69.1778 | 99.5615 | 0
14205 | 912.8827 | 7.3606 | 25.0405 | 109.2371 | 29.3136 | 9.4997 | 70.9151 | 1.8453 |  | 10.5992 | 50.9295 | 7.4978 |  | 62.5998 | 152.2159 | 12.6037 | 28.2499 | 6.1474 | 156 | 38.4425 | 69.0842 | 103.0213 | 0
14206 | 885.6262 | 8.3757 | 24.9386 | 106.4204 | 27.1432 | 8.5503 | 71.3442 | 2.4891 |  | 11.4262 | 45.9892 | 7.6132 |  | 56.4795 | 141.9478 | 11.7241 | 28.1477 | 6.6126 | 138 | 40.4078 | 62.2404 | 100.4624 | 0
14207 | 274.5333 | 2.9279 | 7.2089 | 29.4598 | 14.4616 | 0.002376 | 22.5841 | 0.9762 |  | 3.6919 | 15.239 | 2.4796 |  | 16.0097 | 46.2932 | 3.186 | 7.9581 | 2.326 | 126 | 3.9885 | 8.2639 | 9.236 | 0
14208 | 851.1992 | 9.869 | 24.0491 | 104.2474 | 34.4643 | 8.5503 | 70.2511 | 2.3331 |  | 11.3154 | 43.0833 | 7.2358 |  | 45.3428 | 124.8242 | 11.7449 | 27.8585 | 6.2628 | 116 | 37.5129 | 75.3753 | 97.7108 | 0
14209 | 855.5595 | 8.3618 | 24.2139 | 104.5055 | 35.1129 | 10.4495 | 72.2695 | 1.9217 |  | 11.7366 | 42.2109 | 7.2653 |  | 43.6888 | 122.8751 | 12.5403 | 27.4261 | 5.4109 | 112 | 35.9948 | 68.0001 | 98.1209 | 0
14210 | 839.7014 | 4.1605 | 24.2048 | 104.8583 | 34.5919 | 8.5505 | 72.2213 | 2.3683 |  | 11.7474 | 41.5899 | 8.939 |  | 43.1898 | 120.2553 | 11.6583 | 27.3333 | 4.3759 | 115 | 33.6573 | 73.8184 | 99.9479 | 0
14211 | 834.2378 | 2.2523 | 24.2319 | 102.8731 | 29.485 | 10.4495 | 70.1158 | 1.9895 |  | 11.7708 | 41.9027 | 14.325 |  | 42.6727 | 123.3781 | 11.9418 | 27.3739 | 3.5636 | 109 | 31.808 | 73.1515 | 102.4318 | 0
14212 | 838.4216 | 2.9725 | 24.2902 | 103.3328 | 21.4104 | 9.5003 | 68.9529 | 2.687 |  | 12.4769 | 42.0561 | 15.9557 |  | 42.9671 | 118.4895 | 12.9341 | 27.3137 | 3.1224 | 107 | 35.948 | 69.1279 | 106.0125 | 0
14213 | 845.5636 | 3.711 | 32.3868 | 102.1209 | 15.2703 | 9.5 | 69.6058 | 2.7873 |  | 14.978 | 47.0592 | 9.7993 |  | 47.954 | 116.3871 | 11.408 | 26.9271 | 2.9096 | 118 | 39.8853 | 72.5086 | 116.6926 | 0
14214 | 881.044 | 4.2521 | 48.8932 | 103.9082 | 14.386 | 9.5 | 86.1022 | 1.6613 |  | 17.7233 | 52.415 | 14.3517 |  | 66.0485 | 131.1876 | 11.9605 | 26.8389 | 5.3725 | 163 | 40.4478 | 68.1117 | 137.5928 | 0.031192
14215 | 946.2557 | 8.3361 | 72.4034 | 109.6444 | 7.0475 | 16.1482 | 112.4813 | 2.2288 |  | 16.65 | 62.6619 | 21.9509 |  | 99.6385 | 167.8652 | 11.848 | 29.2828 | 11.1177 | 217 | 59.1776 | 73.9879 | 170.3407 | 0.05098
14216 | 1015.9443 | 10.9034 | 94.1791 | 125.3224 | 8.1402 | 16.15 | 131.6915 | 4.1883 |  | 12.8954 | 68.5613 | 24.17 |  | 121.7801 | 211.031 | 16.267 | 34.2155 | 13.6067 | 255 | 64.0616 | 84.7155 | 198.0455 | 0.08545
14217 | 1068.1161 | 16.0324 | 102.2593 | 135.641 | 11.102 | 16.15 | 142.4827 | 4.3378 |  | 13.986 | 75.2925 | 30.1201 |  | 135.2498 | 241.9504 | 23.9814 | 41.2146 | 13.5728 | 356 | 53.4163 | 83.477 | 208.4992 | 0.078307
14218 | 1100.0226 | 16.4626 | 104.3379 | 144.0522 | 18.2503 | 18.0495 | 152.4484 | 4.5721 |  | 19.8371 | 82.7336 | 35.9571 |  | 142.2265 | 265.8868 | 27.6945 | 50.2601 | 14.323 | 300 | 55.701 | 85.7881 | 208.1609 | 0.16804
14219 | 1118.7471 | 9.9126 | 107.4811 | 148.0907 | 33.9907 | 16.1505 | 157.0674 | 4.923 |  | 22.3327 | 86.4612 | 37.6956 |  | 149.1678 | 274.728 | 28.003 | 55.0815 | 15.3805 | 300 | 53.8148 | 89.0503 | 211.9743 | 0.10579
14220 | 1109.092 | 5.4315 | 106.843 | 145.5644 | 48.7733 | 17.0997 | 164.1968 | 4.9265 |  | 20.6553 | 86.1229 | 36.1362 |  | 152.7445 | 274.5214 | 27.5689 | 52.3459 | 16.7113 | 291 | 54.912 | 93.7182 | 210.9302 | 0.1814
14221 | 1114.124 | 4.5638 | 108.7448 | 146.7371 | 65.7832 | 18.0497 | 166.4972 | 4.3801 |  | 27.7065 | 83.7447 | 36.2424 |  | 157.3819 | 267.1962 | 26.2712 | 54.9713 | 17.9151 | 286 | 50.8584 | 93.8673 | 212.9417 | 0.13036
14222 | 1108.8142 | 4.775 | 109.0919 | 147.82 | 79.348 | 13.3013 | 168.126 | 4.0687 |  | 35.6857 | 83.6444 | 34.449 |  | 156.7382 | 269.4225 | 19.4485 | 53.1869 | 16.8707 | 258 | 48.9202 | 86.9113 | 207.9485 | 0.20498
14223 | 1071.6523 | 4.6825 | 106.9224 | 147.8412 | 70.1144 | 17.0989 | 169.3919 | 4.2165 |  | 33.9952 | 84.2762 | 30.9111 |  | 153.1014 | 262.9995 | 15.9304 | 43.9769 | 15.6813 | 274 | 52.0295 | 90.623 | 196.6721 | 0.19751
14224 | 1033.2195 | 4.2934 | 103.5047 | 141.2212 | 71.1399 | 9.5021 | 154.1274 | 3.8487 |  | 26.9311 | 80.1666 | 20.5981 |  | 145.6312 | 236.513 | 16.281 | 45.8061 | 15.7672 | 238 | 58.1506 | 84.9698 | 174.8154 | 0.12944
14225 | 1009.3539 | 3.7793 | 93.9195 | 124.1054 | 65.2147 | 8.5503 | 104.5783 | 2.8547 |  | 22.0516 | 66.0064 | 19.0104 |  | 124.8537 | 212.1117 | 16.199 | 45.9614 | 16.2569 | 193 | 54.1969 | 75.8099 | 134.3903 | 0.10596
14226 | 970.6648 | 3.9988 | 76.4534 | 109.2183 | 59.6312 | 8.55 | 70.224 | 2.2189 |  | 16.6073 | 56.9988 | 20.3237 |  | 92.238 | 192.381 | 15.0128 | 43.5495 | 14.7934 | 174 | 47.9781 | 74.569 | 122.9124 | 0.12855
14227 | 937.4345 | 4.8496 | 58.3662 | 103.1911 | 58.8841 | 8.55 | 64.2313 | 1.8312 |  | 14.3809 | 54.325 | 23.5427 |  | 75.5532 | 185.9563 | 13.1082 | 38.7431 | 14.0904 | 151 | 48.4178 | 75.5903 | 106.5954 | 0.044744
14228 | 290.1134 | 1.8232 | 15.4421 | 28.4647 | 27.2266 | 0 | 20.3974 | 0.5632 |  | 4.7013 | 18.653 | 8.1747 |  | 21.2858 | 62.8673 | 3.6207 | 10.584 | 4.7255 | 137 | 4.7733 | 10.2497 | 10.4643 | 0
14229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0
14230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0
14231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0
14232 | 855.8911 | 7.434 | 18.9427 | 102.549 | 26.7442 | 8.5495 | 61.1844 | 1.7996 |  | 12.7349 | 40.6253 | 11.8365 |  | 55.3501 | 122.0757 | 11.583 | 26.7745 | 11.9002 | 119 | 33.5411 | 74.4256 | 96.7722 | 0
14233 | 861.9846 | 4.0602 | 20.2842 | 103.4099 | 25.0761 | 7.6003 | 56.3013 | 1.5356 |  | 12.5478 | 40.4709 | 12.0628 |  | 55.9153 | 120.8398 | 13.4206 | 26.8493 | 11.9129 | 114 | 30.2712 | 78.042 | 102.0299 | 0
14234 | 849.5756 | 2.4748 | 31.7601 | 102.6273 | 22.44 | 9.4995 | 48.343 | 1.5212 |  | 12.3669 | 40.25 | 13.432 |  | 55.3253 | 120.8066 | 12.4329 | 26.8852 | 11.9187 | 114 | 29.6297 | 72.9953 | 102.5625 | 0
14235 | 844.7055 | 2.3734 | 35.6264 | 100.9485 | 24.0412 | 7.6005 | 56.5814 | 1.5312 |  | 12.3272 | 41.8958 | 18.2706 |  | 54.7944 | 120.5602 | 12.8935 | 26.7737 | 11.8863 | 112 | 32.3393 | 75.3003 | 105.9863 | 0
14236 | 844.9523 | 2.9055 | 37.4018 | 101.066 | 34.0205 | 7.6 | 62.8487 | 1.829 |  | 13.045 | 41.413 | 18.1438 |  | 54.4737 | 114.9421 | 11.9252 | 26.5802 | 11.8909 | 110 | 28.8609 | 79.0267 | 106.1237 | 0
14237 | 858.155 | 3.7031 | 34.6619 | 100.3606 | 41.5054 | 8.5497 | 63.4419 | 2.2731 |  | 14.5074 | 38.6258 | 15.674 |  | 54.1002 | 116.2041 | 9.0674 | 26.667 | 11.8353 | 109 | 30.8073 | 71.639 | 115.9361 | 0
14238 | 894.9909 | 6.4897 | 40.077 | 103.956 | 43.5967 | 9.4997 | 75.0965 | 1.6461 |  | 17.1569 | 43.3099 | 18.5479 |  | 64.6253 | 122.8697 | 8.9111 | 26.3701 | 11.7146 | 175 | 34.1915 | 75.1701 | 133.8282 | 0.02106
14239 | 955.5975 | 8.6371 | 62.83 | 104.1102 | 39.7671 | 15.1984 | 101.8798 | 2.5925 |  | 17.6823 | 57.9257 | 24.6365 |  | 91.0264 | 159.3365 | 8.8115 | 28.3722 | 11.9911 | 248 | 56.9818 | 82.8785 | 174.0599 | 0.05473
14240 | 1020.3098 | 12.8416 | 93.64 | 115.4542 | 43.4937 | 15.2 | 121.6434 | 3.9498 |  | 18.7761 | 69.8753 | 30.3071 |  | 117.4662 | 220.2621 | 13.303 | 32.7776 | 12.9937 | 271 | 62.5923 | 77.4602 | 194.763 | 0.12987
14241 | 1069.2995 | 9.5043 | 101.7228 | 127.4106 | 44.8017 | 17.0995 | 131.1205 | 4.4533 |  | 21.4519 | 78.5516 | 33.6777 |  | 138.1758 | 268.8821 | 22.2733 | 38.7906 | 14.3817 | 319 | 61.6037 | 86.6841 | 204.4726 | 0.31127
14242 | 1112.3912 | 5.5208 | 102.9114 | 130.6955 | 46.7207 | 17.1 | 142.7652 | 4.3671 |  | 24.7856 | 82.7121 | 36.8327 |  | 153.776 | 299.7251 | 26.4665 | 40.4624 | 16.0667 | 317 | 56.0283 | 94.1449 | 212.9518 | 0.29498
14243 | 1142.001 | 4.6716 | 104.2267 | 131.6475 | 47.0901 | 16.1503 | 144.664 | 4.5823 |  | 26.8158 | 82.0053 | 34.1385 |  | 158.8732 | 311.8764 | 25.2051 | 40.1967 | 17.4914 | 291 | 56.9236 | 91.1508 | 205.0499 | 0.28885
14244 | 1127.3892 | 4.7411 | 106.1711 | 126.7591 | 45.111 | 15.2003 | 147.947 | 4.4354 |  | 24.1898 | 84.1588 | 34.2242 |  | 156.5425 | 301.264 | 25.4609 | 43.4264 | 18.0903 | 308 | 52.949 | 94.2772 | 195.993 | 0.27417
14245 | 1127.71 | 4.4009 | 107.0453 | 130.564 | 43.7854 | 16.1497 | 149.624 | 4.7489 |  | 32.9892 | 85.0971 | 37.9386 |  | 163.3656 | 291.571 | 23.7408 | 48.2764 | 18.6181 | 282 | 54.1065 | 98.9695 | 200.7144 | 0.29283
14246 | 1119.5491 | 5.6604 | 107.0583 | 138.0601 | 45.6238 | 17.0997 | 161.0546 | 4.4383 |  | 40.565 | 86.2409 | 36.5001 |  | 165.3606 | 294.1202 | 16.8423 | 50.0112 | 19.1746 | 243 | 45.7242 | 97.1672 | 199.2027 | 0.21826
14247 | 1081.6251 | 7.6159 | 105.3801 | 139.7211 | 50.9084 | 16.1503 | 154.2112 | 3.9516 |  | 36.763 | 87.2538 | 31.5169 |  | 155.9927 | 278.7918 | 13.7477 | 48.3759 | 19.3233 | 240 | 46.1456 | 96.0133 | 190.8509 | 0.18725
14248 | 1056.8077 | 7.1692 | 101.1262 | 134.0856 | 60.6266 | 9.5018 | 129.1253 | 3.5794 |  | 37.0701 | 81.3485 | 21.5608 |  | 141.8542 | 246.3353 | 13.1163 | 46.8647 | 18.8172 | 190 | 51.0888 | 90.4572 | 167.8078 | 0.22941
14249 | 1019.5474 | 4.8577 | 100.4519 | 118.4615 | 57.4445 | 9.5 | 79.0717 | 2.7438 |  | 32.0631 | 66.0727 | 19.0682 |  | 111.9415 | 207.8891 | 10.2767 | 45.0511 | 18.1358 | 183 | 44.291 | 82.539 | 134.5216 | 0.23486
14250 | 987.7198 | 3.1787 | 85.1644 | 105.8982 | 52.3663 | 8.5503 | 54.364 | 2.672 |  | 19.2449 | 58.1454 | 17.1212 |  | 71.2717 | 181.9027 | 9.6168 | 42.8226 | 14.9067 | 170 | 41.5708 | 74.7993 | 120.4632 | 0.18073
14251 | 949.4813 | 4.2826 | 65.0068 | 101.7063 | 39.7649 | 10.4495 | 56.0024 | 2.6906 |  | 13.5854 | 51.9993 | 14.4547 |  | 55.3903 | 170.9316 | 10.1767 | 40.5175 | 13.655 | 153 | 44.2574 | 66.4185 | 105.1574 | 0.097562
14252 | 934.4935 | 7.1022 | 36.4774 | 99.3104 | 36.4761 | 8.5505 | 60.0224 | 2.9056 |  | 12.4438 | 48.3212 | 11.9522 |  | 53.9595 | 160.4352 | 8.9343 | 39.3573 | 14.2074 | 131 | 47.2288 | 66.1931 | 103.4446 | 0
14253 | 919.4525 | 7.0313 | 27.2379 | 101.6736 | 35.2059 | 10.4495 | 60.7852 | 2.0482 |  | 15.2652 | 47.8551 | 13.2012 |  | 54.9096 | 147.3042 | 9.8297 | 38.4347 | 14.6722 | 129 | 46.9272 | 62.2981 | 101.792 | 0
14254 | 900.2343 | 4.5618 | 27.8218 | 108.1676 | 38.2177 | 8.5505 | 60.733 | 1.5575 |  | 15.0934 | 43.2721 | 12.2096 |  | 49.252 | 135.8194 | 10.0051 | 38.3932 | 15.2005 | 130 | 42.9615 | 62.9691 | 98.2436 | 0
14255 | 273.3023 | 1.2558 | 7.9356 | 30.0759 | 18.6681 | 0.002376 | 18.7707 | 0.4985 |  | 4.6213 | 13.9456 | 3.6196 |  | 13.4097 | 43.7708 | 2.7488 | 10.7006 | 5.0134 | 122 | 3.8199 | 8.124 | 9.5604 | 0
14256 | 870.331 | 2.2628 | 26.8575 | 108.3369 | 31.4597 | 9.4997 | 57.4177 | 1.9777 |  | 12.7558 | 42.0901 | 11.0739 |  | 43.5937 | 122.4035 | 13.5432 | 38.5492 | 13.9302 | 122 | 41.8766 | 81.6689 | 101.0971 | 0
14257 | 862.5969 | 2.2433 | 28.2721 | 108.0558 | 36.7742 | 9.5 | 56.0535 | 1.58 |  | 12.8728 | 40.9939 | 10.9736 |  | 43.6211 | 122.8684 | 14.1325 | 38.3694 | 12.4944 | 111 | 35.7447 | 78.9986 | 100.1694 | 0
14258 | 851.4543 | 2.3327 | 38.8111 | 108.234 | 41.3021 | 8.5503 | 47.7216 | 2.3236 |  | 12.8493 | 41.0819 | 14.1698 |  | 43.9856 | 122.5445 | 14.1677 | 38.1128 | 11.9121 | 111 | 37.0423 | 83.4778 | 98.8558 | 0
14259 | 842.211 | 2.3014 | 43.6662 | 108.8097 | 38.7818 | 9.4997 | 53.6351 | 2.1793 |  | 12.923 | 40.86 | 22.1672 |  | 44.1415 | 123.2504 | 14.1358 | 38.2569 | 12.0801 | 107 | 37.2576 | 81.4014 | 98.0317 | 0
14260 | 841.4209 | 2.7961 | 40.924 | 109.1282 | 36.386 | 10.4497 | 61.4333 | 2.4532 |  | 13.6221 | 40.7567 | 21.9458 |  | 43.9445 | 116.0349 | 13.5247 | 38.1237 | 11.9483 | 113 | 34.9499 | 79.3043 | 100.0374 | 0
14261 | 861.4694 | 3.5665 | 40.5324 | 106.602 | 30.0767 | 10.45 | 62.7478 | 1.771 |  | 15.6169 | 39.9148 | 14.1129 |  | 48.0445 | 113.8224 | 10.2164 | 37.4137 | 11.7364 | 110 | 38.1657 | 83.7733 | 110.2339 | 0
14262 | 904.6829 | 3.8624 | 52.8714 | 107.2448 | 24.6228 | 8.5505 | 74.7444 | 2.007 |  | 18.3815 | 43.9704 | 14.2062 |  | 65.5526 | 119.3152 | 9.3449 | 37.0839 | 11.6198 | 177 | 37.4829 | 75.5887 | 130.427 | 0.15573
14263 | 976.908 | 13.0475 | 69.7499 | 110.2316 | 14.8609 | 15.1982 | 98.0531 | 2.4258 |  | 21.1281 | 56.6505 | 23.8322 |  | 93.9518 | 162.4989 | 10.3081 | 39.5967 | 12.0589 | 252 | 56.692 | 86.0704 | 165.8324 | 0.16148
14264 | 1037.951 | 17.0247 | 94.5862 | 127.2235 | 20.3873 | 14.2503 | 124.242 | 3.4162 |  | 23.4764 | 68.9225 | 28.5159 |  | 124.2375 | 226.6078 | 15.624 | 44.5207 | 12.9964 | 282 | 61.1496 | 92.3279 | 192.4 | 0.11807
14265 | 1092.9306 | 12.9233 | 105.0181 | 134.8846 | 32.9168 | 15.1997 | 141.4434 | 4.2892 |  | 23.4518 | 78.1145 | 29.9916 |  | 141.5994 | 275.1806 | 23.1353 | 48.9379 | 13.7589 | 321 | 61.8904 | 92.2757 | 203.372 | 0.20086
14266 | 1160.5956 | 6.5899 | 103.0232 | 140.9041 | 42.8761 | 18.0492 | 147.1284 | 3.9772 |  | 18.9518 | 83.1556 | 33.3496 |  | 150.6186 | 292.7643 | 27.2242 | 50.7015 | 14.7669 | 338 | 53.9609 | 95.294 | 207.5553 | 0.094097
14267 | 1176.2807 | 7.5924 | 107.9705 | 142.2381 | 55.6964 | 15.2008 | 147.9216 | 4.1406 |  | 17.5339 | 84.787 | 35.0941 |  | 156.2132 | 289.4293 | 26.8745 | 51.4553 | 15.745 | 332 | 59.7902 | 95.5851 | 202.1033 | 0.25721
14268 | 1153.3557 | 9.9897 | 112.0052 | 142.2185 | 66.4443 | 15.2 | 148.9376 | 4.4016 |  | 17.9176 | 84.1586 | 35.8533 |  | 153.8082 | 286.6881 | 26.6864 | 51.6227 | 16.5694 | 368 | 49.4832 | 94.7505 | 198.6286 | 0.2295
14269 | 1128.0736 | 7.5287 | 110.4751 | 143.1263 | 63.6416 | 16.1497 | 176.8347 | 4.6485 |  | 23.8803 | 84.7416 | 35.3274 |  | 153.1122 | 302.6672 | 23.9368 | 54.6304 | 16.9012 | 301 | 42.3283 | 93.5931 | 200.4164 | 0.10778
14270 | 1134.0088 | 5.7233 | 110.5906 | 146.0649 | 64.9713 | 14.2505 | 181.0326 | 4.3242 |  | 23.7348 | 83.8799 | 33.8818 |  | 151.7529 | 304.3704 | 15.7707 | 53.0018 | 17.2953 | 282 | 42.3142 | 93.2916 | 203.7376 | 0.10046
14271 | 1104.884 | 4.7653 | 109.716 | 143.5148 | 64.2011 | 17.0992 | 173.3478 | 3.9855 |  | 21.5062 | 83.4908 | 30.0091 |  | 144.2339 | 286.6268 | 12.7528 | 51.6147 | 17.4126 | 277 | 44.06 | 98.457 | 196.7517 | 0.27285
14272 | 1071.4719 | 4.2298 | 106.5002 | 137.473 | 66.2092 | 12.3513 | 147.1907 | 3.6639 |  | 21.7188 | 76.3798 | 22.8842 |  | 128.9145 | 265.3047 | 11.8518 | 51.1128 | 17.0106 | 257 | 48.0405 | 95.2624 | 170.469 | 0.24017
14273 | 1044.5393 | 3.7424 | 101.803 | 123.3452 | 60.3709 | 9.5008 | 90.3451 | 2.2706 |  | 17.2719 | 60.6662 | 19.8128 |  | 103.8208 | 221.0461 | 9.5462 | 42.0737 | 17.2445 | 216 | 46.2494 | 86.518 | 142.9883 | 0.21837
14274 | 1005.06 | 3.4146 | 90.8594 | 107.0804 | 56.2163 | 6.6508 | 63.8912 | 1.2378 |  | 11.8598 | 53.3158 | 17.4491 |  | 71.5255 | 189.4228 | 9.3615 | 32.6205 | 14.8012 | 203 | 44.3112 | 73.0043 | 124.5971 | 0.21274
14275 | 967.0105 | 3.8109 | 68.6914 | 99.6566 | 55.7893 | 5.7003 | 52.3993 | 1.2047 |  | 10.5245 | 50.6569 | 8.8643 |  | 57.955 | 174.2976 | 8.6257 | 27.6254 | 8.6209 | 184 | 42.3806 | 70.012 | 107.5868 | 0.039961
14276 | 932.6879 | 4.3774 | 37.067 | 100.0318 | 54.2746 | 8.5492 | 57.8344 | 1.2259 |  | 11.5752 | 50.3126 | 6.7928 |  | 56.99 | 152.753 | 9.9251 | 26.2767 | 6.2602 | 173 | 49.8229 | 72.3386 | 101.5068 | 0
14277 | 930.0708 | 4.2219 | 27.1075 | 101.3199 | 55.011 | 7.6003 | 61.7765 | 1.2453 |  | 11.8502 | 50.2032 | 10.62 |  | 55.1637 | 149.3451 | 9.3207 | 26.3302 | 6.4279 | 167 | 43.4093 | 68.9957 | 101.7129 | 0
14278 | 923.4261 | 3.754 | 27.1153 | 101.8271 | 51.9485 | 7.6 | 61.1769 | 1.3313 |  | 11.9728 | 44.2284 | 11.9121 |  | 52.9685 | 152.7188 | 9.4365 | 26.3365 | 6.2663 | 159 | 40.7182 | 68.491 | 99.6879 | 0
14279 | 286.4865 | 0 | 7.7448 | 28.1252 | 23.532 | 0.002112 | 19.2398 | 0.45042 |  | 3.9618 | 14.3587 | 3.8454 |  | 15.0959 | 51.6788 | 2.7528 | 7.3848 | 2.0548 | 151 | 3.9398 | 9.0592 | 10.0321 | 0
14280 | 895.2438 | 2.3177 | 27.0659 | 102.0406 | 44.5686 | 10.4495 | 62.6746 | 1.8299 |  | 11.6816 | 40.0446 | 7.6577 |  | 44.5864 | 146.9048 | 13.3056 | 26.1632 | 5.213 | 148 | 35.6626 | 80.9933 | 99.8993 | 0
14281 | 896.0845 | 2.3522 | 27.7234 | 101.2745 | 38.9989 | 7.6008 | 62.6447 | 1.8298 |  | 12.0381 | 40.0139 | 7.7517 |  | 45.6242 | 139.627 | 14.0637 | 26.3616 | 4.6554 | 139 | 33.1319 | 81.4719 | 101.7047 | 0
14282 | 889.9223 | 2.3657 | 38.5991 | 100.662 | 39.9619 | 6.6503 | 58.8525 | 1.6673 |  | 12.0408 | 39.783 | 9.7011 |  | 45.0669 | 135.8045 | 13.5063 | 26.3381 | 4.112 | 139 | 32.5481 | 84.9787 | 101.4774 | 0
14283 | 892.8897 | 2.5725 | 42.5517 | 101.7138 | 34.0817 | 9.4992 | 51.4099 | 1.5176 |  | 11.613 | 40.2489 | 15.0735 |  | 44.518 | 134.3406 | 13.8861 | 26.4052 | 3.7556 | 139 | 28.9533 | 78.9568 | 103.2936 | 0
14284 | 878.993 | 2.3855 | 44.2976 | 101.2529 | 31.2582 | 9.5 | 53.2856 | 1.5167 |  | 12.0105 | 44.9463 | 14.8403 |  | 44.3337 | 125.934 | 12.0471 | 26.5717 | 3.1709 | 131 | 28.7896 | 82.482 | 106.8473 | 0
14285 | 887.3081 | 2.5515 | 45.5028 | 99.1959 | 37.3824 | 9.5 | 57.9145 | 1.4526 |  | 13.4545 | 42.0697 | 10.6743 |  | 49.4526 | 120.9569 | 10.2487 | 26.1503 | 2.8375 | 129 | 31.3916 | 85.7373 | 114.507 | 0
14286 | 947.7988 | 7.8892 | 54.1428 | 103.4288 | 40.4646 | 9.5 | 75.8699 | 1.3072 |  | 15.8382 | 43.6366 | 17.3291 |  | 68.8267 | 125.3738 | 8.8162 | 25.6372 | 4.9593 | 198 | 31.5818 | 74.6736 | 126.7775 | 0.14538
14287 | 1015.8808 | 14.5941 | 76.2667 | 107.6549 | 44.8435 | 10.4497 | 115.6915 | 2.0588 |  | 19.3165 | 60.9419 | 29.162 |  | 93.0299 | 161.8533 | 10.568 | 27.4259 | 10.3465 | 259 | 57.449 | 85.5093 | 170.4005 | 0.23495
14288 | 1059.3161 | 12.3769 | 99.1264 | 125.0907 | 41.666 | 18.0479 | 136.8982 | 4.0236 |  | 20.5902 | 76.4279 | 28.2294 |  | 115.5658 | 227.5929 | 16.0837 | 32.1686 | 12.8811 | 275 | 66.534 | 84.3816 | 193.5323 | 0.27094
14289 | 1119.9543 | 7.8028 | 106.1697 | 139.2155 | 43.937 | 16.1505 | 141.5965 | 4.3833 |  | 22.3987 | 84.3048 | 23.7957 |  | 137.6918 | 268.5585 | 24.8688 | 36.8077 | 13.816 | 320 | 64.1075 | 96.2072 | 207.1925 | 0.30745
14290 | 1152.915 | 8.6231 | 106.4875 | 147.7061 | 42.0748 | 18.9992 | 151.392 | 4.2965 |  | 28.07 | 87.7218 | 25.2884 |  | 146.9049 | 274.7457 | 28.4923 | 43.1013 | 15.016 | 321 | 62.7277 | 95.6507 | 213.6395 | 0.2925
14291 | 1150.9518 | 6.4193 | 106.9953 | 147.8848 | 46.8669 | 16.1508 | 165.003 | 4.308 |  | 26.2212 | 88.6403 | 28.8446 |  | 151.7085 | 268.1522 | 28.2596 | 50.4912 | 15.4695 | 301 | 62.3198 | 91.0876 | 209.9494 | 0.27227
14292 | 1136.7089 | 4.6125 | 106.3462 | 147.1484 | 48.8925 | 17.0997 | 175.5035 | 4.4482 |  | 21.1592 | 88.4758 | 31.6563 |  | 152.109 | 264.4383 | 27.4432 | 50.6373 | 15.4488 | 333 | 49.7162 | 82.9299 | 205.1927 | 0.27635
14293 | 1121.8395 | 4.4827 | 106.3291 | 149.9408 | 58.2497 | 14.2508 | 176.7831 | 4.3583 |  | 26.6149 | 88.9602 | 36.0533 |  | 159.9763 | 272.8635 | 24.0861 | 50.9403 | 17.6139 | 297 | 50.5608 | 86.0307 | 204.0949 | 0.29603
14294 | 1109.3061 | 4.5672 | 106.7098 | 151.6169 | 63.079 | 13.3003 | 175.4668 | 4.6701 |  | 31.0613 | 87.723 | 37.1013 |  | 162.1557 | 273.4856 | 16.419 | 50.6643 | 17.642 | 274 | 58.1177 | 83.3169 | 209.4889 | 0.29618
14295 | 1088.7076 | 4.1403 | 105.9649 | 143.6553 | 61.5881 | 14.2497 | 174.5502 | 4.1033 |  | 34.9981 | 86.2207 | 31.4639 |  | 156.722 | 254.7828 | 11.9585 | 49.3212 | 17.4444 | 286 | 60.446 | 79.7827 | 205.3095 | 0.22117
14296 | 1085.3903 | 3.5343 | 103.1727 | 129.4053 | 65.0153 | 8.5516 | 149.4104 | 2.8381 |  | 34.6917 | 79.7365 | 17.1327 |  | 143.8993 | 233.8171 | 10.2536 | 48.3825 | 17.6569 | 265 | 56.5585 | 69.8581 | 183.2999 | 0.067551
14297 | 1028.1357 | 2.9813 | 91.0202 | 114.4284 | 59.6657 | 10.4495 | 87.9327 | 1.5121 |  | 29.6687 | 61.9962 | 9.1615 |  | 116.904 | 193.4067 | 10.4144 | 45.2707 | 17.7082 | 241 | 56.0667 | 62.4568 | 147.5271 | 0.15453
14298 | 971.4124 | 2.6995 | 47.5418 | 104.7169 | 59.8952 | 9.5003 | 63.3911 | 1.0567 |  | 18.5943 | 52.1128 | 6.126 |  | 83.2445 | 168.241 | 9.9576 | 42.6061 | 14.8989 | 225 | 49.8763 | 55.0755 | 128.4539 | 0.1358
14299 | 960.8821 | 2.6748 | 27.1184 | 100.9531 | 51.3574 | 10.4497 | 54.3588 | 1.2005 |  | 13.2012 | 47.8032 | 6.8669 |  | 69.5188 | 160.7792 | 10.1719 | 39.4161 | 8.5881 | 196 | 47.961 | 51.1363 | 112.9221 | 0.093064
14300 | 922.2914 | 3.7087 | 25.3611 | 100.8981 | 52.3563 | 5.7013 | 52.929 | 1.1669 |  | 12.6743 | 43.7964 | 7.8733 |  | 67.9298 | 146.7493 | 10.4224 | 37.6531 | 5.4378 | 178 | 45.9019 | 49.593 | 107.3221 | 0
14301 | 898.1386 | 4.1213 | 25.5841 | 103.148 | 44.8886 | 7.5995 | 57.3146 | 1.2623 |  | 13.7809 | 43.8348 | 7.2264 |  | 74.6527 | 142.646 | 10.1926 | 37.3514 | 6.508 | 168 | 36.7478 | 49.4482 | 115.6385 | 0
14302 | 904.1848 | 3.7351 | 25.5427 | 102.3249 | 46.5954 | 7.6 | 59.8292 | 1.3313 |  | 15.0738 | 43.2732 | 6.6273 |  | 80.6901 | 153.5805 | 9.7568 | 37.4437 | 6.8483 | 160 | 41.3881 | 50.2255 | 117.4466 | 0
14303 | 282.1497 | 0 | 7.3302 | 0 | 23.7395 | 0.002112 | 18.9531 | 0.43656 |  | 5.0382 | 14.7147 | 2.1027 |  | 0 | 0 | 2.7292 | 0 | 2.2165 | 160 | 3.9091 | 6.4908 | 11.6242 | 0
14304 | 898.9882 | 6.4026 | 25.3033 | 102.6383 | 46.59 | 6.6503 | 58.9436 | 1.4498 |  | 9.6984 | 41.1374 | 6.5808 |  | 66.6903 | 146.3007 | 13.1557 | 37.2277 | 5.755 | 159 | 40.0214 | 77.7438 | 108.7633 | 0
14305 | 891.9915 | 8.8485 | 25.6133 | 101.2544 | 41.9811 | 7.5997 | 56.4162 | 1.4894 |  | 8.7648 | 40.6971 | 6.4174 |  | 65.1299 | 135.6559 | 14.3005 | 37.1875 | 5.2906 | 159 | 34.038 | 78.4309 | 99.8634 | 0
14306 | 887.2619 | 8.3127 | 30.4543 | 100.804 | 36.7751 | 9.4995 | 54.7108 | 1.3379 |  | 8.6698 | 41.1617 | 6.3954 |  | 63.6653 | 130.4457 | 14.5366 | 37.1568 | 4.8159 | 158 | 34.3028 | 77.777 | 96.7546 | 0
14307 | 881.7997 | 4.2925 | 39.5359 | 101.9839 | 34.605 | 10.4497 | 47.0864 | 2.0618 |  | 8.718 | 41.4075 | 6.4333 |  | 59.5266 | 127.4821 | 14.2416 | 37.0082 | 4.4601 | 143 | 32.948 | 78.9399 | 96.4559 | 0
14308 | 890.5729 | 2.7485 | 44.0757 | 106.1657 | 43.9345 | 7.6008 | 50.4882 | 1.8523 |  | 8.856 | 41.389 | 6.4167 |  | 55.439 | 127.3491 | 12.7532 | 36.8609 | 3.8265 | 137 | 28.2125 | 78.3174 | 93.307 | 0
14309 | 898.6575 | 3.4992 | 36.4683 | 106.296 | 41.422 | 6.6503 | 56.6427 | 1.5326 |  | 7.7928 | 44.1157 | 5.7187 |  | 55.5161 | 124.5511 | 10.3366 | 37.0626 | 3.0033 | 125 | 29.0495 | 74.8628 | 94.9024 | 0
14310 | 912.2289 | 3.122 | 40.9164 | 101.5738 | 35.8761 | 7.5997 | 58.6841 | 1.3533 |  | 6.3779 | 44.1848 | 4.2188 |  | 52.91 | 119.7799 | 9.4439 | 36.8621 | 2.6279 | 122 | 29.9164 | 67.4495 | 93.9537 | 0.059665
14311 | 921.4065 | 2.5108 | 54.2289 | 98.5449 | 34.9851 | 8.5497 | 57.8166 | 1.3003 |  | 5.8735 | 40.0576 | 3.606 |  | 48.289 | 116.3085 | 9.3956 | 36.5845 | 2.5717 | 119 | 41.216 | 67.9468 | 94.874 | 0.22345
14312 | 920.5904 | 2.5146 | 66.358 | 97.6271 | 32.5774 | 9.4997 | 56.4731 | 1.5757 |  | 5.8719 | 38.7712 | 5.1502 |  | 43.6167 | 118.7861 | 9.136 | 36.4795 | 2.6529 | 128 | 53.64 | 69.7319 | 94.3694 | 0.14866
14313 | 921.7062 | 2.4138 | 71.4529 | 99.0471 | 36.3807 | 7.6005 | 56.6983 | 1.8414 |  | 6.0759 | 41.8975 | 12.145 |  | 45.0394 | 119.4121 | 9.0912 | 36.6579 | 5.0433 | 139 | 49.1995 | 70.8082 | 96.6412 | 0.23128
14314 | 936.9413 | 2.3688 | 68.0607 | 101.2473 | 36.8721 | 7.6 | 57.3048 | 1.8997 |  | 6.6605 | 47.5227 | 14.7822 |  | 50.2355 | 129.091 | 9.4914 | 37.1593 | 10.727 | 175 | 50.0105 | 70.4475 | 99.149 | 0.32652
14315 | 928.9079 | 3.7734 | 66.4385 | 100.8694 | 36.9626 | 7.6 | 57.5333 | 1.3161 |  | 11.4954 | 56.608 | 15.258 |  | 53.0014 | 146.0001 | 9.6383 | 37.0585 | 13.4396 | 176 | 45.4567 | 71.4571 | 97.3759 | 0.28417
14316 | 944.4665 | 4.5786 | 67.0284 | 100.4437 | 34.6626 | 8.5497 | 53.676 | 1.0063 |  | 12.9127 | 60.0747 | 15.483 |  | 55.7289 | 153.0706 | 9.7033 | 37.0205 | 13.7511 | 189 | 42.5527 | 69.8487 | 95.4303 | 0.2898
14317 | 952.1395 | 5.1984 | 56.8568 | 101.3662 | 38.9749 | 6.6505 | 48.5907 | 1.1005 |  | 11.3078 | 52.7904 | 14.9578 |  | 63.657 | 159.8181 | 9.6483 | 37.5737 | 14.5559 | 196 | 41.0471 | 69.8778 | 94.2146 | 0.19037
14318 | 958.303 | 3.8014 | 33.2076 | 102.0108 | 37.1459 | 8.5495 | 49.7581 | 1.234 |  | 10.4903 | 49.9311 | 16.5193 |  | 72.0095 | 164.6399 | 9.374 | 37.4837 | 12.6988 | 185 | 32.508 | 70.6655 | 93.7243 | 0.28432
14319 | 951.788 | 2.7072 | 25.8637 | 101.6063 | 41.6566 | 7.6003 | 55.1646 | 1.0883 |  | 9.6208 | 51.2358 | 15.696 |  | 69.2737 | 158.564 | 9.31 | 36.8644 | 7.7124 | 189 | 37.3443 | 72.1044 | 96.0323 | 0.20082
14320 | 959.3427 | 2.5929 | 25.8245 | 101.3532 | 43.7113 | 9.4995 | 60.2578 | 1.002 |  | 8.9689 | 51.0491 | 12.4571 |  | 66.902 | 156.3356 | 9.4236 | 37.2499 | 5.8123 | 192 | 34.1185 | 71.2067 | 97.4768 | 0.11611
14321 | 969.5703 | 2.2788 | 25.3429 | 101.4644 | 46.4419 | 7.6005 | 56.0675 | 1.0135 |  | 8.661 | 47.357 | 6.2408 |  | 65.1201 | 150.1489 | 8.9913 | 37.0308 | 6.0414 | 202 | 35.5812 | 68.6439 | 97.8258 | 0.23457
14322 | 964.7672 | 3.8022 | 25.1231 | 101.6318 | 42.336 | 11.3989 | 56.9575 | 1.6736 |  | 8.4084 | 43.4087 | 3.6119 |  | 60.4362 | 145.6368 | 9.3534 | 36.9241 | 5.5745 | 179 | 42.1378 | 54.6769 | 94.3396 | 0.21868
14323 | 959.0559 | 5.6096 | 24.7307 | 99.6412 | 40.9278 | 8.5508 | 58.7668 | 1.4898 |  | 8.327 | 44.862 | 3.4107 |  | 55.449 | 157.1978 | 9.3156 | 37.514 | 5.1252 | 184 | 39.9562 | 50.4815 | 94.0197 | 0.11877
14324 | 943.6437 | 7.242 | 25.0071 | 98.5045 | 40.6534 | 6.6505 | 56.9763 | 1.3355 |  | 7.8033 | 41.7923 | 4.682 |  | 54.7448 | 158.6443 | 9.1004 | 36.8662 | 4.6236 | 181 | 41.0109 | 50.7807 | 89.6327 | 0
14325 | 928.0113 | 7.7984 | 25.4395 | 100.5199 | 34.8739 | 8.5495 | 57.5508 | 1.7832 |  | 13.8345 | 40.502 | 7.1131 |  | 52.4061 | 155.2771 | 9.6992 | 37.3022 | 4.8856 | 179 | 40.1429 | 51.5564 | 96.8282 | 0
14326 | 905.2972 | 7.8938 | 25.4196 | 102.3051 | 32.5251 | 8.55 | 58.933 | 1.765 |  | 12.5842 | 40.0708 | 9.9054 |  | 51.9531 | 149.9518 | 9.7801 | 37.6692 | 4.9019 | 171 | 40.4451 | 51.445 | 96.4889 | 0
14327 | 282.1403 | 0 | 7.4155 | 0 | 16.955 | 0.002376 | 18.8541 | 0.55236 |  | 3.4681 | 13.8181 | 3.5415 |  | 0 | 0 | 2.8122 | 0 | 1.6121 | 152 | 3.7671 | 6.6141 | 8.2368 | 0
14328 | 888.7349 | 3.1192 | 25.576 | 101.2781 | 33.4709 | 8.5497 | 57.1112 | 1.9166 |  | 10.486 | 39.5341 | 6.3614 |  | 46.7086 | 151.253 | 9.8105 | 38.1564 | 4.6133 | 165 | 43.6025 | 63.1058 | 98.11 | 0
14329 | 899.1705 | 6.2581 | 25.7633 | 101.3892 | 38.4411 | 9.4997 | 55.7631 | 2.2792 |  | 11.2455 | 39.175 | 6.1949 |  | 43.1592 | 146.159 | 10.8451 | 38.0272 | 4.1842 | 163 | 42.3458 | 61.3114 | 91.459 | 0
14330 | 889.4754 | 9.8258 | 25.5174 | 98.9277 | 41.4323 | 9.5 | 55.6721 | 1.8894 |  | 11.1557 | 38.8082 | 6.0794 |  | 42.8927 | 140.176 | 9.5141 | 37.5119 | 3.7371 | 159 | 44.6163 | 61.7551 | 91.4175 | 0
14331 | 874.2972 | 7.304 | 25.2283 | 101.5316 | 41.2283 | 9.5 | 54.3723 | 1.5207 |  | 9.5276 | 38.8091 | 6.1168 |  | 43.0414 | 136.6914 | 9.967 | 37.1796 | 3.3612 | 137 | 43.4838 | 60.8209 | 92.2667 | 0
14332 | 880.5835 | 3.938 | 25.2843 | 102.3122 | 42.3384 | 8.5503 | 51.7439 | 2.4129 |  | 8.981 | 39.3181 | 6.1206 |  | 42.6809 | 127.4426 | 9.9894 | 37.121 | 3.2186 | 131 | 37.4222 | 60.8497 | 91.6735 | 0
14333 | 876.1728 | 3.5521 | 25.221 | 100.9018 | 41.8553 | 8.55 | 55.3987 | 2.0475 |  | 7.6565 | 39.014 | 4.8132 |  | 41.2233 | 126.2313 | 9.275 | 37.2715 | 3.1685 | 123 | 37.599 | 67.8349 | 91.9356 | 0
14334 | 884.3801 | 2.7114 | 24.9788 | 99.0409 | 40.6401 | 9.4997 | 57.7039 | 1.3838 |  | 6.2508 | 39.3607 | 5.1087 |  | 39.9876 | 122.7845 | 9.0786 | 36.8502 | 3.0621 | 122 | 32.0086 | 61.5268 | 87.0687 | 0.15621
14335 | 900.1347 | 2.0002 | 24.7296 | 98.8564 | 42.0733 | 8.5503 | 58.2832 | 1.2545 |  | 5.8968 | 42.6682 | 4.0215 |  | 39.9298 | 122.2846 | 9.2862 | 36.5744 | 3.0407 | 115 | 30.5605 | 61.5424 | 88.0032 | 0.23894
14336 | 905.6095 | 2.0328 | 24.7049 | 99.4762 | 42.7363 | 8.55 | 58.6679 | 1.2932 |  | 6.1645 | 41.7962 | 3.4986 |  | 42.785 | 117.6709 | 9.3814 | 36.6981 | 3.0343 | 142 | 33.3592 | 62.6431 | 89.4304 | 0.30926
14337 | 924.9027 | 2.0373 | 24.8096 | 101.7421 | 43.8496 | 8.55 | 58.1368 | 1.2897 |  | 6.6688 | 38.952 | 3.6769 |  | 47.5302 | 123.4754 | 9.4417 | 37.0368 | 3.9705 | 156 | 29.1678 | 63.2694 | 89.757 | 0.33163
14338 | 945.2711 | 1.9144 | 24.8964 | 106.8418 | 42.4275 | 10.4495 | 58.2464 | 1.2348 |  | 7.0481 | 43.4925 | 3.659 |  | 51.3872 | 136.5878 | 9.6426 | 36.8679 | 5.109 | 170 | -0.37243 | 63.3379 | 92.2328 | 0.33559
14339 | 963.0225 | 2.0645 | 25.018 | 108.0998 | 44.1511 | 10.45 | 58.729 | 1.1775 |  | 7.6848 | 46.773 | 3.5322 |  | 54.7696 | 150.0566 | 9.5058 | 36.6857 | 5.699 | 180 | 24.1195 | 63.4446 | 91.663 | 0.28404
14340 | 949.0613 | 2.6296 | 25.3053 | 104.754 | 47.4059 | 9.5003 | 55.9395 | 1.3184 |  | 9.2536 | 47.7892 | 4.0929 |  | 54.8207 | 138.7862 | 8.8823 | 37.4081 | 6.1959 | 163 | 21.1875 | 62.561 | 90.3138 | 0.28903
14341 | 941.6788 | 2.6875 | 25.2374 | 106.3053 | 48.7476 | 9.5 | 54.9881 | 1.1861 |  | 9.5631 | 48.8727 | 4.2705 |  | 58.3034 | 133.8058 | 9.5422 | 36.5543 | 6.6716 | 163 | 26.8369 | 62.8648 | 89.5063 | 0.30541
14342 | 966.4369 | 2.2397 | 25.1455 | 104.819 | 47.1781 | 9.5 | 51.0812 | 1.0278 |  | 8.3791 | 50.0466 | 4.5064 |  | 60.8559 | 132.0066 | 10.0866 | 36.8869 | 6.8702 | 186 | 38.1875 | 63.9629 | 92.957 | 0.31174
14343 | 954.4103 | 3.0817 | 24.9174 | 103.2105 | 45.8235 | 9.5 | 51.9982 | 0.96346 |  | 7.6344 | 55.6502 | 6.9731 |  | 62.828 | 135.4932 | 9.219 | 36.4679 | 6.9842 | 182 | 26.6858 | 65.3802 | 89.4804 | 0.27189
14344 | 946.1629 | 4.8598 | 24.8663 | 105.2338 | 49.5585 | 6.6508 | 56.955 | 0.93892 |  | 8.1693 | 53.0962 | 11.5357 |  | 59.9589 | 149.6658 | 8.8671 | 36.5371 | 7.1908 | 182 | 24.6607 | 62.716 | 88.9391 | 0.23995
14345 | 943.5692 | 5.8057 | 23.895 | 104.0678 | 46.7075 | 4.7505 | 56.701 | 0.94354 |  | 8.4683 | 52.4771 | 15.9011 |  | 59.1416 | 158.7671 | 9.1941 | 36.3586 | 6.8548 | 176 | 33.6624 | 61.4405 | 88.3562 | 0.24632
14346 | 926.1729 | 5.6414 | 23.4006 | 101.5243 | 35.2873 | 6.6495 | 55.6481 | 0.98232 |  | 8.2835 | 55.4976 | 16.5714 |  | 57.3882 | 153.2686 | 9.5051 | 37.4506 | 6.8562 | 141 | 32.4694 | 53.5437 | 87.721 | 0.21505
14347 | 922.6345 | 5.6547 | 23.32 | 98.9742 | 26.3165 | 7.5997 | 56.8685 | 1.0421 |  | 8.0093 | 51.4125 | 12.4598 |  | 53.8018 | 140.946 | 9.635 | 36.8102 | 7.5102 | 137 | 29.9591 | 49.669 | 90.8204 | 0.10803
14348 | 919.5826 | 4.9269 | 23.3323 | 98.5876 | 22.6079 | 7.6 | 57.5871 | 2.2338 |  | 7.1793 | 43.3121 | 6.8396 |  | 52.2524 | 132.2758 | 9.3536 | 37.0795 | 12.13 | 136 | 29.2648 | 50.6462 | 92.6395 | 0
14349 | 908.4119 | 7.1824 | 23.6874 | 101.86 | 18.9424 | 9.4995 | 57.8195 | 2.0457 |  | 8.2892 | 41.7531 | 6.4598 |  | 49.9982 | 127.3221 | 9.6696 | 38.2031 | 8.3404 | 130 | 29.637 | 49.9059 | 96.7089 | 0
14350 | 902.3414 | 10.3117 | 23.7465 | 102.8867 | 19.6061 | 9.5 | 57.2402 | 2.3235 |  | 8.9458 | 40.1227 | 6.888 |  | 46.1379 | 127.1224 | 9.818 | 38.2852 | 10.8074 | 130 | 34.0405 | 50.7161 | 93.1312 | 0
14351 | 279.0404 | 0 | 6.7801 | 28.4395 | 12.1743 | 0.00264 | 17.8487 | 0.86743 |  | 2.902 | 13.4146 | 2.1811 |  | 12.9489 | 42.7958 | 2.7613 | 10.7374 | 4.4623 | 132 | 3.1977 | 6.5001 | 6.9404 | 0
14352 | [18 empty] | 145 |  |  |  | 0
14353 | [18 empty] | 133 |  |  |  | 0
14354 | [18 empty] | 121 |  |  |  | 0
14355 | [18 empty] | 113 |  |  |  | 0
14356 | [18 empty] | 108 |  |  |  | 0
14357 | [18 empty] | 114 |  |  |  | 0
14358 | [18 empty] | 179 |  |  |  | 0.14638
14359 | [18 empty] | 246 |  |  |  | 0.21094
14360 | [18 empty] | 282 |  |  |  | 0.2724
14361 | [18 empty] | 331 |  |  |  | 0.25121
14362 | [18 empty] | 329 |  |  |  | 0.11784
14363 | [18 empty] | 315 |  |  |  | 0.13345
14364 | [18 empty] | 341 |  |  |  | 0.22561
14365 | [18 empty] | 301 |  |  |  | 0.11289
14366 | [18 empty] | 293 |  |  |  | 0.09458
14367 | [18 empty] | 283 |  |  |  | 0.082345
14368 | [18 empty] | 249 |  |  |  | 0.14269
14369 | [18 empty] | 225 |  |  |  | 0.05326
14370 | [18 empty] | 220 |  |  |  | 0.034295
14371 | [18 empty] | 195 |  |  |  | 0.0061745
14372 | [18 empty] | 173 |  |  |  | 0
14373 | [18 empty] | 176 |  |  |  | 0
14374 | [18 empty] | 170 |  |  |  | 0
14375 | [18 empty] | 159 |  |  |  | 0
14376 | 923.3544 | 2.2674 | 41.1769 | 102.6412 | 29.7549 | 8.55 | 52.0926 | 2.4469 |  | 14.5825 | 41.2435 | 7.9542 |  | 51.5514 | 135.2367 | 10.4751 | 38.1465 | 7.1427 | 149 | 33.8466 | 74.405 | 102.6641 | 0
14377 | 929.605 | 2.2423 | 42.3186 | 102.5193 | 26.2338 | 12.3489 | 54.6965 | 1.9859 |  | 12.8311 | 40.6364 | 7.8163 |  | 49.9785 | 134.8893 | 9.9032 | 38.0854 | 5.473 | 134 | 35.8244 | 73.566 | 105.0607 | 0
14378 | 915.9135 | 2.5069 | 52.6329 | 101.5946 | 32.3005 | 10.4505 | 55.0087 | 1.5395 |  | 12.0579 | 40.1918 | 9.8065 |  | 48.7583 | 132.4102 | 10.5464 | 38.2368 | 4.6755 | 137 | 32.8296 | 72.7852 | 103.6909 | 0
14379 | 909.4895 | 2.39 | 56.5525 | 96.339 | 39.5293 | 7.6008 | 57.7708 | 2.2785 |  | 12.1508 | 40.1738 | 15.3149 |  | 48.7888 | 127.6463 | 9.5166 | 38.0139 | 3.6683 | 135 | 32.249 | 72.9344 | 102.7441 | 0
14380 | 891.5513 | 2.8897 | 53.0797 | 94.2226 | 40.7593 | 8.5497 | 58.8957 | 1.9223 |  | 12.9442 | 40.2014 | 15.242 |  | 48.8844 | 121.517 | 9.8747 | 37.7916 | 3.2804 | 126 | 34.9836 | 73.0579 | 106.556 | 0
14381 | 913.4983 | 4.0705 | 44.7999 | 93.4993 | 40.6911 | 9.4997 | 59.644 | 2.2925 |  | 15.0596 | 45.3172 | 11.8295 |  | 51.5136 | 118.2724 | 10.1614 | 37.3733 | 3.2044 | 125 | 31.4623 | 72.2518 | 111.7155 | 0
14382 | 964.4932 | 4.2722 | 49.9374 | 94.3721 | 39.1216 | 10.4497 | 72.0032 | 2.1667 |  | 18.1744 | 50.723 | 15.2118 |  | 72.0058 | 134.1785 | 12.331 | 36.9975 | 5.1539 | 174 | 37.3332 | 70.5556 | 135.2352 | 0.013265
14383 | 1009.3304 | 4.4779 | 72.462 | 98.9471 | 34.7065 | 14.2489 | 95.2345 | 2.8069 |  | 23.435 | 61.7567 | 24.2218 |  | 103.7281 | 175.366 | 24.6355 | 39.3943 | 10.7281 | 270 | 53.4428 | 82.7365 | 175.8508 | 0.15681
14384 | 1064.4911 | 6.6712 | 95.1782 | 108.6064 | 35.3212 | 16.154 | 108.4732 | 3.9946 |  | 25.4193 | 77.3931 | 29.4647 |  | 128.0619 | 229.3555 | 31.6507 | 44.2416 | 13.4986 | 313 | 57.9888 | 92.7357 | 194.1379 | 0.1513
14385 | 1134.6967 | 10.6718 | 104.484 | 117.727 | 32.8452 | 19.9445 | 123.2168 | 5.0726 |  | 24.4898 | 87.0547 | 28.1191 |  | 145.4441 | 262.7258 | 35.0143 | 50.4443 | 14.1766 | 377 | 48.9388 | 101.3801 | 203.1844 | 0.17733
14386 | 1140.5049 | 8.4688 | 107.2419 | 124.1521 | 40.0304 | 15.2055 | 114.4747 | 5.1138 |  | 23.4337 | 89.5927 | 27.8951 |  | 159.2914 | 289.4955 | 37.8908 | 52.9941 | 15.0397 | 374 | 56.4651 | 103.7167 | 199.0066 | 0.19415
14387 | 1154.4677 | 7.9587 | 104.3793 | 124.9141 | 45.0151 | 18.9947 | 101.7401 | 4.9826 |  | 22.9628 | 87.5212 | 29.7062 |  | 165.3502 | 290.6929 | 38.546 | 53.8176 | 15.6272 | 352 | 58.2638 | 105.7159 | 195.2312 | 0.1737
14388 | 1146.572 | 7.9396 | 105.6727 | 125.1977 | 61.4725 | 15.2011 | 104.1695 | 4.6341 |  | 20.8909 | 87.1242 | 31.4141 |  | 158.9325 | 290.6394 | 37.6094 | 51.2462 | 15.8841 | 349 | 53.699 | 101.8167 | 195.3802 | 0.2156
14389 | 1112.6104 | 10.0432 | 109.6638 | 125.166 | 62.0841 | 15.2 | 109.9333 | 3.9522 |  | 28.7831 | 88.9092 | 30.2987 |  | 164.3928 | 284.0744 | 36.3939 | 52.1931 | 16.0212 | 310 | 56.5406 | 100.6265 | 187.8994 | 0.10181
14390 | 1101.7602 | 8.2623 | 112.8767 | 128.0987 | 56.1584 | 15.2 | 141.027 | 4.5034 |  | 31.943 | 89.1275 | 27.136 |  | 167.516 | 284.8401 | 35.6973 | 53.0905 | 16.4658 | 275 | 57.6682 | 0 | 183.6241 | 0.14247
14391 | 1088.558 | 5.5438 | 110.2322 | 122.9418 | 54.399 | 18.0492 | 169.6495 | 4.2409 |  | 30.4796 | 88.5102 | 23.6611 |  | 162.9411 | 271.9091 | 35.5114 | 54.7252 | 16.7446 | 294 | -0.33374 | 98.5586 | 188.0406 | 0.17906
14392 | 1073.4397 | 6.1314 | 106.6141 | 119.2565 | 59.8583 | 11.405 | 132.3698 | 3.7093 |  | 26.9178 | 82.5081 | 20.0142 |  | 149.2828 | 235.0274 | 29.2273 | 55.1466 | 16.675 | 269 | 53.4704 | 97.1973 | 173.6147 | 0.13791
14393 | 1022.2507 | 7.5779 | 99.761 | 113.1882 | 58.6282 | 9.4974 | 84.2433 | 2.5661 |  | 23.0268 | 66.6081 | 16.8755 |  | 124.3771 | 198.7066 | 16.5465 | 50.9602 | 16.2375 | 255 | 48.4686 | 78.1817 | 135.0251 | 0.068105
14394 | 974.7626 | 7.7794 | 82.3931 | 101.5117 | 61.9816 | 6.6508 | 67.48 | 1.6146 |  | 16.0755 | 57.736 | 11.9556 |  | 85.3767 | 179.4164 | 11.9449 | 46.6474 | 13.5467 | 237 | 42.9124 | 0 | 122.3781 | 0.1009
14395 | 961.2497 | 9.5122 | 64.0289 | 96.4324 | 55.3878 | 8.5495 | 62.8355 | 1.1613 |  | 11.8096 | 54.253 | 5.7534 |  | 68.4004 | 164.9581 | 10.2536 | 43.1389 | 8.1501 | 220 | 46.9544 | 67.9918 | 99.4024 | 0.024448
14396 | 941.6399 | 9.9579 | 45.6831 | 94.4591 | 43.628 | 9.4997 | 59.561 | 2.0586 |  | 9.8297 | 53.4056 | 3.972 |  | 63.7679 | 159.8657 | 9.9011 | 42.1245 | 6.4216 | 193 | 41.8993 | 59.203 | 98.9007 | 0
14397 | 937.4179 | 8.3568 | 40.2699 | 95.5281 | 34.5533 | 8.5503 | 56.4234 | 1.8758 |  | 11.0504 | 52.1471 | 5.8706 |  | 63.3319 | 145.6591 | 10.1035 | 42.4334 | 6.3666 | 192 | 38.5642 | 63.1987 | 100.3262 | 0
14398 | 916.3814 | 7.8317 | 36.8575 | 96.6709 | 32.7409 | 7.6003 | 50.9353 | 2.3012 |  | 10.7525 | 46.4375 | 6.863 |  | 59.8847 | 141.9392 | 10.1358 | 41.8193 | 5.854 | 158 | 40.3874 | 67.2718 | 95.9425 | 0
14399 | 281.1918 | 0 | 10.2496 | 0 | 16.4946 | 0.002112 | 15.3515 | 0.87762 |  | 3.3222 | 15.0751 | 2.2439 |  | 0 | 0 | 2.8905 | 0 | 1.8748 | 150 | 4.0169 | 9.2091 | 8.8683 | 0
14400 | 892.592 | 2.7508 | 33.4366 | 99.032 | 27.0304 | 10.4497 | 54.5326 | 2.5749 |  | 11.6941 | 43.5406 | 6.4569 |  | 55.8893 | 126.3777 | 9.8809 | 41.318 | 4.1636 | 143 | 38.0927 | 84.511 | 96.5655 | 0
14401 | 889.4669 | 2.3191 | 34.267 | 100.843 | 32.0156 | 10.45 | 54.866 | 2.0405 |  | 12.2107 | 42.6793 | 6.7556 |  | 53.3129 | 126.7774 | 10.1327 | 40.8788 | 3.5722 | 129 | 34.2933 | 87.8345 | 98.929 | 0
14402 | 885.4737 | 2.3652 | 33.2559 | 101.2802 | 31.9108 | 8.5505 | 63.3159 | 2.386 |  | 12.2294 | 42.0645 | 9.621 |  | 53.1087 | 129.6951 | 10.2973 | 40.8442 | 3.6529 | 129 | 34.554 | 83.4515 | 101.1257 | 0
14403 | 883.2158 | 2.3484 | 32.9111 | 101.3413 | 23.147 | 9.4997 | 71.8993 | 2.8436 |  | 12.4669 | 41.947 | 8.6827 |  | 53.8039 | 126.0209 | 9.7731 | 40.9578 | 4.1018 | 131 | 33.3598 | 84.3132 | 98.8516 | 0
14404 | 881.6646 | 2.7335 | 32.9361 | 101.7485 | 16.2027 | 11.3995 | 74.4672 | 2.0961 |  | 13.4401 | 44.3342 | 7.5747 |  | 54.0401 | 119.3988 | 10.4675 | 41.327 | 3.8369 | 125 | 33.8501 | 88.2096 | 100.4665 | 0
14405 | 899.7712 | 3.8684 | 35.8964 | 99.7856 | 14.4993 | 10.4503 | 73.2343 | 2.5478 |  | 16.6952 | 43.4523 | 8.3486 |  | 54.3801 | 116.0534 | 9.5171 | 40.6356 | 3.3465 | 123 | 36.2919 | 82.528 | 111.4198 | 0
14406 | 931.0458 | 4.2073 | 48.6721 | 101.7536 | 15.2283 | 10.45 | 73.0373 | 2.7502 |  | 22.5006 | 48.2533 | 14.0361 |  | 71.5492 | 124.4387 | 11.9981 | 40.4934 | 5.2782 | 181 | 36.8209 | 81.1147 | 132.1052 | 0.01303
14407 | 978.7338 | 9.3301 | 69.0091 | 102.643 | 9.7875 | 15.1987 | 78.6779 | 3.3874 |  | 28.2234 | 64.0235 | 24.6894 |  | 102.0835 | 175.503 | 25.9289 | 43.6747 | 10.6395 | 251 | 57.5662 | 94.479 | 158.3605 | 0.07788
14408 | 1057.1014 | 18.9801 | 91.0878 | 113.9426 | 5.7786 | 18.0492 | 87.9438 | 4.1047 |  | 35.248 | 73.7057 | 32.8463 |  | 124.6528 | 229.8547 | 35.3661 | 49.5756 | 14.2358 | 270 | 61.7899 | 101.6807 | 178.8546 | 0.094458
14409 | 1147.4893 | 26.694 | 101.0897 | 127.3681 | 7.2238 | 17.1003 | 95.4124 | 4.3059 |  | 38.1676 | 81.2503 | 35.175 |  | 143.514 | 271.8583 | 38.7151 | 53.5845 | 15.0684 | 328 | 57.796 | 101.7852 | 190.6173 | 0.11588
14410 | 1190.3848 | 21.5838 | 105.9869 | 128.5635 | 8.8648 | 18.0497 | 98.8076 | 4.2016 |  | 37.3789 | 85.2718 | 35.2378 |  | 155.5132 | 285.3112 | 39.384 | 55.1364 | 15.7454 | 336 | 51.5406 | 108.5481 | 188.9625 | 0.15032
14411 | 1180.2709 | 13.9395 | 106.8553 | 129.7996 | 10.2727 | 22.7987 | 105.7258 | 4.7213 |  | 36.1342 | 84.6568 | 35.3452 |  | 160.0396 | 289.1422 | 38.8301 | 55.6169 | 16.9907 | 302 | 51.4706 | 101.0115 | 194.8328 | 0.17105
14412 | 1155.2492 | 11.7129 | 106.8004 | 128.4998 | 18.6569 | 21.8503 | 118.8964 | 5.3464 |  | 31.1946 | 83.6635 | 35.6563 |  | 155.0255 | 286.39 | 37.7987 | 53.7563 | 17.4214 | 330 | 47.7585 | 99.6579 | 193.9084 | 0.24972
14413 | 1154.7613 | 11.1753 | 106.309 | 129.57 | 32.0854 | 16.1516 | 128.232 | 5.0594 |  | 26.5971 | 84.6632 | 35.6393 |  | 157.4664 | 284.7211 | 38.0296 | 52.6022 | 17.7363 | 284 | 46.4143 | 105.655 | 189.0534 | 0.10195
14414 | 1177.6842 | 8.2763 | 105.6714 | 130.2195 | 41.9967 | 15.2003 | 146.6596 | 4.4311 |  | 24.4214 | 85.0532 | 33.5771 |  | 155.909 | 286.1273 | 36.4372 | 53.2728 | 17.0239 | 268 | 45.6395 | 106.6036 | 191.8011 | 0.094012
14415 | 1180.4936 | 5.465 | 104.1498 | 126.8006 | 50.582 | 17.0995 | 142.2136 | 3.8815 |  | 26.6155 | 85.3521 | 29.8133 |  | 148.0608 | 280.3067 | 35.3254 | 53.9665 | 16.2116 | 276 | 46.3754 | 100.891 | 187.2852 | 0.18207
14416 | 1144.5818 | 4.7074 | 100.8106 | 125.1068 | 62.6768 | 11.4016 | 110.8124 | 3.2458 |  | 24.396 | 80.2339 | 23.1896 |  | 137.6479 | 252.2332 | 29.5168 | 51.4979 | 15.3855 | 275 | 47.2489 | 98.7999 | 168.0213 | 0.10465
14417 | 1086.0315 | 4.7753 | 95.0502 | 119.2475 | 61.5147 | 13.2995 | 75.5512 | 2.2663 |  | 19.3474 | 64.6295 | 14.6981 |  | 110.1304 | 211.2515 | 17.0296 | 48.3028 | 15.2155 | 254 | 42.4351 | 91.4244 | 128.4282 | 0.044706
14418 | 1043.9026 | 3.5425 | 78.4941 | 107.7615 | 59.6072 | 10.4508 | 60.76 | 1.8752 |  | 13.7663 | 55.9605 | 7.4191 |  | 77.6707 | 182.091 | 11.0645 | 45.5495 | 13.2846 | 250 | 41.6313 | 76.7722 | 114.583 | 0.022728
14419 | 1003.5727 | 4.2688 | 66.9234 | 100.1965 | 53.8492 | 8.5505 | 56.2907 | 2.1597 |  | 10.6914 | 54.3618 | 4.8377 |  | 66.3412 | 164.7215 | 10.183 | 43.2755 | 12.4133 | 203 | 38.7958 | 67.715 | 97.199 | 0.0050238
14420 | 969.146 | 6.9543 | 50.6689 | 98.7117 | 51.3631 | 7.6003 | 51.449 | 2.1945 |  | 10.6689 | 52.445 | 5.3474 |  | 62.6918 | 155.3394 | 9.4706 | 41.3816 | 13.0896 | 168 | 41.3296 | 68.5842 | 94.3389 | 0
14421 | 954.0012 | 7.8267 | 43.848 | 99.7257 | 38.4888 | 9.4995 | 47.0027 | 2.5031 |  | 11.9393 | 49.4431 | 6.6349 |  | 58.6023 | 149.4754 | 9.4233 | 41.0987 | 8.1528 | 163 | 43.4895 | 70.5854 | 96.6992 | 0
14422 | 944.7516 | 7.1597 | 42.8459 | 101.1966 | 34.9831 | 9.5 | 50.5256 | 1.9239 |  | 12.2537 | 43.4937 | 7.1698 |  | 51.8865 | 148.441 | 9.473 | 41.5274 | 5.2992 | 152 | 42.3605 | 64.0396 | 96.9902 | 0
14423 | 300.3585 | 0 | 12.6168 | 29.0779 | 19.6386 | 0.00264 | 17.0754 | 0.51599 |  | 4.0768 | 14.462 | 2.394 |  | 14.7661 | 51.3393 | 2.7561 | 12.1443 | 1.7824 | 143 | 4.3147 | 8.6766 | 9.5042 | 0
14424 | 917.9998 | 7.3164 | 42.1052 | 99.8814 | 35.0566 | 11.4 | 53.4689 | 2.3755 |  | 12.0574 | 40.3128 | 7.395 |  | 43.4685 | 130.7046 | 9.9965 | 41.8619 | 4.6297 | 135 | 41.8535 | 77.6109 | 93.8421 | 0
14425 | 926.2564 | 4.3877 | 42.3639 | 100.0709 | 32.7415 | 10.4503 | 54.0557 | 2.4692 |  | 12.4282 | 40.5103 | 7.1648 |  | 43.4303 | 124.1765 | 9.5015 | 41.4741 | 4.6701 | 125 | 38.0413 | 73.3381 | 94.4396 | 0
14426 | 911.9479 | 2.4766 | 42.3721 | 101.3203 | 33.6438 | 7.6008 | 53.0459 | 2.79 |  | 12.5579 | 40.276 | 7.0832 |  | 43.7667 | 124.4924 | 9.7968 | 41.7963 | 4.6694 | 127 | 40.8306 | 75.8247 | 96.173 | 0
14427 | 904.7849 | 2.3852 | 42.1777 | 100.864 | 25.8825 | 9.4995 | 52.4915 | 1.9837 |  | 12.4749 | 39.9557 | 7.0207 |  | 44.4939 | 118.889 | 9.8593 | 41.3769 | 4.6718 | 129 | 38.6332 | 78.5096 | 97.9519 | 0
14428 | 899.0264 | 2.7738 | 42.2228 | 100.7411 | 17.2402 | 11.3995 | 52.8569 | 2.4542 |  | 13.7074 | 39.7444 | 6.9995 |  | 43.7977 | 117.0015 | 9.9039 | 41.1831 | 4.4452 | 123 | 37.7178 | 75.1566 | 97.1963 | 0
14429 | 911.1852 | 3.9764 | 39.6485 | 99.6601 | 19.0659 | 8.5508 | 53.0715 | 3.0735 |  | 17.1587 | 42.137 | 7.8475 |  | 47.0175 | 116.5469 | 9.3937 | 40.9375 | 4.2483 | 128 | 40.7088 | 75.894 | 106.5885 | 0
14430 | 967.0223 | 5.5768 | 42.1501 | 100.9083 | 15.7202 | 11.3992 | 62.2583 | 2.4398 |  | 22.6293 | 45.6644 | 20.1191 |  | 70.7397 | 124.3631 | 11.7583 | 40.5452 | 6.2129 | 193 | -0.31472 | 87.8206 | 124.8044 | 0.013482
14431 | 1019.2683 | 8.7831 | 65.5475 | 101.6583 | 9.709 | 16.1487 | 86.3119 | 4.1135 |  | 21.3715 | 59.1646 | 29.7207 |  | 102.8861 | 168.7689 | 26.2157 | 42.8785 | 11.4703 | 255 | 67.1532 | 96.7585 | 157.4094 | 0.034183
14432 | 1086.2383 | 18.1787 | 97.1194 | 106.7222 | 10.3633 | 16.15 | 104.4832 | 4.8523 |  | 20.7218 | 75.0657 | 30.3236 |  | 127.446 | 223.7573 | 36.1553 | 48.1273 | 13.4473 | 313 | 66.3528 | 96.7589 | 188.4447 | 0.086821
14433 | 1174.9693 | 27.9072 | 103.1206 | 111.935 | 12.5107 | 16.15 | 114.5681 | 4.7661 |  | 21.5819 | 83.4913 | 28.1983 |  | 141.7078 | 255.1443 | 40.5597 | 52.4096 | 13.5766 | 342 | 59.8705 | 105.1803 | 194.9584 | 0.18588
14434 | 1219.2376 | 25.3572 | 104.5063 | 111.7477 | 18.5729 | 18.0495 | 126.4238 | 4.6336 |  | 23.8633 | 88.9635 | 30.149 |  | 147.9803 | 272.9981 | 41.8998 | 55.0954 | 15.3298 | 351 | 61.5212 | 108.9995 | 199.0935 | 0.11633
14435 | 1221.4498 | 16.4008 | 103.8904 | 115.3547 | 27.6702 | 16.1505 | 134.6854 | 4.5365 |  | 25.5335 | 88.8209 | 30.9244 |  | 151.4944 | 276.3673 | 42.0002 | 57.226 | 16.224 | 321 | 63.6153 | 108.366 | 203.0112 | 0.25315
14436 | 1189.7607 | 7.979 | 99.6786 | 115.1325 | 28.9076 | 17.0997 | 141.4457 | 4.7513 |  | 28.8076 | 88.0597 | 31.0197 |  | 148.3764 | 276.9966 | 42.465 | 54.965 | 16.3116 | 329 | 59.9265 | 109.6231 | 198.981 | 0.24722
14437 | 1194.5308 | 7.3512 | 96.1653 | 118.7499 | 27.9022 | 18.0497 | 141.1746 | 4.6027 |  | 27.4438 | 88.8664 | 31.0628 |  | 153.6559 | 280.4866 | 42.2717 | 54.9736 | 16.1442 | 289 | 59.7273 | 108.3236 | 199.7593 | 0.14859
14438 | 1227.2156 | 12.5486 | 94.5072 | 121.0935 | 32.4804 | 16.1505 | 147.8152 | 4.5461 |  | 28.351 | 89.022 | 32.1457 |  | 153.4611 | 281.9035 | 39.9026 | 54.7711 | 15.9837 | 291 | 55.004 | 104.7261 | 199.837 | 0.13533
14439 | 1200.5573 | 13.557 | 89.1397 | 118.875 | 34.7393 | 18.0495 | 150.8413 | 4.174 |  | 30.1228 | 89.0592 | 33.5664 |  | 150.5304 | 281.0441 | 38.0664 | 53.9812 | 15.6431 | 293 | 53.9234 | 98.3442 | 194.6953 | 0.21608
14440 | 1140.031 | 10.4849 | 86.4239 | 119.6362 | 43.2657 | 11.4018 | 123.1384 | 3.3229 |  | 28.498 | 83.2629 | 24.4455 |  | 143.8696 | 247.9362 | 32.5319 | 53.7977 | 15.3498 | 268 | 54.2977 | 0 | 173.3674 | 0.11215
14441 | 1080.891 | 6.0387 | 83.1691 | 116.3488 | 45.0254 | 9.5005 | 85.7722 | 2.4782 |  | 21.7279 | 67.2384 | 11.4855 |  | 118.7138 | 206.303 | 24.2112 | 50.849 | 15.0064 | 217 | 46.8075 | 83.5722 | 139.8712 | 0.19678
14442 | 1055.6816 | 5.7125 | 69.685 | 107.2518 | 43.0077 | 7.6005 | 64.9408 | 2.6577 |  | 15.1935 | 58.5047 | 6.2026 |  | 83.9496 | 181.8593 | 13.0786 | 46.1854 | 12.1326 | 221 | 41.3653 | 76.1123 | 126.1806 | 0.17772
14443 | 1017.662 | 6.5028 | 55.9471 | 103.857 | 43.4259 | 7.6 | 56.9888 | 2.5067 |  | 14.8093 | 54.4899 | 7.9922 |  | 69.5791 | 161.2022 | 9.4886 | 43.3005 | 6.2911 | 187 | 40.5132 | 67.9287 | 108.4508 | 0.046622
14444 | 998.5839 | 5.163 | 31.802 | 102.5964 | 42.3797 | 10.4492 | 58.158 | 2.1722 |  | 14.8681 | 52.8206 | 8.8576 |  | 66.2305 | 145.0892 | 9.5551 | 42.6529 | 4.081 | 180 | 36.8647 | 68.4632 | 106.6714 | 0
14445 | 977.7523 | 4.4146 | 24.0009 | 102.1335 | 41.7324 | 10.45 | 57.5873 | 1.7389 |  | 14.8617 | 51.279 | 8.0194 |  | 58.7492 | 133.8407 | 9.3828 | 42.1552 | 4.1343 | 179 | 35.1844 | 69.588 | 109.5438 | 0
14446 | 949.9663 | 4.0083 | 24.1062 | 102.1395 | 45.9659 | 6.6511 | 57.0287 | 2.2572 |  | 14.1146 | 45.3193 | 7.6608 |  | 54.5318 | 131.9658 | 9.865 | 41.72 | 4.2318 | 172 | 33.3857 | 64.8062 | 112.7613 | 0
14447 | 287.0974 | 0 | 6.7788 | 0 | 21.1495 | 0 | 17.6493 | 0.84313 |  | 4.3934 | 14.453 | 2.4331 |  | 0 | 0 | 2.8089 | 0 | 1.396 | 151 | 3.3566 | 8.7508 | 11.9831 | 0
14448 | 919.269 | 2.2785 | 23.7917 | 101.8349 | 43.1094 | 8.55 | 45.0705 | 1.6298 |  | 12.443 | 43.1618 | 7.5157 |  | 51.9947 | 137.8526 | 9.8906 | 41.1549 | 4.7114 | 148 | 31.2945 | 81.2445 | 104.6458 | 0
14449 | 913.7212 | 2.1467 | 25.5497 | 101.5264 | 45.2557 | 7.6003 | 51.9599 | 1.5578 |  | 12.3498 | 42.775 | 7.2672 |  | 50.6785 | 136.7846 | 9.6865 | 41.1799 | 4.2668 | 136 | 30.3826 | 74.5819 | 104.569 | 0
14450 | 917.5762 | 4.4491 | 36.6973 | 100.9861 | 43.1198 | 9.4995 | 55.1358 | 2.288 |  | 11.9064 | 42.3124 | 9.0849 |  | 49.624 | 126.3342 | 10.2638 | 41.2657 | 4.0449 | 138 | 33.0252 | 80.3384 | 105.2846 | 0
14451 | 901.7376 | 8.1212 | 41.1339 | 101.0966 | 43.8135 | 8.5503 | 55.1728 | 1.92 |  | 11.752 | 42.1472 | 14.9381 |  | 50.0299 | 121.7827 | 9.2156 | 41.4306 | 4.047 | 133 | 27.2386 | 81.2751 | 103.5408 | 0
14452 | 896.276 | 7.0105 | 42.4736 | 100.6184 | 44.0499 | 8.55 | 54.5062 | 1.7922 |  | 12.5583 | 43.1025 | 14.8496 |  | 50.3824 | 120.6331 | 9.4429 | 41.3199 | 3.827 | 130 | 27.7573 | 73.6142 | 105.7326 | 0
14453 | 920.2791 | 3.8834 | 44.8766 | 100.6445 | 44.8228 | 8.55 | 44.1509 | 1.7022 |  | 15.4504 | 48.5983 | 12.1175 |  | 52.9236 | 123.8025 | 10.1542 | 41.246 | 3.2259 | 127 | 28.3535 | 75.7669 | 116.4188 | 0
14454 | 975.7975 | 3.8402 | 48.2171 | 102.466 | 43.3987 | 9.4997 | 72.8448 | 2.0513 |  | 19.406 | 51.1231 | 15.1909 |  | 74.4393 | 137.168 | 12.4482 | 40.8822 | 5.5878 | 179 | 31.4342 | 75.7695 | 137.8438 | 0.096192
14455 | 1017.8363 | 11.9303 | 69.7434 | 104.6111 | 38.5292 | 15.1984 | 110.6918 | 2.6738 |  | 23.2217 | 61.2792 | 22.5929 |  | 104.7752 | 175.9068 | 25.212 | 43.7395 | 13.1829 | 259 | 59.2015 | 83.358 | 177.2425 | 0.16177
14456 | 1068.3902 | 13.5709 | 98.5794 | 119.3939 | 40.8203 | 15.2 | 124.9748 | 4.7714 |  | 25.0408 | 72.9846 | 28.8257 |  | 130.6611 | 234.7837 | 35.7694 | 49.2035 | 15.0387 | 296 | 66.6844 | 96.1597 | 198.891 | 0.14418
14457 | 1125.4805 | 15.3398 | 106.8716 | 132.8627 | 43.4107 | 14.2503 | 135.2631 | 4.7624 |  | 26.9573 | 79.6064 | 29.3426 |  | 150.6575 | 279.391 | 39.7033 | 53.109 | 14.7963 | 341 | 59.9005 | 107.2417 | 214.9112 | 0.13876
14458 | 1182.985 | 16.7917 | 106.6283 | 138.8243 | 44.039 | 16.1495 | 148.1805 | 4.5307 |  | 25.6641 | 84.8591 | 29.4373 |  | 161.5136 | 296.872 | 38.9246 | 55.5612 | 15.193 | 332 | 60.3828 | 115.1637 | 209.2839 | 0.20183
14459 | 1169.7245 | 14.7017 | 104.9439 | 140.1438 | 49.0038 | 15.2003 | 153.435 | 4.5095 |  | 22.4675 | 85.4368 | 28.1461 |  | 159.8895 | 290.3674 | 38.0696 | 56.3168 | 15.321 | 295 | 57.504 | 110.7968 | 203.3223 | 0.21059
14460 | 1157.0072 | 8.701 | 103.6719 | 139.6221 | 48.3296 | 17.0995 | 149.898 | 4.8925 |  | 20.8534 | 85.3595 | 29.0597 |  | 152.541 | 287.3744 | 40.9403 | 55.5309 | 15.0051 | 318 | 54.4529 | 105.7927 | 202.6451 | 0.25139
14461 | 1149.7934 | 5.0124 | 106.8418 | 137.4334 | 45.6449 | 16.1503 | 146.9046 | 5.2413 |  | 26.3888 | 86.1519 | 29.0387 |  | 150.1123 | 287.8653 | 43.624 | 56.9667 | 14.4471 | 292 | -0.42466 | 104.8269 | 197.2622 | 0.25939
14462 | 1141.8346 | 4.4034 | 105.985 | 136.0458 | 43.245 | 17.0997 | 140.8029 | 4.3622 |  | 26.4006 | 87.7694 | 25.121 |  | 149.4558 | 280.671 | 41.4019 | 56.1355 | 13.796 | 280 | 54.7896 | 105.1781 | 197.975 | 0.24873
14463 | 1107.3369 | 4.3696 | 103.8786 | 137.2011 | 42.1701 | 18.0497 | 136.0578 | 3.5868 |  | 22.5043 | 86.4923 | 20.6782 |  | 139.2982 | 262.0131 | 36.9842 | 55.1911 | 14.2067 | 276 | 55.9781 | 100.8442 | 182.5478 | 0.30002
14464 | 1063.0369 | 3.8949 | 100.4363 | 128.1836 | 44.9206 | 16.1505 | 120.9197 | 2.9577 |  | 20.3486 | 78.0105 | 13.2621 |  | 130.6487 | 235.7094 | 28.4452 | 52.794 | 14.9786 | 277 | 55.199 | 96.0085 | 163.2573 | 0.23477
14465 | 1009.3353 | 3.8052 | 85.199 | 119.249 | 45.719 | 11.4013 | 81.3269 | 1.7622 |  | 16.1859 | 61.54 | 7.464 |  | 103.5321 | 206.6367 | 15.9455 | 49.2854 | 14.2922 | 225 | 50.4686 | 75.3394 | 130.7249 | 0.21129
14466 | 970.5427 | 4.9787 | 46.0685 | 109.7044 | 44.5095 | 9.5005 | 65.7005 | 1.2933 |  | 9.9104 | 52.4718 | 4.8966 |  | 64.2324 | 187.8494 | 11.7329 | 45.8446 | 11.1731 | 215 | 39.3687 | 67.4541 | 112.8672 | 0.16401
14467 | 948.8918 | 5.146 | 28.9496 | 103.6314 | 46.0459 | 6.6508 | 63.3824 | 1.8929 |  | 7.678 | 48.1278 | 4.1892 |  | 50.9766 | 166.6678 | 11.7877 | 43.7053 | 5.5943 | 209 | 37.4683 | 68.3219 | 96.8607 | 0.0036988
14468 | 931.6952 | 6.2343 | 26.9656 | 101.9404 | 39.723 | 10.4489 | 66.7683 | 1.6982 |  | 8.3294 | 43.5464 | 4.7808 |  | 50.8586 | 149.5703 | 10.7813 | 42.8759 | 3.6332 | 187 | 40.0584 | 62.7005 | 97.3462 | 0
14469 | 918.9742 | 6.6974 | 26.327 | 102.9983 | 35.441 | 9.5003 | 68.3656 | 1.5671 |  | 10.0326 | 44.6503 | 6.2326 |  | 51.9526 | 142.018 | 10.182 | 43.4464 | 3.7787 | 169 | 35.6442 | 62.8582 | 99.9921 | 0
14470 | 909.864 | 4.6588 | 26.0046 | 102.6386 | 34.6426 | 7.6005 | 57.8708 | 1.8109 |  | 10.4761 | 43.7472 | 6.9221 |  | 52.7095 | 146.7154 | 9.6801 | 43.3645 | 3.9986 | 148 | 36.2325 | 67.5841 | 99.3996 | 0
14471 | 276.2588 | 0 | 7.3119 | 27.8402 | 17.0332 | 0.002112 | 16.39 | 0.61726 |  | 3.33 | 14.5178 | 2.2222 |  | 15.0302 | 49.5188 | 2.6401 | 11.9871 | 1.3352 | 132 | 3.7472 | 9.4732 | 10.7492 | 0
14472 | 884.8799 | 2.3105 | 25.6356 | 102.3246 | 34.2872 | 10.4495 | 52.628 | 1.9139 |  | 9.4072 | 40.7203 | 7.4987 |  | 51.1346 | 148.9732 | 9.6285 | 43.5658 | 4.044 | 120 | 30.8089 | 79.1159 | 95.6716 | 0
14473 | 870.4057 | 2.3718 | 27.4121 | 101.94 | 34.6193 | 9.5003 | 46.3146 | 1.5569 |  | 9.3263 | 39.5549 | 6.5861 |  | 51.6773 | 134.8896 | 10.462 | 43.2909 | 4.0618 | 121 | 32.8966 | 80.9746 | 90.0686 | 0
14474 | 861.9652 | 2.4538 | 38.6346 | 102.1388 | 29.6673 | 10.4497 | 51.304 | 1.567 |  | 9.4169 | 38.6919 | 6.2685 |  | 50.1922 | 127.5723 | 9.4723 | 42.8097 | 3.8101 | 118 | 30.5978 | 76.5256 | 88.5485 | 0
14475 | 865.0519 | 2.4 | 43.0442 | 102.9147 | 30.4973 | 6.6511 | 53.2621 | 2.2352 |  | 9.6176 | 38.8409 | 6.4863 |  | 50.1478 | 121.7 | 9.8864 | 43.0636 | 3.4653 | 111 | 29.6479 | 80.2487 | 89.1617 | 0
14476 | 858.6938 | 2.8877 | 43.9707 | 101.7837 | 28.5629 | 7.5997 | 51.3527 | 2.2306 |  | 9.5475 | 41.1299 | 6.3996 |  | 50.5416 | 118.3139 | 9.2636 | 42.8299 | 3.311 | 109 | 30.7458 | 0 | 87.938 | 0
14477 | 874.0122 | 3.6887 | 35.0958 | 100.9572 | 28.6742 | 11.3989 | 43.4719 | 1.7461 |  | 9.9871 | 45.1253 | 7.0201 |  | 48.5218 | 121.9514 | 10.2567 | 42.8201 | 3.2989 | 109 | 27.2438 | 70.9817 | 89.598 | 0
14478 | 887.2519 | 3.4943 | 44.7976 | 99.4734 | 40.2433 | 7.6011 | 42.3902 | 1.357 |  | 9.4184 | 42.3864 | 6.6158 |  | 46.542 | 125.7325 | 9.4896 | 42.534 | 3.4527 | 104 | 30.4881 | 70.6374 | 82.7335 | 0.020124
14479 | 903.0132 | 2.8157 | 53.9199 | 99.3368 | 43.0776 | 8.5497 | 50.9023 | 1.9115 |  | 7.6676 | 38.992 | 6.4757 |  | 46.6058 | 120.5768 | 9.1737 | 42.1583 | 3.3137 | 111 | 44.9358 | 76.9586 | 84.3852 | 0.043862
14480 | 916.1832 | 2.3115 | 63.8624 | 99.1523 | 45.6022 | 7.6003 | 56.1768 | 1.681 |  | 6.8742 | 38.3848 | 6.6506 |  | 47.5303 | 124.1421 | 9.5132 | 42.2254 | 3.4811 | 123 | 50.3155 | 69.392 | 85.4558 | 0.089003
14481 | 930.0421 | 2.0067 | 64.5957 | 99.2898 | 43.7564 | 10.4492 | 56.1687 | 1.876 |  | 7.0916 | 40.805 | 6.4877 |  | 50.5861 | 123.8638 | 8.8138 | 42.2515 | 5.3258 | 143 | 51.636 | 73.367 | 87.8474 | 0.24914
14482 | 942.7816 | 2.1597 | 64.0889 | 100.6547 | 44.1622 | 11.3997 | 49.3673 | 2.7475 |  | 6.9896 | 46.0789 | 6.8279 |  | 49.1477 | 128.1305 | 9.4553 | 42.5111 | 10.3537 | 151 | 48.3662 | 76.2346 | 91.3519 | 0.23913
14483 | 942.9618 | 2.7659 | 64.9538 | 101.1453 | 45.7432 | 10.4503 | 45.563 | 1.8938 |  | 8.1096 | 48.8312 | 7.5181 |  | 45.0937 | 129.9964 | 9.1974 | 42.699 | 12.4313 | 165 | 45.5896 | 72.6451 | 92.9493 | 0.24762
14484 | 941.8138 | 2.6141 | 65.3707 | 101.6652 | 47.935 | 8.5505 | 49.2015 | 1.1117 |  | 13.1308 | 49.5762 | 6.4361 |  | 50.2213 | 140.4582 | 8.9881 | 42.9599 | 12.593 | 170 | 43.3167 | 73.9383 | 89.026 | 0.27628
14485 | 946.7303 | 2.5544 | 57.1421 | 107.3908 | 50.1948 | 5.7008 | 50.9905 | 1.0055 |  | 11.4689 | 49.8983 | 10.8654 |  | 51.6031 | 144.908 | 8.7846 | 42.6477 | 13.0141 | 147 | 34.4937 | 75.6556 | 92.4792 | 0.26825
14486 | 950.5565 | 2.4466 | 31.4839 | 111.5065 | 39.1488 | 6.6497 | 52.086 | 1.0062 |  | 9.0016 | 51.7807 | 8.5675 |  | 50.4074 | 152.3992 | 9.0952 | 42.516 | 10.9509 | 165 | 28.8471 | 77.6803 | 91.3442 | 0.29982
14487 | 931.3995 | 3.4721 | 19.8838 | 110.7765 | 34.9645 | 7.5997 | 52.2789 | 1.2568 |  | 8.4883 | 55.5572 | 4.7215 |  | 51.6958 | 150.6233 | 9.3913 | 42.7024 | 6.1673 | 161 | 34.7682 | 73.3904 | 90.0375 | 0.2969
14488 | 921.0332 | 5.1702 | 17.1715 | 104.8776 | 35.7575 | 8.5497 | 56.7021 | 1.0942 |  | 8.6072 | 58.0449 | 3.8504 |  | 54.6496 | 151.8827 | 9.9313 | 42.7409 | 4.2708 | 161 | 31.8123 | 79.0167 | 91.2744 | 0.059764
14489 | 915.6463 | 5.312 | 16.4036 | 102.5924 | 39.8539 | 7.6003 | 48.3579 | 0.95371 |  | 8.8119 | 50.7722 | 4.0661 |  | 56.6262 | 147.3194 | 8.9502 | 42.3768 | 4.3538 | 179 | 33.6971 | 74.4553 | 89.5592 | 0.039039
14490 | 907.3655 | 3.8677 | 16.0714 | 100.8073 | 34.5882 | 7.6 | 50.6254 | 0.96769 |  | 8.1282 | 43.5263 | 4.0657 |  | 53.2515 | 146.3115 | 8.8883 | 41.5964 | 4.0661 | 176 | 39.2417 | 61.4831 | 85.8078 | 0.13839
14491 | 901.8295 | 4.5903 | 16.355 | 102.0144 | 30.6793 | 8.5497 | 55.9174 | 1.0029 |  | 7.6038 | 40.5688 | 4.374 |  | 54.7516 | 147.4673 | 9.4219 | 41.2394 | 4.0033 | 183 | 37.7998 | 65.11 | 84.963 | 0.015904
14492 | 907.6572 | 6.0321 | 16.6472 | 106.963 | 30.7326 | 8.55 | 55.1218 | 2.0445 |  | 8.6534 | 40.7018 | 5.5936 |  | 56.9381 | 153.0925 | 9.1206 | 41.3499 | 4.6345 | 178 | 39.6026 | 67.3536 | 90.1856 | 0
14493 | 906.0626 | 7.3669 | 17.471 | 109.5268 | 31.1875 | 8.55 | 53.5196 | 1.8762 |  | 9.8576 | 42.8503 | 6.5849 |  | 55.4004 | 153.5396 | 9.2114 | 41.7183 | 4.837 | 193 | 39.0382 | 63.9337 | 89.3095 | 0
14494 | 894.9609 | 7.1838 | 17.2645 | 109.79 | 29.3212 | 10.4495 | 43.8959 | 1.7829 |  | 10.0801 | 43.6839 | 7.587 |  | 51.6117 | 153.2882 | 9.7437 | 42.1293 | 4.7602 | 190 | 40.277 | 68.2893 | 93.4966 | 0
14495 | 272.7995 | 2.3533 | 4.8326 | 30.0409 | 15.9598 | 0.002903 | 12.326 | 0.61306 |  | 3.2349 | 14.9077 | 2.5334 |  | 14.3871 | 50.9784 | 2.7592 | 11.7486 | 1.5555 | 178 | 4.1215 | 9.5193 | 9.2218 | 0
14496 | 869.2481 | 5.8048 | 16.8232 | 102.1327 | 23.1015 | 11.3997 | 54.081 | 1.9042 |  | 11.0083 | 42.32 | 6.8899 |  | 51.2089 | 142.0366 | 12.5558 | 42.6633 | 4.3844 | 192 | 49.5632 | 86.5707 | 91.8158 | 0
14497 | 866.1075 | 3.3941 | 17.3393 | 102.1435 | 25.3501 | 9.5005 | 56.47 | 1.5584 |  | 12.0874 | 42.0674 | 6.9251 |  | 50.0879 | 134.6511 | 13.5977 | 42.3081 | 4.1374 | 195 | 45.3706 | 86.6068 | 96.6791 | 0
14498 | 861.4073 | 2.274 | 16.8691 | 101.5681 | 30.12 | 8.5503 | 55.6019 | 2.2904 |  | 11.9331 | 41.2856 | 6.9606 |  | 48.0608 | 130.2887 | 14.1185 | 42.1299 | 4.1255 | 184 | 44.5251 | 89.2325 | 101.4558 | 0
14499 | 866.706 | 2.6226 | 16.6871 | 101.1965 | 37.7588 | 7.6003 | 43.9406 | 1.9129 |  | 11.5352 | 40.4996 | 7.0234 |  | 43.573 | 122.392 | 13.8052 | 41.9339 | 3.7986 | 170 | 46.2822 | 87.0328 | 98.5721 | 0
14500 | 859.5698 | 2.9997 | 21.4872 | 101.3614 | 41.6873 | 7.6 | 48.4561 | 1.5351 |  | 10.2076 | 40.1285 | 6.9234 |  | 41.865 | 121.2824 | 12.5208 | 42.4482 | 3.2733 | 151 | 45.137 | 84.2546 | 98.3235 | 0
14501 | 861.2656 | 3.6207 | 22.8814 | 100.5217 | 41.2153 | 8.5497 | 51.8377 | 2.249 |  | 9.017 | 39.4389 | 6.4255 |  | 41.9385 | 124.2036 | 10.1859 | 42.1947 | 3.0426 | 145 | 42.9213 | 86.7818 | 96.2212 | 0
14502 | 878.7683 | 3.607 | 18.0735 | 99.1109 | 39.507 | 9.4997 | 51.1781 | 1.9576 |  | 7.4179 | 37.2758 | 4.4887 |  | 39.1979 | 124.6448 | 9.536 | 41.6019 | 2.8773 | 137 | 39.2757 | 69.2096 | 89.1568 | 0.033753
14503 | 885.0454 | 2.4024 | 16.0993 | 99.4404 | 38.9099 | 9.5 | 48.2789 | 1.3842 |  | 6.9631 | 40.1362 | 3.7553 |  | 38.7397 | 119.6664 | 9.1115 | 42.235 | 2.8246 | 134 | 35.3513 | 73.3887 | 85.0686 | 0.035971
14504 | 892.4536 | 2.1113 | 15.8683 | 100.4337 | 39.5539 | 8.5503 | 40.145 | 1.329 |  | 8.6223 | 41.415 | 3.7889 |  | 39.2934 | 116.204 | 9.1075 | 41.7562 | 2.8709 | 143 | 26.3751 | 76.1882 | 88.545 | 0.17883
14505 | 899.9476 | 2.2071 | 15.9891 | 98.8388 | 38.768 | 9.4997 | 50.2135 | 1.3477 |  | 10.9561 | 40.4569 | 4.0292 |  | 41.3522 | 122.8269 | 9.7706 | 41.9439 | 3.1522 | 163 | 23.4027 | 73.6132 | 88.0174 | 0.22451
14506 | 925.6256 | 2.3218 | 16.1325 | 100.3229 | 40.623 | 8.5503 | 56.8567 | 1.2772 |  | 11.3836 | 45.8816 | 4.0049 |  | 44.1997 | 132.9532 | 8.7637 | 41.8445 | 3.156 | 164 | 29.9204 | 72.8177 | 86.9589 | 0.24918
14507 | 937.602 | 2.4795 | 16.2299 | 102.3384 | 43.2113 | 8.55 | 56.7345 | 1.133 |  | 11.1887 | 48.5561 | 4.6522 |  | 48.2918 | 131.6932 | 9.7462 | 41.5705 | 3.6724 | 190 | 25.3707 | 77.6136 | 89.5331 | 0.24505
14508 | 924.417 | 2.5896 | 16.1417 | 100.7497 | 47.2043 | 7.6003 | 57.0469 | 0.99555 |  | 11.3083 | 49.3275 | 4.2012 |  | 51.2983 | 134.7894 | 9.6701 | 42.0499 | 3.7832 | 193 | 28.9475 | 76.0278 | 86.7076 | 0.25791
14509 | 924.528 | 2.4645 | 16.1223 | 99.4151 | 49.365 | 8.5497 | 55.8281 | 2.2155 |  | 10.5799 | 50.2597 | 3.7162 |  | 49.7735 | 135.5077 | 9.3695 | 42.1307 | 3.5525 | 196 | 31.3522 | 74.7468 | 86.5853 | 0.20601
14510 | 915.1192 | 3.2243 | 15.8014 | 101.2132 | 48.7991 | 10.4495 | 49.399 | 2.5905 |  | 9.3315 | 50.5485 | 3.7629 |  | 50.9344 | 151.0136 | 8.9129 | 41.5259 | 3.4342 | 180 | 28.3287 | 79.5282 | 87.7137 | 0.12366
14511 | 907.1626 | 3.1028 | 16.4482 | 104.7763 | 48.7697 | 7.6008 | 43.0343 | 2.6644 |  | 8.6066 | 51.8812 | 3.7866 |  | 53.5369 | 158.3347 | 8.4443 | 41.6111 | 3.4672 | 190 | 31.4224 | 78.6619 | 92.3171 | 0.095915
14512 | 913.7835 | 2.6294 | 16.3469 | 104.9849 | 41.2435 | 6.6503 | 49.1275 | 2.8287 |  | 9.0135 | 52.373 | 3.795 |  | 55.0825 | 157.1296 | 8.9635 | 41.3741 | 3.4935 | 166 | 32.2836 | 71.4799 | 85.6717 | 0.05745
14513 | 912.7428 | 5.3435 | 16.3554 | 100.4117 | 32.7429 | 9.4992 | 55.5165 | 2.5956 |  | 9.2991 | 50.5016 | 4.1622 |  | 55.4676 | 146.7548 | 9.4263 | 41.0033 | 3.7931 | 160 | 29.5806 | 72.5508 | 88.2376 | 0.036949
14514 | 895.3298 | 6.4196 | 16.3051 | 98.8058 | 35.6226 | 8.5503 | 56.0089 | 2.548 |  | 9.3368 | 48.9931 | 4.0329 |  | 54.1415 | 142.4095 | 8.1952 | 40.6944 | 3.6827 | 144 | 34.8481 | 69.5469 | 88.6096 | 0.016846
14515 | 883.8912 | 6.015 | 16.0457 | 98.8854 | 35.6576 | 7.6003 | 55.7326 | 1.6147 |  | 9.1396 | 48.0301 | 3.8421 |  | 52.784 | 137.9426 | 8.3519 | 41.464 | 3.832 | 123 | 33.8427 | 61.6671 | 88.9308 | 0.0015458
14516 | 868.4353 | 4.9834 | 16.4248 | 100.2804 | 33.751 | 7.6 | 55.3193 | 2.0583 |  | 9.2567 | 45.1086 | 5.4415 |  | 53.0937 | 142.9525 | 9.3799 | 41.7919 | 4.3063 | 119 | 32.6493 | 66.506 | 85.5283 | 0
14517 | 872.2142 | 4.2531 | 16.7175 | 101.8673 | 29.6142 | 10.4492 | 50.9781 | 1.8808 |  | 10.0344 | 44.4222 | 6.4296 |  | 52.6384 | 137.8624 | 9.4909 | 41.7399 | 4.117 | 117 | 31.4162 | 66.2331 | 86.9009 | 0
14518 | 856.6534 | 3.9532 | 16.811 | 102.0552 | 27.4022 | 11.3997 | 43.5203 | 1.5629 |  | 10.251 | 44.3619 | 6.5561 |  | 46.6667 | 132.498 | 8.69 | 41.7079 | 3.6526 | 116 | 34.4515 | 61.0199 | 85.1036 | 0
14519 | 262.5722 | 1.3439 | 4.8406 | 28.3518 | 15.7593 | 0.003167 | 12.8278 | 0.51089 |  | 3.3206 | 15.2171 | 2.1192 |  | 12.8443 | 44.2347 | 2.3694 | 11.8075 | 1.1631 | 113 | 3.5584 | 8.2143 | 8.7131 | 0
14520 | 853.6638 | 3.262 | 16.4828 | 101.6438 | 27.3268 | 6.6508 | 50.5694 | 1.884 |  | 11.5463 | 41.304 | 6.8658 |  | 42.2217 | 121.586 | 9.3943 | 42.282 | 3.0341 | 115 | 36.2029 | 89.1283 | 86.0897 | 0
14521 | 854.5078 | 2.3055 | 18.896 | 103.0878 | 23.0703 | 10.4489 | 50.9311 | 2.6265 |  | 12.4079 | 40.581 | 6.7129 |  | 41.3708 | 118.8819 | 9.3516 | 42.2923 | 2.9017 | 115 | 35.206 | 83.8578 | 85.2497 | 0
14522 | 842.3953 | 2.8836 | 31.0015 | 102.2896 | 34.0272 | 7.6008 | 53.3033 | 2.1057 |  | 12.36 | 40.4532 | 6.6039 |  | 42.2623 | 120.4553 | 9.1686 | 42.2685 | 2.8922 | 123 | 38.5518 | 85.4631 | 86.0977 | 0
14523 | 833.6055 | 2.6189 | 35.4623 | 101.6049 | 31.3111 | 9.4995 | 51.5348 | 2.3937 |  | 12.2467 | 40.4006 | 6.4668 |  | 42.6854 | 118.2485 | 9.2186 | 42.1191 | 2.9112 | 126 | 35.2054 | 89.0638 | 87.38 | 0
14524 | 835.9686 | 2.7516 | 31.6273 | 101.8321 | 23.6132 | 9.5 | 43.1923 | 2.4915 |  | 13.1796 | 40.8664 | 6.4987 |  | 41.798 | 114.8213 | 9.5943 | 42.0289 | 2.9385 | 121 | 37.7675 | 84.2077 | 90.4533 | 0
14525 | 844.8477 | 3.6545 | 28.8697 | 100.9828 | 22.1134 | 9.5 | 49.2995 | 2.033 |  | 16.4393 | 44.3105 | 8.6182 |  | 44.8317 | 117.0682 | 9.0315 | 41.8272 | 2.9229 | 120 | 37.7788 | 72.9541 | 98.4303 | 0
14526 | 897.9605 | 4.1539 | 42.6371 | 104.1047 | 25.0096 | 10.4497 | 65.9078 | 2.6836 |  | 24.6504 | 46.8207 | 13.6706 |  | 66.7704 | 130.3909 | 11.621 | 41.7286 | 5.687 | 182 | 38.3911 | 76.0282 | 118.2952 | 0
14527 | 937.7446 | 12.0873 | 68.4739 | 111.2259 | 20.246 | 15.2029 | 88.2402 | 3.2128 |  | 26.7298 | 59.2238 | 25.3502 |  | 104.2444 | 185.9009 | 26.1441 | 44.6256 | 11.6465 | 274 | 56.2303 | 93.7493 | 150.715 | 0.028789
14528 | 1021.0007 | 17.0721 | 98.6454 | 127.3149 | 20.0895 | 15.1958 | 102.7903 | 4.689 |  | 33.0233 | 71.0787 | 33.8663 |  | 133.1566 | 240.4198 | 36.5305 | 49.3752 | 14.5805 | 287 | 51.1409 | 94.3357 | 176.1245 | 0.050729
14529 | 1074.3779 | 22.8125 | 105.356 | 138.3478 | 21.4554 | 16.1497 | 113.2764 | 4.8776 |  | 38.023 | 76.9445 | 37.7732 |  | 153.8868 | 281.9057 | 38.0795 | 54.0558 | 17.361 | 315 | 58.8141 | 100.0221 | 195.0628 | 0.068519
14530 | 1122.2903 | 28.0543 | 92.7893 | 141.2643 | 22.9013 | 18.0244 | 119.1808 | 4.6447 |  | 39.9676 | 79.3779 | 39.1854 |  | 161.5328 | 302.2349 | 37.3202 | 58.4039 | 17.4133 | 334 | 63.9695 | 108.7486 | 183.8965 | 0.1161
14531 | 1140.8568 | 24.4693 | 92.1956 | 140.4719 | 29.9584 | 15.2258 | 129.899 | 4.6686 |  | 42.0719 | 80.8077 | 36.9518 |  | 166.07 | 301.7328 | 37.5991 | 58.6389 | 18.3612 | 339 | 58.0968 | 117.5288 | 187.3114 | 0.093396
14532 | 1119.5561 | 15.4365 | 95.9362 | 141.9484 | 34.6168 | 15.2 | 138.2976 | 4.5055 |  | 38.3733 | 84.7824 | 36.2519 |  | 167.2496 | 300.4769 | 39.7158 | 56.398 | 18.6403 | 390 | 50.9191 | 111.2364 | 183.4602 | 0.099934
14533 | 1117.4823 | 9.2078 | 105.9887 | 141.4642 | 39.1363 | 18.0492 | 140.7449 | 5.0817 |  | 37.9557 | 86.8867 | 39.1082 |  | 165.9131 | 300.163 | 39.4499 | 56.4664 | 16.246 | 301 | 62.0685 | 108.7613 | 191.8496 | 0.14136
14534 | 1136.2559 | 10.9404 | 111.2774 | 148.1296 | 48.6325 | 18.9997 | 153.1331 | 5.2126 |  | 40.0024 | 86.3943 | 39.866 |  | 163.9059 | 302.0985 | 37.3644 | 55.7823 | 16.775 | 289 | 64.6614 | 109.4765 | 187.6348 | 0.089747
14535 | 1115.0429 | 10.4983 | 109.9994 | 146.0508 | 58.2886 | 18.0503 | 147.3801 | 4.6113 |  | 39.3175 | 85.9929 | 33.3839 |  | 159.9687 | 291.7599 | 36.8641 | 53.7289 | 16.1608 | 281 | 62.2143 | 109.7365 | 184.3472 | 0.10811
14536 | 1070.3585 | 7.3129 | 107.1247 | 139.1603 | 64.4307 | 13.3013 | 112.7892 | 3.8499 |  | 36.5291 | 80.2698 | 18.4757 |  | 150.8839 | 251.1486 | 29.6752 | 51.2357 | 14.5991 | 274 | 54.9757 | 105.8231 | 157.6719 | 0.059593
14537 | 983.5656 | 6.9305 | 97.2357 | 128.6106 | 57.2886 | 11.4005 | 75.6815 | 2.4365 |  | 27.6128 | 65.7968 | 9.1928 |  | 122.3931 | 207.9988 | 16.3391 | 45.34 | 14.0102 | 248 | 49.4842 | 89.3554 | 127.5289 | 0.040681
14538 | 965.0602 | 6.2351 | 82.1572 | 117.8332 | 49.7337 | 7.6011 | 70.8897 | 1.8248 |  | 16.6515 | 57.8949 | 5.9922 |  | 87.624 | 194.8331 | 11.2847 | 34.2377 | 11.6636 | 240 | 54.0485 | 76.8275 | 117.8874 | 0.025473
14539 | 950.9902 | 5.5324 | 60.5717 | 112.355 | 42.1602 | 6.6503 | 77.0586 | 1.3948 |  | 13.012 | 57.0261 | 4.8835 |  | 68.7149 | 176.8813 | 12.8307 | 27.9841 | 6.4347 | 216 | 50.3609 | 68.3877 | 97.0429 | 0.0022634
14540 | 926.9269 | 6.6627 | 34.7766 | 107.5911 | 37.8687 | 6.65 | 70.4976 | 1.4384 |  | 13.6074 | 55.4526 | 6.464 |  | 64.6266 | 154.3108 | 13.7109 | 27.1131 | 4.245 | 199 | 51.0689 | 62.3677 | 97.521 | 0
14541 | 920.5235 | 7.7807 | 26.1969 | 104.9285 | 34.5595 | 9.4992 | 57.5023 | 2.1991 |  | 13.843 | 52.1883 | 7.5878 |  | 62.0643 | 136.8172 | 12.2963 | 27.6781 | 4.5226 | 194 | 41.2019 | 65.1462 | 96.2286 | 0
14542 | 910.9983 | 7.7604 | 26.1189 | 104.4761 | 32.2897 | 10.4497 | 51.1234 | 1.9945 |  | 13.3594 | 45.6079 | 7.6366 |  | 61.7269 | 130.664 | 10.5089 | 27.1761 | 4.8324 | 163 | 34.6973 | 65.0295 | 95.0333 | 0
14543 | 337.8084 | 0 | 9.0355 | 35.4247 | 19.9559 | 0.002903 | 18.9826 | 0.6398 |  | 5.0641 | 17.4916 | 2.9364 |  | 21.8635 | 52.2408 | 3.4566 | 9.2095 | 1.9686 | 153 | 3.6156 | 9.8982 | 9.5455 | 0
14544 | 857.9309 | 7.1588 | 24.8622 | 102.7417 | 33.345 | 9.5 | 43.1519 | 1.7665 |  | 14.9523 | 40.6342 | 7.1983 |  | 48.2028 | 121.6688 | 9.5613 | 26.72 | 4.9514 | 151 | 32.532 | 86.6481 | 90.9394 | 0
14545 | 850.1384 | 3.9558 | 27.56 | 102.5818 | 33.0772 | 8.5503 | 48.6326 | 1.7193 |  | 15.6922 | 40.0151 | 6.9618 |  | 45.3288 | 118.8457 | 9.3642 | 26.6802 | 4.7043 | 139 | 30.0979 | 87.2797 | 93.5792 | 0
14546 | 853.8569 | 2.2323 | 39.3102 | 102.324 | 36.3203 | 5.7008 | 53.5221 | 1.6314 |  | 15.4228 | 39.7818 | 8.8952 |  | 44.6788 | 119.3065 | 9.4433 | 26.6258 | 4.4216 | 139 | 33.5331 | 80.0501 | 92.8836 | 0
14547 | 858.0925 | 2.2333 | 44.5755 | 102.3271 | 37.8691 | 5.7 | 52.5015 | 1.642 |  | 15.2913 | 39.6468 | 14.0842 |  | 44.3128 | 119.9958 | 9.483 | 26.5338 | 3.6853 | 142 | 28.5613 | 85.3351 | 91.7344 | 0
14548 | 856.5471 | 2.9598 | 44.8354 | 103.0692 | 34.6684 | 8.5492 | 52.1136 | 1.6187 |  | 16.051 | 39.4992 | 14.2267 |  | 44.2435 | 114.5033 | 9.0164 | 26.4919 | 3.1416 | 140 | 31.2157 | 87.523 | 95.5046 | 0
14549 | 874.4286 | 3.9747 | 43.5743 | 102.0559 | 40.6087 | 7.6003 | 50.0902 | 2.3623 |  | 18.8422 | 42.8934 | 10.0323 |  | 47.8204 | 115.0792 | 9.7129 | 26.4174 | 3.0378 | 141 | 30.4288 | 79.2456 | 104.0425 | 0
14550 | 911.9598 | 5.6714 | 46.9674 | 106.5013 | 40.7326 | 6.6503 | 67.6633 | 1.9749 |  | 21.9334 | 50.5451 | 18.5268 |  | 67.275 | 125.5085 | 12.7248 | 26.4559 | 5.0665 | 225 | 34.0155 | 75.6949 | 120.5914 | 0
14551 | 958.7521 | 12.6387 | 69.6436 | 114.1033 | 31.024 | 14.2479 | 109.2533 | 2.637 |  | 26.7116 | 62.5036 | 30.4066 |  | 110.7807 | 169.5104 | 24.1992 | 29.0422 | 10.1593 | 282 | 56.3421 | 95.6253 | 158.3285 | 0.21894
14552 | 1012.0573 | 16.1961 | 100.0879 | 125.9869 | 35.1557 | 16.1495 | 128.1569 | 3.9051 |  | 33.4683 | 75.2593 | 34.6781 |  | 144.4847 | 231.1869 | 33.7824 | 33.0768 | 13.2162 | 322 | 60.9536 | 106.2345 | 176.4639 | 0.29269
14553 | 1068.8182 | 14.8887 | 108.3525 | 136.2634 | 36.8691 | 16.15 | 138.5369 | 4.206 |  | 39.2907 | 80.3845 | 36.6685 |  | 163.8744 | 274.6704 | 39.0689 | 37.8846 | 14.1001 | 336 | 62.0408 | 109.835 | 191.455 | 0.28926
14554 | 1105.7457 | 11.6765 | 108.5741 | 139.2799 | 36.7245 | 17.0997 | 157.2091 | 4.3632 |  | 42.4566 | 86.0302 | 40.4812 |  | 172.2871 | 304.2387 | 41.912 | 38.8757 | 14.8713 | 376 | 70.4485 | 118.2373 | 200.1599 | 0.28881
14555 | 1121.5553 | 6.8697 | 116.9878 | 139.315 | 41.1332 | 16.1503 | 165.9697 | 4.4296 |  | 39.9299 | 88.2148 | 40.4306 |  | 179.8798 | 322.2587 | 41.1939 | 39.5562 | 15.5878 | 373 | 75.4231 | 124.0437 | 199.6863 | 0.24168
14556 | 1116.532 | 4.8121 | 118.6905 | 144.8015 | 43.5764 | 17.0997 | 160.6263 | 4.8373 |  | 33.5855 | 87.0687 | 40.3537 |  | 176.6387 | 320.3143 | 41.4245 | 38.8394 | 15.6422 | 360 | 67.1881 | 118.2553 | 198.309 | 0.27884
14557 | 1113.7203 | 7.4463 | 115.1789 | 146.1633 | 47.908 | 18.0497 | 178.399 | 4.9341 |  | 34.8788 | 87.8384 | 41.5722 |  | 173.9151 | 312.9293 | 41.9677 | 39.2852 | 15.0575 | 332 | 84.2758 | 121.3511 | 194.471 | 0.30187
14558 | 1097.8711 | 10.6137 | 112.9306 | 146.1088 | 59.4545 | 14.2511 | 185.3707 | 4.4265 |  | 36.3262 | 89.2806 | 39.4914 |  | 171.8505 | 300.6673 | 41.3393 | 41.8848 | 14.8599 | 314 | 83.7957 | 119.0355 | 199.4786 | 0.29359
14559 | 1057.6264 | 10.3046 | 110.2325 | 142.6594 | 66.1033 | 14.25 | 176.3822 | 4.2991 |  | 33.1979 | 89.4627 | 34.5586 |  | 164.6563 | 288.7759 | 37.969 | 49.6482 | 15.4984 | 294 | 73.7432 | 119.0768 | 182.7851 | 0.29913
14560 | 1019.1682 | 8.1917 | 107.1526 | 138.5654 | 68.823 | 10.4511 | 146.6166 | 3.7962 |  | 28.4054 | 81.5054 | 25.7098 |  | 152.8457 | 245.6007 | 30.3949 | 53.0428 | 15.6428 | 270 | 65.9942 | 110.7912 | 171.1185 | 0.23715
14561 | 979.8042 | 6.5299 | 98.9089 | 127.1127 | 63.7902 | 8.5505 | 103.1714 | 2.6783 |  | 21.7175 | 65.4701 | 14.3612 |  | 125.2135 | 205.4789 | 16.8641 | 49.9882 | 15.5712 | 241 | 50.8017 | 90.214 | 134.3555 | 0.23963
14562 | 959.3822 | 6.1756 | 87.6509 | 110.2126 | 57.6242 | 8.55 | 70.1133 | 2.0453 |  | 14.647 | 54.9874 | 8.675 |  | 92.5298 | 188.8539 | 11.5222 | 48.3868 | 13.0843 | 226 | 50.2818 | 76.7513 | 122.8184 | 0.1852
14563 | 929.5084 | 4.994 | 72.1937 | 102.7504 | 55.8295 | 9.4997 | 59.3601 | 1.733 |  | 11.0596 | 51.3514 | 12.1632 |  | 75.6553 | 171.1022 | 10.2538 | 44.9947 | 7.6921 | 208 | 50.5795 | 71.7224 | 103.2866 | 0.016875
14564 | 900.4205 | 6.767 | 43.5603 | 103.7631 | 59.65 | 6.6508 | 59.0919 | 1.4178 |  | 11.8376 | 50.9681 | 16.5894 |  | 72.448 | 155.2413 | 9.0531 | 43.2802 | 5.5457 | 203 | 49.7976 | 68.4775 | 96.4681 | 0
14565 | 888.4943 | 8.7613 | 31.3368 | 102.7442 | 55.2804 | 7.5997 | 53.314 | 1.3438 |  | 12.6667 | 50.7497 | 12.5926 |  | 69.922 | 145.6778 | 9.2889 | 42.6878 | 5.6162 | 195 | 43.2341 | 63.4636 | 94.7306 | 0
14566 | 868.0829 | 7.8767 | 30.717 | 103.5333 | 53.464 | 7.6 | 49.5262 | 1.5209 |  | 12.2808 | 45.4216 | 8.7252 |  | 67.5486 | 143.2795 | 10.8753 | 42.4494 | 5.0058 | 165 | 36.5691 | 59.9638 | 95.4646 | 0
14567 | 319.3141 | 0 | 10.569 | 0 | 29.3655 | 0.002112 | 18.6392 | 0.63464 |  | 4.6945 | 17.486 | 3.237 |  | 0 | 0 | 3.9834 | 0 | 1.8318 | 152 | 3.7466 | 8.9585 | 9.6495 | 0
14568 | 822.2253 | 4.026 | 30.874 | 104.2988 | 54.5204 | 6.6508 | 57.3742 | 1.314 |  | 13.7521 | 40.8192 | 8.1936 |  | 61.6558 | 134.5278 | 12.6045 | 41.9799 | 3.5901 | 139 | 35.6381 | 84.7121 | 96.25 | 0
14569 | 824.5096 | 2.2801 | 30.4965 | 102.4286 | 52.5164 | 7.5997 | 58.1219 | 1.2839 |  | 13.4986 | 40.2599 | 8.048 |  | 59.1625 | 125.3475 | 14.0483 | 42.3632 | 3.1946 | 131 | 29.7025 | 78.9749 | 101.0941 | 0
14570 | 822.8578 | 2.2795 | 36.9518 | 101.6591 | 50.8239 | 8.5497 | 57.0059 | 1.2888 |  | 13.0123 | 39.929 | 10.0903 |  | 59.4728 | 122.7793 | 13.0971 | 42.1546 | 3.0489 | 142 | 30.9548 | 85.1266 | 98.9891 | 0
14571 | 818.4489 | 2.177 | 45.9585 | 101.5406 | 40.8948 | 8.55 | 46.3684 | 2.2687 |  | 13.1142 | 39.7978 | 15.4949 |  | 60.3064 | 118.7314 | 13.5491 | 42.0127 | 3.0459 | 137 | 28.3568 | 85.6317 | 100.8483 | 0
14572 | 828.4882 | 2.6654 | 49.9894 | 101.4177 | 33.9718 | 7.6003 | 48.051 | 2.096 |  | 14.0291 | 39.9236 | 15.5018 |  | 60.4263 | 115.4068 | 13.3553 | 42.0143 | 3.0444 | 127 | 27.9236 | 79.3515 | 100.3438 | 0
14573 | 847.9288 | 3.4538 | 46.7547 | 100.3815 | 32.795 | 9.4995 | 55.77 | 1.5288 |  | 16.4178 | 42.4375 | 13.2791 |  | 61.3071 | 118.08 | 10.4615 | 41.7317 | 2.9958 | 126 | 31.2022 | 84.3586 | 110.816 | 0
14574 | 899.9521 | 3.9826 | 52.0504 | 106.4536 | 30.3189 | 10.4497 | 68.3018 | 1.4822 |  | 18.9688 | 46.0345 | 15.1815 |  | 74.607 | 130.2693 | 11.5068 | 41.5143 | 5.0225 | 205 | 31.3671 | 77.2116 | 130.336 | 0
14575 | 958.7537 | 6.7959 | 73.2812 | 112.6011 | 24.4173 | 15.1987 | 92.3134 | 2.9086 |  | 24.6572 | 57.1523 | 27.7104 |  | 106.0389 | 176.8836 | 24.145 | 43.6822 | 10.1719 | 235 | 50.6878 | 83.7315 | 161.7684 | 0.17488
14576 | 1030.6281 | 18.9718 | 98.8699 | 124.0914 | 25.4973 | 14.2503 | 122.1745 | 4.6327 |  | 34.278 | 69.9191 | 37.1742 |  | 130.5682 | 237.9274 | 33.507 | 49.1853 | 14.0621 | 291 | 54.9305 | 99.5374 | 185.1002 | 0.24805
14577 | 1099.7878 | 22.9219 | 109.7173 | 128.9882 | 26.5258 | 16.1495 | 136.996 | 4.6939 |  | 42.7251 | 79.2894 | 39.2901 |  | 149.8592 | 274.1762 | 37.8294 | 53.1082 | 15.1371 | 338 | 56.9321 | 114.7278 | 197.3938 | 0.2697
14578 | 1123.2422 | 19.8874 | 111.1713 | 127.7649 | 29.1394 | 16.15 | 137.6786 | 4.7942 |  | 47.223 | 85.8711 | 39.4883 |  | 162.0718 | 294.2058 | 38.7838 | 54.4686 | 15.1481 | 352 | 61.4877 | 122.0946 | 196.4201 | 0.14328
14579 | 1139.663 | 14.7016 | 113.733 | 131.7044 | 34.809 | 14.2505 | 138.0676 | 4.9431 |  | 46.5153 | 87.7129 | 38.4879 |  | 173.5855 | 319.8525 | 38.6881 | 53.6804 | 17.1492 | 321 | 65.0624 | 130.5748 | 200.8186 | 0.17279
14580 | 1137.7284 | 9.787 | 114.6023 | 131.9676 | 36.819 | 16.1495 | 142.0756 | 4.8333 |  | 41.2692 | 87.3511 | 39.6613 |  | 175.0559 | 319.5889 | 39.3224 | 53.3905 | 18.0032 | 322 | 59.0881 | 122.6604 | 198.3723 | 0.24495
14581 | 1150.4963 | 6.4062 | 113.2286 | 131.1165 | 32.4325 | 20.8813 | 146.5584 | 5.1629 |  | 38.4558 | 88.9945 | 41.9912 |  | 174.046 | 309.0128 | 39.104 | 54.2966 | 17.5933 | 299 | 85.3692 | 124.5471 | 194.8285 | 0.27186
14582 | 1173.0302 | 4.4574 | 112.3912 | 132.9538 | 33.8096 | 19.9677 | 147.6635 | 4.9968 |  | 40.0127 | 92.4892 | 41.186 |  | 175.2316 | 316.5492 | 38.4481 | 55.4493 | 17.1767 | 279 | 85.5802 | 0 | 196.8398 | 0.27247
14583 | 1150.312 | 4.5236 | 111.7406 | 133.9491 | 32.826 | 19.0003 | 141.9304 | 4.1594 |  | 36.4031 | 93.8957 | 33.495 |  | 169.8467 | 311.5455 | 35.7138 | 55.496 | 16.9172 | 288 | 86.5307 | 125.4406 | 186.0669 | 0.2549
14584 | 1104.1437 | 4.3557 | 108.0615 | 128.0927 | 37.242 | 12.3518 | 124.5239 | 3.8962 |  | 28.6486 | 84.5735 | 24.1612 |  | 156.7655 | 272.6235 | 29.4091 | 54.3879 | 16.6967 | 261 | 77.6096 | 114.2018 | 174.4117 | 0.24181
14585 | 1076.2274 | 5.4795 | 102.4102 | 118.8636 | 35.37 | 9.5008 | 94.7564 | 3.6196 |  | 23.2478 | 69.9935 | 19.5277 |  | 124.9859 | 232.9342 | 18.169 | 51.8414 | 16.5999 | 252 | 65.6365 | 90.2863 | 143.1434 | 0.22962
14586 | 1034.4667 | 6.4773 | 87.7901 | 103.4452 | 31.5816 | 9.5 | 59.0441 | 2.8365 |  | 18.996 | 60.6085 | 15.9708 |  | 85.1611 | 206.899 | 12.2529 | 47.4193 | 13.399 | 241 | 60.1173 | 78.1376 | 127.7752 | 0.17043
14587 | 982.1125 | 5.1668 | 70.9084 | 94.8075 | 35.4035 | 10.4497 | 50.1705 | 3.038 |  | 16.777 | 55.4458 | 10.2138 |  | 67.7365 | 183.2051 | 10.878 | 43.5966 | 7.4835 | 218 | 56.868 | 72.7729 | 110.0515 | 0.0057541
14588 | 952.6285 | 4.6079 | 55.123 | 94.1997 | 38.4876 | 10.45 | 52.1821 | 2.5412 |  | 18.8954 | 53.9631 | 8.1648 |  | 61.016 | 166.4793 | 9.6036 | 41.7681 | 4.8094 | 201 | 56.7914 | 69.8233 | 107.7678 | 0
14589 | 930.5684 | 4.8808 | 43.1477 | 94.3655 | 36.1938 | 10.45 | 49.7366 | 1.6656 |  | 17.2987 | 52.7807 | 10.2698 |  | 55.3594 | 148.5079 | 9.8603 | 41.5906 | 4.8105 | 191 | 44.7055 | 66.8391 | 107.6501 | 0
14590 | 906.8688 | 3.9597 | 39.4634 | 94.3354 | 32.8441 | 11.3997 | 43.4251 | 2.1659 |  | 13.9233 | 48.1805 | 13.1604 |  | 54.9721 | 141.939 | 9.5215 | 41.8278 | 4.5843 | 169 | 43.7249 | 64.0892 | 106.6644 | 0
14591 | 371.7063 | 1.4708 | 15.3403 | 35.8281 | 23.2228 | 0.003167 | 16.3724 | 1.1399 |  | 5.7289 | 20.7376 | 6.2056 |  | 21.8817 | 63.6387 | 3.4985 | 16.1409 | 1.8971 | 153 | 6.5405 | 12.2547 | 16.7995 | 0
14592 | 884.69 | 2.6052 | 38.4833 | 94.752 | 30.928 | 10.4495 | 47.4317 | 2.2317 |  | 14.3576 | 43.7897 | 11.3376 |  | 46.103 | 128.5202 | 10.33 | 40.8892 | 4.2741 | 151 | 39.9225 | 77.4575 | 101.8323 | 0
14593 | 880.1522 | 3.2788 | 38.4974 | 94.0427 | 30.1885 | 10.45 | 49.6928 | 2.2628 |  | 14.9436 | 43.4604 | 10.9546 |  | 44.8224 | 126.4572 | 9.6452 | 40.9741 | 3.9431 | 138 | 43.0763 | 75.2837 | 98.8591 | 0
14594 | 871.8476 | 3.1993 | 38.4006 | 93.9118 | 29.7388 | 9.5003 | 43.0548 | 2.3564 |  | 15.4982 | 43.2015 | 13.0559 |  | 48.1044 | 128.3585 | 9.6523 | 41.0772 | 3.6167 | 142 | 37.2236 | 72.4435 | 99.8608 | 0
14595 | 864.1957 | 2.8041 | 38.1681 | 94.0445 | 28.5883 | 9.5 | 40.7152 | 2.05 |  | 15.2992 | 42.6865 | 18.068 |  | 47.5004 | 127.8727 | 9.3085 | 40.954 | 3.584 | 142 | 38.5149 | 77.2162 | 100.2706 | 0
14596 | 869.5092 | 3.2373 | 38.0373 | 93.9895 | 24.6779 | 11.3995 | 45.8903 | 2.2164 |  | 16.0653 | 42.2002 | 20.2914 |  | 45.3229 | 122.1558 | 10.1982 | 40.8526 | 3.0497 | 125 | 38.4486 | 77.3232 | 101.0023 | 0
14597 | 883.3937 | 4.0727 | 38.7079 | 93.786 | 22.6743 | 11.4 | 50.9198 | 2.065 |  | 19.567 | 44.7371 | 22.4898 |  | 50.7717 | 120.9018 | 9.6294 | 40.9327 | 2.4157 | 130 | 37.1145 | 71.8982 | 111.5943 | 0
14598 | 925.9083 | 4.7585 | 46.2039 | 97.9001 | 19.7259 | 10.4503 | 60.5209 | 2.5541 |  | 22.3042 | 49.4959 | 28.5675 |  | 71.53 | 126.9004 | 13.4452 | 40.6712 | 4.9209 | 197 | 45.9212 | 77.1791 | 134.3349 | 0
14599 | 983.9683 | 6.0536 | 73.2901 | 106.3063 | 12.5302 | 14.2489 | 76.1719 | 4.2731 |  | 25.2878 | 61.5389 | 33.8769 |  | 111.8344 | 167.8212 | 26.7837 | 42.6254 | 10.9721 | 281 | 59.8422 | 91.2596 | 170.5872 | 0.033997
14600 | 1060.1494 | 9.5739 | 100.6009 | 116.9036 | 9.1361 | 17.0992 | 95.9331 | 5.6505 |  | 28.132 | 77.0387 | 36.5112 |  | 146.4356 | 232.54 | 36.4955 | 47.6129 | 14.8584 | 287 | 74.0027 | 106.1742 | 191.7914 | 0.11476
14601 | 1139.2533 | 11.5965 | 111.2287 | 130.8751 | 8.4355 | 18.0497 | 110.9673 | 5.5466 |  | 34.8635 | 85.5501 | 39.6748 |  | 162.2309 | 292.8687 | 41.4957 | 51.957 | 17.5137 | 325 | 79.0475 | 114.3754 | 199.5848 | 0.25339
14602 | 1174.5788 | 9.3342 | 112.569 | 133.037 | 11.5671 | 16.1505 | 118.8361 | 4.8866 |  | 43.4534 | 88.6927 | 41.9608 |  | 169.1648 | 327.4777 | 43.5392 | 54.2609 | 17.7427 | 355 | 83.4718 | 128.8545 | 204.0543 | 0.2692
14603 | 1175.4341 | 10.5513 | 115.474 | 134.9158 | 16.0005 | 16.15 | 123.6333 | 5.5183 |  | 45.5312 | 90.7578 | 38.8969 |  | 176.2129 | 328.1316 | 44.1587 | 54.7683 | 16.4513 | 334 | 78.0951 | 141.3176 | 212.442 | 0.24336
14604 | 1186.2275 | 12.1362 | 116.1392 | 139.0021 | 20.0072 | 17.0997 | 125.0862 | 5.5385 |  | 41.9856 | 94.6051 | 36.778 |  | 177.0647 | 321.8671 | 46.5077 | 54.9736 | 16.3927 | 348 | 78.0375 | 134.8063 | 204.7098 | 0.2766
14605 | 1211.9407 | 11.2095 | 116.2824 | 139.9148 | 18.4388 | 20.8989 | 127.632 | 5.8366 |  | 42.449 | 96.7471 | 35.251 |  | 178.119 | 317.8792 | 45.373 | 54.6134 | 17.9269 | 309 | 86.3097 | 126.2988 | 210.1907 | 0.19601
14606 | 1205.219 | 8.8186 | 115.7583 | 137.7485 | 19.2999 | 20.9 | 126.9892 | 5.4553 |  | 41.3086 | 98.1056 | 35.87 |  | 182.4265 | 311.2736 | 43.1469 | 54.5879 | 18.5188 | 295 | 87.4339 | 125.6293 | 200.0479 | 0.29765
14607 | 1177.6948 | 6.5856 | 112.5851 | 135.7013 | 23.5731 | 17.1011 | 118.9219 | 4.6282 |  | 35.7752 | 96.9334 | 36.1343 |  | 179.5705 | 299.1453 | 40.7755 | 56.0649 | 17.4344 | 288 | 86.3432 | 119.7151 | 198.2745 | 0.28977
14608 | 1138.1151 | 7.2475 | 107.738 | 128.4602 | 31.3035 | 9.5021 | 102.7638 | 4.6372 |  | 31.1323 | 84.6879 | 29.8754 |  | 166.6971 | 276.3603 | 31.2648 | 54.2849 | 16.6762 | 280 | 78.6446 | 109.9888 | 175.3454 | 0.24031
14609 | 1098.1328 | 6.5783 | 100.0656 | 118.1743 | 29.6082 | 11.3995 | 84.1031 | 3.4746 |  | 28.1504 | 66.5982 | 24.9311 |  | 131.9939 | 246.9607 | 18.3572 | 51.6853 | 16.4811 | 245 | 62.8423 | 82.1623 | 137.1662 | 0.22472
14610 | 1068.1358 | 4.3478 | 89.1977 | 104.3168 | 31.84 | 9.5005 | 68.35 | 2.7586 |  | 25.4263 | 55.8423 | 19.245 |  | 87.5853 | 220.7278 | 12.2491 | 48.452 | 13.5812 | 224 | 54.1612 | 70.2989 | 125.1989 | 0.13904
14611 | 1043.4092 | 4.0076 | 73.0651 | 96.914 | 31.3529 | 9.5 | 58.8498 | 2.1711 |  | 26.8786 | 53.8017 | 14.6879 |  | 68.495 | 196.35 | 11.9839 | 45.2711 | 8.38 | 223 | 52.766 | 67.0912 | 108.1063 | 0.0069242
14612 | 998.1148 | 4.1838 | 55.2696 | 95.5615 | 28.4146 | 9.5 | 53.6097 | 2.2543 |  | 29.9301 | 53.6493 | 12.2471 |  | 60.2906 | 173.7931 | 11.3012 | 43.4137 | 5.6087 | 200 | 49.8236 | 58.6548 | 102.7652 | 0
14613 | 970.6042 | 4.0578 | 44.3373 | 96.0873 | 21.5243 | 10.4497 | 42.546 | 2.2477 |  | 26.9692 | 50.6357 | 10.6384 |  | 54.7764 | 160.3629 | 9.8978 | 42.8843 | 5.4274 | 195 | 49.2554 | 62.4923 | 102.332 | 0
14614 | 940.5773 | 3.5382 | 39.64 | 96.8057 | 15.3224 | 12.3495 | 45.3772 | 2.3651 |  | 22.2425 | 44.36 | 9.9257 |  | 53.5137 | 155.1092 | 9.595 | 42.9578 | 5.3445 | 189 | 47.492 | 65.115 | 100.8317 | 0
14615 | 386.15 | 0 | 15.1962 | 0 | 14.5638 | 0.003431 | 22.232 | 1.2148 |  | 9.0437 | 19.0515 | 4.1384 |  | 0 | 0 | 3.8274 | 0 | 2.2708 | 178 | 7.1043 | 12.7793 | 15.9406 | 0
14616 | 902.7098 | 2.2078 | 38.5299 | 94.838 | 15.1894 | 11.4003 | 54.4096 | 2.1421 |  | 22.6144 | 40.2384 | 8.4656 |  | 50.7438 | 151.1151 | 10.9926 | 42.4845 | 4.1999 | 169 | 48.1697 | 70.4834 | 99.1279 | 0
14617 | 906.4044 | 2.1176 | 41.8022 | 95.6614 | 14.2719 | 9.5005 | 53.9614 | 2.2713 |  | 20.6884 | 39.5688 | 7.2629 |  | 49.9236 | 151.373 | 10.2216 | 42.3881 | 3.8974 | 152 | 45.2302 | 73.2487 | 99.819 | 0
14618 | 886.7895 | 2.2895 | 52.5771 | 95.536 | 18.743 | 7.6005 | 58.3462 | 2.3072 |  | 18.5302 | 39.1463 | 6.5235 |  | 48.4398 | 143.9967 | 9.9398 | 42.1666 | 3.7817 | 150 | 42.3488 | 70.4387 | 102.1481 | 0
14619 | 869.6586 | 2.505 | 57.7385 | 94.5458 | 16.9458 | 8.5497 | 62.3024 | 2.3875 |  | 17.2334 | 39.022 | 6.5087 |  | 46.9589 | 137.7743 | 9.4587 | 42.1829 | 3.2991 | 166 | 41.3838 | 68.0791 | 107.8852 | 0
14620 | 857.6873 | 2.3395 | 52.6389 | 95.52 | 15.0031 | 10.4495 | 59.1664 | 2.0675 |  | 17.0797 | 42.0075 | 6.5513 |  | 45.3045 | 132.6605 | 9.7923 | 42.2006 | 2.7879 | 129 | 43.2284 | 71.7822 | 114.1828 | 0
14621 | 860.7439 | 2.3094 | 43.2745 | 94.3747 | 16.7518 | 9.5003 | 55.7424 | 2.1696 |  | 18.6914 | 41.8741 | 8.0426 |  | 50.6698 | 132.1645 | 10.3056 | 41.8306 | 2.6796 | 132 | 41.6085 | 72.7402 | 122.4004 | 0
14622 | 900.7475 | 4.2731 | 48.1201 | 98.6181 | 16.5991 | 10.4497 | 74.4354 | 2.5717 |  | 20.1732 | 42.9731 | 14.4714 |  | 71.7755 | 136.2248 | 13.1689 | 41.7649 | 4.5767 | 215 | 43.4234 | 66.6027 | 140.3633 | 0
14623 | 951.635 | 10.2314 | 73.1999 | 103.9758 | 7.5623 | 18.0329 | 100.4722 | 3.3227 |  | 24.0274 | 56.8654 | 23.286 |  | 109.3059 | 178.9022 | 26.8019 | 44.4086 | 9.4164 | 285 | 51.8297 | 86.2199 | 166.3063 | 0.041724
14624 | 1007.6755 | 18.2206 | 98.0273 | 112.211 | 10.2637 | 16.1655 | 115.8234 | 4.0633 |  | 29.8825 | 71.2071 | 29.6338 |  | 141.6663 | 232.6239 | 36.1006 | 50.3547 | 12.6502 | 300 | 53.966 | 98.4896 | 184.2867 | 0.085178
14625 | 1131.7035 | 21.6263 | 106.6904 | 124.2226 | 10.6627 | 19.9489 | 130.0384 | 4.3353 |  | 35.7757 | 78.7529 | 35.2201 |  | 158.8297 | 270.6738 | 37.9077 | 54.0724 | 15.9728 | 339 | 52.9453 | 113.3767 | 192.0894 | 0.10401
14626 | 1168.4095 | 18.5447 | 107.1609 | 127.0811 | 14.4378 | 19.95 | 138.9106 | 4.6124 |  | 36.9133 | 82.5843 | 39.7133 |  | 168.3252 | 288.5745 | 38.934 | 54.8472 | 15.942 | 332 | 54.6898 | 117.3769 | 198.2069 | 0.12094
14627 | 1184.3144 | 12.2715 | 113.9434 | 127.3918 | 18.4594 | 18.0505 | 149.3606 | 4.6818 |  | 41.135 | 85.6796 | 38.716 |  | 172.4662 | 303.1725 | 40.0226 | 56.0632 | 14.7914 | 345 | 59.034 | 121.6553 | 202.4595 | 0.13567
14628 | 1176.1225 | 11.8982 | 115.7109 | 131.756 | 16.9623 | 20.8992 | 150.7746 | 4.8617 |  | 38.5736 | 86.2722 | 36.3563 |  | 171.4438 | 296.7462 | 40.4036 | 55.8756 | 15.0228 | 356 | 56.0436 | 119.0481 | 192.2162 | 0.096441
14629 | 1158.6269 | 12.503 | 112.0844 | 135.9954 | 18.3979 | 20.9 | 151.1039 | 4.8883 |  | 32.7909 | 87.0304 | 36.2179 |  | 171.659 | 290.5289 | 39.5654 | 54.6295 | 14.6456 | 289 | 56.0445 | 0 | 185.9929 | 0.13874
14630 | 1158.3261 | 11.5895 | 109.7565 | 136.3912 | 22.0608 | 19.0005 | 149.0664 | 4.3 |  | 31.1962 | 87.1397 | 35.634 |  | 170.9117 | 286.0085 | 38.5754 | 54.105 | 14.0356 | 274 | 54.041 | 118.9696 | 184.9411 | 0.088125
14631 | 1110.9383 | 11.2218 | 107.0239 | 133.3978 | 34.0532 | 19.9497 | 143.591 | 4.3365 |  | 28.4726 | 86.6355 | 33.6989 |  | 163.6438 | 270.663 | 36.353 | 53.8393 | 13.9481 | 274 | 53.9189 | 110.2789 | 174.8013 | 0.10668
14632 | 1063.3108 | 12.675 | 105.3596 | 127.4573 | 50.5386 | 13.3018 | 123.3209 | 3.6682 |  | 25.5361 | 81.2884 | 23.8911 |  | 149.0647 | 243.1233 | 26.5386 | 52.0169 | 14.1504 | 268 | 50.3697 | 105.6811 | 156.0764 | 0.052758
14633 | 999.3181 | 12.132 | 90.7122 | 115.5687 | 47.9944 | 12.3503 | 92.4387 | 2.3559 |  | 20.8913 | 67.5526 | 13.7295 |  | 116.6798 | 203.2497 | 15.3414 | 49.2832 | 14.1884 | 248 | 47.176 | 82.6213 | 129.7988 | 0.03342
14634 | 959.1687 | 9.4904 | 48.7592 | 101.8217 | 41.7822 | 12.35 | 78.3788 | 2.3222 |  | 14.9308 | 56.3991 | 11.6623 |  | 74.9916 | 177.5847 | 11.4185 | 47.0237 | 11.9139 | 222 | 47.1952 | 72.0914 | 112.2374 | 0.012843
14635 | 937.4565 | 9.3178 | 26.4729 | 95.2453 | 35.5166 | 8.5511 | 73.4866 | 2.29 |  | 12.5056 | 49.0804 | 8.7826 |  | 53.9577 | 168.8626 | 11.1898 | 45.5014 | 7.1165 | 201 | 46.8211 | 59.2079 | 98.7977 | 0
14636 | 918.4239 | 10.5661 | 23.8252 | 94.6872 | 33.0313 | 8.55 | 70.2762 | 2.0593 |  | 14.062 | 44.0038 | 6.77 |  | 53.2135 | 161.4963 | 10.9727 | 44.0919 | 5.2334 | 186 | 45.2825 | 61.3328 | 96.0439 | 0
14637 | 905.292 | 11.0782 | 23.2323 | 95.1646 | 27.7678 | 10.4495 | 68.1617 | 2.2372 |  | 14.7654 | 42.0173 | 7.4872 |  | 52.9859 | 149.7809 | 9.345 | 43.3795 | 5.9792 | 185 | 42.2958 | 60.2978 | 94.0836 | 0
14638 | 895.5664 | 12.2157 | 23.6791 | 95.5402 | 26.4623 | 12.3495 | 62.8922 | 2.5862 |  | 14.347 | 40.9616 | 8.1911 |  | 50.0828 | 134.2845 | 9.0981 | 42.3877 | 6.2508 | 179 | 41.1334 | 57.2569 | 93.2675 | 0
14639 | 328.9017 | 0 | 8.4435 | 0 | 22.7722 | 0 | 22.919 | 1.0767 |  | 5.5766 | 16.9679 | 3.2654 |  | 0 | 0 | 3.2802 | 0 | 2.4651 | 161 | 4.2745 | 8.6588 | -6.916 | 0
14640 | 888.834 | 11.4989 | 22.8871 | 94.8627 | 32.137 | 11.4 | 57.9736 | 2.4986 |  | 13.1482 | 40.4895 | 7.8026 |  | 51.4395 | 137.9057 | 8.5197 | 41.8789 | 4.3503 | 143 | 40.5196 | 84.2898 | 92.8178 | 0
14641 | 887.8632 | 9.5162 | 22.8241 | 94.9392 | 30.132 | 8.5508 | 63.2161 | 2.9464 |  | 11.5896 | 40.1238 | 7.695 |  | 45.8488 | 138.16 | 8.6093 | 41.7234 | 3.3132 | 142 | 37.9547 | 77.9806 | 90.5243 | 0
14642 | 873.6506 | 4.9661 | 22.5213 | 95.4196 | 21.3293 | 10.4495 | 65.8843 | 2.074 |  | 11.2862 | 40.0367 | 7.5282 |  | 43.8888 | 130.0623 | 9.116 | 41.8772 | 3.2054 | 142 | 32.8033 | 84.0752 | 93.0378 | 0
14643 | 872.1231 | 2.788 | 34.6412 | 94.9635 | 20.3012 | 11.3997 | 64.3532 | 2.3185 |  | 11.2541 | 40.0015 | 7.4674 |  | 43.8062 | 126.0625 | 9.4002 | 41.8449 | 3.3705 | 127 | 37.0353 | 84.6868 | 95.1497 | 0
14644 | 870.8267 | 3.0661 | 41.2374 | 94.7877 | 19.7636 | 10.4503 | 63.6961 | 3.0008 |  | 11.2525 | 39.9225 | 7.4107 |  | 43.797 | 122.3533 | 9.2084 | 42.052 | 2.9853 | 135 | 33.1746 | 77.2436 | 92.7827 | 0
14645 | 874.729 | 5.4779 | 31.0952 | 94.323 | 14.0262 | 12.3495 | 59.0251 | 2.2384 |  | 10.8924 | 40.1431 | 7.2171 |  | 43.5235 | 124.3296 | 8.5326 | 41.6286 | 2.6849 | 134 | 34.1531 | 79.3738 | 92.3858 | 0
14646 | 888.9983 | 8.5656 | 37.0459 | 92.0822 | 16.0892 | 11.4003 | 62.0133 | 2.2323 |  | 9.3229 | 43.21 | 5.612 |  | 43.0807 | 121.8108 | 8.5718 | 41.0698 | 2.5339 | 127 | 33.3364 | 64.2977 | 86.5146 | 0
14647 | 904.0145 | 6.216 | 45.315 | 91.4432 | 18.1301 | 8.5508 | 64.848 | 2.5746 |  | 8.4395 | 44.6526 | 4.6674 |  | 42.8551 | 117.0337 | 8.9617 | 40.8165 | 2.4731 | 125 | 32.4027 | 62.586 | 85.9381 | 0.040798
14648 | 912.9175 | 2.8663 | 58.1263 | 91.5856 | 15.1501 | 9.4997 | 62.9057 | 2.7515 |  | 8.412 | 40.8053 | 4.9483 |  | 45.068 | 115.3078 | 8.3251 | 41.3702 | 2.4991 | 144 | 36.778 | 71.0407 | 93.8015 | 0.057391
14649 | 941.0093 | 2.631 | 65.9513 | 91.778 | 13.3287 | 10.4497 | 72.3691 | 2.508 |  | 8.729 | 41.682 | 5.2938 |  | 49.8911 | 120.2161 | 8.1763 | 41.9052 | 4.9578 | 159 | 28.4971 | 74.3563 | 93.7828 | 0.10533
14650 | 962.0484 | 3.5987 | 65.1772 | 91.9023 | 14.998 | 10.45 | 80.692 | 1.6625 |  | 9.0634 | 47.0975 | 11.118 |  | 50.3876 | 126.4673 | 8.0974 | 41.9613 | 9.597 | 177 | 23.3258 | 65.9987 | 94.9059 | 0.12211
14651 | 959.9257 | 5.4381 | 63.8555 | 91.3507 | 23.0805 | 8.5505 | 81.4141 | 1.2091 |  | 10.5826 | 49.4941 | 12.9061 |  | 51.6885 | 131.0819 | 9.4966 | 41.5047 | 11.4778 | 194 | -0.28284 | 74.415 | 95.8024 | 0.13661
14652 | 951.6644 | 8.9628 | 62.9266 | 90.7494 | 29.9587 | 7.6003 | 77.2225 | 1.2698 |  | 12.1884 | 51.0512 | 11.4228 |  | 56.2516 | 127.4281 | 8.4177 | 40.8521 | 11.4774 | 198 | 21.5167 | 75.7193 | 93.2456 | 0.097554
14653 | 942.3746 | 7.5975 | 59.4465 | 91.4583 | 29.889 | 9.4995 | 67.0979 | 1.1607 |  | 13.8932 | 53.4636 | 15.2663 |  | 57.276 | 137.8186 | 8.1453 | 40.9923 | 11.5662 | 198 | 40.3089 | 73.5975 | 92.1271 | 0.095168
14654 | 936.7187 | 3.4524 | 35.2261 | 91.5337 | 29.6157 | 11.3995 | 76.6744 | 1.0446 |  | 16.7404 | 54.6499 | 12.0519 |  | 55.1973 | 158.3849 | 7.673 | 41.2836 | 9.4979 | 210 | 39.6115 | 73.3067 | 95.4083 | 0.090487
14655 | 936.9005 | 2.3963 | 22.7227 | 92.1494 | 34.2951 | 8.5508 | 88.4077 | 1.0208 |  | 16.1857 | 54.6361 | 11.7028 |  | 58.3965 | 172.8513 | 8.2247 | 41.2916 | 5.485 | 219 | 32.4968 | 78.6185 | 90.5417 | 0.071947
14656 | 938.6118 | 4.4102 | 22.1971 | 92.1533 | 36.7535 | 8.55 | 73.2068 | 0.97057 |  | 15.6263 | 53.1316 | 12.5706 |  | 57.3935 | 156.5143 | 8.9314 | 41.784 | 3.6016 | 226 | 24.3815 | 74.6151 | 89.884 | 0.055341
14657 | 929.6788 | 5.8446 | 21.7737 | 91.4585 | 40.6315 | 7.6003 | 61.2077 | 1.1852 |  | 14.4312 | 49.7372 | 8.0839 |  | 58.297 | 146.2036 | 8.0768 | 42.267 | 6.593 | 233 | 26.4625 | 59.9915 | 87.3828 | 0.063147
14658 | 915.2178 | 5.8041 | 22.2691 | 92.2772 | 40.6887 | 8.5497 | 59.0483 | 1.8068 |  | 11.8147 | 43.9929 | 5.307 |  | 59.1652 | 141.9319 | 8.5272 | 42.4264 | 10.8836 | 219 | 32.3137 | 63.3729 | 87.6994 | 0.011301
14659 | 912.5369 | 4.7969 | 22.3599 | 94.76 | 40.1674 | 9.4997 | 63.2941 | 1.6413 |  | 10.5982 | 41.3376 | 5.3655 |  | 54.9993 | 134.4557 | 7.8654 | 42.0142 | 12.5243 | 209 | 34.8803 | 63.7441 | 92.2349 | 0
14660 | 903.5373 | 4.3941 | 22.5789 | 95.7576 | 38.3056 | 8.5503 | 57.4736 | 1.4869 |  | 11.9026 | 42.5625 | 6.5111 |  | 51.1635 | 134.1634 | 8.2177 | 41.9621 | 12.9948 | 205 | 37.4039 | 54.467 | 94.05 | 0
14661 | 897.5576 | 4.8159 | 22.7436 | 95.3601 | 36.2807 | 9.9746 | 55.985 | 2.2604 |  | 13.0712 | 43.3926 | 7.5724 |  | 48.4287 | 143.1399 | 9.2552 | 42.2131 | 13.5642 | 200 | 34.1839 | 59.0285 | 92.0931 | 0
14662 | 896.0564 | 4.0897 | 22.4696 | 98.2304 | 37.869 | 9.9778 | 61.9415 | 2.1014 |  | 14.7623 | 42.7413 | 7.9757 |  | 47.6659 | 148.3565 | 8.353 | 42.207 | 13.4986 | 189 | 43.449 | 61.1309 | 93.6679 | 0
14663 | 337.4307 | 0 | 7.8787 | 0 | 23.3958 | 0 | 24.423 | 0.67062 |  | 6.1881 | 17.6835 | 3.1326 |  | 0 | 0 | 2.6422 | 0 | 5.2931 | 181 | 4.7968 | 9.352 | 10.7577 | 0
14664 | 893.9032 | 2.4451 | 22.9196 | 95.4668 | 35.5527 | 9.5005 | 59.6137 | 2.1388 |  | 13.4855 | 41.4743 | 8.1888 |  | 51.6477 | 134.9362 | 9.6487 | 42.2368 | 13.0335 | 177 | 45.3244 | 78.5114 | 93.2423 | 0
14665 | 892.5015 | 2.3467 | 22.6578 | 94.2264 | 31.7794 | 9.5 | 57.5707 | 2.2975 |  | 12.8295 | 41.5423 | 7.8775 |  | 47.2224 | 134.1716 | 8.644 | 41.494 | 13.0237 | 186 | 49.5481 | 80.701 | 94.4607 | 0
14666 | 878.042 | 3.5774 | 22.6593 | 94.1706 | 24.6226 | 12.3492 | 62.8703 | 2.5791 |  | 12.2681 | 42.4525 | 7.6121 |  | 45.1291 | 137.5937 | 8.6063 | 41.3723 | 8.0878 | 173 | 43.8069 | 73.5237 | 94.8241 | 0
14667 | 878.0956 | 7.3071 | 22.3204 | 94.0634 | 26.7251 | 11.4003 | 65.1019 | 2.1492 |  | 13.0659 | 43.2837 | 7.785 |  | 44.4846 | 133.0713 | 8.1219 | 41.4186 | 4.0112 | 170 | 41.7103 | 79.0906 | 93.8705 | 0
14668 | 877.1426 | 8.9683 | 22.6883 | 94.088 | 25.3308 | 10.4503 | 59.2096 | 2.479 |  | 12.4651 | 43.8385 | 7.7351 |  | 45.416 | 119.7881 | 9.3028 | 41.6249 | 2.9961 | 160 | 43.3179 | 80.7728 | 91.0818 | 0
14669 | 881.8038 | 7.5258 | 19.3881 | 94.6371 | 19.7471 | 9.5003 | 56.9717 | 2.1552 |  | 11.1966 | 42.8867 | 7.6237 |  | 44.8014 | 117.2291 | 8.7069 | 41.7676 | 2.7044 | 159 | 43.3858 | 77.3645 | 90.3507 | 0
14670 | 889.8019 | 8.4229 | 16.8668 | 92.6802 | 16.2685 | 10.4497 | 57.2597 | 2.2371 |  | 9.4929 | 40.2459 | 5.8533 |  | 42.1017 | 113.5598 | 8.1869 | 41.2447 | 2.6147 | 150 | 38.1221 | 52.6934 | 89.1553 | 0
14671 | 897.0676 | 5.2025 | 16.4582 | 90.6998 | 15.4176 | 10.45 | 56.7693 | 2.7284 |  | 8.601 | 43.1146 | 4.7977 |  | 39.7391 | 111.8541 | 8.4461 | 40.7312 | 2.5341 | 138 | 34.9475 | 60.6652 | 89.7294 | 0.03798
14672 | 905.5373 | 1.8189 | 16.1209 | 91.3448 | 15.2696 | 10.45 | 56.4371 | 1.9659 |  | 8.5508 | 47.1497 | 4.7923 |  | 40.2066 | 112.7022 | 8.2436 | 40.5547 | 2.552 | 136 | 29.7881 | 68.4688 | 87.4891 | 0.064895
14673 | 916.5676 | 2.0347 | 16.1687 | 91.9795 | 16.3844 | 9.5003 | 55.3096 | 1.3577 |  | 8.6563 | 43.4584 | 4.9147 |  | 43.1514 | 118.5818 | 8.6115 | 40.9033 | 2.5631 | 163 | 23.6084 | 68.5231 | 89.6074 | 0.10227
14674 | 924.653 | 2.558 | 16.6052 | 91.1687 | 16.4683 | 9.5 | 51.3323 | 1.2813 |  | 9.0916 | 40.5784 | 4.9387 |  | 46.6738 | 121.6346 | 8.0756 | 41.0116 | 3.1918 | 177 | 14.8796 | 60.6212 | 93.2523 | 0.1196
14675 | 939.7574 | 3.1734 | 16.5991 | 90.3399 | 16.355 | 10.4497 | 56.2729 | 1.2615 |  | 9.3304 | 46.6313 | 4.8724 |  | 50.3137 | 125.8046 | 8.4641 | 40.7469 | 4.1515 | 165 | 13.0965 | 67.0886 | 92.4674 | 0.135
14676 | 950.5859 | 5.2874 | 16.5899 | 93.9354 | 12.0737 | 16.1484 | 59.9178 | 2.1832 |  | 9.7531 | 51.0665 | 4.8813 |  | 54.0143 | 133.3561 | 7.8271 | 40.8809 | 4.525 | 163 | 14.243 | 69.7655 | 96.2652 | 0.098344
14677 | 944.8633 | 6.5252 | 16.5706 | 96.5198 | 19.3115 | 11.4013 | 53.9182 | 2.7926 |  | 10.2398 | 50.8446 | 4.8317 |  | 54.281 | 152.7491 | 8.8905 | 40.6135 | 4.4691 | 169 | 14.5581 | 67.2822 | 92.8411 | 0.093685
14678 | 941.889 | 9.2114 | 16.747 | 92.0167 | 21.3425 | 11.4 | 58.3945 | 2.9875 |  | 10.4575 | 51.036 | 4.8668 |  | 55.2773 | 159.4261 | 8.1168 | 40.6237 | 4.3872 | 175 | 16.7204 | 64.8196 | 89.742 | 0.091205
14679 | 938.4009 | 13.3459 | 16.894 | 90.1447 | 29.535 | 9.5005 | 54.4002 | 2.7356 |  | 10.3238 | 50.523 | 4.9458 |  | 54.8518 | 155.7097 | 7.742 | 40.7142 | 4.4952 | 176 | 17.8134 | 69.2952 | 91.849 | 0.075837
14680 | 933.4631 | 12.585 | 16.7962 | 92.9784 | 39.9375 | 7.6005 | 56.2786 | 2.4698 |  | 10.8795 | 48.9247 | 5.7127 |  | 53.2293 | 158.9994 | 7.8495 | 41.343 | 4.6191 | 181 | 23.0592 | 69.0105 | 86.7056 | 0.051652
14681 | 929.2628 | 7.6829 | 16.8723 | 93.5429 | 42.7372 | 9.4995 | 64.1581 | 2.5967 |  | 11.8003 | 47.6992 | 6.1441 |  | 52.9609 | 174.8174 | 8.3932 | 40.798 | 4.5295 | 163 | 24.931 | 55.3209 | 89.0356 | 0.057921
14682 | 934.1456 | 5.1887 | 16.7186 | 91.51 | 44.8332 | 8.5503 | 60.2959 | 3.1834 |  | 14.0211 | 47.0332 | 5.5462 |  | 55.9277 | 173.0533 | 8.6113 | 40.5614 | 3.9191 | 166 | 31.9141 | 59.1231 | 92.3963 | 0.0095391
14683 | 935.7154 | 6.6441 | 16.9891 | 90.2622 | 42.9338 | 8.55 | 57.6337 | 2.4135 |  | 15.0626 | 46.0431 | 5.1702 |  | 54.3143 | 155.9104 | 8.3767 | 40.5615 | 3.0708 | 187 | 30.8733 | 59.6532 | 90.0478 | 0
14684 | 912.9208 | 7.1773 | 17.0367 | 92.222 | 37.0187 | 11.3992 | 51.96 | 2.333 |  | 16.9356 | 43.0908 | 6.7613 |  | 50.9533 | 145.9682 | 8.6074 | 41.4119 | 3.0622 | 176 | 34.1171 | 51.4104 | 92.1617 | 0
14685 | 903.8312 | 5.2757 | 17.1312 | 93.3909 | 34.2725 | 9.5005 | 55.6284 | 2.0616 |  | 16.5653 | 41.5856 | 7.9926 |  | 47.9576 | 141.9339 | 7.9003 | 42.07 | 3.5652 | 172 | 32.2111 | 54.6312 | 94.1635 | 0
14686 | 902.0948 | 3.6678 | 17.1051 | 93.8213 | 31.7612 | 9.5 | 64.7293 | 2.5313 |  | 14.0449 | 40.9665 | 9.4043 |  | 46.9056 | 136.2756 | 8.425 | 42.5299 | 3.7602 | 164 | 34.7224 | 61.0281 | 96.3799 | 0
14687 | 339.7502 | 0 | 6.0168 | 32.3302 | 21.0641 | 0.00264 | 25.739 | 1.2357 |  | 5.1504 | 16.9574 | 3.9859 |  | 16.6894 | 53.7219 | 3.1195 | 14.8979 | 1.5017 | 147 | 3.7652 | 9.7047 | 11.5743 | 0
14688 | 886.0214 | 2.3164 | 16.7298 | 94.5283 | 24.5892 | 11.3997 | 56.8951 | 2.1929 |  | 12.8393 | 39.2964 | 7.8856 |  | 45.6838 | 126.2639 | 12.2779 | 41.6936 | 3.7408 | 139 | 35.0508 | 78.8123 | 92.4135 | 0
14689 | 884.687 | 2.3694 | 16.9028 | 94.0167 | 25.774 | 11.4 | 53.7493 | 2.1162 |  | 13.4774 | 39.6899 | 7.7744 |  | 44.1926 | 124.0151 | 12.2031 | 41.5077 | 3.5765 | 130 | 35.4849 | 81.2527 | 93.3156 | 0
14690 | 874.853 | 2.3256 | 28.3197 | 94.2416 | 24.7116 | 10.4503 | 55.4494 | 2.4333 |  | 13.5816 | 39.525 | 7.7417 |  | 43.004 | 127.2994 | 12.8685 | 41.4187 | 3.3124 | 128 | 34.2159 | 75.9225 | 94.5284 | 0
14691 | 872.7743 | 2.3249 | 35.4061 | 94.1518 | 19.6563 | 11.3997 | 60.1735 | 2.0842 |  | 13.625 | 39.7342 | 7.7757 |  | 43.5981 | 124.8665 | 13.5763 | 41.8024 | 2.9444 | 121 | 32.0565 | 76.6833 | 95.5002 | 0
14692 | 869.252 | 2.6504 | 35.0855 | 93.5669 | 23.7638 | 9.5005 | 53.9864 | 2.553 |  | 14.318 | 39.8934 | 7.7662 |  | 43.3063 | 119.6852 | 10.1996 | 41.8263 | 2.6843 | 122 | 35.3372 | 79.1909 | 104.6717 | 0
14693 | 880.2184 | 3.6745 | 31.1142 | 93.6026 | 21.9339 | 10.4497 | 58.3548 | 2.192 |  | 17.6648 | 43.4127 | 9.8574 |  | 47.5041 | 120.6265 | 8.6907 | 41.4444 | 2.8309 | 120 | 31.3087 | 67.6409 | 112.5492 | 0
14694 | 921.4087 | 4.8147 | 41.1887 | 95.943 | 15.2843 | 13.2992 | 74.0471 | 2.5118 |  | 20.8194 | 47.4916 | 18.1124 |  | 70.1129 | 132.9389 | 12.7689 | 41.2983 | 5.2276 | 179 | 38.3116 | 62.2302 | 130.9464 | 0
14695 | 979.0872 | 11.5867 | 72.2522 | 99.3487 | 5.3132 | 20.8979 | 91.1769 | 3.271 |  | 29.077 | 58.2353 | 30.867 |  | 105.228 | 189.5518 | 26.2117 | 43.8056 | 12.5911 | 302 | 63.5069 | 82.419 | 160.5624 | 0.05283
14696 | 1066.6388 | 11.2351 | 93.7885 | 106.9123 | 4.2228 | 21.8497 | 109.6092 | 5.0259 |  | 38.6929 | 71.4386 | 38.1191 |  | 137.282 | 250.1954 | 36.093 | 49.0083 | 16.8218 | 279 | 71.8091 | 98.628 | 185.5585 | 0.047576
14697 | 1155.3149 | 5.8464 | 105.1536 | 123.8394 | 3.552 | 23.7495 | 119.7384 | 5.5676 |  | 44.5911 | 80.204 | 38.654 |  | 155.4632 | 293.7877 | 40.1824 | 52.8955 | 17.3316 | 334 | 81.41 | 110.7098 | 203.5431 | 0.14612
14698 | 1215.771 | 8.743 | 105.55 | 136.3989 | -21.9886 | 20.8892 | 124.5099 | 5.1128 |  | 43.7229 | 83.8303 | 40.5277 |  | 164.9079 | 320.0684 | 42.1493 | 55.7746 | 16.991 | 332 | 91.2365 | 115.5406 | 211.9761 | 0.16831
14699 | 1242.0277 | 15.1957 | 108.7945 | 138.4877 | 11.4098 | 20.9116 | 128.3773 | 4.9442 |  | 44.6892 | 83.5175 | 39.7818 |  | 174.7668 | 330.133 | 43.8953 | 57.7616 | 16.7049 | 324 | 83.9599 | 123.5784 | 204.3488 | 0.16109
14700 | 1243.1268 | 14.9035 | 113.1071 | 133.9572 | 13.2018 | 22.7995 | 133.6081 | 5.7922 |  | 41.2212 | 85.8062 | 41.1551 |  | 178.7668 | 323.1175 | 43.9688 | 57.5496 | 16.956 | 363 | 70.2884 | 121.6652 | 201.5296 | 0.16736
14701 | 1234.1959 | 11.0017 | 113.5757 | 137.4966 | 12.9299 | 23.7497 | 134.5962 | 6.3663 |  | 41.9555 | 90.7609 | 44.0506 |  | 177.5985 | 310.6599 | 43.3628 | 58.6392 | 18.6358 | 308 | 79.0041 | 121.5406 | 202.7809 | 0.16691
14702 | 1247.4655 | 9.032 | 114.1744 | 139.7336 | 15.0987 | 22.8003 | 128.6864 | 5.9537 |  | 43.4406 | 90.1257 | 41.7851 |  | 173.2563 | 308.2783 | 43.5186 | 59.3139 | 18.2276 | 272 | 84.8794 | 123.2102 | 202.0815 | 0.18522
14703 | 1225.6841 | 6.6658 | 109.6836 | 133.319 | 19.2893 | 19.9508 | 124.228 | 5.1023 |  | 39.621 | 87.988 | 31.981 |  | 169.7316 | 307.084 | 41.6788 | 59.4235 | 17.3452 | 282 | 78.5463 | 121.0826 | 186.3314 | 0.1233
14704 | 1151.7866 | 4.6983 | 99.138 | 128.1565 | 29.0177 | 11.4024 | 109.8514 | 4.1837 |  | 36.3063 | 80.2663 | 18.8246 |  | 158.504 | 280.3504 | 33.097 | 55.5606 | 16.5954 | 261 | 70.4477 | 109.256 | 164.3583 | 0.10396
14705 | 1091.1589 | 4.1029 | 94.0575 | 121.7011 | 27.6479 | 13.2995 | 99.2607 | 4.1094 |  | 28.861 | 66.1668 | 12.1275 |  | 131.7007 | 237.1768 | 19.4152 | 50.7302 | 15.7917 | 219 | 53.5648 | 89.1152 | 123.8443 | 0.028358
14706 | 1072.4204 | 4.1271 | 83.7239 | 113.309 | 31.3851 | 10.4508 | 92.5997 | 3.4152 |  | 23.4879 | 57.3074 | 9.7176 |  | 92.208 | 214.3127 | 11.5453 | 47.8514 | 12.6291 | 211 | 52.913 | 82.8885 | 116.2125 | 0.0096486
14707 | 1033.4701 | 4.5814 | 66.7527 | 105.7965 | 30.0167 | 11.3997 | 87.7421 | 2.4269 |  | 21.461 | 53.3344 | 11.0891 |  | 74.22 | 188.2953 | 10.147 | 44.7141 | 7.1339 | 194 | 42.326 | 70.1476 | 95.2198 | 0
14708 | 1002.7357 | 4.7272 | 37.2432 | 99.4301 | 27.7341 | 12.3497 | 73.1119 | 2.501 |  | 20.4529 | 51.4994 | 12.4088 |  | 65.1013 | 155.745 | 9.3028 | 42.8846 | 4.7045 | 172 | 43.9292 | 63.5187 | 92.3796 | 0
14709 | 980.6243 | 4.3768 | 24.1253 | 95.3956 | 25.2293 | 9.5008 | 67.0322 | 2.2047 |  | 17.8733 | 48.8237 | 11.0077 |  | 56.0481 | 148.3285 | 9.3532 | 42.444 | 4.4634 | 175 | 40.1457 | 53.7789 | 93.6238 | 0
14710 | 949.6422 | 4.4517 | 23.5551 | 94.1873 | 16.7655 | 12.3492 | 65.7867 | 2.4609 |  | 14.3234 | 43.5202 | 9.7034 |  | 51.4978 | 141.4148 | 9.3139 | 41.9326 | 4.2602 | 156 | 35.8496 | 58.3497 | 92.7379 | 0
14711 | 350.456 | 0 | 8.1753 | 31.6947 | 14.3486 | 0.003431 | 24.1951 | 1.1304 |  | 5.145 | 17.2063 | 3.6358 |  | 17.7638 | 54.2184 | 3.1705 | 14.39 | 1.6701 | 142 | 3.7547 | 8.8954 | 9.2634 | 0
14712 | 925.4113 | 3.5822 | 19.1902 | 92.9779 | 18.0726 | 9.5003 | 61.229 | 2.1521 |  | 14.3887 | 39.7908 | 9.2217 |  | 49.1371 | 121.7096 | 9.2821 | 41.4556 | 4.4161 | 139 | 35.198 | 63.0526 | 90.3568 | 0
14713 | 921.4138 | 2.1867 | 17.5734 | 92.6565 | 17.5806 | 9.5 | 61.3595 | 2.0982 |  | 14.9204 | 39.3281 | 9.0337 |  | 46.165 | 120.6014 | 9.1755 | 41.7338 | 3.8539 | 134 | 29.0148 | 66.5939 | 93.5516 | 0
14714 | 905.3997 | 2.1017 | 17.7915 | 92.6446 | 16.0314 | 10.4497 | 60.1562 | 1.8945 |  | 14.9413 | 39.4252 | 9.1059 |  | 44.0187 | 120.5451 | 9.0834 | 41.5272 | 2.8204 | 127 | 31.0595 | 69.1659 | 91.6673 | 0
14715 | 896.8944 | 3.7269 | 17.3615 | 92.5803 | 15.6251 | 10.45 | 59.3053 | 2.3871 |  | 14.9553 | 39.9467 | 8.8915 |  | 43.3774 | 120.2068 | 9.0609 | 41.413 | 2.2663 | 139 | 26.5232 | 62.6356 | 92.4408 | 0
14716 | 894.5286 | 6.5598 | 17.0324 | 92.6715 | 15.6011 | 10.45 | 62.9353 | 2.0103 |  | 15.6904 | 39.4361 | 8.6638 |  | 43.5823 | 115.6029 | 9.8129 | 41.4575 | 2.2639 | 125 | 27.912 | 67.0272 | 96.3453 | 0
14717 | 900.9469 | 5.7167 | 25.3641 | 92.6129 | 13.6961 | 12.3495 | 66.4964 | 2.2572 |  | 18.6454 | 43.958 | 11.0297 |  | 48.6083 | 118.616 | 9.1639 | 41.4325 | 2.4045 | 120 | 28.9063 | 70.0378 | 104.9865 | 0
14718 | 958.9002 | 4.8672 | 40.8525 | 96.9395 | 14.5741 | 11.4003 | 76.3379 | 1.8676 |  | 19.7222 | 50.1208 | 16.9693 |  | 67.9337 | 139.3116 | 12.2589 | 40.8351 | 5.1601 | 189 | 33.2048 | 66.7729 | 132.4934 | 0
14719 | 1022.3112 | 10.5634 | 65.3652 | 103.9747 | 6.9278 | 18.0482 | 97.5862 | 3.1317 |  | 24.8626 | 58.5232 | 26.5388 |  | 107.4328 | 188.7126 | 25.4958 | 43.5667 | 11.7441 | 277 | 53.3696 | 79.4236 | 155.8369 | 0.020081
14720 | 1089.3184 | 16.2444 | 88.9268 | 115.1128 | 2.8848 | 21.8489 | 116.716 | 5.1943 |  | 34.3682 | 69.9937 | 34.7495 |  | 147.481 | 253.7518 | 36.0252 | 48.8064 | 13.5977 | 310 | 55.8229 | 94.8835 | 176.614 | 0.040608
14721 | 1181.9996 | 15.6571 | 105.5212 | 129.3878 | 9.3481 | 21.85 | 140.3144 | 5.7603 |  | 40.9819 | 79.3766 | 39.941 |  | 170.2094 | 289.8465 | 39.4173 | 52.6384 | 13.1524 | 350 | 58.5001 | 105.2763 | 194.4563 | 0.061552
14722 | 1239.9538 | 15.6936 | 111.7939 | 136.6211 | 15.1958 | 21.85 | 156.6324 | 5.4455 |  | 40.3558 | 81.6917 | 42.8206 |  | 181.2605 | 313.4382 | 40.458 | 54.4103 | 15.8055 | 363 | 74.1181 | 115.8493 | 199.6761 | 0.087647
14723 | 1266.8254 | 11.4602 | 115.3607 | 135.2216 | 16.9288 | 22.3125 | 156.6157 | 5.4317 |  | 39.2706 | 83.2588 | 43.0862 |  | 189.435 | 328.4847 | 41.1291 | 56.9252 | 17.3063 | 318 | 77.638 | 126.9552 | 207.0671 | 0.1233
14724 | 1277.1336 | 0 | 0 | 0 | -23.4935 | 22.3188 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0.15685
14725 | 1273.8902 | 9.2357 | 113.7299 | 137.0592 | 21.1659 | 21.8749 | 154.6351 | 5.5422 |  | 39.441 | 86.803 | 43.0725 |  | 192.2747 | 327.6159 | 44.3423 | 59.9027 | 17.3436 | 309 | 83.1056 | 118.3881 | 220.0386 | 0.15347
14726 | 1253.9235 | 11.008 | 113.5976 | 140.0932 | 25.8116 | 20.9003 | 156.1073 | 5.5352 |  | 44.4086 | 86.7528 | 41.7778 |  | 190.1107 | 322.6293 | 45.1824 | 61.2996 | 17.455 | 304 | 79.7515 | 121.9303 | 224.4421 | 0.11267
14727 | 1227.4607 | 9.4979 | 115.2435 | 134.8984 | 32.1874 | 18.0508 | 154.0112 | 5.0494 |  | 36.3735 | 86.4458 | 37.4822 |  | 187.28 | 321.1141 | 40.5278 | 61.1533 | 17.6649 | 278 | 79.1687 | 116.0296 | 216.1305 | 0.11988
14728 | 1176.1223 | 5.9852 | 111.1728 | 127.6878 | 41.5655 | 10.4521 | 130.9017 | 4.1453 |  | 25.846 | 82.7168 | 28.5813 |  | 176.7483 | 284.1888 | 31.3999 | 59.4318 | 17.9495 | 239 | 74.1359 | 108.9451 | 198.4349 | 0.072479
14729 | 1124.5508 | 6.3114 | 104.804 | 117.7821 | 34.1914 | 16.1484 | 96.8875 | 3.5057 |  | 21.8517 | 69.7412 | 15.496 |  | 143.7183 | 221.2064 | 18.9371 | 54.7885 | 17.5749 | 242 | 57.4925 | 92.5025 | 136.72 | 0.043284
14730 | 1082.8673 | 8.1145 | 84.2097 | 105.5215 | 38.286 | 10.4516 | 91.6131 | 3.6276 |  | 16.8282 | 59.3532 | 6.4509 |  | 96.0569 | 184.8083 | 11.9657 | 51.1888 | 13.7369 | 246 | 54.0703 | 80.7384 | 118.8208 | 0.014102
14731 | 1044.3103 | 7.2498 | 62.4052 | 98.784 | 37.2787 | 11.3997 | 100.1423 | 2.7593 |  | 14.6428 | 56.4347 | 5.7003 |  | 77.5872 | 167.247 | 10.5049 | 46.777 | 7.751 | 205 | 49.3357 | 74.1308 | 101.8485 | 0
14732 | 1017.9224 | 5.7065 | 36.9027 | 96.1439 | 39.5492 | 9.5005 | 80.0412 | 1.7516 |  | 16.6918 | 54.0518 | 6.8434 |  | 76.2992 | 155.821 | 9.7932 | 42.7335 | 4.9339 | 196 | 46.3161 | 65.575 | 100.8971 | 0
14733 | 992.956 | 4.8711 | 26.0351 | 94.641 | 38.9473 | 9.5 | 58.3906 | 1.6493 |  | 17.8308 | 50.0234 | 6.9566 |  | 75.5381 | 135.8815 | 8.908 | 41.2959 | 4.7939 | 193 | 34.3056 | 63.4484 | 101.0753 | 0
14734 | 972.2721 | 4.9482 | 25.8758 | 95.4474 | 35.9629 | 9.5 | 56.5791 | 1.8703 |  | 16.4071 | 44.6614 | 7.2184 |  | 70.1794 | 130.0333 | 8.798 | 41.2288 | 4.8818 | 162 | 35.051 | 64.0825 | 104.1707 | 0
14735 | 365.3126 | 0 | 9.144 | 0 | 21.5813 | 0.00264 | 22.3159 | 0.77951 |  | 6.1057 | 17.6611 | 2.8902 |  | 0 | 0 | 3.1041 | 0 | 1.9436 | 144 | 3.836 | 9.8502 | 11.4835 | 0
14736 | 948.7724 | 5.2393 | 24.7282 | 93.1428 | 36.5176 | 9.5003 | 62.1096 | 2.0034 |  | 13.4068 | 41.4062 | 7.0954 |  | 60.859 | 127.5937 | 9.5244 | 41.8928 | 4.1543 | 139 | 29.0343 | 73.6252 | 99.3631 | 0
14737 | 942.4581 | 2.2445 | 24.5718 | 93.0182 | 36.2071 | 9.5 | 63.3435 | 1.5531 |  | 14.2883 | 40.8498 | 6.9677 |  | 57.5848 | 123.6282 | 9.3076 | 41.4754 | 3.0724 | 144 | 28.4041 | 66.7539 | 100.8632 | 0
14738 | 939.6564 | 2.1502 | 36.994 | 92.9037 | 35.0963 | 10.4497 | 64.493 | 1.5545 |  | 14.3171 | 41.1345 | 6.857 |  | 55.3133 | 122.9805 | 9.363 | 41.1763 | 2.3509 | 152 | 29.7255 | 71.0199 | 97.9949 | 0
14739 | 937.8533 | 2.0881 | 44.7163 | 92.6666 | 35.2278 | 10.45 | 62.1302 | 2.4343 |  | 14.0127 | 40.811 | 6.7013 |  | 54.9632 | 120.7062 | 9.4882 | 41.0588 | 2.2368 | 144 | 25.9587 | 74.5772 | 100.6844 | 0
14740 | 927.3582 | 2.7478 | 44.1571 | 92.8834 | 36.235 | 9.5003 | 60.4781 | 2.1787 |  | 14.6256 | 40.127 | 6.6663 |  | 56.3284 | 115.4431 | 9.301 | 41.0047 | 2.2297 | 121 | 29.5418 | 74.8801 | 99.6667 | 0
14741 | 942.9959 | 3.726 | 40.6797 | 92.6042 | 36.0589 | 9.5 | 60.9091 | 1.5912 |  | 17.6382 | 40.1489 | 8.8773 |  | 56.6539 | 116.8583 | 9.3517 | 40.9812 | 2.2163 | 117 | 27.6917 | 72.992 | 111.3457 | 0
14742 | 997.8958 | 4.7999 | 48.6277 | 99.762 | 34.6898 | 10.4497 | 74.3863 | 1.4709 |  | 21.0181 | 45.9417 | 18.2431 |  | 72.3278 | 132.8165 | 12.3167 | 40.7312 | 4.3131 | 183 | 33.8198 | 62.025 | 135.1681 | 0
14743 | 1058.9518 | 9.2799 | 78.1736 | 106.8599 | 27.2991 | 17.0982 | 108.8561 | 4.0489 |  | 27.5172 | 66.178 | 30.4451 |  | 114.1161 | 183.9634 | 25.8017 | 43.4847 | 9.6192 | 293 | 56.03 | 86.5135 | 159.4372 | 0.058024
14744 | 1143.8012 | 14.7666 | 97.0555 | 116.5886 | 24.6667 | 18.9995 | 132.54 | 5.2921 |  | 35.9423 | 83.0808 | 37.1991 |  | 150.6199 | 256.802 | 36.3809 | 48.7704 | 13.391 | 304 | 69.687 | 106.0792 | 189.6934 | 0.095555
14745 | 1198.7708 | 17.3084 | 108.9791 | 132.5125 | 23.7516 | 19.9497 | 137.7951 | 5.0344 |  | 40.9827 | 88.2989 | 40.6003 |  | 168.5559 | 312.0745 | 41.1845 | 54.4758 | 14.8907 | 341 | 73.7959 | 114.9034 | 199.9323 | 0.15088
14746 | 1238.2868 | 13.7572 | 110.7198 | 145.7938 | 23.3773 | 21.8495 | 140.1462 | 5.1726 |  | 44.5205 | 90.7821 | 41.6687 |  | 178.3822 | 334.2268 | 42.6394 | 59.0891 | 15.9764 | 384 | 84.5954 | 122.1257 | 212.0149 | 0.11135
14747 | 1269.5362 | 7.0959 | 114.2102 | 137.0735 | 24.7031 | 20.9003 | 146.9373 | 5.6188 |  | 47.9262 | 90.998 | 40.9542 |  | 190.6136 | 340.8977 | 42.1921 | 60.1757 | 16.2874 | 344 | 87.9374 | 138.8648 | 213.3714 | 0.13617
14748 | 1277.0938 | 5.942 | 118.1915 | 131.282 | 24.4629 | 20.9 | 151.5966 | 5.6359 |  | 46.9153 | 88.7176 | 41.8443 |  | 194.2549 | 338.3117 | 41.4231 | 58.5313 | 17.1102 | 338 | 78.555 | 134.1581 | 209.9809 | 0.18743
14749 | 1270.8035 | 7.5874 | 119.5244 | 134.8448 | 23.6499 | 22.7995 | 152.7233 | 5.5523 |  | 44.8966 | 88.3852 | 41.1109 |  | 190.2756 | 343.1654 | 41.8348 | 58.1972 | 18.1844 | 274 | 80.359 | 142.6647 | 210.2509 | 0.14429
14750 | 1278.4564 | 6.069 | 118.0505 | 141.604 | 25.1203 | 21.8503 | 148.2754 | 5.0959 |  | 44.851 | 89.3631 | 41.1289 |  | 190.5296 | 337.214 | 41.2622 | 57.6543 | 20.6286 | 272 | 84.5676 | 136.7375 | 205.9848 | 0.1322
14751 | 1243.1883 | 4.5808 | 112.3012 | 143.9216 | 28.6737 | 19.0008 | 138.4973 | 4.8223 |  | 40.4352 | 89.7411 | 38.038 |  | 185.7303 | 317.6506 | 37.5506 | 57.1191 | 20.1631 | 271 | 78.4003 | 137.09 | 208.3993 | 0.12253
14752 | 1208.8706 | 4.8331 | 107.4397 | 138.5808 | 36.4613 | 12.3518 | 115.5211 | 4.7073 |  | 35.1698 | 83.3622 | 27.239 |  | 178.5592 | 289.7302 | 29.4115 | 56.1033 | 18.5781 | 254 | 71.114 | 118.3022 | 184.1479 | 0.073858
14753 | 1147.5558 | 5.4454 | 104.7564 | 130.0174 | 35.5823 | 12.35 | 87.1555 | 3.6359 |  | 30.5427 | 67.0055 | 19.7853 |  | 142.7917 | 264.6561 | 18.1975 | 52.8779 | 17.7511 | 249 | 59.7166 | 95.357 | 137.5412 | 0.074824
14754 | 1083.1647 | 5.5791 | 86.6042 | 119.1348 | 31.5742 | 14.2495 | 71.4099 | 3.0851 |  | 24.9069 | 56.045 | 15.8071 |  | 100.2396 | 239.4317 | 12.5944 | 49.211 | 14.2909 | 229 | 53.8508 | 82.0857 | 116.5921 | 0.014045
14755 | 1021.2465 | 5.2886 | 64.2313 | 113.0283 | 29.6168 | 14.25 | 67.4035 | 3.1015 |  | 21.5273 | 52.2126 | 13.789 |  | 76.1016 | 209.3171 | 11.1323 | 46.0244 | 8.4004 | 201 | 51.5792 | 72.8803 | 97.9939 | 0
14756 | 972.5392 | 4.8733 | 35.5877 | 109.1816 | 30.8742 | 11.4008 | 70.5157 | 2.3961 |  | 20.1843 | 51.6169 | 16.6079 |  | 70.962 | 185.4031 | 10.5482 | 44.1937 | 5.8834 | 191 | 54.5951 | 66.6504 | 97.2128 | 0
14757 | 951.8629 | 4.2327 | 22.4356 | 106.6722 | 24.7383 | 13.2995 | 65.6431 | 2.5305 |  | 16.8214 | 49.334 | 17.667 |  | 64.1283 | 168.1374 | 10.4238 | 43.5265 | 5.4503 | 176 | 53.5068 | 64.5706 | 94.3091 | 0
14758 | 931.5647 | 3.5961 | 21.0467 | 102.9146 | 17.5917 | 14.2497 | 58.329 | 2.1891 |  | 13.5162 | 42.641 | 16.8942 |  | 61.597 | 161.2329 | 10.1429 | 43.0885 | 4.8902 | 160 | 49.1055 | 62.917 | 92.907 | 0
14759 | 337.724 | 0 | 7.1102 | 0 | 14.2989 | 0.00396 | 20.8906 | 0.67373 |  | 4.8087 | 16.041 | 6.3379 |  | 0 | 0 | 3.3946 | 0 | 1.8206 | 149 | 5.0522 | 9.2286 | 10.1939 | 0
14760 | 915.7384 | 7.1476 | 20.3182 | 101.0315 | 13.0058 | 12.3497 | 58.9016 | 2.3015 |  | 13.7635 | 38.1805 | 10.804 |  | 54.8491 | 145.4087 | 10.0291 | 43.082 | 3.466 | 142 | 42.5993 | 69.3942 | 91.1864 | 0
14761 | 904.9675 | 9.4661 | 19.8405 | 100.5894 | 12.9433 | 11.4003 | 58.3556 | 2.454 |  | 14.4978 | 38.2978 | 6.8127 |  | 50.7664 | 134.4263 | 10.1239 | 42.9741 | 3.0447 | 126 | 37.8664 | 64.1459 | 92.3599 | 0
14762 | 895.0531 | 4.9512 | 29.4509 | 100.1193 | 10.6918 | 12.3497 | 64.9914 | 2.2782 |  | 14.5865 | 38.8826 | 6.6003 |  | 48.6571 | 126.6478 | 10.3529 | 42.8508 | 3.0437 | 129 | 38.1348 | 69.7673 | 92.2218 | 0
14763 | 890.8464 | 2.1501 | 26.0285 | 100.1129 | 9.332 | 13.2997 | 62.3461 | 2.6437 |  | 14.6272 | 38.9581 | 6.622 |  | 46.9382 | 122.1552 | 9.9312 | 42.6847 | 2.9455 | 127 | 33.5373 | 71.8013 | 92.1055 | 0
14764 | 883.9666 | 2.6061 | 19.1128 | 101.5705 | 10.2407 | 12.3503 | 58.0343 | 3.0621 |  | 15.5711 | 38.8652 | 6.56 |  | 46.8123 | 118.1393 | 9.8529 | 42.5068 | 2.621 | 122 | 33.16 | 71.5977 | 95.6125 | 0
14765 | 899.8788 | 3.7912 | 24.9928 | 100.8579 | 10.1936 | 12.35 | 65.396 | 2.2434 |  | 18.4601 | 41.615 | 7.9554 |  | 50.846 | 118.4685 | 10.0741 | 42.6016 | 2.5078 | 117 | 34.9183 | 73.2773 | 110.861 | 0
14766 | 940.6118 | 9.3354 | 36.6553 | 106.2699 | 8.2679 | 14.2495 | 76.4556 | 2.3239 |  | 22.6863 | 45.2646 | 12.9911 |  | 75.1563 | 145.7188 | 14.4502 | 42.0925 | 4.7243 | 191 | 38.7196 | 69.6972 | 125.384 | 0
14767 | 999.6486 | 17.9548 | 61.5685 | 112.3085 | -0.24846 | 22.7976 | 91.8573 | 3.5348 |  | 30.3908 | 60.6809 | 25.175 |  | 118.5054 | 189.2149 | 26.2828 | 43.9684 | 9.6856 | 268 | 64.7446 | 85.551 | 158.6324 | 0.1374
14768 | 1081.1846 | 20.5058 | 89.4849 | 122.5434 | -0.67825 | 23.7497 | 105.5123 | 5.5452 |  | 37.5131 | 78.2622 | 35.4237 |  | 148.9752 | 238.5374 | 35.608 | 48.2509 | 12.9206 | 308 | 76.265 | 104.4572 | 185.0487 | 0.21712
14769 | 1179.8132 | 18.6702 | 102.6502 | 134.7903 | -1.0532 | 24.6997 | 122.9166 | 5.2928 |  | 44.0582 | 83.8316 | 40.2482 |  | 162.648 | 276.5435 | 40.0335 | 52.7903 | 14.3489 | 349 | 85.3932 | 118.8386 | 201.8225 | 0.26538
14770 | 1235.5562 | 14.1478 | 104.2018 | 137.7527 | -1.6118 | 26.5995 | 130.9197 | 5.0577 |  | 44.0361 | 84.3057 | 41.717 |  | 167.6079 | 291.557 | 40.5405 | 54.4233 | 15.5945 | 356 | 80.7697 | 126.9152 | 209.1043 | 0.25231
14771 | 1256.9165 | 10.6435 | 106.55 | 135.9333 | 12.3696 | 23.7508 | 130.4694 | 5.8474 |  | 44.6019 | 85.7199 | 40.223 |  | 174.9625 | 299.4008 | 40.9118 | 54.5993 | 15.8873 | 328 | 74.5199 | 138.1484 | 207.1873 | 0.10892
14772 | 1249.4859 | 10.8678 | 106.4093 | 136.5354 | 25.6013 | 22.8003 | 131.5246 | 5.5359 |  | 42.1452 | 87.2178 | 39.7624 |  | 177.2179 | 304.337 | 43.3352 | 53.9413 | 15.9996 | 365 | 61.0035 | 132.239 | 208.7036 | 0.25623
14773 | 1245.5854 | 9.5773 | 104.7603 | 140.8816 | 30.1285 | 22.8 | 134.5916 | 4.8091 |  | 37.6912 | 92.2932 | 40.3273 |  | 183.5212 | 311.8802 | 42.3496 | 56.7049 | 16.0161 | 309 | 68.3577 | 132.9741 | 199.8136 | 0.26799
14774 | 1244.9913 | 6.3488 | 108.2195 | 143.1466 | 31.2974 | 23.7497 | 131.4644 | 4.9373 |  | 34.9689 | 96.9809 | 39.8677 |  | 188.3234 | 305.5255 | 40.1476 | 58.1605 | 15.8297 | 278 | 69.2786 | 135.4373 | 204.4728 | 0.1504
14775 | 1210.1404 | 4.7935 | 109.6286 | 139.0076 | 35.9603 | 19.9511 | 128.7695 | 5.0249 |  | 36.1429 | 93.8813 | 36.3889 |  | 185.3353 | 287.761 | 39.0337 | 57.1747 | 15.5783 | 303 | 64.4654 | 121.0769 | 190.6804 | 0.085764
14776 | 1162.7786 | 4.5843 | 105.4461 | 129.578 | 43.0504 | 13.3018 | 105.3081 | 4.4138 |  | 34.3773 | 83.6925 | 30.2014 |  | 175.788 | 267.1667 | 32.6282 | 55.4528 | 15.1592 | 284 | 56.5735 | 110.0674 | 167.4173 | 0.068768
14777 | 1108.4459 | 3.9688 | 99.319 | 120.7162 | 42.2356 | 15.1995 | 86.8045 | 3.8958 |  | 27.0397 | 68.1546 | 28.6006 |  | 139.8425 | 240.1287 | 23.9953 | 51.5291 | 14.7085 | 215 | 50.1756 | 87.3839 | 125.4341 | 0.039791
14778 | 1055.7798 | 3.3928 | 79.5895 | 107.3169 | 39.0674 | 12.3542 | 83.6579 | 3.1592 |  | 16.1703 | 58.1237 | 24.3926 |  | 92.977 | 212.6539 | 13.9426 | 48.3618 | 14.036 | 208 | 42.7663 | 78.7435 | 111.5276 | 0.015477
14779 | 1020.9058 | 3.9875 | 56.462 | 102.5428 | 28.2719 | 14.246 | 79.5967 | 3.0434 |  | 12.1359 | 56.4244 | 13.9676 |  | 73.9434 | 187.4393 | 9.6916 | 45.0456 | 13.4383 | 198 | 44.4729 | 76.6198 | 97.0601 | 0
14780 | 998.7207 | 5.0228 | 32.4019 | 102.1683 | 29.5464 | 12.3505 | 69.0013 | 2.384 |  | 14.2422 | 59.2204 | 8.5209 |  | 71.2035 | 170.0881 | 9.8992 | 43.5855 | 14.1844 | 191 | 45.1067 | 72.8128 | 93.1852 | 0
14781 | 970.9378 | 4.8042 | 23.0926 | 98.7604 | 25.9437 | 13.2997 | 64.8813 | 2.6271 |  | 15.2731 | 54.5602 | 7.8357 |  | 66.6012 | 154.7342 | 10.5501 | 43.074 | 14.3542 | 194 | 37.6357 | 67.6506 | 90.1078 | 0
14782 | 952.4491 | 3.7035 | 22.7876 | 95.5957 | 22.6111 | 13.3 | 58.7122 | 2.6308 |  | 14.3322 | 45.7343 | 7.7255 |  | 59.2912 | 146.4496 | 10.5117 | 42.1187 | 10.0828 | 180 | 37.4946 | 64.5126 | 91.5739 | 0
14783 | 353.4672 | 0 | 7.9141 | 0 | 17.5796 | 0 | 20.6216 | 0.90781 |  | 5.33 | 17.6746 | 2.9757 |  | 0 | 0 | 3.5774 | 0 | 2.9683 | 156 | 3.9259 | 9.4579 | 10.1556 | 0
14784 | 924.3935 | 2.1058 | 22.9648 | 95.3709 | 24.3699 | 15.1997 | 61.9267 | 2.6787 |  | 13.8103 | 42.7744 | 7.3003 |  | 49.6002 | 129.2394 | 10.4277 | 41.6761 | 4.4727 | 153 | 31.3449 | 62.4234 | 88.8779 | 0
14785 | 921.808 | 2.1178 | 22.9085 | 94.6376 | 22.8017 | 11.4011 | 65.6535 | 2.4018 |  | 14.4764 | 42.4402 | 7.0705 |  | 48.3674 | 127.3744 | 9.8724 | 41.5058 | 3.819 | 138 | 34.9123 | 65.805 | 87.6095 | 0
14786 | 908.9878 | 2.3893 | 22.898 | 94.2415 | 19.431 | 13.2995 | 62.9254 | 2.6366 |  | 14.5803 | 41.9976 | 7.0779 |  | 47.537 | 128.231 | 10.6496 | 41.7701 | 3.1612 | 139 | 31.5909 | 68.5619 | 89.3351 | 0
14787 | 902.1677 | 2.3575 | 22.7274 | 94.4602 | 25.3861 | 14.2497 | 60.4308 | 2.3588 |  | 14.6699 | 42.1722 | 7.053 |  | 46.7474 | 128.2934 | 9.8697 | 41.8268 | 2.5561 | 136 | 31.271 | 68.8484 | 88.3313 | 0
14788 | 909.7511 | 2.173 | 22.2261 | 94.6073 | 29.4051 | 15.1997 | 58.5682 | 2.4878 |  | 15.4287 | 41.6932 | 7.0381 |  | 46.2165 | 122.5543 | 10.6865 | 41.7299 | 2.2064 | 116 | 32.4698 | 69.226 | 93.0084 | 0
14789 | 924.8741 | 4.6634 | 31.4586 | 94.8286 | 29.8546 | 12.3508 | 59.8088 | 2.9193 |  | 20.0967 | 45.7063 | 8.375 |  | 50.0178 | 121.8454 | 9.8418 | 41.4601 | 2.1395 | 115 | 29.6026 | 67.2238 | 102.0153 | 0
14790 | 967.2435 | 8.5941 | 43.1958 | 99.4186 | 23.5722 | 13.2997 | 68.1735 | 2.0584 |  | 30.2821 | 52.958 | 14.5168 |  | 70.5463 | 128.4636 | 13.3344 | 41.1935 | 4.2195 | 182 | 40.1445 | 62.6505 | 126.1119 | 0
14791 | 1030.8358 | 9.9181 | 65.8968 | 106.696 | 12.9444 | 19.9482 | 90.3778 | 3.4826 |  | 35.9008 | 62.5101 | 19.8632 |  | 115.0037 | 180.7856 | 25.7261 | 44.0356 | 9.3505 | 247 | 60.3772 | 86.5107 | 154.2307 | 0.060817
14792 | 1126.6028 | 14.6996 | 94.8259 | 118.993 | 8.4433 | 22.7992 | 113.9618 | 5.3222 |  | 40.3663 | 73.1293 | 25.452 |  | 150.1539 | 245.1683 | 35.2548 | 48.9056 | 13.1832 | 304 | 69.6276 | 109.3434 | 182.6243 | 0.059771
14793 | 1197.3587 | 17.5872 | 105.243 | 131.7654 | 9.725 | 21.8503 | 126.9092 | 5.712 |  | 43.6011 | 80.813 | 34.3209 |  | 168.0958 | 296.8194 | 39.3989 | 54.0072 | 15.1469 | 368 | 77.4047 | 120.3212 | 192.1271 | 0.076033
14794 | 1231.5324 | 13.5309 | 106.3871 | 139.0315 | 13.3527 | 23.7495 | 127.7255 | 5.1922 |  | 42.4792 | 88.1425 | 39.5707 |  | 179.7039 | 335.0608 | 41.0362 | 59.9045 | 16.1668 | 355 | 82.706 | 129.8681 | 200.9865 | 0.10922
14795 | 1251.2764 | 8.2034 | 110.5911 | 137.2711 | 22.1406 | 23.75 | 122.2537 | 5.114 |  | 43.2056 | 92.5076 | 38.7427 |  | 189.0652 | 347.7362 | 40.698 | 61.5436 | 16.9309 | 326 | 77.0814 | 138.6312 | 200.9857 | 0.1251
14796 | 1254.1628 | 6.8322 | 113.0502 | 135.3193 | 31.9393 | 19.9511 | 124.4749 | 5.5988 |  | 39.5636 | 92.6609 | 36.9872 |  | 188.0745 | 332.8699 | 43.2864 | 60.3032 | 17.5627 | 369 | 72.0659 | 127.5558 | 203.7518 | 0.13316
14797 | 1254.4982 | 7.7856 | 112.8953 | 138.7887 | 7.6667 | 21.8495 | 131.9816 | 5.4501 |  | 30.7759 | 95.5519 | 37.3957 |  | 186.7992 | 325.5803 | 44.5995 | 59.8972 | 17.2976 | 322 | 75.3696 | 124.3747 | 210.2026 | 0.12012
14798 | 1241.0067 | 11.8444 | 111.7016 | 142.0821 | -16.8113 | 19.9505 | 128.6652 | 5.4684 |  | 27.8396 | 95.8135 | 35.6429 |  | 186.4966 | 326.3606 | 42.7691 | 60.6764 | 18.5931 | 292 | 75.8487 | 124.0202 | 198.924 | 0.13009
14799 | 1204.0533 | 12.233 | 110.4039 | 140.2988 | -22.6397 | 21.8495 | 124.5255 | 5.5247 |  | 25.3999 | 92.2375 | 29.4413 |  | 180.3754 | 304.4735 | 39.2175 | 59.4489 | 18.5755 | 289 | 70.3489 | 113.516 | 179.5311 | 0.10516
14800 | 1151.6747 | 7.0476 | 104.3956 | 133.3148 | -17.6396 | 17.1013 | 108.0553 | 4.015 |  | 26.2686 | 84.7838 | 22.0258 |  | 168.5882 | 258.7172 | 31.3206 | 57.996 | 17.624 | 280 | 67.8741 | 102.8329 | 155.8926 | 0.071972
14801 | 1097.8131 | 4.1511 | 87.6495 | 120.8466 | -15.6408 | 15.2005 | 80.4229 | 2.7395 |  | 26.2236 | 69.032 | 19.4665 |  | 132.0855 | 206.0443 | 19.6447 | 53.7244 | 16.9042 | 243 | 64.1801 | 82.3907 | 124.0494 | 0.081238
14802 | 1041.2593 | 3.989 | 46.9736 | 105.8843 | -11.6405 | 11.4011 | 67.484 | 2.5912 |  | 21.1804 | 57.5947 | 18.0975 |  | 88.2657 | 179.2291 | 12.3206 | 48.5334 | 13.4581 | 218 | 60.4944 | 69.3083 | 111.1698 | 0.046399
14803 | 998.5338 | 3.8953 | 24.8862 | 97.6311 | -11.6382 | 11.4 | 64.0963 | 1.9959 |  | 18.0773 | 51.9038 | 15.0669 |  | 65.8736 | 172.2483 | 9.8314 | 44.7183 | 7.7057 | 196 | 49.7423 | 64.6267 | 97.4759 | 0
14804 | 968.2905 | 3.8428 | 23.5153 | 95.5447 | -11.6367 | 11.4 | 67.5711 | 2.4873 |  | 18.3959 | 46.5549 | 12.329 |  | 59.003 | 162.0306 | 9.6366 | 43.3194 | 4.9441 | 177 | 46.6729 | 61.692 | 95.595 | 0
14805 | 932.3695 | 4.0103 | 23.4997 | 94.8854 | -12.6337 | 12.3497 | 63.2739 | 2.2673 |  | 16.8315 | 45.0682 | 9.6983 |  | 55.1563 | 155.4443 | 9.1865 | 42.8711 | 4.745 | 181 | 38.7458 | 58.7513 | 87.4624 | 0
14806 | 904.1237 | 3.4557 | 23.0682 | 94.5944 | -13.6325 | 13.2997 | 60.7916 | 1.765 |  | 14.658 | 43.8259 | 9.4347 |  | 52.5471 | 150.0485 | 8.659 | 42.8364 | 4.7845 | 165 | 35.7738 | 58.8939 | 91.9887 | 0
14807 | 337.1527 | 0 | 8.0656 | 0 | 0.17763 | 0.003696 | 23.551 | 0.70419 |  | 5.5247 | 17.8393 | 3.8747 |  | 0 | 0 | 2.9659 | 0 | 1.9163 | 155 | 3.8304 | 8.9669 | 10.6573 | 0
14808 | 882.4192 | 2.109 | 22.4235 | 94.4839 | -12.6315 | 12.3503 | 60.5543 | 2.363 |  | 13.0177 | 43.377 | 8.8132 |  | 50.0934 | 150.6727 | 9.0436 | 42.8396 | 4.8637 | 136 | 35.1179 | 74.7117 | 95.6763 | 0
14809 | 885.5441 | 2.2258 | 22.928 | 94.0603 | -9.6313 | 9.5008 | 60.7117 | 2.5175 |  | 12.849 | 42.9012 | 8.3244 |  | 49.1625 | 140.6902 | 9.0861 | 43.2879 | 4.4091 | 127 | 37.8513 | 70.9037 | 92.4885 | 0
14810 | 876.7694 | 2.1955 | 23.1807 | 94.1161 | -10.6322 | 10.4497 | 53.2146 | 2.5247 |  | 12.8372 | 42.2023 | 7.9251 |  | 46.4981 | 133.8589 | 9.9779 | 42.8123 | 4.0578 | 143 | 41.9773 | 77.4162 | 91.711 | 0
14811 | 868.4874 | 2.1771 | 22.8115 | 94.1041 | -10.6337 | 10.45 | 60.0506 | 2.3322 |  | 12.7812 | 42.7908 | 7.7662 |  | 44.5689 | 133.6202 | 9.404 | 42.0719 | 4.2099 | 148 | 38.4143 | 78.726 | 91.6646 | 0
14812 | 864.816 | 2.7328 | 22.5533 | 94.0734 | -11.6367 | 11.3997 | 63.1781 | 2.7092 |  | 12.7943 | 42.7379 | 7.7243 |  | 44.8498 | 131.6772 | 8.9101 | 41.8564 | 4.3948 | 119 | 40.6828 | 74.4786 | 89.7325 | 0
14813 | 861.5221 | 3.4886 | 24.8568 | 94.4013 | -10.6375 | 10.4503 | 58.6784 | 2.221 |  | 12.926 | 44.5186 | 7.6693 |  | 45.7024 | 131.907 | 8.6503 | 41.9 | 4.1175 | 111 | 37.5675 | 72.134 | 90.8657 | 0
14814 | 872.3625 | 3.768 | 38.9272 | 95.8491 | -12.6353 | 12.3495 | 61.8823 | 2.5816 |  | 11.4733 | 47.5019 | 6.4575 |  | 44.416 | 126.9829 | 8.8994 | 41.6911 | 3.3477 | 112 | 37.9584 | 61.7832 | 87.7846 | 0
14815 | 887.7417 | 3.3287 | 48.9923 | 95.0652 | -12.6364 | 12.35 | 59.2078 | 2.0948 |  | 10.3744 | 47.1927 | 5.5406 |  | 43.1082 | 124.0875 | 8.1867 | 41.6225 | 2.6723 | 118 | 44.9338 | 68.7445 | 85.8019 | 0.063302
14816 | 909.5229 | 2.3699 | 56.3867 | 94.2818 | -11.6391 | 11.4003 | 56.4839 | 2.1743 |  | 10.3666 | 43.2979 | 8.198 |  | 43.3704 | 121.1897 | 8.8362 | 41.7354 | 2.4836 | 120 | 44.6833 | 75.1655 | 86.4585 | 0.22729
14817 | 940.9181 | 2.1297 | 63.3517 | 94.3377 | -12.6397 | 12.3497 | 58.0742 | 2.5874 |  | 10.4119 | 43.9003 | 10.3261 |  | 50.9178 | 121.5147 | 8.825 | 42.0524 | 4.7791 | 130 | 40.0364 | 77.4435 | 86.876 | 0.26826
14818 | 954.5064 | 2.4796 | 62.5159 | 95.2456 | -10.6401 | 10.4505 | 58.8399 | 2.028 |  | 10.4371 | 48.3887 | 11.1171 |  | 58.5692 | 132.9238 | 8.4608 | 42.1136 | 9.721 | 142 | 30.695 | 74.0491 | 93.9976 | 0.27568
14819 | 954.9953 | 2.1985 | 61.3867 | 95.1699 | -11.6356 | 11.3997 | 63.3298 | 1.531 |  | 11.1613 | 50.4024 | 10.2836 |  | 62.8936 | 144.7095 | 8.5797 | 42.2404 | 12.0261 | 142 | 40.1867 | 74.2751 | 98.5871 | 0.25983
14820 | 953.8352 | 2.6752 | 61.5708 | 95.8251 | -10.6383 | 10.4503 | 68.3516 | 2.0942 |  | 11.6677 | 51.1503 | 9.1407 |  | 62.1033 | 144.6399 | 8.6425 | 42.2371 | 12.0261 | 141 | 56.7004 | 73.569 | 95.954 | 0.27976
14821 | 947.0027 | 4.682 | 58.8247 | 96.7782 | -11.6393 | 11.3997 | 72.4269 | 2.8135 |  | 11.667 | 52.75 | 9.2745 |  | 62.8683 | 153.8098 | 8.5324 | 42.6311 | 12.2409 | 146 | 58.2844 | 66.1626 | 96.058 | 0.24807
14822 | 944.6857 | 4.7811 | 36.0536 | 97.7968 | -10.6373 | 10.4503 | 76.2128 | 2.9399 |  | 11.6486 | 53.2741 | 10.0864 |  | 65.7277 | 156.5718 | 8.5524 | 42.7007 | 10.0563 | 162 | 48.5148 | 68.9441 | 93.1735 | 0.20178
14823 | 937.7341 | 2.8267 | 22.7051 | 98.1982 | -9.6352 | 9.5003 | 70.1177 | 3.561 |  | 13.1027 | 53.334 | 10.9346 |  | 66.7921 | 158.1524 | 8.3951 | 42.5415 | 6.1174 | 167 | 40.9117 | 73.0109 | 92.1943 | 0.14996
14824 | 929.8464 | 3.5403 | 22.24 | 98.1227 | -11.6366 | 11.3995 | 60.5037 | 3.4575 |  | 13.8376 | 52.3496 | 11.3373 |  | 68.0099 | 162.5962 | 8.038 | 42.5766 | 4.4694 | 179 | 33.565 | 72.8557 | 92.4255 | 0.10378
14825 | 931.9065 | 3.9923 | 22.5204 | 98.7315 | -12.6394 | 12.3497 | 56.6894 | 3.6453 |  | 14.2824 | 50.8282 | 13.5918 |  | 68.4462 | 166.9921 | 8.6931 | 42.6126 | 4.5372 | 198 | 34.7958 | 65.6213 | 96.9026 | 0.048962
14826 | 911.7721 | 3.6955 | 22.0825 | 98.5216 | -10.6393 | 10.4505 | 61.3555 | 2.9391 |  | 13.2139 | 46.538 | 14.3458 |  | 67.8474 | 159.3298 | 8.0257 | 42.4382 | 4.1372 | 205 | 33.1744 | 63.7826 | 95.5659 | 0.019813
14827 | 892.4312 | 4.3089 | 21.9196 | 96.4672 | -10.6402 | 10.45 | 61.2908 | 2.1482 |  | 11.7422 | 44.0189 | 12.1704 |  | 66.7313 | 151.2278 | 9.0652 | 42.219 | 3.7541 | 200 | 32.1622 | 58.821 | 98.9313 | 0
14828 | 882.335 | 4.3212 | 22.083 | 94.3191 | -12.6372 | 12.3495 | 57.5753 | 2.4069 |  | 12.3727 | 44.7878 | 10.5919 |  | 65.2228 | 147.3751 | 8.3793 | 42.3928 | 4.6083 | 211 | 32.3209 | 55.3734 | 104.911 | 0
14829 | 874.7471 | 5.706 | 22.7089 | 93.5358 | -12.6366 | 12.35 | 60.1436 | 2.1023 |  | 13.0663 | 45.2795 | 10.3674 |  | 61.6089 | 149.6027 | 9.2596 | 42.7792 | 10.0798 | 198 | 30.5383 | 59.2474 | 99.7632 | 0
14830 | 861.272 | 7.1294 | 22.7637 | 93.829 | -13.6348 | 13.2997 | 59.472 | 2.4422 |  | 12.9575 | 43.2807 | 9.3281 |  | 61.0252 | 139.265 | 8.6766 | 42.991 | 12.9154 | 201 | 38.1319 | 61.3639 | 92.8299 | 0
14831 | 324.8033 | 0 | 8.0535 | 0 | 0.17846 | 0.003696 | 22.1584 | 1.1475 |  | 5.0931 | 17.6759 | 3.3979 |  | 0 | 0 | 2.7279 | 0 | 5.0735 | 191 | 4.2116 | 9.3971 | 9.2454 | 0
14832 | 847.5527 | 6.1867 | 22.3005 | 93.903 | -10.6328 | 10.4497 | 54.0573 | 2.2059 |  | 12.2553 | 41.2725 | 7.9033 |  | 56.1953 | 146.4812 | 9.1182 | 42.8189 | 12.6883 | 201 | 42.6263 | 75.158 | 89.2204 | 0
14833 | 850.1216 | 4.4166 | 22.1775 | 93.782 | -11.6337 | 11.3997 | 57.874 | 2.4286 |  | 12.272 | 41.5585 | 10.1846 |  | 48.0147 | 143.024 | 8.713 | 42.6161 | 12.4094 | 207 | 42.7745 | 66.9212 | 91.16 | 0
14834 | 842.9987 | 2.4247 | 22.2979 | 93.7988 | -10.636 | 10.4503 | 60.3962 | 2.1674 |  | 12.2971 | 42.4149 | 9.5173 |  | 47.7294 | 138.0022 | 8.7021 | 42.6771 | 12.2095 | 195 | 48.3909 | 71.596 | 95.1661 | 0
14835 | 832.8954 | 2.1828 | 22.5183 | 93.8637 | -11.635 | 11.3997 | 59.4841 | 2.7039 |  | 12.3216 | 43.0244 | 7.5967 |  | 46.1721 | 134.9414 | 9.9284 | 42.4068 | 8.338 | 175 | 45.9066 | 74.3978 | 96.0527 | 0
14836 | 829.6252 | 2.7731 | 22.5244 | 94.0546 | -12.6354 | 12.3497 | 61.0295 | 3.0319 |  | 12.3962 | 42.5651 | 7.2878 |  | 44.1773 | 128.0961 | 9.6942 | 42.2371 | 4.5121 | 149 | 47.9074 | 78.2355 | 95.7919 | 0
14837 | 833.0494 | 3.5179 | 22.5719 | 93.9337 | -11.6355 | 11.4003 | 59.6141 | 2.2961 |  | 12.5212 | 41.9243 | 8.5247 |  | 44.3371 | 122.0131 | 8.4692 | 42.6228 | 3.497 | 135 | 48.9541 | 71.1337 | 96.2356 | 0
14838 | 848.9231 | 3.6004 | 22.067 | 93.8168 | -13.634 | 13.2995 | 60.7931 | 2.4692 |  | 10.8525 | 40.9071 | 6.6311 |  | 42.6623 | 123.8225 | 8.8288 | 41.9153 | 2.8392 | 131 | 42.8265 | 53.6966 | 88.4024 | 0
14839 | 860.3817 | 2.6135 | 22.0597 | 94.0878 | -11.6376 | 11.4005 | 57.644 | 1.9496 |  | 9.6752 | 43.3262 | 4.7766 |  | 42.253 | 125.4831 | 8.2303 | 41.3231 | 2.4199 | 126 | 36.8464 | 68.9652 | 83.8094 | 0.047362
14840 | 862.8715 | 1.891 | 22.3004 | 94.225 | -12.6385 | 12.3497 | 54.831 | 2.2643 |  | 9.5841 | 45.2935 | 5.0179 |  | 44.6522 | 121.9595 | 8.3772 | 41.3186 | 2.3638 | 141 | 28.941 | 74.0231 | 84.1482 | 0.075522
14841 | 875.4352 | 2.0226 | 22.9788 | 94.5963 | -11.641 | 11.4003 | 56.5337 | 2.8595 |  | 9.5334 | 44.5489 | 4.9694 |  | 50.0483 | 118.5291 | 8.443 | 41.878 | 2.37 | 172 | 29.2551 | 72.1833 | 83.4642 | 0.11881
14842 | 904.8532 | 2.1793 | 23.3652 | 96.4372 | -10.6396 | 10.4503 | 57.6175 | 3.0315 |  | 9.7966 | 47.6372 | 4.7768 |  | 57.0476 | 119.8351 | 8.2731 | 43.468 | 2.408 | 196 | 22.5048 | 70.3662 | 86.1239 | 0.17947
14843 | 923.358 | 2.4735 | 22.5595 | 96.1565 | -10.6349 | 10.45 | 62.5941 | 3.43 |  | 10.2654 | 50.1216 | 4.9603 |  | 61.6659 | 123.8629 | 8.2752 | 44.222 | 2.4197 | 180 | 21.9176 | 71.7019 | 88.4299 | 0.15859
14844 | 926.3332 | 6.0214 | 22.1318 | 95.9281 | -10.6376 | 10.45 | 65.973 | 3.1292 |  | 10.4677 | 49.726 | 5.2804 |  | 62.1703 | 129.2939 | 8.7979 | 43.4854 | 2.5276 | 200 | 20.0532 | 65.3059 | 85.8362 | 0.14648
14845 | 914.319 | 5.0679 | 22.1445 | 96.3836 | -9.6394 | 9.5003 | 62.9386 | 2.6811 |  | 10.5353 | 50.0321 | 6.2635 |  | 62.2616 | 140.2294 | 8.2258 | 43.2652 | 3.0585 | 179 | 19.8196 | 70.1467 | 84.2208 | 0.089347
14846 | 891.6052 | 2.2768 | 21.7934 | 97.2223 | -10.6354 | 10.4497 | 52.4863 | 2.4516 |  | 10.8071 | 49.6863 | 8.4935 |  | 63.6101 | 144.8119 | 9.2217 | 44.0355 | 9.4294 | 187 | 29.4082 | 76.7387 | 86.6114 | 0.1158
14847 | 889.5429 | 2.3618 | 18.0575 | 96.6511 | -12.6332 | 12.3495 | 53.1949 | 2.0034 |  | 11.2136 | 50.0897 | 9.3536 |  | 66.2844 | 150.4622 | 8.5085 | 43.9263 | 13.8304 | 205 | 31.8264 | 76.8447 | 87.257 | 0.15401
14848 | 891.0487 | 2.8252 | 16.0775 | 95.8042 | -9.6354 | 9.5008 | 57.9757 | 1.802 |  | 11.9014 | 51.5768 | 8.3574 |  | 61.7883 | 151.5471 | 8.5348 | 43.547 | 13.9629 | 192 | 34.8884 | 76.7214 | 87.1717 | 0.11646
14849 | 903.1484 | 2.6775 | 17.411 | 95.9966 | -12.6381 | 12.3492 | 60.56 | 0 |  | 11.7638 | 51.8748 | 8.4772 |  | 60.262 | 153.4443 | 8.1003 | 43.2335 | 11.897 | 182 | 38.5746 | 64.03 | 85.3976 | 0.040854
14850 | 906.2322 | 6.5518 | 17.4886 | 95.8018 | -9.6402 | 9.5008 | 59.3996 | 1.5824 |  | 11.6149 | 51.564 | 8.7737 |  | 56.902 | 144.9182 | 8.3018 | 43.4051 | 6.7318 | 154 | 37.3339 | 55.3602 | 83.9688 | 0.023228
14851 | 886.3913 | 9.3146 | 17.1376 | 96.1702 | -10.6399 | 10.4497 | 57.6624 | 2.1531 |  | 12.0917 | 50.8397 | 6.6178 |  | 52.4139 | 137.5812 | 8.7405 | 42.9393 | 4.1703 | 125 | 38.4578 | 60.8993 | 88.4524 | 0
14852 | 859.1228 | 6.6625 | 17.425 | 95.754 | -12.6396 | 12.3495 | 58.3254 | 2.0953 |  | 12.9948 | 48.2295 | 6.7543 |  | 51.9589 | 130.7014 | 8.3316 | 43.1729 | 4.3508 | 127 | 35.5342 | 61.5477 | 90.7752 | 0
14853 | 849.08 | 4.3381 | 17.3155 | 94.5839 | -10.6338 | 10.4505 | 61.7864 | 1.9336 |  | 13.4282 | 44.8855 | 7.3733 |  | 50.3903 | 126.1351 | 8.4104 | 43.4296 | 4.1438 | 123 | 30.1384 | 60.7296 | 87.5728 | 0
14854 | 844.4842 | 3.3914 | 17.1934 | 94.2084 | -11.6323 | 11.3997 | 58.9147 | 2.5836 |  | 13.5899 | 42.3408 | 7.4586 |  | 49.4432 | 122.484 | 8.9526 | 43.5969 | 3.4862 | 120 | 30.8395 | 62.1866 | 89.7867 | 0
14855 | 0 | 0 | 0 | 0 | 0.18086 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0
14856 | 821.1334 | 2.2001 | 16.8677 | 94.9519 | -10.6323 | 10.45 | 59.1235 | 2.215 |  | 14.3234 | 40.6856 | 7.3701 |  | 43.7044 | 118.8457 | 8.8369 | 43.2239 | 2.7858 | 115 | 29.6456 | 75.9754 | 89.0673 | 0
14857 | 824.5519 | 2.1033 | 16.8592 | 94.3067 | -11.6321 | 11.3997 | 60.8334 | 2.2853 |  | 14.943 | 41.6888 | 7.2581 |  | 43.3687 | 118.4926 | 9.0805 | 43.0916 | 2.6179 | 112 | 30.1427 | 81.38 | 89.0669 | 0
14858 | 819.8387 | 2.3646 | 16.8023 | 94.3026 | -10.6323 | 10.4503 | 63.2942 | 1.889 |  | 14.92 | 42.0028 | 7.2502 |  | 43.2056 | 121.5382 | 8.4447 | 43.271 | 2.598 | 115 | 28.9779 | 81.993 | 89.8716 | 0
14859 | 811.6427 | 4.5172 | 16.4453 | 95.3554 | -10.6353 | 10.45 | 65.561 | 2.3954 |  | 15.067 | 41.8294 | 7.3219 |  | 42.5065 | 120.1993 | 9.137 | 43.2122 | 2.4444 | 113 | 27.2242 | 82.2474 | 88.9249 | 0
14860 | 808.6082 | 5.3233 | 16.6526 | 94.5213 | -13.6345 | 13.2992 | 66.2605 | 2.169 |  | 15.9299 | 42.2917 | 7.2601 |  | 44.9597 | 117.3132 | 9.1523 | 42.9416 | 2.4201 | 111 | 34.0289 | 78.3872 | 97.5347 | 0
14861 | 825.0692 | 4.3778 | 25.5827 | 93.8574 | -12.6375 | 12.3503 | 61.8792 | 2.6932 |  | 18.7874 | 44.9875 | 9.599 |  | 50.2787 | 120.1652 | 8.5908 | 42.8484 | 3.7833 | 110 | 29.0099 | 68.9877 | 106.2324 | 0
14862 | 874.3715 | 4.9403 | 38.929 | 99.5709 | -11.6397 | 11.4003 | 68.9321 | 2.5292 |  | 23.0975 | 47.8827 | 12.8507 |  | 70.8652 | 133.3158 | 12.1799 | 42.54 | 8.7907 | 237 | 37.7844 | 57.9608 | 127.2386 | 0
14863 | 932.2307 | 10.7095 | 60.4919 | 106.9306 | -18.3305 | 18.0482 | 86.7713 | 3.4638 |  | 29.9185 | 58.115 | 19.3528 |  | 110.4076 | 172.3786 | 26.6615 | 45.2505 | 12.5027 | 283 | 51.5921 | 90.5603 | 155.271 | 0.11128
14864 | 1007.7259 | 15.7318 | 94.518 | 117.6996 | -19.3643 | 18.9997 | 105.4367 | 4.4891 |  | 39.646 | 68.0598 | 29.2668 |  | 141.1901 | 238.388 | 37.3974 | 49.9754 | 13.8913 | 306 | 56.0942 | 104.1533 | 197.8243 | 0.13087
14865 | 1111.4707 | 15.3238 | 111.1776 | 132.1521 | -21.6445 | 20.8995 | 127.5827 | 5.3788 |  | 43.6763 | 75.65 | 38.9873 |  | 161.423 | 296.8246 | 42.0385 | 54.3088 | 14.8949 | 362 | 61.7742 | 110.5818 | 236.9977 | 0.12259
14866 | 1193.4352 | 12.7105 | 110.5945 | 138.8918 | -21.6443 | 20.9 | 135.2307 | 5.4164 |  | 41.6771 | 81.224 | 43.1518 |  | 174.3816 | 328.4204 | 42.9937 | 49.3315 | 16.2165 | 394 | 68.1223 | 115.7722 | 242.762 | 0.26486
14867 | 1243.2395 | 9.0477 | 106.5476 | 140.2442 | -20.6464 | 19.9503 | 133.4362 | 5.2044 |  | 43.002 | 82.4696 | 41.5217 |  | 188.3804 | 342.2963 | 43.0083 | 47.0252 | 17.3659 | 350 | 66.2927 | 126.7429 | 239.2343 | 0.24592
14868 | 1229.1768 | 6.045 | 113.3929 | 139.6725 | -20.648 | 19.95 | 129.8198 | 6.1433 |  | 38.7067 | 83.7732 | 42.6057 |  | 196.5652 | 335.7367 | 42.6241 | 46.2986 | 18.1299 | 378 | 67.6206 | 115.9666 | 243.6698 | 0.18655
14869 | 1216.5408 | 4.8623 | 114.6766 | 141.4256 | -23.6402 | 22.7992 | 129.5727 | 6.4673 |  | 40.2493 | 84.4297 | 44.4159 |  | 192.0757 | 323.9639 | 43.3382 | 44.9305 | 18.8617 | 329 | 79.1101 | 123.7575 | 245.1785 | 0.25924
14870 | 1191.0186 | 4.6183 | 113.9698 | 147.3121 | -19.4357 | 19.0011 | 134.7227 | 5.5206 |  | 42.6834 | 86.4024 | 41.5003 |  | 190.0095 | 316.1505 | 42.5586 | 44.6252 | 18.9827 | 276 | 81.468 | 119.5958 | 220.2557 | 0.21732
14871 | 1156.8509 | 4.3747 | 114.1384 | 143.3421 | -16.4058 | 16.1508 | 136.1102 | 4.7031 |  | 36.0748 | 86.0275 | 33.7292 |  | 187.8805 | 307.1581 | 40.9578 | 43.315 | 18.7102 | 278 | 75.4677 | 115.7582 | 214.1971 | 0.12534
14872 | 1104.8021 | 4.4821 | 111.6543 | 132.2008 | -11.2093 | 11.4013 | 119.1583 | 5.0667 |  | 33.3422 | 79.7875 | 22.2632 |  | 179.8101 | 270.8631 | 31.7253 | 42.0521 | 18.52 | 266 | 74.4993 | 108.7499 | 211.7301 | 0.07503
14873 | 1055.9484 | 4.6063 | 104.5486 | 122.5751 | -10.1909 | 10.4503 | 87.354 | 3.9854 |  | 26.3132 | 65.3047 | 15.9744 |  | 146.982 | 215.9845 | 16.8464 | 38.5006 | 17.8651 | 228 | 53.6585 | 91.2943 | 157.7322 | 0.02966
14874 | 998.284 | 3.6364 | 88.2641 | 110.4728 | -8.4281 | 8.5505 | 77.0652 | 2.9978 |  | 17.588 | 56.3096 | 14.4219 |  | 99.5924 | 183.8202 | 11.729 | 33.6937 | 14.0333 | 224 | 49.8775 | 76.6546 | 124.0447 | 0.017252
14875 | 962.3298 | 3.9218 | 65.8726 | 105.526 | -9.5393 | 9.4997 | 86.821 | 3.2153 |  | 15.1532 | 55.068 | 10.5258 |  | 77.0056 | 171.3157 | 10.7691 | 28.5281 | 7.7984 | 215 | 50.3006 | 70.119 | 103.6324 | 0
14876 | 936.2979 | 4.6017 | 35.6492 | 101.4951 | -8.6372 | 8.5503 | 85.8166 | 2.353 |  | 17.3197 | 55.0123 | 7.4573 |  | 67.7775 | 162.8818 | 10.0003 | 26.9422 | 4.8179 | 204 | 51.5237 | 64.9663 | 103.1452 | 0
14877 | 921.351 | 4.248 | 23.6388 | 98.137 | -8.6367 | 8.55 | 72.9125 | 2.5761 |  | 17.4115 | 52.7785 | 8.1286 |  | 61.3767 | 152.8135 | 9.9384 | 28.6478 | 4.5762 | 196 | 42.5639 | 62.7813 | 98.1747 | 0
14878 | 891.1351 | 3.3818 | 23.2889 | 96.1259 | -9.6378 | 9.5024 | 62.6277 | 2.254 |  | 15.6951 | 47.2806 | 8.0139 |  | 56.2813 | 140.5196 | 9.9139 | 30.0832 | 4.3626 | 156 | 37.6795 | 60.5055 | 97.7734 | 0
14879 | 0 | 0 | 0 | 0 | 0.17744 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0
14880 | 860.8644 | 5.7732 | 23.3666 | 97.3957 | -8.631 | 8.55 | 55.614 | 2.221 |  | 15.2967 | 43.5571 | 6.6484 |  | 46.5265 | 130.785 | 8.737 | 28.8511 | 4.4253 | 126 | 38.0354 | 62.1843 | 95.2975 | 0
14881 | 854.6395 | 8.812 | 23.2478 | 96.2911 | -9.5738 | 9.4997 | 59.0987 | 2.7039 |  | 15.663 | 43.0495 | 6.7371 |  | 44.1399 | 125.0561 | 8.9819 | 28.7913 | 3.5943 | 123 | 33.4066 | 61.3205 | 93.7098 | 0
14882 | 851.421 | 9.2642 | 35.1614 | 95.4785 | -8.5805 | 8.5503 | 57.3454 | 2.3456 |  | 15.6847 | 43.5247 | 6.6516 |  | 44.598 | 122.9081 | 9.7058 | 27.9054 | 2.98 | 120 | 36.5142 | 66.0919 | 93.3448 | 0
14883 | 845.2196 | 5.4946 | 42.0129 | 94.918 | -8.415 | 8.55 | 60.5179 | 2.4471 |  | 15.7532 | 44.023 | 6.5431 |  | 44.1061 | 122.8667 | 9.5387 | 27.5349 | 2.8974 | 121 | 34.7356 | 70.0757 | 94.8619 | 0
14884 | 844.8825 | 2.9152 | 41.5476 | 94.7913 | -9.4398 | 9.4997 | 61.7235 | 2.1692 |  | 16.5939 | 47.788 | 6.5478 |  | 43.7624 | 119.9613 | 9.8011 | 27.6133 | 2.8982 | 116 | 35.8006 | 70.3431 | 104.6371 | 0
14885 | 867.212 | 3.5984 | 36.6026 | 95.698 | -8.6332 | 8.5503 | 61.9613 | 2.4726 |  | 20.3539 | 50.7926 | 9.907 |  | 48.4596 | 122.2597 | 8.8779 | 27.5905 | 3.0304 | 110 | 37.7009 | 64.6681 | 114.8587 | 0
14886 | 899.8699 | 4.5836 | 42.1534 | 102.0644 | -9.6358 | 9.4997 | 71.8366 | 2.1914 |  | 25.4218 | 52.1269 | 15.3339 |  | 68.4451 | 132.9475 | 12.9183 | 27.2156 | 5.7868 | 194 | 39.1111 | 60.9822 | 134.7773 | 0
14887 | 962.7524 | 8.7253 | 65.8517 | 109.4718 | -16.1898 | 16.1482 | 88.7935 | 3.6613 |  | 27.3558 | 61.1302 | 24.3612 |  | 112.3057 | 184.5452 | 25.4355 | 29.3853 | 10.7086 | 276 | 55.0275 | 87.5589 | 167.2678 | 0.049502
14888 | 1045.6594 | 11.7846 | 94.3975 | 118.4313 | -15.6002 | 16.15 | 115.3418 | 4.7732 |  | 31.1569 | 71.8922 | 35.1887 |  | 151.118 | 251.4114 | 34.35 | 34.9903 | 13.5556 | 309 | 61.5292 | 106.8926 | 207.7078 | 0.10158
14889 | 1119.2082 | 13.9912 | 107.5158 | 131.5417 | -17.274 | 18.0495 | 137.9437 | 4.562 |  | 37.8356 | 78.0244 | 40.0023 |  | 173.5625 | 291.7566 | 38.9459 | 41.4725 | 14.5769 | 393 | 57.8203 | 116.7479 | 237.3431 | 0.19804
14890 | 1178.3123 | 15.6206 | 110.1883 | 133.4736 | -18.9711 | 19.9495 | 153.2655 | 4.6687 |  | 40.1554 | 82.5474 | 41.4628 |  | 184.3315 | 311.412 | 41.3498 | 42.3196 | 16.2853 | 360 | 63.7076 | 125.4711 | 236.9955 | 0.086204
14891 | 1193.1693 | 14.7776 | 119.0834 | 130.9978 | -15.8533 | 17.1008 | 156.5436 | 5.1017 |  | 41.5205 | 84.5595 | 39.4707 |  | 194.7197 | 320.2224 | 41.5747 | 41.3025 | 17.6188 | 350 | 64.1767 | 142.733 | 216.341 | 0.13927
14892 | 1194.5222 | 13.2723 | 120.4328 | 134.5087 | -13.7834 | 15.2005 | 149.5619 | 5.764 |  | 39.8945 | 85.832 | 37.164 |  | 194.2455 | 311.9536 | 41.6117 | 39.1498 | 18.2682 | 343 | 59.9599 | 127.1436 | 212.6876 | 0.23568
14893 | 1179.0968 | 11.8657 | 120.595 | 136.9805 | -12.5065 | 14.2503 | 151.4978 | 5.5224 |  | 38.6259 | 87.256 | 37.8519 |  | 188.6081 | 298.2371 | 40.6819 | 39.0607 | 17.8627 | 298 | 72.2092 | 116.7903 | 208.8669 | 0.29409
14894 | 1172.254 | 9.3719 | 120.4187 | 139.3746 | -13.0837 | 15.1997 | 156.4049 | 4.7973 |  | 38.8347 | 87.6953 | 37.35 |  | 184.4136 | 298.6483 | 40.1051 | 39.7478 | 17.3295 | 275 | 77.5279 | 119.4663 | 211.1054 | 0.26299
14895 | 1147.3385 | 6.2707 | 119.014 | 135.1325 | -14.0105 | 16.1497 | 147.2447 | 4.6341 |  | 36.1539 | 87.8387 | 29.7215 |  | 180.34 | 299.4989 | 39.5535 | 38.9016 | 17.4785 | 289 | 74.8114 | 122.5091 | 191.6859 | 0.11514
14896 | 1108.0824 | 4.7995 | 113.8367 | 129.3915 | -9.249 | 11.4013 | 123.8706 | 4.4786 |  | 30.5006 | 80.6999 | 20.0944 |  | 173.6662 | 271.6199 | 32.0856 | 38.6486 | 17.2653 | 235 | 71.7991 | 110.3917 | 168.754 | 0.071549
14897 | 1052.9466 | 4.0649 | 107.7061 | 120.8448 | -5.5927 | 7.6011 | 85.7835 | 3.4178 |  | 23.6944 | 66.5065 | 15.9167 |  | 146.5293 | 227.9673 | 18.9052 | 37.1371 | 16.4094 | 212 | 61.1645 | 86.4668 | 134.6999 | 0.032916
14898 | 1031.3418 | 4.1618 | 88.8376 | 110.2936 | -6.064 | 7.6 | 68.6313 | 2.7311 |  | 16.6648 | 59.1835 | 15.7487 |  | 103.2519 | 198.6373 | 13.0529 | 34.0853 | 13.0834 | 207 | 52.3602 | 75.8251 | 119.7069 | 0.0046929
14899 | 1015.9513 | 5.2146 | 63.5493 | 106.5623 | -5.9979 | 6.6503 | 65.4964 | 2.0081 |  | 15.7768 | 59.0734 | 18.2275 |  | 84.4165 | 182.5336 | 11.7893 | 31.1011 | 7.7541 | 193 | 46.8014 | 70.4364 | 107.2963 | 0
14900 | 971.0603 | 7.0631 | 31.6588 | 101.6356 | -7.6342 | 7.5997 | 58.0576 | 1.6811 |  | 16.8504 | 58.876 | 18.6501 |  | 77.6875 | 168.3739 | 11.5021 | 30.0763 | 4.9416 | 181 | 41.5266 | 67.0216 | 98.375 | 0
14901 | 941.0305 | 7.7687 | 18.4308 | 96.8428 | -6.6344 | 6.6503 | 54.9546 | 2.5906 |  | 15.0463 | 55.4592 | 14.186 |  | 68.8751 | 150.8627 | 11.436 | 29.0712 | 4.4715 | 165 | 38.5406 | 63.8274 | 91.3321 | 0
14902 | 928.9824 | 6.3947 | 17.4718 | 95.5029 | -7.6351 | 7.5997 | 60.2107 | 2.2698 |  | 12.9892 | 49.2762 | 11.6046 |  | 62.9789 | 139.5784 | 10.5311 | 28.3779 | 4.4627 | 152 | 40.8008 | 66.6416 | 92.4209 | 0
14903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0
14904 | 896.8362 | 3.452 | 17.2327 | 94.1057 | -7.6297 | 7.5997 | 59.1276 | 2.1394 |  | 14.1978 | 46.1251 | 11.113 |  | 57.7072 | 130.5942 | 10.0105 | 27.925 | 4.534 | 133 | 37.4765 | 84.811 | 90.6376 | 0
14905 | 894.0483 | 7.11 | 17.5493 | 93.9655 | -7.6325 | 7.6 | 57.6855 | 2.5756 |  | 14.8952 | 45.0811 | 10.7622 |  | 56.2689 | 127.3105 | 11.4129 | 27.6609 | 3.9412 | 127 | 39.9678 | 78.6206 | 91.6411 | 0
14906 | 876.2699 | 8.502 | 29.342 | 94.0314 | -6.6348 | 6.6503 | 58.6398 | 2.273 |  | 14.8892 | 44.7318 | 10.7217 |  | 55.8188 | 126.8609 | 10.4915 | 27.5324 | 3.1274 | 122 | 33.5569 | 81.5768 | 88.1912 | 0
14907 | 874.1815 | 4.5756 | 35.7826 | 93.8104 | -7.6365 | 7.5997 | 56.133 | 2.4239 |  | 14.9577 | 44.508 | 10.6456 |  | 56.3694 | 123.3958 | 11.092 | 27.5236 | 2.7788 | 115 | 32.7698 | 89.4679 | 91.9034 | 0
14908 | 874.8622 | 2.6259 | 34.8986 | 93.8341 | -6.6404 | 6.6503 | 53.7038 | 2.1583 |  | 15.7417 | 44.34 | 10.6348 |  | 55.8973 | 116.1959 | 10.1914 | 27.466 | 2.7278 | 113 | 34.7387 | 89.2573 | 93.8302 | 0
14909 | 887.4441 | 3.6008 | 29.1758 | 93.7081 | -7.6391 | 7.5997 | 53.4384 | 2.4013 |  | 18.7335 | 46.853 | 12.6112 |  | 57.1407 | 121.267 | 10.4026 | 27.2569 | 2.8415 | 109 | 30.993 | 83.4924 | 105.6125 | 0
14910 | 938.6416 | 4.9149 | 36.3165 | 101.2642 | -21.6356 | 20.8963 | 69.2389 | 2.3975 |  | 20.2474 | 51.7491 | 14.6076 |  | 76.1545 | 134.8797 | 14.431 | 27.0822 | 5.7981 | 187 | 41.9522 | 70.2682 | 133.3989 | 0
14911 | 1029.0369 | 11.8184 | 61.7595 | 108.7465 | -26.6388 | 25.6487 | 93.6109 | 3.1463 |  | 25.4923 | 62.7617 | 20.5505 |  | 116.0685 | 181.9994 | 26.2314 | 29.3463 | 10.6373 | 243 | 59.9321 | 93.0045 | 158.3476 | 0.1426
14912 | 1123.8444 | 19.2484 | 90.3769 | 118.6186 | -25.6431 | 24.7003 | 107.1322 | 4.1917 |  | 34.6633 | 74.4055 | 33.2289 |  | 147.3707 | 236.3391 | 36.3019 | 34.1166 | 13.6185 | 274 | 71.4324 | 106.1814 | 178.4161 | 0.2293
14913 | 1204.4504 | 24.2431 | 106.6166 | 133.1137 | -23.6466 | 22.8005 | 116.2313 | 4.8879 |  | 37.8741 | 82.258 | 40.6035 |  | 168.2241 | 293.1176 | 39.9907 | 39.9414 | 15.9335 | 337 | 74.6221 | 114.8929 | 204.8004 | 0.2703
14914 | 1270.7679 | 24.9818 | 108.1444 | 138.2874 | -22.6472 | 21.8503 | 122.8864 | 5.1029 |  | 43.8636 | 91.4676 | 41.3514 |  | 178.6225 | 320.7755 | 41.7681 | 45.3479 | 17.4683 | 393 | 87.1369 | 122.2482 | 202.1667 | 0.26799
14915 | 0 | 16.1786 | 111.311 | 140.3999 | -24.6466 | 23.7495 | 125.1992 | 5.3397 |  | 47.7793 | 90.6805 | 39.8652 |  | 187.968 | 325.5212 | 41.5645 | 46.2787 | 18.2432 | 338 | 74.299 | 141.4684 | 211.4563 | 0.25358
14916 | 0 | 11.4703 | 117.9991 | 140.6076 | -21.6484 | 20.9008 | 130.5274 | 5.4151 |  | 44.4316 | 86.2281 | 37.5347 |  | 189.3947 | 320.9529 | 43.0204 | 44.8141 | 18.6074 | 337 | 69.6272 | 128.2414 | 212.4442 | 0.278
14917 | 1312.13 | 9.9956 | 117.8988 | 138.3641 | -21.6487 | 20.9 | 130.2253 | 6.0786 |  | 39.5296 | 89.954 | 39.4239 |  | 193.0973 | 315.9049 | 42.5167 | 43.1243 | 18.4956 | 294 | 72.8472 | 130.3662 | 204.4175 | 0.29972
14918 | 1312.1076 | 11.7479 | 116.8442 | 139.8076 | -19.6468 | 19.0005 | 133.8071 | 5.7289 |  | 36.2082 | 90.4437 | 38.8976 |  | 194.6538 | 318.0847 | 42.4556 | 43.1062 | 18.1641 | 298 | 73.6545 | 127.9323 | 205.3286 | 0.20714
14919 | 1282.3227 | 12.917 | 114.1577 | 136.772 | -20.6404 | 19.9497 | 127.5449 | 4.7193 |  | 33.0843 | 88.248 | 31.2529 |  | 190.0812 | 313.7463 | 38.2457 | 44.217 | 17.81 | 301 | 72.12 | 125.9584 | 195.8032 | 0.22545
14920 | 1227.1012 | 9.8628 | 109.2093 | 132.6483 | -13.6421 | 13.3018 | 102.9036 | 4.7897 |  | 28.8721 | 81.2116 | 19.4047 |  | 178.8614 | 282.0151 | 29.8471 | 43.2363 | 17.0681 | 276 | -0.017801 | 123.1733 | 182.905 | 0.22332
14921 | 1147.9889 | 7.5036 | 103.2532 | 123.7803 | -11.6436 | 11.4005 | 75.4256 | 3.676 |  | 23.845 | 64.6455 | 13.4554 |  | 139.57 | 242.3334 | 25.1098 | 39.593 | 16.7457 | 245 | 60.3869 | 100.4697 | 137.4918 | 0.14771
14922 | 1090.0461 | 6.0448 | 88.9075 | 110.5506 | -10.6415 | 10.4503 | 67.2155 | 3.0519 |  | 17.4862 | 55.9747 | 10.1905 |  | 95.1405 | 220.7238 | 17.7323 | 35.2397 | 13.219 | 234 | 56.8601 | 87.3558 | 119.3719 | 0.041679
14923 | 1059.81 | 4.8046 | 68.1042 | 102.5224 | -11.6359 | 11.3997 | 70.9118 | 2.5453 |  | 14.4866 | 55.4019 | 8.4047 |  | 71.1427 | 203.6733 | 11.4871 | 32.2882 | 10.9747 | 218 | 49.4902 | 80.2775 | 106.0696 | 0
14924 | 1025.1339 | 4.9992 | 43.8626 | 98.8104 | -12.6353 | 12.3497 | 66.3386 | 2.7557 |  | 15.661 | 55.6494 | 7.9549 |  | 62.1273 | 179.0572 | 9.8368 | 31.0488 | 12.6639 | 202 | 46.7 | 74.791 | 105.8374 | 0
14925 | 995.038 | 4.484 | 31.7389 | 96.7384 | -10.6375 | 10.4505 | 62.2591 | 2.4684 |  | 15.9257 | 52.8233 | 7.7562 |  | 57.4242 | 154.7199 | 10.5658 | 29.9947 | 13.1821 | 197 | 40.3796 | 72.2013 | 104.554 | 0
14926 | 957.2862 | 3.503 | 28.2381 | 95.6374 | -10.6357 | 10.45 | 57.6552 | 2.3959 |  | 15.1453 | 47.2798 | 7.8832 |  | 51.381 | 139.9819 | 10.5296 | 28.7944 | 12.926 | 171 | 35.2254 | 70.4384 | 102.0474 | 0
14927 | 376.7606 | 0 | 10.3338 | 0 | 0.18515 | 0 | 22.2558 | 1.094 |  | 6.1348 | 19.845 | 3.2555 |  | 0 | 0 | 3.8503 | 0 | 5.4088 | 158 | 4.831 | 13.2607 | 15.5628 | 0
14928 | 916.8632 | 2.2424 | 27.2003 | 95.0106 | -7.6331 | 7.6008 | 55.2388 | 2.4439 |  | 14.9975 | 42.87 | 7.087 |  | 45.6728 | 135.6052 | 10.7388 | 28.4658 | 12.5103 | 143 | 36.1547 | 77.4838 | 101.8838 | 0
14929 | 897.7801 | 2.4791 | 26.7486 | 95.5726 | -8.6297 | 8.5497 | 54.7651 | 2.642 |  | 15.6533 | 42.9153 | 7.2126 |  | 44.5487 | 134.7617 | 9.9331 | 28.4706 | 11.7766 | 115 | 31.8019 | 69.8991 | 97.3328 | 0
14930 | 879.2044 | 2.3208 | 27.414 | 95.3818 | -8.6326 | 8.55 | 54.1854 | 3.0372 |  | 15.7039 | 42.5584 | 7.1415 |  | 45.2586 | 133.9884 | 10.6294 | 28.4382 | 11.3933 | 117 | 32.4679 | 74.6217 | 96.8358 | 0
14931 | 865.7372 | 2.2589 | 27.167 | 94.8969 | -8.6309 | 8.55 | 63.4207 | 2.2425 |  | 15.7097 | 42.1126 | 6.9954 |  | 44.6371 | 129.0773 | 9.8266 | 28.3984 | 11.4449 | 112 | 34.3027 | 80.6239 | 98.7857 | 0
14932 | 877.5265 | 2.6659 | 26.7347 | 94.7932 | -8.6318 | 8.55 | 71.2853 | 2.6117 |  | 16.8144 | 41.7804 | 6.9617 |  | 43.7699 | 121.5984 | 10.7081 | 28.4931 | 11.4863 | 109 | 30.7753 | 77.9704 | 102.0876 | 0
14933 | 885.1713 | 3.6049 | 28.5327 | 95.0822 | -8.636 | 8.55 | 72.921 | 3.3648 |  | 22.5623 | 44.1953 | 8.9358 |  | 48.5113 | 125.0013 | 9.7798 | 28.3481 | 11.4121 | 111 | 32.6856 | 72.165 | 116.0062 | 0
14934 | 916.9705 | 7.5973 | 36.82 | 101.6805 | -8.6373 | 8.55 | 84.9348 | 3.2306 |  | 29.1931 | 48.2884 | 12.7613 |  | 74.5496 | 134.4721 | 12.5477 | 27.8244 | 13.6561 | 225 | 38.6639 | 66.7623 | 138.8943 | 0
14935 | 1028.8809 | 13.605 | 68.0806 | 113.6318 | -16.6395 | 16.1479 | 103.0809 | 3.8688 |  | 32.8595 | 63.6308 | 25.0566 |  | 126.3071 | 200.0616 | 28.3389 | 32.4518 | 16.7054 | 279 | 60.1422 | 95.9715 | 178.1895 | 0.016251
14936 | 0 | 0 | 0 | 0 | -19.9825 | 18.9834 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0.048376
14937 | 1177.2321 | 15.0847 | 99.8018 | 129.0696 | -18.6641 | 18.0661 | 118.4475 | 4.5969 |  | 41.2483 | 78.0536 | 34.8922 |  | 168.5481 | 277.544 | 39.7384 | 39.6758 | 18.9113 | 374 | 73.0402 | 119.2865 | 204.7813 | 0.087717
14938 | 1252.967 | 14.4568 | 108.6945 | 138.3494 | -19.6464 | 18.9997 | 131.2111 | 6.3109 |  | 45.5689 | 84.038 | 40.2586 |  | 181.6576 | 300.7129 | 42.5615 | 42.9327 | 18.7661 | 335 | 74.1592 | 122.5249 | 202.0688 | 0.068546
14939 | 1264.9288 | 13.0203 | 113.3637 | 135.8865 | -17.6419 | 17.1005 | 133.3124 | 5.7263 |  | 48.6528 | 86.7747 | 41.4328 |  | 187.5713 | 316.8672 | 41.6242 | 43.712 | 18.3614 | 322 | 66.0063 | 136.234 | 202.559 | 0.088155
14940 | 1264.2095 | 15.8732 | 116.6306 | 137.3597 | -19.6431 | 18.9995 | 134.9709 | 4.6426 |  | 44.494 | 87.6699 | 41.0875 |  | 183.4923 | 319.0544 | 40.9361 | 42.1766 | 18.2962 | 321 | 57.8801 | 128.2476 | 199.3155 | 0.11953
14941 | 1273.6499 | 15.5618 | 115.5681 | 137.5521 | -22.6464 | 21.8492 | 137.2865 | 4.5238 |  | 40.4386 | 90.4016 | 40.8455 |  | 177.7492 | 314.0403 | 39.5752 | 41.949 | 18.3312 | 280 | 63.9282 | 130.6181 | 191.6985 | 0.084428
14942 | 1273.8285 | 10.6254 | 115.1257 | 141.3081 | -21.6429 | 20.9003 | 134.2369 | 4.6514 |  | 38.5323 | 94.1157 | 39.5786 |  | 176.4414 | 314.1051 | 38.4942 | 41.8798 | 19.6945 | 266 | 67.1054 | 131.1088 | 192.0385 | 0.1383
14943 | 1238.2527 | 8.3001 | 113.6526 | 139.8785 | -17.6431 | 17.1011 | 126.7315 | 4.5892 |  | 33.3085 | 94.1196 | 33.133 |  | 171.9612 | 312.5062 | 37.2208 | 41.9378 | 19.4088 | 273 | 66.4528 | 125.9145 | 185.7843 | 0.092756
14944 | 1180.3688 | 7.4198 | 109.3179 | 131.8524 | -8.6482 | 8.5524 | 107.9061 | 4.1415 |  | 27.642 | 84.895 | 22.0791 |  | 160.911 | 289.4968 | 29.2214 | 41.3429 | 17.7027 | 265 | 60.5596 | 112.2468 | 171.654 | 0.03784
14945 | 1123.1765 | 5.2669 | 103.8804 | 121.6222 | -6.6417 | 6.6505 | 82.4648 | 3.2512 |  | 21.992 | 68.241 | 15.7824 |  | 129.3351 | 253.9937 | 18.4783 | 39.1318 | 17.245 | 238 | 54.339 | 92.4618 | 136.3863 | 0.019164
14946 | 1065.682 | 3.862 | 94.8347 | 108.7362 | -7.6379 | 7.5997 | 72.982 | 2.2721 |  | 14.8073 | 56.3436 | 12.4418 |  | 87.6934 | 222.6497 | 13.7493 | 34.7613 | 16.7957 | 212 | 50.4775 | 75.8412 | 111.4065 | 0.0071645
14947 | 1037.4227 | 4.7749 | 78.6473 | 102.5715 | -6.6393 | 6.6503 | 80.6214 | 2.4249 |  | 13.3635 | 54.5893 | 11.2667 |  | 71.8228 | 195.1453 | 12.317 | 31.2782 | 15.9872 | 186 | 49.4597 | 74.2828 | 100.0156 | 0
14948 | 1014.1135 | 4.8258 | 45.6694 | 100.8345 | -7.9997 | 7.5997 | 73.6133 | 2.3698 |  | 14.7182 | 55.9603 | 12.1019 |  | 69.8525 | 174.5307 | 10.0035 | 30.3995 | 14.857 | 179 | 45.0011 | 73.007 | 91.5314 | 0
14949 | 981.7323 | 4.2031 | 23.8321 | 97.8419 | -7.6336 | 7.6 | 60.642 | 2.2929 |  | 14.0648 | 52.6529 | 11.0304 |  | 60.117 | 155.3834 | 9.5247 | 29.8132 | 9.4594 | 174 | 40.2676 | 68.8234 | 90.6411 | 0
14950 | 959.6621 | 4.4588 | 23.4666 | 96.3558 | -7.7728 | 7.6 | 58.6534 | 2.9385 |  | 13.7344 | 46.7383 | 10.4824 |  | 53.071 | 141.8097 | 10.7246 | 28.9588 | 4.7671 | 154 | 41.5464 | 70.9961 | 88.9096 | 0
14951 | 467.7965 | 0 | 11.2368 | 0 | -0.002223 | 0 | 28.3312 | 1.5204 |  | 6.9108 | 23.265 | 5.2818 |  | 0 | 0 | 5.1312 | 0 | 2.486 | 135 | 9.6812 | 19.8509 | 20.4229 | 0
14952 | 906.438 | 2.6564 | 23.0192 | 96.511 | -7.6315 | 7.6003 | 64.4447 | 2.5822 |  | 14.9801 | 43.5284 | 10.5029 |  | 48.9682 | 125.8248 | 10.2255 | 28.4431 | 3.5111 | 119 | 32.5587 | 85.6614 | 88.9498 | 0
14953 | 906.7486 | 2.2512 | 22.9626 | 95.8111 | -8.6299 | 8.5497 | 70.4716 | 3.0514 |  | 15.3797 | 43.3911 | 10.4189 |  | 46.6236 | 124.6931 | 10.6092 | 29.0914 | 3.3555 | 115 | 34.5404 | 80.4488 | 89.0509 | 0
14954 | 900.0413 | 2.2738 | 22.7026 | 96.904 | -9.6284 | 9.4997 | 72.9489 | 2.8583 |  | 15.4252 | 43.3379 | 10.3683 |  | 45.2745 | 124.6142 | 9.3795 | 29.9048 | 3.1671 | 123 | 32.3465 | 76.6903 | 89.8103 | 0
14955 | 901.5348 | 2.2275 | 23.5798 | 96.9586 | -8.6318 | 8.5503 | 72.8022 | 2.3914 |  | 15.4002 | 47.1768 | 10.2566 |  | 44.7116 | 122.1801 | 10.3962 | 30.1345 | 3.0494 | 111 | 31.0264 | 81.883 | 88.8004 | 0
14956 | 915.7792 | 2.3459 | 24.0339 | 95.7727 | -8.0003 | 7.6003 | 62.5131 | 2.5855 |  | 16.2077 | 50.8395 | 10.1816 |  | 44.5842 | 120.1255 | 10.6298 | 29.225 | 2.9081 | 109 | 33.2682 | 82.657 | 96.0269 | 0
14957 | 932.4236 | 2.3711 | 31.7091 | 96.5976 | -8.6363 | 8.5497 | 57.7107 | 3.2729 |  | 20.5433 | 46.9068 | 12.1801 |  | 50.863 | 123.9103 | 9.0981 | 27.6518 | 3.0148 | 109 | 31.645 | 71.8759 | 104.7022 | 0
14958 | 984.4677 | 3.9233 | 51.7908 | 101.2595 | -8.639 | 8.55 | 77.7241 | 2.51 |  | 23.6267 | 48.1385 | 12.916 |  | 74.4597 | 140.9808 | 13.9274 | 27.298 | 7.0581 | 188 | 40.437 | 66.7155 | 126.3701 | 0
14959 | 1047.6054 | 12.5605 | 77.6853 | 109.4114 | -16.6413 | 16.1479 | 96.4093 | 2.9248 |  | 27.6878 | 61.138 | 15.894 |  | 113.7916 | 187.6402 | 23.5086 | 30.5539 | 13.1403 | 294 | 60.9412 | 86.6509 | 161.3599 | 0.08852
14960 | 1127.4352 | 22.5107 | 98.1483 | 122.404 | -32.6395 | 31.3458 | 105.2224 | 4.5349 |  | 34.456 | 75.5822 | 24.1139 |  | 146.4836 | 251.5574 | 28.7971 | 35.1246 | 15.2347 | 316 | 61.438 | 105.5536 | 190.2256 | 0.077071
14961 | 1210.7735 | 21.6427 | 109.2199 | 133.7175 | -28.6536 | 27.5587 | 114.7936 | 5.1078 |  | 39.3341 | 85.8038 | 31.479 |  | 163.6472 | 296.5752 | 30.3306 | 39.1062 | 15.7239 | 385 | 64.1422 | 114.7752 | 220.1095 | 0.06752
14962 | 1260.6029 | 13.1811 | 109.6742 | 138.8806 | -27.6354 | 26.5926 | 122.471 | 5.1989 |  | 41.262 | 90.883 | 35.9383 |  | 172.3161 | 319.0864 | 29.7409 | 43.0622 | 17.0808 | 338 | 71.0365 | 129.1458 | 225.1637 | 0.17793
14963 | 1276.9943 | 11.3996 | 111.5888 | 141.7589 | -23.6452 | 22.8011 | 136.8981 | 4.7399 |  | 42.5853 | 92.1286 | 35.4478 |  | 178.2377 | 319.2644 | 29.1432 | 43.4896 | 17.5447 | 330 | 62.9529 | 138.1336 | 226.5308 | 0.18272
14964 | 1271.5081 | 15.0797 | 114.6683 | 142.6534 | -20.6482 | 19.9508 | 145.4496 | 4.6968 |  | 43.2564 | 92.3675 | 33.0107 |  | 178.6672 | 317.0657 | 28.4039 | 41.4574 | 17.097 | 360 | 59.5678 | 126.5525 | 226.432 | 0.23871
14965 | 1258.9412 | 11.7903 | 115.4029 | 146.1515 | -21.6448 | 20.8997 | 142.868 | 5.1472 |  | 43.2031 | 92.4984 | 33.6458 |  | 176.0514 | 315.9055 | 28.0326 | 41.601 | 17.0637 | 308 | 63.9979 | 127.8936 | 212.922 | 0.079906
14966 | 1231.0283 | 6.693 | 117.187 | 144.2404 | -26.6418 | 25.6487 | 120.2371 | 5.3929 |  | 42.6278 | 91.3776 | 33.5197 |  | 172.9759 | 308.5772 | 28.7005 | 42.1569 | 17.0964 | 300 | 65.5062 | 131.4661 | 204.6348 | 0.28887
14967 | 1181.5167 | 4.8944 | 111.6035 | 133.9576 | -22.646 | 21.8511 | 84.4422 | 4.6558 |  | 35.5094 | 89.2837 | 26.6104 |  | 166.4616 | 292.2432 | 27.2752 | 41.4516 | 16.7772 | 294 | 71.8164 | 123.7461 | 181.948 | 0.24899
14968 | 1129.693 | 8.2952 | 103.4065 | 125.4538 | -20.6388 | 19.9505 | 70.0853 | 3.9654 |  | 26.4262 | 81.6732 | 17.9761 |  | 156.9824 | 260.8086 | 22.3093 | 47.217 | 16.4041 | 310 | 69.7326 | 112.8519 | 157.0941 | 0.20792
14969 | 1077.9294 | 12.0346 | 88.196 | 115.1266 | -11.6423 | 11.4024 | 65.8647 | 3.3454 |  | 20.8481 | 66.4112 | 13.6417 |  | 132.8464 | 219.1994 | 13.3845 | 51.6598 | 15.9223 | 267 | 64.7047 | 87.4121 | 127.4303 | 0.1641
14970 | 1040.9706 | 8.6479 | 58.0666 | 105.8026 | -12.6374 | 12.3497 | 65.1377 | 2.5537 |  | 16.9712 | 56.3182 | 11.9029 |  | 101.6159 | 189.9755 | 8.641 | 48.6446 | 12.7682 | 237 | 56.5928 | 74.0677 | 117.7031 | 0.041828
14971 | 999.9311 | 4.7102 | 36.9727 | 100.79 | -11.6333 | 11.4003 | 66.4052 | 2.7435 |  | 13.1065 | 51.6345 | 11.5244 |  | 77.6785 | 175.1771 | 9.3751 | 44.7114 | 7.1816 | 207 | 55.2195 | 67.5744 | 103.9304 | 0
14972 | 953.0848 | 7.8059 | 34.4575 | 98.2374 | -10.6372 | 10.4503 | 59.6407 | 2.46 |  | 12.2561 | 45.2793 | 11.3088 |  | 64.0104 | 165.6575 | 8.6936 | 42.6285 | 7.5879 | 187 | 51.6318 | 62.7654 | 101.3101 | 0
14973 | 932.6652 | 11.3759 | 34.5664 | 98.2956 | -11.635 | 11.3997 | 59.4869 | 2.284 |  | 12.1343 | 42.819 | 9.745 |  | 58.3248 | 158.8404 | 8.7681 | 42.6372 | 12.0678 | 195 | 46.6664 | 61.4445 | 99.7904 | 0
14974 | 915.1943 | 10.0948 | 33.428 | 97.5583 | -11.769 | 11.4 | 61.352 | 2.5101 |  | 12.5024 | 42.8792 | 9.5529 |  | 56.2255 | 149.1098 | 9.6282 | 42.6555 | 13.5037 | 186 | 40.4556 | 67.1546 | 100.7265 | 0
14975 | 464.9747 | 0 | 15.7644 | 46.2056 | -0.003334 | 0.003167 | 30.3737 | 1.0868 |  | 7.0346 | 23.6301 | 5.4459 |  | 27.3578 | 76.8598 | 4.6927 | 20.6493 | 7.1579 | 177 | 9.7319 | 20.5652 | 24.6848 | 0
14976 | 901.1531 | 8.6672 | 33.4151 | 96.2784 | -12.6314 | 12.3497 | 51.6443 | 3.0091 |  | 11.6574 | 42.4505 | 10.7363 |  | 50.5819 | 132.3026 | 9.6984 | 42.4881 | 12.2855 | 161 | 37.7386 | 86.8678 | 100.2552 | 0
14977 | 895.8167 | 4.7588 | 33.1848 | 96.3922 | -11.6338 | 11.4003 | 64.8711 | 2.7086 |  | 11.4808 | 42.6419 | 10.3586 |  | 48.2874 | 128.0074 | 9.2364 | 42.2448 | 11.6837 | 156 | 34.4438 | 81.2133 | 99.5693 | 0
14978 | 880.657 | 2.2476 | 33.2354 | 96.1141 | -11.6316 | 11.4 | 74.3752 | 2.37 |  | 11.3786 | 43.2425 | 10.5283 |  | 46.8404 | 124.7833 | 9.3409 | 42.2316 | 11.7022 | 153 | 35.3655 | 82.1818 | 101.7336 | 0
14979 | 866.9838 | 2.2848 | 32.7543 | 96.4964 | -10.6302 | 10.4503 | 76.027 | 2.7522 |  | 11.4709 | 43.5308 | 10.6027 |  | 45.7467 | 122.7594 | 9.0743 | 42.2627 | 11.6909 | 142 | 35.8225 | 85.9565 | 98.1994 | 0
14980 | 860.2371 | 2.8001 | 32.8134 | 96.6091 | -12.6309 | 12.3495 | 74.7656 | 3.0749 |  | 11.7359 | 43.1508 | 10.3456 |  | 45.2525 | 121.676 | 9.6331 | 42.3723 | 11.7063 | 144 | 35.915 | 88.5278 | 94.0929 | 0
14981 | 869.3064 | 5.4228 | 34.1279 | 96.3312 | -11.6331 | 11.4003 | 73.8819 | 2.8147 |  | 11.5957 | 44.4708 | 10.2966 |  | 45.2134 | 121.9719 | 9.2239 | 42.3017 | 11.7192 | 134 | 37.861 | 82.6845 | 93.3321 | 0
14982 | 880.7749 | 7.4626 | 39.7482 | 96.2693 | -12.6313 | 12.3497 | 70.8437 | 2.5321 |  | 11.4312 | 47.7451 | 9.9736 |  | 45.7117 | 124.8459 | 9.945 | 42.7011 | 11.7146 | 129 | 36.8089 | 67.2917 | 90.8584 | 0
14983 | 883.3135 | 4.5956 | 51.7316 | 96.0994 | -12.6372 | 12.35 | 59.3717 | 2.7054 |  | 11.2711 | 47.4298 | 9.643 |  | 46.4147 | 125.8251 | 9.7012 | 42.1647 | 11.7024 | 120 | 38.8307 | 68.5375 | 89.0092 | 0.025895
14984 | 911.1771 | 2.0522 | 61.5831 | 96.5286 | -14.6394 | 14.2495 | 47.3255 | 2.4699 |  | 10.9983 | 47.2565 | 9.3663 |  | 48.0944 | 126.7399 | 9.2505 | 41.5949 | 11.7939 | 117 | 41.6181 | 75.4245 | 92.2505 | 0.055202
14985 | 953.1668 | 2.3589 | 70.4095 | 96.9719 | -13.6368 | 13.3003 | 46.9465 | 2.0559 |  | 11.0578 | 50.0562 | 8.2602 |  | 53.189 | 131.889 | 9.5324 | 41.9021 | 12.0911 | 142 | 38.0282 | 77.5074 | 91.231 | 0.092085
14986 | 977.063 | 2.5379 | 77.6742 | 96.7437 | -12.6401 | 12.3503 | 54.0004 | 2.2308 |  | 11.834 | 50.3653 | 7.3923 |  | 58.4517 | 142.4096 | 9.0282 | 41.8467 | 12.2354 | 191 | 33.4069 | 77.6852 | 96.5103 | 0.14556
14987 | 980.8506 | 3.379 | 79.9175 | 96.6123 | -12.6437 | 12.35 | 57.873 | 2.5278 |  | 13.8963 | 51.7368 | 7.5529 |  | 59.2637 | 140.9578 | 9.8687 | 42.0578 | 12.2268 | 196 | 28.6332 | 78.2162 | 101.4599 | 0.13097
14988 | 969.0608 | 4.2132 | 81.0477 | 96.4122 | -12.6437 | 12.35 | 56.1359 | 2.7463 |  | 15.3051 | 53.6353 | 6.5531 |  | 60.6637 | 132.1077 | 9.127 | 42.2726 | 12.3885 | 204 | 34.6797 | 76.0359 | 101.8178 | 0.13818
14989 | 963.4333 | 2.7597 | 71.9949 | 96.6504 | -11.641 | 11.4003 | 47.9543 | 2.3199 |  | 15.3325 | 54.3962 | 7.0422 |  | 65.189 | 137.4157 | 9.2773 | 42.1579 | 12.494 | 207 | 40.1247 | 75.058 | 98.851 | 0.12297
14990 | 959.9163 | 2.1791 | 47.6435 | 97.2992 | -8.642 | 8.5508 | 46.5733 | 1.6063 |  | 15.6947 | 54.6945 | 9.0792 |  | 69.0557 | 149.7818 | 9.7064 | 42.7257 | 12.5087 | 186 | 32.4462 | 79.4427 | 100.8849 | 0.076107
14991 | 952.9574 | 2.3098 | 27.6526 | 96.9883 | -12.6413 | 12.3489 | 52.4729 | 1.4148 |  | 16.2812 | 54.4663 | 10.7468 |  | 70.9525 | 148.315 | 8.5955 | 43.0946 | 12.5696 | 198 | 23.8947 | 82.8356 | 103.8395 | 0.075933
14992 | 944.2377 | 3.7609 | 22.7399 | 96.7265 | -9.6423 | 9.5008 | 52.2133 | 1.3783 |  | 17.6065 | 53.6999 | 12.0581 |  | 67.3067 | 144.3975 | 9.8023 | 42.9409 | 12.6692 | 226 | 22.8378 | 83.915 | 108.285 | 0.048407
14993 | 926.5516 | 5.1391 | 22.5386 | 96.3113 | -9.6424 | 9.5 | 51.7386 | 1.9654 |  | 16.9802 | 53.4896 | 9.6007 |  | 59.603 | 143.9639 | 9.365 | 42.7043 | 12.6962 | 209 | 28.4723 | 71.9241 | 107.2999 | 0.018721
14994 | 915.6739 | 3.9405 | 22.4227 | 97.398 | -11.6493 | 11.3995 | 50.6106 | 2.0759 |  | 14.0408 | 51.3948 | 6.9916 |  | 56.67 | 146.0851 | 8.6272 | 42.429 | 12.8776 | 203 | 30.7207 | 65.3719 | 103.9404 | 0.0050794
14995 | 929.6586 | 3.1211 | 22.9012 | 98.9177 | -9.6405 | 9.5005 | 55.0151 | 2.1464 |  | 13.7266 | 48.023 | 6.6438 |  | 56.0916 | 148.3505 | 9.913 | 42.8131 | 13.1813 | 203 | 36.3766 | 59.2979 | 106.1969 | 0
14996 | 920.933 | 3.9033 | 22.9139 | 98.0582 | -10.6293 | 10.4497 | 59.5485 | 3.0049 |  | 15.99 | 47.0009 | 6.5478 |  | 54.154 | 144.2762 | 9.3916 | 42.8718 | 13.4989 | 201 | 39.4287 | 60.9382 | 104.2822 | 0
14997 | 892.2318 | 5.6342 | 23.393 | 97.0311 | -10.6322 | 10.45 | 59.9009 | 2.4819 |  | 16.7405 | 46.3714 | 6.4548 |  | 51.8584 | 134.2581 | 9.6775 | 42.63 | 13.7034 | 183 | 36.0882 | 64.114 | 97.3557 | 0
14998 | 884.4797 | 7.1126 | 23.7719 | 98.1278 | -10.7697 | 10.45 | 57.3617 | 2.4224 |  | 15.1412 | 45.8794 | 7.3927 |  | 53.0839 | 132.0722 | 10.1598 | 43.0468 | 13.5601 | 168 | 35.5332 | 65.7849 | 94.9874 | 0
14999 | 453.204 | 0 | 11.3126 | 47.2147 | -0.003056 | 0.002903 | 27.7928 | 1.6432 |  | 7.4583 | 25.2251 | 4.4614 |  | 27.0613 | 69.5168 | 4.5906 | 20.826 | 7.2199 | 143 | 8.9051 | 19.449 | 23.668 | 0
15000 | 881.2521 | 10.2777 | 23.2777 | 96.5089 | -12.6406 | 12.35 | 47.3727 | 2.6679 |  | 13.376 | 44.5687 | 11.2563 |  | 49.3224 | 130.6416 | 8.9199 | 42.3218 | 13.375 | 152 | 37.4656 | 70.1114 | 90.4326 | 0
15001 | 879.7396 | 12.1953 | 23.0824 | 97.1109 | -11.6438 | 11.4003 | 56.7003 | 2.3736 |  | 12.2944 | 43.7538 | 8.5095 |  | 46.6773 | 130.5204 | 9.6313 | 41.8898 | 10.7546 | 148 | 36.3475 | 66.7249 | 89.1091 | 0
15002 | 873.5896 | 8.0869 | 22.8101 | 98.4276 | -11.6405 | 11.4 | 59.5099 | 3.0941 |  | 12.4624 | 43.6083 | 6.6583 |  | 44.5396 | 132.7639 | 8.9689 | 41.8573 | 5.8595 | 147 | 37.6296 | 71.6411 | 87.8925 | 0
15003 | 868.7205 | 3.3195 | 22.5438 | 98.4919 | -8.6377 | 8.5508 | 56.7586 | 2.5275 |  | 12.2257 | 43.5667 | 6.0638 |  | 44.2895 | 126.7564 | 9.737 | 41.7625 | 3.0682 | 141 | 40.9909 | 74.1675 | 90.0003 | 0
15004 | 864.3423 | 3.0922 | 22.6994 | 97.0665 | -10.9994 | 10.4495 | 48.9289 | 2.4444 |  | 12.0993 | 43.753 | 6.1261 |  | 44.819 | 118.0046 | 10.2745 | 41.8289 | 2.8182 | 142 | 47.892 | 78.5586 | 96.9387 | 0
15005 | 861.135 | 3.6257 | 22.8599 | 96.2624 | -12.6369 | 12.3495 | 50.4812 | 3.1636 |  | 11.7431 | 43.9946 | 6.0489 |  | 44.9265 | 117.3707 | 8.8734 | 41.9743 | 2.8161 | 126 | 47.8346 | 73.5055 | 98.2718 | 0
15006 | 876.6345 | 3.7402 | 23.0132 | 96.2748 | -12.6417 | 12.35 | 56.0139 | 2.6332 |  | 11.3717 | 43.6102 | 6.0017 |  | 44.6916 | 118.1426 | 9.1526 | 41.9484 | 2.7952 | 117 | 47.3934 | 65.6892 | 98.1112 | 0
15007 | 893.5892 | 3.1031 | 22.9752 | 96.5921 | -11.6436 | 11.4003 | 54.4051 | 2.3409 |  | 11.0943 | 46.714 | 6.0308 |  | 46.1486 | 119.8218 | 9.936 | 41.7094 | 2.7918 | 112 | 44.2161 | 75.961 | 96.8441 | 0.14395
15008 | 903.6519 | 2.04 | 23.0422 | 97.0664 | -11.6434 | 11.4 | 48.2295 | 2.8419 |  | 11.4396 | 52.2612 | 5.4645 |  | 47.3155 | 123.1568 | 8.8716 | 41.7745 | 3.1605 | 138 | 40.6924 | 78.9211 | 95.9081 | 0.17843
15009 | 915.9177 | 1.8516 | 22.5756 | 97.2306 | -9.6434 | 9.5005 | 44.8541 | 2.2667 |  | 13.1678 | 53.4754 | 4.131 |  | 48.4009 | 132.2543 | 9.1988 | 41.8574 | 3.5863 | 155 | 37.3017 | 77.6415 | 94.8584 | 0.13883
15010 | 932.9021 | 2.0731 | 22.2898 | 97.059 | -10.6403 | 10.4497 | 54.1827 | 1.5216 |  | 14.6212 | 53.4456 | 3.3329 |  | 51.5569 | 138.0098 | 9.8764 | 41.9551 | 3.6426 | 176 | 34.1444 | 78.5055 | 94.7551 | 0.08609
15011 | 948.477 | 2.2065 | 22.4654 | 96.8964 | -9.6392 | 9.5003 | 59.3707 | 1.9405 |  | 14.6504 | 54.0089 | 4.2005 |  | 58.4296 | 134.3211 | 8.8648 | 42.0426 | 3.9381 | 188 | 30.0862 | 79.4352 | 97.7634 | 0.19884
15012 | 960.9113 | 2.0874 | 22.5866 | 97.1745 | -10.6391 | 10.4497 | 56.6058 | 2.0435 |  | 14.2034 | 55.0222 | 6.7778 |  | 68.6811 | 129.506 | 9.6545 | 42.1765 | 7.0145 | 178 | 29.624 | 74.7531 | 97.2427 | 0.13977
15013 | 953.9312 | 2.3514 | 22.9638 | 97.5042 | -11.6412 | 11.3997 | 54.2459 | 1.6027 |  | 13.8176 | 55.7157 | 7.852 |  | 74.6521 | 135.7378 | 9.7761 | 42.659 | 12.124 | 179 | 26.5616 | 77.9654 | 96.6011 | 0.078123
15014 | 941.2685 | 2.7896 | 22.9848 | 97.4171 | -10.6407 | 10.4503 | 48.9379 | 2.0449 |  | 14.2896 | 55.0767 | 6.9983 |  | 75.2012 | 137.2714 | 8.4227 | 43.3366 | 14.3416 | 206 | 30.9073 | 84.515 | 95.7272 | 0.069381
15015 | 935.8552 | 4.3141 | 22.7528 | 97.2279 | -11.6384 | 11.3997 | 49.1454 | 1.9823 |  | 14.3354 | 54.9917 | 9.117 |  | 74.2322 | 139.801 | 9.6879 | 43.5409 | 14.4035 | 185 | 35.4634 | 85.3832 | 93.5709 | 0.097059
15016 | 915.6899 | 5.3835 | 24.0715 | 96.1637 | -12.6423 | 12.3497 | 52.786 | 1.9958 |  | 13.2719 | 54.8686 | 11.7312 |  | 74.1266 | 149.8494 | 9.6408 | 42.9758 | 14.1355 | 182 | 40.8943 | 82.2729 | 91.5581 | 0.046522
15017 | 916.4181 | 4.9204 | 24.2684 | 96.2383 | -11.6455 | 11.4003 | 52.8173 | 2.2125 |  | 13.0839 | 55.6623 | 12.0857 |  | 75.8178 | 156.054 | 8.3412 | 42.6898 | 13.5589 | 154 | 40.3758 | 75.6914 | 90.3428 | 0.037317
15018 | 944.2993 | 6.8769 | 23.2837 | 98.0359 | -12.6364 | 12.3497 | 55.9905 | 2.0129 |  | 13.1032 | 57.4538 | 11.4905 |  | 75.8592 | 155.7936 | 9.9996 | 43.1616 | 13.3356 | 133 | 39.1711 | 67.9452 | 94.6723 | 0.0039199
15019 | 920.2099 | 7.486 | 23.0902 | 98.5152 | -12.6339 | 12.35 | 52.6873 | 2.6165 |  | 12.3219 | 59.173 | 10.9525 |  | 71.6175 | 148.012 | 9.8073 | 43.2653 | 13.5246 | 135 | 38.2306 | 63.2048 | 96.5426 | 0
15020 | 880.7747 | 6.566 | 22.5166 | 97.8163 | -12.6337 | 12.35 | 54.3773 | 3.2473 |  | 11.4657 | 55.0299 | 10.8502 |  | 64.5231 | 140.3822 | 8.4164 | 42.8647 | 13.6035 | 134 | 35.3002 | 65.5106 | 97.0512 | 0
15021 | 864.4448 | 7.0887 | 22.7281 | 97.069 | -12.63 | 12.35 | 67.2985 | 3.0954 |  | 11.0467 | 46.3776 | 10.6626 |  | 59.4884 | 132.9525 | 10.0918 | 43.0609 | 13.8335 | 120 | 35.105 | 65.3022 | 92.9589 | 0
15022 | 849.6495 | 7.0501 | 23.0303 | 97.7267 | -13.7671 | 13.2997 | 72.4564 | 2.5096 |  | 10.9039 | 44.1047 | 10.0507 |  | 56.9463 | 125.1319 | 10.0529 | 43.1658 | 13.6165 | 117 | 37.0118 | 66.3189 | 89.6993 | 0
15023 | 432.5713 | 0 | 11.1528 | 47.1176 | -0.00389 | 0.003696 | 37.6575 | 1.3257 |  | 5.9264 | 24.0825 | 4.8929 |  | 27.1845 | 68.8784 | 4.1288 | 20.7163 | 7.0955 | 114 | 9.4259 | 19.8149 | 22.0816 | 0
15024 | 818.9782 | 5.8682 | 22.6655 | 97.1378 | -13.6308 | 13.2997 | 69.5896 | 3.1921 |  | 12.3534 | 43.3484 | 6.3693 |  | 54.0239 | 120.6799 | 9.6935 | 42.2545 | 4.7723 | 109 | 35.0192 | 70.6642 | 90.9469 | 0
15025 | 823.0362 | 7.109 | 22.8875 | 96.9782 | -12.6334 | 12.3503 | 69.389 | 3.2127 |  | 13.1256 | 42.8068 | 6.261 |  | 52.2132 | 120.9324 | 9.7577 | 42.2989 | 2.7771 | 107 | 34.1276 | 70.5135 | 91.4533 | 0
15026 | 814.1863 | 9.2323 | 23.1547 | 96.8931 | -14.6289 | 14.2495 | 71.7115 | 2.9695 |  | 13.2154 | 43.0413 | 6.1508 |  | 52.1426 | 119.6751 | 9.0459 | 42.5012 | 2.7705 | 107 | 33.119 | 73.61 | 89.2354 | 0
15027 | 816.374 | 9.0369 | 23.1992 | 96.3634 | -13.6277 | 13.3003 | 74.6759 | 2.7797 |  | 13.291 | 45.7653 | 6.1575 |  | 52.4906 | 120.6909 | 9.8237 | 42.5711 | 2.7753 | 102 | 34.6037 | 74.1069 | 89.3137 | 0
15028 | 811.4144 | 5.7635 | 23.0903 | 96.227 | -13.6316 | 13.3 | 74.3544 | 3.0936 |  | 13.989 | 46.2628 | 6.2055 |  | 51.8836 | 117.9209 | 9.0315 | 42.3523 | 2.7782 | 107 | 34.0861 | 78.6936 | 101.9963 | 0
15029 | 814.2285 | 3.9392 | 33.1303 | 96.0918 | -12.6382 | 12.3503 | 73.5026 | 3.3048 |  | 21.2167 | 43.4874 | 7.8709 |  | 57.326 | 122.0947 | 9.7219 | 41.8373 | 2.7596 | 106 | 32.355 | 77.7263 | 113.4365 | 0
15030 | 869.6933 | 5.7023 | 51.9889 | 99.7863 | -15.6383 | 15.1992 | 75.1839 | 3.6552 |  | 32.4715 | 50.5273 | 12.5641 |  | 81.7576 | 145.6804 | 14.0581 | 41.0948 | 5.0733 | 174 | 42.039 | 71.7706 | 132.7236 | 0
15031 | 933.7454 | 11.6588 | 77.1075 | 108.742 | -21.4684 | 20.8984 | 82.422 | 5.0125 |  | 43.027 | 67.8401 | 23.1598 |  | 120.5405 | 196.6483 | 25.8344 | 43.514 | 10.1023 | 278 | 59.0519 | 92.3807 | 166.5243 | 0.023387
15032 | 1010.0187 | 12.5338 | 99.8572 | 121.4101 | -18.3676 | 18.0508 | 101.7461 | 6.0354 |  | 52.7056 | 81.546 | 34.3947 |  | 153.334 | 252.0945 | 38.2644 | 49.057 | 13.4434 | 348 | 66.5501 | 111.344 | 189.3094 | 0.077684
15033 | 1118.64 | 8.9029 | 108.4429 | 137.6126 | -23.6374 | 22.7987 | 108.4903 | 6.4029 |  | 52.7121 | 87.0558 | 37.5865 |  | 173.9786 | 302.4057 | 41.5313 | 54.5759 | 14.974 | 334 | 68.2734 | 126.5335 | 205.7755 | 0.052052
15034 | 1233.0031 | 11.1491 | 111.0431 | 143.5065 | -23.6401 | 22.8 | 111.3906 | 6.3671 |  | 47.0554 | 89.6748 | 38.5208 |  | 182.7292 | 330.336 | 43.1216 | 59.6606 | 16.4546 | 366 | 65.8014 | 131.8411 | 216.1987 | 0.066711
15035 | 1331.1426 | 7.713 | 117.3431 | 146.0168 | -20.644 | 19.9508 | 124.1433 | 6.0613 |  | 46.3882 | 90.1742 | 38.5635 |  | 189.3989 | 335.8202 | 41.2128 | 61.8622 | 19.0924 | 357 | 68.0778 | 145.4773 | 217.0941 | 0.076519
15036 | 1323.2116 | 5.3232 | 121.3143 | 139.1147 | -20.6421 | 19.95 | 123.5477 | 6.9543 |  | 43.517 | 89.4282 | 39.4024 |  | 185.2711 | 330.4469 | 41.5959 | 59.0847 | 18.8709 | 370 | 59.5198 | 127.5824 | 211.1945 | 0.10128
15037 | 1312.8436 | 5.3175 | 119.5126 | 138.1286 | -20.6425 | 19.95 | 123.7591 | 7.1366 |  | 43.8428 | 90.0531 | 41.4738 |  | 180.9537 | 317.2376 | 42.9441 | 58.1024 | 18.1648 | 290 | 68.3086 | 129.1861 | 204.7898 | 0.088455
15038 | 1303.9822 | 9.1579 | 117.5412 | 144.7505 | -24.64 | 23.7489 | 122.774 | 5.7439 |  | 42.7837 | 90.7808 | 41.9877 |  | 180.4741 | 314.2974 | 42.2514 | 56.1375 | 18.1018 | 288 | 73.95 | 135.3737 | 198.2135 | 0.077607
15039 | 1295.4828 | 11.5329 | 114.0616 | 141.1041 | -23.6404 | 22.8003 | 116.4111 | 5.056 |  | 39.6376 | 90.4556 | 35.0199 |  | 175.379 | 307.9605 | 41.7677 | 54.4223 | 17.9813 | 267 | 73.281 | 128.1709 | 192.9019 | 0.090046
15040 | 1254.0237 | 9.6645 | 108.7283 | 130.6717 | -14.6446 | 14.2524 | 105.5567 | 5.3955 |  | 38.2242 | 83.2705 | 20.1761 |  | 164.6431 | 279.6195 | 33.4704 | 53.0168 | 17.4616 | 242 | 71.518 | 120.8776 | 175.3553 | 0.17278
15041 | 1170.7271 | 6.3391 | 102.3213 | 121.5507 | -13.639 | 13.3003 | 79.8091 | 4.0306 |  | 32.37 | 67.0627 | 13.3846 |  | 127.6492 | 232.2045 | 18.9269 | 51.1957 | 16.2779 | 233 | 62.7265 | 100.0617 | 139.315 | 0.05205
15042 | 1113.2893 | 4.5131 | 98.1316 | 110.9456 | -13.6383 | 13.3 | 78.5339 | 3.699 |  | 19.4691 | 56.9429 | 11.8829 |  | 87.9872 | 192.5026 | 12.5459 | 47.6884 | 12.4117 | 215 | 61.2192 | 79.8161 | 121.515 | 0.0030366
15043 | 1077.4795 | 4.8339 | 82.8788 | 109.4336 | -13.6401 | 13.3 | 78.6272 | 3.2519 |  | 13.89 | 57.0494 | 9.4811 |  | 79.1321 | 182.8738 | 10.5488 | 43.0015 | 7.4295 | 194 | 56.2588 | 74.4054 | 109.4296 | 0
15044 | 1054.9101 | 4.9973 | 43.0549 | 106.8886 | -12.6316 | 12.3503 | 65.2814 | 2.9516 |  | 14.052 | 58.3806 | 7.8276 |  | 76.2484 | 170.1644 | 9.9307 | 41.4616 | 5.4515 | 192 | 54.796 | 72.0009 | 103.2624 | 0
15045 | 1022.3344 | 4.3833 | 24.1934 | 102.4888 | -7.6324 | 7.6013 | 58.5633 | 3.1761 |  | 13.2993 | 56.1036 | 7.3631 |  | 63.3666 | 147.6878 | 9.2951 | 40.9669 | 5.1185 | 182 | 43.0988 | 69.1616 | 103.8909 | 0
15046 | 978.7493 | 3.4405 | 23.512 | 100.8201 | -7.6362 | 7.6 | 55.2908 | 2.5055 |  | 12.1379 | 49.2008 | 7.0156 |  | 54.1385 | 136.6414 | 9.0886 | 40.6051 | 4.5632 | 152 | 38.1869 | 69.6353 | 102.9596 | 0
15047 | 361.7604 | 0 | 8.2904 | 0 | 0.17723 | 0.002112 | 20.3945 | 0.80692 |  | 4.5692 | 18.9743 | 2.6454 |  | 0 | 0 | 3.1812 | 0 | 1.7045 | 136 | 4.0814 | 10.9198 | 12.448 | 0
15048 | 907.8619 | 2.1334 | 23.043 | 99.8881 | -6.6373 | 6.6503 | 45.2761 | 2.5351 |  | 12.3293 | 44.8677 | 6.6308 |  | 46.0865 | 130.5614 | 9.9337 | 39.935 | 3.224 | 123 | 38.301 | 82.8726 | 101.9806 | 0
15049 | 909.6472 | 2.2015 | 22.9511 | 100.4323 | -7.6375 | 7.5997 | 47.5974 | 2.4254 |  | 12.871 | 44.4537 | 6.4231 |  | 43.6167 | 126.9719 | 9.5506 | 39.5757 | 2.7322 | 119 | 33.7775 | 80.2417 | 100.5221 | 0
15050 | 900.6761 | 2.1869 | 32.4047 | 100.5379 | -6.6348 | 6.6503 | 56.5781 | 2.9799 |  | 12.8791 | 45.0019 | 6.3318 |  | 43.1304 | 126.1343 | 9.3987 | 39.5916 | 2.8054 | 122 | 35.6799 | 69.9331 | 101.9628 | 0
15051 | 893.2785 | 2.1407 | 36.1047 | 99.0913 | -7.6388 | 7.5997 | 57.8101 | 2.4218 |  | 12.886 | 44.8097 | 6.273 |  | 42.9547 | 125.9755 | 10.1562 | 39.6437 | 2.8918 | 116 | 33.9295 | 72.5182 | 101.8308 | 0
15052 | 884.9153 | 2.6827 | 33.5709 | 98.9774 | -6.6405 | 6.6503 | 51.7727 | 2.5392 |  | 13.6643 | 44.4032 | 6.2619 |  | 43.1436 | 121.9091 | 8.969 | 39.7474 | 2.7797 | 119 | 33.6328 | 76.9482 | 106.5363 | 0
15053 | 903.4044 | 3.6055 | 41.3376 | 98.8391 | -6.6383 | 6.65 | 49.0939 | 2.2231 |  | 20.6053 | 48.0078 | 8.3713 |  | 51.6211 | 124.2221 | 9.8791 | 39.553 | 2.9155 | 108 | 37.0906 | 78.3132 | 116.2801 | 0
15054 | 978.6257 | 4.9796 | 52.4412 | 103.6662 | -9.6392 | 9.4992 | 64.5809 | 2.6867 |  | 32.0661 | 56.2548 | 14.0094 |  | 76.2326 | 135.5763 | 12.6983 | 39.6054 | 5.1249 | 203 | 41.1677 | 70.8174 | 137.1201 | 0
15055 | 1071.8457 | 11.2593 | 74.6657 | 111.4484 | -19.6427 | 18.9974 | 85.1799 | 3.2573 |  | 37.7784 | 70.6675 | 19.1707 |  | 115.6207 | 184.584 | 26.0827 | 42.0597 | 10.9008 | 256 | 59.1915 | 90.9978 | 166.2097 | 0.030844
15056 | 1179.0075 | 14.1486 | 100.5747 | 126.6577 | -30.6436 | 29.4471 | 101.9246 | 4.8331 |  | 44.4317 | 86.9063 | 27.704 |  | 151.4175 | 256.3714 | 36.804 | 47.107 | 16.3349 | 311 | 69.8731 | 107.9466 | 191.836 | 0.064225
15057 | 1255.1058 | 13.6472 | 105.54 | 140.0701 | -27.6442 | 26.6008 | 118.6414 | 5.5685 |  | 49.3008 | 95.0625 | 36.723 |  | 173.295 | 298.6827 | 40.5203 | 53.3432 | 16.7284 | 344 | 68.6936 | 116.2321 | 204.472 | 0.11797
15058 | 1312.6903 | 17.8333 | 108.1423 | 146.7187 | -25.643 | 24.7005 | 135.3635 | 5.5639 |  | 48.3161 | 93.677 | 42.8265 |  | 185.7769 | 318.2451 | 42.7834 | 56.1622 | 16.2954 | 331 | 71.685 | 129.3288 | 202.8097 | 0.18384
15059 | 1333.5039 | 21.0806 | 115.593 | 147.2762 | -25.6434 | 24.7 | 141.2688 | 5.8486 |  | 50.3936 | 94.3224 | 43.425 |  | 197.946 | 333.2528 | 44.647 | 58.008 | 16.7983 | 373 | 79.4045 | 145.0432 | 203.0926 | 0.21067
15060 | 1345.5518 | 19.4962 | 118.9849 | 148.1809 | -25.6457 | 24.7 | 135.0686 | 5.695 |  | 47.4262 | 94.3754 | 42.5773 |  | 196.2329 | 340.4388 | 46.3435 | 57.0428 | 17.2654 | 356 | 73.1556 | 129.3737 | 195.4077 | 0.14873
15061 | 1343.0128 | 10.5153 | 116.1817 | 147.4305 | -24.6454 | 23.7503 | 133.4017 | 5.6258 |  | 45.0112 | 92.2779 | 41.8296 |  | 196.5021 | 335.5889 | 48.2914 | 57.7422 | 17.5354 | 314 | 85.9201 | 114.2371 | 206.4159 | 0.17332
15062 | 1340.8824 | 6.8801 | 110.9525 | 149.6814 | -25.6431 | 24.6997 | 135.4715 | 5.7688 |  | 44.1366 | 92.4354 | 40.4638 |  | 198.4804 | 322.2452 | 46.2347 | 58.4949 | 17.4157 | 289 | 90.4678 | 120.4232 | 205.3927 | 0.061646
15063 | 1329.0098 | 8.5454 | 108.9354 | 145.4745 | -20.6445 | 19.9513 | 127.9774 | 5.0824 |  | 39.2871 | 93.8488 | 36.4164 |  | 191.7134 | 312.1697 | 41.7765 | 57.0685 | 17.582 | 284 | 79.9818 | 130.1205 | 202.5633 | 0.047377
15064 | 1280.4687 | 6.3273 | 107.6983 | 137.3687 | -18.6477 | 18.0505 | 110.6814 | 4.9591 |  | 32.2002 | 87.9417 | 29.943 |  | 175.4149 | 275.0513 | 32.6319 | 53.7187 | 17.4987 | 263 | 74.471 | 121.9389 | 180.9629 | 0.032329
15065 | 1212.875 | 6.6189 | 105.1483 | 128.3333 | -12.6457 | 12.3516 | 93.4489 | 3.9405 |  | 25.9192 | 69.8424 | 19.5481 |  | 149.4097 | 230.7665 | 19.3185 | 50.3393 | 17.0958 | 230 | 66.2314 | 90.8261 | 136.2355 | 0.015037
15066 | 1160.9141 | 10.16 | 97.8661 | 113.9651 | -9.6371 | 9.5008 | 91.6486 | 3.7051 |  | 18.4436 | 59.2317 | 10.2556 |  | 113.6189 | 200.0621 | 12.8744 | 47.333 | 14.128 | 222 | 63.0767 | 84.1041 | 128.608 | 0.0011042
15067 | 1113.2338 | 9.2426 | 76.5641 | 104.8863 | -8.6369 | 8.5503 | 86.1093 | 2.8428 |  | 14.2156 | 58.3877 | 7.74 |  | 96.1893 | 193.5154 | 10.7654 | 43.7518 | 9.0169 | 197 | 57.0344 | 79.0344 | 112.106 | 0
15068 | 1058.3204 | 5.6417 | 39.4075 | 102.0218 | -8.6349 | 8.55 | 70.3314 | 2.6185 |  | 14.3528 | 58.0825 | 8.0936 |  | 86.7241 | 180.2517 | 9.4136 | 42.085 | 6.2352 | 184 | 48.1704 | 74.1188 | 107.4715 | 0
15069 | 1030.9884 | 4.9992 | 24.4837 | 99.4143 | -9.6323 | 9.4997 | 60.8869 | 3.0492 |  | 14.0986 | 55.4158 | 8.6146 |  | 77.5712 | 155.648 | 9.6293 | 41.773 | 5.4256 | 163 | 41.3986 | 68.5476 | 101.1784 | 0
15070 | 1006.5296 | 4.7282 | 23.7809 | 97.6119 | -8.6349 | 8.5503 | 53.7041 | 2.6675 |  | 13.109 | 49.2588 | 8.0825 |  | 70.952 | 145.1109 | 9.5163 | 40.7159 | 4.3875 | 145 | 40.9504 | 63.1641 | 100.7192 | 0
15071 | 360.2003 | 0 | 7.9464 | 31.7603 | 0.17271 | 0.002376 | 18.5239 | 0.92127 |  | 4.8628 | 18.907 | 2.862 |  | 23.389 | 56.3605 | 3.1067 | 13.3557 | 1.5019 | 134 | 3.9622 | 9.0853 | 10.7558 | 0
15072 | 924.2443 | 2.9247 | 24.824 | 96.1327 | -9.6332 | 9.4997 | 72.1009 | 3.0024 |  | 13.883 | 45.6766 | 7.3381 |  | 66.3332 | 133.141 | 9.5593 | 40.2718 | 3.2009 | 116 | 34.8739 | 57.5644 | 99.8578 | 0
15073 | 918.7329 | 6.9142 | 24.4048 | 96.783 | -9.632 | 9.5 | 70.559 | 3.1617 |  | 14.4448 | 45.7836 | 7.2835 |  | 63.8102 | 127.1366 | 9.6126 | 40.2941 | 2.8186 | 118 | 35.4365 | 49.1799 | 100.1781 | 0
15074 | 907.2693 | 6.4261 | 24.2092 | 96.2358 | -9.63 | 9.5 | 70.6125 | 2.7677 |  | 14.6254 | 46.6866 | 7.2519 |  | 63.3395 | 124.8317 | 9.1612 | 40.3453 | 2.8787 | 112 | 31.4225 | 49.5659 | 103.6088 | 0
15075 | 894.3939 | 3.3176 | 23.4619 | 95.6556 | -8.6302 | 8.5503 | 74.6523 | 2.5508 |  | 14.6376 | 46.5394 | 7.6441 |  | 64.2317 | 124.4916 | 9.9885 | 40.2996 | 2.904 | 109 | 32.765 | 55.0674 | 102.3799 | 0
15076 | 884.9054 | 2.7935 | 23.8986 | 95.5495 | -9.6316 | 9.4997 | 75.3157 | 3.1278 |  | 15.2444 | 45.7281 | 7.2912 |  | 64.3395 | 123.4315 | 9.9198 | 40.3754 | 2.7904 | 107 | 34.3425 | 56.0001 | 105.1383 | 0
15077 | 901.0888 | 3.5416 | 37.2994 | 95.439 | -9.6342 | 9.5 | 74.281 | 3.2979 |  | 23.0773 | 47.502 | 9.6947 |  | 66.3221 | 128.7233 | 9.9441 | 40.2849 | 3.0469 | 104 | 31.8554 | 56.6348 | 116.1889 | 0
15078 | 958.7519 | 5.1264 | 47.2996 | 100.9135 | -28.608 | 27.5221 | 85.4763 | 3.1022 |  | 30.9882 | 52.3212 | 12.7594 |  | 82.1635 | 142.9953 | 10.0335 | 39.8769 | 8.1478 | 184 | 40.3236 | 56.3884 | 128.495 | 0
15079 | 1024.4095 | 12.1081 | 74.4229 | 107.6306 | -30.6658 | 29.4724 | 105.1675 | 3.2639 |  | 37.0221 | 65.4227 | 24.1855 |  | 118.5274 | 196.2467 | 17.2033 | 41.5892 | 13.198 | 296 | 56.8093 | 80.3648 | 160.1058 | 0.013789
15080 | 1117.5605 | 16.9877 | 94.0119 | 120.6949 | -29.6485 | 28.5003 | 102.6079 | 5.1094 |  | 40.593 | 79.8905 | 31.4907 |  | 152.6707 | 257.0158 | 23.0097 | 45.0958 | 15.4665 | 311 | 69.9403 | 98.1577 | 188.7861 | 0.033967
15081 | 1218.6562 | 18.2797 | 109.4614 | 135.4377 | -27.6485 | 26.6005 | 108.7561 | 6.0417 |  | 46.1809 | 86.7708 | 34.4734 |  | 171.7341 | 303.2869 | 27.1222 | 50.5325 | 17.3415 | 335 | 75.499 | 119.5011 | 202.9807 | 0.048783
15082 | 1295.9448 | 14.3039 | 111.4662 | 142.4708 | -25.6435 | 24.7005 | 120.4013 | 5.502 |  | 55.5921 | 93.2923 | 38.7133 |  | 183.4605 | 318.7062 | 30.8688 | 52.7847 | 19.4354 | 355 | 80.0342 | 124.3011 | 208.3529 | 0.064489
15083 | 1314.2274 | 10.8007 | 113.7702 | 143.6748 | -24.6423 | 23.7503 | 124.6985 | 4.963 |  | 55.9858 | 94.902 | 38.5284 |  | 196.8142 | 320.7841 | 29.2344 | 53.5012 | 20.8727 | 345 | 76.7351 | 129.9501 | 209.7502 | 0.075348
15084 | 1313.5619 | 12.9681 | 115.5702 | 136.3595 | -23.6442 | 22.8003 | 122.7299 | 5.7682 |  | 47.5473 | 91.7985 | 38.2526 |  | 198.6376 | 326.4219 | 38.0528 | 54.0698 | 20.1049 | 365 | 75.1273 | 121.4733 | 208.0567 | 0.10105
15085 | 1315.7972 | 14.1895 | 118.221 | 138.5316 | -26.6451 | 25.6492 | 126.2559 | 5.5317 |  | 46.9038 | 94.6768 | 39.8248 |  | 194.9325 | 326.576 | 43.1124 | 54.0919 | 19.6343 | 319 | 80.0712 | 119.521 | 202.5327 | 0.13378
15086 | 1333.5096 | 14.0666 | 116.9186 | 141.9191 | -23.6469 | 22.8008 | 126.8654 | 5.3971 |  | 47.4086 | 98.7701 | 39.7348 |  | 194.6455 | 324.9665 | 37.6056 | 55.2229 | 19.631 | 293 | 80.8218 | 122.1497 | 198.582 | 0.095589
15087 | 1306.6002 | 9.5916 | 112.5448 | 133.4666 | -27.6429 | 26.5989 | 121.9793 | 4.7471 |  | 43.8774 | 97.2194 | 35.2869 |  | 191.8503 | 314.309 | 33.5933 | 56.3474 | 18.8337 | 313 | 79.3228 | 120.746 | 199.9204 | 0.10476
15088 | 1247.6693 | 5.4789 | 109.8046 | 124.3719 | -22.6466 | 21.8513 | 103.6324 | 5.2995 |  | 40.3079 | 89.2053 | 28.1323 |  | 184.5361 | 283.4078 | 36.5191 | 55.3469 | 17.9522 | 290 | 77.5404 | 111.3289 | 176.3552 | 0.060147
15089 | 1161.4843 | 4.4041 | 108.7877 | 115.3455 | -15.6444 | 15.2018 | 74.996 | 3.9175 |  | 33.2657 | 68.488 | 22.0615 |  | 148.6095 | 258.1303 | 30.0001 | 52.0858 | 17.7122 | 269 | 70.227 | 83.7732 | 132.3539 | 0.015475
15090 | 1116.708 | 6.9534 | 102.4908 | 104.7858 | -15.6386 | 15.2 | 67.8216 | 3.0546 |  | 22.283 | 55.8155 | 14.7264 |  | 100.1105 | 231.5408 | 29.6029 | 48.7139 | 14.5415 | 249 | 65.5887 | 71.195 | 122.8241 | 0.00066252
15091 | 1057.9637 | 8.9538 | 82.6006 | 98.3472 | -14.6407 | 14.2503 | 66.7418 | 3.5495 |  | 18.9335 | 54.3411 | 11.7646 |  | 81.0788 | 208.9706 | 25.8473 | 42.9491 | 8.3445 | 228 | 60.2856 | 66.1652 | 107.8649 | 0
15092 | 1032.501 | 8.4928 | 54.9819 | 96.6159 | -13.6364 | 13.3003 | 54.4563 | 2.7195 |  | 19.1886 | 55.4304 | 11.6678 |  | 72.9104 | 181.993 | 15.0204 | 40.811 | 5.262 | 199 | 53.3196 | 62.0335 | 108.5009 | 0
15093 | 1013.3316 | 7.9258 | 40.6379 | 91.9546 | -15.6336 | 15.1995 | 54.0686 | 2.3845 |  | 16.8829 | 54.1288 | 9.2747 |  | 65.3647 | 163.421 | 10.0164 | 40.1868 | 4.8125 | 190 | 48.3343 | 57.6 | 105.7442 | 0
15094 | 991.0785 | 7.269 | 35.5347 | 88.6089 | -13.6339 | 13.3005 | 55.6049 | 1.9687 |  | 14.2052 | 48.3833 | 7.4132 |  | 60.3008 | 146.9963 | 10.3783 | 39.912 | 4.5226 | 175 | 46.2732 | 62.7897 | 100.2003 | 0
15095 | 370.8729 | 0 | 11.9752 | 0 | 0.17839 | 0.003696 | 20.7192 | 0.6305 |  | 5.242 | 19.0668 | 2.7813 |  | 0 | 0 | 3.76 | 0 | 1.7569 | 162 | 4.9446 | 9.9407 | 10.7953 | 0
15096 | 941.5041 | 2.7397 | 33.7551 | 87.8813 | -9.6336 | 9.5003 | 54.2678 | 2.5302 |  | 15.112 | 45.0701 | 6.597 |  | 57.5172 | 137.4495 | 10.4316 | 39.5379 | 3.7044 | 148 | 42.0546 | 73.0693 | 92.875 | 0
15097 | 949.7446 | 3.8924 | 33.8291 | 87.6094 | -9.6322 | 9.5 | 47.2715 | 1.9462 |  | 15.8417 | 44.7878 | 6.3461 |  | 55.806 | 135.4617 | 10.8028 | 39.5636 | 3.4929 | 142 | 38.8572 | 62.1397 | 90.4777 | 0
15098 | 921.6388 | 7.6189 | 32.9983 | 87.5744 | -8.6329 | 8.5503 | 52.8819 | 2.1943 |  | 15.9095 | 44.4048 | 6.2534 |  | 54.4643 | 132.983 | 9.8573 | 39.3116 | 3.5011 | 140 | 33.3299 | 55.9909 | 88.7743 | 0
15099 | 905.917 | 9.38 | 32.8152 | 87.5701 | -11.6345 | 11.3992 | 69.4536 | 2.6062 |  | 15.9881 | 44.2808 | 6.2502 |  | 54.3632 | 127.937 | 10.3861 | 39.3583 | 3.3857 | 135 | 33.739 | 55.5979 | 89.004 | 0
15100 | 895.667 | 6.1915 | 32.5607 | 87.4942 | -9.6408 | 9.5005 | 73.1973 | 1.8325 |  | 17.0631 | 44.3174 | 6.2176 |  | 54.241 | 119.6745 | 10.351 | 39.1835 | 3.0669 | 127 | 34.0697 | 54.3707 | 91.923 | 0
15101 | 899.5149 | 4.0716 | 33.9762 | 87.607 | -9.64 | 9.5 | 73.387 | 2.1148 |  | 24.0178 | 47.0637 | 8.0503 |  | 59.4628 | 124.067 | 9.9622 | 39.1511 | 3.3777 | 119 | 30.6554 | 56.0597 | 105.2451 | 0
15102 | 942.687 | 9.1559 | 44.5199 | 94.5765 | -10.6393 | 10.4497 | 87.1694 | 2.7559 |  | 32.2537 | 54.3729 | 13.4247 |  | 85.2731 | 138.6728 | 14.2007 | 39.2646 | 9.1395 | 204 | 40.3314 | 59.2121 | 124.6924 | 0
15103 | 1054.9486 | 11.9447 | 80.5912 | 109.153 | -17.6412 | 17.0982 | 96.0881 | 4.0762 |  | 35.9365 | 73.9961 | 22.1827 |  | 132.4775 | 202.6389 | 29.7982 | 42.8269 | 14.9969 | 260 | 63.5867 | 94.0728 | 169.8044 | 0.014468
15104 | 1108.1551 | 0 | 0 | 0 | -18.9892 | 18.0397 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0.02713
15105 | 1202.7165 | 7.3087 | 98.4634 | 128.257 | -20.657 | 19.9595 | 107.4782 | 4.7282 |  | 42.4488 | 90.7173 | 32.1264 |  | 166.8018 | 287.6128 | 41.7182 | 50.3578 | 20.2624 | 379 | 79.5519 | 124.6344 | 197.9682 | 0.049113
15106 | 1284.6661 | 4.7362 | 100.7104 | 135.3025 | -20.6469 | 19.95 | 119.5024 | 5.22 |  | 45.0153 | 99.3517 | 39.5631 |  | 180.5998 | 322.0666 | 43.0519 | 55.0082 | 20.5503 | 334 | 74.8801 | 129.4094 | 211.5073 | 0.064376
15107 | 1315.6355 | 4.7056 | 106.7677 | 136.845 | -18.647 | 18.0505 | 118.9455 | 4.933 |  | 47.3825 | 100.4687 | 41.0852 |  | 190.2735 | 329.869 | 44.6063 | 56.4199 | 19.3871 | 324 | 77.0499 | 147.0638 | 206.8588 | 0.12239
15108 | 1305.2778 | 4.6241 | 109.3533 | 136.3924 | -17.6467 | 17.1003 | 118.8099 | 5.919 |  | 45.9748 | 95.697 | 41.0827 |  | 192.0573 | 331.7106 | 45.0065 | 55.1851 | 19.5169 | 370 | 72.3693 | 126.6965 | 205.587 | 0.12465
15109 | 1305.8114 | 4.479 | 111.5359 | 144.26 | -19.6472 | 18.9995 | 125.5461 | 6.3971 |  | 45.0865 | 96.6188 | 40.7061 |  | 192.5823 | 331.3826 | 44.9531 | 54.9484 | 19.3334 | 328 | 74.4195 | 134.9891 | 207.4057 | 0.18947
15110 | 1291.4094 | 6.2803 | 113.2431 | 137.4149 | -18.6473 | 18.0503 | 125.6821 | 5.15 |  | 44.868 | 99.2707 | 40.3956 |  | 195.0799 | 331.5324 | 44.0397 | 55.8938 | 19.2325 | 274 | 72.7586 | 148.1856 | 201.8689 | 0.18828
15111 | 1249.2837 | 8.3152 | 116.9723 | 127.5931 | -16.6433 | 16.1505 | 119.1138 | 4.9799 |  | 37.1998 | 97.9996 | 37.0114 |  | 187.7066 | 321.6035 | 41.1799 | 54.6678 | 19.4654 | 271 | 70.7589 | 142.159 | 193.4187 | 0.14911
15112 | 1175.3318 | 6.2565 | 110.2395 | 120.5364 | -10.1232 | 10.4516 | 102.5576 | 3.852 |  | 31.5719 | 88.8496 | 22.6063 |  | 174.1069 | 283.9716 | 31.1409 | 53.4233 | 19.2551 | 253 | 69.9293 | 122.2045 | 172.9358 | 0.13068
15113 | 1142.3354 | 4.0016 | 104.2911 | 112.7052 | -13.7191 | 14.2529 | 82.9066 | 3.1162 |  | 28.254 | 69.8572 | 17.4323 |  | 145.5804 | 252.4911 | 16.3214 | 50.6494 | 19.0069 | 238 | 60.7067 | 86.3871 | 135.0984 | 0.064773
15114 | 1090.6302 | 4.3132 | 97.4505 | 97.583 | -7.2787 | 8.5476 | 70.5797 | 2.0716 |  | 18.6234 | 57.5674 | 15.778 |  | 100.8751 | 214.1853 | 10.4001 | 45.3843 | 15.4123 | 217 | 55.499 | 72.4482 | 123.3762 | 0.0016578
15115 | 1036.0934 | 4.6643 | 74.9734 | 91.263 | -6.8273 | 8.5524 | 69.1961 | 2.1989 |  | 16.0686 | 55.6987 | 15.674 |  | 77.0839 | 191.0682 | 9.9159 | 41.0727 | 12.9106 | 194 | 51.8712 | 67.8963 | 103.3331 | 0
15116 | 1001.0034 | 4.2137 | 39.2173 | 90.734 | -6.822 | 8.55 | 64.6956 | 2.2643 |  | 17.1666 | 53.5288 | 16.915 |  | 70.7326 | 166.7673 | 9.459 | 39.5326 | 14.0726 | 179 | 52.9745 | 64.4885 | 96.8069 | 0
15117 | 974.3526 | 3.9116 | 24.9984 | 88.6179 | -6.9043 | 8.5476 | 50.4511 | 1.8986 |  | 16.7623 | 49.0814 | 15.577 |  | 62.6557 | 143.2072 | 8.8872 | 38.5098 | 14.71 | 188 | 49.9444 | 62.7261 | 94.9128 | 0
15118 | 966.7115 | 3.3702 | 25.0555 | 86.6025 | -7.9069 | 9.4997 | 57.6052 | 2.5166 |  | 15.6542 | 43.5327 | 11.8765 |  | 55.5287 | 131.5603 | 8.5398 | 38.0597 | 14.2038 | 155 | 48.6111 | 60.1104 | 92.0913 | 0
15119 | 345.8721 | 0 | 8.4551 | 0 | 0.97354 | 0.00264 | 23.7595 | 1.1076 |  | 5.6139 | 16.368 | 3.7433 |  | 0 | 0 | 2.796 | 0 | 5.2819 | 135 | 5.1337 | 8.8537 | 10.1488 | 0
15120 | 925.8895 | 3.8747 | 22.8243 | 84.4011 | -9.1832 | 9.4997 | 69.2663 | 2.0105 |  | 16.0028 | 41.0195 | 10.2815 |  | 50.2664 | 118.971 | 8.7269 | 37.8805 | 6.0905 | 121 | 44.9867 | 61.1855 | 90.7821 | 0
15121 | 921.7635 | 7.4805 | 22.6504 | 84.754 | -9.8081 | 10.4497 | 69.3155 | 2.0758 |  | 16.6924 | 40.9525 | 10.0407 |  | 47.0254 | 121.5856 | 8.8466 | 37.969 | 4.4412 | 122 | 45.3166 | 60.6558 | 90.9389 | 0
15122 | 908.3842 | 9.2825 | 22.6783 | 84.3538 | -8.519 | 9.5003 | 69.1726 | 2.5888 |  | 16.7045 | 41.0636 | 9.9224 |  | 46.073 | 121.4384 | 8.7657 | 38.0322 | 4.174 | 125 | 43.1061 | 61.0613 | 87.961 | 0
15123 | 903.6905 | 7.4136 | 22.5364 | 84.1267 | -8.1773 | 9.5 | 72.5268 | 2.9714 |  | 16.7194 | 42.0872 | 10.4973 |  | 45.8648 | 115.2458 | 8.6579 | 37.9167 | 3.4022 | 117 | 40.7699 | 58.245 | 88.6897 | 0
15124 | 896.9687 | 3.8441 | 22.5608 | 84.0471 | -8.046 | 9.5 | 73.5091 | 2.4073 |  | 17.3892 | 43.3492 | 10.8735 |  | 45.3089 | 109.3196 | 8.5511 | 38.6888 | 2.9915 | 109 | 43.1977 | 57.01 | 98.6087 | 0
15125 | 904.1952 | 2.2512 | 32.4352 | 84.2105 | -9.9481 | 11.3995 | 72.11 | 2.0203 |  | 24.1518 | 47.7844 | 12.1448 |  | 51.758 | 112.6664 | 8.7159 | 39.5965 | 3.1788 | 112 | 39.3272 | 55.4233 | 108.7204 | 0
15126 | 939.254 | 5.8878 | 51.2343 | 90.1913 | -7.8587 | 9.5005 | 84.3356 | 2.3888 |  | 33.3641 | 52.352 | 14.5142 |  | 78.9577 | 132.8411 | 12.594 | 38.2461 | 6.5446 | 179 | 45.6843 | 60.3838 | 126.9919 | 0
15127 | 1001.7267 | 10.3535 | 75.8274 | 95.8775 | -16.3421 | 17.0979 | 103.7838 | 3.1416 |  | 39.5011 | 61.9611 | 21.597 |  | 122.2235 | 186.0507 | 26.1233 | 39.1372 | 13.0825 | 241 | 59.2356 | 89.7956 | 158.4933 | 0.10757
15128 | 1080.8159 | 8.1496 | 94.1164 | 107.386 | -18.9176 | 18.9995 | 104.3902 | 4.2002 |  | 45.8209 | 74.2241 | 28.8064 |  | 154.8697 | 236.1766 | 36.1267 | 42.9639 | 16.2869 | 317 | 62.7442 | 113.2903 | 187.2776 | 0.13525
15129 | 1161.9731 | 5.0309 | 100.1644 | 120.9439 | -19.9247 | 19.9497 | 112.6854 | 5.0198 |  | 51.4048 | 82.3673 | 33.8405 |  | 171.5862 | 275.2949 | 39.6755 | 47.6459 | 16.754 | 374 | 69.5479 | 122.3841 | 199.4428 | 0.24767
15130 | 1225.7477 | 4.3563 | 102.2688 | 125.1434 | -19.2227 | 19.95 | 127.8339 | 4.4996 |  | 52.2773 | 85.7314 | 37.5746 |  | 182.5551 | 305.8352 | 40.7408 | 51.4805 | 18.1164 | 369 | 71.4552 | 126.9716 | 193.1534 | 0.27562
15131 | 1246.0227 | 4.2672 | 106.1444 | 126.2066 | -15.5243 | 17.1008 | 132.0264 | 4.4296 |  | 56.027 | 86.2145 | 37.5862 |  | 190.4746 | 313.5313 | 40.5785 | 52.4471 | 19.0613 | 337 | 69.3661 | 129.983 | 204.544 | 0.2456
15132 | 1230.7079 | 4.4695 | 105.3673 | 126.0554 | -15.2307 | 17.1 | 133.9841 | 4.5965 |  | 47.6898 | 86.2386 | 36.5289 |  | 187.6706 | 307.508 | 40.4101 | 51.3577 | 19.04 | 387 | 55.0396 | 116.2516 | 195.5306 | 0.26947
15133 | 1210.2335 | 4.4447 | 108.6084 | 126.4225 | -16.1758 | 18.0497 | 133.7885 | 4.7065 |  | 38.8147 | 89.8455 | 36.818 |  | 183.6235 | 296.2921 | 40.9112 | 51.5403 | 19.1451 | 316 | 60.9927 | 128.5007 | 194.0049 | 0.28135
15134 | 1213.28 | 4.4703 | 110.5825 | 131.6538 | -15.2793 | 17.1003 | 127.1547 | 5.6146 |  | 38.5598 | 89.9941 | 36.7307 |  | 184.8969 | 300.4125 | 41.1257 | 52.6348 | 19.1168 | 293 | 70.1875 | 128.5216 | 186.9338 | 0.25954
15135 | 1193.0631 | 4.3764 | 110.1638 | 126.5372 | -16.4691 | 18.0497 | 116.3312 | 4.5155 |  | 39.6134 | 88.8589 | 32.0459 |  | 177.9444 | 292.4109 | 38.7161 | 52.6352 | 18.9138 | 306 | 69.7799 | 116.3252 | 181.5445 | 0.17524
15136 | 1147.8603 | 3.9675 | 107.0009 | 120.262 | -9.6311 | 11.4018 | 97.0377 | 3.4752 |  | 34.1508 | 81.2118 | 20.3247 |  | 165.3704 | 252.9753 | 31.89 | 51.8978 | 18.1472 | 288 | 64.852 | 103.0479 | 160.2483 | 0.11036
15137 | 1089.6819 | 4.3412 | 90.5665 | 110.0075 | -5.6653 | 7.5926 | 73.6926 | 2.3782 |  | 29.5596 | 62.8083 | 10.9672 |  | 129.5009 | 209.4855 | 27.1802 | 48.2026 | 16.3405 | 246 | 60.3873 | 85.9042 | 121.6311 | 0.0785
15138 | 1034.0511 | 4.4741 | 50.6075 | 98.4131 | -6.7264 | 8.5582 | 67.7716 | 2.2233 |  | 21.3671 | 52.7346 | 6.0927 |  | 91.8374 | 179.5396 | 21.5477 | 45.0752 | 12.2818 | 222 | 56.6492 | 78.9466 | 109.4912 | 0.0014785
15139 | 1015.3278 | 4.5425 | 29.4653 | 92.1523 | -6.6119 | 8.55 | 69.1109 | 1.7681 |  | 17.411 | 51.8985 | 6.3181 |  | 81.4486 | 168.0354 | 15.069 | 33.7311 | 6.5062 | 198 | 49.9054 | 78.3506 | 93.0584 | 0
15140 | 981.1963 | 4.1181 | 25.5028 | 87.0315 | -7.4073 | 9.4997 | 60.9815 | 2.188 |  | 17.0875 | 46.7959 | 7.2077 |  | 76.878 | 157.118 | 11.9539 | 27.0389 | 4.1529 | 195 | 49.8443 | 74.3579 | 87.3512 | 0
15141 | 948.374 | 3.9122 | 24.7886 | 85.1633 | -6.419 | 8.5503 | 51.8989 | 1.8431 |  | 16.2124 | 42.7525 | 7.1848 |  | 70.2018 | 151.0277 | 11.1587 | 26.4049 | 4.1825 | 205 | 43.6935 | 69.2969 | 86.758 | 0
15142 | 936.3348 | 3.4979 | 24.962 | 84.7818 | -6.6092 | 8.55 | 54.7458 | 2.0033 |  | 14.3522 | 41.3878 | 6.5438 |  | 62.2183 | 146.7191 | 12.9569 | 25.7122 | 4.0734 | 189 | 41.7862 | 55.4415 | 87.5414 | 0
15143 | 349.9344 | 0 | 8.7263 | 0 | 1.091 | 0.002376 | 21.9174 | 0.953 |  | 5.2345 | 17.0232 | 2.3807 |  | 0 | 0 | 4.8814 | 0 | 1.5887 | 167 | 4.5249 | 8.3621 | 10.4803 | 0
15144 | 912.4168 | 2.1994 | 25.085 | 84.4873 | -6.6016 | 8.55 | 56.1437 | 1.8996 |  | 13.0991 | 41.0829 | 5.9915 |  | 52.3146 | 135.9877 | 12.9679 | 25.6219 | 3.7446 | 160 | 35.2173 | 52.9824 | 86.02 | 0
15145 | 919.4363 | 2.108 | 25.7495 | 84.797 | -6.5749 | 8.55 | 54.3245 | 1.926 |  | 12.5605 | 41.3197 | 5.9827 |  | 48.5139 | 126.4408 | 9.7434 | 25.7011 | 3.0636 | 155 | 35.9964 | 53.3854 | 87.4358 | 0
15146 | 907.4306 | 2.1201 | 35.8385 | 84.8687 | -7.5142 | 9.4997 | 50.8187 | 1.6953 |  | 12.3586 | 41.4602 | 5.9177 |  | 45.2671 | 122.2619 | 9.1769 | 25.2615 | 2.9304 | 149 | 33.2345 | 52.6455 | 87.493 | 0
15147 | 896.3514 | 2.1223 | 38.8089 | 85.2906 | -5.5149 | 7.6005 | 53.6601 | 1.9223 |  | 11.6206 | 41.3415 | 5.8915 |  | 42.4425 | 122.2939 | 8.7134 | 25.0927 | 2.847 | 142 | 31.6089 | 52.2451 | 84.9133 | 0
15148 | 891.1423 | 2.611 | 39.9995 | 84.8454 | -6.5168 | 8.5497 | 55.9825 | 1.7688 |  | 11.2018 | 44.5669 | 5.8656 |  | 41.877 | 117.7009 | 8.3997 | 26.0296 | 2.7028 | 138 | 30.4506 | 51.7769 | 85.7423 | 0
15149 | 876.0007 | 3.4401 | 33.0487 | 84.658 | -6.611 | 8.55 | 56.5109 | 2.1378 |  | 11.2473 | 49.5117 | 5.8367 |  | 41.5842 | 114.4095 | 8.5385 | 27.0733 | 2.6978 | 131 | 29.3944 | 51.8422 | 86.6858 | 0
15150 | 870.8211 | 3.7588 | 44.58 | 84.7289 | -6.6079 | 8.55 | 47.3538 | 1.9147 |  | 10.5498 | 47.119 | 5.3575 |  | 42.0771 | 116.6502 | 8.4568 | 25.5315 | 2.6519 | 130 | 29.896 | 51.758 | 84.5721 | 0
15151 | 875.5996 | 3.9194 | 58.773 | 84.4626 | -6.5295 | 8.55 | 45.9946 | 1.7486 |  | 8.9891 | 42.1026 | 3.8498 |  | 41.1189 | 112.602 | 8.2848 | 24.3214 | 2.5583 | 139 | 41.0051 | 57.2259 | 83.823 | 0.051804
15152 | 892.2643 | 3.0198 | 64.8913 | 85.2618 | -6.5362 | 8.55 | 50.0798 | 1.3845 |  | 11.6101 | 43.9437 | 3.2748 |  | 42.3998 | 113.4683 | 8.5074 | 24.3201 | 2.5116 | 135 | 53.6848 | 69.3093 | 85.179 | 0.092949
15153 | 915.6043 | 2.5065 | 71.8051 | 90.9055 | -5.5042 | 7.6003 | 52.2102 | 1.7588 |  | 17.1556 | 49.09 | 3.2358 |  | 48.3036 | 115.8196 | 8.0722 | 24.5438 | 4.6796 | 133 | 55.272 | 69.8757 | 82.6784 | 0.091904
15154 | 952.3506 | 2.5944 | 75.5792 | 92.4813 | -6.4042 | 8.5497 | 56.432 | 1.7623 |  | 19.6265 | 52.1992 | 3.174 |  | 55.8898 | 126.3976 | 8.0624 | 24.5375 | 9.3811 | 158 | 48.8868 | 71.2293 | 88.3408 | 0.22297
15155 | 973.7667 | 2.3934 | 76.7765 | 92.81 | -6.3516 | 8.55 | 48.9715 | 1.3215 |  | 20.5287 | 51.796 | 3.2469 |  | 65.4436 | 135.321 | 8.5201 | 24.5576 | 12.1935 | 192 | 39.3248 | 72.123 | 89.5768 | 0.10469
15156 | 980.6917 | 4.0303 | 78.3241 | 92.278 | -5.3104 | 7.6003 | 49.053 | 1.5512 |  | 20.859 | 51.2041 | 6.3337 |  | 70.1812 | 140.1365 | 11.7598 | 24.5213 | 13.4352 | 204 | 34.6786 | 74.0384 | 87.922 | 0.17998
15157 | 985.7173 | 4.0154 | 68.9263 | 96.9244 | -5.2428 | 7.6 | 54.5116 | 1.3464 |  | 17.0126 | 51.2255 | 8.6598 |  | 72.1214 | 145.8587 | 11.7524 | 25.0523 | 14.4913 | 201 | 35.3121 | 74.7701 | 87.1717 | 0.068139
15158 | 995.362 | 2.4328 | 37.9669 | 99.258 | -4.1498 | 6.6503 | 56.0169 | 1.0183 |  | 12.9523 | 51.7011 | 8.4032 |  | 76.0105 | 146.3887 | 9.9486 | 25.3445 | 12.4048 | 201 | 34.7949 | 77.6337 | 87.0348 | 0.11162
15159 | 1000.1773 | 2.2459 | 24.6956 | 93.9903 | -5.1574 | 7.5997 | 55.0493 | 0.97812 |  | 11.6065 | 51.8165 | 8.5282 |  | 76.7214 | 150.1444 | 9.1338 | 24.8457 | 7.7025 | 200 | 32.7363 | 78.5156 | 88.6798 | 0.18355
15160 | 978.8465 | 2.7446 | 23.6218 | 89.5605 | -5.3661 | 7.6021 | 44.791 | 0.94704 |  | 11.4925 | 52.0133 | 8.2455 |  | 72.615 | 156.6546 | 8.4168 | 26.134 | 5.7934 | 208 | 29.7697 | 76.3181 | 89.0917 | 0.1372
15161 | 978.2957 | 2.923 | 23.1937 | 91.574 | -5.4371 | 7.5979 | 48.1566 | 1.5446 |  | 11.857 | 50.2981 | 7.8616 |  | 72.2871 | 153.6016 | 10.1748 | 27.5535 | 5.5805 | 216 | 31.717 | 62.5995 | 88.0147 | 0.057484
15162 | 955.0919 | 6.8638 | 25.034 | 92.7811 | -5.4831 | 7.6 | 56.5923 | 1.3346 |  | 11.0824 | 44.827 | 9.1713 |  | 75.018 | 153.3709 | 8.9764 | 27.6347 | 5.021 | 209 | 32.7018 | 60.3702 | 83.9462 | 0
15163 | 924.6325 | 10.0158 | 25.8101 | 90.0026 | -5.4898 | 7.6 | 61.0583 | 1.1691 |  | 11.7147 | 43.6672 | 8.0787 |  | 73.0526 | 150.143 | 8.3424 | 27.437 | 4.9591 | 208 | 29.8626 | 60.5928 | 86.8611 | 0
15164 | 917.7725 | 8.7185 | 25.3149 | 88.9709 | -5.3621 | 7.6 | 60.4283 | 2.232 |  | 12.8678 | 44.246 | 6.3058 |  | 64.2222 | 151.9584 | 10.0175 | 26.9442 | 4.8068 | 200 | 28.1427 | 59.1679 | 84.0099 | 0
15165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0
15166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0
15167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0
15168 | 876.6493 | 4.9219 | 24.2187 | 87.3668 | -5.2895 | 7.6 | 52.147 | 1.6446 |  | 11.9759 | 43.1392 | 5.8482 |  | 56.5336 | 137.2745 | 9.6155 | 26.2278 | 3.0158 | 152 | 29.0063 | 77.2452 | 82.3272 | 0
15169 | 887.912 | 3.0112 | 24.3587 | 87.4589 | -6.3775 | 8.5497 | 54.1575 | 1.2825 |  | 11.2043 | 42.5068 | 5.7368 |  | 47.886 | 135.5191 | 9.1112 | 25.2956 | 2.9828 | 150 | 27.8194 | 75.5894 | 87.3495 | 0
15170 | 878.9631 | 2.2104 | 24.0433 | 87.3863 | -18.3692 | 19.9468 | 54.1944 | 1.9506 |  | 10.6972 | 42.3545 | 5.733 |  | 43.9245 | 137.8237 | 9.7976 | 24.7416 | 3.1663 | 148 | 27.2749 | 75.4189 | 93.2579 | 0
15171 | 865.2085 | 2.1784 | 23.8126 | 87.2224 | -14.2644 | 16.1511 | 47.6161 | 1.6771 |  | 10.8457 | 42.6846 | 5.7682 |  | 42.7983 | 137.3575 | 9.3204 | 24.7796 | 3.1476 | 154 | 27.5418 | 75.7645 | 96.7432 | 0
15172 | 855.3664 | 2.6536 | 23.811 | 87.1012 | -12.2604 | 14.2505 | 51.612 | 2.1869 |  | 10.839 | 43.6449 | 5.698 |  | 43.2665 | 140.4944 | 10.2308 | 25.6757 | 3.0211 | 142 | 30.6701 | 75.8037 | 94.8113 | 0
15173 | 861.2483 | 3.4173 | 24.183 | 87.2798 | -6.2919 | 8.5516 | 55.8806 | 1.8249 |  | 10.7656 | 42.9176 | 5.6343 |  | 43.3973 | 139.644 | 9.1987 | 27.006 | 2.9892 | 128 | 34.9283 | 71.8201 | 93.2318 | 0
15174 | 871.9551 | 3.8271 | 23.8969 | 87.0372 | -5.2776 | 7.6003 | 55.4208 | 1.2132 |  | 10.1024 | 41.2119 | 6.2901 |  | 42.0443 | 128.6514 | 9.7317 | 25.9218 | 2.9468 | 126 | 33.0383 | 55.5715 | 90.6792 | 0
15175 | 888.4866 | 2.6432 | 23.3877 | 87.3568 | -5.4491 | 7.6 | 51.7379 | 1.7423 |  | 8.451 | 43.988 | 4.3439 |  | 41.8682 | 118.4643 | 10.0052 | 24.3579 | 2.8366 | 127 | 32.4112 | 57.104 | 85.1566 | 0.017025
15176 | 890.7214 | 1.7772 | 22.6968 | 87.9482 | -6.5153 | 8.5497 | 43.1659 | 1.4675 |  | 8.0507 | 48.3839 | 2.8552 |  | 48.089 | 120.0392 | 8.5609 | 24.0075 | 2.7937 | 126 | 29.2613 | 68.0823 | 81.8831 | 0.032241
15177 | 899.6071 | 2.0424 | 23.5648 | 89.7846 | -5.48 | 7.6003 | 46.7687 | 1.0418 |  | 8.7935 | 50.0465 | 2.8481 |  | 52.0618 | 124.367 | 9.5254 | 24.0832 | 3.1707 | 139 | 26.9495 | 71.7837 | 80.7096 | 0.073135
15178 | 928.0332 | 2.0532 | 24.1011 | 89.2585 | -5.5263 | 7.6 | 50.8801 | 1.605 |  | 9.5967 | 50.4936 | 3.1318 |  | 56.9455 | 137.0876 | 8.6825 | 23.9556 | 3.8831 | 172 | 26.0895 | 73.1587 | 85.4626 | 0.11868
15179 | 949.2938 | 1.8414 | 24.2626 | 89.1389 | -5.5462 | 7.6 | 55.0558 | 1.38 |  | 10.7382 | 50.4022 | 3.394 |  | 62.7631 | 149.2374 | 9.1867 | 23.8227 | 4.1942 | 157 | 26.5756 | 72.9141 | 88.9643 | 0.18091
15180 | 959.5255 | 2.0943 | 23.9217 | 89.8816 | -4.5676 | 6.6503 | 47.5023 | 1.2161 |  | 11.4546 | 50.819 | 5.6701 |  | 69.8126 | 153.1183 | 8.9995 | 24.938 | 4.2753 | 149 | 25.7261 | 73.1904 | 90.1424 | 0.17571
15181 | 954.0021 | 2.1226 | 23.268 | 90.7402 | -5.6962 | 7.5997 | 49.7294 | 0.95288 |  | 12.778 | 50.9035 | 7.7197 |  | 72.6257 | 161.6354 | 8.8663 | 26.5276 | 4.4859 | 159 | 26.929 | 75.6022 | 87.5065 | 0.19102
15182 | 946.4893 | 2.1977 | 24.7718 | 92.2211 | -6.5892 | 8.5497 | 54.7018 | 0.69413 |  | 12.3265 | 51.7767 | 6.7646 |  | 77.2316 | 165.7213 | 9.3578 | 26.4025 | 4.6772 | 168 | 26.4284 | 74.1817 | 88.5279 | 0.16566
15183 | 938.7554 | 2.359 | 24.4276 | 90.0572 | -4.5768 | 6.6505 | 55.5913 | 0.66067 |  | 11.1635 | 53.098 | 8.7399 |  | 78.5049 | 154.8437 | 9.1631 | 25.7824 | 4.804 | 180 | 26.8932 | 62.0555 | 87.9221 | 0.19814
15184 | 918.0257 | 2.6302 | 23.8073 | 87.9581 | -5.7361 | 7.5997 | 53.9457 | 0.63762 |  | 10.7268 | 51.5608 | 9.0754 |  | 74.8524 | 153.9354 | 8.3807 | 25.4753 | 4.7238 | 183 | 26.7472 | 60.7414 | 88.0376 | 0.12343
15185 | 924.0379 | 4.9163 | 24.2761 | 88.1964 | -4.6124 | 6.6503 | 50.7835 | 0.67911 |  | 10.8427 | 50.0278 | 7.6144 |  | 72.5101 | 160.5266 | 9.0808 | 25.2983 | 4.6262 | 169 | 28.3693 | 59.8869 | 82.4668 | 0.045388
15186 | 947.7578 | 8.9659 | 23.9383 | 89.1765 | -4.5995 | 6.65 | 44.7949 | 1.4891 |  | 11.2991 | 51.2825 | 8.0722 |  | 63.7077 | 163.2316 | 8.6062 | 25.7277 | 8.7291 | 141 | 31.3884 | 61.586 | 85.6696 | 0
15187 | 948.3026 | 7.799 | 24.1866 | 89.946 | -5.5506 | 7.5997 | 52.0714 | 1.5257 |  | 12.0991 | 52.0186 | 8.1747 |  | 60.3014 | 163.4111 | 9.0885 | 26.3865 | 12.8137 | 134 | 32.1608 | 59.7231 | 89.8808 | 0
15188 | 912.3895 | 4.8393 | 24.124 | 89.1393 | -6.299 | 8.5497 | 59.2501 | 1.9221 |  | 12.7873 | 47.5214 | 6.8843 |  | 64.9741 | 157.5096 | 9.6984 | 26.6628 | 13.8166 | 133 | 30.1388 | 56.9175 | 92.139 | 0
15189 | 893.7701 | 6.0439 | 21.8404 | 88.1083 | -5.2933 | 7.6003 | 58.8341 | 1.9219 |  | 11.894 | 44.1343 | 6.2635 |  | 62.0259 | 150.9599 | 9.2169 | 26.4476 | 13.6835 | 130 | 29.4142 | 56.4492 | 92.3836 | 0
15190 | 898.0582 | 4.8837 | 19.145 | 88.1257 | -6.394 | 8.5497 | 56.5614 | 1.5198 |  | 10.8421 | 43.2605 | 6.1421 |  | 54.8314 | 143.7634 | 9.8426 | 26.3141 | 13.1777 | 128 | 32.5676 | 58.5761 | 86.9896 | 0
15191 | 332.3692 | 0 | 6.3253 | 0 | 1.2215 | 0 | 20.7283 | 0.5537 |  | 4.0791 | 17.6424 | 2.3155 |  | 0 | 0 | 3.5497 | 0 | 5.0329 | 125 | 3.442 | 9.0096 | 10.1112 | 0
15192 | 903.4014 | 2.414 | 18.2232 | 87.2935 | -6.7375 | 8.55 | 48.7687 | 1.6702 |  | 12.3415 | 43.3427 | 5.8689 |  | 56.5116 | 128.3625 | 12.3812 | 25.9597 | 11.7345 | 115 | 31.8102 | 75.5412 | 86.7803 | 0
15193 | 893.9323 | 2.3621 | 18.4443 | 87.6724 | -5.6174 | 7.6003 | 53.3524 | 1.9599 |  | 13.1036 | 42.3336 | 5.7298 |  | 50.1116 | 123.1088 | 14.2797 | 24.948 | 11.6244 | 114 | 30.309 | 74.9034 | 88.1323 | 0
15194 | 882.1453 | 2.1785 | 28.5006 | 87.9593 | -6.4226 | 8.5497 | 54.9031 | 1.6901 |  | 13.1663 | 41.5938 | 6.259 |  | 46.7846 | 123.0787 | 13.4349 | 24.4692 | 11.5825 | 117 | 27.2838 | 74.9256 | 87.4252 | 0
15195 | 871.755 | 2.2278 | 32.383 | 87.1153 | -6.5105 | 8.55 | 49.8485 | 2.1538 |  | 13.1951 | 41.3794 | 6.7965 |  | 47.7974 | 121.3259 | 14.1517 | 24.4095 | 11.7054 | 116 | 24.5663 | 75.0514 | 87.3376 | 0
15196 | 858.6465 | 2.6526 | 31.4417 | 86.875 | -6.6756 | 8.55 | 49.2355 | 1.9078 |  | 13.9238 | 41.3158 | 7.3607 |  | 48.9254 | 118.8601 | 13.8304 | 25.3685 | 11.6627 | 111 | 28.9317 | 75.9415 | 93.0307 | 0
15197 | 873.2303 | 3.5578 | 30.5713 | 87.0828 | -5.7259 | 7.6003 | 54.6495 | 2.0555 |  | 16.3914 | 44.7929 | 8.3013 |  | 53.594 | 123.6775 | 10.414 | 26.4009 | 11.873 | 112 | 28.9309 | 71.359 | 101.3785 | 0
15198 | 919.8602 | 4.9445 | 47.9886 | 91.3441 | -7.7923 | 9.4995 | 65.9996 | 2.1222 |  | 20.798 | 50.1582 | 11.3158 |  | 77.2904 | 142.3669 | 12.6975 | 25.1729 | 12.8863 | 191 | 36.2469 | 60.3683 | 130.6011 | 0
15199 | 988.4113 | 8.369 | 76.8234 | 98.2536 | -14.9136 | 16.1482 | 81.2264 | 3.5593 |  | 29.3068 | 63.1795 | 18.1508 |  | 114.7482 | 191.5621 | 27.5134 | 26.885 | 13.9526 | 344 | 50.1166 | 79.2293 | 159.1686 | 0.045408
15200 | 1098.8104 | 12.2373 | 95.8703 | 110.8002 | -14.9279 | 16.15 | 97.3227 | 4.9617 |  | 37.0196 | 76.3011 | 28.7871 |  | 146.7775 | 245.7959 | 37.2299 | 31.1213 | 17.0449 | 322 | 61.2515 | 102.6006 | 166.3708 | 0.16343
15201 | 1184.2845 | 14.9842 | 105.1019 | 124.6554 | -13.7846 | 15.2003 | 109.8033 | 5.0872 |  | 41.0151 | 84.3937 | 35.2768 |  | 166.906 | 285.092 | 40.2837 | 34.4918 | 17.7704 | 346 | 55.6403 | 125.7392 | 182.9277 | 0.24097
15202 | 1246.1462 | 11.8921 | 108.8819 | 127.0177 | -14.0679 | 15.6749 | 121.5571 | 4.8963 |  | 38.985 | 90.8442 | 39.1609 |  | 180.3606 | 306.5176 | 42.1042 | 37.7591 | 17.6714 | 381 | 52.2855 | 131.2593 | 195.0823 | 0.25545
15203 | 1312.7434 | 6.3909 | 111.9386 | 127.5887 | -14.9035 | 15.6794 | 121.2843 | 4.6795 |  | 40.5929 | 95.6682 | 39.4001 |  | 191.1692 | 320.7059 | 40.4839 | 38.895 | 17.9423 | 354 | 53.153 | 147.7734 | 193.1662 | 0.20326
15204 | 1304.2596 | 4.7036 | 113.0121 | 128.901 | -16.4369 | 16.1499 | 116.3537 | 5.0299 |  | 38.1114 | 94.7384 | 37.8372 |  | 187.1728 | 321.4509 | 41.3293 | 37.612 | 17.7987 | 334 | 53.312 | 126.3877 | 191.2155 | 0.23543
15205 | 1286.1005 | 4.993 | 112.6091 | 130.2093 | -21.0259 | 20.8987 | 127.4419 | 5.3039 |  | 40.1268 | 91.871 | 40.2223 |  | 183.9982 | 316.2047 | 41.5832 | 39.546 | 17.5546 | 306 | 59.5302 | 135.5473 | 196.3168 | 0.26368
15206 | 1269.5942 | 8.9948 | 115.9609 | 132.1568 | -16.8072 | 18.0508 | 138.9474 | 4.6548 |  | 42.3898 | 91.3766 | 41.3981 |  | 184.8081 | 308.2882 | 41.9142 | 40.412 | 17.73 | 265 | 64.358 | 138.711 | 192.7536 | 0.26643
15207 | 1238.4571 | 8.8257 | 116.3015 | 129.94 | -13.9843 | 16.1505 | 139.1367 | 4.1343 |  | 36.9899 | 90.7763 | 33.601 |  | 177.352 | 294.3468 | 41.7597 | 39.552 | 18.164 | 275 | 69.3595 | 137.3879 | 192.1129 | 0.24108
15208 | 1195.5549 | 5.4708 | 112.1726 | 120.619 | -13.9635 | 16.15 | 110.5571 | 3.3015 |  | 31.4484 | 82.5878 | 21.9982 |  | 161.8206 | 272.1057 | 32.15 | 38.1558 | 18.2083 | 258 | 70.5732 | 124.632 | 175.2018 | 0.1628
15209 | 1151.1003 | 4.6591 | 109.8979 | 113.2402 | -7.3845 | 9.5018 | 82.9012 | 2.0446 |  | 26.2116 | 65.2675 | 16.0009 |  | 127.4591 | 236.7863 | 27.0577 | 35.7634 | 18.2285 | 224 | 53.6186 | 97.1249 | 135.5207 | 0.069699
15210 | 1112.823 | 4.8469 | 106.9227 | 101.2488 | -6.6387 | 7.6005 | 86.387 | 1.7793 |  | 18.8967 | 54.7349 | 14.482 |  | 87.713 | 204.9481 | 16.74 | 32.3014 | 17.364 | 215 | 49.0746 | 85.5197 | 120.0373 | 0
15211 | 1073.2599 | 4.6386 | 91.2839 | 95.6316 | -14.5657 | 14.2482 | 82.2125 | 1.5674 |  | 14.681 | 54.3665 | 15.592 |  | 75.202 | 185.5384 | 10.8963 | 29.4682 | 15.2804 | 207 | 44.0059 | 78.8722 | 106.74 | 0
15212 | 1028.3496 | 6.4552 | 58.5318 | 98.0895 | -9.6348 | 9.5013 | 61.7082 | 1.4386 |  | 13.8233 | 55.4025 | 10.9652 |  | 71.266 | 175.253 | 10.6173 | 28.0631 | 13.605 | 189 | 43.4336 | 72.7682 | 102.8824 | 0
15213 | 1001.0459 | 6.5885 | 39.6178 | 95.1381 | -7.6333 | 7.6005 | 55.5195 | 2.1555 |  | 13.5782 | 53.7913 | 7.2229 |  | 64.9905 | 161.426 | 10.2678 | 27.8952 | 13.0319 | 176 | 34.2456 | 0 | 101.0123 | 0
15214 | 979.6813 | 4.0258 | 31.2716 | 89.7323 | -17.6311 | 17.0974 | 58.2317 | 1.7922 |  | 13.2082 | 47.8849 | 7.1466 |  | 59.4305 | 151.2609 | 9.6513 | 28.1046 | 12.3114 | 154 | 35.273 | 57.9778 | 100.0102 | 0
15215 | 357.8474 | 0 | 9.7803 | 0 | 0.17234 | 0.004751 | 21.9291 | 0.51078 |  | 5.0159 | 18.3812 | 2.7608 |  | 0 | 0 | 3.2008 | 0 | 4.6333 | 138 | 3.5412 | 8.3432 | 11.4821 | 0
15216 | 940.5191 | 2.2212 | 29.3713 | 87.7938 | -19.6345 | 19.0011 | 49.0119 | 1.9707 |  | 14.8116 | 44.7446 | 6.4833 |  | 55.2657 | 130.8018 | 10.3554 | 27.6946 | 12.2778 | 125 | 32.3534 | 54.3032 | 100.6022 | 0
15217 | 925.8167 | 2.3014 | 30.0427 | 87.6707 | -15.6334 | 15.2011 | 56.0454 | 1.9646 |  | 15.6199 | 44.4435 | 6.4659 |  | 52.0259 | 129.9166 | 11.0647 | 27.7623 | 12.3229 | 122 | 32.0236 | 54.5003 | 100.2815 | 0
15218 | 926.5995 | 4.1247 | 38.4397 | 87.6006 | -15.6335 | 15.2 | 54.0413 | 2.1804 |  | 15.7097 | 44.5995 | 6.374 |  | 50.8159 | 129.4468 | 10.1841 | 27.7741 | 11.9489 | 121 | 33.655 | 53.9034 | 100.1825 | 0
15219 | 920.149 | 7.6483 | 39.7447 | 88.7162 | -14.6327 | 14.2503 | 45.9142 | 1.7905 |  | 15.7365 | 44.7008 | 6.2554 |  | 50.7934 | 128.6088 | 9.8058 | 27.7782 | 11.777 | 120 | 32.6022 | 53.6563 | 100.4915 | 0
15220 | 908.8136 | 8.0979 | 36.6052 | 88.5512 | -13.6322 | 13.3003 | 44.1411 | 2.04 |  | 16.5185 | 46.7649 | 6.2513 |  | 50.7432 | 123.7412 | 11.4593 | 27.7707 | 11.7868 | 119 | 31.2786 | 54.0832 | 104.5226 | 0
15221 | 933.7864 | 5.3909 | 31.792 | 87.6409 | -13.6323 | 13.3 | 53.4577 | 1.7706 |  | 19.9936 | 50.1543 | 8.2884 |  | 56.2646 | 126.765 | 10.1507 | 27.7472 | 11.9592 | 114 | 32.848 | 55.3923 | 113.8901 | 0
15222 | 984.9069 | 8.3908 | 40.9396 | 93.7087 | -13.6348 | 13.3 | 71.3588 | 2.1657 |  | 23.3159 | 53.5307 | 14.6448 |  | 79.9011 | 139.9866 | 13.8702 | 27.5442 | 12.0149 | 191 | 37.7587 | 58.3719 | 141.0793 | 0
15223 | 1060.474 | 12.4161 | 68.73 | 102.1994 | -21.6416 | 20.8979 | 93.4531 | 3.2535 |  | 27.1641 | 65.7952 | 23.4135 |  | 117.9993 | 183.9943 | 27.2398 | 30.1635 | 13.4704 | 258 | 57.2147 | 85.1584 | 169.6702 | 0
15224 | 1184.7139 | 11.2008 | 93.323 | 115.679 | -21.6457 | 20.9 | 110.5342 | 5.0154 |  | 34.5108 | 79.0134 | 34.9304 |  | 150.9116 | 244.1816 | 38.2334 | 34.8668 | 16.054 | 325 | 72.6184 | 126.3648 | 190.865 | 0.064144
15225 | 1284.0461 | 13.8744 | 102.0906 | 124.8766 | -23.6423 | 22.7995 | 118.0593 | 5.3058 |  | 39.297 | 85.8242 | 39.5738 |  | 169.9393 | 291.9757 | 40.8872 | 39.4666 | 17.8981 | 362 | 67.8439 | 149.9948 | 202.0747 | 0.10283
15226 | 1339.4763 | 16.5929 | 104.405 | 124.8765 | -21.6451 | 20.9005 | 125.0041 | 4.8665 |  | 39.9473 | 89.2363 | 40.2269 |  | 181.261 | 315.1661 | 42.9498 | 41.2733 | 18.5155 | 392 | 65.4165 | 152.7723 | 206.4905 | 0.05601
15227 | 1356.9823 | 14.7845 | 114.1432 | 129.2164 | -24.6455 | 23.7492 | 131.891 | 4.7229 |  | 42.4792 | 90.1963 | 40.4436 |  | 197.1834 | 330.9948 | 44.1455 | 42.179 | 18.7082 | 371 | 78.5939 | 168.3572 | 201.096 | 0.073658
15228 | 1323.212 | 9.5177 | 120.0349 | 130.0681 | -23.6449 | 22.8003 | 140.9347 | 4.9716 |  | 40.3343 | 90.6722 | 39.715 |  | 199.8417 | 327.3584 | 43.2558 | 42.4771 | 18.7059 | 372 | 72.6404 | 152.4364 | 197.805 | 0.068375
15229 | 1307.6236 | 6.8709 | 118.7579 | 130.7139 | -24.6424 | 23.7497 | 150.3783 | 5.5854 |  | 42.8993 | 90.3923 | 39.1795 |  | 199.6344 | 322.1585 | 43.3849 | 43.0227 | 18.6279 | 310 | 84.4269 | 159.5997 | 211.4896 | 0.11063
15230 | 1296.8813 | 5.829 | 117.26 | 132.2845 | -22.6443 | 21.8505 | 152.3376 | 4.9236 |  | 43.3489 | 90.6648 | 35.8026 |  | 197.3539 | 325.5965 | 43.1594 | 42.6915 | 18.488 | 304 | 86.8244 | 158.9265 | 197.6778 | 0.085451
15231 | 1270.9284 | 4.46 | 112.1093 | 129.8118 | -21.6465 | 20.9003 | 137.6397 | 4.0186 |  | 34.7062 | 91.1203 | 28.6657 |  | 186.6075 | 315.4909 | 41.2318 | 41.2173 | 18.427 | 297 | 84.3638 | 151.272 | 197.0542 | 0.13895
15232 | 1211.0443 | 6.9309 | 110.0678 | 124.8629 | -19.8922 | 19.9503 | 112.1968 | 2.8723 |  | 26.4032 | 84.7309 | 17.7082 |  | 176.4025 | 284.4884 | 31.7252 | 40.2977 | 18.0256 | 265 | 81.1545 | 135.0562 | 176.7553 | 0.026103
15233 | 1143.4298 | 6.514 | 112.7394 | 115.0673 | -11.0509 | 12.3521 | 79.7 | 1.4917 |  | 19.2858 | 67.0208 | 13.6027 |  | 146.3147 | 241.9901 | 17.7046 | 36.0797 | 16.975 | 230 | 62.6588 | 116.3855 | 134.9684 | 0.020128
15234 | 1081.3253 | 6.6036 | 106.6687 | 101.0531 | -9.2773 | 10.4505 | 73.2256 | 1.4696 |  | 13.3022 | 55.8409 | 13.3572 |  | 110.581 | 210.8037 | 10.6398 | 31.7804 | 15.1056 | 231 | 55.3373 | 89.009 | 112.6819 | 0
15235 | 1072.0556 | 6.8386 | 88.1949 | 95.9232 | -11.1654 | 11.3997 | 75.2641 | 1.4546 |  | 13.43 | 55.8439 | 13.2904 |  | 99.1727 | 202.3638 | 10.4308 | 29.4601 | 14.6966 | 198 | 52.1116 | 86.9173 | 96.0852 | 0
15236 | 1023.9157 | 6.6187 | 40.8315 | 91.0376 | -12.6315 | 12.3497 | 66.7966 | 1.4285 |  | 13.8429 | 54.3145 | 12.1639 |  | 87.7444 | 182.8358 | 10.3582 | 28.199 | 14.5751 | 190 | 45.201 | 85.2123 | 92.5643 | 0
15237 | 991.707 | 8.498 | 20.0136 | 88.4934 | -11.6355 | 11.4003 | 60.1328 | 1.3631 |  | 12.6249 | 51.0964 | 11.4375 |  | 74.4778 | 162.639 | 9.9793 | 27.7055 | 14.1923 | 169 | 37.0811 | 80.6864 | 92.9694 | 0
15238 | 964.1226 | 7.9579 | 18.5381 | 88.1717 | -11.6367 | 11.4 | 53.3591 | 1.6158 |  | 11.1164 | 46.0834 | 11.3794 |  | 71.8572 | 151.1791 | 9.3475 | 27.2208 | 13.4107 | 152 | 36.5698 | 69.1915 | 90.0797 | 0
15239 | 341.9883 | 0 | 6.1407 | 0 | 0.17074 | 0.003167 | 18.3102 | 0.69442 |  | 3.9758 | 17.576 | 4.2304 |  | 0 | 0 | 3.0052 | 0 | 4.9855 | 140 | 3.4681 | 9.7781 | 8.6705 | 0
15240 | 929.7618 | 4.0301 | 17.9975 | 88.9272 | -12.6335 | 12.3495 | 51.0235 | 1.5726 |  | 12.1395 | 42.9628 | 11.6626 |  | 66.7772 | 128.9517 | 10.013 | 27.0468 | 11.9742 | 128 | 30.9785 | 57.0099 | 91.1406 | 0
15241 | 931.9386 | 5.7311 | 19.0552 | 89.1181 | -7.6359 | 7.6013 | 53.4318 | 2.0047 |  | 12.8837 | 42.9548 | 11.6226 |  | 65.1927 | 124.1581 | 10.3604 | 27.1185 | 11.6992 | 119 | 33.5704 | 58.335 | 91.0533 | 0
15242 | 914.4131 | 8.6578 | 29.5425 | 87.9087 | -8.6336 | 8.5497 | 52.9744 | 1.6729 |  | 12.9256 | 42.6457 | 11.5092 |  | 63.9864 | 121.4921 | 9.526 | 27.1647 | 11.7148 | 122 | 33.4305 | 62.5686 | 90.4994 | 0
15243 | 903.3593 | 7.218 | 36.2109 | 87.5288 | -9.6312 | 9.4997 | 42.8002 | 1.2793 |  | 12.9651 | 41.9975 | 11.4319 |  | 63.3599 | 122.9486 | 9.5584 | 27.1511 | 11.7045 | 116 | 31.9446 | 63.0958 | 93.0661 | 0
15244 | 906.1406 | 4.1998 | 34.7518 | 87.096 | -12.6331 | 12.3492 | 50.9949 | 1.8985 |  | 13.7439 | 41.6789 | 11.4429 |  | 63.4136 | 118.792 | 10.5778 | 27.0064 | 11.6951 | 117 | 35.4707 | 63.4193 | 92.6752 | 0
15245 | 928.6305 | 3.5166 | 32.1624 | 86.9858 | -9.6374 | 9.5008 | 58.6832 | 1.6346 |  | 16.7388 | 45.7091 | 13.2458 |  | 64.7955 | 123.3939 | 9.6801 | 26.9695 | 11.687 | 109 | 33.3475 | 61.5635 | 104.1221 | 0
15246 | 975.7552 | 9.6976 | 54.4282 | 92.6704 | -11.6385 | 11.3995 | 68.3705 | 2.2063 |  | 21.3429 | 50.9924 | 13.159 |  | 84.4372 | 130.4503 | 13.9727 | 27.1805 | 12.1221 | 179 | 39.2965 | 61.6127 | 120.7402 | 0
15247 | 1046.4666 | 16.2049 | 78.4857 | 99.6895 | -20.6408 | 19.9476 | 88.3869 | 2.6551 |  | 27.6748 | 64.5233 | 19.7695 |  | 118.9781 | 182.3226 | 27.3843 | 28.3731 | 14.6833 | 276 | 56.1427 | 84.304 | 154.8165 | 0
15248 | 1145.94 | 13.8837 | 92.8759 | 114.2353 | -20.6473 | 19.95 | 101.2357 | 3.7203 |  | 35.2159 | 79.3558 | 33.2999 |  | 149.502 | 250.4511 | 36.0261 | 32.1897 | 16.0923 | 318 | 64.3821 | 102.9783 | 172.4303 | 0.057426
15249 | 1223.1936 | 11.3063 | 100.9519 | 124.6115 | -23.6453 | 22.7992 | 109.8512 | 4.2655 |  | 43.0246 | 85.6357 | 39.7509 |  | 167.4271 | 300.8831 | 40.7582 | 35.6129 | 16.2237 | 326 | 67.7656 | 120.3392 | 187.5745 | 0.15998
15250 | 1275.5608 | 9.2291 | 106.324 | 128.3849 | -20.6476 | 19.9508 | 116.3883 | 4.5511 |  | 45.6567 | 88.9616 | 40.7727 |  | 173.7135 | 319.0206 | 40.4676 | 45.7231 | 16.7475 | 348 | 76.6446 | 133.6797 | 200.0342 | 0.25815
15251 | 1296.1388 | 5.4194 | 111.801 | 129.1491 | -19.6489 | 19.0003 | 123.7417 | 4.9026 |  | 50.391 | 90.7031 | 40.0561 |  | 183.3435 | 326.7949 | 38.9649 | 51.4315 | 17.1046 | 350 | 77.5032 | 159.1728 | 202.1102 | 0.2351
15252 | 1286.4985 | 4.2883 | 116.166 | 127.1305 | -22.6482 | 21.8492 | 133.5818 | 5.1437 |  | 47.5308 | 89.8246 | 38.9926 |  | 184.9738 | 332.4093 | 40.321 | 49.8708 | 17.2085 | 367 | 70.1235 | 169.4038 | 194.9365 | 0.24341
15253 | 1273.7616 | 5.7321 | 119.0688 | 129.8023 | -22.5884 | 21.85 | 144.4236 | 5.0061 |  | 44.3929 | 91.2794 | 39.0875 |  | 184.3873 | 326.8576 | 33.0219 | 49.662 | 17.2451 | 312 | 74.6446 | 176.3872 | 198.8859 | 0.27249
15254 | 1291.3357 | 9.1627 | 123.551 | 132.4427 | -19.6486 | 19.9505 | 140.7886 | 4.3879 |  | 45.0017 | 93.062 | 39.3369 |  | 188.1938 | 321.5908 | 27.7153 | 50.6497 | 17.447 | 284 | 76.7437 | 168.3324 | 214.9441 | 0.2533
15255 | 1245.4103 | 11.052 | 118.9848 | 126.2163 | -20.2827 | 21.8495 | 135.8729 | 3.8002 |  | 43.2765 | 92.2375 | 35.4047 |  | 185.0775 | 309.0699 | 32.6243 | 51.8586 | 17.4469 | 279 | 75.571 | 156.4324 | 208.9166 | 0.21048
15256 | 1146.9631 | 11.0444 | 113.1439 | 118.082 | -21.4494 | 23.7495 | 117.82 | 2.9577 |  | 37.1274 | 83.8097 | 26.8695 |  | 172.025 | 281.9457 | 30.0646 | 50.5379 | 16.833 | 257 | 68.4541 | 133.5028 | 171.3743 | 0.16201
15257 | 1098.7877 | 8.5364 | 111.3247 | 111.7157 | -9.0085 | 12.3532 | 81.6346 | 2.2962 |  | 31.9454 | 67.0364 | 18.5879 |  | 138.5863 | 248.5488 | 20.6643 | 47.5959 | 16.2981 | 217 | 55.6257 | 114.8071 | 132.3205 | 0.076228
15258 | 1070.0648 | 7.4816 | 103.7853 | 104.1699 | -7.0213 | 10.4505 | 67.6221 | 1.6814 |  | 25.0449 | 57.3332 | 11.8314 |  | 103.973 | 211.3217 | 13.4898 | 44.1643 | 16.3469 | 223 | 50.9313 | 98.6866 | 118.6228 | 0
15259 | 1053.2636 | 7.0179 | 87.6986 | 98.364 | -8.6381 | 11.3997 | 70.0978 | 2.5357 |  | 20.559 | 57.1533 | 9.021 |  | 90.5453 | 191.3694 | 18.121 | 40.8048 | 16.157 | 190 | 47.5045 | 90.0694 | 106.6791 | 0
15260 | 1023.0471 | 6.6063 | 56.2474 | 91.2825 | -7.6935 | 9.5005 | 63.4871 | 2.043 |  | 18.4082 | 56.4292 | 8.1963 |  | 73.2017 | 179.35 | 15.7332 | 39.1747 | 15.2085 | 173 | 41.162 | 90.4479 | 101.5854 | 0
15261 | 983.612 | 7.3187 | 40.9784 | 88.5523 | -12.0022 | 12.3492 | 49.6969 | 1.4464 |  | 16.7916 | 52.9739 | 7.245 |  | 59.1492 | 165.2004 | 12.4265 | 39.0027 | 13.6493 | 155 | 35.5768 | 84.8908 | 95.2968 | 0
15262 | 955.5775 | 7.3861 | 30.9748 | 87.8465 | -9.6353 | 9.5008 | 51.9188 | 2.0134 |  | 15.408 | 51.8629 | 7.2412 |  | 54.4503 | 147.9096 | 10.1224 | 38.9932 | 13.8888 | 150 | 40.3684 | 73.9507 | 96.0179 | 0
15263 | 357.5534 | 0 | 9.2424 | 0 | 0.17721 | 0.00264 | 21.5837 | 0.91338 |  | 5.8176 | 21.9871 | 2.9208 |  | 0 | 0 | 3.1119 | 0 | 5.7743 | 134 | 4.4229 | 11.4099 | 10.3533 | 0
15264 | 914.8661 | 5.6422 | 20.3599 | 88.1089 | -12.6299 | 12.3495 | 53.8687 | 2.0727 |  | 14.8356 | 46.4899 | 6.4627 |  | 46.6963 | 142.3442 | 11.1983 | 38.687 | 12.512 | 124 | 35.6464 | 58.5893 | 90.7162 | 0
15265 | 908.9824 | 3.5311 | 20.7176 | 87.9599 | -12.6306 | 12.35 | 54.9233 | 1.7719 |  | 15.3117 | 44.5506 | 6.3882 |  | 49.2478 | 142.2912 | 9.9076 | 38.7469 | 12.214 | 118 | 35.329 | 54.797 | 92.3161 | 0
15266 | 894.1764 | 2.4015 | 30.0326 | 88.9084 | -10.6312 | 10.4505 | 46.0977 | 1.9623 |  | 15.5422 | 43.6609 | 6.4089 |  | 47.7715 | 134.8162 | 9.6782 | 38.7324 | 12.1624 | 120 | 32.3126 | 61.5067 | 91.3007 | 0
15267 | 884.4651 | 2.5751 | 25.1052 | 88.5187 | -12.6309 | 12.3495 | 52.3065 | 1.7362 |  | 15.6736 | 42.6518 | 6.3608 |  | 44.4797 | 127.6379 | 10.6676 | 38.6729 | 11.9994 | 112 | 31.887 | 63.0425 | 91.631 | 0
15268 | 890.9231 | 2.8733 | 20.0068 | 87.7744 | -11.6347 | 11.4003 | 57.8197 | 2.0733 |  | 16.8103 | 42.262 | 6.2859 |  | 44.1527 | 119.3315 | 9.5555 | 38.7178 | 12.0268 | 107 | 34.8255 | 63.1801 | 94.2278 | 0
15269 | 909.8426 | 3.5341 | 30.346 | 87.6347 | -10.6324 | 10.4503 | 57.0862 | 1.8761 |  | 20.3181 | 44.9462 | 8.1412 |  | 50.4915 | 123.1711 | 10.4136 | 38.746 | 12.2633 | 110 | 32.3363 | 65.5924 | 105.0702 | 0
15270 | 946.8471 | 4.8282 | 49.3346 | 93.4655 | -11.6353 | 11.3997 | 70.4656 | 1.974 |  | 23.2887 | 49.8255 | 13.1183 |  | 80.5477 | 133.7924 | 13.9988 | 38.6148 | 12.4451 | 169 | 36.8266 | 61.0563 | 128.3688 | 0
15271 | 1031.287 | 9.5142 | 75.5308 | 100.7237 | -20.6407 | 19.9476 | 84.787 | 3.074 |  | 25.0035 | 63.2286 | 22.1547 |  | 119.2881 | 185.8291 | 26.7122 | 40.1792 | 12.6906 | 260 | 55.4015 | 94.1155 | 155.1328 | 0
15272 | 1123.7888 | 10.0582 | 95.6311 | 115.2337 | -22.6418 | 21.8495 | 96.1593 | 5.1684 |  | 28.2968 | 77.9864 | 30.2835 |  | 148.1676 | 248.2941 | 38.2757 | 45.5129 | 14.8489 | 306 | 67.6009 | 131.7821 | 183.2505 | 0.075763
15273 | 1204.4745 | 9.4775 | 110.6124 | 122.5131 | -24.6433 | 23.7495 | 109.6777 | 5.1448 |  | 34.7386 | 86.3815 | 34.3958 |  | 163.7596 | 289.431 | 42.358 | 50.2798 | 16.1606 | 370 | 70.0592 | 147.3858 | 187.4802 | 0.086755
15274 | 1234.7886 | 11.2988 | 111.9022 | 122.1879 | -23.6444 | 22.8003 | 125.9093 | 4.267 |  | 42.6037 | 89.8631 | 39.3178 |  | 172.1265 | 308.498 | 42.0114 | 53.4254 | 16.0579 | 389 | 63.5721 | 168.7258 | 191.4345 | 0.072664
15275 | 1236.2881 | 10.6247 | 114.2954 | 123.0036 | -21.6451 | 20.9005 | 135.6749 | 4.4532 |  | 43.726 | 89.2355 | 39.5347 |  | 181.9955 | 322.2275 | 36.5143 | 53.7211 | 16.5755 | 334 | 63.9368 | 178.9305 | 196.6567 | 0.075714
15276 | 1246.9895 | 9.7889 | 115.992 | 123.5385 | -21.6479 | 20.9 | 144.7116 | 4.9034 |  | 43.859 | 88.3954 | 39.5631 |  | 180.6427 | 324.1384 | 32.8664 | 53.6325 | 17.7179 | 349 | 64.6848 | 152.4428 | 188.5048 | 0.06599
15277 | 1254.2699 | 11.4118 | 114.2315 | 129.3514 | -21.6476 | 20.9 | 143.1733 | 5.0162 |  | 40.695 | 88.2744 | 41.6583 |  | 183.7186 | 314.3329 | 30.2132 | 53.533 | 18.297 | 297 | 69.7414 | 153.273 | 191.0452 | 0.063592
15278 | 1246.6958 | 14.023 | 114.1561 | 130.4431 | -22.6453 | 21.8497 | 140.1831 | 4.919 |  | 36.3932 | 89.0337 | 41.6364 |  | 185.2911 | 313.7954 | 29.001 | 51.9924 | 18.1733 | 339 | 59.0227 | 150.933 | 186.7934 | 0.10989
15279 | 1221.5727 | 11.2015 | 112.6123 | 125.0012 | -20.6463 | 19.9505 | 141.1142 | 4.5957 |  | 32.8642 | 89.5201 | 34.2571 |  | 177.544 | 312.4493 | 34.8009 | 50.6879 | 18.5201 | 272 | 65.0911 | 138.7983 | 186.0134 | 0.041101
15280 | 1186.2591 | 6.7072 | 110.5714 | 117.9263 | -20.4885 | 19.95 | 120.3943 | 3.7769 |  | 30.2142 | 82.5791 | 20.7348 |  | 164.492 | 276.7851 | 29.8468 | 48.2528 | 18.2362 | 269 | 62.848 | 124.1449 | 162.6467 | 0.047535
15281 | 1141.6415 | 4.2953 | 110.0718 | 111.0173 | -15.0625 | 15.2013 | 96.2116 | 3.0833 |  | 27.0495 | 67.0248 | 18.9039 |  | 130.9776 | 235.5479 | 17.7137 | 47.5955 | 17.8856 | 250 | 52.4231 | 104.4286 | 121.2764 | 0.012945
15282 | 1084.0805 | 4.4209 | 101.183 | 100.3196 | -11.2432 | 11.4011 | 90.2009 | 1.8058 |  | 19.6658 | 58.2562 | 17.5864 |  | 95.1345 | 212.406 | 11.6415 | 45.0468 | 17.016 | 216 | 47.3573 | 90.9232 | 105.5667 | 0
15283 | 1044.8055 | 5.0825 | 78.6233 | 97.6994 | -11.637 | 11.4 | 85.0581 | 1.2143 |  | 16.3847 | 57.6716 | 15.2111 |  | 84.3418 | 194.4305 | 9.8712 | 43.4317 | 15.6693 | 204 | 47.0017 | 85.3081 | 94.5277 | 0
15284 | 1012.7475 | 5.0222 | 40.7521 | 93.8983 | -13.636 | 13.2995 | 75.9954 | 2.0407 |  | 16.1423 | 56.6147 | 12.4495 |  | 73.2107 | 175.1469 | 9.4732 | 43.203 | 15.0382 | 206 | 44.1949 | 80.2899 | 92.842 | 0
15285 | 981.5564 | 4.3752 | 25.3544 | 90.8309 | -10.6362 | 10.4508 | 65.1002 | 1.7358 |  | 14.4025 | 54.1007 | 10.6075 |  | 59.5584 | 162.3748 | 9.3136 | 43.4944 | 12.5245 | 198 | 38.2896 | 73.8843 | 92.6833 | 0
15286 | 956.4828 | 3.3405 | 25.2521 | 89.8625 | -11.6346 | 11.3997 | 59.8534 | 1.9091 |  | 12.6928 | 49.4343 | 10.4551 |  | 51.8343 | 157.1218 | 10.3947 | 43.4348 | 7.4897 | 179 | 33.9588 | 62.5111 | 89.6746 | 0
15287 | 350.483 | 0 | 8.6993 | 29.9739 | 0.17584 | 0.003167 | 22.1734 | 0.91309 |  | 4.6946 | 19.3007 | 3.975 |  | 17.2897 | 61.3499 | 3.7807 | 14.7037 | 2.0286 | 162 | 3.5669 | 9.1569 | 10.2476 | 0
15288 | 923.3079 | 2.2939 | 24.6439 | 88.9819 | -12.6305 | 12.35 | 51.5712 | 2.1607 |  | 12.971 | 45.6083 | 10.2145 |  | 46.435 | 135.773 | 9.7831 | 43.3648 | 5.0939 | 153 | 34.098 | 56.8937 | 84.4811 | 0
15289 | 920.7388 | 2.1547 | 25.1865 | 88.9645 | -12.6287 | 12.35 | 52.5356 | 1.8376 |  | 13.623 | 44.2052 | 10.1046 |  | 44.5117 | 127.2973 | 10.1314 | 43.4976 | 4.3991 | 133 | 30.3561 | 56.722 | 88.0185
15290 | 905.5296 | 2.1083 | 33.9712 | 88.8644 | -10.6324 | 10.4505 | 51.1883 | 1.8192 |  | 13.6945 | 43.5449 | 10.0819 |  | 44.1341 | 126.2709 | 8.9909 | 43.4274 | 3.3081 | 132 | 27.86 | 57.2104 | 87.5337
15291 | 898.5177 | 2.3169 | 40.8514 | 88.805 | -10.6332 | 10.45 | 48.8404 | 1.7144 |  | 13.7506 | 43.3678 | 10.1192 |  | 44.3631 | 123.5401 | 10.4213 | 43.3011 | 2.8647 | 123 | 27.1995 | 57.0867 | 85.6734
15292 | 904.3645 | 2.8581 | 37.8293 | 89.1629 | -13.6306 | 13.2992 | 52.042 | 1.4919 |  | 14.5112 | 43.3396 | 10.074 |  | 43.8908 | 121.0101 | 9.5021 | 43.1673 | 2.9617 | 119 | 27.4947 | 57.592 | 90.946
15293 | 924.4484 | 6.7457 | 38.7915 | 88.9692 | -10.6327 | 10.4508 | 55.4092 | 1.8922 |  | 17.5186 | 46.6722 | 11.1991 |  | 49.8068 | 122.5232 | 9.6032 | 43.1554 | 2.933 | 119 | 27.516 | 73.9788 | 97.8796
15294 | 974.5411 | 8.1632 | 53.5291 | 95.2306 | -11.637 | 11.3997 | 67.6192 | 2.249 |  | 21.8617 | 57.5799 | 16.7653 |  | 77.2749 | 132.64 | 13.6803 | 43.1602 | 5.5676 | 167 | 33.1635 | 85.4206 | 119.8444
15295 | 1029.0798 | 9.0854 | 78.338 | 98.7442 | -19.6411 | 18.9979 | 86.3475 | 3.2168 |  | 28.1307 | 69.8721 | 22.2413 |  | 120.6517 | 183.3604 | 25.9134 | 44.9925 | 12.9791 | 252 | 49.8768 | 96.6722 | 151.8125
15296 | 1113.3806 | 8.2535 | 100.7396 | 108.9213 | -20.644 | 19.9497 | 101.0262 | 4.3749 |  | 36.0849 | 78.1897 | 31.9073 |  | 156.0269 | 250.3577 | 37.0222 | 50.1426 | 18.577 | 282 | 64.0475 | 112.1225 | 184.4007
15297 | 1201.7973 | 9.1766 | 108.0983 | 124.5916 | -20.6436 | 19.95 | 107.1235 | 5.0365 |  | 41.674 | 84.8538 | 38.1163 |  | 171.4564 | 295.2806 | 39.4967 | 53.7077 | 18.7832 | 368 | 70.2977 | 132.2445 | 191.7448
15298 | 1236.4153 | 12.9293 | 107.9125 | 128.1555 | -24.6429 | 23.7489 | 112.8604 | 4.8891 |  | 44.2251 | 89.6986 | 39.4656 |  | 179.6231 | 321.886 | 40.8194 | 57.7118 | 19.2892 | 359 | 75.0108 | 140.6413 | 198.0004
15299 | 1251.1213 | 10.4781 | 109.5621 | 128.9163 | -25.6455 | 24.6997 | 119.3643 | 4.7215 |  | 43.7727 | 90.6229 | 39.0371 |  | 187.7764 | 327.3422 | 41.9342 | 57.5159 | 19.9521 | 324 | 67.1582 | 150.0121 | 197.1887
15300 | 1259.1832 | 7.4608 | 113.672 | 131.632 | -22.6468 | 21.8508 | 137.4663 | 4.7574 |  | 37.7624 | 91.0547 | 38.4997 |  | 186.6147 | 319.1282 | 43.5702 | 55.3489 | 18.679 | 354 | 59.6097 | 131.8151 | 197.1295
15301 | 1266.9121 | 6.7798 | 113.3676 | 138.2657 | -23.6457 | 22.7997 | 137.6232 | 4.3266 |  | 32.8917 | 92.2881 | 38.6013 |  | 186.9738 | 318.0593 | 42.8622 | 55.0333 | 18.0181 | 319 | 61.9367 | 137.7075 | 196.3664
15302 | 1241.4449 | 7.1306 | 110.6724 | 141.6833 | -24.6449 | 23.7497 | 127.1637 | 4.2191 |  | 33.6385 | 91.0024 | 37.6087 |  | 186.4544 | 311.0459 | 41.3716 | 54.9268 | 17.9223 | 294 | 62.7496 | 147.5644 | 187.7224
15303 | 1208.6403 | 7.8519 | 110.5785 | 132.592 | -31.6411 | 30.3982 | 127.3758 | 4.0511 |  | 31.3665 | 89.9556 | 31.6895 |  | 179.5693 | 295.5243 | 40.1508 | 53.3506 | 17.694 | 304 | 54.2125 | 139.6302 | 181.7054
15304 | 1147.3507 | 6.7859 | 106.1772 | 123.6282 | -16.6498 | 16.154 | 112.7578 | 2.85 |  | 24.9806 | 83.4117 | 20.4755 |  | 168.126 | 268.6035 | 31.1399 | 50.5014 | 16.3544 | 289 | 51.2176 | 123.8224 | 167.8022
15305 | 1099.8261 | 4.3335 | 91.5159 | 119.1596 | -17.6455 | 17.0997 | 74.3953 | 2.28 |  | 21.4141 | 67.167 | 12.4904 |  | 136.7739 | 234.9298 | 20.2162 | 44.3054 | 15.2539 | 267 | 41.2617 | 110.0977 | 135.7008
15306 | 1061.1221 | 3.8828 | 50.8936 | 109.6582 | -11.6409 | 11.4016 | 57.9388 | 2.4139 |  | 18.2388 | 57.0897 | 10.1058 |  | 91.0169 | 205.7552 | 15.9421 | 36.6992 | 12.3886 | 245 | 39.7026 | 94.9853 | 121.3069
15307 | 1017.6523 | 4.1361 | 27.7198 | 103.2501 | -11.6354 | 11.4 | 61.6997 | 2.3753 |  | 18.2402 | 55.8968 | 11.97 |  | 71.4345 | 177.5702 | 13.8296 | 31.9705 | 6.8988 | 232 | 38.0138 | 92.1563 | 104.2477
15308 | 987.8964 | 4.0051 | 25.5707 | 101.2174 | -10.6357 | 10.4503 | 60.8535 | 2.308 |  | 19.6891 | 50.856 | 12.3562 |  | 73.7926 | 157.1567 | 11.5863 | 28.4035 | 4.1999 | 196 | 37.4052 | 84.8437 | 100.0257
15309 | 970.9511 | 4.0012 | 25.2067 | 102.0468 | -13.6335 | 13.2992 | 55.9375 | 1.705 |  | 19.6903 | 46.8616 | 11.8396 |  | 72.0878 | 148.0877 | 10.8419 | 27.14 | 3.2819 | 192 | 36.8362 | 82.4042 | 101.9668
15310 | 953.5001 | 3.3788 | 24.3413 | 101.3354 | -13.6344 | 13.3 | 46.7409 | 1.6174 |  | 19.8131 | 45.4919 | 11.665 |  | 62.9628 | 152.1961 | 11.4834 | 27.0405 | 2.9643 | 170 | 37.2426 | 70.0458 | 102.5415
15311 | 350.7024 | 0 | 8.297 | 0 | 0.17385 | 0.003696 | 15.9456 | 0.70202 |  | 7.7291 | 18.4891 | 4.4316 |  | 0 | 0 | 4.0901 | 0 | 1.1886 | 164 | 4.0211 | 10.3556 | 11.7686
15312 | 923.1247 | 5.0685 | 23.4687 | 100.9724 | -11.6343 | 11.3997 | 54.0938 | 2.415 |  | 17.9445 | 45.1635 | 11.5708 |  | 47.4205 | 148.0061 | 10.9027 | 26.8777 | 3.4748 | 147 | 33.1992 | 66.297 | 99.0974
15313 | 922.4418 | 7.5924 | 23.6867 | 101.8786 | -12.6312 | 12.3497 | 56.2938 | 1.7846 |  | 18.3119 | 44.3367 | 11.4974 |  | 44.8364 | 146.564 | 11.3418 | 26.9876 | 3.6097 | 143 | 31.1156 | 66.3866 | 98.9777
15314 | 913.3703 | 8.8504 | 23.5854 | 101.4103 | -13.6288 | 13.2997 | 50.6892 | 2.0611 |  | 17.1141 | 42.9021 | 11.4324 |  | 44.4873 | 145.5132 | 12.1176 | 27.0784 | 3.3376 | 139 | 31.0412 | 60.5836 | 95.6373
15315 | 913.0286 | 7.1432 | 23.3343 | 101.1057 | -10.6309 | 10.4508 | 51.653 | 1.8114 |  | 17.0317 | 42.1709 | 12.9569 |  | 43.3824 | 140.8202 | 11.7302 | 27.3025 | 3.0523 | 143 | 30.5766 | 56.8491 | 97.4317
15316 | 908.4267 | 4.0941 | 23.46 | 102.3842 | -11.6313 | 11.3997 | 56.1344 | 2.3457 |  | 15.9887 | 43.8835 | 12.79 |  | 42.4931 | 138.5275 | 11.7434 | 27.555 | 2.9712 | 128 | 30.2088 | 56.3278 | 95.2363
15317 | 915.6494 | 5.2548 | 24.7466 | 102.3959 | -13.6289 | 13.2995 | 57.712 | 2.7718 |  | 15.3921 | 48.5237 | 11.544 |  | 42.9353 | 134.2117 | 10.8378 | 27.6459 | 2.9855 | 131 | 30.4887 | 56.5271 | 98.3203
15318 | 929.5488 | 6.0179 | 38.6234 | 102.0075 | -12.6297 | 12.3503 | 56.7216 | 1.8183 |  | 14.4476 | 46.2645 | 10.6987 |  | 43.7329 | 128.5294 | 11.855 | 27.4831 | 2.9459 | 125 | 29.4985 | 56.7207 | 102.4267
15319 | 935.2526 | 7.6376 | 55.946 | 99.6046 | -10.6348 | 10.4505 | 44.646 | 1.9093 |  | 11.8649 | 41.1531 | 9.1458 |  | 41.5895 | 120.6632 | 10.7908 | 27.0857 | 2.8262 | 118 | 32.3038 | 62.176 | 95.3351
15320 | 944.4191 | 5.3419 | 66.6424 | 98.3175 | -13.6355 | 13.2992 | 45.4871 | 1.5692 |  | 10.6435 | 42.4759 | 8.3822 |  | 42.8023 | 121.0401 | 11.4014 | 26.8897 | 2.8441 | 116 | 35.0231 | 74.3704 | 93.8129
15321 | 967.9545 | 2.4688 | 76.3964 | 98.2195 | -10.6379 | 10.4508 | 50.4945 | 1.8274 |  | 11.9552 | 46.2398 | 11.1412 |  | 50.417 | 126.9626 | 10.4304 | 27.0168 | 5.3583 | 129 | 33.4984 | 77.3066 | 94.6215
15322 | 991.8853 | 2.4504 | 79.1642 | 96.8039 | -14.6389 | 14.2489 | 55.1817 | 1.7462 |  | 12.5776 | 48.8539 | 13.1928 |  | 56.7024 | 141.1708 | 11.521 | 26.7264 | 10.4053 | 163 | 29.9018 | 77.8065 | 94.6815
15323 | 998.7828 | 2.5007 | 78.9614 | 93.3716 | -11.6422 | 11.4008 | 57.1738 | 1.5885 |  | 12.7297 | 50.7131 | 12.8976 |  | 63.6667 | 150.8165 | 11.0574 | 26.8747 | 12.7003 | 181 | 26.5255 | 77.9324 | 94.8543
15324 | 1004.1693 | 2.7554 | 80.3554 | 95.2784 | -10.6432 | 10.4503 | 45.8623 | 1.2821 |  | 13.2785 | 52.0448 | 10.5236 |  | 65.0315 | 156.12 | 11.4437 | 26.7699 | 12.83 | 164 | 23.8769 | 78.8284 | 91.5403
15325 | 996.7649 | 2.8529 | 73.4281 | 97.9628 | -9.6416 | 9.5003 | 48.2521 | 0.99242 |  | 14.3441 | 51.1902 | 8.9377 |  | 66.4367 | 157.7052 | 10.5556 | 26.5561 | 13.2524 | 167 | 28.6919 | 79.0217 | 91.4428
15326 | 1008.5521 | 2.6788 | 51.4719 | 96.2531 | -11.64 | 11.3995 | 54.1751 | 1.0058 |  | 15.4029 | 50.4708 | 10.3725 |  | 66.7799 | 159.1418 | 10.5792 | 26.4194 | 11.3793 | 160 | 23.9883 | 80.0895 | 93.3699
15327 | 1012.7499 | 2.6651 | 41.556 | 94.8292 | -11.6418 | 11.4 | 53.3203 | 1.5734 |  | 15.948 | 50.8111 | 15.596 |  | 63.7805 | 158.9314 | 10.2822 | 26.5886 | 6.7508 | 169 | 25.8326 | 80.1071 | 91.7094
15328 | 990.5656 | 3.0817 | 30.5967 | 94.7446 | -11.6416 | 11.4 | 52.1063 | 1.361 |  | 17.7747 | 49.9095 | 17.9013 |  | 60.6312 | 162.8707 | 11.1435 | 26.3852 | 4.6505 | 170 | 24.1826 | 78.496 | 91.0143
15329 | 976.9296 | 3.2256 | 23.7011 | 94.2454 | -11.6434 | 11.4 | 43.2986 | 1.2538 |  | 21.7535 | 47.6971 | 12.6687 |  | 66.9623 | 161.648 | 10.4433 | 26.6054 | 4.5819 | 173 | 25.1774 | 70.0752 | 82.4891
15330 | 986.686 | 5.2189 | 22.934 | 94.2851 | -12.6381 | 12.3497 | 49.2956 | 1.9216 |  | 21.0767 | 43.8182 | 9.5309 |  | 73.726 | 158.6126 | 10.6904 | 27.0697 | 3.7773 | 182 | 30.716 | 70.0022 | 84.3725
15331 | 972.244 | 11.2225 | 23.6905 | 95.2466 | -13.6329 | 13.2997 | 58.1658 | 1.7741 |  | 18.8086 | 42.7429 | 10.977 |  | 67.7093 | 156.178 | 11.3055 | 27.0499 | 3.1353 | 185 | 36.1181 | 62.7228 | 86.7012
15332 | 946.1616 | 15.7226 | 23.8977 | 94.7422 | -12.634 | 12.3503 | 58.1304 | 1.9867 |  | 17.7955 | 43.4205 | 11.9246 |  | 59.4859 | 153.215 | 10.6948 | 26.9871 | 3.1956 | 193 | 37.6982 | 59.682 | 90.8785
15333 | 946.0672 | 11.755 | 23.5949 | 94.1148 | -10.6339 | 10.4505 | 56.6887 | 2.46 |  | 18.0261 | 43.4134 | 12.0449 |  | 53.8414 | 152.6893 | 11.4128 | 27.159 | 3.5379 | 181 | 33.8962 | 60.8534 | 90.2892
15334 | 933.1778 | 5.9609 | 23.6646 | 94.3721 | -10.6347 | 10.45 | 46.8584 | 1.8324 |  | 18.4697 | 42.5281 | 11.9066 |  | 57.8743 | 147.3543 | 11.5888 | 27.1915 | 3.0958 | 170 | 32.3628 | 59.4862 | 88.214
15335 | 343.082 | 0 | 8.2171 | 0 | 0.17494 | 0.002903 | 15.5073 | 0.53992 |  | 7.1669 | 17.3308 | 4.54 |  | 0 | 0 | 3.9157 | 0 | 1.0651 | 151 | 3.4305 | 8.9472 | 9.7299
15336 | 916.7035 | 2.3885 | 23.9017 | 95.0221 | -12.6335 | 12.3497 | 59.7049 | 2.1472 |  | 17.4207 | 42.1752 | 11.5261 |  | 56.9794 | 137.393 | 11.4808 | 27.2308 | 3.3978 | 139 | 32.3398 | 56.6701 | 88.2066
15337 | 913.0782 | 2.6296 | 23.9148 | 94.7738 | -11.6347 | 11.4003 | 54.2617 | 2.2411 |  | 16.9394 | 41.9913 | 11.2614 |  | 49.9833 | 134.9522 | 10.7559 | 27.3035 | 3.0538 | 138 | 29.5614 | 56.9453 | 90.4857
15338 | 910.2843 | 3.03 | 24.0024 | 94.5959 | -12.6352 | 12.3497 | 51.7947 | 2.5544 |  | 16.8787 | 42.5379 | 11.176 |  | 45.538 | 137.3052 | 11.0457 | 27.2999 | 3.0347 | 142 | 29.094 | 55.9873 | 89.351
15339 | 904.3032 | 6.8876 | 24.3877 | 94.46 | -12.6341 | 12.35 | 60.9991 | 1.8223 |  | 17.3816 | 43.052 | 11.1173 |  | 43.7918 | 139.2948 | 12.0917 | 27.3812 | 2.9396 | 128 | 28.801 | 55.7774 | 87.8713
15340 | 907.9603 | 7.6011 | 24.0826 | 94.5847 | -12.6312 | 12.35 | 58.471 | 2.1364 |  | 16.5457 | 42.6711 | 11.1179 |  | 43.058 | 137.9131 | 11.2373 | 27.69 | 2.7713 | 121 | 29.7303 | 55.8741 | 86.8202
15341 | 906.2185 | 5.0097 | 24.0433 | 94.5253 | -12.6318 | 12.35 | 56.253 | 2.5833 |  | 15.5811 | 42.8 | 11.1917 |  | 42.9671 | 137.1074 | 11.2256 | 27.6028 | 2.6711 | 125 | 35.5723 | 70.3027 | 89.6086
15342 | 913.5326 | 3.9629 | 23.6801 | 94.1295 | -10.6343 | 10.4505 | 56.6575 | 1.8283 |  | 13.8589 | 42.9652 | 11.0777 |  | 42.5847 | 135.5848 | 11.8654 | 27.2177 | 2.6441 | 119 | 39.9516 | 73.8125 | 88.0856
15343 | 927.2888 | 3.0049 | 23.4084 | 92.3446 | -12.6367 | 12.3495 | 54.5126 | 1.9245 |  | 11.8067 | 44.31 | 9.3616 |  | 41.9552 | 124.0326 | 10.5365 | 26.6922 | 2.5254 | 112 | 38.9036 | 65.7462 | 85.0527
15344 | 922.1069 | 2.1083 | 23.2847 | 91.7585 | -12.6407 | 12.35 | 49.9214 | 1.8231 |  | 13.545 | 45.8119 | 8.2407 |  | 43.7852 | 122.5631 | 10.8449 | 26.8286 | 2.4521 | 121 | 37.2918 | 67.8447 | 85.5674
15345 | 941.58 | 1.9245 | 23.1373 | 92.6665 | -11.6421 | 11.4003 | 47.0615 | 1.2583 |  | 16.5079 | 48.021 | 8.2196 |  | 51.6473 | 131.6 | 10.8071 | 26.5048 | 2.4947 | 164 | 30.772 | 73.6179 | 88.6454
15346 | 955.1917 | 1.9969 | 23.0374 | 88.978 | -11.6427 | 11.4 | 49.2753 | 1.6882 |  | 17.9161 | 49.7701 | 8.1729 |  | 61.4223 | 137.4583 | 10.7452 | 26.3243 | 2.5561 | 166 | 23.4001 | 81.5372 | 87.0344
15347 | 962.8265 | 2.5619 | 23.2067 | 86.9167 | -11.6407 | 11.4 | 52.7246 | 1.4532 |  | 18.3362 | 50.5369 | 8.2656 |  | 70.9722 | 136.4544 | 10.8517 | 26.6309 | 2.705 | 176 | 28.3631 | 82.0545 | 89.2513
15348 | 975.3697 | 2.7469 | 24.5159 | 89.8864 | -11.6375 | 11.4 | 59.0279 | 1.0308 |  | 20.0563 | 50.9811 | 8.5186 |  | 82.1121 | 136.7519 | 12.7222 | 27.1414 | 2.8751 | 191 | 27.1873 | 80.707 | 91.4778
15349 | 983.5115 | 2.5085 | 24.2761 | 91.5811 | -10.637 | 10.4503 | 58.22 | 1.2885 |  | 18.9498 | 52.3537 | 9.1201 |  | 82.9651 | 144.0473 | 11.1736 | 27.103 | 3.0518 | 191 | 29.7664 | 81.0237 | 93.9185
15350 | 971.7881 | 2.2497 | 23.3581 | 88.8098 | -10.6375 | 10.45 | 55.1953 | 1.5042 |  | 14.9594 | 53.8234 | 11.7259 |  | 79.0845 | 158.503 | 9.7484 | 28.4174 | 3.1702 | 190 | 30.2113 | 80.1538 | 93.5089
15351 | 972.0293 | 3.7916 | 23.8118 | 87.8323 | -11.6349 | 11.3997 | 55.5261 | 1.2279 |  | 13.3242 | 53.6086 | 12.5112 |  | 73.0322 | 161.346 | 11.4843 | 28.9671 | 3.6571 | 181 | 30.7534 | 70.6099 | 85.5271
15352 | 965.4054 | 6.3024 | 23.2159 | 89.4575 | -12.639 | 12.3497 | 54.7763 | 1.9191 |  | 12.9194 | 51.7616 | 9.6219 |  | 67.0693 | 154.3535 | 10.6566 | 27.2885 | 3.986 | 170 | 30.9219 | 67.6732 | 86.5767
15353 | 986.3743 | 7.8466 | 23.2519 | 92.2136 | -12.6405 | 12.3534 | 53.0158 | 1.6299 |  | 12.9076 | 51.1392 | 8.2298 |  | 66.3296 | 155.2379 | 10.0223 | 26.9348 | 4.0447 | 146 | 32.3372 | 66.391 | 90.423
15354 | 994.5134 | 5.8073 | 24.3791 | 94.0154 | -12.6299 | 12.3466 | 51.8696 | 1.8939 |  | 13.7647 | 51.7496 | 7.4116 |  | 69.1323 | 162.2799 | 11.8165 | 27.0876 | 4.0485 | 132 | 32.9588 | 63.1576 | 88.6804
15355 | 986.6518 | 4.0776 | 23.8898 | 94.6898 | -13.6371 | 13.2997 | 54.8105 | 1.7359 |  | 15.1043 | 51.1114 | 6.5771 |  | 68.8196 | 152.23 | 11.207 | 27.3064 | 5.3651 | 129 | 32.4286 | 62.1414 | 89.3086
15356 | 952.9223 | 4.2619 | 24.1117 | 94.4495 | -11.6369 | 11.4005 | 61.4295 | 2.0282 |  | 15.6978 | 48.3868 | 6.4649 |  | 66.4156 | 141.7157 | 10.9514 | 27.6627 | 10.9531 | 125 | 32.1982 | 61.9661 | 90.8143
15357 | 926.1001 | 3.9986 | 24.3818 | 94.1279 | -11.6336 | 11.4 | 59.8666 | 1.7657 |  | 14.5524 | 45.8389 | 6.865 |  | 59.9794 | 136.9327 | 12.5648 | 27.3851 | 13.9109 | 122 | 30.6276 | 58.0179 | 91.5527
15358 | 917.9622 | 3.3856 | 24.066 | 93.7871 | -10.6332 | 10.4503 | 58.9893 | 2.0746 |  | 12.353 | 43.585 | 6.8067 |  | 51.2504 | 136.8647 | 11.2938 | 27.124 | 13.3355 | 115 | 31.3792 | 61.6322 | 90.4672
15359 | 335.4434 | 1.299 | 8.1161 | 30.8615 | 0.17422 | 0.002903 | 22.177 | 0.9785 |  | 4.3647 | 17.4344 | 2.5171 |  | 16.4641 | 54.1032 | 3.4523 | 9.0703 | 5.0175 | 116 | 3.3865 | 9.3291 | 10.1469
15360 | 903.2729 | 5.7122 | 23.6601 | 93.3047 | -13.6279 | 13.2997 | 58.5541 | 2.2576 |  | 13.1846 | 41.749 | 6.4016 |  | 45.8133 | 127.4964 | 12.4064 | 27.3449 | 11.6693 | 110 | 31.0445 | 78.1344 | 86.6777
15361 | 906.7642 | 7.5606 | 24.4719 | 93.2886 | -11.6293 | 11.4005 | 56.4818 | 2.2348 |  | 13.9371 | 41.5314 | 6.4273 |  | 43.5106 | 124.6178 | 11.5363 | 27.4087 | 11.5865 | 109 | 28.9222 | 78.6248 | 90.0778
15362 | 894.1568 | 4.3089 | 21.3517 | 94.3206 | -12.6324 | 12.3497 | 54.0165 | 1.9154 |  | 13.8938 | 41.0566 | 6.2563 |  | 42.2373 | 124.8715 | 10.2958 | 27.3311 | 11.6122 | 108 | 28.2115 | 78.68 | 89.5211
15363 | 880.4901 | 2.2107 | 18.625 | 93.4387 | -12.631 | 12.35 | 55.5676 | 2.2894 |  | 14.1468 | 40.6329 | 6.1834 |  | 42.1313 | 123.3158 | 11.8732 | 27.2725 | 11.6004 | 106 | 28.1923 | 78.5997 | 90.6781
15364 | 866.6893 | 2.6178 | 18.0898 | 92.5476 | -13.6305 | 13.2997 | 55.9874 | 1.8392 |  | 14.804 | 40.558 | 6.1834 |  | 42.2111 | 121.3984 | 11.1411 | 27.1369 | 11.5811 | 107 | 27.8328 | 79.8001 | 97.6124
15365 | 881.9063 | 4.01 | 26.5388 | 93.0978 | -10.6372 | 10.4508 | 53.0919 | 2.1009 |  | 21.0475 | 40.5716 | 7.7312 |  | 49.2483 | 124.9124 | 11.0619 | 27.074 | 11.8602 | 104 | 27.731 | 89.1417 | 103.5656
15366 | 934.3313 | 5.1011 | 42.8796 | 97.8504 | -12.6408 | 12.3495 | 67.9803 | 1.817 |  | 31.2692 | 50.5191 | 11.9062 |  | 79.1349 | 147.4653 | 15.6018 | 26.8978 | 13.8962 | 174 | 33.045 | 83.7654 | 126.685
15367 | 991.6094 | 12.0672 | 73.3423 | 105.1624 | -21.335 | 20.8976 | 86.9641 | 3.4723 |  | 42.8036 | 68.0715 | 19.9071 |  | 120.4904 | 206.0743 | 27.9371 | 29.3555 | 14.7868 | 294 | 48.171 | 92.5716 | 150.7759
15368 | 1089.1434 | 14.4094 | 96.3796 | 113.5502 | -23.3716 | 22.7995 | 103.2877 | 5.5679 |  | 52.0964 | 80.6719 | 30.0389 |  | 152.0699 | 263.9785 | 39.2328 | 35.0479 | 15.4753 | 327 | 61.1907 | 104.0396 | 166.7517
15369 | 1194.2765 | 8.3507 | 104.0466 | 125.5632 | -24.6459 | 23.7497 | 120.5847 | 5.3706 |  | 50.6854 | 83.7053 | 36.8518 |  | 171.737 | 302.8664 | 41.7651 | 41.0355 | 16.6778 | 373 | 68.322 | 130.7953 | 171.5013
15370 | 1279.4299 | 4.9521 | 105.0657 | 132.2268 | -27.6458 | 26.5992 | 134.2584 | 5.3832 |  | 46.7839 | 86.3554 | 41.6786 |  | 184.5324 | 326.7841 | 43.7168 | 45.3408 | 17.7329 | 392 | 72.8059 | 143.1681 | 182.56
15371 | 1331.3746 | 4.833 | 108.6951 | 132.8084 | -25.6457 | 24.7005 | 139.7923 | 5.0168 |  | 47.3163 | 89.8958 | 41.8173 |  | 189.0471 | 333.9859 | 43.276 | 45.9816 | 18.3792 | 336 | 71.7496 | 160.5075 | 180.6001
15372 | 1315.9277 | 5.0478 | 116.2682 | 131.2388 | -24.6499 | 23.7569 | 137.4547 | 4.533 |  | 44.0713 | 90.2495 | 40.0098 |  | 183.6767 | 351.1004 | 43.423 | 48.8374 | 19.4371 | 382 | 68.6292 | 160.4434 | 185.7418
15373 | 1312.935 | 6.8032 | 117.3642 | 135.0707 | -24.6369 | 23.7434 | 138.0825 | 4.9937 |  | 42.6142 | 90.7413 | 40.7902 |  | 189.0083 | 354.2162 | 43.533 | 54.9456 | 19.5938 | 314 | 72.6138 | 164.6301 | 181.6161
15374 | 1329.9105 | 13.8595 | 116.3216 | 139.1665 | -24.6426 | 23.75 | 135.0611 | 5.6424 |  | 41.2011 | 91.9877 | 41.7315 |  | 192.3446 | 348.3473 | 42.9035 | 56.4258 | 20.1402 | 305 | 72.4021 | 174.5775 | 178.1076
15375 | 1301.5733 | 19.9994 | 112.2853 | 139.8757 | -24.6374 | 23.75 | 121.7636 | 5.2144 |  | 36.9865 | 91.4591 | 37.9555 |  | 189.919 | 339.2065 | 41.1087 | 52.8751 | 19.3402 | 288 | 0 | 170.5918 | 172.5416
15376 | 1255.0897 | 19.0454 | 106.4912 | 134.5087 | -20.6413 | 19.9511 | 105.389 | 4.3413 |  | 31.2271 | 83.7445 | 31.321 |  | 177.8552 | 309.2421 | 32.7014 | 44.2553 | 18.3237 | 249 | 62.5349 | 159.5652 | 150.7041
15377 | 1181.427 | 10.8628 | 100.2256 | 123.1025 | -19.6419 | 19.0003 | 84.1134 | 3.2463 |  | 27.5302 | 66.5729 | 20.4171 |  | 142.2749 | 264.4432 | 19.8347 | 36.8842 | 17.3767 | 214 | 52.9612 | 132.9161 | 130.661
15378 | 1124.0463 | 5.6342 | 98.7957 | 110.6728 | -11.6419 | 11.4021 | 84.0648 | 1.9784 |  | 20.3316 | 57.062 | 15.7405 |  | 100.8384 | 229.76 | 14.5954 | 32.8938 | 16.2772 | 201 | 47.9216 | 105.0782 | 114.0882
15379 | 1091.8127 | 4.613 | 75.8377 | 107.46 | -11.6346 | 11.4 | 91.3845 | 2.0002 |  | 17.7882 | 57.4291 | 13.9177 |  | 81.8488 | 204.9344 | 13.8232 | 30.1528 | 15.5794 | 184 | 48.4922 | 98.4365 | 99.6445
15380 | 1049.2552 | 4.5935 | 35.215 | 105.4208 | -11.6325 | 11.4 | 78.3747 | 1.6608 |  | 17.049 | 56.884 | 11.972 |  | 73.6504 | 178.3486 | 11.2878 | 27.5515 | 14.8512 | 175 | 40.9369 | 81.4408 | 93.0514
15381 | 1013.4493 | 4.4285 | 20.9092 | 102.3783 | -12.6354 | 12.3497 | 61.6662 | 1.8532 |  | 14.0892 | 54.5078 | 10.7178 |  | 63.7336 | 146.3662 | 9.9056 | 26.7353 | 13.7756 | 164 | 35.9727 | 81.1178 | 90.7726
15382 | 987.5111 | 3.7042 | 20.2871 | 100.1802 | -13.6372 | 13.2997 | 53.3518 | 1.8851 |  | 11.6892 | 48.8094 | 9.346 |  | 58.9768 | 137.632 | 9.8553 | 26.9449 | 13.2253 | 145 | 34.2324 | 69.3856 | 93.5165
15383 | 358.1718 | 1.409 | 6.7819 | 33.1475 | 0.17124 | 0.003696 | 19.0536 | 0.63663 |  | 4.1521 | 18.6737 | 3.3512 |  | 20.0792 | 54.9889 | 3.3725 | 9.1226 | 5.101 | 133 | 3.6743 | 10.2916 | 9.9196
15384 | 948.2641 | 2.3077 | 19.1799 | 98.6024 | -11.6326 | 11.4005 | 56.8822 | 1.9681 |  | 12.3308 | 48.1702 | 8.8366 |  | 49.4498 | 130.8064 | 10.5486 | 26.7647 | 13.0117 | 126 | 32.2182 | 56.1746 | 89.106
15385 | 944.4121 | 2.2548 | 18.3559 | 98.6764 | -11.6307 | 11.4 | 58.5573 | 2.0027 |  | 13.3251 | 48.3592 | 8.5536 |  | 48.4014 | 128.919 | 11.3156 | 26.8277 | 12.3378 | 124 | 31.8561 | 51.9006 | 92.9679
15386 | 928.0705 | 2.1231 | 18.897 | 97.8735 | -12.6318 | 12.3497 | 60.9477 | 2.0977 |  | 13.2317 | 46.6491 | 8.5624 |  | 46.7277 | 131.5225 | 9.8019 | 26.8357 | 11.896 | 125 | 31.6775 | 46.8637 | 92.0353
15387 | 909.5946 | 2.1262 | 18.936 | 97.3849 | -15.6294 | 15.1992 | 61.8157 | 2.3817 |  | 13.1712 | 45.964 | 8.5495 |  | 46.6902 | 134.8175 | 10.4903 | 26.8661 | 11.5609 | 123 | 31.9225 | 54.2579 | 93.263
15388 | 910.3639 | 2.5848 | 18.5257 | 97.5985 | -11.6323 | 11.4011 | 57.4612 | 1.7436 |  | 13.9831 | 44.9538 | 8.5423 |  | 46.9469 | 129.8511 | 9.9978 | 26.8279 | 11.3734 | 119 | 31.9661 | 59.1121 | 97.8835
15389 | 937.161 | 3.6852 | 25.6375 | 97.7337 | -12.6343 | 12.3497 | 56.9331 | 2.0146 |  | 21.0505 | 50.2084 | 9.8375 |  | 49.6715 | 128.1903 | 11.0445 | 26.7566 | 11.5588 | 114 | 32.1415 | 61.925 | 109.395
15390 | 1001.5759 | 7.5565 | 43.6999 | 104.0338 | -13.6408 | 13.2997 | 69.0661 | 1.7352 |  | 29.4171 | 54.8808 | 14.847 |  | 74.2075 | 133.8834 | 13.8309 | 26.7352 | 12.0447 | 193 | 38.6281 | 79.3542 | 128.3295
15391 | 1089.1915 | 19.241 | 75.2802 | 109.1098 | -23.6382 | 22.7974 | 90.7075 | 3.3384 |  | 36.0372 | 64.6669 | 20.4751 |  | 119.9859 | 192.5489 | 26.9308 | 29.4127 | 12.7175 | 301 | 54.6003 | 97.844 | 139.1976
15392 | 1184.7322 | 23.4373 | 96.6298 | 118.371 | -25.6405 | 24.6995 | 103.8245 | 4.5062 |  | 43.7794 | 70.0883 | 29.0057 |  | 157.4909 | 262.1976 | 35.7231 | 34.2026 | 14.0855 | 284 | 66.0351 | 119.5075 | 157.8798
15393 | 1283.362 | 17.2501 | 106.3771 | 131.8821 | -23.6434 | 22.8005 | 115.483 | 5.3979 |  | 47.6742 | 87.9431 | 38.236 |  | 181.2173 | 300.669 | 40.8763 | 40.7416 | 15.6854 | 367 | 71.4781 | 147.9063 | 174.5089
15394 | 1319.7629 | 11.0483 | 109.326 | 134.6206 | -23.6407 | 22.8 | 126.691 | 5.5555 |  | 48.9487 | 90.2495 | 44.1082 |  | 189.9685 | 330.4274 | 41.6751 | 46.8948 | 16.9027 | 367 | 75.5027 | 161.9736 | 177.1983
15395 | 1351.5131 | 7.6567 | 118.2639 | 137.8791 | -27.6395 | 26.5989 | 132.9819 | 4.8675 |  | 50.6062 | 90.352 | 44.1526 |  | 200.7168 | 338.0711 | 42.7892 | 49.1653 | 17.6071 | 368 | 74.1905 | 179.3837 | 180.371
15396 | 1342.4661 | 6.7516 | 118.5252 | 136.8181 | -29.6404 | 28.4995 | 133.351 | 4.8917 |  | 46.7641 | 89.839 | 41.402 |  | 199.0064 | 333.7971 | 42.7173 | 46.4855 | 17.4378 | 407 | 65.6372 | 155.1618 | 183.6867
15397 | 1298.2063 | 10.1416 | 116.8835 | 140.756 | -29.6395 | 28.5 | 131.6761 | 6.0124 |  | 46.6347 | 90.2356 | 40.4654 |  | 199.4884 | 327.2847 | 43.3063 | 52.707 | 17.3642 | 347 | 74.0882 | 151.9254 | 178.394
15398 | 1286.1145 | 13.5019 | 117.3621 | 144.4665 | -21.6426 | 20.9021 | 128.0656 | 5.5686 |  | 48.261 | 89.5575 | 38.9133 |  | 196.505 | 331.9801 | 43.8039 | 56.5454 | 17.2552 | 296 | 75.6219 | 160.2705 | 176.061
15399 | 1252.5191 | 10.1322 | 118.9051 | 136.7634 | -24.6388 | 23.7492 | 124.2291 | 4.9533 |  | 43.8694 | 88.5568 | 35.8417 |  | 190.3172 | 325.1168 | 41.7966 | 56.1584 | 17.2745 | 312 | 70.3054 | 162.6532 | 165.2764
15400 | 1199.1279 | 5.7203 | 115.0649 | 129.7365 | -23.6449 | 22.8003 | 107.811 | 4.4961 |  | 37.9449 | 80.5093 | 28.5125 |  | 179.8179 | 288.43 | 32.8385 | 52.6514 | 16.8823 | 275 | 66.2707 | 149.7591 | 145.795
15401 | 1151.2968 | 4.5453 | 110.9445 | 120.7952 | -18.6474 | 18.0513 | 82.7733 | 3.5761 |  | 35.8786 | 65.0667 | 19.5289 |  | 147.4988 | 245.3475 | 20.7255 | 48.021 | 16.5698 | 232 | 57.1317 | 113.5081 | 121.2772
15402 | 1100.2477 | 5.0237 | 105.229 | 110.7274 | -13.6395 | 13.3013 | 70.3715 | 2.3549 |  | 28.7496 | 57.9152 | 14.0474 |  | 103.8834 | 217.1148 | 14.9481 | 40.756 | 16.089 | 198 | 52.8202 | 99.7408 | 111.7765
15403 | 1055.7888 | 5.0546 | 80.9348 | 106.3461 | -12.6366 | 12.3503 | 62.5841 | 2.23 |  | 25.3123 | 56.9453 | 12.2137 |  | 85.3612 | 200.4457 | 13.0858 | 31.1612 | 14.7981 | 187 | 42.248 | 95.0985 | 98.5912
15404 | 1016.8598 | 4.6942 | 41.0243 | 100.8563 | -13.6369 | 13.2997 | 57.0802 | 1.9243 |  | 25.1682 | 56.0622 | 11.6746 |  | 82.8992 | 175.6964 | 11.8324 | 27.2048 | 14.0509 | 175 | 35.3372 | 88.9022 | 97.1428
15405 | 998.8212 | 5.0756 | 25.5547 | 97.972 | -12.6337 | 12.3503 | 53.6099 | 2.1122 |  | 21.712 | 53.8773 | 11.3548 |  | 71.9866 | 154.5307 | 11.3427 | 26.7579 | 13.9666 | 167 | 33.1218 | 83.6969 | 90.5152
15406 | 964.2791 | 6.2492 | 25.0477 | 97.3087 | -12.6336 | 12.35 | 54.6598 | 1.7118 |  | 16.1259 | 49.3804 | 10.8694 |  | 70.5465 | 145.1165 | 10.6272 | 26.7359 | 13.7317 | 148 | 32.7932 | 72.6506 | 90.5561
15407 | 0 | 0 | 8.4949 | 0 | 0.17608 | 0 | 0 | 0.48877 |  | 0 | 19.3426 | 4.0303 |  | 0 | 0 | 0 | 0 | 5.2471 | 131 | 0 | 0 | -2.4061
15408 | 915.2372 | 3.2033 | 25.1899 | 97.4767 | -13.6319 | 13.3 | 58.7834 | 1.8794 |  | 15.5087 | 46.5333 | 10.2506 |  | 60.2738 | 131.314 | 11.2709 | 26.0432 | 13.1647 | 128 | 30.5643 | 66.5751 | 88.5063
15409 | 914.9239 | 2.4093 | 24.7773 | 97.1312 | -13.6334 | 13.3 | 57.085 | 2.0807 |  | 15.702 | 45.7921 | 10.0899 |  | 55.3712 | 128.234 | 11.1207 | 25.8991 | 12.4088 | 121 | 29.0577 | 67.6051 | 90.1528
15410 | 904.0345 | 2.3306 | 24.3289 | 96.3386 | -11.6352 | 11.4005 | 51.6606 | 1.75 |  | 15.3643 | 45.1889 | 10.1628 |  | 54.9112 | 125.7065 | 12.0832 | 25.7869 | 11.9349 | 120 | 27.8759 | 65.6467 | 91.1365
15411 | 900.5444 | 2.1652 | 24.1516 | 96.0053 | -14.6357 | 14.2492 | 49.7471 | 2.0159 |  | 15.2924 | 44.4462 | 9.8546 |  | 55.8266 | 123.4424 | 10.7897 | 25.7907 | 11.7437 | 117 | 27.562 | 63.6019 | 90.4971
15412 | 901.7481 | 2.703 | 24.4402 | 96.0851 | -14.6397 | 14.25 | 51.5065 | 1.7478 |  | 15.971 | 43.6402 | 9.5661 |  | 56.4349 | 118.8862 | 11.4722 | 26.81 | 11.5865 | 114 | 27.6057 | 56.7594 | 90.9301
15413 | 908.7794 | 3.6192 | 35.2874 | 97.4039 | -12.6417 | 12.3505 | 52.4922 | 2.1468 |  | 21.8958 | 46.4427 | 10.942 |  | 61.615 | 123.3485 | 10.7546 | 27.8766 | 11.8085 | 108 | 27.9937 | 65.524 | 101.4121
15414 | 969.6951 | 10.4087 | 53.8763 | 106.1936 | -12.6419 | 12.35 | 70.8122 | 2.8506 |  | 28.0636 | 51.8983 | 21.2637 |  | 86.546 | 136.5607 | 15.425 | 26.6022 | 12.352 | 179 | 35.6109 | 69.3867 | 117.8636
15415 | 1044.4866 | 15.7503 | 84.4232 | 110.3277 | -21.6412 | 20.8976 | 103.0988 | 2.8035 |  | 34.6616 | 63.7269 | 33.3501 |  | 125.5666 | 203.5373 | 28.511 | 28.0052 | 14.4716 | 290 | 50.4544 | 97.1279 | 137.8381
15416 | 1125.6535 | 12.066 | 100.7191 | 118.0208 | -21.6451 | 20.9 | 121.936 | 4.2414 |  | 40.8825 | 76.6554 | 38.5677 |  | 153.0012 | 267.1106 | 36.2666 | 32.7612 | 14.8903 | 305 | 68.7537 | 116.3563 | 159.232
15417 | 1217.7452 | 9.8423 | 106.17 | 131.1529 | -22.6444 | 21.8497 | 132.6262 | 4.8173 |  | 47.7004 | 84.0015 | 39.8173 |  | 167.6896 | 304.1057 | 41.4711 | 38.9682 | 16.1763 | 363 | 72.964 | 135.0575 | 176.2733
15418 | 1272.0495 | 7.3203 | 111.7521 | 141.6099 | -21.6407 | 20.9003 | 127.9679 | 4.9156 |  | 49.7988 | 94.214 | 39.8491 |  | 181.585 | 329.603 | 43.8637 | 42.5246 | 17.8334 | 383 | 70.3994 | 145.3821 | 178.9582
15419 | 1297.6836 | 6.9441 | 116.8725 | 143.4537 | -20.6397 | 19.9503 | 125.1495 | 5.2604 |  | 47.7883 | 93.3554 | 38.934 |  | 193.3633 | 335.4666 | 43.1883 | 43.8087 | 18.4092 | 349 | 72.9134 | 162.3189 | 182.6308
15420 | 1285.5232 | 8.5211 | 114.0334 | 141.6763 | -21.6391 | 20.8997 | 138.8909 | 5.7427 |  | 45.6159 | 86.5782 | 39.2171 |  | 200.5207 | 335.5676 | 44.9099 | 44.2177 | 18.9415 | 349 | 0 | 147.1472 | 193.4908
15421 | 1270.246 | 8.4385 | 111.6234 | 143.384 | -23.6371 | 22.7995 | 149.8047 | 6.3281 |  | 40.9869 | 88.328 | 40.4655 |  | 202.7277 | 337.1973 | 46.224 | 45.7925 | 19.3806 | 336 | 80.3481 | 150.0153 | 182.6842
15422 | 1253.5022 | 8.4926 | 115.5655 | 144.0383 | -21.6425 | 20.9005 | 150.2435 | 5.4391 |  | 35.7253 | 90.4842 | 40.017 |  | 197.9188 | 340.4401 | 46.4921 | 46.5989 | 19.2057 | 313 | 80.615 | 147.3305 | 180.1755
15423 | 1217.1443 | 9.4767 | 113.9177 | 139.4026 | -24.639 | 23.7492 | 143.7559 | 5.2424 |  | 35.9768 | 91.1853 | 35.8973 |  | 189.4168 | 332.1647 | 43.3072 | 44.7998 | 18.8335 | 291 | 70.6345 | 142.5399 | 170.7053
15424 | 1176.6793 | 12.9685 | 113.6993 | 132.4202 | -22.6388 | 21.8505 | 116.7629 | 4.1871 |  | 40.2889 | 84.0213 | 23.6564 |  | 178.2683 | 298.7907 | 37.584 | 41.8307 | 17.9824 | 278 | 67.1205 | 136.3521 | 153.1177
15425 | 1110.2758 | 10.391 | 108.9095 | 119.6216 | -20.6462 | 19.9505 | 89.429 | 3.7563 |  | 34.915 | 66.0778 | 17.4431 |  | 141.4709 | 258.7167 | 23.9169 | 37.553 | 16.8323 | 239 | 58.4133 | 118.8916 | 126.316
15426 | 1076.3004 | 9.4138 | 101.0478 | 107.7128 | -22.6419 | 21.8495 | 81.8661 | 3.2851 |  | 22.5852 | 58.3383 | 13.4728 |  | 100.8825 | 225.9616 | 13.9073 | 33.7412 | 16.2845 | 210 | 54.2059 | 107.1788 | 119.9904
15427 | 1036.3355 | 11.536 | 81.2417 | 102.621 | -22.6355 | 21.85 | 79.0832 | 3.1383 |  | 18.0243 | 58.6826 | 11.7837 |  | 82.7197 | 207.951 | 10.6085 | 30.3101 | 15.3626 | 194 | 49.1304 | 95.4761 | 106.4291
15428 | 994.1478 | 9.6745 | 45.182 | 100.3765 | -22.6376 | 21.85 | 69.8858 | 2.8411 |  | 18.5938 | 57.0848 | 12.1809 |  | 74.5222 | 187.1746 | 10.6539 | 28.8844 | 14.2954 | 174 | 42.7747 | 88.5093 | 100.8617
15429 | 973.8845 | 5.7242 | 28.659 | 98.1119 | -19.6375 | 19.0008 | 63.7996 | 1.9523 |  | 17.9652 | 54.1085 | 12.0448 |  | 68.9405 | 170.7447 | 10.5093 | 28.7101 | 13.3151 | 167 | 38.2069 | 83.9108 | 98.8518
15430 | 943.0725 | 3.8854 | 26.8676 | 97.0073 | -19.635 | 19 | 58.7162 | 2.2247 |  | 15.3189 | 48.6399 | 11.8498 |  | 65.0878 | 155.6247 | 10.3965 | 28.491 | 12.8838 | 148 | 36.5347 | 66.9032 | 99.0323
15431 | 344.7705 | 0 | 9.1922 | 0 | 0.17194 | 0 | 21.1256 | 1.0187 |  | 5.4029 | 18.9169 | 4.5144 |  | 0 | 0 | 3.6256 | 0 | 5.0424 | 133 | 3.913 | 10.0016 | 11.6478
15432 | 914.3028 | 3.3429 | 24.4288 | 99.4032 | -10.6312 | 10.45 | 71.3967 | 2.2415 |  | 15.1127 | 45.1431 | 11.4688 |  | 58.5949 | 134.2669 | 10.6068 | 28.4217 | 12.0065 | 125 | 36.141 | 60.654 | 93.4563
15433 | 908.9039 | 7.1404 | 24.1304 | 98.1909 | -10.6303 | 10.45 | 69.4163 | 2.1255 |  | 15.3152 | 44.7359 | 11.5313 |  | 54.5669 | 130.7762 | 11.1689 | 28.3804 | 11.9541 | 114 | 30.7027 | 62.7638 | 90.715
15434 | 899.3895 | 9.4026 | 23.6889 | 98.526 | -10.6284 | 10.45 | 67.8974 | 2.4855 |  | 15.2479 | 44.223 | 11.5649 |  | 52.8351 | 132.0537 | 10.4868 | 28.5262 | 12.0575 | 117 | 29.662 | 62.3861 | 90.8114
15435 | 890.3721 | 7.821 | 23.265 | 98.8856 | -9.6338 | 9.5003 | 67.2673 | 2.6454 |  | 15.1949 | 43.0815 | 11.3435 |  | 53.2066 | 129.9022 | 10.5686 | 28.299 | 11.7037 | 112 | 30.9832 | 61.9437 | 92.5165
15436 | 889.3752 | 4.6015 | 22.8198 | 98.4519 | -10.6386 | 10.4497 | 69.4239 | 1.9717 |  | 15.9099 | 42.5615 | 11.2852 |  | 52.5093 | 123.0655 | 10.1845 | 29.2064 | 11.4916 | 109 | 29.2149 | 55.511 | 95.7271
15437 | 903.6106 | 3.7434 | 30.9913 | 98.4974 | -10.6416 | 10.45 | 73.0451 | 2.2962 |  | 23.0713 | 45.7707 | 12.7435 |  | 54.2333 | 125.1375 | 10.5775 | 30.3598 | 11.4891 | 109 | 29.0059 | 58.9571 | 105.6371
15438 | 941.7213 | 7.148 | 49.018 | 104.7309 | -10.6423 | 10.45 | 83.7896 | 2.6824 |  | 33.5384 | 51.2996 | 18.3474 |  | 80.6053 | 142.6692 | 13.7299 | 28.8312 | 11.7358 | 189 | 36.7298 | 69.3712 | 132.8622
15439 | 1030.1002 | 17.5205 | 76.8827 | 109.2079 | -16.6404 | 16.1484 | 101.9099 | 3.4708 |  | 38.3895 | 63.5399 | 24.5209 |  | 123.254 | 191.8709 | 27.5827 | 30.2799 | 13.4166 | 276 | 53.2818 | 98.1426 | 141.9703
15440 | 1135.443 | 27.2252 | 97.1624 | 122.1235 | -17.6434 | 17.0997 | 117.6211 | 3.9348 |  | 38.8485 | 76.6141 | 30.7411 |  | 152.4711 | 241.9274 | 35.3914 | 34.7768 | 15.3936 | 323 | 63.2862 | 117.9964 | 156.8759
15441 | 1211.7151 | 25.5917 | 102.8916 | 136.8772 | -18.6454 | 18.0497 | 119.8044 | 5.008 |  | 44.4931 | 84.5123 | 36.2002 |  | 170.0868 | 288.0008 | 41.2094 | 37.9212 | 16.5493 | 357 | 63.4004 | 146.9683 | 168.4585
15442 | 1246.2133 | 20.6957 | 106.7512 | 137.4566 | -18.6462 | 18.05 | 119.4387 | 4.5287 |  | 50.0757 | 88.9676 | 39.7993 |  | 177.7342 | 308.2342 | 43.301 | 40.7586 | 17.938 | 385 | 59.2773 | 153.9131 | 177.248
15443 | 1259.3668 | 16.3359 | 111.9731 | 135.27 | -19.6447 | 18.9997 | 124.3988 | 4.9767 |  | 50.6061 | 89.363 | 39.9985 |  | 186.6544 | 305.7935 | 42.8787 | 40.722 | 18.3812 | 358 | 60.9049 | 176.1342 | 182.7122
15444 | 1264.4009 | 13.1456 | 112.1146 | 132.8875 | -18.4916 | 18.0503 | 136.3895 | 5.4019 |  | 45.0207 | 88.1497 | 40.0884 |  | 191.9781 | 305.549 | 43.3833 | 39.93 | 18.5058 | 360 | 54.7935 | 143.0597 | 179.3962
15445 | 1264.9628 | 11.7535 | 110.8487 | 128.3439 | -18.5521 | 18.9997 | 144.1655 | 5.5221 |  | 43.232 | 91.8536 | 39.8922 |  | 192.1042 | 307.9558 | 42.611 | 42.9883 | 18.4844 | 375 | 57.2709 | 142.006 | 180.5261
15446 | 1252.169 | 10.3943 | 111.6678 | 133.2208 | -15.4986 | 17.1005 | 139.2958 | 5.2162 |  | 42.3527 | 94.4477 | 38.1252 |  | 190.7604 | 313.2021 | 40.8254 | 50.3442 | 18.4468 | 291 | 63.9499 | 151.2411 | 176.2076
15447 | 1212.5939 | 6.9912 | 111.4334 | 136.4312 | -16.2679 | 18.0497 | 133.517 | 5.2236 |  | 40.0169 | 92.6947 | 33.4544 |  | 183.229 | 301.9701 | 39.072 | 52.6046 | 18.0705 | 283 | 64.6258 | 147.3042 | 171.5111
15448 | 1166.9325 | 4.7256 | 102.8008 | 124.6512 | -8.5054 | 10.4521 | 103.0772 | 4.1915 |  | 37.0594 | 83.0167 | 28.7511 |  | 170.9067 | 259.3076 | 29.5802 | 51.7562 | 17.2991 | 271 | 64.1492 | 139.9972 | 157.5195
15449 | 1124.2424 | 4.4872 | 98.7697 | 113.6546 | -7.5213 | 9.5029 | 74.7563 | 3.0232 |  | 36.121 | 68.0328 | 27.9204 |  | 139.9322 | 221.2658 | 17.6757 | 49.5486 | 16.329 | 228 | 59.1146 | 116.3147 | 132.1955
15450 | 1079.4856 | 4.9387 | 90.366 | 102.0396 | -7.4682 | 9.4974 | 75.6502 | 2.7841 |  | 31.2311 | 58.5237 | 28.7516 |  | 98.1702 | 196.5504 | 11.9058 | 45.8761 | 15.3587 | 209 | 56.0794 | 99.1542 | 120.4146
15451 | 1037.9954 | 5.059 | 80.1649 | 97.7293 | -8.5667 | 10.4497 | 81.7431 | 2.4748 |  | 27.8719 | 56.0988 | 29.7564 |  | 82.0181 | 178.8509 | 10.5319 | 41.9888 | 14.6792 | 183 | 51.5844 | 90.5347 | 104.5891
15452 | 1006.183 | 6.791 | 47.8248 | 96.7254 | -8.7662 | 10.45 | 77.6247 | 1.8855 |  | 25.1711 | 53.7465 | 29.7518 |  | 75.3907 | 161.8663 | 10.0691 | 38.8602 | 14.5376 | 176 | 46.3339 | 86.3827 | 105.2683
15453 | 976.9107 | 9.9459 | 26.2918 | 95.615 | -8.9113 | 10.45 | 72.6323 | 2.4527 |  | 18.9718 | 51.3491 | 26.9754 |  | 61.0145 | 146.9326 | 9.4843 | 37.6634 | 14.179 | 182 | 38.2898 | 83.0484 | 101.6121
15454 | 949.5062 | 10.0263 | 23.4181 | 95.4233 | -10.4774 | 11.3997 | 72.394 | 2.9218 |  | 14.2413 | 47.0998 | 24.1058 |  | 51.7987 | 134.128 | 9.3867 | 37.4386 | 13.904 | 151 | 38.7786 | 69.1328 | 96.9223
15455 | 350.56 | 0 | 8.2002 | 0 | 0.48002 | 0.003167 | 27.4748 | 1.1307 |  | 5.0715 | 18.4821 | 8.9762 |  | 0 | 0 | 3.2771 | 0 | 5.4638 | 128 | 4.1445 | 10.3452 | 9.7261
15456 | 919.8043 | 4.7057 | 22.1254 | 97.8944 | -10.7614 | 11.3997 | 68.5355 | 2.9371 |  | 15.2033 | 41.5516 | 14.7898 |  | 47.201 | 126.6845 | 9.2021 | 37.12 | 13.6666 | 121 | 32.6438 | 67.0277 | 98.1569
15457 | 906.0202 | 2.2931 | 22.1888 | 98.1245 | -10.4462 | 11.4 | 59.6527 | 2.9846 |  | 15.2258 | 41.4101 | 11.2845 |  | 47.267 | 126.1544 | 9.3202 | 36.8471 | 13.1637 | 121 | 30.2597 | 66.978 | 100.0286
15458 | 903.3747 | 3.7535 | 22.0831 | 94.8232 | -10.9151 | 11.4 | 64.0485 | 3.1473 |  | 14.0502 | 40.8186 | 11.4934 |  | 46.3863 | 121.3522 | 9.5111 | 36.5773 | 12.9052 | 114 | 28.944 | 66.9488 | 98.0312
15459 | 897.0724 | 7.7874 | 22.1116 | 92.5888 | -11.2073 | 11.4 | 72.709 | 2.7801 |  | 13.3391 | 40.4846 | 11.2913 |  | 45.0873 | 115.1076 | 9.8571 | 36.5579 | 12.8646 | 106 | 29.429 | 68.3235 | 98.2498
15460 | 895.0358 | 9.4531 | 22.0636 | 91.6056 | -10.2882 | 10.4503 | 65.7514 | 2.6447 |  | 14.0432 | 41.8326 | 10.9876 |  | 45.3172 | 111.3854 | 10.1474 | 37.4289 | 12.3123 | 108 | 28.227 | 67.2689 | 100.5656
15461 | 901.8845 | 5.3022 | 29.5365 | 91.821 | -11.5949 | 11.3997 | 58.1257 | 2.7374 |  | 22.3164 | 47.5706 | 12.0635 |  | 47.3574 | 113.8452 | 9.8742 | 38.3639 | 11.7472 | 104 | 28.4187 | 64.6892 | 114.6009
15462 | 956.2883 | 3.9583 | 47.7244 | 98.6963 | -13.6437 | 13.2995 | 78.9703 | 2.8462 |  | 31.715 | 51.2662 | 18.4352 |  | 75.2949 | 128.3 | 13.5629 | 37.5393 | 11.5956 | 189 | 33.1406 | 66.5476 | 131.8167
15463 | 1030.1924 | 7.4071 | 75.0511 | 101.5215 | -21.6409 | 20.8979 | 101.0935 | 4.0605 |  | 33.1564 | 61.2146 | 22.3149 |  | 121.2954 | 178.0844 | 26.2878 | 39.7181 | 12.392 | 264 | 50.9549 | 88.1889 | 155.4061
15464 | 1098.2155 | 10.9706 | 91.693 | 110.2463 | -21.6478 | 20.9 | 105.7163 | 5.3268 |  | 32.0083 | 75.9213 | 27.7213 |  | 154.4172 | 243.0827 | 35.2464 | 44.1633 | 14.5414 | 312 | 57.6366 | 113.6486 | 175.6494
15465 | 1170.0137 | 11.5223 | 96.5659 | 119.0773 | -20.6464 | 19.9503 | 117.9333 | 5.6653 |  | 33.4756 | 84.3585 | 33.7282 |  | 172.1959 | 277.9303 | 38.1524 | 48.1901 | 17.0102 | 368 | 55.1595 | 137.419 | 186.1819
15466 | 1214.7364 | 9.4427 | 98.3577 | 123.6208 | -20.2253 | 19.95 | 132.849 | 5.5721 |  | 32.3057 | 86.3872 | 36.5204 |  | 169.3497 | 298.1843 | 39.9443 | 50.9646 | 18.2939 | 370 | 55.7594 | 146.738 | 188.1758
15467 | 1228.0296 | 9.9146 | 102.9893 | 124.2633 | -19.5165 | 19.95 | 138.458 | 5.1632 |  | 31.4437 | 86.2662 | 37.1165 |  | 168.3994 | 298.6711 | 41.3492 | 51.4393 | 18.2539 | 325 | 55.6379 | 151.1419 | 191.1213
15468 | 1223.4261 | 13.8673 | 103.328 | 127.4905 | -18.7471 | 19.95 | 129.4236 | 5.3701 |  | 33.8926 | 86.7629 | 37.0411 |  | 174.8391 | 291.1377 | 42.8209 | 45.1726 | 18.2184 | 346 | 51.0294 | 133.4229 | 184.3975
15469 | 1222.0156 | 23.8 | 104.2243 | 129.7438 | -19.2301 | 20.8997 | 132.7007 | 5.0743 |  | 35.3268 | 88.2375 | 37.0155 |  | 179.8094 | 293.4517 | 43.0215 | 42.1968 | 18.5036 | 310 | 50.2653 | 136.5241 | 172.5958
15470 | 1219.847 | 24.2225 | 106.4143 | 133.9679 | -16.9556 | 19.0005 | 135.8675 | 4.7475 |  | 38.1994 | 89.0384 | 36.6535 |  | 177.9946 | 289.6112 | 41.5446 | 41.8603 | 18.5539 | 290 | 50.5702 | 142.7328 | 172.47
15471 | 1180.5699 | 14.0897 | 103.9368 | 129.3279 | -16.8328 | 19 | 125.4981 | 4.3666 |  | 42.0959 | 88.3782 | 28.2101 |  | 168.8471 | 282.2311 | 38.6332 | 40.6461 | 18.0468 | 295 | 52.1035 | 139.2446 | 162.8131
15472 | 1132.2658 | 6.8917 | 99.5947 | 122.4978 | -7.893 | 10.4524 | 103.9913 | 2.8969 |  | 38.0352 | 80.644 | 16.4711 |  | 156.6148 | 260.6163 | 30.6804 | 38.983 | 17.2096 | 275 | 52.489 | 129.3941 | 141.953
15473 | 1063.8424 | 4.2591 | 83.3386 | 111.1311 | -12.0228 | 14.2489 | 79.8764 | 2.1158 |  | 26.6703 | 62.1159 | 12.6083 |  | 125.62 | 227.7594 | 18.9736 | 35.5078 | 16.2226 | 237 | 49.1788 | 121.4489 | 122.6153
15474 | 1015.1045 | 4.3044 | 48.823 | 99.4924 | -8.2089 | 10.4511 | 70.1885 | 2.5128 |  | 16.7767 | 52.1266 | 12.3262 |  | 95.5801 | 204.7774 | 13.014 | 36.8946 | 15.5462 | 236 | 45.9696 | 116.0788 | 118.3259
15475 | 997.9171 | 4.5356 | 26.9731 | 97.626 | -9.265 | 11.3997 | 72.19 | 2.0669 |  | 14.3467 | 50.1082 | 15.0654 |  | 84.7244 | 182.5053 | 11.0306 | 39.1148 | 14.9696 | 223 | 44.9511 | 99.7573 | 103.7566
15476 | 953.6876 | 4.5974 | 22.857 | 96.5164 | -8.4649 | 10.4503 | 73.7325 | 2.0915 |  | 14.3262 | 44.2253 | 15.0573 |  | 74.2841 | 153.8723 | 9.6594 | 38.5901 | 13.971 | 215 | 41.4728 | 90.764 | 102.6428
15477 | 930.3656 | 4.3353 | 22.5157 | 93.9648 | -8.6916 | 10.45 | 73.2184 | 2.5786 |  | 13.9453 | 40.3935 | 12.7681 |  | 64.9967 | 142.4211 | 9.1741 | 37.9727 | 13.3021 | 197 | 36.375 | 87.378 | 103.5124
15478 | 917.9292 | 3.8017 | 22.0908 | 92.8604 | -7.6906 | 9.5003 | 72.8226 | 2.9349 |  | 13.6436 | 39.5984 | 11.1565 |  | 59.8031 | 141.3426 | 8.8493 | 37.5742 | 12.967 | 197 | 34.7212 | 72.119 | 103.0924
15479 | 335.886 | 0 | 7.4959 | 0 | 1.1035 | 0.00264 | 27.0841 | 1.1895 |  | 5.1647 | 16.1721 | 4.054 |  | 0 | 0 | 2.9563 | 0 | 5.0039 | 187 | 3.7192 | 10.4758 | 11.6771
15480 | 892.7016 | 2.1713 | 21.9969 | 91.9167 | -7.346 | 9.5 | 69.0617 | 2.0448 |  | 12.695 | 38.6652 | 10.6407 |  | 47.7571 | 135.8314 | 8.6425 | 37.2849 | 12.3889 | 174 | 34.6211 | 62.1026 | 98.617
15481 | 897.929 | 2.3313 | 22.0195 | 91.8355 | -7.2742 | 9.5 | 68.8156 | 2.4581 |  | 13.0365 | 38.7929 | 10.6625 |  | 44.8777 | 132.2393 | 8.5689 | 37.0461 | 12.644 | 158 | 32.7715 | 61.1355 | 103.7744
15482 | 881.6313 | 2.4682 | 22.2752 | 91.9051 | -7.311 | 9.5 | 72.3344 | 2.6982 |  | 12.0413 | 39.9348 | 10.4683 |  | 42.6685 | 136.9041 | 8.5426 | 37.0368 | 12.5244 | 159 | 0 | 59.809 | 100.73
15483 | 871.3262 | 2.316 | 22.307 | 91.805 | -6.1994 | 8.5503 | 73.5997 | 2.0407 |  | 11.2662 | 40.2226 | 10.3235 |  | 42.8606 | 132.4794 | 8.7064 | 37.053 | 12.0482 | 145 | 28.4104 | 59.1718 | 95.6081
15484 | 880.1504 | 2.7559 | 19.8536 | 91.8546 | -7.1541 | 9.4997 | 67.1735 | 2.3176 |  | 11.11 | 40.6941 | 10.4694 |  | 43.4905 | 123.4275 | 8.7287 | 38.0231 | 11.8501 | 134 | 28.6833 | 59.0707 | 95.8632
15485 | 882.2269 | 3.6148 | 18.759 | 91.8214 | -7.43 | 9.5 | 59.9757 | 2.7288 |  | 11.2084 | 44.2768 | 10.5329 |  | 42.7269 | 120.3158 | 8.5782 | 38.6602 | 11.8583 | 127 | 28.6854 | 58.9664 | 98.5486
15486 | 893.2325 | 3.9742 | 36.8096 | 91.8892 | -7.7194 | 9.5 | 54.1137 | 2.3247 |  | 11.4448 | 47.9842 | 10.3718 |  | 42.6926 | 119.6453 | 8.5298 | 37.576 | 11.8487 | 116 | 28.5753 | 59.0989 | 96.6982
15487 | 897.7555 | 3.7033 | 51.7454 | 89.4436 | -7.7707 | 9.5 | 49.0291 | 1.7645 |  | 9.9502 | 44.4503 | 9.2003 |  | 44.4783 | 116.2079 | 9.3441 | 36.5942 | 11.7459 | 105 | 37.445 | 63.1623 | 95.5153
15488 | 904.832 | 2.7717 | 57.5923 | 87.9567 | -7.8455 | 9.5 | 50.767 | 2.0853 |  | 13.1576 | 43.9455 | 8.3424 |  | 47.194 | 117.1498 | 11.4906 | 36.4136 | 11.7954 | 120 | 46.9659 | 73.1538 | 95.0819
15489 | 935.5756 | 2.6144 | 63.5402 | 87.8981 | -7.8228 | 9.5 | 54.1129 | 2.0018 |  | 22.1952 | 47.9922 | 8.561 |  | 54.7335 | 123.8062 | 11.4437 | 36.5342 | 12.3101 | 131 | 52.2986 | 76.5234 | 96.7972
15490 | 944.4721 | 2.8234 | 68.466 | 88.763 | -7.7151 | 9.5 | 58.6472 | 2.0881 |  | 28.613 | 50.0774 | 9.2641 |  | 62.1967 | 130.0824 | 11.186 | 36.3361 | 12.6156 | 180 | 54.0868 | 77.5167 | 98.1022
15491 | 957.7511 | 2.4098 | 70.3262 | 89.5039 | -6.691 | 8.5503 | 58.9465 | 2.3675 |  | 27.0787 | 50.6975 | 11.6835 |  | 65.2503 | 130.5462 | 10.6882 | 36.2573 | 12.7439 | 208 | 55.1918 | 77.929 | 97.8427
15492 | 947.4861 | 2.2631 | 71.4456 | 90.2307 | -7.9718 | 9.4997 | 59.6674 | 1.6959 |  | 23.2304 | 50.7956 | 11.4256 |  | 67.4772 | 135.163 | 10.4907 | 36.3845 | 13.3426 | 207 | 54.215 | 78.1196 | 99.1369
15493 | 947.7587 | 2.4341 | 65.891 | 91.3372 | -9.5204 | 10.4497 | 66.7576 | 1.6852 |  | 23.5321 | 51.1531 | 15.5308 |  | 71.3632 | 139.1828 | 10.6374 | 36.6032 | 13.5612 | 208 | 52.8625 | 81.8472 | 99.8079
15494 | 962.8593 | 2.2574 | 46.0851 | 91.8858 | -8.5464 | 9.5003 | 68.2989 | 2.1709 |  | 23.615 | 52.1449 | 18.5866 |  | 68.5596 | 147.2895 | 11.0521 | 36.3863 | 13.4934 | 216 | 46.5994 | 81.2086 | 99.1811
15495 | 971.5492 | 2.6674 | 28.0057 | 91.0705 | -6.9994 | 8.5503 | 61.5265 | 2.131 |  | 20.5181 | 52.1141 | 15.7413 |  | 68.5129 | 149.7294 | 10.7261 | 36.3323 | 13.5864 | 216 | 45.0858 | 80.0313 | 103.5191
15496 | 958.6863 | 3.0449 | 17.7882 | 90.4554 | -8.7623 | 10.4495 | 58.3172 | 1.7929 |  | 16.0312 | 50.2928 | 19.2563 |  | 74.038 | 145.5491 | 10.8167 | 36.3984 | 13.8061 | 217 | 44.0855 | 78.5022 | 106.2038
15497 | 945.7061 | 3.6266 | 16.0916 | 90.2848 | -7.8147 | 9.5003 | 59.8347 | 2.0448 |  | 16.2458 | 47.5652 | 20.7141 |  | 75.3708 | 146.6978 | 9.0891 | 36.5086 | 13.7866 | 208 | 40.2377 | 71.5315 | 106.0793
15498 | 931.3887 | 6.4825 | 17.374 | 92.2015 | -8.0054 | 9.5 | 70.849 | 2.5149 |  | 16.3326 | 43.0663 | 13.296 |  | 69.2898 | 146.0354 | 8.2386 | 36.9792 | 13.7067 | 203 | 31.8409 | 73.6787 | 105.145
15499 | 921.8235 | 8.5435 | 17.1683 | 92.4418 | -9.9544 | 10.4497 | 75.6216 | 2.8194 |  | 15.3401 | 41.8671 | 9.7387 |  | 69.4139 | 142.0442 | 8.4129 | 37.074 | 13.6509 | 207 | 29.0705 | 70.6568 | 103.4601
15500 | 906.1376 | 6.3882 | 16.6133 | 91.0714 | -10.6353 | 10.45 | 72.613 | 2.9653 |  | 14.9619 | 41.6179 | 11.1696 |  | 69.6097 | 139.3314 | 8.4852 | 36.6626 | 13.3287 | 192 | 28.4436 | 67.4601 | 102.2492
15501 | 913.8066 | 4.481 | 16.2689 | 92.2522 | -10.4668 | 10.45 | 72.6873 | 3.1782 |  | 13.7532 | 41.2294 | 12.5574 |  | 65.7121 | 141.6359 | 8.6779 | 37.2964 | 13.2883 | 190 | 28.3181 | 68.2979 | 104.5745
15502 | 907.4163 | 5.803 | 16.0338 | 91.9332 | -11.4919 | 11.3997 | 71.6568 | 3.3221 |  | 12.4469 | 40.5113 | 12.3674 |  | 56.8497 | 142.7528 | 9.2598 | 37.3702 | 13.1444 | 176 | 27.3077 | 66.4619 | 107.4369
15503 | 332.615 | 0 | 5.4954 | 0 | 0.17255 | 0.003167 | 26.3949 | 1.2991 |  | 4.6687 | 16.4991 | 4.6151 |  | 0 | 0 | 3.2498 | 0 | 5.1002 | 153 | 2.9091 | 10.0132 | 11.2573
15504 | 880.5869 | 6.5473 | 16.2308 | 93.6716 | -10.6329 | 10.4503 | 60.7675 | 2.7284 |  | 11.6571 | 41.1858 | 7.0418 |  | 53.2703 | 138.1123 | 9.4843 | 37.1093 | 12.1318 | 149 | 28.504 | 67.1296 | 107.5501
15505 | 881.4932 | 7.5685 | 16.3873 | 93.7562 | -11.6315 | 11.3997 | 67.6265 | 2.7754 |  | 11.2086 | 41.6471 | 7.2081 |  | 52.5708 | 129.6164 | 9.48 | 37.2521 | 12.1182 | 148 | 28.1135 | 65.3299 | 107.0903
15506 | 870.879 | 11.0639 | 15.9818 | 93.1295 | -20.6298 | 19.9476 | 68.0086 | 3.0662 |  | 11.2396 | 41.5841 | 7.1705 |  | 53.6901 | 126.4005 | 9.2273 | 36.8815 | 12.1533 | 146 | 27.2893 | 64.9557 | 104.7027
15507 | 868.9383 | 11.0259 | 16.3929 | 92.0806 | -17.6352 | 17.1008 | 60.6205 | 3.2844 |  | 11.2591 | 42.1689 | 6.994 |  | 53.7776 | 126.693 | 9.3803 | 36.731 | 12.1655 | 138 | 25.2285 | 66.107 | 98.1232
15508 | 861.3312 | 9.8952 | 16.4215 | 90.9076 | -16.6309 | 16.1503 | 64.0235 | 3.3353 |  | 11.2437 | 42.1509 | 6.9883 |  | 47.217 | 123.5452 | 9.5192 | 37.473 | 12.1721 | 135 | 25.5738 | 64.9259 | 97.2851
15509 | 868.2498 | 9.3451 | 16.8911 | 90.2021 | -11.6336 | 11.4013 | 68.2671 | 3.6044 |  | 11.4134 | 42.9005 | 6.9902 |  | 44.1243 | 122.1373 | 9.4379 | 38.6659 | 12.179 | 130 | 28.035 | 64.9153 | 95.6038
15510 | 876.1454 | 7.906 | 16.4257 | 90.0337 | -11.6349 | 11.4 | 60.6017 | 3.591 |  | 11.4776 | 46.2993 | 7.0784 |  | 44.2838 | 122.1352 | 9.2627 | 37.4069 | 12.1541 | 132 | 27.2442 | 65.098 | 98.1599
15511 | 889.0821 | 6.6152 | 15.4521 | 87.7684 | -11.636 | 11.4 | 55.326 | 3.2428 |  | 9.7384 | 47.257 | 5.3083 |  | 43.2235 | 118.3305 | 9.3698 | 36.0063 | 12.0527 | 133 | 29.5071 | 67.7406 | 95.1936
15512 | 891.5422 | 4.1507 | 15.3982 | 84.6051 | -11.637 | 11.4 | 60.1772 | 3.1077 |  | 13.5996 | 46.6093 | 4.2936 |  | 44.4845 | 115.6524 | 11.1245 | 35.8521 | 11.9663 | 140 | 29.1323 | 70.9183 | 93.7234
15513 | 917.7838 | 2.6983 | 15.5875 | 83.5424 | -11.6364 | 11.4 | 62.5926 | 2.9092 |  | 20.0409 | 46.111 | 4.2692 |  | 51.1103 | 116.4488 | 11.5834 | 36.2412 | 11.771 | 149 | 24.6026 | 74.7761 | 91.6246
15514 | 935.8353 | 2.7109 | 16.3819 | 83.1054 | -11.4316 | 11.4 | 65.1388 | 2.7985 |  | 22.2738 | 45.4434 | 5.4814 |  | 56.9472 | 118.7357 | 11.2047 | 36.6255 | 12.0591 | 152 | 20.6079 | 79.7373 | 97.4178
15515 | 938.6475 | 2.9269 | 16.3676 | 83.0086 | -9.8572 | 10.4503 | 68.0136 | 2.6423 |  | 20.8651 | 45.9862 | 8.1195 |  | 60.1527 | 121.8757 | 10.5054 | 36.5283 | 12.3693 | 156 | 18.1103 | 82.2328 | 101.34
15516 | 936.0654 | 3.1444 | 15.8989 | 86.9892 | -11.222 | 12.3495 | 67.9374 | 2.6962 |  | 22.0594 | 46.5297 | 14.4502 |  | 61.5966 | 127.822 | 9.2708 | 36.8576 | 12.116 | 157 | 17.5432 | 80.8653 | 101.5808
15517 | 934.207 | 2.9762 | 15.8115 | 89.7504 | -8.877 | 10.4505 | 65.3346 | 1.7143 |  | 22.038 | 47.2509 | 20.1566 |  | 70.0727 | 131.5835 | 9.6099 | 37.0427 | 12.8881 | 159 | 21.5093 | 78.8325 | 100.109
15518 | 930.4006 | 2.7894 | 15.9662 | 86.4843 | -7.5292 | 9.5003 | 60.478 | 1.8513 |  | 23.0792 | 47.7372 | 21.8129 |  | 78.2563 | 140.6806 | 10.2347 | 37.274 | 13.664 | 162 | 25.1552 | 77.4949 | 101.6021
15519 | 924.3351 | 5.3369 | 16.0224 | 84.4872 | -7.2973 | 9.5 | 56.9745 | 2.3955 |  | 21.7103 | 47.7962 | 20.387 |  | 78.3942 | 148.4408 | 10.1833 | 36.8625 | 13.6933 | 161 | 32.1496 | 68.5224 | 104.6969
15520 | 922.3606 | 4.272 | 15.463 | 83.3789 | -7.3927 | 9.5 | 50.8944 | 1.525 |  | 15.8464 | 47.1528 | 21.7543 |  | 73.74 | 148.1719 | 9.5179 | 36.6046 | 13.7592 | 162 | 34.248 | 67.8 | 103.6847
15521 | 935.2845 | 3.2265 | 15.2107 | 84.3335 | -7.6147 | 9.5 | 54.2168 | 1.7842 |  | 12.2457 | 46.6171 | 24.484 |  | 74.4981 | 146.0238 | 8.521 | 37.204 | 13.7603 | 143 | 35.0166 | 66.1707 | 100.1635
15522 | 953.0709 | 6.2706 | 15.5573 | 85.5606 | -7.8914 | 9.5 | 65.4555 | 2.5724 |  | 12.1237 | 48.1166 | 25.2174 |  | 75.3077 | 145.6519 | 8.2677 | 31.4487 | 13.9935 | 125 | 36.4204 | 70.4842 | 104.7639
15523 | 954.234 | 8.1688 | 16.5534 | 87.8762 | -9.7254 | 10.4497 | 72.0752 | 3.1458 |  | 13.5403 | 49.5017 | 16.6898 |  | 67.9397 | 145.7825 | 8.6175 | 28.2667 | 14.5946 | 127 | 36.178 | 71.8221 | 103.4892
15524 | 920.6005 | 11.6848 | 17.1434 | 90.6547 | -10.2148 | 10.45 | 71.2243 | 3.1188 |  | 14.0648 | 45.6215 | 8.4996 |  | 60.138 | 132.1324 | 8.772 | 27.7788 | 14.3048 | 123 | 32.8189 | 65.0776 | 102.3821
15525 | 888.5188 | 12.5264 | 16.5668 | 92.4513 | -10.1696 | 10.45 | 69.2293 | 3.0068 |  | 12.8786 | 42.443 | 7.2449 |  | 56.7869 | 129.7912 | 8.6299 | 27.6407 | 13.8841 | 125 | 32.7325 | 63.9834 | 101.9619
15526 | 877.3637 | 10.8154 | 16.0034 | 93.0157 | -10.1636 | 10.45 | 69.1234 | 2.9293 |  | 11.8951 | 39.9039 | 7.2822 |  | 55.1739 | 124.6331 | 8.4971 | 27.4937 | 13.5033 | 113 | 30.7078 | 62.7971 | 104.7099
15527 | 330.1219 | 4.3768 | 5.6097 | 32.0015 | 0.42774 | 0.002903 | 26.3841 | 1.124 |  | 4.5905 | 15.9902 | 2.7647 |  | 19.4173 | 47.5974 | 2.9798 | 9.5473 | 5.2813 | 108 | 3.3261 | 9.9614 | 10.8624
15528 | 879.6866 | 6.7359 | 16.098 | 90.2775 | -10.5322 | 10.45 | 66.3916 | 2.83 |  | 13.4565 | 38.9728 | 6.7332 |  | 50.8484 | 116.3342 | 9.3325 | 27.1842 | 11.9292 | 106 | 28.174 | 59.3585 | 101.2166
15529 | 884.7234 | 5.9332 | 16.2801 | 90.251 | -11.6325 | 11.3997 | 66.018 | 3.0729 |  | 14.1566 | 41.1138 | 6.4411 |  | 46.7043 | 119.7167 | 9.4514 | 27.2562 | 11.783 | 106 | 27.0898 | 59.3869 | 104.6609
15530 | 868.4632 | 4.1298 | 16.2776 | 90.4282 | -10.6363 | 10.4503 | 67.1046 | 3.2956 |  | 14.1272 | 43.2669 | 6.8225 |  | 44.7406 | 121.5203 | 9.2932 | 27.1873 | 11.8498 | 110 | 26.9798 | 59.4769 | 101.5185
15531 | 852.3934 | 2.5957 | 16.2773 | 91.8354 | -11.6394 | 11.3997 | 67.8881 | 3.3038 |  | 14.1353 | 43.6587 | 6.7573 |  | 43.1432 | 116.86 | 9.2024 | 27.0726 | 11.892 | 103 | 28.4281 | 59.4332 | 98.8601
15532 | 857.0681 | 2.8114 | 18.5468 | 93.0893 | -10.6397 | 10.4503 | 65.5025 | 3.357 |  | 14.8839 | 42.7078 | 6.4188 |  | 43.0243 | 112.6932 | 9.1946 | 27.8975 | 11.7974 | 106 | 27.1992 | 59.7125 | 109.632
15533 | 888.8585 | 3.847 | 25.7781 | 91.2348 | -11.6381 | 11.3997 | 67.318 | 3.277 |  | 21.9213 | 41.0319 | 7.924 |  | 46.9568 | 114.6866 | 9.3542 | 28.6393 | 11.8949 | 105 | 27.311 | 73.2013 | 118.4171
15534 | 935.0075 | 5.3432 | 48.6695 | 95.5958 | -11.6414 | 11.4 | 81.504 | 3.3998 |  | 34.772 | 47.575 | 13.9841 |  | 80.4159 | 130.9833 | 12.9052 | 27.924 | 14.8444 | 178 | 36.0186 | 72.7534 | 133.7723
15535 | 1013.0595 | 12.0537 | 71.9016 | 99.5529 | -20.404 | 19.9476 | 90.8299 | 4.1381 |  | 42.7087 | 64.0472 | 21.6624 |  | 121.8009 | 180.7343 | 26.7952 | 29.225 | 15.5519 | 285 | 48.7361 | 93.8 | 154.0352
15536 | 1108.107 | 17.2998 | 91.2694 | 106.9364 | -20.4323 | 19.95 | 101.9443 | 5.2167 |  | 50.1742 | 74.7128 | 32.1659 |  | 150.8114 | 234.4939 | 37.0413 | 33.4206 | 16.499 | 327 | 58.7037 | 111.9414 | 165.8016
15537 | 1186.4459 | 14.661 | 100.6024 | 117.9543 | -22.6429 | 21.8495 | 121.1466 | 5.4605 |  | 53.3468 | 79.645 | 37.6203 |  | 167.6281 | 272.7729 | 39.731 | 37.5877 | 17.6666 | 334 | 61.384 | 127.2435 | 186.3657
15538 | 1241.6787 | 10.9105 | 102.5861 | 127.0711 | -22.6433 | 21.85 | 138.8044 | 5.5481 |  | 51.3422 | 84.169 | 38.998 |  | 180.2404 | 297.0927 | 40.3587 | 40.8884 | 17.6239 | 360 | 64.9837 | 143.512 | 184.1958
15539 | 1258.0408 | 9.1619 | 108.7685 | 124.4373 | -25.382 | 24.6992 | 143.9457 | 5.5087 |  | 56.4643 | 84.7347 | 38.0549 |  | 190.9799 | 304.1461 | 40.8697 | 41.4509 | 17.5822 | 352 | 63.1303 | 160.1807 | 181.3027
15540 | 1268.5109 | 10.1866 | 107.7683 | 122.7107 | -22.6111 | 22.8005 | 139.1195 | 4.9662 |  | 54.7693 | 82.8782 | 37.4155 |  | 191.6998 | 293.9867 | 41.7181 | 41.3373 | 17.7984 | 352 | 58.9367 | 142.2981 | 167.9781
15541 | 1244.311 | 13.6195 | 105.1577 | 127.155 | -19.7867 | 20.9005 | 131.945 | 5.7963 |  | 53.9757 | 83.3802 | 38.7934 |  | 191.0406 | 285.5094 | 42.5314 | 42.3858 | 18.3132 | 285 | 66.4087 | 146.7318 | 179.2939
15542 | 1243.5464 | 14.4518 | 106.2117 | 131.4269 | -17.312 | 19.0005 | 124.5146 | 5.8572 |  | 53.7651 | 85.2859 | 38.1956 |  | 191.1513 | 281.1674 | 42.3483 | 42.4912 | 18.7184 | 284 | 68.2152 | 150.2047 | 179.0395
15543 | 1235.7546 | 10.5671 | 105.9454 | 124.507 | -17.1089 | 19 | 119.5494 | 4.5343 |  | 48.2854 | 85.6558 | 32.6504 |  | 183.5156 | 274.8712 | 40.3983 | 41.4981 | 18.7097 | 261 | 63.2656 | 145.6258 | 177.0512
15544 | 1189.6303 | 7.5927 | 102.1564 | 115.7689 | -14.036 | 16.1508 | 100.08 | 4.0865 |  | 39.8993 | 77.5812 | 25.8098 |  | 168.942 | 252.7291 | 31.0707 | 40.197 | 18.1195 | 236 | 57.2141 | 134.1106 | 157.3246
15545 | 1138.0239 | 5.834 | 100.5248 | 109.3952 | -6.9422 | 9.5018 | 69.1385 | 2.5279 |  | 35.2622 | 62.4756 | 18.9046 |  | 140.5304 | 227.2489 | 17.6155 | 37.0173 | 17.2134 | 214 | 50.3887 | 106.0517 | 128.6513
15546 | 1103.6849 | 5.513 | 97.9802 | 103.8353 | -7.0117 | 9.5 | 65.3261 | 2.311 |  | 26.8102 | 54.7223 | 15.4938 |  | 99.422 | 210.3925 | 10.9668 | 33.8578 | 16.2221 | 196 | 48.2736 | 93.773 | 124.0866
15547 | 1071.05 | 5.2272 | 82.1401 | 102.856 | -8.1566 | 10.4497 | 83.3137 | 2.7212 |  | 21.402 | 51.9 | 15.1041 |  | 78.2287 | 182.9353 | 10.0863 | 31.4266 | 14.9427 | 175 | 46.9372 | 86.8567 | 113.1257
15548 | 1023.3331 | 6.8147 | 46.3949 | 101.5894 | -8.3439 | 10.45 | 84.0308 | 2.6329 |  | 19.137 | 49.2728 | 14.2408 |  | 70.767 | 158.1543 | 9.5628 | 29.8883 | 13.9879 | 169 | 38.4369 | 82.2406 | 110.8233
15549 | 989.524 | 8.4768 | 26.1037 | 97.1851 | -9.6314 | 11.3997 | 75.4672 | 2.3627 |  | 17.2417 | 46.3531 | 12.336 |  | 64.4111 | 139.3489 | 9.3335 | 29.18 | 13.6113 | 163 | 29.6422 | 75.8501 | 108.9373
15550 | 965.4032 | 7.8678 | 23.1971 | 94.5134 | -9.8747 | 11.4 | 71.0249 | 2.3546 |  | 15.7917 | 41.525 | 9.7028 |  | 59.3335 | 126.7892 | 9.2767 | 29.166 | 12.9633 | 142 | 26.6876 | 61.4064 | 103.8182
15551 | 346.8342 | 0 | 7.8882 | 30.9754 | 0.93908 | 0.003167 | 25.6514 | 0.92826 |  | 5.751 | 15.8033 | 3.244 |  | 19.6879 | 47.8033 | 3.1006 | 9.76 | 4.826 | 124 | 2.7627 | 8.7407 | 10.3316
15552 | 929.2991 | 7.4677 | 22.7198 | 91.4689 | -10.1132 | 10.4503 | 68.8408 | 3.2677 |  | 14.4381 | 38.9634 | 8.3835 |  | 49.8697 | 122.2989 | 9.8211 | 28.7325 | 12.2846 | 116 | 26.3002 | 58.8121 | 103.7844
15553 | 928.2929 | 3.6477 | 22.7177 | 91.0529 | -11.5834 | 11.3997 | 66.691 | 3.3005 |  | 14.3856 | 39.6804 | 8.0971 |  | 47.0678 | 123.1849 | 9.9833 | 28.5158 | 12.3272 | 114 | 24.1009 | 59.8974 | 102.164
15554 | 909.8253 | 2.2837 | 23.0411 | 90.702 | -11.5769 | 11.4 | 57.1337 | 3.1897 |  | 14.3506 | 40.7959 | 8.1763 |  | 45.7998 | 126.1261 | 10.0936 | 28.4546 | 12.3049 | 116 | 23.699 | 58.9708 | 104.2326
15555 | 904.3121 | 2.2794 | 23.1065 | 92.0815 | -11.5845 | 11.4 | 56.302 | 3.2468 |  | 14.3923 | 40.5408 | 8.0525 |  | 44.8263 | 129.2684 | 9.9348 | 28.3117 | 12.3096 | 111 | 23.4721 | 58.2142 | 103.3843
15556 | 902.537 | 2.841 | 22.9023 | 91.7535 | -11.6405 | 11.4 | 66.4957 | 3.3453 |  | 15.245 | 41.4676 | 7.8502 |  | 44.7998 | 124.5612 | 9.8083 | 29.1577 | 12.3302 | 109 | 23.7436 | 58.7713 | 110.1169
15557 | 922.4706 | 4.0899 | 31.6506 | 90.6196 | -11.6416 | 11.4 | 63.096 | 3.4578 |  | 22.5678 | 46.0719 | 9.7652 |  | 49.365 | 123.9813 | 9.7801 | 29.9199 | 12.3322 | 108 | 23.4699 | 62.2863 | 116.2233
15558 | 975.6243 | 9.4838 | 47.0182 | 94.4394 | -11.6418 | 11.4 | 68.7703 | 3.733 |  | 35.6738 | 50.6001 | 14.5788 |  | 82.2639 | 131.6597 | 13.5153 | 29.2134 | 13.0768 | 165 | 31.2301 | 67.0165 | 135.9864
15559 | 1054.7977 | 16.955 | 72.0368 | 98.3289 | -22.6402 | 21.8471 | 93.1262 | 4.8779 |  | 40.7958 | 60.922 | 23.8241 |  | 125.3213 | 180.4633 | 26.1214 | 30.8437 | 14.7405 | 270 | 46.4164 | 91.1133 | 154.8896
15560 | 1129.119 | 14.8212 | 91.818 | 106.1083 | -21.6442 | 20.9003 | 109.8726 | 5.9242 |  | 43.3797 | 73.417 | 34.8501 |  | 158.6119 | 247.7327 | 37.3051 | 35.5117 | 16.3724 | 292 | 58.3696 | 113.6878 | 172.1207
15561 | 1216.9616 | 7.574 | 102.8786 | 116.994 | -23.6461 | 22.7995 | 111.71 | 6.071 |  | 49.2969 | 84.3893 | 37.7039 |  | 177.8603 | 288.0986 | 41.2141 | 38.5567 | 17.1763 | 385 | 56.3567 | 137.7084 | 182.3065
15562 | 1258.1706 | 5.0087 | 103.926 | 120.3969 | -21.5925 | 20.9005 | 122.1286 | 5.9398 |  | 52.1572 | 85.8408 | 38.7074 |  | 189.4766 | 301.4179 | 41.7722 | 40.4531 | 17.9045 | 346 | 54.6173 | 146.5587 | 192.1724
15563 | 1272.9842 | 4.9186 | 106.9865 | 121.5236 | -21.9565 | 21.8497 | 132.8356 | 5.764 |  | 53.0166 | 85.504 | 39.2147 |  | 201.8974 | 302.0636 | 41.9422 | 42.1815 | 18.5585 | 329 | 53.4823 | 161.8471 | 182.7843
15564 | 1256.658 | 5.9592 | 106.5415 | 121.644 | -24.8536 | 25.6489 | 125.5113 | 5.064 |  | 53.2241 | 86.5579 | 36.5943 |  | 203.7589 | 290.7222 | 42.0127 | 40.8744 | 18.8188 | 334 | 48.0156 | 143.5627 | 184.3269
15565 | 1243.3393 | 9.1238 | 103.6411 | 124.5676 | -22.0333 | 23.7505 | 122.4153 | 5.4012 |  | 52.5187 | 88.9067 | 36.6829 |  | 204.9214 | 286.9034 | 43.2469 | 41.1939 | 18.7933 | 315 | 56.224 | 152.2223 | 179.7745
15566 | 1251.2764 | 11.4999 | 102.4791 | 127.953 | -21.9533 | 23.75 | 116.9588 | 5.0568 |  | 51.2432 | 88.9812 | 37.8401 |  | 205.4115 | 290.3866 | 43.1174 | 42.2005 | 18.7186 | 282 | 59.439 | 146.1473 | 173.7248
15567 | 1237.4828 | 11.1793 | 104.6343 | 125.292 | -20.1777 | 21.8505 | 112.1376 | 5.0594 |  | 50.4235 | 87.8998 | 34.4415 |  | 198.8037 | 289.8876 | 41.2424 | 46.5609 | 18.7387 | 264 | 60.6812 | 139.3354 | 173.8073
15568 | 1191.7873 | 8.4216 | 103.7369 | 118.938 | -13.207 | 15.2018 | 105.6574 | 4.7401 |  | 44.5301 | 79.3885 | 26.7438 |  | 183.0066 | 264.7643 | 33.7514 | 49.3746 | 18.3913 | 250 | 58.6409 | 122.9214 | 157.1032
15569 | 1134.9656 | 6.3183 | 99.4298 | 109.9937 | -10.29 | 12.3508 | 91.5005 | 2.5011 |  | 36.0518 | 63.6899 | 17.5852 |  | 150.2596 | 230.3212 | 19.7115 | 45.6748 | 17.9868 | 199 | 49.8139 | 0 | 130.9245
15570 | 1093.0791 | 5.2873 | 91.9558 | 100.9815 | -10.2855 | 12.3534 | 88.5128 | 2.2368 |  | 26.5714 | 55.1834 | 11.6604 |  | 118.3847 | 211.234 | 13.3688 | 43.0192 | 16.6989 | 198 | 47.3182 | 102.7695 | 126.7218
15571 | 1059.0445 | 4.9118 | 70.3661 | 97.1914 | -10.4582 | 12.3466 | 89.7253 | 2.7265 |  | 19.2046 | 52.8478 | 10.0516 |  | 106.8532 | 184.2725 | 11.5924 | 39.4508 | 14.8027 | 175 | 40.5436 | 91.5774 | 110.4345
15572 | 1024.6612 | 4.3654 | 35.2657 | 93.7704 | -9.7172 | 11.4003 | 82.3604 | 2.6389 |  | 16.8852 | 49.5205 | 10.9431 |  | 100.606 | 159.9091 | 10.5082 | 37.796 | 14.0095 | 172 | 33.8371 | 86.596 | 105.8699
15573 | 990.0558 | 4.0855 | 22.2425 | 92.2503 | -9.541 | 11.4 | 66.4307 | 1.9159 |  | 16.1527 | 45.443 | 8.6034 |  | 90.1976 | 143.3017 | 10.424 | 37.0272 | 13.8495 | 159 | 28.2846 | 80.289 | 103.3706
15574 | 960.7234 | 3.7028 | 21.898 | 92.0406 | -9.2783 | 11.4 | 58.0498 | 2.154 |  | 13.765 | 40.2153 | 6.1857 |  | 82.435 | 133.5499 | 10.457 | 36.5631 | 13.2753 | 141 | 25.9581 | 65.3425 | 97.0402
15575 | 343.0126 | 0 | 7.3017 | 0 | 1.2859 | 0.003167 | 20.8363 | 0.96998 |  | 4.7041 | 15.1455 | 2.1573 |  | 0 | 0 | 3.4898 | 0 | 4.9298 | 127 | 2.7122 | 9.3925 | 10.751
15576 | 934.7666 | 7.3451 | 21.8851 | 92.4429 | -9.3935 | 11.3997 | 53.2917 | 1.9824 |  | 14.1719 | 38.9482 | 6.0235 |  | 70.1242 | 116.8471 | 10.2301 | 36.7949 | 11.6756 | 113 | 25.9759 | 64.8221 | 98.1524
15577 | 919.9782 | 9.3202 | 21.7115 | 91.889 | -8.4739 | 10.4503 | 53.4064 | 2.1989 |  | 14.7774 | 38.8156 | 5.8792 |  | 65.6336 | 112.0953 | 10.5025 | 36.5275 | 11.598 | 111 | 25.4141 | 59.7374 | 99.4934
15578 | 909.8213 | 8.3573 | 21.9547 | 91.4131 | -8.424 | 10.45 | 62.4968 | 2.6014 |  | 14.8436 | 38.653 | 5.7313 |  | 64.3015 | 114.4388 | 10.7732 | 36.4308 | 11.6143 | 110 | 24.3099 | 58.8159 | 100.5607
15579 | 910.7616 | 4.5559 | 19.3941 | 91.974 | -9.515 | 11.3997 | 67.2424 | 1.9516 |  | 14.9006 | 38.4585 | 5.7331 |  | 64.6623 | 114.0041 | 10.6471 | 36.3839 | 11.6297 | 108 | 23.7579 | 58.3951 | 100.8594
15580 | 906.3146 | 2.7596 | 17.0163 | 93.0041 | -9.5405 | 11.4 | 66.8688 | 2.0525 |  | 15.7067 | 38.2592 | 5.7097 |  | 64.8959 | 110.3721 | 10.4238 | 36.306 | 11.6515 | 104 | 23.8614 | 58.4768 | 100.7361
15581 | 909.9962 | 3.7298 | 24.4605 | 92.3164 | -8.618 | 10.4503 | 67.173 | 2.8091 |  | 23.8196 | 31.2848 | 8.8419 |  | 69.2859 | 113.656 | 10.1146 | 36.1277 | 11.6386 | 102 | 23.7553 | 62.6418 | 112.4356
15582 | 954.7608 | 5.4129 | 41.9811 | 96.5028 | -20.0106 | 20.8971 | 79.0746 | 3.3112 |  | 36.1758 | 47.6531 | 13.0843 |  | 91.4028 | 124.5593 | 13.8511 | 36.3883 | 11.6414 | 175 | 29.576 | 68.7869 | 128.5932
15583 | 1036.303 | 10.1231 | 71.3038 | 99.558 | -25.0016 | 24.6989 | 98.0845 | 3.7255 |  | 42.9559 | 61.2057 | 20.9453 |  | 126.4524 | 175.6307 | 26.58 | 38.3949 | 12.3948 | 282 | 43.586 | 89.666 | 155.8781
15584 | 1131.4234 | 14.9845 | 89.396 | 107.8004 | -27.6446 | 26.5995 | 114.9664 | 4.6049 |  | 46.7419 | 74.7186 | 32.728 |  | 157.8164 | 247.9887 | 35.3694 | 42.5942 | 14.5171 | 325 | 55.564 | 113.0923 | 166.0412
15585 | 1199.9236 | 16.6703 | 97.1706 | 117.2006 | -27.7813 | 27.5497 | 119.3126 | 4.5507 |  | 50.9182 | 82.9869 | 37.2571 |  | 181.1694 | 285.7045 | 41.3511 | 46.5351 | 16.6046 | 378 | 56.4163 | 128.8056 | 182.6605
15586 | 1240.5345 | 15.2996 | 103.106 | 123.5808 | -25.533 | 26.6003 | 128.4582 | 4.8174 |  | 51.6813 | 89.2643 | 37.2416 |  | 191.9128 | 305.3581 | 41.7905 | 51.3621 | 17.9939 | 357 | 57.3725 | 136.9314 | 185.2581
15587 | 1271.8086 | 11.8664 | 109.0167 | 124.1094 | -20.9587 | 22.8011 | 134.323 | 4.7508 |  | 56.1127 | 94.3721 | 37.5519 |  | 200.2796 | 306.7676 | 39.0961 | 52.5971 | 18.3783 | 339 | 59.8512 | 147.9857 | 187.5257
15588 | 1259.2776 | 8.966 | 110.9882 | 122.716 | -21.8479 | 23.7497 | 127.5998 | 4.7059 |  | 53.6033 | 96.4104 | 35.5054 |  | 200.2375 | 306.2751 | 40.2628 | 50.8806 | 18.6122 | 368 | 60.0622 | 137.7608 | 191.796
15589 | 1245.2239 | 8.8876 | 111.6125 | 127.4735 | -22.8502 | 24.6997 | 128.3905 | 5.618 |  | 51.7854 | 95.8524 | 37.2764 |  | 200.789 | 303.0477 | 42.459 | 52.0296 | 19.3585 | 348 | 67.515 | 149.2264 | 179.3867
15590 | 1264.3592 | 10.7385 | 115.5266 | 132.4065 | -20.8922 | 22.8005 | 132.7397 | 5.2496 |  | 51.7056 | 93.9595 | 39.1184 |  | 202.2634 | 292.3299 | 41.8912 | 53.9401 | 19.5283 | 325 | 70.0445 | 151.4149 | 178.719
15591 | 1256.3341 | 10.2949 | 113.8484 | 132.9281 | -21.9371 | 23.7497 | 127.0516 | 5.015 |  | 48.8152 | 93.1767 | 33.7891 |  | 197.3106 | 289.0036 | 39.0484 | 53.1757 | 18.8406 | 294 | 67.6241 | 155.7086 | 173.7937
15592 | 1197.6643 | 7.1991 | 108.7202 | 128.5883 | -17.8532 | 19.9511 | 110.3352 | 4.4428 |  | 44.6746 | 86.4363 | 24.646 |  | 183.8189 | 264.1818 | 30.8891 | 51.4259 | 17.334 | 257 | 60.973 | 139.966 | 155.4652
15593 | 1135.6844 | 6.0783 | 105.2053 | 120.3984 | -11.7502 | 14.2516 | 87.0391 | 4.1597 |  | 36.319 | 68.4479 | 22.2126 |  | 150.517 | 245.9985 | 17.1709 | 47.5264 | 16.3482 | 213 | 49.5093 | 113.0173 | 135.8171
15594 | 1094.4601 | 5.935 | 100.2141 | 110.071 | -9.7682 | 12.3505 | 76.8547 | 3.3252 |  | 26.6326 | 58.4571 | 22.8586 |  | 112.0396 | 236.1245 | 10.7812 | 44.1535 | 15.9178 | 232 | 45.1697 | 103.0873 | 135.5701
15595 | 1050.1271 | 5.1279 | 78.444 | 104.4208 | -8.8 | 11.4003 | 69.3168 | 2.9732 |  | 22.5649 | 55.7241 | 18.5029 |  | 94.3329 | 204.6638 | 9.8344 | 39.8899 | 14.7048 | 211 | 39.9619 | 92.8795 | 125.344
15596 | 1017.0212 | 6.7013 | 42.1571 | 100.566 | -9.6572 | 12.3497 | 63.0986 | 2.0451 |  | 20.7312 | 51.9142 | 12.455 |  | 88.094 | 173.9774 | 9.3651 | 37.4331 | 13.831 | 202 | 34.7134 | 86.7877 | 120.11
15597 | 989.0749 | 6.8355 | 24.9869 | 95.49 | -10.5053 | 13.2997 | 64.3243 | 1.4111 |  | 17.4182 | 46.9449 | 10.9977 |  | 71.9499 | 153.9646 | 9.3329 | 36.6995 | 13.3197 | 188 | 30.1846 | 82.631 | 115.1426
15598 | 959.7192 | 4.3022 | 23.0745 | 93.2363 | -9.5275 | 12.3503 | 59.6765 | 2.0995 |  | 13.935 | 41.0841 | 10.7531 |  | 59.0031 | 144.0615 | 9.2354 | 36.0983 | 13.3221 | 148 | 27.7112 | 65.8689 | 112.0495
15599 | 351.3439 | 0 | 7.983 | 0 | 1.6172 | 0.003431 | 21.0114 | 0.97143 |  | 4.9093 | 15.9776 | 3.9688 |  | 0 | 0 | 3.161 | 0 | 5.2676 | 135 | 2.9541 | 9.5234 | 12.991
15600 | 916.8387 | 2.1432 | 22.6633 | 92.7929 | -6.6523 | 9.4997 | 63.2528 | 1.9778 |  | 14.2426 | 38.0629 | 6.7353 |  | 52.9127 | 128.4882 | 8.9212 | 36.0001 | 13.2337 | 119 | 25.6667 | 61.9788 | 109.7672
15601 | 913.1634 | 2.1301 | 22.7275 | 92.8131 | -5.5956 | 8.5503 | 57.2254 | 1.9026 |  | 14.4269 | 38.0488 | 6.7413 |  | 50.3143 | 124.1074 | 8.6813 | 35.8718 | 12.9493 | 117 | 23.3008 | 60.9978 | 111.6187
15602 | 911.5192 | 2.1133 | 22.3638 | 92.853 | -6.516 | 9.4997 | 63.3218 | 2.1385 |  | 14.1409 | 38.3722 | 6.4688 |  | 47.5686 | 126.1658 | 8.9767 | 35.9414 | 10.2587 | 114 | 0 | 60.9217 | 112.0627
15603 | 908.256 | 2.1338 | 22.5222 | 92.7744 | -6.4809 | 9.5 | 64.0978 | 1.7594 |  | 14.195 | 37.6899 | 6.3998 |  | 46.5196 | 123.5239 | 9.2823 | 36.1762 | 10.021 | 109 | 22.8256 | 60.5804 | 111.9555
15604 | 364.5379 | 0.96124 | 8.5666 | 34.0742 | 1.9046 | 0.00264 | 24.8293 | 0.54485 |  | 5.9477 | 16.5101 | 2.6711 |  | 17.6144 | 51.8151 | 3.4955 | 13.5009 | 4.65 | 111 | 2.6863 | 10.2741 | 14.1305
15605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0
15606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0
15607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0
15608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0
15609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0
15610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0
15611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0
15612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0
15613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0
15614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0
15615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0
15616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 0
15617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0
15618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0
15619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0
15620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0
15621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0
15622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0
15623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0
15624 | [18 empty] | 132
15625 | [18 empty] | 126
15626 | [18 empty] | 114
15627 | [18 empty] | 108
15628 | [18 empty] | 107
15629 | [18 empty] | 107
15630 | [18 empty] | 182
15631 | [18 empty] | 249
15632 | [18 empty] | 298
15633 | [18 empty] | 347
15634 | [18 empty] | 350
15635 | [18 empty] | 365
15636 | [18 empty] | 374
15637 | [18 empty] | 316
15638 | [18 empty] | 286
15639 | [18 empty] | 286
15640 | [18 empty] | 274
15641 | [18 empty] | 249
15642 | [18 empty] | 232
15643 | [18 empty] | 211
15644 | [18 empty] | 198
15645 | [18 empty] | 191
15646 | [18 empty] | 174
15647 | [18 empty] | 171
15648 | [18 empty] | 169
15649 | [18 empty] | 154
15650 | [18 empty] | 160
15651 | [18 empty] | 168
15652 | [18 empty] | 156
15653 | [18 empty] | 152
15654 | [18 empty] | 129
15655 | [18 empty] | 122
15656 | [18 empty] | 126
15657 | [18 empty] | 132
15658 | [18 empty] | 164
15659 | [18 empty] | 167
15660 | [18 empty] | 160
15661 | [18 empty] | 166
15662 | [18 empty] | 179
15663 | [18 empty] | 190
15664 | [18 empty] | 196
15665 | [18 empty] | 195
15666 | [18 empty] | 197
15667 | [18 empty] | 198
15668 | [18 empty] | 183
15669 | [18 empty] | 166
15670 | [18 empty] | 155
15671 | [18 empty] | 127
15672 | [18 empty] | 138
15673 | [18 empty] | 136
15674 | [18 empty] | 129
15675 | [18 empty] | 117
15676 | [18 empty] | 110
15677 | [18 empty] | 100
15678 | [18 empty] | 102
15679 | [18 empty] | 104
15680 | [18 empty] | 111
15681 | [18 empty] | 155
15682 | [18 empty] | 173
15683 | [18 empty] | 166
15684 | [18 empty] | 176
15685 | [18 empty] | 187
15686 | [18 empty] | 172
15687 | [18 empty] | 177
15688 | [18 empty] | 185
15689 | [18 empty] | 171
15690 | [18 empty] | 157
15691 | [18 empty] | 151
15692 | [18 empty] | 137
15693 | [18 empty] | 141
15694 | [18 empty] | 128
15695 | [18 empty] | 115
15696 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0
15697 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0
15698 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0
15699 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0
15700 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0
15701 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0
15702 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0
15703 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0
15704 | 978.3615 | 0 | 0 | 0 | -11.2704 | 10.7069 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0
15705 | 1109.2117 | 6.3029 | 86.8867 | 122.736 | -14.4006 | 17.1012 | 104.4822 | 4.281 |  | 39.5244 | 70.7433 | 29.4211 |  | 155.9588 | 249.0819 | 31.9045 | 43.909 | 15.9777 | 346 | 65.6763 | 134.3396 | 173.9646
15706 | 1222.4791 | 6.6653 | 104.6509 | 135.8651 | -15.3116 | 18.0497 | 119.7897 | 4.824 |  | 46.6636 | 87.2125 | 38.7072 |  | 192.063 | 310.1531 | 40.3617 | 49.3314 | 19.1049 | 341 | 71.6598 | 142.8352 | 191.7436
15707 | 1260.0124 | 6.6781 | 110.8786 | 134.6633 | -15.3394 | 18.05 | 120.0329 | 4.7535 |  | 45.2816 | 88.6367 | 38.7804 |  | 201.8972 | 319.5109 | 40.156 | 51.1245 | 19.3823 | 323 | 69.9523 | 163.891 | 184.9512
15708 | 1238.46 | 8.4446 | 113.2778 | 131.6544 | -15.267 | 18.05 | 119.801 | 5.5491 |  | 39.7769 | 91.1452 | 38.0506 |  | 205.2709 | 315.0954 | 40.0239 | 50.8352 | 19.3933 | 379 | 66.5151 | 147.5259 | 183.7689
15709 | 1219.2734 | 8.92 | 111.6438 | 133.5639 | -14.1329 | 17.1003 | 130.4755 | 6.4641 |  | 41.7012 | 91.8487 | 38.4749 |  | 203.5365 | 310.0954 | 39.768 | 49.9033 | 19.5348 | 374 | 72.8619 | 145.1548 | 175.6692
15710 | 1224.4499 | 7.6325 | 112.2289 | 137.8643 | -15.0848 | 18.0497 | 131.4646 | 5.6523 |  | 45.3535 | 90.7395 | 38.3425 |  | 198.7109 | 307.8831 | 39.5435 | 50.3186 | 20.8901 | 314 | 74.2498 | 147.5656 | 174.9364
15711 | 1219.1628 | 5.6468 | 111.8056 | 135.2066 | -15.0205 | 18.05 | 120.131 | 4.734 |  | 38.2589 | 88.952 | 35.7377 |  | 195.9544 | 305.3336 | 38.9396 | 50.0112 | 19.852 | 266 | 74.8222 | 142.8708 | 166.9827
15712 | 1179.448 | 4.7439 | 108.2218 | 126.0013 | -11.8629 | 15.2008 | 100.5723 | 4.9856 |  | 32.6618 | 80.0599 | 30.5059 |  | 188.0809 | 283.1968 | 30.2393 | 48.9783 | 18.3761 | 257 | 73.859 | 135.1299 | 145.9707
15713 | 1117.9321 | 5.0773 | 103.1215 | 116.2087 | -6.7202 | 10.4513 | 79.1243 | 3.0626 |  | 28.0009 | 62.581 | 26.2352 |  | 149.8435 | 240.8661 | 17.0432 | 46.1498 | 17.7458 | 225 | 61.6795 | 119.4799 | 126.5381
15714 | 1071.0722 | 5.525 | 97.0622 | 108.6493 | -3.8868 | 7.6029 | 79.2313 | 2.3188 |  | 21.6684 | 53.6929 | 26.5424 |  | 110.2817 | 213.064 | 11.2157 | 43.7034 | 16.3794 | 222 | 53.2005 | 102.526 | 122.6065
15715 | 1031.9856 | 5.5234 | 78.1737 | 103.5007 | -5.1813 | 8.5476 | 77.6888 | 1.8381 |  | 19.4854 | 51.334 | 26.3539 |  | 94.7833 | 192.386 | 9.4379 | 40.7865 | 14.9837 | 191 | 46.4519 | 97.5835 | 113.894
15716 | 991.3157 | 4.7518 | 49.8584 | 98.5924 | -5.4295 | 8.55 | 53.9256 | 2.0306 |  | 19.3843 | 49.6458 | 25.5032 |  | 87.2103 | 166.6484 | 8.673 | 39.1267 | 14.2214 | 195 | 41.0731 | 89.6495 | 110.74
15717 | 973.2115 | 4.5104 | 39.6135 | 95.4874 | -4.5716 | 7.6003 | 48.8467 | 2.3186 |  | 18.4464 | 48.008 | 21.2421 |  | 74.2969 | 146.581 | 8.6478 | 37.9453 | 13.6963 | 184 | 33.9837 | 83.184 | 107.1766
15718 | 945.624 | 5.4294 | 38.2253 | 94.5137 | -5.6153 | 8.5497 | 52.7286 | 2.019 |  | 15.5361 | 41.9315 | 13.9862 |  | 60.9146 | 136.4755 | 8.5341 | 37.51 | 13.2121 | 154 | 27.8308 | 65.8334 | 104.541
15719 | 349.508 | 0 | 13.1407 | 0 | 1.608 | 0.002376 | 20.0555 | 0.75206 |  | 5.503 | 16.0871 | 4.3083 |  | 0 | 0 | 2.9289 | 0 | 5.1913 | 142 | 2.9313 | 9.8255 | 11.6319
15720 | 904.7163 | 2.1032 | 35.8911 | 93.7374 | -4.1579 | 7.6 | 53.0015 | 1.7429 |  | 12.345 | 37.9744 | 9.7996 |  | 51.1878 | 121.8854 | 8.4457 | 37.2279 | 12.9961 | 129 | 24.8821 | 57.6908 | 104.6176
15721 | 909.0031 | 2.1066 | 35.5736 | 93.7063 | -4.0079 | 7.6 | 47.9696 | 2.1756 |  | 12.9358 | 38.6745 | 9.7308 |  | 48.526 | 114.7182 | 8.1411 | 36.8582 | 12.3304 | 123 | 22.5424 | 57.3933 | 105.533
15722 | 900.3907 | 2.0948 | 35.6285 | 93.4847 | -3.8684 | 7.6 | 49.7172 | 1.8692 |  | 12.8006 | 38.7048 | 9.691 |  | 48.3214 | 115.4471 | 8.3427 | 36.7006 | 11.8673 | 120 | 22.4052 | 57.1092 | 101.9535
15723 | 890.8292 | 2.0936 | 35.4995 | 93.2781 | -3.757 | 7.6 | 54.5221 | 1.3096 |  | 12.7532 | 38.8149 | 9.8517 |  | 47.95 | 119.2531 | 8.3407 | 36.6991 | 11.7974 | 115 | 26.6794 | 57.141 | 104.6151
15724 | 889.0483 | 2.6681 | 35.3075 | 93.3046 | -3.5168 | 7.6 | 54.4551 | 1.9618 |  | 13.4717 | 39.0065 | 9.7268 |  | 47.049 | 116.5878 | 8.2752 | 36.5837 | 11.7493 | 118 | 22.9609 | 57.2019 | 106.6384
15725 | 900.4103 | 3.9298 | 37.4005 | 93.4019 | -2.3232 | 6.6503 | 53.634 | 1.6976 |  | 17.896 | 40.6779 | 11.4716 |  | 50.0868 | 118.275 | 8.4283 | 36.4095 | 11.8165 | 112 | 22.8664 | 60.9073 | 115.6273
15726 | 939.7349 | 8.6589 | 48.0951 | 100.8061 | -4.5749 | 8.5495 | 64.9036 | 1.7638 |  | 24.6878 | 53.2316 | 14.9887 |  | 84.4407 | 132.6827 | 12.1296 | 36.7686 | 13.9527 | 200 | 30.4606 | 66.1335 | 134.2102
15727 | 999.6934 | 16.1947 | 75.775 | 105.7038 | -12.8747 | 16.1479 | 88.1404 | 3.4332 |  | 31.8444 | 71.1018 | 20.7918 |  | 129.3553 | 188.1874 | 24.873 | 40.2666 | 16.6525 | 284 | 46.312 | 94.2989 | 156.4044
15728 | 1096.0375 | 19.0932 | 93.0234 | 117.3191 | -15.0431 | 18.0495 | 106.8892 | 4.2515 |  | 37.9489 | 79.269 | 30.9188 |  | 160.7598 | 253.3911 | 33.9068 | 43.613 | 17.1582 | 321 | 56.08 | 122.6697 | 169.9057
15729 | 1186.7196 | 17.0217 | 101.5447 | 129.3446 | -17.3778 | 19.9495 | 115.3272 | 5.2011 |  | 45.1946 | 83.0826 | 37.0715 |  | 180.8432 | 284.5412 | 37.4365 | 47.437 | 17.6295 | 360 | 59.3549 | 138.8204 | 182.0385
15730 | 1228.4428 | 10.815 | 104.8248 | 133.4118 | -17.517 | 19.95 | 121.1207 | 5.0056 |  | 47.9259 | 88.3348 | 39.9111 |  | 191.8561 | 303.785 | 39.4744 | 50.0988 | 18.2289 | 357 | 64.9605 | 149.7934 | 193.4236
15731 | 1243.1133 | 5.9508 | 109.1568 | 133.4677 | -15.3453 | 18.0505 | 127.7309 | 5.1137 |  | 48.1733 | 91.1767 | 39.405 |  | 205.0062 | 317.9402 | 39.2546 | 51.9306 | 18.7628 | 329 | 64.707 | 168.1122 | 196.9997
15732 | 1244.8433 | 7.7869 | 111.0792 | 133.5148 | -15.2906 | 18.05 | 131.8877 | 5.7579 |  | 43.1504 | 91.8814 | 37.9868 |  | 208.1744 | 314.6727 | 39.9873 | 50.7205 | 19.1541 | 349 | 60.9848 | 152.1407 | 179.7281
15733 | 1256.4898 | 14.9051 | 108.7812 | 138.8653 | -14.5989 | 17.1003 | 135.4181 | 5.8307 |  | 41.6843 | 91.2402 | 38.4678 |  | 202.7789 | 308.9965 | 42.1585 | 51.8928 | 19.0525 | 304 | 63.3341 | 148.4955 | 190.7296
15734 | 1251.4499 | 11.5906 | 110.9124 | 144.2295 | -17.2962 | 18.0497 | 135.9471 | 5.9505 |  | 41.4018 | 90.4988 | 38.3551 |  | 200.9876 | 307.4506 | 43.2723 | 53.5479 | 18.9551 | 267 | 67.1797 | 148.0806 | 177.0501
15735 | 1248.0079 | 5.5838 | 108.8218 | 136.527 | -21.3838 | 20.8992 | 127.1868 | 4.985 |  | 40.4775 | 90.9698 | 34.96 |  | 197.2176 | 301.9135 | 42.3361 | 53.4296 | 19.2211 | 280 | 68.5945 | 146.4496 | 161.9319
15736 | 1181.7348 | 4.8048 | 105.1251 | 128.8347 | -18.42 | 18.0508 | 106.8489 | 3.9873 |  | 42.5756 | 81.6591 | 25.8249 |  | 184.4103 | 267.7982 | 34.0028 | 51.6937 | 19.1655 | 244 | 66.6643 | 136.3687 | 145.141
15737 | 1126.9809 | 5.2773 | 104.391 | 121.6984 | -9.6511 | 9.5024 | 78.0506 | 3.8184 |  | 35.0138 | 63.9886 | 19.2897 |  | 157.4405 | 229.8423 | 21.5969 | 47.692 | 19.1425 | 217 | 58.7314 | 113.9059 | 124.8774
15738 | 1090.7379 | 7.5533 | 99.0774 | 113.0183 | -8.6375 | 8.5503 | 64.9204 | 3.3737 |  | 24.8819 | 56.8724 | 15.8595 |  | 124.0943 | 208.5599 | 14.0093 | 44.6079 | 18.577 | 208 | 53.2651 | 102.4728 | 121.6172
15739 | 1039.9119 | 7.5075 | 73.3216 | 105.1887 | -9.6356 | 9.4997 | 62.4757 | 3.2193 |  | 20.2421 | 54.2947 | 14.28 |  | 106.7578 | 192.1442 | 10.6373 | 40.7562 | 16.4244 | 180 | 44.6049 | 94.9527 | 104.7414
15740 | 996.0446 | 5.2329 | 39.8939 | 101.7739 | -8.6395 | 8.5503 | 52.2646 | 2.1256 |  | 19.5244 | 50.9886 | 12.5459 |  | 95.3379 | 165.5261 | 8.9531 | 38.2184 | 14.9058 | 176 | 39.8491 | 88.7237 | 95.895
15741 | 963.5978 | 4.2021 | 28.2884 | 99.5366 | -9.6394 | 9.4997 | 55.9888 | 1.4836 |  | 17.9875 | 47.6692 | 8.5464 |  | 81.7635 | 147.3912 | 8.2077 | 37.4894 | 14.0805 | 171 | 33.2321 | 82.1059 | 94.467
15742 | 940.3375 | 3.6629 | 27.6594 | 96.6255 | -8.6405 | 8.5503 | 60.078 | 2.0903 |  | 15.5989 | 42.1617 | 6.5069 |  | 73.1812 | 138.1358 | 8.3571 | 37.4854 | 12.7917 | 152 | 28.6039 | 66.0421 | 91.7309
15743 | 340.7903 | 0 | 9.3441 | 31.6185 | 0.17327 | 0.002376 | 21.8121 | 0.93916 |  | 5.7219 | 16.2779 | 2.4438 |  | 24.4628 | 52.9355 | 2.8731 | 12.6065 | 4.7567 | 129 | 2.9943 | 9.4892 | 10.2147
15744 | [6 empty] | 53.5941 | [11 empty] | 121 | 23.6798 | 61.2205 | 90.6919
15745 | [6 empty] | 47.6384 | [11 empty] | 121 | 23.14 | 60.5109 | 92.2748
15746 | [6 empty] | 49.8658 | [11 empty] | 118 | 22.8363 | 60.0689 | 95.2565
15747 | [6 empty] | 52.7742 | [11 empty] | 112 | 22.9668 | 60.1107 | 92.4547
15748 | [6 empty] | 52.5366 | [11 empty] | 111 | 23.3516 | 60.2312 | 95.9537
15749 | [6 empty] | 46.7398 | [11 empty] | 104 | 23.6551 | 63.0313 | 105.7426
15750 | [6 empty] | 64.2721 | [11 empty] | 207 | 28.1995 | 68.2279 | 120.5732
15751 | [6 empty] | 91.3135 | [11 empty] | 261 | 47.022 | 93.249 | 146.3135
15752 | [6 empty] | 107.4956 | [11 empty] | 297 | 60.2076 | 118.7309 | 161.2895
15753 | [6 empty] | 120.2598 | [11 empty] | 376 | 66.9963 | 134.0459 | 181.4927
15754 | [6 empty] | 134.3434 | [11 empty] | 330 | 67.571 | 140.2393 | 172.133
15755 | [6 empty] | 141.3625 | [11 empty] | 340 | 63.214 | 148.1951 | 171.1296
15756 | [6 empty] | 144.8247 | [11 empty] | 353 | 59.5323 | 138.7232 | 175.9117
15757 | [6 empty] | 128.9506 | [11 empty] | 308 | 59.3605 | 141.6237 | 165.5849
15758 | [6 empty] | 124.2071 | [11 empty] | 272 | 61.7776 | 140.8621 | 160.9149
15759 | [6 empty] | 125.4467 | [11 empty] | 278 | 62.9837 | 134.462 | 159.7994
15760 | [6 empty] | 107.9448 | [11 empty] | 254 | 62.0191 | 128.1035 | 141.4359
15761 | [6 empty] | 89.9966 | [11 empty] | 225 | 57.2842 | 115.1629 | 113.6906
15762 | [6 empty] | 94.383 | [11 empty] | 209 | 53.438 | 106.7808 | 107.2052
15763 | [6 empty] | 95.2626 | [11 empty] | 191 | 48.2834 | 96.5825 | 102.4909
15764 | [6 empty] | 80.8301 | [11 empty] | 167 | 43.083 | 90.4543 | 100.6973
15765 | [6 empty] | 70.9353 | [11 empty] | 167 | 35.5686 | 84.4451 | 91.807
15766 | [6 empty] | 68.9554 | [11 empty] | 138 | 30.0198 | 68.8224 | 89.0267
15767 | [6 empty] | 25.6137 | [11 empty] | 127 | 3.2393 | 10.0371 | 10.1499
15768 | [18 empty] | 118
15769
15770
15771
15772
15773
15774
15775
15776
15777
15778
15779
15780
15781
15782
15783
15784
15785
15786
15787
15788
15789
15790
15791
15792
15793
15794
15795
15796
15797
15798
15799
15800
15801
15802
15803
15804
15805
15806
15807
15808
15809
15810
15811
15812
15813
15814
15815
15816
15817
15818
15819
15820
15821
15822
15823
15824
15825
15826
15827
15828
15829
15830
15831
15832
15833
15834
15835
15836
15837
15838
15839
15840
15841
15842
15843
15844
15845
15846
15847
15848
15849
15850
15851
15852
15853
15854
15855
15856
15857
15858
15859
15860
15861
15862
15863
15864
15865
15866
15867
15868
15869
15870
15871
15872
15873
15874
15875
15876
15877
15878
15879
15880
15881
15882
15883
15884
15885
15886
15887
15888
15889
15890
15891
15892
15893
15894
15895
15896
15897
15898
15899
15900
15901
15902
15903
15904
15905
15906
15907
15908
15909
15910
15911
15912
15913
15914
15915
15916
15917
15918
15919
15920
15921
15922
15923
15924
15925
15926
15927
15928
15929
15930
15931
15932
15933
15934
15935
15936
15937
15938
15939
15940
15941
15942
15943
15944
15945
15946
15947
15948
15949
15950
15951
15952
15953
15954
15955
15956
15957
15958
15959
15960
15961
15962
15963
15964
15965
15966
15967
15968
15969
15970
15971
15972
15973
15974
15975
15976
15977
15978
15979
15980
15981
15982
15983
15984
15985
15986
15987
15988
15989
15990
15991
15992
15993
15994
15995
15996
15997
15998
15999
16000
16001
16002
16003
16004
16005
16006
16007
16008
16009
16010
16011
16012
16013
16014
16015
16016
16017
16018
16019
16020
16021
16022
16023
16024
16025
16026
16027
16028
16029
16030
16031
16032
16033
16034
16035
16036
16037
16038
16039
16040
16041
16042
16043
16044
16045
16046
16047
16048
16049
16050
16051
16052
16053
16054
16055
16056
16057
16058
16059
16060
16061
16062
16063
16064
16065
16066
16067
16068
16069
16070
16071
16072
16073
16074
16075
16076
16077
16078
16079
16080
16081
16082
16083
16084
16085
16086
16087
16088
16089
16090
16091
16092
16093
16094
16095
16096
16097
16098
16099
16100
16101
16102
16103
16104
16105
16106
16107
16108
16109
16110
16111
16112
16113
16114
16115
16116
16117
16118
16119
16120
16121
16122
16123
16124
16125
16126
16127
16128
16129
16130
16131
16132
16133
16134
16135
16136
16137
16138
16139
16140
16141
16142
16143
16144
16145
16146
16147
16148
16149
16150
16151
16152
16153
16154
16155
16156
16157
16158
16159
16160
16161
16162
16163
16164
16165
16166
16167
16168
16169
16170
16171
16172
16173
16174
16175
16176
16177
16178
16179
16180
16181
16182
16183
16184
16185
16186
16187
16188
16189
16190
16191
16192
16193
16194
16195
16196
16197
16198
16199
16200
16201
16202
16203
16204
16205
16206
16207
16208
16209
16210
16211
16212
16213
16214
16215
16216
16217
16218
16219
16220
16221
16222
16223
16224
16225
16226
16227
16228
16229
16230
16231
16232
16233
16234
16235
16236
16237
16238
16239
16240
16241
16242
16243
16244
16245
16246
16247
16248
16249
16250
16251
16252
16253
16254
16255
16256
16257
16258
16259
16260
16261
16262
16263
16264
16265
16266
16267
16268
16269
16270
16271
16272
16273
16274
16275
16276
16277
16278
16279
16280
16281
16282
16283
16284
16285
16286
16287
16288
16289
16290
16291
16292
16293
16294
16295
16296
16297
16298
16299
16300
16301
16302
16303
16304
16305
16306
16307
16308
16309
16310
16311
16312
16313
16314
16315
16316
16317
16318
16319
16320
16321
16322
16323
16324
16325
16326
16327
16328
16329
16330
16331
16332
16333
16334
16335
16336
16337
16338
16339
16340
16341
16342
16343
16344
16345
16346
16347
16348
16349
16350
16351
16352
16353
16354
16355
16356
16357
16358
16359
16360
16361
16362
16363
16364
16365
16366
16367
16368
16369
16370
16371
16372
16373
16374
16375
16376
16377
16378
16379
16380
16381
16382
16383
16384
16385
16386
16387
16388
16389
16390
16391
16392
16393
16394
16395
16396
16397
16398
16399
16400
16401
16402
16403
16404
16405
16406
16407
16408
16409
16410
16411
16412
16413
16414
16415
16416
16417
16418
16419
16420
16421
16422
16423
16424
16425
16426
16427
16428
16429
16430
16431
16432
16433
16434
16435
16436
16437
16438
16439
16440
16441
16442
16443
16444
16445
16446
16447
16448
16449
16450
16451
16452
16453
16454
16455
16456
16457
16458
16459
16460
16461
16462
16463
16464
16465
16466
16467
16468
16469
16470
16471
16472
16473
16474
16475
16476
16477
16478
16479
16480
16481
16482
16483
16484
16485
16486
16487
16488
16489
16490
16491
16492
16493
16494
16495
16496
16497
16498
16499
16500
16501
16502
16503
16504
16505
16506
16507
16508
16509
16510
16511
16512
16513
16514
16515
16516
16517
16518
16519
16520
16521
16522
16523
16524
16525
16526
16527
16528
16529
16530
16531
16532
16533
16534
16535
16536
16537
16538
16539
16540
16541
16542
16543
16544
16545
16546
16547
16548
16549
16550
16551
16552
16553
16554
16555
16556
16557
16558
16559
16560
16561
16562
16563
16564
16565
16566
16567
16568
16569
16570
16571
16572
16573
16574
16575
16576
16577
16578
16579
16580
16581
16582
16583
16584
16585
16586
16587
16588
16589
16590
16591
16592
16593
16594
16595
16596
16597
16598
16599
16600
16601
16602
16603
16604
16605
16606
16607
16608
16609
16610
16611
16612
16613
16614
16615
16616
16617
16618
16619
16620
16621
16622
16623
16624
16625
16626
16627
16628
16629
16630
16631
16632
16633
16634
16635
16636
16637
16638
16639
16640
16641
16642
16643
16644
16645
16646
16647
16648
16649
16650
16651
16652
16653
16654
16655
16656
16657
16658
16659
16660
16661
16662
16663
16664
16665
16666
16667
16668
16669
16670
16671
16672
16673
16674
16675
16676
16677
16678
16679
16680
16681
16682
16683
16684
16685
16686
16687
16688
16689
16690
16691
16692
16693
16694
16695
16696
16697
16698
16699
16700
16701
16702
16703
16704
16705
16706
16707
16708
16709
16710
16711
16712
16713
16714
16715
16716
16717
16718
16719
16720
16721
16722
16723
16724
16725
16726
16727
16728
16729
16730
16731
16732
16733
16734
16735
16736
16737
16738
16739
16740
16741
16742
16743
16744
16745
16746
16747
16748
16749
16750
16751
16752
16753
16754
16755
16756
16757
16758
16759
16760
16761
16762
16763
16764
16765
16766
16767
16768
16769
16770
16771
16772
16773
16774
16775
16776
16777
16778
16779
16780
16781
16782
16783
16784
16785
16786
16787
16788
16789
16790
16791
16792
16793
16794
16795
16796
16797
16798
16799
16800
16801
16802
16803
16804
16805
16806
16807
16808
16809
16810
16811
16812
16813
16814
16815
16816
16817
16818
16819
16820
16821
16822
16823
16824
16825
16826
16827
16828
16829
16830
16831
16832
16833
16834
16835
16836
16837
16838
16839
16840
16841
16842
16843
16844
16845
16846
16847
16848
16849
16850
16851
16852
16853
16854
16855
16856
16857
16858
16859
16860
16861
16862
16863
16864
16865
16866
16867
16868
16869
16870
16871
16872
16873
16874
16875
16876
16877
16878
16879
16880
16881
16882
16883
16884
16885
16886
16887
16888
16889
16890
16891
16892
16893
16894
16895
16896
16897
16898
16899
16900
16901
16902
16903
16904
16905
16906
16907
16908
16909
16910
16911
16912
16913
16914
16915
16916
16917
16918
16919
16920
16921
16922
16923
16924
16925
16926
16927
16928
16929
16930
16931
16932
16933
16934
16935
16936
16937
16938
16939
16940
16941
16942
16943
16944
16945
16946
16947
16948
16949
16950
16951
16952
16953
16954
16955
16956
16957
16958
16959
16960
16961
16962
16963
16964
16965
16966
16967
16968
16969
16970
16971
16972
16973
16974
16975
16976
16977
16978
16979
16980
16981
16982
16983
16984
16985
16986
16987
16988
16989
16990
16991
16992
16993
16994
16995
16996
16997
16998
16999
17000
17001
17002
17003
17004
17005
17006
17007
17008
17009
17010
17011
17012
17013
17014
17015
17016
17017
17018
17019
17020
17021
17022
17023
17024
17025
17026
17027
17028
17029
17030
17031
17032
17033
17034
17035
17036
17037
17038
17039
17040
17041
17042
17043
17044
17045
17046
17047
17048
17049
17050
17051
17052
17053
17054
17055
17056
17057
17058
17059
17060
17061
17062
17063
17064
17065
17066
17067
17068
17069
17070
17071
17072
17073
17074
17075
17076
17077
17078
17079
17080
17081
17082
17083
17084
17085
17086
17087
17088
17089
17090
17091
17092
17093
17094
17095
17096
17097
17098
17099
17100
17101
17102
17103
17104
17105
17106
17107
17108
17109
17110
17111
17112
17113
17114
17115
17116
17117
17118
17119
17120
17121
17122
17123
17124
17125
17126
17127
17128
17129
17130
17131
17132
17133
17134
17135
17136
17137
17138
17139
17140
17141
17142
17143
17144
17145
17146
17147
17148
17149
17150
17151
17152
17153
17154
17155
17156
17157
17158
17159
17160
17161
17162
17163
17164
17165
17166
17167
17168
17169
17170
17171
17172
17173
17174
17175
17176
17177
17178
17179
17180
17181
17182
17183
17184
17185
17186
17187
17188
17189
17190
17191
17192
17193
17194
17195
17196
17197
17198
17199
17200
17201
17202
17203
17204
17205
17206
17207
17208
17209
17210
17211
17212
17213
17214
17215
17216
17217
17218
17219
17220
17221
17222
17223
17224
17225
17226
17227
17228
17229
17230
17231
17232
17233
17234
17235
17236
17237
17238
17239
17240
17241
17242
17243
17244
17245
17246
17247
17248
17249
17250
17251
17252
17253
17254
17255
17256
17257
17258
17259
17260
17261
17262
17263
17264
17265
17266
17267
17268
17269
17270
17271
17272
17273
17274
17275
17276
17277
17278
17279
17280
17281
17282
17283
17284
17285
17286
17287
17288
17289
17290
17291
17292
17293
17294
17295
17296
17297
17298
17299
17300
17301
17302
17303
17304
17305
17306
17307
17308
17309
17310
17311
17312
17313
17314
17315
17316
17317
17318
17319
17320
17321
17322
17323
17324
17325
17326
17327
17328
17329
17330
17331
17332
17333
17334
17335
17336
17337
17338
17339
17340
17341
17342
17343
17344
17345
17346
17347
17348
17349
17350
17351
17352
17353
17354
17355
17356
17357
17358
17359
17360
17361
17362
17363
17364
17365
17366
17367
17368
17369
17370
17371
17372
17373
17374
17375
17376
17377
17378
17379
17380
17381
17382
17383
17384
17385
17386
17387
17388
17389
17390
17391
17392
17393
17394
17395
17396
17397
17398
17399
17400
17401
17402
17403
17404
17405
17406
17407
17408
17409
17410
17411
17412
17413
17414
17415
17416
17417
17418
17419
17420
17421
17422
17423
17424
17425
17426
17427
17428
17429
17430
17431
17432
17433
17434
17435
17436
17437
17438
17439
17440
17441
17442
17443
17444
17445
17446
17447
17448
17449
17450
17451
17452
17453
17454
17455
17456
17457
17458
17459
17460
17461
17462
17463
17464
17465
17466
17467
17468
17469
17470
17471
17472
17473
17474
17475
17476
17477
17478
17479
17480
17481
17482
17483
17484
17485
17486
17487
17488
17489
17490
17491
17492
17493
17494
17495
17496
17497
17498
17499
17500
17501
17502
17503
17504
17505
17506
17507
17508
17509
17510
17511
17512
17513
17514
17515
17516
17517
17518
17519
17520
17521
17522
17523
17524
17525
17526
17527
17528
17529
17530
17531
17532
17533
17534
17535
17536
17537
17538
17539
17540
17541
17542
17543
17544
Note on B2: Kalid Yunus: this demand consists of Friskis and Svetis; hence Friskis is removed
Note on J2: Kalid Yunus: Data from UF
Note on K12144: Kalid Yunus: reading=54495,558469
Note on K12145: Kalid Yunus: Reading=21004,292339

## Loads, DERs, IEDs per bus
MV-ID number | LV-ID number | Building code (AH) | Building Name | Available resources | Available Measurement | Presence of Load | File Name historic consumption data | ID of data in the DB | Comments on historical data | ID of consumption Data from API | Presence of PVs ? | File Name historic production data | ID of production Data from API | Question to AH | TFO | GPS | Comment | Data_Pertinence | Data_Pertinence_production | Column1 | PV data | Load data | PV prediction | Load prediction
1 |  | 7:08 | connection to external grid | None | Total active power consumption Chalmers Campus Voltage per phase | NO | Chalmers test site\Historical data\Mätdata\Mätdata\Inkommande el campus |  | We have some historical data but it is not in AH API | INKOP_EL_SUM_PROD_PV | NO |  |  | is this the correct tag correct: O0007008_EL_901_PV2 | - | 57.68936959071839, 11.977282946239676
2 |  | 07:8.1 | rum 4026 (Kraftcentralen) | None | None | NO |  |  |  |  | NO |  |  |  | -
3 |  | 07:8.1.3 | rum 4023 (Kraftcentralen) | None | None | ??? |  |  |  |  | NO |  |  | Är det någon last ansluten hit? I cant find the measurement for this, I think it should be 2 transformers here but i cant find any data for those. | T08.5
4 | 39 | 7:19 | Karhus CFAB,Karhus studenter, Cadministration | Load | Active power consumption Voltage per phase Current per phase | YES | 9653 |  | No data for begining of 2019, a large peak in begining of january | O0007019_EL_SUM_CONS_PV | NO |  |  | Does this include data for kårhus and kårhus student as well? | T19.1 | 57.68889361071283, 11.974691932327556 |  | No data after 05/2019 | [6 empty] | 25, 26, 29 nodes : same building
5 | 40 | 7:23 | SB2 | Load Solar PV | Active power consumption Voltage per phase Current per phase | YES | 9614 |  |  | O0007023_EL_SUM_CONS_PV | YES | 16821 | O0007023_EL_SUM_PROD_PV |  | T23.1 | 57.687683561108855, 11.976344173083652 | [8 empty] | How to model the power injection/consumption from the blue area
5 | 40 | 7:26 | SB1 Arkitektur | Load Solar PV | Active power consumption Voltage per phase Current per phase | YES | 9658 |  |  | O0007026_EL_SUM_CONS_PV | YES | 16710 | O0007026_EL_SUM_PROD_PV |  | T23.2
6 | 7 | 7:27 | SB3 | Load Solar PV (Q control) | Active power consumption Voltage per phase Current per phase | YES | 9659 | O7:43 is included in O7:27 in external file |  | O0007027_EL_SUM_CONS_PV | YES | 16871 (norra) | O0007027_EL_SUM_PROD_PV | O0007027_EL_SUM_PROD_PV : is it the sum of the two pv panels production ? Or is it only norra ? If so | T27.2 | 57.68645053059342, 11.977481429706609 | [9 empty] | probably not possible to have all the measurements
6 | 7 | 7:43 | Phus | Load (EV charger + light) | Active power consumption Voltage per phase Current per phase | YES | 15755 | O7:43 is included in O7:27 in external file |  | O0007043_EL_SUM_CONS_PV | NO |  |  |  | T27.2 | 57.68645053059342, 11.977481429706609 | [9 empty] | agreagated
6 | 7 | 07:27.44 | AWL + PV on södra hallen | Load Solar PV Battery | Active power consumption Voltage per phase Current per phase | YES | 16991 |  | New building no historical data since 2019 | O0007044_EL_SUM_CONS_PV | YES | 16884 | O0007044_EL_SUM_PROD_PV |  | T27.2 | 57.685762309280555, 11.978436296118316 | located under 07:27 | Last months have a static value | I think there has been some communication errors here as well | [6 empty] | small area and small voltage deviations
8 | 9 | 07:29E | MC2 | Load | Active power consumption Voltage per phase Current per phase | YES | Chalmers test site\Historical data\Mätdata\Mätdata\MC2 |  | We have some historical data but it is not in AH system | O3060133_EL_SUM_CONS_PV | NO |  |  |  | T1, T3, T5 | 57.6911616280284, 11.97519082321022
10 |  | 07:8.1.1 | - | None |  | NO |  |  |  |  | NO |  |  |  | -
11 | 12 | 07:8.1.1.1 | Kraftcentral | Load Solar PV Heat pump * 2 CHP | Active power consumption Voltage per phase Current per phase | YES | 9513 |  |  | O0007008_EL_SUM_CONS_PV | YES | 16943 | O0007008_EL_SUM_PROD_PV | Förbrukningen för lokalkontoret är inkluderat i kraftcentralen i webport, hur ser det ut i historisk data? | T08.1, T08.3 | 57.68936959071839, 11.977282946239676
11 | 12 | 07:8.1.1.1 / 07:0888 | Lokalkontor | Load Controlable Ventilation | Active power consumption Voltage per phase Current per phase | YES | 9821 |  |  | O0007888_EL_001_PV2 | NO |  |  | Är förbrukningen för lokalkontoret inkluderat i kraftcentralen i den historiska datan? | T08.1, T08.3 | 57.68936959071839, 11.977282946239676
13 |  | 07:8.1.2 | - | None |  | NO |  |  |  |  | NO |  |  |  | -
14 | 15 | 7:06 | NyaMatte | Load | Active power consumption Voltage per phase Current per phase | YES | 14506 |  |  | O0007006_EL_SUM_CONS_PV | NO |  |  |  | T06.1 | 57.69022691242387, 11.977663819927612
14 | 15 | 7:17 | Bibliotek | Load Solar PV (Q control) | Active power consumption Voltage per phase Current per phase | YES | 9613 | in the external file this is also included in O7:06 |  | O0007017_EL_SUM_CONS_PV | YES | 16872 | O0007017_EL_SUM_PROD_PV | data also available here 07_17 external file | T06.1 | 57.690437640065284, 11.97860173793054 | Located under 07:06
16 | 17 | 7:18 | Idelara | Load | Active power consumption Voltage per phase Current per phase |  | 9652 |  |  | O0007018_EL_SUM_CONS_PV | NO |  |  |  | T11.2 | 57.68763768164879, 11.978323643339133
16 | 17 | 07:11B | Studentbostader | Load | Active power consumption Voltage per phase Current per phase | ??? | 9514 |  | The data file is empty |  | NO |  |  | Do we have any data for studentbostäder? Where is this consumption measured | T11.2 | 57.68763768164879, 11.978323643339133 |  | No data | This is owned by another landlord so they do probably not have any data for this building but im investigating. | [8 empty] | Node 7 : maybe part of node 5 ? Or not existing ?
16 | 17 | 7:24 | Edit | Load Solar PV (Q control) | Active power consumption Voltage per phase Current per phase | YES | 14497 |  |  | O0007024_EL_SUM_CONS_PV | YES | O7_24 external file | O0007024_EL_SUM_PROD_PV |  | T11.2 | 57.68763768164879, 11.978323643339133 | located under 07:11b
18 | 19 | 7:28 | Maskinteknik | Load Solar PV Battery HP | Active power consumption Voltage per phase Current per phase | YES | 9686 | in external file 07:28 include 07:22 but not O7:25 |  | O0007028_EL_SUM_CONS_PV | YES | O7_28 external file+E22D22:K23N23F22:K23C22:K23 | O0007028_EL_SUM_PROD_PV | OBS: In the realtime data consumption for HP at Maskin is merged with consumption kraftcentralen, is it the same for historical data? | T28.1, T28.3 | 57.689191815776, 11.978468482627191
18 | 19 | 7:25 | HB | Load | Active power consumption Voltage per phase Current per phase | YES | 9657 | in external file 07:28 include 07:22 but not O7:25 |  | O0007022_EL_SUM_CONS_PV | NO |  |  |  | T28.1, T28.3 | 57.689191815776, 11.978468482627191
18 | 19 | 7:22 | HA | Load | Active power consumption Voltage per phase Current per phase | YES | 9656 | in external file 07:28 include 07:22 but not O7:25 |  | O0007025_EL_SUM_CONS_PV | NO |  |  |  | T28.1, T28.3 | 57.689191815776, 11.978468482627191
21 | 24 | 7:01 | Fysik Origo | Load | Active power consumption Voltage per phase Current per phase | YES | 14505 |  |  | O0007001_EL_SUM_CONS_PV | NO |  |  |  | T01.1, T01.2 | 57.69007207990653, 11.975974028244467
22 | 23 | O11 | Fysik Soliden | Load | Active power consumption Voltage per phase Current per phase | YES | 14503 |  |  | O0011001_EL_SUM_CONS_PV | NO |  |  |  | T13.1 | 57.69022691242387, 11.975035255087162 |  | Strange data 24/01/2021 -> 23/02/2021 | There was some error in the communication system causing this issue. Cant do anything about it
22 | 23 | O05 | Polymerteknologi | Load | Active power consumption Voltage per phase Current per phase | YES | 9648 |  |  | O0007005_EL_SUM_CONS_PV | NO |  |  | Is this the same as IT gymnasiet villan? | ??? |  |  | Strange data 24/01/2021 -> 23/02/2021 | There was some error in the communication system causing this issue. Cant do anything about it | [7 empty] | hj
22 | 23 | O13 | Keramforskning | Load | Active power consumption Voltage per phase Current per phase | YES | 9738 |  |  | O0013001_EL_SUM_CONS_PV | NO |  |  | s this the same as IT gymnasiet? | ??? |  |  | Strange data 24/01/2021 -> 23/02/2021 | There was some error in the communication system causing this issue. Cant do anything about it
31 | 37 | 07:35(SF) | - | None |  | ??? | 9820 |  | The data file is empty |  | NO |  |  | Vi har ingen data för "ställverk förråd" | - |  |  | No data | It could be that there are no loads here.
33 | 34 | 7:12 | Elkraftteknik | Load | Active power consumption Voltage per phase Current per phase | YES | 9651 |  |  | O0007012_EL_SUM_CONS_PV | NO |  |  |  | T12.1, T12.2 | 57.68733659628452, 11.979782765041815
33 | 34 | 7:21 | HC | Load | Active power consumption Voltage per phase Current per phase | YES | 9655 |  |  | O0007021_EL_SUM_CONS_PV | NO |  |  |  | T12.1, T12.2 | 57.68733659628452, 11.979782765041815
33 | 34 | 7:14 | Gibraltar herrgard | Load | Active power consumption Voltage per phase Current per phase | YES | 9515 |  |  | O0007014_EL_SUM_CONS_PV | NO |  |  |  | T12.1, T12.2 | 57.68733659628452, 11.979782765041815 |  | Strange data 24/01/2021 -> 23/02/2021 | Im not sure why.
35 | 36 | 7:41 | GamlaMatte | Load | Active power consumption Voltage per phase Current per phase | YES | 9687 |  |  | O0007040_EL_SUM_CONS_PV | NO |  |  | Is this the same as eklandagatan 86 difference between 07:40 and 07:41? | T40.1 | 57.68553576690779, 11.981858794825294
[11 empty] | NO |  |  |  | -
25 | 28 | 07:4.1 | Kemi | Load Solar PV |  | We do not have separete measurements for this, part of 07:3/4 | 24/03/2021 : David will investigate the possibility to collect historic data from nodes 25,26,29 |  |  | included in 07:03/4 | There is only one plant at kemi i suggest to model this as 1 node. |  |  | No division between the transformers in your data
26 | 27 | 07:4.2 | Kemi | Load Solar PV |  | We do not have separete measurements for this, part of 07:3/4 | 24/03/2021 : David will investigate the possibility to collect historic data from nodes 25,26,29 |  |  | included in 07:03/4 | There is only one plant at kemi i suggest to model this as 1 node.
29 | 30 | 07:3/4 | Kemi | Load Solar PV | Active power consumption Voltage per phase Current per phase | YES | \Chalmers test site\Historical data\Mätdata\Mätdata\Kemi |  | We have some historical data but it is not in AH system. | O3060132_EL_SUM_CONS_PV | YES | Chalmers test site\Historical data\Mätdata\Mätdata\Kemi\Solceller | 24/03/2021 : David to provide the ID to collect these data in RT | Does this include PV production e.g. net consumption? | T04.6 | 57.691022665628765, 11.977301451630304
O7:17
38 kWp reactive
66 kWp re.
73 kWp
reactive
46 kWp
42 kWp
reactive
125 kWp
Reactive
(norra)
116 + 61 kWp
Reactive (södra+AWL)
16 kWp
248 kWp
reactive
25
26
8
29
1
33
31
2
22
21
4
11
10
13
18
14
16
5
6
35
3
99?
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AH API for historical data Reply: The python script (AH_data_import.py) Reply: Energislag_id: what each id means can be found in Energiportalen Light 2020-04-30.ppt. Reply: The colors: red means that something is wrong with the data (i.e. strange, missing, high peaks, etc). Green the data is checked and looks good. Reply: resolution 1 hour
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: for reading the real time data Reply: resolution 1 min Reply: it is the gross consumption not the net! Reply: The ITS API needs to be used to read these tags Reply: readAPI_AH.m (matlab file David has made for reading)
Note on H3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Données dispo dans le dossier "Historic Data", un fichier excel par point, nom précédé par "BID" Reply: Données météo également présentes
Note on D5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Info from el diagram (AH). You may check this and remove my comment. If wrong, leave it blank ('-')
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Info from el diagram (AH). You may check this and remove my comment. If wrong, leave it blank ('-')
Note on P6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Info in 'Transformers'. You may check this and remove my comment. If wrong, leave it blank ('-')
Note on B9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In reality this is on another trafo connected to node 5 but place it at node 40 for now
Note on N10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This should only be norra, södra is physically connected to O7:44
Note on N15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I will check if this also include CHP unit or only PV
Note on K24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The names are the other way around! 7022 for 7025, and the other way around!
Note on K25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The names are the other way around! 7022 for 7025, and the other way around!
Note on P28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which trafo?
Note on P29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which trafo?
Note on K30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I have asked for data, most probably there are no data here or it is included in O7:12
Note on H36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Asked for historical data
Note on K38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is including demand for O7:4:1 and O7:4:2
Note on N38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I have asked for data but this plant is owned by another rel estate owner.

## Important notes
no | Problem / Issue | Solution
1 | Electricity consumption for VKA1 is included in 07:08 although actual (electrical) connected to 07:28 | Remove meter XXX from 07:08 Add meter XXX to 07:28

## 07_44
Energy storage at bus 07:44 (AWL)
Capacities/limitations | Value | Comment | TAG
Peak power | Xx kW
Energy capacity | 200 kW
Ramprate
Control signals
Active power charge/discharge | X kW |  | O0007028_A_FERRO_POWER_SP
Activate external control | Binary 0/1 |  | O0007028_A_FERRO_ACTIVATE_CMD
Execute external command | Binary 0/1 | Should be set to 0 after execution | O0007028_A_FERRO_EXECUTE_CMD
O0007044_FERRO_GRIDFREQ_PV | O0007044_FERRO_GRIDFREQ_PV | O0007044_FERRO_GRIDFREQ_PV | O0007044_FERRO_GRIDFREQ_PV
Measurement
Active power |  |  | O0007044_EHUB_PBAT_PV
Grid Frequency |  |  | O0007044_FERRO_GRIDFREQ_PV
SoC
O0007044_EL_904_U1_PV
O0007044_EL_904_U2_PV
O0007044_EL_904_U3_PV

## Cable properties-reference
| R_ohm_per_km | L_mH_per_km | c_nf_per_km | max_i_kA
Al240 | 0.125 | 0.27 | 420 | 0.34
Al150 | 0.206 | 0.29 | 350 | 0.26
Al95 | 0.32 | 0.31 | 300 | 0.205
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This sheet is used for calculating the line properties Reply: Reference: Kraftkabel Handboken-Ericsson Cables. P. 124 for Resistance P. 127 for Inductance and capacitance P. 114 (Table 17) for max_i_kA